## Summary
Transmission capacity calculation of supply centers of IDGC of Centre - Belgorodenergo division following the results of measurements of peak loads in winter 2011 | [9 empty] | Transmission capacity calculation of supply centers of IDGC of Centre - Belgorodenergo division following the results of measurements of peak loads in winter 2011
[13 empty] | Table 1 | [12 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [10 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | P | Q | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
[5 empty] | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
1 | SS-110/35/10kV D.Polyana | 6.3 | 1297 | 572 | 1.4175 | 1.457 | 45 | 1.457 | 0 | 1.457 | 0.039469 | -0.033615 |  | 1 | SS-110/35/10kV D.Polyana | 6.3 | 0 | 1.4175 | 1.457 | 45 | -0.039469 | 0 | 1.457 | 0.039469 | -0.033615
| S nom MV, МVА | 6.3 | 920 | 370 | 0.99161 | 0.958 | 0 | 0.958 | 0 | 0.958 | -0.033615 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0.99161 | 0.958 | 0 | 0.033615 | 0 | 0.958 | -0.033615
| S nom LV, МVА | 6.3 | 377 | 202 | 0.42771 | 0.499 | 0 | 0.499 | 0 | 0.499 | 0.071293 |  |  |  | S nom LV, МVА | 6.3 | 0 | 0.42771 | 0.499 | 0 | -0.071293 | 0 | 0.499 | 0.071293
2 | SS-110/35/10kV Konshino | 6.3 | 323 | 171 | 0.36547 | 0.39 | 20 | 0.39 | 0 | 0.39 | 0.024528 | 0 |  | 2 | SS-110/35/10kV Konshino | 6.3 | 0 | 0.36547 | 0.39 | 20 | -0.024528 | 0 | 0.39 | 0.024528 | 0
| S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, МVА | 6.3 | 323 | 171 | 0.36547 | 0.39 | 0 | 0.39 | 0 | 0.39 | 0.024528 |  |  |  | S nom LV, МVА | 6.3 | 0 | 0.36547 | 0.39 | 0 | -0.024528 | 0 | 0.39 | 0.024528
3 | SS-110/35/10kV Orositelnaya | 16 | 12776 | 4356 | 13.4982 | 11.607 | 120 | 11.607 | 0 | 11.607 | -1.8912 | -1.8912 |  | 3 | SS-110/35/10kV Orositelnaya | 16 | 0 | 13.4982 | 11.607 | 120 | 1.8912 | 0 | 11.607 | -1.8912 | -1.8912
| S nom MV, МVА | 16 | 8266 | 2995 | 8.7919 | 8.606 | 0 | 8.606 | 0 | 8.606 | -0.18586 |  |  |  | S nom MV, МVА | 16 | 0 | 8.7919 | 8.606 | 0 | 0.18586 | 0 | 8.606 | -0.18586
| S nom LV, МVА | 16 | 4510 | 1361 | 4.7109 | 3.001 | 0 | 3.001 | 0 | 3.001 | -1.7099 |  |  |  | S nom LV, МVА | 16 | 0 | 4.7109 | 3.001 | 0 | 1.7099 | 0 | 3.001 | -1.7099
4 | SS-110/35/10kV Rovenki | 16 | 2483 | 1113 | 2.721 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.71896 | 0.71896 |  | 4 | SS-110/35/10kV Rovenki | 16 | 0 | 2.721 | 3.44 | 120 | -0.71896 | 0 | 3.44 | 0.71896 | 0.71896
| S nom MV, МVА | 16 | 2 | 0 | 0.002 | 4 | 0 | 4 | 0 | 4 | 3.998 |  |  |  | S nom MV, МVА | 16 | 0 | 0.002 | 4 | 0 | -3.998 | 0 | 4 | 3.998
| S nom LV, МVА | 16 | 2481 | 1113 | 2.7192 | 3.44 | 0 | 3.44 | 0 | 3.44 | 0.72079 |  |  |  | S nom LV, МVА | 16 | 0 | 2.7192 | 3.44 | 0 | -0.72079 | 0 | 3.44 | 0.72079
5 | SS-110/35/10kV Serebryanka | 10 | 866 | 344 | 0.93182 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.84818 | 0 |  | 5 | SS-110/35/10kV Serebryanka | 10 | 0 | 0.93182 | 1.78 | 45 | -0.84818 | 0 | 1.78 | 0.84818 | 0
| S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, MVА | 10 | 866 | 344 | 0.93182 | 1.78 | 0 | 1.78 | 0 | 1.78 | 0.84818 |  |  |  | S nom LV, MVА | 10 | 0 | 0.93182 | 1.78 | 0 | -0.84818 | 0 | 1.78 | 0.84818
6 | SS-35/10kV Afanasyevka | 2.5 | 880 | 320 | 0.93638 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.28998 | -0.28998 |  | 6 | SS-35/10kV Afanasyevka | 1.6 | 0 | 0.93638 | 0.6464 | 45 | 0.28998 | 0 | 0.6464 | -0.28998 | -0.28998
7 | SS-35/10kV Borisovka | 1.6 | 664 | 200 | 0.69347 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | -0.0099667 | -0.0099667 |  | 7 | SS-35/10kV Borisovka | 1.6 | 0 | 0.69347 | 0.6835 | 45 | 0.0099667 | 0 | 0.6835 | -0.0099667 | -0.0099667
8 | SS-35/10kV Borisy | 1.6 | 798 | 366 | 0.87793 | 0 | 20 | 0 | 0 | 0 | -0.87793 | -0.87793 |  | 8 | SS-35/10kV Borisy | 1.6 | 0 | 0.87793 | 0 | 20 | 0.87793 | 0 | 0 | -0.87793 | -0.87793
9 | SS-35/10kV Gostishchevo | 4 | 2680 | 1016 | 2.8661 | 2.64 | 80 | 2.64 | 0 | 2.64 | -0.22612 | -0.22612 |  | 9 | SS-35/10kV Gostishchevo | 4 | 0 | 2.8661 | 2.64 | 80 | 0.22612 | 0 | 2.64 | -0.22612 | -0.22612
10 | SS-35/10kV Gruzskoe | 1.6 | 612 | 288 | 0.67638 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.37362 | 0.37362 |  | 10 | SS-35/10kV Gruzskoe | 1.6 | 0 | 0.67638 | 1.05 | 80 | -0.37362 | 0 | 1.05 | 0.37362 | 0.37362
11 | SS-35/10kV Zemsnaryad | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | SS-35/10kV Zemsnaryad | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 348 | 120 | 0.36811 | 0 | 0 | 0 | 0 | 0 | -0.36811 | -0.36811 |  | 12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 0 | 0.36811 | 0 | 0 | 0.36811 | 0 | 0 | -0.36811 | -0.36811
13 | SS-35/10kV Kamyzino | 2.5 | 1184 | 784 | 1.42 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.87904 | -0.87904 |  | 13 | SS-35/10kV Kamyzino | 2.5 | 0 | 1.42 | 0.541 | 45 | 0.87904 | 0 | 0.541 | -0.87904 | -0.87904
14 | SS-35/10kV Koloskovo | 2.5 | 1712 | 544 | 1.7964 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.13375 | -0.13375 |  | 14 | SS-35/10kV Koloskovo | 2.5 | 0 | 1.7964 | 1.6626 | 45 | 0.13375 | 0 | 1.6626 | -0.13375 | -0.13375
15 | SS-35/10jkV Kryukovo | 2.5 | 1140 | 468 | 1.2323 | 1.55 | 45 | 1.55 | 0 | 1.55 | 0.31768 | 0.31768 |  | 15 | SS-35/10jkV Kryukovo | 2.5 | 0 | 1.2323 | 1.55 | 45 | -0.31768 | 0 | 1.55 | 0.31768 | 0.31768
16 | SS-35/10kV Kushchino | 1.6 | 360 | 132 | 0.38344 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.026663 | 0.026663 |  | 16 | SS-35/10kV Kushchino | 1.6 | 0 | 0.38344 | 0.4101 | 80 | -0.026663 | 0 | 0.4101 | 0.026663 | 0.026663
17 | SS-35/10kV Lopukhinka | 2.5 | 304 | 120 | 0.32683 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.080173 | 0.080173 |  | 17 | SS-35/10kV Lopukhinka | 2.5 | 0 | 0.32683 | 0.407 | 20 | -0.080173 | 0 | 0.407 | 0.080173 | 0.080173
18 | SS-35/10kV Malakeevo | 2.5 | 1032 | 564 | 1.1761 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.20394 | 0.20394 |  | 18 | SS-35/10kV Malakeevo | 2.5 | 0 | 1.1761 | 1.38 | 120 | -0.20394 | 0 | 1.38 | 0.20394 | 0.20394
19 | SS-35/10kV Murom | 2.5 | 1192 | 512 | 1.2973 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.24269 | 0.24269 |  | 19 | SS-35/10kV Murom | 2.5 | 0 | 1.2973 | 1.54 | 45 | -0.24269 | 0 | 1.54 | 0.24269 | 0.24269
20 | SS-35/10kV Nikolaevka | 2.5 | 672 | 304 | 0.73756 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.072864 | -0.072864 |  | 20 | SS-35/10kV Nikolaevka | 2.5 | 0 | 0.73756 | 0.6647 | 45 | 0.072864 | 0 | 0.6647 | -0.072864 | -0.072864
21 | SS-35/10kV Nikolskoe | 4 | 1632 | 408 | 1.6822 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.90223 | -0.90223 |  | 21 | SS-35/10kV Nikolskoe | 4 | 0 | 1.6822 | 0.78 | 120 | 0.90223 | 0 | 0.78 | -0.90223 | -0.90223
22 | SS-35/10kV Pokrovka | 2.5 | 576 | 204 | 0.61106 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.11094 | 0.11094 |  | 22 | SS-35/10kV Pokrovka | 4 | 0 | 0.61106 | 0.722 | 45 | -0.11094 | 0 | 0.722 | 0.11094 | 0.11094
23 | SS-35/10kV Pyatnitskoe | 4 | 2062 | 834 | 2.2243 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.38428 | -0.38428 |  | 23 | SS-35/10kV Pyatnitskoe | 4 | 0 | 2.2243 | 1.84 | 80 | 0.38428 | 0 | 1.84 | -0.38428 | -0.38428
24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 590 | 511 | 0.78053 | 1.676 | 80 | 1.676 | 0 | 1.676 | 0.89547 | 0.89547 |  | 24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 0 | 0.78053 | 1.676 | 80 | -0.89547 | 0 | 1.676 | 0.89547 | 0.89547
25 | SS-35/10kV Svistovka | 2.5 | 488 | 224 | 0.53695 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.15025 | 0.15025 |  | 25 | SS-35/10kV Svistovka | 2.5 | 0 | 0.53695 | 0.6872 | 45 | -0.15025 | 0 | 0.6872 | 0.15025 | 0.15025
26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 512 | 176 | 0.54141 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.18239 | 0.18239 |  | 26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 0 | 0.54141 | 0.7238 | 120 | -0.18239 | 0 | 0.7238 | 0.18239 | 0.18239
27 | SS-35/10kV Kharkovskaya | 2.5 | 572 | 244 | 0.62187 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.057832 | 0.057832 |  | 27 | SS-35/10kV Kharkovskaya | 2.5 | 0 | 0.62187 | 0.6797 | 120 | -0.057832 | 0 | 0.6797 | 0.057832 | 0.057832
Two- and more transformer substations | [13 empty] | 1: Two- and more transformer substations
28 | SS-110/6kV Automobile maintenance plant | 16+16 | 11055 | 5112 | 12.1797 | 3.561 | 45 | 8.6187 | 0 | 16.8 | 8.1813 | 8.1813 |  | 28 | SS-110/6kV Automobile maintenance plant | 16+16 | 0 | 12.1797 | 3.561 | 45 | 8.6187 | 0 | 16.8 | 8.1813 | 8.1813
29 | SS-110/35/10kV Aydar | 16+10 | 8005 | 3233 | 8.6332 | 8.95 | 120 | -0.31679 | 0 | 10.5 | 10.8168 | 10.5637 |  | 29 | SS-110/35/10kV Aydar | 16+10 | 0 | 8.6332 | 8.95 | 120 | -0.31679 | 0 | 10.5 | 10.8168 | 10.5637
| S nom MV, МVА | 16+10 | 6709 | 2685 | 7.2263 | 7.29 | 0 | -0.063666 | 0 | 10.5 | 10.5637 |  |  |  | S nom MV, МVА | 16+10 | 0 | 7.2263 | 7.29 | 0 | -0.063666 | 0 | 10.5 | 10.5637
| S nom LV, МVА | 16+10 | 1296 | 548 | 1.4071 | 1.66 | 0 | -0.2529 | 0 | 10.5 | 10.7529 |  |  |  | S nom LV, МVА | 16+10 | 0 | 1.4071 | 1.66 | 0 | -0.2529 | 0 | 10.5 | 10.7529
30 | SS-110/35/10kV Alexandrovka | 25+25 | 14291 | 5721 | 15.3936 | 8.37 | 80 | 7.0236 | 0 | 26.25 | 19.2264 | 19.2264 |  | 30 | SS-110/35/10kV Alexandrovka | 25+25 | 0 | 15.3936 | 8.37 | 80 | 7.0236 | 0 | 26.25 | 19.2264 | 19.2264
| S nom MV, МVА | 25+25 | 6817 | 2487 | 7.2565 | 6.697 | 0 | 0.55949 | 0 | 26.25 | 25.6905 |  |  |  | S nom MV, МVА | 25+25 | 0 | 7.2565 | 6.697 | 0 | 0.55949 | 0 | 26.25 | 25.6905
| S nom LV, МVА | 25+25 | 7474 | 3234 | 8.1437 | 1.673 | 0 | 6.4707 | 0 | 26.25 | 19.7793 |  |  |  | S nom LV, МVА | 25+25 | 0 | 8.1437 | 1.673 | 0 | 6.4707 | 0 | 26.25 | 19.7793
31 | SS-110/35/10kV Alexeevka | 25+25+25 | 39234 | 13535 | 41.503 | 5.322 | 120 | 36.181 | 0 | 52.5 | 16.319 | 16.319 |  | 31 | SS-110/35/10kV Alexeevka | 25+25+25 | 0 | 41.503 | 5.322 | 120 | 36.181 | 0 | 52.5 | 16.319 | 16.319
| S nom MV, МVА | 25+25+25 | 18194 | 4255 | 18.6849 | 3.102 | 0 | 15.5829 | 0 | 52.5 | 36.9171 |  |  |  | S nom MV, МVА | 25+25+25 | 0 | 18.6849 | 3.102 | 0 | 15.5829 | 0 | 52.5 | 36.9171
| S nom LV, МVА | 25+25+25 | 21040 | 9280 | 22.9957 | 2.22 | 0 | 20.7757 | 0 | 52.5 | 31.7243 |  |  |  | S nom LV, МVА | 25+25+25 | 0 | 22.9957 | 2.22 | 0 | 20.7757 | 0 | 52.5 | 31.7243
32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 8788 | 3690 | 9.5313 | 8.87 | 45 | 0.66127 | 0 | 10.5 | 9.8387 | 9.8387 |  | 32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 0 | 9.5313 | 8.87 | 45 | 0.66127 | 0 | 10.5 | 9.8387 | 9.8387
| S nom MV, МVА | 10+16 | 8463 | 3599 | 9.1965 | 8.867 | 0 | 0.32948 | 0 | 10.5 | 10.1705 |  |  |  | S nom MV, МVА | 10+16 | 0 | 9.1965 | 8.867 | 0 | 0.32948 | 0 | 10.5 | 10.1705
| S nom LV, МVА | 10+16 | 325 | 91 | 0.3375 | 0 | 0 | 0.3375 | 0 | 10.5 | 10.1625 |  |  |  | S nom LV, МVА | 10+16 | 0 | 0.3375 | 0 | 0 | 0.3375 | 0 | 10.5 | 10.1625
33 | SS-110/6kV Belgorod-1 | 40+40+40 | 28766 | 12827 | 31.4963 | 0 | 120 | 31.4963 | 0 | 84 | 52.5037 | 52.5037 |  | 33 | SS-110/6kV Belgorod-1 | 40+40+40 | 0 | 31.4963 | 0 | 120 | 31.4963 | 0 | 84 | 52.5037 | 52.5037
34 | SS-110/35/10kV Borisovka | 16+16 | 10972 | 4956 | 12.0394 | 11.433 | 120 | 0.60638 | 0 | 16.8 | 16.1936 | 5.6302 |  | 34 | SS-110/35/10kV Borisovka | 16+16 | 0 | 12.0394 | 11.433 | 120 | 0.60638 | 0 | 16.8 | 16.1936 | 5.6302
| S nom MV, МVА | 16+16 | 5280 | 2848 | 5.9991 | 8.133 | 0 | -2.1339 | 0 | 8.4 | 10.5339 |  |  |  | S nom MV, МVА | 16+8 | 0 | 5.9991 | 8.133 | 0 | -2.1339 | 0 | 8.4 | 10.5339
| S nom LV, МVА | 16+16 | 5692 | 2108 | 6.0698 | 3.3 | 0 | 2.7698 | 0 | 8.4 | 5.6302 |  |  |  | S nom LV, МVА | 16+8 | 0 | 6.0698 | 3.3 | 0 | 2.7698 | 0 | 8.4 | 5.6302
35 | SS-110/35/10kV V.Pokrovka | 10+10 | 9963 | 3940 | 10.7138 | 11.5 | 120 | -0.78623 | 0 | 10.5 | 11.2862 | 8.955 |  | 35 | SS-110/35/10kV V.Pokrovka | 10+10 | 0 | 10.7138 | 11.5 | 120 | -0.78623 | 0 | 10.5 | 11.2862 | 8.955
| S nom MV, МVА | 10+10 | 8666 | 3497 | 9.345 | 7.8 | 0 | 1.545 | 0 | 10.5 | 8.955 |  |  |  | S nom MV, МVА | 10+10 | 0 | 9.345 | 7.8 | 0 | 1.545 | 0 | 10.5 | 8.955
| S nom LV, МVА | 10+10 | 1297 | 443 | 1.3706 | 3.7 | 0 | -2.3294 | 0 | 10.5 | 12.8294 |  |  |  | S nom LV, МVА | 10+10 | 0 | 1.3706 | 3.7 | 0 | -2.3294 | 0 | 10.5 | 12.8294
36 | SS-110/35/10kV Veydelevka | 10+10 | 7968 | 3078 | 8.5418 | 8.83 | 120 | -0.28816 | 0 | 10.5 | 10.7882 | 9.8726 |  | 36 | SS-110/35/10kV Veydelevka | 10+10 | 0 | 8.5418 | 8.83 | 120 | -0.28816 | 0 | 10.5 | 10.7882 | 9.8726
| S nom MV, МVА | 10+10 | 4277 | 1645 | 4.5824 | 3.955 | 0 | 0.62744 | 0 | 10.5 | 9.8726 |  |  |  | S nom MV, МVА | 10+10 | 0 | 4.5824 | 3.955 | 0 | 0.62744 | 0 | 10.5 | 9.8726
| S nom LV, МVА | 10+10 | 3691 | 1433 | 3.9594 | 4.875 | 0 | -0.91558 | 0 | 10.5 | 11.4156 |  |  |  | S nom LV, МVА | 10+10 | 0 | 3.9594 | 4.875 | 0 | -0.91558 | 0 | 10.5 | 11.4156
37 | SS-110/6kV Vitamin plant | 25+25 | 13444 | 5411 | 14.4921 | 1.46 | 45 | 13.0321 | 0 | 26.25 | 13.2179 | 13.2179 |  | 37 | SS-110/6kV Vitamin plant | 25+25 | 0 | 14.4921 | 1.46 | 45 | 13.0321 | 0 | 26.25 | 13.2179 | 13.2179
38 | SS-110/35/10kV Volokonovka | 25+25 | 15310 | 7548 | 17.0695 | 10.651 | 120 | 6.4185 | 0 | 26.25 | 19.8315 | 19.8315 |  | 38 | SS-110/35/10kV Volokonovka | 25+25 | 0 | 17.0695 | 10.651 | 120 | 6.4185 | 0 | 26.25 | 19.8315 | 19.8315
| S nom MV, МVА | 25+25 | 7879 | 4389 | 9.019 | 8.576 | 0 | 0.44298 | 0 | 26.25 | 25.807 |  |  |  | S nom MV, МVА | 25+25 | 0 | 9.019 | 8.576 | 0 | 0.44298 | 0 | 26.25 | 25.807
| S nom LV, МVА | 25+25 | 7431 | 3159 | 8.0746 | 2.075 | 0 | 5.9996 | 0 | 26.25 | 20.2504 |  |  |  | S nom LV, МVА | 25+25 | 0 | 8.0746 | 2.075 | 0 | 5.9996 | 0 | 26.25 | 20.2504
39 | SS-110/35/6kV Vostochnaya | 25+25 | 36506 | 13922 | 39.0706 | 0 | 120 | 39.0706 | 0 | 26.25 | -12.8206 | -12.8206 |  | 39 | SS-110/35/6kV Vostochnaya | 25+25 | 0 | 39.0706 | 0 | 120 | 39.0706 | 0 | 26.25 | -12.8206 | -12.8206
| S nom MV, МVА | 25+25 | 21043 | 7602 | 22.3741 | 0 | 0 | 22.3741 | 0 | 26.25 | 3.8759 |  |  |  | S nom MV, МVА | 25+25 | 0 | 22.3741 | 0 | 0 | 22.3741 | 0 | 26.25 | 3.8759
| S nom LV, МVА | 25+25 | 15463 | 6320 | 16.7047 | 0 | 0 | 16.7047 | 0 | 26.25 | 9.5453 |  |  |  | S nom LV, МVА | 25+25 | 0 | 16.7047 | 0 | 0 | 16.7047 | 0 | 26.25 | 9.5453
40 | SS-110/10/6kV Golofeevka | 16+16 | 1892 | 844 | 2.0717 | 0 | 0 | 2.0717 | 0 | 26.25 | 24.1783 | 11.0533 |  | 40 | SS-110/10/6kV Golofeevka | 16+16 | 0 | 2.0717 | 0 | 0 | 2.0717 | 0 | 26.25 | 24.1783 | 11.0533
| S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.125 | 13.125 |  |  |  | S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 13.125 | 13.125
| S nom LV, МVА | 16+16 | 1892 | 844 | 2.0717 | 0 | 0 | 2.0717 | 0 | 13.125 | 11.0533 |  |  |  | S nom LV, МVА | 16+16 | 0 | 2.0717 | 0 | 0 | 2.0717 | 0 | 13.125 | 11.0533
41 | SS-110/10kV Gotnya | 16+16 | 7966 | 3934 | 8.8845 | 6.43 | 120 | 2.4545 | 0 | 16.8 | 14.3455 | 14.3455 |  | 41 | SS-110/10kV Gotnya | 16+16 | 0 | 8.8845 | 6.43 | 120 | 2.4545 | 0 | 16.8 | 14.3455 | 14.3455
42 | SS-110/35/10kV Grayvoron | 16+16 | 11753 | 5119 | 12.8194 | 13.953 | 80 | -1.1336 | 0 | 16.8 | 17.9336 | 14.7436 |  | 42 | SS-110/35/10kV Grayvoron | 16+16 | 0 | 12.8194 | 13.953 | 80 | -1.1336 | 0 | 16.8 | 17.9336 | 14.7436
| S nom MV, МVА | 16+16 | 7085 | 3049 | 7.7132 | 10.903 | 0 | -3.1898 | 0 | 16.8 | 19.9898 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.7132 | 10.903 | 0 | -3.1898 | 0 | 16.8 | 19.9898
| S nom LV, МVА | 16+16 | 4668 | 2070 | 5.1064 | 3.05 | 0 | 2.0564 | 0 | 16.8 | 14.7436 |  |  |  | S nom LV, МVА | 16+16 | 0 | 5.1064 | 3.05 | 0 | 2.0564 | 0 | 16.8 | 14.7436
43 | SS-110/6kV Donets | 40+40 | 24768 | 7776 | 25.96 | 6.73 | 120 | 19.23 | 0 | 42 | 22.77 | 22.77 |  | 43 | SS-110/6kV Donets | 40+40 | 0 | 25.96 | 6.73 | 120 | 19.23 | 0 | 42 | 22.77 | 22.77
44 | SS-110/10kV Dubovoe | 40+40 | 14374 | 2966 | 14.6768 | 11.23 | 120 | 3.4468 | 0 | 42 | 38.5532 | 38.5532 |  | 44 | SS-110/10kV Dubovoe | 40+40 | 0 | 14.6768 | 11.23 | 120 | 3.4468 | 0 | 42 | 38.5532 | 38.5532
45 | SS-110/35/6kV Zhuravliki | 40+25 | 19168 | 6753 | 20.3228 | 12.4 | 120 | 7.9228 | 0 | 42 | 34.0772 | 32.987 |  | 45 | SS-110/35/6kV Zhuravliki | 40+25 | 0 | 20.3228 | 12.4 | 120 | 7.9228 | 0 | 42 | 34.0772 | 32.987
| S nom MV, МVА | 40+25 | 14146 | 5670 | 15.24 | 6.227 | 0 | 9.013 | 0 | 42 | 32.987 |  |  |  | S nom MV, МVА | 40+25 | 0 | 15.24 | 6.227 | 0 | 9.013 | 0 | 42 | 32.987
| S nom LV, МVА | 40+25 | 5022 | 1083 | 5.1374 | 6.173 | 0 | -1.0356 | 0 | 42 | 43.0356 |  |  |  | S nom LV, МVА | 40+25 | 0 | 5.1374 | 6.173 | 0 | -1.0356 | 0 | 42 | 43.0356
46 | SS-110/10kV Zapadnaya | 16+16 | 15349 | 4383 | 15.9625 | 1.249 | 80 | 14.7135 | 0 | 16.8 | 2.0865 | 2.0865 |  | 46 | SS-110/10kV Zapadnaya | 16+16 | 0 | 15.9625 | 1.249 | 80 | 14.7135 | 0 | 16.8 | 2.0865 | 2.0865
47 | SS-110/35/10kV Ivnya | 10+10 | 5687 | 2849 | 6.3607 | 6.16 | 80 | 0.20072 | 0 | 10.5 | 10.2993 | 10.0222 |  | 47 | SS-110/35/10kV Ivnya | 10+10 | 0 | 6.3607 | 6.16 | 80 | 0.20072 | 0 | 10.5 | 10.2993 | 10.0222
| S nom MV, МVА | 10+10 | 2411 | 1525 | 2.8528 | 2.375 | 0 | 0.47781 | 0 | 10.5 | 10.0222 |  |  |  | S nom MV, МVА | 10+10 | 0 | 2.8528 | 2.375 | 0 | 0.47781 | 0 | 10.5 | 10.0222
| S nom LV, МVА | 10+10 | 3276 | 1324 | 3.5334 | 3.785 | 0 | -0.25157 | 0 | 10.5 | 10.7516 |  |  |  | S nom LV, МVА | 10+10 | 0 | 3.5334 | 3.785 | 0 | -0.25157 | 0 | 10.5 | 10.7516
48 | SS-110/35/10kV K.Gvardiya | 16+16 | 12564 | 5234 | 13.6106 | 7.7116 | 120 | 5.899 | 0 | 16.8 | 10.901 | 10.901 |  | 48 | SS-110/35/10kV K.Gvardiya | 16+16 | 0 | 13.6106 | 7.7116 | 120 | 5.899 | 0 | 16.8 | 10.901 | 10.901
| S nom MV, МVА | 16+16 | 6168 | 2716 | 6.7395 | 4.854 | 0 | 1.8855 | 0 | 16.8 | 14.9145 |  |  |  | S nom MV, МVА | 16+16 | 0 | 6.7395 | 4.854 | 0 | 1.8855 | 0 | 16.8 | 14.9145
| S nom LV, МVА | 16+16 | 6396 | 2518 | 6.8738 | 2.8576 | 0 | 4.0162 | 0 | 16.8 | 12.7838 |  |  |  | S nom LV, МVА | 16+16 | 0 | 6.8738 | 2.8576 | 0 | 4.0162 | 0 | 16.8 | 12.7838
49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 10838 | 3920 | 11.5251 | 9.65 | 80 | 1.8751 | 0 | 26.25 | 24.3749 | 20.1687 |  | 49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 0 | 11.5251 | 9.65 | 80 | 1.8751 | 0 | 26.25 | 24.3749 | 20.1687
| S nom MV, МVА | 25+25 | 1372 | 452 | 1.4445 | 1.384 | 0 | 0.060537 | 0 | 26.25 | 26.1895 |  |  |  | S nom MV, МVА | 25+25 | 0 | 1.4445 | 1.384 | 0 | 0.060537 | 0 | 26.25 | 26.1895
| S nom LV, МVА | 25+25 | 9466 | 3468 | 10.0813 | 4 | 0 | 6.0813 | 0 | 26.25 | 20.1687 |  |  |  | S nom LV, МVА | 25+25 | 0 | 10.0813 | 4 | 0 | 6.0813 | 0 | 26.25 | 20.1687
50 | SS-110/35/10kV Korocha | 16+16+16 | 20782 | 9337 | 22.7831 | 2.019 | 20 | 20.7641 | 0 | 33.6 | 12.8359 | 12.8359 |  | 50 | SS-110/35/10kV Korocha | 16+16+16 | 0 | 22.7831 | 2.019 | 20 | 20.7641 | 0 | 33.6 | 12.8359 | 12.8359
| S nom MV, МVА | 16+16+16 | 7844 | 3297 | 8.5087 | 1.719 | 0 | 6.7897 | 0 | 33.6 | 26.8103 |  |  |  | S nom MV, МVА | 16+16+16 | 0 | 8.5087 | 1.719 | 0 | 6.7897 | 0 | 33.6 | 26.8103
| S nom LV, МVА | 16+16+16 | 12938 | 6040 | 14.2784 | 0.3 | 0 | 13.9784 | 0 | 33.6 | 19.6216 |  |  |  | S nom LV, МVА | 16+16+16 | 0 | 14.2784 | 0.3 | 0 | 13.9784 | 0 | 33.6 | 19.6216
51 | SS-110/10kV Krapivenskaya | 16+16 | 3910 | 1344 | 4.1345 | 0 | 0 | 4.1345 | 0 | 16.8 | 12.6655 | 12.6655 |  | 51 | SS-110/10kV Krapivenskaya | 10+10 | 0 | 9.6441 | 9.158 | 120 | 0.48607 | 0 | 10.5 | 10.0139 | 9.7276
52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 8819 | 3903 | 9.6441 | 9.158 | 120 | 0.48607 | 0 | 10.5 | 10.0139 | 9.7276 |  | 52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 0 | 4.2924 | 3.52 | 0 | 0.77239 | 0 | 10.5 | 9.7276
| S nom MV, МVА | 10+10 | 3963 | 1649 | 4.2924 | 3.52 | 0 | 0.77239 | 0 | 10.5 | 9.7276 |  |  |  | S nom MV, МVА | 10+10 | 0 | 5.3536 | 5.638 | 0 | -0.28438 | 0 | 10.5 | 10.7844
| S nom LV, МVА | 10+10 | 4856 | 2254 | 5.3536 | 5.638 | 0 | -0.28438 | 0 | 10.5 | 10.7844 |  |  |  | S nom LV, МVА | 16+16 | 0 | 4.1345 | 0 | 0 | 4.1345 | 0 | 16.8 | 12.6655 | 12.6655
53 | SS-110/10/10kV Mayskaya | 40+40 | 9072 | 1687 | 9.2275 | 0 | 0 | 9.2275 | 0 | 42 | 32.7725 | 32.7725 |  | 53 | SS-110/10/10kV Mayskaya | 40+40 | 0 | 9.2275 | 0 | 0 | 9.2275 | 0 | 42 | 32.7725 | 32.7725
54 | SS-110/35/10kV Maximovka | 16+16 | 11362 | 6568 | 13.1238 | 11.48 | 45 | 1.6438 | 0 | 16.8 | 15.1562 | 14.6504 |  | 54 | SS-110/35/10kV Maximovka | 16+16 | 0 | 13.1238 | 11.48 | 45 | 1.6438 | 0 | 16.8 | 15.1562 | 14.6504
| S nom MV, МVА | 16+16 | 9914 | 6020 | 11.5986 | 9.449 | 0 | 2.1496 | 0 | 16.8 | 14.6504 |  |  |  | S nom MV, МVА | 16+16 | 0 | 11.5986 | 9.449 | 0 | 2.1496 | 0 | 16.8 | 14.6504
| S nom LV, МVА | 16+16 | 1448 | 548 | 1.5482 | 2.031 | 0 | -0.48277 | 0 | 16.8 | 17.2828 |  |  |  | S nom LV, МVА | 16+16 | 0 | 1.5482 | 2.031 | 0 | -0.48277 | 0 | 16.8 | 17.2828
55 | SS-110/35/10kV N.Oskol | 25+31,5 | 16135 | 6490 | 17.3913 | 9.119 | 80 | 8.2723 | 0 | 26.25 | 17.9777 | 16.3926 |  | 55 | SS-110/35/10kV N.Oskol | 25+31,5 | 0 | 17.3913 | 9.119 | 80 | 8.2723 | 0 | 26.25 | 17.9777 | 16.3926
| S nom MV, МVА | 25+31,5 | 5615 | 2806 | 6.2771 | 7.83 | 0 | -1.5529 | 0 | 26.25 | 27.8029 |  |  |  | S nom MV, МVА | 25+31,5 | 0 | 6.2771 | 7.83 | 0 | -1.5529 | 0 | 26.25 | 27.8029
| S nom LV, МVА | 25+31,5 | 10520 | 3684 | 11.1464 | 1.289 | 0 | 9.8574 | 0 | 26.25 | 16.3926 |  |  |  | S nom LV, МVА | 25+31,5 | 0 | 11.1464 | 1.289 | 0 | 9.8574 | 0 | 26.25 | 16.3926
56 | SS-110/10kV Obukhovskaya | 25+25 | 2046 | 713 | 2.1667 | 0 | 0 | 2.1667 | 0 | 26.25 | 24.0833 | 24.0833 |  | 56 | SS-110/10kV Obukhovskaya | 25+25 | 0 | 2.1667 | 0 | 0 | 2.1667 | 0 | 26.25 | 24.0833 | 24.0833
57 | SS-110/6kV Ochistnye | 16+16 | 4472 | 2208 | 4.9874 | 0 | 0 | 4.9874 | 0 | 16.8 | 11.8126 | 11.8126 |  | 57 | SS-110/6kV Ochistnye | 16+16 | 0 | 4.9874 | 0 | 0 | 4.9874 | 0 | 16.8 | 11.8126 | 11.8126
58 | SS-110/35/6kV Pishcheprom | 25+25 | 3557 | 1394 | 3.8204 | 6.679 | 120 | 6.679 | 0 | 26.25 | 22.4296 | 22.4296 |  | 58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 3.8204 | 6.679 | 120 | -2.8586 | 0 | 26.25 | 22.4296 | 22.4296
| S nom MV, МVА | 25+25 | 176 | 205 | 0.27019 | 2.022 | 0 | 2.022 | 0 | 26.25 | 25.9798 |  |  |  | S nom MV, МVА | 25+25 | 0 | 0.27019 | 2.022 | 0 | -1.7518 | 0 | 26.25 | 25.9798
| S nom LV, МVА | 25+25 | 3381 | 1189 | 3.584 | 4.657 | 0 | 4.657 | 0 | 26.25 | 22.666 |  |  |  | S nom LV, МVА | 25+25 | 0 | 3.584 | 4.657 | 0 | -1.073 | 0 | 26.25 | 22.666
59 | SS-110/10kV Promyshlennaya | 25+25 | 15211 | 7256 | 16.853 | 0 | 0 | 16.853 | 0 | 26.25 | 9.397 | 9.397 |  | 59 | SS-110/10kV Promyshlennaya | 25+25 | 0 | 16.853 | 0 | 0 | 16.853 | 0 | 26.25 | 9.397 | 9.397
60 | SS-110/10kV Poultry plant | 16+16 | 11361 | 6643 | 13.1606 | 1.296 | 80 | 11.8646 | 0 | 16.8 | 4.9354 | 4.9354 |  | 60 | SS-110/10kV Poultry plant | 16+16 | 0 | 13.1606 | 1.296 | 80 | 11.8646 | 0 | 16.8 | 4.9354 | 4.9354
61 | SS-110/10kV Pushkarnaya | 40+40 | 28662 | 9012 | 30.0454 | 0 | 60 | 30.0454 | 0 | 42 | 11.9546 | 11.9546 |  | 61 | SS-110/10kV Pushkarnaya | 40+40 | 0 | 30.0454 | 0 | 60 | 30.0454 | 0 | 42 | 11.9546 | 11.9546
62 | SS-110/35/10kV Rakitnoe | 10+10 | 9613 | 5415 | 11.0332 | 8.98 | 120 | 2.0532 | 0 | 10.5 | 8.4468 | 8.4468 |  | 62 | SS-110/35/10kV Rakitnoe | 10+10 | 0 | 11.0332 | 8.98 | 120 | 2.0532 | 0 | 10.5 | 8.4468 | 8.4468
| S nom MV, МVА | 10+10 | 6619 | 4137 | 7.8055 | 6.407 | 0 | 1.3985 | 0 | 10.5 | 9.1015 |  |  |  | S nom MV, МVА | 10+10 | 0 | 7.8055 | 6.407 | 0 | 1.3985 | 0 | 10.5 | 9.1015
| S nom LV, МVА | 10+10 | 2994 | 1278 | 3.2554 | 2.573 | 0 | 0.68235 | 0 | 10.5 | 9.8176 |  |  |  | S nom LV, МVА | 10+10 | 0 | 3.2554 | 2.573 | 0 | 0.68235 | 0 | 10.5 | 9.8176
63 | SS-110/35/6kV Rudnik | 25+25 | 16522 | 9562 | 19.0895 | 10.46 | 45 | 8.6295 | 0 | 26.25 | 17.6205 | 17.6205 |  | 63 | SS-110/35/6kV Rudnik | 25+25 | 0 | 19.0895 | 10.46 | 45 | 8.6295 | 0 | 26.25 | 17.6205 | 17.6205
| S nom MV, МVА | 25+25 | 10086 | 5369 | 11.426 | 10.46 | 0 | 0.966 | 0 | 26.25 | 25.284 |  |  |  | S nom MV, МVА | 25+25 | 0 | 11.426 | 10.46 | 0 | 0.966 | 0 | 26.25 | 25.284
| S nom LV, МVА | 25+25 | 6436 | 4193 | 7.6814 | 0 | 0 | 7.6814 | 0 | 26.25 | 18.5686 |  |  |  | S nom LV, МVА | 25+25 | 0 | 7.6814 | 0 | 0 | 7.6814 | 0 | 26.25 | 18.5686
64 | SS-110/10kV Severnaya | 40+40 | 13031 | 3928 | 13.6101 | 3.312 | 45 | 10.2981 | 0 | 42 | 31.7019 | 31.7019 |  | 64 | SS-110/10kV Severnaya | 40+40 | 0 | 13.6101 | 3.312 | 45 | 10.2981 | 0 | 42 | 31.7019 | 31.7019
65 | SS-110/35/10kV Skorodnoe | 16+16 | 10734 | 4354 | 11.5834 | 10.36 | 120 | 1.2234 | 0 | 16.8 | 15.5766 | 15.4492 |  | 65 | SS-110/35/10kV Skorodnoe | 16+16 | 0 | 11.5834 | 10.36 | 120 | 1.2234 | 0 | 16.8 | 15.5766 | 15.4492
| S nom MV, МVА | 16+16 | 6880 | 2818 | 7.4348 | 7.562 | 0 | -0.12725 | 0 | 16.8 | 16.9272 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.4348 | 7.562 | 0 | -0.12725 | 0 | 16.8 | 16.9272
| S nom LV, МVА | 16+16 | 3854 | 1536 | 4.1488 | 2.798 | 0 | 1.3508 | 0 | 16.8 | 15.4492 |  |  |  | S nom LV, МVА | 16+16 | 0 | 4.1488 | 2.798 | 0 | 1.3508 | 0 | 16.8 | 15.4492
66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 28060 | 14706 | 31.6801 | 0 | 0 | 31.6801 | 0 | 47.25 | 15.5699 | 15.5699 |  | 66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 0 | 31.6801 | 0 | 0 | 31.6801 | 0 | 47.25 | 15.5699 | 15.5699
| S nom MV, МVА | 20+25+25 | 8530 | 5342 | 10.0647 | 0 | 0 | 10.0647 | 0 | 47.25 | 37.1853 |  |  |  | S nom MV, МVА | 20+25+25 | 0 | 10.0647 | 0 | 0 | 10.0647 | 0 | 47.25 | 37.1853
| S nom LV, МVА | 20+25+25 | 19530 | 9364 | 21.6588 | 0 | 0 | 21.6588 | 0 | 47.25 | 25.5912 |  |  |  | S nom LV, МVА | 20+25+25 | 0 | 21.6588 | 0 | 0 | 21.6588 | 0 | 47.25 | 25.5912
67 | SS-110/35/10kV Streletskaya | 16+16 | 6219 | 1734 | 6.4562 | 2.23 | 80 | 4.2262 | 0 | 16.8 | 12.5738 | 6.1583 |  | 67 | SS-110/35/10kV Streletskaya | 16+16 | 0 | 6.4562 | 2.23 | 80 | 4.2262 | 0 | 16.8 | 12.5738 | 6.1583
| S nom MV, МVА | 16+8 | 1932 | 462 | 1.9865 | 0 | 0 | 1.9865 | 0 | 8.4 | 6.4135 |  |  |  | S nom MV, МVА | 16+8 | 0 | 1.9865 | 0 | 0 | 1.9865 | 0 | 8.4 | 6.4135
| S nom LV, МVА | 16+8 | 4287 | 1272 | 4.4717 | 2.23 | 0 | 2.2417 | 0 | 8.4 | 6.1583 |  |  |  | S nom LV, МVА | 16+8 | 0 | 4.4717 | 2.23 | 0 | 2.2417 | 0 | 8.4 | 6.1583
68 | SS-110/6kV Stroitel | 15+15 | 11154 | 4901 | 12.1832 | 0 | 0 | 12.1832 | 0 | 15.75 | 3.5668 | 3.5668 |  | 68 | SS-110/6kV Stroitel | 15+15 | 0 | 12.1832 | 0 | 0 | 12.1832 | 0 | 15.75 | 3.5668 | 3.5668
69 | SS-110/35/10kV Tomarovka | 16+16 | 13683 | 6359 | 15.0885 | 3.46 | 45 | 11.6285 | 0 | 16.8 | 5.1715 | 5.1715 |  | 69 | SS-110/35/10kV Tomarovka | 16+16 | 0 | 15.0885 | 3.46 | 45 | 11.6285 | 0 | 16.8 | 5.1715 | 5.1715
| S nom MV, МVА | 16+16 | 6657 | 3175 | 7.3754 | 3.46 | 0 | 3.9154 | 0 | 16.8 | 12.8846 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.3754 | 3.46 | 0 | 3.9154 | 0 | 16.8 | 12.8846
| S nom LV, МVА | 16+16 | 7026 | 3184 | 7.7138 | 0 | 0 | 7.7138 | 0 | 16.8 | 9.0862 |  |  |  | S nom LV, МVА | 16+16 | 0 | 7.7138 | 0 | 0 | 7.7138 | 0 | 16.8 | 9.0862
70 | SS-110/6kV Chemical plant | 32+32 | 11768 | 5854 | 13.1436 | 5.56 | 45 | 7.5836 | 0 | 33.6 | 26.0164 | 26.0164 |  | 70 | SS-110/6kV Chemical plant | 32+32 | 0 | 13.1436 | 5.56 | 45 | 7.5836 | 0 | 33.6 | 26.0164 | 26.0164
71 | SS-110/10kV Tsentralnaya | 40+40 | 27276 | 5364 | 27.7984 | 0 | 0 | 27.7984 | 0 | 42 | 14.2016 | 14.2016 |  | 71 | SS-110/10kV Tsentralnaya | 40+40 | 0 | 27.7984 | 0 | 0 | 27.7984 | 0 | 42 | 14.2016 | 14.2016
72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 15286 | 6193 | 16.4929 | 20.54 | 80 | -4.0471 | 0 | 26.25 | 30.2971 | 24.4172 |  | 72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 0 | 16.4929 | 20.54 | 80 | -4.0471 | 0 | 26.25 | 30.2971 | 24.4172
| S nom MV, МVА | 25+25 | 13793 | 5130 | 14.7161 | 19.676 | 0 | -4.9599 | 0 | 26.25 | 31.2099 |  |  |  | S nom MV, МVА | 25+25 | 0 | 14.7161 | 19.676 | 0 | -4.9599 | 0 | 26.25 | 31.2099
| S nom LV, МVА | 25+25 | 1493 | 1063 | 1.8328 | 0 | 0 | 1.8328 | 0 | 26.25 | 24.4172 |  |  |  | S nom LV, МVА | 25+25 | 0 | 1.8328 | 0 | 0 | 1.8328 | 0 | 26.25 | 24.4172
73 | SS-110/35/10kV Chernyanka | 16+16 | 13608 | 5777 | 14.7835 | 5.969 | 120 | 8.8145 | 0 | 16.8 | 7.9855 | 7.7874 |  | 73 | SS-110/35/10kV Chernyanka | 16+16 | 0 | 14.7835 | 5.969 | 120 | 8.8145 | 0 | 16.8 | 7.9855 | 7.7874
| S nom MV, МVА | 16+16 | 5246 | 2415 | 5.7752 | 5.969 | 0 | -0.19382 | 0 | 16.8 | 16.9938 |  |  |  | S nom MV, МVА | 16+16 | 0 | 5.7752 | 5.969 | 0 | -0.19382 | 0 | 16.8 | 16.9938
| S nom LV, МVА | 16+16 | 8362 | 3362 | 9.0126 | 0 | 0 | 9.0126 | 0 | 16.8 | 7.7874 |  |  |  | S nom LV, МVА | 16+16 | 0 | 9.0126 | 0 | 0 | 9.0126 | 0 | 16.8 | 7.7874
74 | SS-110/35/6kV Shebekino | 40+40 | 25120 | 12318 | 27.9776 | 16.65 | 120 | 11.3276 | 0 | 42 | 30.6724 | 30.6724 |  | 74 | SS-110/35/6kV Shebekino | 40+40 | 0 | 27.9776 | 16.65 | 120 | 11.3276 | 0 | 42 | 30.6724 | 30.6724
| S nom MV, МVА | 40+40 | 13436 | 7362 | 15.3207 | 11.682 | 0 | 3.6387 | 0 | 42 | 38.3613 |  |  |  | S nom MV, МVА | 40+40 | 0 | 15.3207 | 11.682 | 0 | 3.6387 | 0 | 42 | 38.3613
| S nom LV, МVА | 40+40 | 11684 | 4956 | 12.6916 | 4.968 | 0 | 7.7236 | 0 | 42 | 34.2764 |  |  |  | S nom LV, МVА | 40+40 | 0 | 12.6916 | 4.968 | 0 | 7.7236 | 0 | 42 | 34.2764
75 | SS-110/10kV Sheino | 3,2+10 | 2220 | 795 | 2.3581 | 0 | 0 | 2.3581 | 0 | 3.36 | 1.0019 | 1.0019 |  | 75 | SS-110/10kV Sheino | 3,2+10 | 0 | 2.3581 | 0 | 0 | 2.3581 | 0 | 3.36 | 1.0019 | 1.0019
76 | SS-110/10/6kV Yuzhnaya | 40+40 | 36431 | 10427 | 37.8938 | 12.94 | 120 | 24.9538 | 0 | 42 | 17.0462 | 17.0462 |  | 76 | SS-110/10/6kV Yuzhnaya | 40+40 | 0 | 37.8938 | 12.94 | 120 | 24.9538 | 0 | 42 | 17.0462 | 17.0462
| S nom MV, МVА | 40+40 | 5694 | 1164 | 5.8118 | 3.42 | 0 | 2.3918 | 0 | 42 | 39.6082 |  |  |  | S nom MV, МVА | 40+40 | 0 | 5.8118 | 3.42 | 0 | 2.3918 | 0 | 42 | 39.6082
| S nom LV, МVА | 40+40 | 30737 | 9263 | 32.1024 | 9.52 | 0 | 22.5824 | 0 | 42 | 19.4176 |  |  |  | S nom LV, МVА | 40+40 | 0 | 32.1024 | 9.52 | 0 | 22.5824 | 0 | 42 | 19.4176
77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 792 | 304 | 0.84834 | 0.43267 | 120 | 0.41567 | 0 | 2.625 | 2.2093 | 2.2093 |  | 77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 0 | 0.84834 | 0.43267 | 120 | 0.41567 | 0 | 2.625 | 2.2093 | 2.2093
78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 848 | 320 | 0.90637 | 0.46639 | 120 | 0.43998 | 0 | 2.625 | 2.185 | 2.185 |  | 78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 0 | 0.90637 | 0.46639 | 120 | 0.43998 | 0 | 2.625 | 2.185 | 2.185
79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 2364 | 1296 | 2.6959 | 0 | 0 | 2.6959 | 0 | 4.2 | 1.5041 | 1.5041 |  | 79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 0 | 2.6959 | 0 | 0 | 2.6959 | 0 | 4.2 | 1.5041 | 1.5041
80 | SS-35/10kV Annovka | 2,5+2,5 | 876 | 354 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267 |  | 80 | SS-35/10kV Annovka | 2,5+2,5 | 0 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267
81 | SS-35/10kV Artelnoe | 6,3+6,3 | 5480 | 3788 | 6.6618 | 0.55 | 45 | 6.1118 | 0 | 6.615 | 0.50322 | 0.50322 |  | 81 | SS-35/10kV Artelnoe | 6,3+6,3 | 0 | 6.6618 | 0.55 | 45 | 6.1118 | 0 | 6.615 | 0.50322 | 0.50322
82 | SS-35/10kV B.Dvory | 4+4 | 2352 | 960 | 2.5404 | 1.191 | 120 | 1.3494 | 0 | 4.2 | 2.8506 | 2.8506 |  | 82 | SS-35/10kV B.Dvory | 4+4 | 0 | 2.5404 | 1.191 | 120 | 1.3494 | 0 | 4.2 | 2.8506 | 2.8506
83 | SS-35/10kV B.Ivanovka | 2,5+2,5 | 976 | 400 | 1.0548 | 0.62488 | 80 | 0.42991 | 0 | 4.2 | 3.7701 | 3.7701 |  | 83 | SS-35/10kV B.Ivanovka | 4+4 | 0 | 1.0548 | 0.62488 | 80 | 0.42991 | 0 | 4.2 | 3.7701 | 3.7701
84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 756 | 318 | 0.82016 | 0.44779 | 45 | 0.37236 | 0 | 2.625 | 2.2526 | 2.2526 |  | 84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 0 | 0.82016 | 0.44779 | 45 | 0.37236 | 0 | 2.625 | 2.2526 | 2.2526
85 | SS-35/10kV B.Ples | 2,5+2,5 | 672 | 280 | 0.728 | 0.606 | 45 | 0.122 | 0 | 2.625 | 2.503 | 2.503 |  | 85 | SS-35/10kV B.Ples | 2,5+2,5 | 0 | 0.728 | 0.606 | 45 | 0.122 | 0 | 2.625 | 2.503 | 2.503
86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 2672 | 948 | 2.8352 | 2.83 | 45 | 0.0051875 | 0 | 6.615 | 6.6098 | 6.6098 |  | 86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 0 | 2.8352 | 2.83 | 45 | 0.0051875 | 0 | 6.615 | 6.6098 | 6.6098
87 | SS-35/10kV Belovskoe | 4+4 | 3408 | 1496 | 3.7219 | 1.21 | 80 | 2.5119 | 0 | 4.2 | 1.6881 | 1.6881 |  | 87 | SS-35/10kV Belovskoe | 4+4 | 0 | 3.7219 | 1.21 | 80 | 2.5119 | 0 | 4.2 | 1.6881 | 1.6881
88 | SS-35/10kV Belyanka | 2,5+4 | 1776 | 928 | 2.0038 | 1.3214 | 45 | 0.68244 | 0 | 2.625 | 1.9426 | 1.9426 |  | 88 | SS-35/10kV Belyanka | 2,5+4 | 0 | 2.0038 | 1.3214 | 45 | 0.68244 | 0 | 2.625 | 1.9426 | 1.9426
89 | SS-35/10kV Bessonovka | 6,3+6,3 | 4344 | 2400 | 4.9629 | 0.918 | 120 | 4.0449 | 0 | 6.615 | 2.5701 | 2.5701 |  | 89 | SS-35/10kV Bessonovka | 6,3+6,3 | 0 | 4.9629 | 0.918 | 120 | 4.0449 | 0 | 6.615 | 2.5701 | 2.5701
90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 1112 | 376 | 1.1738 | 0.522 | 45 | 0.65185 | 0 | 1.68 | 1.0282 | 1.0282 |  | 90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 0 | 1.1738 | 0.522 | 45 | 0.65185 | 0 | 1.68 | 1.0282 | 1.0282
91 | SS-35/10kV V.Mikhailovka | 4+4 | 2508 | 984 | 2.6941 | 1.45 | 80 | 1.2441 | 0 | 4.2 | 2.9559 | 2.9559 |  | 91 | SS-35/10kV V.Mikhailovka | 4+4 | 0 | 2.6941 | 1.45 | 80 | 1.2441 | 0 | 4.2 | 2.9559 | 2.9559
92 | SS-35/10kV Varvarovka | 2,5+2,5 | 1656 | 680 | 1.7902 | 1.0795 | 120 | 0.71063 | 0 | 2.625 | 1.9144 | 1.9144 |  | 92 | SS-35/10kV Varvarovka | 2,5+2,5 | 0 | 1.7902 | 1.0795 | 120 | 0.71063 | 0 | 2.625 | 1.9144 | 1.9144
93 | SS-35/10kV Vengerovka | 2,5+2,5 | 1620 | 588 | 1.7234 | 0.4 | 120 | 1.3234 | 0 | 2.625 | 1.3016 | 1.3016 |  | 93 | SS-35/10kV Vengerovka | 2,5+2,5 | 0 | 1.7234 | 0.4 | 120 | 1.3234 | 0 | 2.625 | 1.3016 | 1.3016
94 | SS-35/10kV Verkhopenye | 2,5+4 | 1536 | 704 | 1.6896 | 1.0177 | 45 | 0.67199 | 0 | 2.625 | 1.953 | 1.953 |  | 94 | SS-35/10kV Verkhopenye | 2,5+4 | 0 | 1.6896 | 1.0177 | 45 | 0.67199 | 0 | 2.625 | 1.953 | 1.953
95 | SS-35/10kV Viktoropol | 2,5+4 | 1376 | 460 | 1.4509 | 0.95536 | 120 | 0.4955 | 0 | 2.625 | 2.1295 | 2.1295 |  | 95 | SS-35/10kV Viktoropol | 2,5+4 | 0 | 1.4509 | 0.95536 | 120 | 0.4955 | 0 | 2.625 | 2.1295 | 2.1295
96 | SS-35/10kV Vislaya Dubrava | 4+4 | 1968 | 564 | 2.0472 | 0.616 | 80 | 1.4312 | 0 | 4.2 | 2.7688 | 2.7688 |  | 96 | SS-35/10kV Vislaya Dubrava | 4+4 | 0 | 2.0472 | 0.616 | 80 | 1.4312 | 0 | 4.2 | 2.7688 | 2.7688
97 | SS-35/10kV Vladimirovka | 4+4 | 520 | 278 | 0.58965 | 0 | 0 | 0.58965 | 0 | 4.2 | 3.6104 | 3.6104 |  | 97 | SS-35/10kV Vladimirovka | 4+4 | 0 | 0.58965 | 0 | 0 | 0.58965 | 0 | 4.2 | 3.6104 | 3.6104
98 | SS-35/10kV Water storage | 4+6,3 | 1848 | 660 | 1.9623 | 0.305 | 45 | 1.6573 | 0 | 4.2 | 2.5427 | 2.5427 |  | 98 | SS-35/10kV Water storage | 4+6,3 | 0 | 1.9623 | 0.305 | 45 | 1.6573 | 0 | 4.2 | 2.5427 | 2.5427
99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 2895 | 1109 | 3.1001 | 1.43 | 120 | 1.6701 | 0 | 6.615 | 4.9449 | 4.9449 |  | 99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 0 | 3.1001 | 1.43 | 120 | 1.6701 | 0 | 6.615 | 4.9449 | 4.9449
100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 1410 | 588 | 1.5277 | 0.99513 | 120 | 0.53256 | 0 | 2.625 | 2.0924 | 2.0924 |  | 100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 0 | 1.5277 | 0.99513 | 120 | 0.53256 | 0 | 2.625 | 2.0924 | 2.0924
101 | SS-35/10kV Glinnoe | 6,3+6,3 | 2256 | 1488 | 2.7025 | 1.4036 | 80 | 1.2989 | 0 | 6.615 | 5.3161 | 5.3161 |  | 101 | SS-35/10kV Glinnoe | 6,3+6,3 | 0 | 2.7025 | 1.4036 | 80 | 1.2989 | 0 | 6.615 | 5.3161 | 5.3161
102 | SS-35/10kV Golovchino | 2,5+2,5 | 2232 | 828 | 2.3806 | 0.617 | 45 | 1.7636 | 0 | 2.625 | 0.86137 | 0.86137 |  | 102 | SS-35/10kV Golovchino | 2,5+2,5 | 0 | 2.3806 | 0.617 | 45 | 1.7636 | 0 | 2.625 | 0.86137 | 0.86137
103 | SS-35/10kV Gora-Podol | 2,5+4 | 1380 | 540 | 1.4819 | 0.9085 | 45 | 0.57339 | 0 | 2.625 | 2.0516 | 2.0516 |  | 103 | SS-35/10kV Gora-Podol | 2,5+4 | 0 | 1.4819 | 0.9085 | 45 | 0.57339 | 0 | 2.625 | 2.0516 | 2.0516
104 | SS-35/10kV Gorodishche | 4+4 | 2576 | 1104 | 2.8026 | 0 | 0 | 2.8026 | 0 | 4.2 | 1.3974 | 1.3974 |  | 104 | SS-35/10kV Gorodishche | 4+4 | 0 | 2.8026 | 0 | 0 | 2.8026 | 0 | 4.2 | 1.3974 | 1.3974
105 | SS-35/10kV Dmitrievka | 4+4 | 1152 | 636 | 1.3159 | 0.78237 | 80 | 0.53353 | 0 | 4.2 | 3.6665 | 3.6665 |  | 105 | SS-35/10kV Dmitrievka | 4+4 | 0 | 1.3159 | 0.78237 | 80 | 0.53353 | 0 | 4.2 | 3.6665 | 3.6665
106 | SS-35/10kV Dorogoshch | 4+4 | 2288 | 944 | 2.4751 | 1.054 | 45 | 1.4211 | 0 | 4.2 | 2.7789 | 2.7789 |  | 106 | SS-35/10kV Dorogoshch | 4+4 | 0 | 2.4751 | 1.054 | 45 | 1.4211 | 0 | 4.2 | 2.7789 | 2.7789
107 | SS-35/10kV Dragunka | 2,5+2,5 | 320 | 144 | 0.35091 | 0.62999 | 80 | -0.27908 | 0 | 2.625 | 2.9041 | 2.9041 |  | 107 | SS-35/10kV Dragunka | 2,5+2,5 | 0 | 0.35091 | 0.62999 | 80 | -0.27908 | 0 | 2.625 | 2.9041 | 2.9041
108 | SS-35/10kV Zhuravlevka | 2,5+4 | 1264 | 336 | 1.3079 | 0.274 | 80 | 1.0339 | 0 | 2.625 | 1.5911 | 1.5911 |  | 108 | SS-35/10kV Zhuravlevka | 2,5+4 | 0 | 1.3079 | 0.274 | 80 | 1.0339 | 0 | 2.625 | 1.5911 | 1.5911
109 | SS-35/6kV Zhuravliki | 10+10 | 7104 | 1872 | 7.3465 | 4.051 | 120 | 3.2955 | 0 | 10.5 | 7.2045 | 7.2045 |  | 109 | SS-35/6kV Zhuravliki | 10+10 | 0 | 7.3465 | 4.051 | 120 | 3.2955 | 0 | 10.5 | 7.2045 | 7.2045
110 | SS-35/10kV Zavidovka | 2,5+2,5 | 808 | 584 | 0.99696 | 0.42 | 80 | 0.57696 | 0 | 2.625 | 2.048 | 2.048 |  | 110 | SS-35/10kV Zavidovka | 2,5+2,5 | 0 | 0.99696 | 0.42 | 80 | 0.57696 | 0 | 2.625 | 2.048 | 2.048
111 | SS-35/6kV Zapadnaya | 10+10+10 | 5664 | 2496 | 6.1896 | 1.707 | 120 | 4.4826 | 0 | 21 | 16.5174 | 16.5174 |  | 111 | SS-35/6kV Zapadnaya | 10+10+10 | 0 | 6.1896 | 1.707 | 120 | 4.4826 | 0 | 21 | 16.5174 | 16.5174
112 | SS-35/10kV Zozuli | 6,3+6,3 | 5808 | 2912 | 6.4971 | 3.88 | 80 | 2.6171 | 0 | 6.615 | 3.9979 | 3.9979 |  | 112 | SS-35/10kV Zozuli | 6,3+6,3 | 0 | 6.4971 | 3.88 | 80 | 2.6171 | 0 | 6.615 | 3.9979 | 3.9979
113 | SS-35/10kV Ivitsa | 2,5+2,5 | 976 | 448 | 1.0739 | 0.58603 | 80 | 0.48788 | 0 | 2.625 | 2.1371 | 2.1371 |  | 113 | SS-35/10kV Ivitsa | 2,5+2,5 | 0 | 1.0739 | 0.58603 | 80 | 0.48788 | 0 | 2.625 | 2.1371 | 2.1371
114 | SS-35/10kV Ilovka | 4+4 | 2280 | 744 | 2.3983 | 2.056 | 45 | 0.34232 | 0 | 4.2 | 3.8577 | 3.8577 |  | 114 | SS-35/10kV Ilovka | 4+4 | 0 | 2.3983 | 2.056 | 45 | 0.34232 | 0 | 4.2 | 3.8577 | 3.8577
115 | SS-35/10kV Istobnoe | 4+2,5 | 1096 | 600 | 1.2495 | 0.93935 | 120 | 0.31013 | 0 | 2.625 | 2.3149 | 2.3149 |  | 115 | SS-35/10kV Istobnoe | 4+2,5 | 0 | 1.2495 | 0.93935 | 120 | 0.31013 | 0 | 2.625 | 2.3149 | 2.3149
116 | SS-35/10kV Kazatskaya | 2,5+4 | 1054 | 381 | 1.1207 | 0.87141 | 45 | 0.24934 | 0 | 2.625 | 2.3757 | 2.3757 |  | 116 | SS-35/10kV Kazatskaya | 2,5+4 | 0 | 1.1207 | 0.87141 | 45 | 0.24934 | 0 | 2.625 | 2.3757 | 2.3757
117 | SS-35/10kV Kazinka | 4+4 | 2364 | 804 | 2.497 | 0.736 | 120 | 1.761 | 0 | 4.2 | 2.439 | 2.439 |  | 117 | SS-35/10kV Kazinka | 4+4 | 0 | 2.497 | 0.736 | 120 | 1.761 | 0 | 4.2 | 2.439 | 2.439
118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 920 | 308 | 0.97019 | 0.712 | 120 | 0.25819 | 0 | 2.625 | 2.3668 | 2.3668 |  | 118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 0 | 0.97019 | 0.712 | 120 | 0.25819 | 0 | 2.625 | 2.3668 | 2.3668
119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 2952 | 1404 | 3.2689 | 0.7035 | 120 | 2.5654 | 0 | 6.615 | 4.0496 | 4.0496 |  | 119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 0 | 3.2689 | 0.7035 | 120 | 2.5654 | 0 | 6.615 | 4.0496 | 4.0496
120 | SS-35/10kV Kotovo | 2,5+2,5 | 2304 | 720 | 2.4139 | 1.648 | 20 | 0.76587 | 0 | 2.625 | 1.8591 | 1.8591 |  | 120 | SS-35/10kV Kotovo | 2,5+2,5 | 0 | 2.4139 | 1.648 | 20 | 0.76587 | 0 | 2.625 | 1.8591 | 1.8591
121 | SS-35/10kV Kochetovka | 2,5+4 | 1224 | 516 | 1.3283 | 0.6286 | 45 | 0.69972 | 0 | 2.625 | 1.9253 | 1.9253 |  | 121 | SS-35/10kV Kochetovka | 2,5+4 | 0 | 1.3283 | 0.6286 | 45 | 0.69972 | 0 | 2.625 | 1.9253 | 1.9253
122 | SS-35/10kV Krasnoe | 4+2,5 | 1016 | 368 | 1.0806 | 1.1395 | 80 | -0.058929 | 0 | 2.625 | 2.6839 | 2.6839 |  | 122 | SS-35/10kV Krasnoe | 4+2,5 | 0 | 1.0806 | 1.1395 | 80 | -0.058929 | 0 | 2.625 | 2.6839 | 2.6839
123 | SS-35/10kV Kretovo | 4+2,5 | 1016 | 468 | 1.1186 | 0.67818 | 120 | 0.44043 | 0 | 2.625 | 2.1846 | 2.1846 |  | 123 | SS-35/10kV Kretovo | 4+2,5 | 0 | 1.1186 | 0.67818 | 120 | 0.44043 | 0 | 2.625 | 2.1846 | 2.1846
124 | SS-35/10kV Kurasovka | 4+4 | 2640 | 1248 | 2.9201 | 1.797 | 80 | 1.1231 | 0 | 4.2 | 3.0769 | 3.0769 |  | 124 | SS-35/10kV Kurasovka | 4+4 | 0 | 2.9201 | 1.797 | 80 | 1.1231 | 0 | 4.2 | 3.0769 | 3.0769
125 | SS-35/6kV Lebedi | 4+5,6 | 3586 | 1166 | 3.7708 | 0.581 | 120 | 3.1898 | 0 | 4.2 | 1.0102 | 1.0102 |  | 125 | SS-35/6kV Lebedi | 4+5,6 | 0 | 3.7708 | 0.581 | 120 | 3.1898 | 0 | 4.2 | 1.0102 | 1.0102
126 | SS-35/6kV Ledovaya | 4+4 | 2549 | 1325 | 2.8728 | 1.321 | 80 | 1.5518 | 0 | 4.2 | 2.6482 | 2.6482 |  | 126 | SS-35/6kV Ledovaya | 4+4 | 0 | 2.8728 | 1.321 | 80 | 1.5518 | 0 | 4.2 | 2.6482 | 2.6482
127 | SS-35/10kV Livenka | 4+4 | 3252 | 1452 | 3.5614 | 1.541 | 120 | 2.0204 | 0 | 4.2 | 2.1796 | 2.1796 |  | 127 | SS-35/10kV Livenka | 4+4 | 0 | 3.5614 | 1.541 | 120 | 2.0204 | 0 | 4.2 | 2.1796 | 2.1796
128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 732 | 336 | 0.80543 | 0.66672 | 80 | 0.13872 | 0 | 2.625 | 2.4863 | 2.4863 |  | 128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 0 | 0.80543 | 0.66672 | 80 | 0.13872 | 0 | 2.625 | 2.4863 | 2.4863
129 | SS-35/10kV M.Pristan | 10+10 | 6456 | 1992 | 6.7563 | 1.81 | 45 | 4.9463 | 0 | 10.5 | 5.5537 | 5.5537 |  | 129 | SS-35/10kV M.Pristan | 10+10 | 0 | 6.7563 | 1.81 | 45 | 4.9463 | 0 | 10.5 | 5.5537 | 5.5537
130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 744 | 304 | 0.80371 | 0.60716 | 80 | 0.19655 | 0 | 2.625 | 2.4284 | 2.4284 |  | 130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 0 | 0.80371 | 0.60716 | 80 | 0.19655 | 0 | 2.625 | 2.4284 | 2.4284
131 | SS-35/10kV Malinovka | 10+10 | 6352 | 3984 | 7.498 | 1.357 | 120 | 6.141 | 0 | 10.5 | 4.359 | 4.359 |  | 131 | SS-35/10kV Malinovka | 10+10 | 0 | 7.498 | 1.357 | 120 | 6.141 | 0 | 10.5 | 4.359 | 4.359
132 | SS-35/10kV Mandrovo | 2,5+2,5 | 1188 | 336 | 1.2346 | 0.65565 | 80 | 0.57895 | 0 | 2.625 | 2.046 | 2.046 |  | 132 | SS-35/10kV Mandrovo | 2,5+2,5 | 0 | 1.2346 | 0.65565 | 80 | 0.57895 | 0 | 2.625 | 2.046 | 2.046
133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 1266 | 462 | 1.3477 | 0.643 | 80 | 0.70466 | 0 | 2.625 | 1.9203 | 1.9203 |  | 133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 0 | 1.3477 | 0.643 | 80 | 0.70466 | 0 | 2.625 | 1.9203 | 1.9203
134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 1158 | 522 | 1.2702 | 0.59315 | 120 | 0.67706 | 0 | 2.625 | 1.9479 | 1.9479 |  | 134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 0 | 1.2702 | 0.59315 | 120 | 0.67706 | 0 | 2.625 | 1.9479 | 1.9479
135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 3168 | 1168 | 3.3765 | 2.78 | 120 | 0.59645 | 0 | 6.615 | 6.0185 | 6.0185 |  | 135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 0 | 3.3765 | 2.78 | 120 | 0.59645 | 0 | 6.615 | 6.0185 | 6.0185
136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 3288 | 1200 | 3.5001 | 0.842 | 45 | 2.6581 | 0 | 6.615 | 3.9569 | 3.9569 |  | 136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 0 | 3.5001 | 0.842 | 45 | 2.6581 | 0 | 6.615 | 3.9569 | 3.9569
137 | SS-35/10kV N.Ukolovo | 4+2,5 | 1384 | 524 | 1.4799 | 0.57 | 80 | 0.90988 | 0 | 2.625 | 1.7151 | 1.7151 |  | 137 | SS-35/10kV N.Ukolovo | 4+2,5 | 0 | 1.4799 | 0.57 | 80 | 0.90988 | 0 | 2.625 | 1.7151 | 1.7151
138 | SS-35/10kV N.Khutornoe | 2,5+4 | 260 | 89 | 0.27481 | 0.19 | 80 | 0.084811 | 0 | 2.625 | 2.5402 | 2.5402 |  | 138 | SS-35/10kV N.Khutornoe | 2,5+4 | 0 | 0.27481 | 0.19 | 80 | 0.084811 | 0 | 2.625 | 2.5402 | 2.5402
139 | SS-35/10kV Neminushchee | 2,5+2,5 | 1732 | 628 | 1.8423 | 0.65147 | 80 | 1.1909 | 0 | 2.625 | 1.4341 | 1.4341 |  | 139 | SS-35/10kV Neminushchee | 2,5+2,5 | 0 | 1.8423 | 0.65147 | 80 | 1.1909 | 0 | 2.625 | 1.4341 | 1.4341
140 | SS-35/10kV Nechaevka | 4+4 | 1100 | 400 | 1.1705 | 0.451 | 120 | 0.71947 | 0 | 4.2 | 3.4805 | 3.4805 |  | 140 | SS-35/10kV Nechaevka | 4+4 | 0 | 1.1705 | 0.451 | 120 | 0.71947 | 0 | 4.2 | 3.4805 | 3.4805
141 | SS-35/10kV Nikitovka | 2,5+2,5 | 2016 | 768 | 2.1573 | 1.4354 | 80 | 0.7219 | 0 | 2.625 | 1.9031 | 1.9031 |  | 141 | SS-35/10kV Nikitovka | 2,5+2,5 | 0 | 2.1573 | 1.4354 | 80 | 0.7219 | 0 | 2.625 | 1.9031 | 1.9031
142 | SS-35/10kV Novenkoe | 4+4 | 1964 | 616 | 2.0583 | 1.7332 | 80 | 0.32513 | 0 | 4.2 | 3.8749 | 3.8749 |  | 142 | SS-35/10kV Novenkoe | 4+4 | 0 | 2.0583 | 1.7332 | 80 | 0.32513 | 0 | 4.2 | 3.8749 | 3.8749
143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 3968 | 1888 | 4.3943 | 0.872 | 80 | 3.5223 | 0 | 6.615 | 3.0927 | 3.0927 |  | 143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 0 | 4.3943 | 0.872 | 80 | 3.5223 | 0 | 6.615 | 3.0927 | 3.0927
144 | SS-35/10kV Orlik | 4+4 | 1728 | 912 | 1.9539 | 0.553 | 80 | 1.4009 | 0 | 4.2 | 2.7991 | 2.7991 |  | 144 | SS-35/10kV Orlik | 4+4 | 0 | 1.9539 | 0.553 | 80 | 1.4009 | 0 | 4.2 | 2.7991 | 2.7991
145 | SS-35/10kV Podolkhi | 2,5+2,5 | 2076 | 740 | 2.2039 | 1.1225 | 45 | 1.0815 | 0 | 2.625 | 1.5435 | 1.5435 |  | 145 | SS-35/10kV Podolkhi | 2,5+2,5 | 0 | 2.2039 | 1.1225 | 45 | 1.0815 | 0 | 2.625 | 1.5435 | 1.5435
146 | SS-35/10kV Popovka | 6,3+4 | 2016 | 792 | 2.166 | 0.64636 | 80 | 1.5196 | 0 | 4.2 | 2.6804 | 2.6804 |  | 146 | SS-35/10kV Popovka | 6,3+4 | 0 | 2.166 | 0.64636 | 80 | 1.5196 | 0 | 4.2 | 2.6804 | 2.6804
147 | SS-35/10kV Prelestnoe | 4+4 | 1668 | 612 | 1.7767 | 0 | 0 | 1.7767 | 0 | 4.2 | 2.4233 | 2.4233 |  | 147 | SS-35/10kV Prelestnoe | 4+4 | 0 | 1.7767 | 0 | 0 | 1.7767 | 0 | 4.2 | 2.4233 | 2.4233
148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 4608 | 2376 | 5.1845 | 0 | 0 | 5.1845 | 0 | 6.615 | 1.4305 | 1.4305 |  | 148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 0 | 5.1845 | 0 | 0 | 5.1845 | 0 | 6.615 | 1.4305 | 1.4305
149 | SS-35/10kV Prilepy | 2,5+2,5 | 468 | 274 | 0.54231 | 0.37638 | 80 | 0.16593 | 0 | 2.625 | 2.4591 | 2.4591 |  | 149 | SS-35/10kV Prilepy | 2,5+2,5 | 0 | 0.54231 | 0.37638 | 80 | 0.16593 | 0 | 2.625 | 2.4591 | 2.4591
150 | SS-35/10kV Printsevka | 2,5+2,5 | 1722 | 622 | 1.8309 | 0.352 | 120 | 1.4789 | 0 | 2.625 | 1.1461 | 1.1461 |  | 150 | SS-35/10kV Printsevka | 2,5+2,5 | 0 | 1.8309 | 0.352 | 120 | 1.4789 | 0 | 2.625 | 1.1461 | 1.1461
151 | SS-35/10kV Radkovka | 6,3+6,3 | 2576 | 1072 | 2.7902 | 0.164 | 45 | 2.6262 | 0 | 6.615 | 3.9888 | 3.9888 |  | 151 | SS-35/10kV Radkovka | 6,3+6,3 | 0 | 2.7902 | 0.164 | 45 | 2.6262 | 0 | 6.615 | 3.9888 | 3.9888
152 | SS-35/10kV Razdornoe | 2,5+2,5 | 1302 | 654 | 1.457 | 0.662 | 80 | 0.79502 | 0 | 2.625 | 1.83 | 1.83 |  | 152 | SS-35/10kV Razdornoe | 2,5+2,5 | 0 | 1.457 | 0.662 | 80 | 0.79502 | 0 | 2.625 | 1.83 | 1.83
153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 1728 | 828 | 1.9161 | 0.88491 | 80 | 1.0312 | 0 | 2.625 | 1.5938 | 1.5938 |  | 153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 0 | 1.9161 | 0.88491 | 80 | 1.0312 | 0 | 2.625 | 1.5938 | 1.5938
154 | SS-35/10kV Rzhevka | 6,3+6,3 | 3384 | 1824 | 3.8443 | 2.53 | 45 | 1.3143 | 0 | 6.615 | 5.3007 | 5.3007 |  | 154 | SS-35/10kV Rzhevka | 6,3+6,3 | 0 | 3.8443 | 2.53 | 45 | 1.3143 | 0 | 6.615 | 5.3007 | 5.3007
155 | SS-35/10kV Rovenki | 4+4 | 3036 | 1116 | 3.2346 | 1.7393 | 120 | 1.4953 | 0 | 4.2 | 2.7047 | 2.7047 |  | 155 | SS-35/10kV Rovenki | 4+4 | 0 | 3.2346 | 1.7393 | 120 | 1.4953 | 0 | 4.2 | 2.7047 | 2.7047
156 | SS-35/10kV Rogovatoe | 4+4 | 2208 | 1312 | 2.5684 | 0 | 0 | 2.5684 | 0 | 2.625 | 0.056614 | 0.056614 |  | 156 | SS-35/10kV Rogovatoe | 4+4 | 0 | 2.5684 | 0 | 0 | 2.5684 | 0 | 2.625 | 0.056614 | 0.056614
157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 2091 | 1064 | 2.3461 | 0 | 0 | 2.3461 | 0 | 2.625 | 0.27886 | 0.27886 |  | 157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 0 | 0 | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625
158 | SS-35/10kV Saprykino | 2,5+2,5 | 456 | 256 | 0.52295 | 0.22751 | 120 | 0.29543 | 0 | 2.625 | 2.3296 | 2.3296 |  | 158 | SS-35/10kV Saprykino | 2,5+2,5 | 0 | 0.52295 | 0.22751 | 120 | 0.29543 | 0 | 2.625 | 2.3296 | 2.3296
159 | SS-35/6kV Severnaya | 6,3+6,3 | 6739 | 2088 | 7.0551 | 4.8049 | 120 | 2.2502 | 0 | 6.615 | 4.3648 | 4.3648 |  | 159 | SS-35/6kV Severnaya | 6,3+6,3 | 0 | 7.0551 | 4.8049 | 120 | 2.2502 | 0 | 6.615 | 4.3648 | 4.3648
160 | SS-35/10kV Setishche | 2,5+2,5 | 1734 | 628 | 1.8442 | 1.0621 | 80 | 0.7821 | 0 | 2.625 | 1.8429 | 1.8429 |  | 160 | SS-35/10kV Setishche | 2,5+2,5 | 0 | 1.8442 | 1.0621 | 80 | 0.7821 | 0 | 2.625 | 1.8429 | 1.8429
161 | SS-35/10kV Slonovka | 4+4 | 2896 | 1680 | 3.348 | 1.1306 | 120 | 2.2174 | 0 | 4.2 | 1.9826 | 1.9826 |  | 161 | SS-35/10kV Slonovka | 4+4 | 0 | 3.348 | 1.1306 | 120 | 2.2174 | 0 | 4.2 | 1.9826 | 1.9826
162 | SS-35/6kV St.Oskol -2 | 16+16 | 10140 | 4435 | 11.0675 | 1.21 | 80 | 9.8575 | 0 | 16.8 | 6.9425 | 6.9425 |  | 162 | SS-35/6kV St.Oskol -2 | 16+16 | 0 | 11.0675 | 1.21 | 80 | 9.8575 | 0 | 16.8 | 6.9425 | 6.9425
163 | SS-35/10kV Starikovo | 4+4 | 2448 | 624 | 2.5263 | 1.3453 | 45 | 1.181 | 0 | 4.2 | 3.019 | 3.019 |  | 163 | SS-35/10kV Starikovo | 4+4 | 0 | 2.5263 | 1.3453 | 45 | 1.181 | 0 | 4.2 | 3.019 | 3.019
164 | SS-35/10kV Tavrovo | 10+10 | 8520 | 1512 | 8.6531 | 0.531 | 45 | 8.1221 | 0 | 10.5 | 2.3779 | 2.3779 |  | 164 | SS-35/10kV Tavrovo | 10+10 | 0 | 8.6531 | 0.531 | 45 | 8.1221 | 0 | 10.5 | 2.3779 | 2.3779
165 | SS-35/10kV Terebrino | 2,5+2,5 | 1020 | 564 | 1.1655 | 0.44978 | 80 | 0.71576 | 0 | 2.625 | 1.9092 | 1.9092 |  | 165 | SS-35/10kV Terebrino | 2,5+2,5 | 0 | 1.1655 | 0.44978 | 80 | 0.71576 | 0 | 2.625 | 1.9092 | 1.9092
166 | SS-35/10kV Urazovo | 6,3+6,3 | 3180 | 1080 | 3.3584 | 1.39 | 120 | 1.9684 | 0 | 6.615 | 4.6466 | 4.6466 |  | 166 | SS-35/10kV Urazovo | 6,3+6,3 | 0 | 3.3584 | 1.39 | 120 | 1.9684 | 0 | 6.615 | 4.6466 | 4.6466
167 | SS-35/10kV Utochka | 1,6+2,5 | 664 | 248 | 0.7088 | 0.47242 | 80 | 0.23639 | 0 | 1.68 | 1.4436 | 1.4436 |  | 167 | SS-35/10kV Utochka | 1,6+2,5 | 0 | 0.7088 | 0.47242 | 80 | 0.23639 | 0 | 1.68 | 1.4436 | 1.4436
168 | SS-35/6kV Fedoseevka | 4+4 | 1594 | 614 | 1.7082 | 0 | 0 | 1.7082 | 0 | 4.2 | 2.4918 | 2.4918 |  | 168 | SS-35/6kV Fedoseevka | 4+4 | 0 | 1.7082 | 0 | 0 | 1.7082 | 0 | 4.2 | 2.4918 | 2.4918
169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 752 | 304 | 0.81112 | 0.78681 | 45 | 0.024316 | 0 | 1.68 | 1.6557 | 1.6557 |  | 169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 0 | 0.81112 | 0.78681 | 45 | 0.024316 | 0 | 1.68 | 1.6557 | 1.6557
170 | SS-35/10kV Kholodnoe | 4+4 | 1864 | 620 | 1.9644 | 0 | 0 | 1.9644 | 0 | 4.2 | 2.2356 | 2.2356 |  | 170 | SS-35/10kV Kholodnoe | 4+4 | 0 | 1.9644 | 0 | 0 | 1.9644 | 0 | 4.2 | 2.2356 | 2.2356
171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 1152 | 768 | 1.3845 | 1.3513 | 20 | 0.033266 | 0 | 6.615 | 6.5817 | 6.5817 |  | 171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 0 | 1.3845 | 1.3513 | 20 | 0.033266 | 0 | 6.615 | 6.5817 | 6.5817
172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 1284 | 432 | 1.3547 | 1 | 80 | 0.35473 | 0 | 2.625 | 2.2703 | 2.2703 |  | 172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0 | 1.3547 | 1 | 80 | 0.35473 | 0 | 1 | 0.64527 | 0.64527
173 | SS-35/10kV Shatalovka | 6,3+6,3 | 1584 | 704 | 1.7334 | 0 | 0 | 1.7334 | 0 | 6.615 | 4.8816 | 4.8816 |  | 173 | SS-35/10kV Shatalovka | 6,3+6,3 | 0 | 1.7334 | 0 | 0 | 1.7334 | 0 | 6.615 | 4.8816 | 4.8816
174 | SS-35/10kV Shakhovka | 4+4 | 1518 | 582 | 1.6257 | 0.79066 | 80 | 0.83508 | 0 | 2.625 | 1.7899 | 1.7899 |  | 174 | SS-35/10kV Shakhovka | 2,5+2,5 | 0 | 1.6257 | 0.79066 | 80 | 0.83508 | 0 | 2.625 | 1.7899 | 1.7899
175 | SS-35/10kV Shishino | 6,3+6,3 | 3432 | 1008 | 3.577 | 1.03 | 80 | 2.547 | 0 | 6.615 | 4.068 | 4.068 |  | 175 | SS-35/10kV Shishino | 6,3+6,3 | 0 | 3.577 | 1.03 | 80 | 2.547 | 0 | 6.615 | 4.068 | 4.068
176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 767 | 623 | 0.98814 | 0 | 0 | 0.98814 | 0 | 1.68 | 0.69186 | 0.69186 |  | 176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 1.68 | 1.68
177 | SS-35/10kV Yablonovo | 4+4 | 1440 | 608 | 1.5631 | 1.1284 | 80 | 0.43467 | 0 | 4.2 | 3.7653 | 3.7653 |  | 177 | SS-35/10kV Yablonovo | 4+4 | 0 | 1.5631 | 1.1284 | 80 | 0.43467 | 0 | 4.2 | 3.7653 | 3.7653
178 | SS-35/10kV Yarskoe | 2,5+2,5 | 248 | 80 | 0.26058 | 0.14648 | 80 | 0.11411 | 0 | 2.625 | 2.5109 | 2.5109 |  | 178 | SS-35/10kV Yarskoe | 2,5+2,5 | 0 | 0.26058 | 0.14648 | 80 | 0.11411 | 0 | 2.625 | 2.5109 | 2.5109
| TOTAL: | 3303.1 |  |  | 2538.0096 | 1078.5217 |  | 1544.3037 | [5 empty] | 2: TOTAL:; 3: 3303.1; 4: 0; 5: 2528.9701; MVA 6: 1077.731; Min 8: 1451.239
| deficit | [10 empty] | -15.1131 |  | 2: deficit; Min 12: -18.8896
| proficit | [10 empty] | 1050.0349 |  | 2: proficit; Min 12: 1055.5207

## Current deficit - winter
The list of closed supply centers of IDGC of Centre according to winter load in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class, transformer capacity (installed MVA) |  | Current deficit, MVA
Belgorodenergo |  |  |  | cos
1 | SS-110/35/10kV D.Poljana | 6.3 | -0.033615 | 0.91497
2 | SS-110/35/10kV Irrigating | 16 | -1.8912 | 0.9465
3 | SS-35/10kV Afanasevka | 2.5 | -0.28998 | 0.93979
4 | SS-35/10kV Borisovka | 1.6 | -0.0099667 | 0.95751
5 | SS-35/10kV Boriss | 1.6 | -0.87793 | 0.90896
6 | SS-35/10kV Gostishchevo | 4 | -0.22612 | 0.93506
7 | SS-35/10kV Cossack Fox | 2.5 | -0.36811 | 0.94537
8 | SS-35/10kV Kamyzino | 2.5 | -0.87904 | 0.83378
9 | SS-35/10kV Koloskovo | 2.5 | -0.13375 | 0.95304
10 | SS-35/10kV Nikolaevka | 2.5 | -0.072864 | 0.91111
11 | SS-35/10kV Nikolsky | 4 | -0.90223 | 0.97014
12 | SS-35/10kV Pjatnitsky | 4 | -0.38428 | 0.92704
13 | SS-110/35/6kV East | 25+25 | -12.8206 | 0.93436
Total current deficit |  |  | -18.8896

## Expected deficit
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class |  | Current deficit, MVA
Belgorodenergo |  |  |  | cos
1 | SS-110/35/10kV D.Polyana | 6.3 | -0.033615 | 0.91497
2 | SS-110/35/10kV Irrigating | 16 | -1.8912 | 0.9465
3 | SS-35/10kV Afanasevka | 2.5 | -0.28998 | 0.93979
4 | SS-35/10kV Borisovka | 1.6 | -0.0099667 | 0.95751
5 | SS-35/10kV Borisy | 1.6 | -0.87793 | 0.90896
6 | SS-35/10kV Gostishchevo | 4 | -0.22612 | 0.93506
7 | SS-35/10kV Cossack Fox | 2.5 | -0.36811 | 0.94537
8 | SS-35/10kV Kamyzino | 2.5 | -0.87904 | 0.83378
9 | SS-35/10kV Koloskovo | 2.5 | -0.13375 | 0.95304
10 | SS-35/10kV Nikolaevka | 2.5 | -0.072864 | 0.91111
11 | SS-35/10kV Nikolsky | 4 | -0.90223 | 0.97014
12 | SS-35/10kV Pyatnitsky | 4 | -0.38428 | 0.92704
13 | SS-110/35/6kV East | 25+25 | -12.8206 | 0.93436
Total current deficit |  |  | -18.8896