## Kostromaenergo
Transmission capacity of supply centers of IDGC of Centre - Kostromaenergo division following the results of measurements of winter peak loads in 2011
[9 empty] | table 1 | [11 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | Sandogora 35/6 kV | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | available | 1 | Sandogora 35/6 kV | 1 | 0.141 | 0.611 | 0.55 | 120 | 0.061 | 0 | 0.55 | -0.061 | -0.061 | unavailable
2 | Gridino 35/10 kV | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | available | 2 | Gridino 35/10 kV | 1.8 | 0.406 | 1.136 | 1.2 | 120 | -0.064 | 0 | 1.2 | 0.064 | 0.064 | available
3 | Novinki 35/10 kV | 1.8 | 0.15 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.29 | 1.29 | available | 3 | Novinki 35/10 kV | 1.8 | 0 | 0.15 | 1.44 | 120 | -1.29 | 0 | 1.44 | 1.29 | 1.29 | available
4 | Priskokovo 35/10kV | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | available | 4 | Priskokovo 35/10kV | 2.5 | 0.295 | 1.795 | 1.5 | 120 | 0.295 | 0 | 1.5 | -0.295 | -0.295 | unavailable
5 | Grigortsevo 110/10 kV | 2.5 | 0.29 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.21 | 1.21 | available | 5 | Grigortsevo 110/10 kV | 2.5 | 0.019 | 0.309 | 1.5 | 120 | -1.191 | 0 | 1.5 | 1.191 | 1.191 | available
6 | Klementyevo 110/10 kV | 6.3 | 0.68 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.02 | 3.02 | available | 6 | Klementyevo 110/10 kV | 6.3 | 0.006 | 0.686 | 3.7 | 120 | -3.014 | 0 | 3.7 | 3.014 | 3.014 | available
7 | Rudino 35/10 kV | 2.5 | 0.52 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.98 | 0.98 | available | 7 | Rudino 35/10 kV | 2.5 | 0.034 | 0.554 | 1.5 | 120 | -0.946 | 0 | 1.5 | 0.946 | 0.946 | available
8 | Stoyankovo 35/10 kV | 1.6 | 0.28 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.44 | 0.44 | available | 8 | Stoyankovo 35/10 kV | 1.6 | 0.008 | 0.288 | 0.72 | 120 | -0.432 | 0 | 0.72 | 0.432 | 0.432 | available
9 | Adishchevo 35/10 kV | 4 | 1.39 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.21 | 1.21 | available | 9 | Adishchevo 35/10 kV | 4 | 0.239 | 1.629 | 2.6 | 120 | -0.971 | 0 | 2.6 | 0.971 | 0.971 | available
10 | Stolbovo 110/10 kV | 10 | 0.44 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.16 | 4.16 | available | 10 | Stolbovo 110/10 kV | 10 | 0.011 | 0.451 | 4.6 | 120 | -4.149 | 0 | 4.6 | 4.149 | 4.149 | available
11 | Raslovo 35/10 kV | 2.5 | 0.73 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.65 | 0.65 | available | 11 | Raslovo 35/10 kV | 2.5 | 0.067 | 0.797 | 1.38 | 120 | -0.583 | 0 | 1.38 | 0.583 | 0.583 | available
12 | Andreevskoe 35/10 kV | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | available | 12 | Andreevskoe 35/10 kV | 1.6 | 0.006 | 0.186 | 0.93 | 120 | -0.744 | 0 | 0.93 | 0.744 | 0.744 | available
13 | Popadyino 35/10 kV | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | available | 13 | Popadyino 35/10 kV | 1.6 | 0 | 0.22 | 0.88 | 120 | -0.66 | 0 | 0.88 | 0.66 | 0.66 | available
14 | Elegino 110/10 kV | 2.5 | 0.21 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.77 | 0.77 | available | 14 | Elegino 110/10 kV | 2.5 | 0.321 | 0.531 | 0.98 | 120 | -0.449 | 0 | 0.98 | 0.449 | 0.449 | available
15 | Krenyovo 35/10 kV | 2.5 | 0.47 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.03 | 2.03 | available | 15 | Krenyovo 35/10 kV | 2.5 | 0 | 0.47 | 2.5 | 1 day and night | -2.03 | 0 | 2.5 | 2.03 | 2.03 | available
16 | Semyonovskoe 35/10 kV | 1.6 | 0.2 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.4 | 1.4 | available | 16 | Semyonovskoe 35/10 kV | 1.6 | 0.041 | 0.241 | 1.6 | 1 day and night | -1.359 | 0 | 1.6 | 1.359 | 1.359 | available
17 | Khimik 35/10 kV | 3.2 | 0.35 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.09 | 1.09 | available | 17 | Khimik 35/10 kV | 3.2 | 0 | 0.35 | 1.44 | 120 | -1.09 | 0 | 1.44 | 1.09 | 1.09 | available
18 | N. Beryozovets 35/10 kV | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | available | 18 | N. Beryozovets 35/10 kV | 2.5 | 0.018 | 0.348 | 0.43 | 120 | -0.082 | 0 | 0.43 | 0.082 | 0.082 | available
19 | Stepanovo 35/10 kV | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | available | 19 | Stepanovo 35/10 kV | 4 | 0.11 | 0.43 | 2.32 | 120 | -1.89 | 0 | 2.32 | 1.89 | 1.89 | available
20 | Gorbachevo 35/10 kV | 1 | 0.15 | 1.7 | 120 | 1.7 | 0 | 1.7 | 1.55 | 1.55 | available | 20 | Gorbachevo 35/10 kV | 1 | 0 | 0.15 | 1.7 | 120 | -1.55 | 0 | 1.7 | 1.55 | 1.55 | available
21 | Kalinino 35/10 kV | 1 | 0.13 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.43 | 0.43 | available | 21 | Kalinino 35/10 kV | 1 | 0.017 | 0.147 | 0.56 | 120 | -0.413 | 0 | 0.56 | 0.413 | 0.413 | available
22 | Kuzemino 35/10 kV | 1.6 | 0.32 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.28 | 1.28 | available | 22 | Kuzemino 35/10 kV | 1.6 | 0 | 0.32 | 1.6 | 1 day and night | -1.28 | 0 | 1.6 | 1.28 | 1.28 | available
23 | Sovega 35/10 kV | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | available | 23 | Sovega 35/10 kV | 1 | 0.03 | 0.12 | 0.65 | 120 | -0.53 | 0 | 0.65 | 0.53 | 0.53 | available
24 | Lukovtsino 110/10 kV | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | available | 24 | Lukovtsino 110/10 kV | 2.5 | 0.011 | 0.201 | 1.38 | 120 | -1.179 | 0 | 1.38 | 1.179 | 1.179 | available
25 | Fyodorovskoe 110/10 kV | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | available | 25 | Fyodorovskoe 110/10 kV | 2.5 | 0.087 | 0.237 | 1.5 | 120 | -1.263 | 0 | 1.5 | 1.263 | 1.263 | available
26 | Pankratovo 35/10 kV | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | available | 26 | Pankratovo 35/10 kV | 1 | 0.068 | 0.128 | 0.39 | 120 | -0.262 | 0 | 0.39 | 0.262 | 0.262 | available
27 | Petrovskoe 35/10 kV | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | available | 27 | Petrovskoe 35/10 kV | 1.6 | 0.071 | 0.391 | 0.77 | 120 | -0.379 | 0 | 0.77 | 0.379 | 0.379 | available
28 | Kotelnikovo 35/10 kV | 1 | 0.13 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.13 | 0.13 | available | 28 | Kotelnikovo 35/10 kV | 1 | 0.018 | 0.148 | 0.26 | 120 | -0.112 | 0 | 0.26 | 0.112 | 0.112 | available
29 | Legitovo 35/10 kV | 2.5 | 0.38 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.72 | 0.72 | available | 29 | Legitovo 35/10 kV | 2.5 | 0 | 0.38 | 1.1 | 120 | -0.72 | 0 | 1.1 | 0.72 | 0.72 | available
30 | Sloboda 35/10 kV | 2.5 | 0.2 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.65 | 0.65 | available | 30 | Sloboda 35/10 kV | 2.5 | 0.009 | 0.209 | 0.85 | 120 | -0.641 | 0 | 0.85 | 0.641 | 0.641 | available
31 | Zavrazhye 35/10 kV | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | available | 31 | Zavrazhye 35/10 kV | 1.6 | 0.163 | 0.453 | 0.74 | 120 | -0.287 | 0 | 0.74 | 0.287 | 0.287 | available
32 | Okulovo 35/10 kV | 1.6 | 0.18 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.72 | 0.72 | available | 32 | Okulovo 35/10 kV | 1.6 | 0.063 | 0.243 | 0.9 | 120 | -0.657 | 0 | 0.9 | 0.657 | 0.657 | available
33 | Chernyshevo 35/10 kV | 4 | 0.69 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.11 | 1.11 | available | 33 | Chernyshevo 35/10 kV | 4 | 0.145 | 0.835 | 1.8 | 120 | -0.965 | 0 | 1.8 | 0.965 | 0.965 | available
34 | Yakovlevo 110/35/10 kV | 10 | 0.09 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.21 | 5.21 | available | 34 | Yakovlevo 110/35/10 kV | 10 | 0 | 0.09 | 5.3 | 120 | -5.21 | 0 | 5.3 | 5.21 | 5.21 | available
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.09 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.21 |  |  |  | Nom. Capacity LV, MVA | 10 | 0 | 0.09 | 5.3 | 120 | -5.21 | 0 | 5.3 | 5.21
35 | Chermenino 35/10 kV | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | available | 35 | Chermenino 35/10 kV | 1.6 | 0 | 0.07 | 0.86 | 120 | -0.79 | 0 | 0.86 | 0.79 | 0.79 | available
36 | Nezhitino 35/10 kV | 1 | 0.24 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.3 | 0.3 | available | 36 | Nezhitino 35/10 kV | 1 | 0.066 | 0.306 | 0.54 | 120 | -0.234 | 0 | 0.54 | 0.234 | 0.234 | available
37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.49 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.5 | 0.5 | available | 37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.209 | 0.699 | 0.99 | 120 | -0.291 | 0 | 0.99 | 0.291 | 0.291 | available
38 | Gusevo 110/10 kV | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | available | 38 | Gusevo 110/10 kV | 2.5 | 0.018 | 0.308 | 1.63 | 120 | -1.322 | 0 | 1.63 | 1.322 | 1.322 | available
39 | Medveditsa 35/10 kV | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | available | 39 | Medveditsa 35/10 kV | 2.5 | 0 | 0.53 | 1.3 | 120 | -0.77 | 0 | 1.3 | 0.77 | 0.77 | available
40 | Novinskoe 110/10 kV | 2.5 | 0.05 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.18 | 1.18 | available | 40 | Novinskoe 110/10 kV | 2.5 | 0.006 | 0.056 | 1.23 | 120 | -1.174 | 0 | 1.23 | 1.174 | 1.174 | available
41 | Filino 35/10 kV | 1.6 | 0.4 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.56 | 0.56 | available | 41 | Filino 35/10 kV | 1.6 | 0.063 | 0.463 | 0.96 | 120 | -0.497 | 0 | 0.96 | 0.497 | 0.497 | available
42 | Dyakonovo 110/10 kV | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | available | 42 | Dyakonovo 110/10 kV | 2.5 | 0.046 | 0.326 | 1.13 | 120 | -0.804 | 0 | 1.13 | 0.804 | 0.804 | available
43 | Oktyabrskaya 110/10 kV | 2.5 | 0.91 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.59 | 1.59 | available | 43 | Oktyabrskaya 110/10 kV | 2.5 | 0.034 | 0.944 | 2.5 | 1 day and night | -1.556 | 0 | 2.5 | 1.556 | 1.556 | available
44 | Kuzhbal 35/10 kV | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | available | 44 | Kuzhbal 35/10 kV | 2.5 | 0.006 | 0.406 | 1.48 | 120 | -1.074 | 0 | 1.48 | 1.074 | 1.074 | available
45 | Nikolo-Poloma 110/10 kV | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | available | 45 | Nikolo-Poloma 110/10 kV | 2.5 | 0.137 | 1.177 | 1.13 | 120 | 0.047 | 0 | 1.13 | -0.047 | -0.047 | unavailable
46 | Nikola 110/35/10 kV | 6.3 | 0.52 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.63 | 2.63 | available | 46 | Nikola 110/35/10 kV | 6.3 | 0.03 | 0.55 | 3.15 | 120 | -2.6 | 0 | 3.15 | 2.6 | 2.6 | available
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.52 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.63 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0.03 | 0.55 | 3.15 | 120 | -2.6 | 0 | 3.15 | 2.6
47 | Zavetluzhye 35/10 kV | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | available | 47 | Zavetluzhye 35/10 kV | 1.6 | 0 | 0.11 | 0.67 | 120 | -0.56 | 0 | 0.67 | 0.56 | 0.56 | available
48 | Talitsa 35/10 kV | 1.6 | 0.26 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.34 | 1.34 | available | 48 | Talitsa 35/10 kV | 1.6 | 0.018 | 0.278 | 1.6 | 1 day and night | -1.322 | 0 | 1.6 | 1.322 | 1.322 | available
49 | Khoroshaya 35/10 kV | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | available | 49 | Khoroshaya 35/10 kV | 2.5 | 0 | 0.06 | 1.95 | 120 | -1.89 | 0 | 1.95 | 1.89 | 1.89 | available
50 | Zabegaevo 35/10 kV | 1.6 | 0.11 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.77 | 0.77 | available | 50 | Zabegaevo 35/10 kV | 1.6 | 0 | 0.11 | 0.88 | 120 | -0.77 | 0 | 0.88 | 0.77 | 0.77 | available
51 | Ilyinskoe 35/10 kV | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | available | 51 | Ilyinskoe 35/10 kV | 1.6 | 0 | 0.04 | 0.9 | 120 | -0.86 | 0 | 0.9 | 0.86 | 0.86 | available
52 | Luptyug 35/10 kV | 2.5 | 0.19 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.16 | 1.16 | available | 52 | Luptyug 35/10 kV | 2.5 | 0.04 | 0.23 | 1.35 | 120 | -1.12 | 0 | 1.35 | 1.12 | 1.12 | available
53 | Solovetskoe 35/10 kV | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | available | 53 | Solovetskoe 35/10 kV | 1.6 | 0 | 0.09 | 0.72 | 120 | -0.63 | 0 | 0.72 | 0.63 | 0.63 | available
54 | Gudkovo 110/10 kV | 2.5 | 0.06 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.32 | 1.32 | available | 54 | Gudkovo 110/10 kV | 2.5 | 0.043 | 0.103 | 1.38 | 120 | -1.277 | 0 | 1.38 | 1.277 | 1.277 | available
55 | Shortyug 110/10 kV | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | available | 55 | Shortyug 110/10 kV | 6.3 | 0.012 | 0.532 | 3.47 | 120 | -2.938 | 0 | 3.47 | 2.938 | 2.938 | available
56 | Yakshanga 110/10 kV | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | available | 56 | Yakshanga 110/10 kV | 6.3 | 0.157 | 1.567 | 3.47 | 120 | -1.903 | 0 | 3.47 | 1.903 | 1.903 | available
57 | Katunino 35/10 kV | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | available | 57 | Katunino 35/10 kV | 2.5 | 0.005 | 0.175 | 1.33 | 120 | -1.155 | 0 | 1.33 | 1.155 | 1.155 | available
58 | Konyovo 35/10 kV | 1.6 | 0.33 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.55 | 0.55 | available | 58 | Konyovo 35/10 kV | 1.6 | 0.033 | 0.363 | 0.88 | 120 | -0.517 | 0 | 0.88 | 0.517 | 0.517 | available
59 | Shekshema 110/10 kV | 6.3 | 0.58 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.92 | 1.92 | available | 59 | Shekshema 110/10 kV | 6.3 | 0.091 | 0.671 | 2.5 | 1 day and night | -1.829 | 0 | 2.5 | 1.829 | 1.829 | available
60 | Golovino 35/10 kV | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | available | 60 | Golovino 35/10 kV | 1 | 0 | 0.06 | 0.12 | 120 | -0.06 | 0 | 0.12 | 0.06 | 0.06 | available
61 | Pishchyovka 35/10 kV | 1 | 0.19 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.26 | 0.26 | available | 61 | Pishchyovka 35/10 kV | 1 | 0.103 | 0.293 | 0.45 | 120 | -0.157 | 0 | 0.45 | 0.157 | 0.157 | available
62 | Vasilyovo 110/35/10 kV | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | available | 62 | Vasilyovo 110/35/10 kV | 10+10 | 0.766 | 2.896 | 0.86 | 120 | 2.036 | 0 | 10.5 | 8.464 | 8.464 | available
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.766 | 2.306 | 0.86 | 120 | 1.446 | 0 | 10.5 | 9.054
63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 6.32 | available | 63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 0.173 | 6.293 | 1.15 | 120 | 5.143 | 0 | 12.18 | 7.037 | 6.32 | available
| Nom. Capacity MV, MVA | 10+10+1,6 | 5.86 | 0 | 120 | 5.86 | 0 | 12.18 | 6.32 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 5.86 | 0 | 120 | 5.86 | 0 | 12.18 | 6.32
| Nom. Capacity LV, MVA | 10+10+1,6 | 0.26 | 1.15 | 120 | -0.89 | 0 | 12.18 | 13.07 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.173 | 0.433 | 1.15 | 120 | -0.717 | 0 | 12.18 | 12.897
64 | Apraksino 35/10 kV | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | available | 64 | Apraksino 35/10 kV | 2,5+2,5 | 0.516 | 2.246 | 0.425 | 120 | 1.821 | 0 | 2.625 | 0.804 | 0.804 | available
65 | Borshchino 35/10 kV | 4+4 | 0.66 | 0.62 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | available | 65 | Borshchino 35/10 kV | 4+4 | 0.723 | 1.383 | 0.62 | 120 | 0.763 | 0 | 4.2 | 3.437 | 3.437 | available
66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 1.41 | 0.11 | 120 | 1.3 | 0 | 1.68 | 0.38 | 0.38 | available | 66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 0.048 | 1.458 | 0.11 | 120 | 1.348 | 0 | 1.68 | 0.332 | 0.332 | available
67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | available | 67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 0.92 | 3.25 | 0.55 | 120 | 2.7 | 0 | 2.625 | -0.075 | -0.075 | unavailable
68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 1.18 | 0.4 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available | 68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 0.769 | 1.949 | 0.4 | 120 | 1.549 | 0 | 2.625 | 1.076 | 1.076 | available
69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.74 | 0.29 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | available | 69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.196 | 0.936 | 0.29 | 120 | 0.646 | 0 | 1.68 | 1.034 | 1.034 | available
70 | Minskoe 35/10 kV | 2,5+2,5 | 2.3 | 0.43 | 120 | 1.87 | 0 | 2.625 | 0.755 | 0.755 | available | 70 | Minskoe 35/10 kV | 2,5+2,5 | 0.905 | 3.205 | 0.43 | 120 | 2.775 | 0 | 2.625 | -0.15 | -0.15 | unavailable
71 | Miskovo 35/6 kV | 1,8+1,8 | 0.44 | 0.2 | 120 | 0.24 | 0 | 1.89 | 1.65 | 1.65 | available | 71 | Miskovo 35/6 kV | 1,8+1,8 | 0.043 | 0.483 | 0.2 | 120 | 0.283 | 0 | 1.89 | 1.607 | 1.607 | available
72 | Nikolskoe 35/6 kV | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | available | 72 | Nikolskoe 35/6 kV | 4+4 | 0.348 | 2.848 | 0.92 | 120 | 1.928 | 0 | 4.2 | 2.272 | 2.272 | available
73 | Samet 35/6 kV | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | available | 73 | Samet 35/6 kV | 1,6+4 | 0.243 | 1.673 | 0 | 0 | 1.673 | 0 | 1.68 | 0.007 | 0.007 | available
74 | Sukhonogovo 35/10 kV | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | available | 74 | Sukhonogovo 35/10 kV | 3,2+4 | 1.349 | 4.059 | 0 | 0 | 4.059 | 0 | 3.36 | -0.699 | -0.699 | unavailable
75 | Sushchevo 35/10 kV | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | available | 75 | Sushchevo 35/10 kV | 4+4 | 0.333 | 4.013 | 0.76 | 120 | 3.253 | 0 | 4.2 | 0.947 | 0.947 | available
76 | EMZ 35/6 kV | 1+1 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | available | 76 | EMZ 35/6 kV | 1+1 | 0 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | available
77 | Krasnoe 110/35/10 kV | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | available | 77 | Krasnoe 110/35/10 kV | 16+16 | 1.66 | 14.07 | 0 | 0 | 14.07 | 0 | 16.8 | 2.73 | 2.73 | available
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 1.66 | 13.3 | 0 | 0 | 13.3 | 0 | 16.8 | 3.5
78 | Isaevo 35/10 kV | 4+4 | 1.65 | 1.03 | 120 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | available | 78 | Isaevo 35/10 kV | 4+4 | 2.858 | 4.508 | 1.03 | 120 | 3.478 | 0 | 4.2 | 0.722 | 0.722 | available
79 | Chapaevo 35/10 kV | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 79 | Chapaevo 35/10 kV | 2,5+2,5 | 0.18 | 1.45 | 0.43 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | available
80 | Chernevo 35/10 kV | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | available | 80 | Chernevo 35/10 kV | 1,8+1,8 | 0.01 | 0.38 | 0.43 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | available
81 | Nerekhta-1 110/35/10 kV | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | available | 81 | Nerekhta-1 110/35/10 kV | 25+25 | 1.214 | 19.724 | 2.75 | 120 | 16.974 | 0 | 26.25 | 9.276 | 9.276 | available
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 1.214 | 13.204 | 2.75 | 120 | 10.454 | 0 | 26.25 | 15.796
| Nerekhta-1 110/10 kV | 16+16 | 5.79 | 2.2 | 120 | 3.59 | 0 | 16.8 | 13.21 |  |  |  | Nerekhta-1 110/10 kV | 16+16 | 0.027 | 5.817 | 2.2 | 120 | 3.617 | 0 | 16.8 | 13.183
82 | Nerekhta-2 110/10/6 kV | 5,6+10 | 1.15 | 1.55 | 120 | -0.4 | 0 | 5.88 | 6.28 | 6.28 | available | 82 | Nerekhta-2 110/10/6 kV | 10+10 | 0.34 | 1.49 | 1.55 | 120 | -0.06 | 0 | 10.5 | 10.56 | 10.56 | available
83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.78 | 0.41 | 120 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | available | 83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.209 | 0.989 | 0.41 | 120 | 0.579 | 0 | 1.68 | 1.101 | 1.101 | available
84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.38 | 0.23 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | available | 84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.008 | 0.388 | 0.23 | 120 | 0.158 | 0 | 1.68 | 1.522 | 1.522 | available
85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 4 | 0.76 | 120 | 3.24 | 0 | 6.615 | 3.375 | 3.375 | available | 85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 0.098 | 4.098 | 0.76 | 120 | 3.338 | 0 | 6.615 | 3.277 | 3.277 | available
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315
| Nom. Capacity LV, MVA | 6,3+6,3 | 3.7 | 0.76 | 120 | 2.94 | 0 | 6.615 | 3.675 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.098 | 3.798 | 0.76 | 120 | 3.038 | 0 | 6.615 | 3.577
86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 4.3 | 1.28 | 120 | 3.02 | 0 | 10.5 | 7.48 | 7.48 | available | 86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 1.309 | 5.609 | 1.28 | 120 | 4.329 | 0 | 10.5 | 6.171 | 6.171 | available
| Nom. Capacity MV, MVA | 10+10 | 0.52 | 0 | 120 | 0.52 | 0 | 10.5 | 9.98 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.52 | 0 | 120 | 0.52 | 0 | 10.5 | 9.98
| Nom. Capacity LV, MVA | 10+10 | 3.78 | 1.28 | 120 | 2.5 | 0 | 10.5 | 8 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.309 | 5.089 | 1.28 | 120 | 3.809 | 0 | 10.5 | 6.691
87 | Igodovo 35/10 kV | 1,6+1,6 | 0.4 | 0.25 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | available | 87 | Igodovo 35/10 kV | 1,6+1,6 | 0.073 | 0.473 | 0.25 | 120 | 0.223 | 0 | 1.68 | 1.457 | 1.457 | available
88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | available | 88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.023 | 0.823 | 0.56 | 120 | 0.263 | 0 | 1.68 | 1.417 | 1.417 | available
89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 0.118 | 1.438 | 0.52 | 120 | 0.918 | 0 | 2.625 | 1.707 | 1.707 | available
90 | Sudislavl 110/10 kV | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | available | 90 | Sudislavl 110/10 kV | 10+10 | 0.522 | 8.662 | 1.8 | 120 | 6.862 | 0 | 10.5 | 3.638 | 3.638 | available
91 | Voronye 35/10 kV | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | available | 91 | Voronye 35/10 kV | 1,8+1,8 | 0.06 | 0.55 | 0.4 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | available
92 | Susanino 110/35/10 kV | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | available | 92 | Susanino 110/35/10 kV | 10+10 | 0.527 | 4.457 | 1.89 | 120 | 2.567 | 0 | 10.5 | 7.933 | 7.933 | available
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.527 | 4.077 | 1.89 | 120 | 2.187 | 0 | 10.5 | 8.313
93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.25 | 0.07 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.046 | 0.296 | 0.07 | 120 | 0.226 | 0 | 2.625 | 2.399 | 2.399 | available
94 | Airport 110/35/6 kV | 16+16 | 5.91 | 2.88 | 120 | 3.03 | 0 | 16.8 | 13.77 | 13.77 | available | 94 | Airport 110/35/6 kV | 16+16 | 3.02 | 8.93 | 2.88 | 120 | 6.05 | 0 | 16.8 | 10.75 | 10.75 | available
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.91 | 2.88 | 120 | 3.03 | 0 | 16.8 | 13.77 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 3.02 | 8.93 | 2.88 | 120 | 6.05 | 0 | 16.8 | 10.75
95 | Vostochnaya-2 110/35/10 kV | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | available | 95 | Vostochnaya-2 110/35/10 kV | 25+25 | 2.114 | 25.154 | 0.02 | 120 | 25.134 | 0 | 26.25 | 1.116 | 1.116 | available
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 2.114 | 5.914 | 0.02 | 120 | 5.894 | 0 | 26.25 | 20.356
96 | Kostroma-3 110/35/10 kV | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | unavailable | 96 | Kostroma-3 110/35/10 kV | 10+16 | 1.688 | 13.178 | 0 | 120 | 13.178 | 0 | 10.5 | -2.678 | -2.678 | unavailable
| Nom. Capacity MV, MVA | 10+16 | 2.67 | 0 | 120 | 2.67 | 0 | 10.5 | 7.83 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 2.67 | 0 | 120 | 2.67 | 0 | 10.5 | 7.83
| Nom. Capacity LV, MVA | 10+16 | 8.82 | 0 | 120 | 8.82 | 0 | 10.5 | 1.68 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.688 | 10.508 | 0 | 120 | 10.508 | 0 | 10.5 | -0.008
97 | Yuzhnaya 110/35/10 kV | 25+25 | 13.98 | 0 | 120 | 13.98 | 0 | 26.25 | 12.27 | 12.27 | available | 97 | Yuzhnaya 110/35/10 kV | 25+25 | 5.143 | 19.123 | 0 | 120 | 19.123 | 0 | 26.25 | 7.127 | 7.127 | available
| Nom. Capacity MV, MVA | 25+25 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9
| Nom. Capacity LV, MVA | 25+25 | 9.63 | 0 | 120 | 9.63 | 0 | 26.25 | 16.62 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 5.143 | 14.773 | 0 | 120 | 14.773 | 0 | 26.25 | 11.477
98 | Davydovskaya 110/10 kV | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | available | 98 | Davydovskaya 110/10 kV | 25+25 | 1.336 | 10.246 | 0.02 | 120 | 10.226 | 0 | 26.25 | 16.024 | 16.024 | available
99 | Kostroma-1 110/6 kV | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | available | 99 | Kostroma-1 110/6 kV | 10+10 | 0.928 | 11.308 | 0 | 0 | 11.308 | 0 | 10.5 | -0.808 | -0.808 | unavailable
100 | Severnaya 110/6 kV | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | available | 100 | Severnaya 110/6 kV | 20+25 | 2.813 | 22.053 | 0 | 0 | 22.053 | 0 | 21 | -1.053 | -1.053 | unavailable
101 | Strommashina 110/6 kV | 40+40 | 13.83 | 0 | 0 | 13.83 | 0 | 42 | 28.17 | 28.17 | available | 101 | Strommashina 110/6 kV | 40+40 | 1.039 | 14.869 | 0 | 0 | 14.869 | 0 | 42 | 27.131 | 27.131 | available
102 | Tsentralnaya 110/10/6 kV | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | available | 102 | Tsentralnaya 110/10/6 kV | 25+25 | 5.13 | 21.57 | 0 | 0 | 21.57 | 0 | 26.25 | 4.68 | 4.68 | available
103 | Baydarka 35/6 kV | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | available | 103 | Baydarka 35/6 kV | 6,3+6,3 | 0.37 | 2.36 | 1.2 | 120 | 1.16 | 0 | 6.615 | 5.455 | 5.455 | available
104 | Volzhskaya 35/6 kV | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | available | 104 | Volzhskaya 35/6 kV | 4+4 | 0.847 | 2.137 | 0.76 | 120 | 1.377 | 0 | 4.2 | 2.823 | 2.823 | available
105 | Vostochnaya-1 35/6 kV | 25+25 | 22.36 | 0 | 0 | 22.36 | 0 | 26.25 | 3.89 | 3.89 | available | 105 | Vostochnaya-1 35/6 kV | 25+25 | 1.495 | 23.855 | 0 | 0 | 23.855 | 0 | 26.25 | 2.395 | 2.395 | available
106 | Karavaevo 35/10 kV | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | available | 106 | Karavaevo 35/10 kV | 6,3+6,3 | 0.84 | 4.3 | 0 | 0 | 4.3 | 0 | 6.615 | 2.315 | 2.315 | available
107 | Korkino 35/10 kV | 2,5+2,5 | 1.73 | 0.85 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | available | 107 | Korkino 35/10 kV | 2,5+2,5 | 0.993 | 2.723 | 0.85 | 120 | 1.873 | 0 | 2.625 | 0.752 | 0.752 | available
108 | KPD 110/35/10 kV | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | available | 108 | KPD 110/35/10 kV | 16+16 | 11.047 | 18.587 | 1.44 | 120 | 17.147 | 0 | 16.8 | -0.347 | -0.347 | unavailable
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 11.047 | 17.967 | 1.44 | 120 | 16.527 | 0 | 16.8 | 0.273
109 | SM State district power station 110/35/6 kV | 10+16 | 6.69 | 0 | 0 | 6.69 | 0 | 10.5 | 3.81 | 3.81 | available | 109 | SM State district power station 110/35/6 kV | 10+16 | 1.531 | 8.221 | 0 | 0 | 8.221 | 0 | 10.5 | 2.279 | 2.279 | available
| Nom. Capacity MV, MVA | 10+16 | 0.31 | 0 | 0 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.31 | 0 | 0 | 0.31 | 0 | 10.5 | 10.19
| Nom. Capacity LV, MVA | 10+16 | 6.38 | 0 | 0 | 6.38 | 0 | 10.5 | 4.12 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.531 | 7.911 | 0 | 0 | 7.911 | 0 | 10.5 | 2.589
110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.76 | 0.88 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.285 | 1.045 | 0.88 | 120 | 0.165 | 0 | 2.625 | 2.46 | 2.46 | available
111 | Buy (r) 110/35/10 kV | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | available | 111 | Buy (r) 110/35/10 kV | 4+10 | 0.591 | 2.461 | 0 | 120 | 2.461 | 0 | 4.2 | 1.739 | 1.739 | available
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 0 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0.591 | 0.591 | 0 | 120 | 0.591 | 0 | 4.2 | 3.609
112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | available | 112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 0.583 | 6.833 | 1.2 | 120 | 5.633 | 0 | 6.615 | 0.982 | 0.982 | available
113 | Zapadnaya 110/10 kV | 10+10 | 5.84 | 2.63 | 120 | 3.21 | 0 | 10.5 | 7.29 | 7.29 | available | 113 | Zapadnaya 110/10 kV | 10+10 | 0.037 | 5.877 | 2.63 | 120 | 3.247 | 0 | 10.5 | 7.253 | 7.253 | available
114 | Dor 35/10 kV | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | available | 114 | Dor 35/10 kV | 1,6+1,6 | 0 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | available
115 | Dyakonovo 35/10 kV | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | available | 115 | Dyakonovo 35/10 kV | 1+1 | 0.046 | 0.276 | 0.26 | 120 | 0.016 | 0 | 1.05 | 1.034 | 1.034 | available
116 | Likurga 35/10 kV | 1,8+1,6 | 0.4 | 0.12 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 116 | Likurga 35/10 kV | 1,8+1,6 | 0 | 0.4 | 0.12 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available
117 | Shushkodom 35/10 kV | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | available | 117 | Shushkodom 35/10 kV | 1+1 | 0.033 | 0.323 | 0.06 | 120 | 0.263 | 0 | 1.05 | 0.787 | 0.787 | available
118 | Novaya 110/35/10 kV | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | available | 118 | Novaya 110/35/10 kV | 6,3+6,3 | 0.404 | 3.334 | 0.64 | 120 | 2.694 | 0 | 6.615 | 3.921 | 3.921 | available
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.404 | 1.504 | 0.64 | 120 | 0.864 | 0 | 6.615 | 5.751
119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | available | 119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 0.073 | 1.433 | 0 | 120 | 1.433 | 0 | 6.615 | 5.182 | 5.182 | available
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.073 | 0.903 | 0 | 120 | 0.903 | 0 | 6.615 | 5.712
120 | Loparevo 110/10 kV | 2,5+2,5 | 0.61 | 0.55 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available | 120 | Loparevo 110/10 kV | 2,5+2,5 | 0.005 | 0.615 | 0.55 | 120 | 0.065 | 0 | 2.625 | 2.56 | 2.56 | available
121 | Poultry farm 35/10 kV | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | available | 121 | Poultry farm 35/10 kV | 4+4 | 0.03 | 1.76 | 1.28 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | available
122 | Kabanovo 35/10 kV | 2,5+2,5 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 122 | Kabanovo 35/10 kV | 2,5+2,5 | 0 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available
123 | Levkovo 35/10 kV | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | available | 123 | Levkovo 35/10 kV | 1,6+1,6 | 0.018 | 0.238 | 0.74 | 120 | -0.502 | 0 | 1.68 | 2.182 | 2.182 | available
124 | Pronino 35/10 kV | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 124 | Pronino 35/10 kV | 4+2,5 | 0.035 | 0.415 | 0.2 | 120 | 0.215 | 0 | 2.625 | 2.41 | 2.41 | available
125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.25 | 0.13 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available | 125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.111 | 0.361 | 0.13 | 120 | 0.231 | 0 | 2.625 | 2.394 | 2.394 | available
126 | Soligalich 110/35/10 kV | 10+10 | 5.73 | 1.7 | 120 | 4.03 | 0 | 10.5 | 6.47 | 6.47 | available | 126 | Soligalich 110/35/10 kV | 10+10 | 0.319 | 6.049 | 1.7 | 120 | 4.349 | 0 | 10.5 | 6.151 | 6.151 | available
| Nom. Capacity MV, MVA | 10+10 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35
| Nom. Capacity LV, MVA | 10+10 | 4.58 | 1.7 | 120 | 2.88 | 0 | 10.5 | 7.62 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.319 | 4.899 | 1.7 | 120 | 3.199 | 0 | 10.5 | 7.301
127 | Pochinok 35/10 kV | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 127 | Pochinok 35/10 kV | 1,6+2,5 | 0.023 | 0.553 | 0.34 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | available
128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | available | 128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 0.493 | 4.463 | 2.06 | 120 | 2.403 | 0 | 6.615 | 4.212 | 4.212 | available
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.493 | 3.343 | 2.06 | 120 | 1.283 | 0 | 6.615 | 5.332
129 | Suday 35/10 kV | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | available | 129 | Suday 35/10 kV | 1,6+1,6 | 0.34 | 1.35 | 0.49 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | available
130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 6.48 | 0.38 | 120 | 6.1 | 0 | 6.615 | 0.515 | 0.515 | available | 130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 0.106 | 6.586 | 0.38 | 120 | 6.206 | 0 | 6.615 | 0.409 | 0.409 | available
| Nom. Capacity MV, MVA | 6,3+16 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025
| Nom. Capacity LV, MVA | 6,3+16 | 1.89 | 0.38 | 120 | 1.51 | 0 | 6.615 | 5.105 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.106 | 1.996 | 0.38 | 120 | 1.616 | 0 | 6.615 | 4.999
131 | Palkino 35/10 kV | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | available | 131 | Palkino 35/10 kV | 2,5+4 | 0.046 | 0.746 | 0.45 | 120 | 0.296 | 0 | 2.625 | 2.329 | 2.329 | available
132 | Slovinka 35/10 kV | 1,6+1,6 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | available | 132 | Slovinka 35/10 kV | 1,6+1,6 | 0.003 | 0.153 | 0.1 | 120 | 0.053 | 0 | 1.68 | 1.627 | 1.627 | available
133 | Kady 110/35/10 kV | 10+10 | 3.87 | 0.69 | 120 | 3.18 | 0 | 10.5 | 7.32 | 7.32 | available | 133 | Kady 110/35/10 kV | 10+10 | 0.287 | 4.157 | 0.69 | 120 | 3.467 | 0 | 10.5 | 7.033 | 7.033 | available
| Nom. Capacity MV, MVA | 10+10 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44
| Nom. Capacity LV, MVA | 10+10 | 2.81 | 0.69 | 120 | 2.12 | 0 | 10.5 | 8.38 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.287 | 3.097 | 0.69 | 120 | 2.407 | 0 | 10.5 | 8.093
134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available | 134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.056 | 0.146 | 0.1 | 120 | 0.046 | 0 | 1.68 | 1.634 | 1.634 | available
135 | Ilyinskoe 110/35/10 kV | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | available | 135 | Ilyinskoe 110/35/10 kV | 10+10 | 0.006 | 5.366 | 0.04 | 120 | 5.326 | 0 | 10.5 | 5.174 | 5.174 | available
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.006 | 0.116 | 0.04 | 120 | 0.076 | 0 | 10.5 | 10.424
136 | Kologriv 35/10 kV | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | available | 136 | Kologriv 35/10 kV | 4+4 | 0.165 | 2.285 | 1.42 | 120 | 0.865 | 0 | 4.2 | 3.335 | 3.335 | available
137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0.4 | 0.08 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | available | 137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0.023 | 0.423 | 0.08 | 120 | 0.343 | 0 | 1.68 | 1.337 | 1.337 | available
138 | Makaryev-1 110/35/10 kV | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | available | 138 | Makaryev-1 110/35/10 kV | 10+10 | 0.16 | 7.7 | 0.8 | 120 | 6.9 | 0 | 10.5 | 3.6 | 3.6 | available
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.16 | 2.34 | 0.8 | 120 | 1.54 | 0 | 10.5 | 8.96
139 | Gorchukha 35/10 kV | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | available | 139 | Gorchukha 35/10 kV | 2,5+2,5 | 0.359 | 1.549 | 0 | 0 | 1.549 | 0 | 2.625 | 1.076 | 1.076 | available
140 | Makaryev-2 35/10 kV | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | available | 140 | Makaryev-2 35/10 kV | 4+4 | 0.053 | 3.053 | 1.58 | 120 | 1.473 | 0 | 4.2 | 2.727 | 2.727 | available
141 | Timoshino 35/10 kV | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | available | 141 | Timoshino 35/10 kV | 1+1 | 0.004 | 0.184 | 0 | 0 | 0.184 | 0 | 1.05 | 0.866 | 0.866 | available
142 | Unzha 35/10 kV | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | available | 142 | Unzha 35/10 kV | 1+1,6 | 0.027 | 0.837 | 0.1 | 120 | 0.737 | 0 | 1.05 | 0.313 | 0.313 | available
143 | Yakimovo 35/10 kV | 1,6+2,5 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | available | 143 | Yakimovo 35/10 kV | 1,6+2,5 | 0.009 | 0.399 | 0.32 | 120 | 0.079 | 0 | 1.68 | 1.601 | 1.601 | available
144 | BKhZ 110/6 kV | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | available | 144 | BKhZ 110/6 kV | 25+25 | 0.166 | 2.746 | 0 | 0 | 2.746 | 0 | 26.25 | 23.504 | 23.504 | available
145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | available | 145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.03 | 0.47 | 0.15 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | available
146 | Georgievskoe 35/10 kV | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | available | 146 | Georgievskoe 35/10 kV | 2,5+2,5 | 0.105 | 2.255 | 1.23 | 120 | 1.025 | 0 | 2.625 | 1.6 | 1.6 | available
147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | available | 147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 0.164 | 16.214 | 3.6 | 120 | 12.614 | 0 | 48.615 | 36.001 | 36.001 | available
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.164 | 7.684 | 3.6 | 120 | 4.084 | 0 | 48.615 | 44.531
148 | Vozherovo 35/10 kV | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | available | 148 | Vozherovo 35/10 kV | 1,6+1,6 | 0.017 | 0.167 | 0.12 | 120 | 0.047 | 0 | 1.68 | 1.633 | 1.633 | available
149 | Matveevo 35/10 kV | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | available | 149 | Matveevo 35/10 kV | 1,8+4 | 0.053 | 0.563 | 0.42 | 120 | 0.143 | 0 | 1.89 | 1.747 | 1.747 | available
150 | Parfenyevo 35/10 kV | 4+4 | 3.05 | 1.89 | 120 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | available | 150 | Parfenyevo 35/10 kV | 4+4 | 0.349 | 3.399 | 1.89 | 120 | 1.509 | 0 | 4.2 | 2.691 | 2.691 | available
151 | Vokhma 110/35/10 kV | 6,3+16 | 5.63 | 0 | 0 | 5.63 | 0 | 6.615 | 0.985 | 0.985 | available | 151 | Vokhma 110/35/10 kV | 6,3+16 | 0.268 | 5.898 | 0 | 0 | 5.898 | 0 | 6.615 | 0.717 | 0.717 | available
| Nom. Capacity MV, MVA | 6,3+16 | 2.64 | 0 | 0 | 2.64 | 0 | 6.615 | 3.975 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 2.64 | 0 | 0 | 2.64 | 0 | 6.615 | 3.975
| Nom. Capacity LV, MVA | 6,3+16 | 2.99 | 0 | 0 | 2.99 | 0 | 6.615 | 3.625 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.268 | 3.258 | 0 | 0 | 3.258 | 0 | 6.615 | 3.357
152 | Lapshino 35/10 kV | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available | 152 | Lapshino 35/10 kV | 2,5+2,5 | 0 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available
153 | Spass 35/10 kV | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 153 | Spass 35/10 kV | 1,6+2,5 | 0.041 | 0.391 | 0.35 | 120 | 0.041 | 0 | 1.68 | 1.639 | 1.639 | available
154 | Bogovarovo 35/10 kV | 2,5+4 | 1.66 | 1 | 120 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | available | 154 | Bogovarovo 35/10 kV | 2,5+4 | 0.033 | 1.693 | 1 | 120 | 0.693 | 0 | 2.625 | 1.932 | 1.932 | available
155 | Pavino 110/35/10 kV | 10+6,3 | 2.56 | 0 | 0 | 2.56 | 0 | 6.615 | 4.055 | 4.055 | available | 155 | Pavino 110/35/10 kV | 10+6,3 | 0.082 | 2.642 | 0 | 0 | 2.642 | 0 | 6.615 | 3.973 | 3.973 | available
| Nom. Capacity MV, MVA | 10+6,3 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175
| Nom. Capacity LV, MVA | 10+6,3 | 2.12 | 0 | 0 | 2.12 | 0 | 6.615 | 4.495 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.082 | 2.202 | 0 | 0 | 2.202 | 0 | 6.615 | 4.413
156 | Ledengskaya 35/10 kV | 1,6+4 | 0.22 | 0.07 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | available | 156 | Ledengskaya 35/10 kV | 1,6+4 | 0.003 | 0.223 | 0.07 | 120 | 0.153 | 0 | 1.68 | 1.527 | 1.527 | available
157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | available | 157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 0.228 | 2.648 | 0 | 0 | 2.648 | 0 | 6.615 | 3.967 | 3.967 | available
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.228 | 2.528 | 0 | 0 | 2.528 | 0 | 6.615 | 4.087
158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | available | 158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 0.138 | 1.908 | 0.75 | 120 | 1.158 | 0 | 4.2 | 3.042 | 3.042 | available
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.138 | 1.218 | 0.75 | 120 | 0.468 | 0 | 4.2 | 3.732
159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.37 | 0.27 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | available | 159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.036 | 0.406 | 0.27 | 120 | 0.136 | 0 | 1.68 | 1.544 | 1.544 | available
160 | Sharya (r) 110/35/6 kV | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | available | 160 | Sharya (r) 110/35/6 kV | 20+25 | 1.461 | 20.481 | 2 | 120 | 18.481 | 0 | 21 | 2.519 | 2.519 | available
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 1.461 | 8.281 | 2 | 120 | 6.281 | 0 | 21 | 14.719
161 | Industrial hub 110/6/6 kV | 25+25 | 5.71 | 2.5 | 120 | 3.21 | 0 | 26.25 | 23.04 | 23.04 | available | 161 | Industrial hub 110/6/6 kV | 25+25 | 0.182 | 5.892 | 2.5 | 120 | 3.392 | 0 | 26.25 | 22.858 | 22.858 | available
162 | Krivyachka 35/10 kV | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | available | 162 | Krivyachka 35/10 kV | 1,6+1 | 0.02 | 0.84 | 0.57 | 120 | 0.27 | 0 | 1.05 | 0.78 | 0.78 | available
163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.89 | 0 | 0 | 0.89 | 0 | 1.68 | 0.79 | 0.79 | available | 163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.184 | 1.074 | 0 | 0 | 1.074 | 0 | 1.68 | 0.606 | 0.606 | available
164 | Tsentralnaya 35/6 kV | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | available | 164 | Tsentralnaya 35/6 kV | 10+10 | 2.775 | 11.735 | 3 | 120 | 8.735 | 0 | 10.5 | 1.765 | 1.765 | available
| Total over Kostromaenergo | 1728.7 | 429.73 | [8 empty] | 2: Total over Kostromaenergo; 3: 1728.7; 4: 71.534; 5: 501.264
| deficit | [8 empty] | -0.99 |  | 2: deficit; Min 12: -6.213
| proficit | [8 empty] | 499.805 |  | 2: proficit; Min 12: 438.314

## Total current deficit
The list of closed supply centers of IDGC of Centre - Kostromaenergo following the results of peak load operation in 2011 (current deficit of capacity).
Item # | Name of supply center, voltage class |  | Current deficit, MVA
Kostromaenergo
1 | SS 110/35/10 kV Kostroma-3 | 10+16 | -0.99
| Nom. capacity MV, MVA | 10+16
| Nom. capacity LV, MVA | 10+16
Total current deficit (winter) |  |  | -0.99

## Total expected deficit
The list of closed supply centers of IDGC of Centre - Kostromaenergo with expected load taking into account new connections and other development of the electical networks.
Item # | Name of supply center, voltage class | Expected deficit/proficit |  | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Current deficit/proficit, MVA
1 | 2 | 3 | 12 | 13
Kostromaenergo
1 | SS 35/6 kV Sandogora | 1 | -0.061 | unavailable
2 | SS 35/10kV Priskokovo | 2.5 | -0.295 | unavailable
3 | SS 110/10 kV Nikolo-Poloma | 2.5 | -0.047 | unavailable
4 | SS 35/10 kV Ilinsky | 2,5+2,5 | -0.075 | unavailable
5 | SS 35/10 kV Minsk | 2,5+2,5 | -0.15 | unavailable
6 | SS 35/10 kV Sukhonogovo | 3,2+4 | -0.699 | unavailable
7 | SS 110/35/6 kV Kostroma-3 | 10+16 | -2.678 | unavailable
| Nom. capacity MV, MVA | 10+16
| Nom. capacity LV, MVA | 10+16
8 | SS 110/6 kV Kostroma-1 | 10+10 | -0.808 | unavailable
9 | SS 110/6 kV Northern | 20+25 | -1.053 | unavailable
10 | SS 110/35/10 kV KPD | 16+16 | -0.347 | unavailable
| Nom. capacity MV, MVA | 16+16
| Nom. capacity LV, MVA | 16+16
| Total: |  | -6.213