## Orel
Transmission capacity of supply centers of IDGC of Centre - Orelenergo division following the results of measurements of peak loads in winter 2011-2012
table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kV Almazovo | 2.5 | 0.37 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.46 | 0.46 | available | 1 | SS 35/10 kV Almazovo | 2.5 | 0.029 | 0.399 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.431 | 0.431 | available
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available | 2 | SS 35/10 kV Voronets | 2.5 | 0 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available
3 | SS 35/10 kV Gostoml | 2.5 | 0.75 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.85 | 0.85 | available | 3 | SS 35/10 kV Gostoml | 2.5 | 0.055 | 0.805 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.795 | 0.795 | available
4 | SS 35/10 kV Gubkino | 3.2 | 0.37 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.19 | 1.19 | available | 4 | SS 35/10 kV Gubkino | 3.2 | 0.032 | 0.402 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.158 | 1.158 | available
5 | SS 35/10 kV Devyatino | 1.6 | 0.16 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.55 | 0.55 | available | 5 | SS 35/10 kV Devyatino | 1.6 | 0 | 0.16 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.55 | 0.55 | available
6 | SS 35/10 kV Kamenka | 2.5 | 0.75 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.85 | 0.85 | available | 6 | SS 35/10 kV Kamenka | 2.5 | 0.02 | 0.77 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.83 | 0.83 | available
7 | SS 35/10 kV Kozminskaya | 1.6 | 0.23 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.06 | 1.06 | available | 7 | SS 35/10 kV Kozminskaya | 1.6 | 0.038 | 0.268 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.022 | 1.022 | available
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.02 | 6.14 | 60 | 2.12 | 0 | 6.14 | 2.12 | 0.32 | available | 8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 2.697 | 6.717 | 6.14 | 60 | 6.14 | 0 | 6.14 | -0.577 | -0.577 | unavailable
| Nom. capacity MV, MVA | 10 | 1.62 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.32 |  |  |  | Nom. capacity MV, MVA | 10 | 0.077 | 1.697 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.243
| Nom. capacity LV, MVA | 10 | 2.4 | 4.2 | 60 | 1.8 | 0 | 4.2 | 1.8 |  |  |  | Nom. capacity LV, MVA | 10 | 2.62 | 5.02 | 4.2 | 60 | 4.2 | 0 | 4.2 | -0.82
9 | SS 110/35/10 kV Novopolevo | 16 | 4.05 | 4.31 | 30 | 4.31 | 0 | 4.31 | 0.26 | -0.4 | unavailable | 9 | SS 110/35/10 kV Novopolevo | 16 | 0.42125 | 4.4713 | 4.31 | 30 | 4.31 | 0 | 4.31 | -0.16125 | -0.16125 | unavailable
| Nom. capacity MV, MVA | 16 | 2.54 | 3.2 | 30 | 3.2 | 0 | 3.2 | 0.66 |  |  |  | Nom. capacity MV, MVA | 16 | 0.10625 | 2.6463 | 3.2 | 30 | 3.2 | 0 | 3.2 | 0.55375
| Nom. capacity LV, MVA | 16 | 1.51 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.4 |  |  |  | Nom. capacity LV, MVA | 16 | 0.315 | 1.825 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.715
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.56 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.77 | 0.77 | available | 10 | SS 35/10 kV Nikolskaya | 2.5 | 0.0135 | 0.5735 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.7565 | 0.7565 | available
11 | SS 35/10 kV Paramonovo | 1.8 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | available | 11 | SS 35/10 kV Paramonovo | 1.8 | 0.044 | 0.194 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.286 | 0.286 | available
12 | SS 35/10 kV Senkovo | 1.6 | 0.47 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.82 | 0.82 | available | 12 | SS 35/10 kV Senkovo | 1.6 | 0.01775 | 0.48775 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.80225 | 0.80225 | available
13 | SS 35/10 kV Somovo | 2.5 | 0.29 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.67 | 0.67 | available | 13 | SS 35/10 kV Somovo | 2.5 | 0.025 | 0.315 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.645 | 0.645 | available
14 | SS 110/35/10 kV Trosna | 16 | 3.67 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.49 | -0.02 | unavailable | 14 | SS 110/35/10 kV Trosna | 16 | 0.2951 | 3.9651 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.1949 | -0.1001 | unavailable
| Nom. capacity MV, MVA | 16 | 2.38 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.02 |  |  |  | Nom. capacity MV, MVA | 16 | 0.0801 | 2.4601 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.1001
| Nom. capacity LV, MVA | 16 | 1.29 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.51 |  |  |  | Nom. capacity LV, MVA | 16 | 0.215 | 1.505 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.295
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available | 15 | SS 35/10 kV Shablykino | 5.6 | 0 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available
16 | SS 35/10 kV Yuryevo | 2.5 | 0.13 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.94 | 0.94 | available | 16 | SS 35/10 kV Yuryevo | 2.5 | 0.025 | 0.155 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.915 | 0.915 | available
17 | SS 110/35/10 kV Region V | 10 | 3.53 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.87 | 1.87 | available | 17 | SS 110/35/10 kV Region V | 10 | 0.2 | 3.583 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.817 | 1.817 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 3.53 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.87 |  |  |  | Nom. capacity LV, MVA | 10 | 0.053 | 3.583 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.817
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.62 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.255 | 0.255 | available | 18 | SS 110/10 kV Pishchevaya | 6.3 | 0.8165 | 2.4365 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.5615 | -0.5615 | unavailable
19 | SS 110/10 kV Telchye | 3.2 | 1.63 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.17 | -0.17 | unavailable | 19 | SS 110/10 kV Telchye | 3.2 | 0.038 | 1.668 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.208 | -0.208 | unavailable
20 | SS 110/10 kV B.Chern | 2.5 | 0.17 | 1 | 120 | 1 | 0 | 1 | 0.83 | 0.83 | available | 20 | SS 110/10 kV B.Chern | 2.5 | 0.015 | 0.185 | 1 | 120 | 1 | 0 | 1 | 0.815 | 0.815 | available
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.26 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.54 | 0.54 | available | 21 | SS 35/10 kV Bashkatovo | 1.6 | 0 | 0.26 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.54 | 0.54 | available
22 | SS 35/10 kV Vysokoe | 1.6 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | available | 22 | SS 35/10 kV Vysokoe | 1.6 | 0.048 | 0.228 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.012 | 1.012 | available
23 | SS 35/10 kV Gladkoe | 2.5 | 0.34 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.12 | 1.12 | available | 23 | SS 35/10 kV Gladkoe | 2.5 | 0.014 | 0.354 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.106 | 1.106 | available
24 | SS 35/10 kV Lykovo | 2.5 | 0.68 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.56 | 0.56 | available | 24 | SS 35/10 kV Lykovo | 2.5 | 0.161 | 0.841 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.399 | 0.399 | available
25 | SS 35/6 kV Sugar mill | 4 | 0.01 | 1 | 120 | 1 | 0 | 1 | 0.99 | 0.99 | available | 25 | SS 35/6 kV Sugar mill | 4 | 0 | 0.01 | 1 | 120 | 1 | 0 | 1 | 0.99 | 0.99 | available
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.24 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.44 | 0.44 | available | 26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.07 | 0.31 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.37 | 0.37 | available
27 | SS 35/10 kV Koptevo | 1.6 | 0.32 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.12 | 0.12 | available | 27 | SS 35/10 kV Koptevo | 1.6 | 0 | 0.32 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.12 | 0.12 | available
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.68 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.45 | 0.45 | available | 28 | SS 110/35/10/6 kV Meat processing factory | 10 | 0.012 | 1.711 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.419 | 0.419 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.68 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.45 |  |  |  | Nom. capacity LV, MVA | 10 | 0.031 | 1.711 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.419
29 | SS 110/35/10 kV Shatilovo | 10 | 0.9 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.21 | -0.21 | unavailable | 29 | SS 110/35/10 kV Shatilovo | 10 | 0.005 | 0.959 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.269 | -0.269 | unavailable
| Nom. capacity MV, MVA | 10 | 0.32 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.16 |  |  |  | Nom. capacity MV, MVA | 10 | 0.029 | 0.349 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.189
| Nom. capacity LV, MVA | 10 | 0.58 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.05 |  |  |  | Nom. capacity LV, MVA | 10 | 0.03 | 0.61 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.08
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.12 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.84 | 1.58 | available | 30 | SS 110/35/10 kV Sovkhoznaya | 10 | 0.6555 | 3.7755 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.1845 | 1.546 | available
| Nom. capacity MV, MVA | 10 | 2.36 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.26 |  |  |  | Nom. capacity MV, MVA | 10 | 0.6215 | 2.9815 | 6.62 | 120 | 6.62 | 0 | 6.62 | 3.6385
| Nom. capacity LV, MVA | 10 | 0.76 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.58 |  |  |  | Nom. capacity LV, MVA | 10 | 0.034 | 0.794 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.546
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.62 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.06 | 0.06 | available | 31 | SS 35/10 kV Danilovskaya | 1.6 | 0 | 0.62 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.06 | 0.06 | available
32 | SS 35/10 kV Korseevo | 1.8 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | available | 32 | SS 35/10 kV Korseevo | 1.8 | 0 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | available
33 | SS 35/10 kV Lipovets | 2.5 | 0.83 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.56 | 0.56 | available | 33 | SS 35/10 kV Lipovets | 2.5 | 0.191 | 1.021 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.369 | 0.369 | available
34 | SS 35/10 kV Misaylovo | 1.6 | 0.38 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.22 | 1.22 | available | 34 | SS 35/10 kV Misaylovo | 1.6 | 0.025 | 0.405 | 1.6 |  | 1.6 | 0 | 1.6 | 1.195 | 1.195 | available
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.29 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.02 | 0.02 | available | 35 | SS 35/10 kV Mikhaylovka | 2.5 | 0 | 0.29 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.02 | 0.02 | available
36 | SS 35/10 kV Pankovo | 1.8 | 0.32 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.28 | 1.28 | available | 36 | SS 35/10 kV Pankovo | 1.8 | 0.029 | 0.349 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.251 | 1.251 | available
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.8 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.8 | 0.8 | available | 37 | SS 35/10 kV Sudbishchi | 2.5 | 0 | 0.8 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.8 | 0.8 | available
38 | SS 35/10 kV Tim | 1.6 | 0.58 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.02 | 1.02 | available | 38 | SS 35/10 kV Tim | 1.6 | 0.017 | 0.597 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.003 | 1.003 | available
39 | SS 35/10 kV Topki | 1 | 0.55 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.05 | 1.05 | available | 39 | SS 35/10 kV Topki | 1 | 0.062 | 0.612 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.988 | 0.988 | available
40 | SS 35/10 kV Yarishche | 2.5 | 0.32 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.28 | 1.28 | available | 40 | SS 35/10 kV Yarishche | 2.5 | 0.0488 | 0.3688 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.2312 | 1.2312 | available
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.31 | 3.88 | 30 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | available | 41 | SS 110/10 kV Alshanskaya | 10+10 | 1.4678 | 5.7777 | 3.88 | 30 | 1.8977 | 0 | 10.5 | 8.6023 | 8.6023 | available
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.57 | 0.93 | 90 | -0.36 | 0 | 2.625 | 2.985 | 2.985 | available | 42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.016 | 0.586 | 0.93 | 90 | -0.344 | 0 | 2.625 | 2.969 | 2.969 | available
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.54 | 0 | - | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.315 | 0.855 | 0 |  | 0.855 | 0 | 1.68 | 0.825 | 0.825 | available
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.36 | 3.06 | 90 | -0.7 | 0 | 10.5 | 11.2 | 10.75 | available | 44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 0.681 | 3.041 | 3.06 | 90 | -0.019 | 0 | 10.5 | 10.519 | 10.519 | available
| Nom. capacity MV, MVA | 10+10 | 2.18 | 2.43 | 90 | -0.25 | 0 | 10.5 | 10.75 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.666 | 2.846 | 2.43 | 90 | 0.416 | 0 | 10.5 | 10.084
| Nom. capacity LV, MVA | 10+10 | 0.18 | 0.63 | 90 | -0.45 | 0 | 10.5 | 10.95 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.015 | 0.195 | 0.63 | 90 | -0.435 | 0 | 10.5 | 10.935
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.83 | 0.64 | 60 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.28 | 1.11 | 0.64 | 60 | 0.47 | 0 | 1.68 | 1.21 | 1.21 | available
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.09 | 2.05 | 90 | 1.04 | 0 | 6.615 | 5.575 | 5.575 | available | 46 | SS 35/10 kV Biofactory | 6,3+6,3 | 1.3315 | 4.4215 | 2.05 | 90 | 2.3715 | 0 | 6.615 | 4.2435 | 4.2435 | available
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.56 | 1.46 | 30 | 2.1 | 0 | 2.625 | 0.525 | 0.525 | available | 47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 4.046 | 7.606 | 1.46 | 30 | 6.146 | 0 | 2.625 | -3.521 | -3.521 | unavailable
48 | SS 110/10 kV Vostochnaya | 15+15 | 12.83 | 5.87 | 120 | 6.96 | 0 | 15.75 | 8.79 | 8.79 | available | 48 | SS 110/10 kV Vostochnaya | 15+15 | 0.563 | 13.393 | 5.87 | 120 | 7.523 |  | 15.75 | 8.227 | 8.227 | available
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.62 | 0.7 | 60 | 2.92 | 0 | 10.5 | 7.58 | 7.58 | available | 49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 0.028 | 3.648 | 0.7 | 60 | 2.948 | 0 | 10.5 | 7.552 | 7.552 | available
| Nom. capacity MV, MVA | 10+10 | 0.62 | 0.25 | 120 | 0.37 | 0 | 10.5 | 10.13 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.62 | 0.25 |  | 0.37 | 0 | 10.5 | 10.13
| Nom. capacity LV, MVA | 10+10 | 3 | 0.45 | 60 | 2.55 | 0 | 10.5 | 7.95 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.028 | 3.028 | 0.45 | 60 | 2.578 | 0 | 10.5 | 7.922
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.28 | 3.98 | 180 | 7.3 | 0 | 16.8 | 9.5 | 9.5 | available | 50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 0.3486 | 11.6286 | 3.98 | 180 | 7.6486 | 0 | 16.8 | 9.1514 | 9.1514 | available
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.63 | 0.64 | 60 | -0.01 | 0 | 1.89 | 1.9 | 1.9 | available | 51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.0779 | 0.7079 | 0.64 | 60 | 0.0679 | 0 | 1.89 | 1.8221 | 1.8221 | available
52 | SS 110/6 kV Zavodskaya | 40+25 | 15.35 | 4.39 | 150 | 10.96 | 0 | 26.25 | 15.29 | 15.29 | available | 52 | SS 110/6 kV Zavodskaya | 40+25 | 0.7174 | 16.0674 | 4.39 | 150 | 11.6774 | 0 | 26.25 | 14.5726 | 14.5726 | available
53 | SS 110/6 kV Zapadnaya | 63+63 | 24.88 | 5.37 | 120 | 19.51 | 19 | 66.15 | 27.64 | 27.64 | available | 53 | SS 110/6 kV Zapadnaya | 63+63 | 0 | 24.88 | 5.37 | 120 | 19.51 | 19 | 66.15 | 27.64 | 27.64 | available
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 2.27 | 1.48 | 60 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.995 | 4.265 | 1.48 | 60 | 2.785 | 0 | 2.625 | -0.16 | -0.16 | unavailable
55 | SS 35/10 kV Ilyinskaya | 3,2+2,5 | 0.76 | 1.18 | 30 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | available | 55 | SS 35/10 kV Ilyinskaya | 3,2+2,5 | 0.506 | 1.266 | 1.18 | 30 | 0.086 | 0 | 2.625 | 2.539 | 2.539 | available
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 6.3 | 0.44 | 90 | 5.86 | 0 | 10.5 | 4.64 | 4.64 | available | 56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 3.8375 | 10.1375 | 0.44 | 90 | 9.6975 | 0 | 10.5 | 0.8025 | 0.8025 | available
| Nom. capacity MV, MVA | 10+10 | 2.39 | 0 | 0 | 2.39 | 0 | 10.5 | 8.11 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.7755 | 3.1655 | 0 | 0 | 3.1655 | 0 | 10.5 | 7.3345
| Nom. capacity LV, MVA | 10+10 | 3.91 | 0.44 | 90 | 3.47 | 0 | 10.5 | 7.03 |  |  |  | Nom. capacity LV, MVA | 10+10 | 3.062 | 6.972 | 0.44 | 90 | 6.532 | 0 | 10.5 | 3.968
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.23 | 9.43 | 45 | -3.2 | 0 | 16.8 | 20 | 18.23 | available | 57 | SS 110/35/10 kV Kromskaya | 16+16 | 4.006 | 10.236 | 9.43 | 45 | 0.806 | 0 | 16.8 | 15.994 | 15.994 | available
| Nom. capacity MV, MVA | 16+16 | 3.23 | 5 | 45 | -1.77 | 0 | 16.8 | 18.57 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.444 | 3.674 | 5 | 45 | -1.326 | 0 | 16.8 | 18.126
| Nom. capacity LV, MVA | 16+16 | 3 | 4.43 | 45 | -1.43 | 0 | 16.8 | 18.23 |  |  |  | Nom. capacity LV, MVA | 16+16 | 3.562 | 6.562 | 4.43 | 45 | 2.132 | 0 | 16.8 | 14.668
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.4 | 0.95 | 30 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available | 58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 0.0801 | 1.4801 | 0.95 | 30 | 0.5301 | 0 | 2.625 | 2.0949 | 2.0949 | available
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.54 | 0 | - | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.033 | 0.573 | 0 |  | 0.573 | 0 | 1.68 | 1.107 | 1.107 | available
60 | SS 35/10 kV Kutafino | 6,3+6,3 | 0.77 | 0.83 | 30 | -0.06 | 0 | 6.615 | 6.675 | 6.675 | available | 60 | SS 35/10 kV Kutafino | 6,3+6,3 | 0.015 | 0.785 | 0.83 | 30 | -0.045 | 0 | 6.615 | 6.66 | 6.66 | available
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.9 | 1.59 | 30 | -0.69 | 0 | 2.625 | 3.315 | 3.315 | available | 61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.04775 | 0.94775 | 1.59 | 30 | -0.64225 | 0 | 2.625 | 3.2673 | 3.2673 | available
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.45 | 0.47 | 60 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available | 62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0 | 0.45 | 0.47 | 60 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.5 | 0.99 | 90 | -0.49 | 0 | 1.89 | 2.38 | 2.38 | available | 63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.025 | 0.525 | 0.99 | 90 | -0.465 | 0 | 1.89 | 2.355 | 2.355 | available
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.44 | 1.7 | 30 | -1.26 | 0 | 5.88 | 7.14 | 7.14 | available | 64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.92 | 1.36 | 1.7 | 30 | -0.34 | 0 | 5.88 | 6.22 | 6.22 | available
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 6.71 | 3.31 | 90 | 3.4 | 0 | 10.5 | 7.1 | 5.28 | available | 65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 0.525 | 7.235 | 3.31 | 90 | 3.925 | 0 | 10.5 | 6.575 | 6.575 | available
| Nom. capacity MV, MVA | 10+10 | 0.94 | 2.76 | 90 | -1.82 | 0 | 10.5 | 12.32 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.05 | 0.99 | 2.76 | 90 | -1.77 | 0 | 10.5 | 12.27
| Nom. capacity LV, MVA | 10+10 | 5.77 | 0.55 | 90 | 5.22 | 0 | 10.5 | 5.28 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.475 | 6.245 | 0.55 | 90 | 5.695 | 0 | 10.5 | 4.805
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.63 | 1.63 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 | available | 66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.00775 | 0.63775 | 1.63 | 45 | -0.99225 | 0 | 2.625 | 3.6172 | 3.6172 | available
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.39 | 0 |  | 0.39 | 0 | 1.68 | 1.29 | 1.29 | available | 67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.0165 | 0.4065 | 0 | 0 | 0.4065 | 0 | 1.68 | 1.2735 | 1.2735 | available
68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.49 | 1.53 | 90 | -1.04 | 0 | 2.625 | 3.665 | 3.665 | available | 68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.344 | 0.834 | 1.53 | 90 | -0.696 | 0 | 2.625 | 3.321 | 3.321 | available
69 | SS 110/10 kV Pishchevaya* | 40+25 | 5.7 | 2.22 | 60 | 3.48 | 0 | 26.25 | 22.77 | 22.77 | available | 69 | SS 110/10 kV Pishchevaya* | 40+25 | 0.031 | 5.731 | 2.22 | 60 | 3.511 | 0 | 26.25 | 22.739 | 22.739 | available
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.39 | 0.65 | 90 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | available | 70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.035 | 0.425 | 0.65 | 90 | -0.225 | 0 | 2.625 | 2.85 | 2.85 | available
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.81 | 1.98 | 45 | 0.83 | 0 | 10.5 | 9.67 | 9.43 | available | 71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 0.591 | 3.401 | 1.98 | 45 | 1.421 | 0 | 10.5 | 9.079 | 9.079 | available
| Nom. capacity MV, MVA | 10+10 | 1.17 | 1.41 | 45 | -0.24 | 0 | 10.5 | 10.74 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.068 | 1.238 | 1.41 | 45 | -0.172 | 0 | 10.5 | 10.672
| Nom. capacity LV, MVA | 10+10 | 1.64 | 0.57 | 45 | 1.07 | 0 | 10.5 | 9.43 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.523 | 2.163 | 0.57 | 45 | 1.593 | 0 | 10.5 | 8.907
72 | SS 35/10 kV Streletskaya | 4+4 | 1.42 | 0.91 | 90 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | available | 72 | SS 35/10 kV Streletskaya | 4+4 | 2.18 | 3.6 | 0.91 | 90 | 2.69 | 0 | 4.2 | 1.51 | 1.51 | available
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 26.53 | 3.86 | 180 | 22.67 | 0 | 68.25 | 45.58 | 20.34 | available | 73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 6.5484 | 24.1684 | 3.86 | 180 | 20.3084 | 0 | 68.25 | 47.9416 | 19.2566 | available
| Nom. capacity MV -35kV; MVA | 20+20 | 4.57 | 6.74 | 90 | -2.17 | 0 | 21 | 23.17 |  |  |  | Nom. capacity MV -35kV; MVA | 20+20 | 3.9134 | 8.4834 | 6.74 | 90 | 1.7434 | 0 | 21 | 19.2566
| Nom. capacity LV-10kV; MVA | 25+40 | 8.91 | 3 | 180 | 5.91 | 0 | 26.25 | 20.34 |  |  |  | Nom. capacity LV-10kV; MVA | 25+40 | 0 | 8.91 | 3 | 180 | 5.91 | 0 | 26.25 | 20.34
| Nom. capacity LV-6kV; MVA | 20+20+40 | 13.05 | 3.86 | 180 | 9.19 | 0 | 42 | 32.81 |  |  |  | Nom. capacity LV-6kV; MVA | 20+20+40 | 2.635 | 15.685 | 3.86 | 180 | 11.825 | 0 | 42 | 30.175
74 | SS 35/10 kV Soskovskaya | 4+3,2 | 1.02 | 0.64 | 90 | 0.38 | 0 | 3.36 | 2.98 | 2.98 | available | 74 | SS 35/10 kV Soskovskaya | 4+3,2 | 0.012 | 1.032 | 0.64 | 90 | 0.392 | 0 | 3.36 | 2.968 | 2.968 | available
75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.76 | 1.76 | 30 | -1 | 0 | 3.36 | 4.36 | 4.36 | available | 75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.0422 | 0.8022 | 1.76 | 30 | -0.9578 | 0 | 3.36 | 4.3178 | 4.3178 | available
76 | SS 110/10 kV Khimmash | 25+25 | 5.86 | 1.51 | 120 | 4.35 | 0 | 26.25 | 21.9 | 21.9 | available | 76 | SS 110/10 kV Khimmash | 25+25 | 3.514 | 9.374 | 1.51 | 120 | 7.864 | 0 | 26.25 | 18.386 | 18.386 | available
77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.77 | 2.6 | 120 | -1.83 | 0 | 5.88 | 7.71 | 7.71 | available | 77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.012 | 0.782 | 2.6 | 120 | -1.818 | 0 | 5.88 | 7.698 | 7.698 | available
78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 2.05 | 1.49 | 80 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | available | 78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 0.641 | 2.691 | 1.49 | 80 | 1.201 | 0 | 2.625 | 1.424 | 1.424 | available
79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.47 | 1.03 | 80 | -0.56 | 0 | 1.68 | 2.24 | 2.24 | available | 79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.005 | 0.475 | 1.03 | 80 | -0.555 | 0 | 1.68 | 2.235 | 2.235 | available
80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 13.57 | 3.46 | 135 | 10.11 | 0 | 26.25 | 16.14 | 16.14 | available | 80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 1.3 | 14.87 | 3.46 | 135 | 11.41 | 0 | 26.25 | 14.84 | 14.84 | available
81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 2.14 | 1.36 | 30 | 0.78 | 0 | 6.615 | 5.835 | 5.835 | available | 81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 0.046 | 2.186 | 1.36 | 30 | 0.826 | 0 | 6.615 | 5.789 | 5.789 | available
| Nom. capacity MV, MVA | 6,3+6,3 | 0.76 | 0.54 | 30 | 0.22 | 0 | 6.615 | 6.395 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.03 | 0.79 | 0.54 | 30 | 0.25 | 0 | 6.615 | 6.365
| Nom. capacity LV, MVA | 6,3+6,3 | 1.38 | 0.82 | 30 | 0.56 | 0 | 6.615 | 6.055 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.016 | 1.396 | 0.82 | 30 | 0.576 | 0 | 6.615 | 6.039
82 | SS 110/35/10 kV Shakhovo | 10+10 | 2.48 | 2.55 | 120 | -0.07 | 0 | 10.5 | 10.57 | 10.4 | available | 82 | SS 110/35/10 kV Shakhovo | 10+10 | 3.709 | 6.189 | 2.55 | 120 | 3.639 | 0 | 10.5 | 6.861 | 6.861 | available
| Nom. capacity MV, MVA | 10+10 | 0.49 | 0.39 | 120 | 0.1 | 0 | 10.5 | 10.4 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.344 | 0.834 | 0.39 | 120 | 0.444 | 0 | 10.5 | 10.056
| Nom. capacity LV, MVA | 10+10 | 1.99 | 2.16 | 120 | -0.17 | 0 | 10.5 | 10.67 |  |  |  | Nom. capacity LV, MVA | 10+10 | 3.365 | 5.355 | 2.16 | 120 | 3.195 | 0 | 10.5 | 7.305
83 | SS 35/10 kV Shepino | 2,5+2,5 | 1.3 | 1.1 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 83 | SS 35/10 kV Shepino | 2,5+2,5 | 0.7755 | 2.0755 | 1.1 | 120 | 0.9755 | 0 | 2.625 | 1.6495 | 1.6495 | available
84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 10.88 | 0.74 | 60 | 10.14 | 0 | 26.25 | 16.11 | 16.11 | available | 84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 2.008 | 12.888 | 0.74 | 60 | 12.148 | 0 | 26.25 | 14.102 | 14.102 | available
85 | SS 110/10 kV Yuzhnaya | 10+10 | 4.61 | 1.05 | 90 | 3.56 | 0 | 10.5 | 6.94 | 6.94 | available | 85 | SS 110/10 kV Yuzhnaya | 10+10 | 3.0387 | 7.6487 | 1.05 | 90 | 6.5987 | 0 | 10.5 | 3.9013 | 3.9013 | available
86 | SS 220/110/10 kV Mtsensk | 40+40 | 10.99 | 0 | - | 10.99 | 0 | 42 | 31.01 | 31.01 | available | 86 | SS 220/110/10 kV Mtsensk | 40+40 | 2.5804 | 13.5705 | 0 |  | 13.5705 | 0 | 42 | 28.4295 | 28.4295 | available
87 | SS 110/35/10 kV Kommash | 10+16 | 10.46 | 4.65 | 90 | 5.81 | 0 | 10.5 | 4.69 | 4.69 | available | 87 | SS 110/35/10 kV Kommash | 10+16 | 3.771 | 14.231 | 4.65 | 90 | 9.581 | 0 | 10.5 | 0.919 | 0.919 | available
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.46 | 4.65 | 90 | 5.81 | 0 | 10.5 | 4.69 |  |  |  | Nom. capacity LV, MVA | 10+16 | 3.771 | 14.231 | 4.65 | 90 | 9.581 | 0 | 10.5 | 0.919
88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 1.6 | 4.13 | 120 | -2.53 | 0 | 6.615 | 9.145 | 7.535 | available | 88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 0.238 | 1.838 | 4.13 | 120 | -2.292 | 0 | 6.615 | 8.907 | 7.297 | available
| Nom. capacity MV, MVA | 6,3+10 | 1.48 | 2.4 | 120 | -0.92 | 0 | 6.615 | 7.535 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.238 | 1.718 | 2.4 | 120 | -0.682 | 0 | 6.615 | 7.297
| Nom. capacity LV, MVA | 6,3+10 | 0.12 | 1.73 | 120 | -1.61 | 0 | 6.615 | 8.225 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.12 | 1.73 | 120 | -1.61 | 0 | 6.615 | 8.225
89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 2.14 | 1.83 | 120 | 0.31 | 0 | 6.615 | 6.305 | 6.305 | available | 89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 1.3 | 3.44 | 1.83 | 120 | 1.61 | 0 | 6.615 | 5.005 | 5.005 | available
90 | SS 110/35/10 kV Zalegoshch | 10+16 | 4.87 | 3.95 | 120 | 0.92 | 0 | 10.5 | 9.58 | 9.39 | available | 90 | SS 110/35/10 kV Zalegoshch | 10+16 | 0.099 | 4.969 | 3.95 | 120 | 1.019 | 0 | 10.5 | 9.481 | 9.481 | available
| Nom. capacity MV, MVA | 10+16 | 2.2 | 2.39 | 120 | -0.19 | 0 | 10.5 | 10.69 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.057 | 2.257 | 2.39 | 120 | -0.133 | 0 | 10.5 | 10.633
| Nom. capacity LV, MVA | 10+16 | 2.67 | 1.56 | 120 | 1.11 | 0 | 10.5 | 9.39 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.042 | 2.712 | 1.56 | 120 | 1.152 | 0 | 10.5 | 9.348
91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.22 | 0.66 | 120 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | available | 91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.123 | 0.343 | 0.66 | 120 | -0.317 | 0 | 2.625 | 2.942 | 2.942 | available
92 | SS 110/35/10 kV Bolkhov | 10+10 | 7.5 | 4.1 | 120 | 3.4 | 0 | 10.5 | 7.1 | 6.91 | available | 92 | SS 110/35/10 kV Bolkhov | 10+10 | 1.246 | 8.746 | 4.1 | 120 | 4.646 | 0 | 10.5 | 5.854 | 5.854 | available
| Nom. capacity MV, MVA | 10+10 | 2.26 | 2.45 | 120 | -0.19 | 0 | 10.5 | 10.69 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.139 | 2.399 | 2.45 | 120 | -0.051 | 0 | 10.5 | 10.551
| Nom. capacity LV, MVA | 10+10 | 5.24 | 1.65 | 120 | 3.59 | 0 | 10.5 | 6.91 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.107 | 6.347 | 1.65 | 120 | 4.697 | 0 | 10.5 | 5.803
93 | SS 110/35/10 kV Novosil | 10+10 | 2.9 | 2.98 | 120 | -0.08 | 0 | 10.5 | 10.58 | 9.82 | available | 93 | SS 110/35/10 kV Novosil | 10+10 | 0.245 | 3.145 | 2.98 | 120 | 0.165 | 0 | 10.5 | 10.335 | 10.335 | available
| Nom. capacity MV, MVA | 10+10 | 0.7 | 1.46 | 120 | -0.76 | 0 | 10.5 | 11.26 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.105 | 0.805 | 1.46 | 120 | -0.655 | 0 | 10.5 | 11.155
| Nom. capacity LV, MVA | 10+10 | 2.2 | 1.52 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.14 | 2.34 | 1.52 | 120 | 0.82 | 0 | 10.5 | 9.68
94 | SS 110/35/10 kV Znamenskaya | 10+10 | 1.8 | 1.78 | 120 | 0.02 | 0 | 10.5 | 10.48 | 10.32 | available | 94 | SS 110/35/10 kV Znamenskaya | 10+10 | 0.055294 | 1.8553 | 1.78 | 120 | 0.075294 | 0 | 10.5 | 10.4247 | 10.4247 | available
| Nom. capacity MV, MVA | 10+10 | 0.52 | 0.34 | 120 | 0.18 | 0 | 10.5 | 10.32 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.52 | 0.34 | 120 | 0.18 | 0 | 10.5 | 10.32
| Nom. capacity LV, MVA | 10+10 | 1.28 | 1.44 | 120 | -0.16 | 0 | 10.5 | 10.66 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.055294 | 1.3353 | 1.44 | 120 | -0.10471 | 0 | 10.5 | 10.6047
95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.51 | 0.48 | 120 | 0.03 | 0 | 1.89 | 1.86 | 1.86 | available | 95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.018 | 0.528 | 0.48 | 120 | 0.048 | 0 | 1.89 | 1.842 | 1.842 | available
96 | SS 35/10 kV Podberyozovo | 4+1 | 0.16 | 0.59 | 120 | -0.43 | 0 | 1.05 | 1.48 | 1.48 | available | 96 | SS 35/10 kV Podberyozovo | 4+1 | 0 | 0.16 | 0.59 | 120 | -0.43 | 0 | 1.05 | 1.48 | 1.48 | available
97 | SS 35/10 kV Protasovo | 2,5+1,6 | 1 | 0 |  | 1 | 0 | 1.68 | 0.68 | 0.68 | available | 97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0 | 1 | 0 |  | 1 | 0 | 1.68 | 0.68 | 0.68 | available
98 | SS 35/10 kV Alyoshnya | 1+1 | 0.27 | 0.24 | 120 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | available | 98 | SS 35/10 kV Alyoshnya | 1+1 | 0 | 0.27 | 0.24 | 120 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | available
99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0.89 | 0 | - | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available | 99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0 | 0.89 | 0 |  | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available
100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.82 | 0.63 | 120 | 0.19 |  | 2.625 | 2.435 | 2.435 | available | 100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.046 | 0.866 | 0.63 | 120 | 0.236 | 0 | 2.625 | 2.389 | 2.389 | available
101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.22 | 0.47 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | available | 101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.011 | 0.231 | 0.47 | 120 | -0.239 | 0 | 1.68 | 1.919 | 1.919 | available
102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.24 | 0 | - | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.006 | 0.246 | 0 |  | 0.246 | 0 | 2.625 | 2.379 | 2.379 | available
103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.67 | 0.67 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.039 | 0.709 | 0.67 | 120 | 0.039 | 0 | 2.625 | 2.586 | 2.586 | available
104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.35 | 0.37 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available | 104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.006 | 0.356 | 0.37 | 120 | -0.014 | 0 | 1.68 | 1.694 | 1.694 | available
105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.44 | 0.69 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | available | 105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.025 | 0.465 | 0.69 | 120 | -0.225 | 0 | 2.625 | 2.85 | 2.85 | available
106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.28 | 0 | - | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.036 | 0.316 | 0 |  | 0.316 | 0 | 1.68 | 1.364 | 1.364 | available
107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available | 107 | SS 35/10 kV Uzkoe | 1,6+1 | 0 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available
108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.92 | 0.69 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.308 | 1.228 | 0.69 | 120 | 0.538 | 0 | 2.625 | 2.087 | 2.087 | available
109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.81 | 0.76 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.044 | 0.854 | 0.76 | 120 | 0.094 | 0 | 2.625 | 2.531 | 2.531 | available
110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.16 | 0 | - | 0.16 | 0 | 1.68 | 1.52 | 1.52 | available | 110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.015 | 0.175 | 0 |  | 0.175 | 0 | 1.68 | 1.505 | 1.505 | available
111 | SS 110/35/10 kV Verkhovye I | 16+10 | 7.3 | 3.65 | 120 | 3.65 | 0 | 10.5 | 6.85 | 6.85 | available | 111 | SS 110/35/10 kV Verkhovye I | 16+10 | 0.287 | 7.587 | 3.65 | 120 | 3.937 | 0 | 10.5 | 6.563 | 6.563 | available
| Nom. capacity MV, MVA | 16+10 | 2.47 | 2.05 | 120 | 0.42 | 0 | 10.5 | 10.08 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.252 | 2.722 | 2.05 | 120 | 0.672 | 0 | 10.5 | 9.828
| Nom. capacity LV, MVA | 16+10 | 4.83 | 1.6 | 120 | 3.23 | 0 | 10.5 | 7.27 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.035 | 4.865 | 1.6 | 120 | 3.265 | 0 | 10.5 | 7.235
112 | SS 110/35/10 kV Verkhovye II | 40+40 | 10.32 | 0.3 | - | 10.02 | 0 | 42 | 31.98 | 31.98 | available | 112 | SS 110/35/10 kV Verkhovye II | 40+40 | 0.012 | 10.332 | 0.3 |  | 10.032 | 0 | 42 | 31.968 | 31.968 | available
| Nom. capacity MV, MVA | 40+40 | 0.38 | 0.3 | - | 0.08 | 0 | 42 | 41.92 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.012 | 0.392 | 0.3 |  | 0.092 | 0 | 42 | 41.908
| Nom. capacity LV, MVA | 40+40 | 9.94 | 0 | - | 9.94 | 0 | 42 | 32.06 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 9.94 | 0 |  | 9.94 | 0 | 42 | 32.06
113 | SS 110/35/10 kV Dolgoe | 16+10 | 4.83 | 3.38 | 120 | 1.45 | 0 | 10.5 | 9.05 | 8.78 | available | 113 | SS 110/35/10 kV Dolgoe | 16+10 | 0.421 | 5.251 | 3.38 | 120 | 1.871 | 0 | 10.5 | 8.629 | 8.408 | available
| Nom. capacity MV, MVA | 16+10 | 2.11 | 2.38 | 120 | -0.27 | 0 | 10.5 | 10.77 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.049 | 2.159 | 2.38 | 120 | -0.221 | 0 | 10.5 | 10.721
| Nom. capacity LV, MVA | 16+10 | 2.72 | 1 | 120 | 1.72 | 0 | 10.5 | 8.78 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.372 | 3.092 | 1 | 120 | 2.092 | 0 | 10.5 | 8.408
114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 4.6 | 2.79 | 120 | 1.81 | 0 | 10.5 | 8.69 | 8.69 | available | 114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 0.23 | 4.83 | 2.79 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.875 | available
| Nom. capacity MV, MVA | 10+16 | 2.75 | 2.46 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.125 | 2.875 | 2.46 | 120 | 0.415 | 0 | 10.5 | 10.085
| Nom. capacity LV, MVA | 10+16 | 1.85 | 0.33 | 120 | 1.52 | 0 | 10.5 | 8.98 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.105 | 1.955 | 0.33 | 120 | 1.625 | 0 | 10.5 | 8.875
115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 4.18 | 1.54 | 120 | 2.64 | 0 | 10.5 | 7.86 | 7.86 | available | 115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 0 | 4.18 | 1.54 | 120 | 2.64 | 0 | 10.5 | 7.86 | 7.86 | available
| Nom. capacity MV, MVA | 10+10 | 1.54 | 1.29 | 120 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.54 | 1.29 | 120 | 0.25 | 0 | 10.5 | 10.25
| Nom. capacity LV, MVA | 10+10 | 2.64 | 0.25 | 120 | 2.39 | 0 | 10.5 | 8.11 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.64 | 0.25 | 120 | 2.39 | 0 | 10.5 | 8.11
116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 5.52 | 2.84 | 120 | 2.68 | 0 | 10.5 | 7.82 | 7.82 | available | 116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 0.6335 | 6.1535 | 2.84 | 120 | 3.3135 | 0 | 10.5 | 7.1865 | 7.1865 | available
| Nom. capacity MV, MVA | 10+10 | 2.73 | 2.12 | 120 | 0.61 | 0 | 10.5 | 9.89 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.1405 | 2.8705 | 2.12 | 120 | 0.7505 | 0 | 10.5 | 9.7495
| Nom. capacity LV, MVA | 10+10 | 2.79 | 0.72 | 120 | 2.07 | 0 | 10.5 | 8.43 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.493 | 3.283 | 0.72 | 120 | 2.563 | 0 | 10.5 | 7.937
117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 27.05 | 13.39 | 120 | 13.66 | 0 | 26.25 | 12.59 | 12.59 | available | 117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 2.2768 | 29.3268 | 13.39 | 120 | 15.9368 | 0 | 26.25 | 10.3132 | 10.3132 | available
| Nom. capacity MV, MVA | 40+25 | 19.55 | 10.84 | 120 | 8.71 | 0 | 26.25 | 17.54 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.2768 | 21.8268 | 10.84 | 120 | 10.9868 | 0 | 26.25 | 15.2632
| Nom. capacity LV, MVA | 40+25 | 7.5 | 2.55 | 120 | 4.95 | 0 | 26.25 | 21.3 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0 | 7.5 | 2.55 | 120 | 4.95 | 0 | 26.25 | 21.3
118 | SS 110/6 kV Plastmass | 16+16 | 9.76 | 0 | - | 9.76 | 0 | 16.8 | 7.04 | 7.04 | available | 118 | SS 110/6 kV Plastmass | 16+16 | 0 | 9.76 | 0 |  | 9.76 | 0 | 16.8 | 7.04 | 7.04 | available
119 | SS 110/10 kV PM | 10+10 | 5.02 | 0 | - | 5.02 | 0 | 10.5 | 5.48 | 5.48 | available | 119 | SS 110/10 kV PM | 10+10 | 0 | 5.02 | 0 |  | 5.02 | 0 | 10.5 | 5.48 | 5.48 | available
120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.99 | 1.85 | 120 | -0.86 | 0 | 6.615 | 7.475 | 7.475 | available | 120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.034 | 1.024 | 1.85 | 120 | -0.826 | 0 | 6.615 | 7.441 | 7.441 | available
121 | SS 110/10 kV R.Brod | 5,6+10 | 1.34 | 0.29 | 120 | 1.05 | 0 | 5.88 | 4.83 | 4.83 | available | 121 | SS 110/10 kV R.Brod | 5,6+10 | 0.018 | 1.358 | 0.29 | 120 | 1.068 | 0 | 5.88 | 4.812 | 4.812 | available
122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.67 | 0.13 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.0465 | 0.7165 | 0.13 | 120 | 0.5865 | 0 | 1.68 | 1.0935 | 1.0935 | available
123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 1.33 | 0.65 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available | 123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.051 | 1.381 | 0.65 | 120 | 0.731 | 0 | 2.625 | 1.894 | 1.894 | available
124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.46 | 0.43 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | available | 124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.007 | 0.467 | 0.43 | 120 | 0.037 | 0 | 2.625 | 2.588 | 2.588 | available
125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.55 | 0.56 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available | 125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0 | 0.55 | 0.56 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available
126 | SS 35/10 kV Droskovo | 4+2,5 | 1.44 | 0 | - | 1.44 | 0 | 2.625 | 1.185 | 1.185 | available | 126 | SS 35/10 kV Droskovo | 4+2,5 | 0.094 | 1.534 | 0 |  | 1.534 | 0 | 2.625 | 1.091 | 1.091 | available
127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 1.03 | 0.39 | 120 | 0.64 | 0 | 6.615 | 5.975 | 5.975 | available | 127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.015 | 1.045 | 0.39 | 120 | 0.655 | 0 | 6.615 | 5.96 | 5.96 | available
128 | SS 35/10 kV Krutoe | 2,5+2,5 | 1.84 | 0.87 | 120 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | available | 128 | SS 35/10 kV Krutoe | 2,5+2,5 | 0.065 | 1.905 | 0.87 | 120 | 1.035 | 0 | 2.625 | 1.59 | 1.59 | available
129 | SS 35/10 kV Mezentsevo | 4+6,3 | 2.13 | 1.11 | 80 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | available | 129 | SS 35/10 kV Mezentsevo | 4+6,3 | 0.097 | 2.227 | 1.11 | 80 | 1.117 | 0 | 4.2 | 3.083 | 3.083 | available
130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.11 | 0 | - | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available | 130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0 | 0.11 | 0 |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available
131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.46 | 0.39 | - | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.008 | 0.468 | 0.39 |  | 0.078 | 0 | 2.625 | 2.547 | 2.547 | available
132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 1.48 | 0.54 | 80 | 0.94 | 0 | 2.625 | 1.685 | 1.685 | available | 132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 0.045 | 1.525 | 0.54 | 80 | 0.985 | 0 | 2.625 | 1.64 | 1.64 | available
133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.38 | 1.67 | 120 | -1.29 | 0 | 3.36 | 4.65 | 4.65 | available | 133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.012 | 0.392 | 1.67 | 120 | -1.278 | 0 | 3.36 | 4.638 | 4.638 | available
134 | SS 35/6 kV Pushkarskaya | 4+4 | 5.35 | 0 |  | 5.35 | 0 | 4.2 | -1.15 | -1.15 | unavailable | 134 | SS 35/6 kV Pushkarskaya | 4+4 | 0 | 5.35 | 0 |  | 5.35 | 0 | 4.2 | -1.15 | -1.15 | unavailable
135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0.43 | 0.25 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0 | 0.43 | 0.25 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available
136 | SS 35/10 kV Rosstani | 2,5+2,5 | 1.44 | 0.7 | 80 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | available | 136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.02 | 1.46 | 0.7 | 80 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available
137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.24 | 1.5 | 120 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | available | 137 | SS 35/10 kV Sergievskaya | 4+2,5 | 0.4305 | 1.6705 | 1.5 | 120 | 0.1705 | 0 | 2.625 | 2.4545 | 2.4545 | available
138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.59 | 0.33 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.003 | 0.593 | 0.33 | 120 | 0.263 | 0 | 1.68 | 1.417 | 1.417 | available
139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.34 | 0 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | available | 139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.015 | 0.355 | 0 |  | 0.355 | 0 | 1.68 | 1.325 | 1.325 | available
140 | SS 35/10 kV SSK | 1,6+1,6 | 0.09 | 0 |  | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available | 140 | SS 35/10 kV SSK | 1,6+1,6 | 0 | 0.09 | 0 |  | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available
141 | SS 35/10 kV Urynok | 1,6+1,6 | 1.08 | 0.52 | 20 | 0.56 | 0 | 1.68 | 1.12 | 1.12 | available | 141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.025 | 1.105 | 0.52 | 20 | 0.585 | 0 | 1.68 | 1.095 | 1.095 | available
142 | SS 35/10 kV Khomutovo | 4+4 | 1.89 | 0.31 | 80 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | available | 142 | SS 35/10 kV Khomutovo | 4+4 | 0.249 | 2.139 | 0.31 | 80 | 1.829 | 0 | 4.2 | 2.371 | 2.371 | available
| Total: | [10 empty] | 2: Total:; 4: 101.8454; 5: 652.7114
| deficit | [8 empty] | -1.95 |  | 2: deficit; Min 12: -6.7078
| proficit | [8 empty] | 628.35 |  | 2: proficit; Min 12: 500.2593
* | Substations are not assets of the division, but IDGC of Center - Orelenergo issues technical specifications for customer connections.
SWG-10kV SS Mtsensk is in sublease, and SS Pischevaya is actually ownerless.

## Total current deficit
The list of closed supply centers of IDGC of Centre - Orelenergo division in winter 2010 (current deficit of capacity).
Item # | Name of supply center, voltage class | [7 empty] | Current deficit, MVA
Orelenergo
1 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | -0.4
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
2 | SS 110/35/10 kV Trosna | 16 | [6 empty] | -0.02
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.17
4 | SS 35/6 kV Pushkarskaya | 4+4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -1.15
5 | SS 110/35/10 kV Shatilovo | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.21
| Nom. capacity MV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Nom. capacity LV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total current deficit |  | 53.2 | [6 empty] | -1.95

## Total expected deficit
The list of closed supply centers of IDGC of Centre - Orelenergo with expected load taking into account new connections and other development of the electical networks.
Item # | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 4 | 5
Orelenergo
1 | SS 110/35/10 kV Maloarkhangelskaya | 10 | [6 empty] | #REF! |  | -0.577 | unavailable
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
2 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | #REF! |  | -0.16125 | unavailable
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Pishchevaya | 6.3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.5615 | unavailable
4 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.208 | unavailable
5 | SS 110/35/10 kV Shatilovo | 10 | [6 empty] | #REF! |  | -0.269 | unavailable
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
6 | SS 110/10 kV Volodarskaya | 2,5+6,3 | [8 empty] | -3.521 | unavailable
7 | SS 35/6 kV Pushkarskaya | 4+4 | [8 empty] | -1.15 | unavailable
8 | SS 110/35/10 kV Trosna | 16 | [8 empty] | -0.1001 | unavailable
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
9 | SS 35/10 kV Zvyaginki | 2,5+2,5 | [8 empty] | -0.16 | unavailable
| Total: | 83.3 | [8 empty] | -6.7078