## Смоленскэнерго
Annex 2
Calculation of transmission capacity of supply centres of IDGC of Center - Orelenergo following the winter peak load measurements in 2010
[9 empty] | Table1 | [11 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.3 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.4 | 0.4 | available | 1 | Gerchiki 35/10 | 2.5 | 0.4 | 0.7 | 0.7 | 1 day and night | 0 | 0 | 0.7 | 0 | 0 | available
2 | Verkhovye 35/10 | 4 | 0.55 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.81 | 0.81 | available | 2 | Verkhovye 35/10 | 4 | 0 | 0.55 | 1.36 | 1 day and night | -0.81 | 0 | 1.36 | 0.81 | 0.81 | available
3 | Neykovo 35/10 | 2.5 | 0.22 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.51 | 1.51 | available | 3 | Neykovo 35/10 | 2.5 | 0 | 0.22 | 1.73 | 1 day and night | -1.51 | 0 | 1.73 | 1.51 | 1.51 | available
4 | Merlino 110/35/10 | 6.3 | 0.35 | 0.35 | 1 day and night | 0.35 | 0 | 0.35 | 0 | 0 | available | 4 | Merlino 110/35/10 | 6.3 | 0.43 | 0.78 | 0.78 | 1 day and night | 0 | 0 | 0.78 | 0 | 0 | available
| Nom. capacity MV, МVА | 6.3 | 0.05 | 0.05 | 1 day and night | 0.05 | 0 | 0.05 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0.39 | 0.44 | 0.44 |  | 0 | 0 | 0.44 | 0
| Nom. capacity LV, МVА | 6.3 | 0.3 | 0.3 | 1 day and night | 0.3 | 0 | 0.3 | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.04 | 0.34 | 0.34 | 1 day and night | 0 | 0 | 0.34 | 0
5 | Belyaevo 35/10 | 1.6 | 0.22 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 1.46 | 1.46 | available | 5 | Belyaevo 35/10 | 1.6 | 0 | 0.22 | 1.68 | 1 day and night | -1.46 | 0 | 1.68 | 1.46 | 1.46 | available
6 | Zaozerye 35/10 | 1.6 | 0.15 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.7 | 0.7 | available | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.15 | 0.85 | 1 day and night | -0.7 | 0 | 0.85 | 0.7 | 0.7 | available
7 | Selezni 35/10 | 2.5 | 0.41 | 2.21 | 1 day and night | 2.21 | 0 | 2.21 | 1.8 | 1.8 | available | 7 | Selezni 35/10 | 2.5 | 0 | 0.41 | 2.21 | 1 day and night | -1.8 | 0 | 2.21 | 1.8 | 1.8 | available
8 | Logovo 110/10 | 6.3 | 0.43 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.93 | 0.93 | available | 8 | Logovo 110/10 | 6.3 | 0 | 0.43 | 1.36 | 1 day and night | -0.93 | 0 | 1.36 | 0.93 | 0.93 | available
9 | Dubrovka 35/10 | 2.5 | 0.43 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.93 | 0.93 | available | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.53 | 1.36 | 1 day and night | -0.83 | 0 | 1.36 | 0.83 | 0.83 | available
10 | Svistovichi 35/10 | 2.5 | 0.17 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.68 | 0.68 | available | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.17 | 0.85 | 1 day and night | -0.68 | 0 | 0.85 | 0.68 | 0.68 | available
11 | Elsha 35/10 | 1.6 | 0.09 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.76 | 0.76 | available | 11 | Elsha 35/10 | 1.6 | 0 | 0.09 | 0.85 | 1 day and night | -0.76 | 0 | 0.85 | 0.76 | 0.76 | available
12 | Sapsho 35/10 | 4 | 0.76 | 2.12 | 1 day and night | 2.12 | 0 | 2.12 | 1.36 | 1.36 | available | 12 | Sapsho 35/10 | 4 | 0.18 | 0.94 | 2.12 | 1 day and night | -1.18 | 0 | 2.12 | 1.18 | 1.18 | available
13 | Divo 110/10 | 2.5 | 0.43 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.42 | 0.42 | available | 13 | Divo 110/10 | 2.5 | 0.23 | 0.66 | 0.85 | 1 day and night | -0.19 | 0 | 0.85 | 0.19 | 0.19 | available
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 1 day and night | 1.02 | 0 | 1.02 | 0.57 | 0.57 | available | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.45 | 1.02 | 1 day and night | -0.57 | 0 | 1.02 | 0.57 | 0.57 | available
15 | Zamoshye 35/10 | 2.5 | 0.14 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.54 | 0.54 | available | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.14 | 0.68 | 1 day and night | -0.54 | 0 | 0.68 | 0.54 | 0.54 | available
16 | Loino 35/10 | 2.5 | 0.19 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.66 | 0.66 | available | 16 | Loino 35/10 | 2.5 | 0 | 0.19 | 0.85 | 1 day and night | -0.66 | 0 | 0.85 | 0.66 | 0.66 | available
17 | Rokot 35/10 | 2.5 | 0.22 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 1.08 | 1.08 | available | 17 | Rokot 35/10 | 2.5 | 0 | 0.22 | 1.3 | 1 day and night | -1.08 | 0 | 1.3 | 1.08 | 1.08 | available
18 | Nikontsy 35/10 | 2.5 | 0.14 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.71 | 0.71 | available | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.14 | 0.85 | 1 day and night | -0.71 | 0 | 0.85 | 0.71 | 0.71 | available
19 | Batishchevo 35/10 | 2.5 | 0.36 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.37 | 1.37 | available | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.36 | 1.73 | 1 day and night | -1.37 | 0 | 1.73 | 1.37 | 1.37 | available
20 | Vasino 35/10 | 2.5 | 1.08 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 1.47 | 1.47 | available | 20 | Vasino 35/10 | 2.5 | 0 | 1.08 | 2.55 | 1 day and night | -1.47 | 0 | 2.55 | 1.47 | 1.47 | available
21 | Bulgakovo 35/10 | 2.5 | 0.36 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.37 | 1.37 | available | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.36 | 1.73 | 1 day and night | -1.37 | 0 | 1.73 | 1.37 | 1.37 | available
22 | Spas-Ugly 35/10 | 1.6 | 0.18 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.5 | 0.5 | available | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.18 | 0.68 | 1 day and night | -0.5 | 0 | 0.68 | 0.5 | 0.5 | available
23 | Tretyakovo 35/10 | 4 | 0.36 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.19 | 2.19 | available | 23 | Tretyakovo 35/10 | 4 | 0 | 0.36 | 2.55 | 1 day and night | -2.19 | 0 | 2.55 | 2.19 | 2.19 | available
24 | Velisto 35/10 | 2.5 | 0.14 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 1.16 | 1.16 | available | 24 | Velisto 35/10 | 2.5 | 0 | 0.14 | 1.3 | 1 day and night | -1.16 | 0 | 1.3 | 1.16 | 1.16 | available
25 | Baturino 35/10 | 1.6 | 0.14 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.71 | 0.71 | available | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.32 | 0.85 | 1 day and night | -0.53 | 0 | 0.85 | 0.53 | 0.53 | available
26 | Pechatniki 35/10 | 2.5 | 0.72 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 1.905 | 1.905 | available | 26 | Pechatniki 35/10 | 2.5 | 0 | 0.72 | 2.625 | 1 day and night | -1.905 | 0 | 2.625 | 1.905 | 1.905 | available
27 | Garistovo 35/10 | 1.6 | 0.1 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.75 | 0.75 | available | 27 | Garistovo 35/10 | 1.6 | 0 | 0.1 | 0.85 | 1 day and night | -0.75 | 0 | 0.85 | 0.75 | 0.75 | available
28 | Bezzaboty 35/10 | 2.5 | 0.14 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.59 | 1.59 | available | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.14 | 1.73 | 1 day and night | -1.59 | 0 | 1.73 | 1.59 | 1.59 | available
29 | Vysokoe 35/10 | 2.5 | 0.14 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.41 | 2.41 | available | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.14 | 2.55 | 1 day and night | -2.41 | 0 | 2.55 | 2.41 | 2.41 | available
30 | Zaytsevo 35/10 | 1.6 | 0.38 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.47 | 0.47 | available | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.38 | 0.85 | 1 day and night | -0.47 | 0 | 0.85 | 0.47 | 0.47 | available
31 | Saveevo 35/10 | 2.5 | 0.33 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.52 | 0.52 | available | 31 | Saveevo 35/10 | 2.5 | 0 | 0.33 | 0.85 | 1 day and night | -0.52 | 0 | 0.85 | 0.52 | 0.52 | available
32 | Gorenovo 35/10 | 1.6 | 0.21 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 1.47 | 1.47 | available | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.21 | 1.68 | 1 day and night | -1.47 | 0 | 1.68 | 1.47 | 1.47 | available
33 | Shpunty 35/10 | 2.5 | 0.36 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.49 | 0.49 | available | 33 | Shpunty 35/10 | 2.5 | 0.42 | 0.78 | 0.85 | 1 day and night | -0.07 | 0 | 0.85 | 0.07 | 0.07 | available
34 | Kadino 35/10 | 2.5 | 0.14 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.59 | 1.59 | available | 34 | Kadino 35/10 | 2.5 | 0 | 0.14 | 1.73 | 1 day and night | -1.59 | 0 | 1.73 | 1.59 | 1.59 | available
35 | Стегримово 35/10 | 2.5 | 0.12 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 2.505 | 2.505 | available | 35 | Стегримово 35/10 | 2.5 | 0 | 0.12 | 2.625 | 1 day and night | -2.505 | 0 | 2.625 | 2.505 | 2.505 | available
36 | Zhukovo 35/10 | 2.5 | 0.26 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.47 | 1.47 | available | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.26 | 1.73 | 1 day and night | -1.47 | 0 | 1.73 | 1.47 | 1.47 | available
37 | Mikshino 35/10 | 2.5 | 0.11 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.62 | 1.62 | available | 37 | Mikshino 35/10 | 2.5 | 0 | 0.11 | 1.73 | 1 day and night | -1.62 | 0 | 1.73 | 1.62 | 1.62 | available
38 | Petrovichi 35/10 | 2.5 | 0.16 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.39 | 2.39 | available | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.16 | 2.55 | 1 day and night | -2.39 | 0 | 2.55 | 2.39 | 2.39 | available
39 | Mikulichi 35/10 | 2.5 | 0.35 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 2.275 | 2.275 | available | 39 | Mikulichi 35/10 | 2.5 | 0.07 | 0.42 | 2.625 | 1 day and night | -2.205 | 0 | 2.625 | 2.205 | 2.205 | available
40 | Nedeykovichi 35/10 | 2.5 | 0.24 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.61 | 0.61 | available | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.24 | 0.85 | 1 day and night | -0.61 | 0 | 0.85 | 0.61 | 0.61 | available
41 | Posyolki 110/35/10 | 6.3 | 0.48 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.46 | 0.46 | available | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.48 | 0.94 | 1 day and night | -0.46 | 0 | 0.94 | 0.46 | 0.46 | available
42 | Kuzmichi 35/10 | 2.5 | 0.21 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.52 | 1.52 | available | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.21 | 1.73 | 1 day and night | -1.52 | 0 | 1.73 | 1.52 | 1.52 | available
43 | Maksheevo 110/10 | 6.3 | 0.53 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.02 | 2.02 | available | 43 | Maksheevo 110/10 | 6.3 | 0 | 0.53 | 2.55 | 1 day and night | -2.02 | 0 | 2.55 | 2.02 | 2.02 | available
44 | Putkovo 35/10 | 1.8 | 0.22 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.63 | 0.63 | available | 44 | Putkovo 35/10 | 1.8 | 0.06 | 0.28 | 0.85 | 1 day and night | -0.57 | 0 | 0.85 | 0.57 | 0.57 | available
45 | Uspenskoe 35/10 | 2.5 | 0.45 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.1 | 2.1 | available | 45 | Uspenskoe 35/10 | 2.5 | 0.15 | 0.6 | 2.55 | 1 day and night | -1.95 | 0 | 2.55 | 1.95 | 1.95 | available
46 | Kalpita 35/10 | 1.6 | 0.05 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.8 | 0.8 | available | 46 | Kalpita 35/10 | 1.6 | 0 | 0.05 | 0.85 | 1 day and night | -0.8 | 0 | 0.85 | 0.8 | 0.8 | available
47 | Kasnya 110/10 | 2.5 | 0.29 | 2.62 | 1 day and night | 2.62 | 0 | 2.62 | 2.33 | 2.33 | available | 47 | Kasnya 110/10 | 2.5 | 0 | 0.29 | 2.62 | 1 day and night | -2.33 | 0 | 2.62 | 2.33 | 2.33 | available
48 | Akatovo 35/10 | 1.6 | 1.06 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 0.62 | 0.62 | available | 48 | Akatovo 35/10 | 1.6 | 1.34 | 2.4 | 1.68 | 1 day and night | 0.72 | 0 | 1.68 | -0.72 | -0.72 | unavailable
49 | Gorki 35/10 | 1.6 | 0.19 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.49 | 0.49 | available | 49 | Gorki 35/10 | 1.6 | 0 | 0.19 | 0.68 | 1 day and night | -0.49 | 0 | 0.68 | 0.49 | 0.49 | available
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.06 | 0.06 | available | 50 | Druzhba 35/10 | 2.5 | 0 | 0.79 | 0.85 | 1 day and night | -0.06 | 0 | 0.85 | 0.06 | 0.06 | available
51 | NS-21 110/10 | 16 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 | 0 | available | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 | 0 | available
52 | NS-22 110/35/10 | 25 | 2.97 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0 | 0 | available | 52 | NS-22 110/35/10 | 25 | 1.81 | 4.78 | 4.78 | 1 day and night | 0 | 0 | 4.78 | 0 | 0 | available
| Nom. capacity MV, МVА | 25 | 2.97 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 1.81 | 4.78 | 4.78 | 1 day and night | 0 | 0 | 4.78 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.44 | 2.62 | 1 day and night | 2.62 | 0 | 2.62 | 2.18 | 2.18 | available | 53 | Shuyskoe 35/10 | 2.5 | 0.05 | 0.49 | 2.62 | 1 day and night | -2.13 | 0 | 2.62 | 2.13 | 2.13 | available
54 | Torbeevo 110/10 | 6.3 | 0.3 | 2.89 | 1 day and night | 2.89 | 0 | 2.89 | 2.59 | 2.59 | available | 54 | Torbeevo 110/10 | 6.3 | 0.15 | 0.45 | 2.89 | 1 day and night | -2.44 | 0 | 2.89 | 2.44 | 2.44 | available
55 | Leuzdovo 35/10 | 1 | 0.14 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.54 | 0.54 | available | 55 | Leuzdovo 35/10 | 1 | 0.3 | 0.44 | 0.68 | 1 day and night | -0.24 | 0 | 0.68 | 0.24 | 0.24 | available
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.56 | 1.56 | available | 56 | Maltsevo 35/10 | 2.5 | 0.01 | 0.18 | 1.73 | 1 day and night | -1.55 | 0 | 1.73 | 1.55 | 1.55 | available
57 | Avrora 35/10 | 2.5 | 0.26 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.42 | 0.42 | available | 57 | Avrora 35/10 | 2.5 | 3.38 | 3.64 | 0.68 | 1 day and night | 2.96 | 0 | 0.68 | -2.96 | -2.96 | unavailable
58 | Bekhteevo 35/10 | 2.5 | 0.13 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.55 | 0.55 | available | 58 | Bekhteevo 35/10 | 2.5 | 0.07 | 0.2 | 0.68 | 1 day and night | -0.48 | 0 | 0.68 | 0.48 | 0.48 | available
59 | Sereda 35/10 | 2.5 | 0.31 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.37 | 0.37 | available | 59 | Sereda 35/10 | 2.5 | 0 | 0.31 | 0.68 | 1 day and night | -0.37 | 0 | 0.68 | 0.37 | 0.37 | available
60 | Mikhali 35/10 | 2.5 | 0.08 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.77 | 0.77 | available | 60 | Mikhali 35/10 | 2.5 | 0 | 0.08 | 0.85 | 1 day and night | -0.77 | 0 | 0.85 | 0.77 | 0.77 | available
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 1 day and night | 0 | 0 | 0 | -0.06 | -0.06 | unavailable | 61 | Mytishino 35/10 | 1.6 | 0 | 0.06 | 0 | 1 day and night | 0.06 | 0 | 0 | -0.06 | -0.06 | unavailable
62 | Zakharyevskoe 35/10 | 1.6 | 0.04 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.81 | 0.81 | available | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.04 | 0.85 | 1 day and night | -0.81 | 0 | 0.85 | 0.81 | 0.81 | available
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.8 | 0.8 | available | 63 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 1 day and night | -0.8 | 0 | 0.85 | 0.8 | 0.8 | available
64 | Baskakovka 35/10 | 4 | 0.24 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.49 | 1.49 | available | 64 | Baskakovka 35/10 | 4 | 0 | 0.24 | 1.73 | 1 day and night | -1.49 | 0 | 1.73 | 1.49 | 1.49 | available
65 | Ekimtsevo 110/10 | 2.5 | 0.25 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.48 | 1.48 | available | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0.25 | 1.73 | 1 day and night | -1.48 | 0 | 1.73 | 1.48 | 1.48 | available
Two-transformer substations | [11 empty] | 1: Two-transformer substations
66 | Смоленск 1 (ФСК) 110/35/6 | 40+40 | 35.1 | 4.35 | 120 | 30.75 | 0 | 42 | 11.25 | 11.25 | available | 66 | Смоленск 1 (ФСК) 110/35/6 | 40+40 | 24.29 | 59.39 | 10.83 | 120 | 48.56 | 0 | 42 | -6.56 | -6.56 | unavailable
| Ном. Мощность СН, МВА | 40+40 | 2.43 | 2.43 |  | 0 | 0 | 42 | 42 |  |  |  | Ном. Мощность СН, МВА | 40+40 | 6.48 | 8.91 | 8.91 |  | 0 | 0 | 42 | 42
| Ном. мощность НН, МВА | 40+40 | 32.67 | 1.92 | 120 | 30.75 | 0 | 42 | 11.25 |  |  |  | Ном. мощность НН, МВА | 40+40 | 17.81 | 50.48 | 1.92 | 120 | 48.56 | 0 | 42 | -6.56
67 | Water intake 35/6 | 4+4 | 2.18 | 1.2 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | available | 67 | Water intake 35/6 | 4+4 | 3.21 | 5.39 | 1.2 | 120 | 4.19 | 0 | 4.2 | 0.01 | 0.01 | available
68 | Tychinino 35/10 | 4+4 | 1.06 | 0.91 | 120 | 0.15 | 0 | 4.2 | 4.05 | 4.05 | available | 68 | Tychinino 35/10 | 4+4 | 0.41 | 1.47 | 0.91 | 120 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | available
69 | Ryabtsevo 35/10 | 4+4 | 3.29 | 0 | 120 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | available | 69 | Ryabtsevo 35/10 | 4+4 | 2.7 | 5.99 | 0 | 120 | 5.99 | 0 | 4.2 | -1.79 | -1.79 | unavailable
70 | Smolensk 2 110/6 | 40+40 | 18.45 | 6.41 | 120 | 12.04 | 0 | 42 | 29.96 | 29.96 | available | 70 | Smolensk 2 110/6 | 40+40 | 7.53 | 25.98 | 6.41 | 120 | 19.57 | 0 | 42 | 22.43 | 22.43 | available
71 | Vostochnaya 110/6 | 25+16 | 8.22 | 0 | 120 | 8.22 | 0 | 16.8 | 8.58 | 8.58 | available | 71 | Vostochnaya 110/6 | 25+16 | 9.56 | 17.78 | 0 | 120 | 17.78 | 0 | 16.8 | -0.98 | -0.98 | unavailable
72 | Diffuzion 110/6 | 25+25 | 14.7 | 1.06 | 120 | 13.64 | 0 | 26.25 | 12.61 | 12.61 | available | 72 | Diffuzion 110/6 | 25+25 | 22.28 | 36.98 | 1.06 | 120 | 35.92 | 0 | 26.25 | -9.67 | -9.67 | unavailable
73 | Zavodskaya 110/35/10 | 16+16 | 10.63 | 9.34 | 120 | 1.29 | 0 | 16.8 | 15.51 | 13.11 | available | 73 | Zavodskaya 110/35/10 | 16+16 | 16.75 | 27.38 | 12.015 | 120 | 15.365 | 0 | 16.8 | 1.435 | 1.435 | available
| Nom. capacity MV, МVА | 16+16 | 7.38 | 3.69 |  | 3.69 | 0 | 16.8 | 13.11 |  |  |  | Nom. capacity MV, МVА | 16+16 | 5.35 | 12.73 | 6.365 |  | 6.365 | 0 | 16.8 | 10.435
| Nom. capacity LV, МVА | 16+16 | 3.25 | 5.65 | 120 | -2.4 | 0 | 16.8 | 19.2 |  |  |  | Nom. capacity LV, МVА | 16+16 | 11.4 | 14.65 | 5.65 | 120 | 9 | 0 | 16.8 | 7.8
74 | Yasennaya 35/6 | 10+10 | 8.82 | 0 | 120 | 8.82 | 0 | 10.5 | 1.68 | 1.68 | available | 74 | Yasennaya 35/6 | 10+10 | 1.54 | 10.36 | 0 | 120 | 10.36 | 0 | 10.5 | 0.14 | 0.14 | available
75 | Gnezodovo 35/6 | 7,5+7,5 | 5.89 | 0.42 | 120 | 5.47 | 0 | 7.875 | 2.405 | 2.405 | available | 75 | Gnezodovo 35/6 | 7,5+7,5 | 3.79 | 9.68 | 0.42 | 120 | 9.26 | 0 | 7.875 | -1.385 | -1.385 | unavailable
76 | Zapadnaya 110/6 | 25+16 | 13.4 | 0.63 | 120 | 12.77 | 0 | 16.8 | 4.03 | 4.03 | available | 76 | Zapadnaya 110/6 | 25+16 | 9.58 | 22.98 | 0.63 | 120 | 22.35 | 0 | 16.8 | -5.55 | -5.55 | unavailable
77 | Katyn 2 110/35/10 | 10+16 | 3.69 | 1.44 | 120 | 2.25 | 0 | 10.5 | 8.25 | 8.25 | available | 77 | Katyn 2 110/35/10 | 10+16 | 10.57 | 14.26 | 6.79 | 120 | 7.47 | 0 | 10.5 | 3.03 | 3.03 | available
| Nom. capacity MV, МVА | 10+16 | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 5.35 | 6.79 | 6.79 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.25 | 0 | 120 | 2.25 | 0 | 10.5 | 8.25 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.22 | 7.47 | 0 | 120 | 7.47 | 0 | 10.5 | 3.03
78 | Katyn 1 35/10 | 4+4 | 1.69 | 0.05 | 120 | 1.64 | 0 | 4.2 | 2.56 | 2.56 | available | 78 | Katyn 1 35/10 | 4+4 | 1.46 | 3.15 | 0.05 | 120 | 3.1 | 0 | 4.2 | 1.1 | 1.1 | available
79 | Lubnya 35/10 | 4+4 | 1.2 | 0.13 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 | available | 79 | Lubnya 35/10 | 4+4 | 3.03 | 4.23 | 0.13 | 120 | 4.1 | 0 | 4.2 | 0.1 | 0.1 | available
80 | Kozino 110/35/10 | 10+10 | 10.41 | 6.5 | 120 | 3.91 | 0 | 10.5 | 6.59 | 6.59 | available | 80 | Kozino 110/35/10 | 10+10 | 16.2 | 26.61 | 2.24 | 120 | 24.37 | 0 | 10.5 | -13.87 | -13.87 | unavailable
| Nom. capacity MV, МVА | 10+10 | 6.49 | 6.49 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 10.71 | 17.2 | 2.23 |  | 14.97 | 0 | 10.5 | -4.47
| Nom. capacity LV, МVА | 10+10 | 3.92 | 0.01 | 120 | 3.91 | 0 | 10.5 | 6.59 |  |  |  | Nom. capacity LV, МVА | 10+10 | 5.49 | 9.41 | 0.01 | 120 | 9.4 | 0 | 10.5 | 1.1
81 | Odintsovo 35/10 | 6,3+6,3 | 5.97 | 2.15 | 120 | 3.82 | 0 | 6.615 | 2.795 | 2.795 | available | 81 | Odintsovo 35/10 | 6,3+6,3 | 9 | 14.97 | 2.15 | 120 | 12.82 | 0 | 6.615 | -6.205 | -6.205 | unavailable
82 | Trudilovo 35/10 | 2,5+2,5 | 1.1 | 0.08 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | available | 82 | Trudilovo 35/10 | 2,5+2,5 | 1.22 | 2.32 | 0.08 | 120 | 2.24 | 0 | 2.625 | 0.385 | 0.385 | available
83 | KS-3 SSNo.2 110/10 | 40+40 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | available | 83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | available
84 | Pronino 110/35/6 | 10+10 | 6.31 | 4.62 | 120 | 1.69 | 0 | 10.5 | 8.81 | 8.81 | available | 84 | Pronino 110/35/6 | 10+10 | 6.33 | 12.64 | 9.83 | 120 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | available
| Nom. capacity MV, МVА | 10+10 | 3.43 | 3.43 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 5.21 | 8.64 | 8.64 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.88 | 1.19 | 120 | 1.69 | 0 | 10.5 | 8.81 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.12 | 4 | 1.19 | 120 | 2.81 | 0 | 10.5 | 7.69
85 | Olsha 35/10 | 2,5+2,5 | 1.06 | 0 | 120 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | available | 85 | Olsha 35/10 | 2,5+2,5 | 1.03 | 2.09 | 0 | 120 | 2.09 | 0 | 2.625 | 0.535 | 0.535 | available
86 | Krasny bor 35/6 | 4+4 | 3.08 | 0 | 120 | 3.08 | 0 | 4.2 | 1.12 | 1.12 | available | 86 | Krasny bor 35/6 | 4+4 | 4.18 | 7.26 | 0 | 120 | 7.26 | 0 | 4.2 | -3.06 | -3.06 | unavailable
87 | Severnaya 110/35/6 | 25+25 | 19.98 | 10.5 | 120 | 9.48 | 0 | 26.25 | 16.77 | 16.77 | available | 87 | Severnaya 110/35/6 | 25+25 | 10.88 | 30.86 | 9.67 | 120 | 21.19 | 0 | 26.25 | 5.06 | 5.06 | available
| Nom. capacity MV, МVА | 25+25 | 7.91 | 7.91 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 7.08 | 7.08 | 7.08 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 12.07 | 2.59 | 120 | 9.48 | 0 | 26.25 | 16.77 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.8 | 15.87 | 2.59 | 120 | 13.28 | 0 | 26.25 | 12.97
88 | Peсhersk 35/6 | 4+4 | 3.32 | 0.34 | 120 | 2.98 | 0 | 4.2 | 1.22 | 1.22 | available | 88 | Peсhersk 35/6 | 4+4 | 5.06 | 8.38 | 0.34 | 120 | 8.04 | 0 | 4.2 | -3.84 | -3.84 | unavailable
89 | Kolodnya 35/6 | 6,3+4 | 3.01 | 0 | 120 | 3.01 | 0 | 4.2 | 1.19 | 1.19 | available | 89 | Kolodnya 35/6 | 6,3+4 | 2.02 | 5.03 | 0 | 120 | 5.03 | 0 | 4.2 | -0.83 | -0.83 | unavailable
90 | Tsentralnaya 110/10/6 | 25+25 | 19.2 | 7.75 | 120 | 11.45 | 0 | 26.25 | 14.8 | 14.8 | available | 90 | Tsentralnaya 110/10/6 | 25+25 | 13.15 | 32.35 | 8.43 | 120 | 23.92 | 0 | 26.25 | 2.33 | 2.33 | available
| Nom. capacity MV, МVА | 25+25 | 1.99 | 1.99 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 8.34 | 10.33 | 3 |  | 7.33 | 0 | 26.25 | 18.92
| Nom. capacity LV, МVА | 25+25 | 17.21 | 5.76 | 120 | 11.45 | 0 | 26.25 | 14.8 |  |  |  | Nom. capacity LV, МVА | 25+25 | 4.81 | 22.02 | 5.43 | 120 | 16.59 | 0 | 26.25 | 9.66
91 | Chernushki 110/10/6 | 25+25 | 20.97 | 0 | 120 | 20.97 | 0 | 26.25 | 5.28 | 5.28 | available | 91 | Chernushki 110/10/6 | 25+25 | 16.32 | 37.29 | 2.12 | 120 | 35.17 | 0 | 26.25 | -8.92 | -8.92 | unavailable
| Nom. capacity MV, МVА | 25+25 | 8.1 | 0 |  | 8.1 | 0 | 26.25 | 18.15 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.92 | 14.02 | 0 |  | 14.02 | 0 | 26.25 | 12.23
| Nom. Capacity LV, МVА | 25+25 | 12.87 | 0 | 120 | 12.87 | 0 | 26.25 | 13.38 |  |  |  | Nom. Capacity LV, МVА | 25+25 | 10.4 | 23.27 | 2.12 | 120 | 21.15 | 0 | 26.25 | 5.1
92 | Yuzhnaya 110/35/6 | 40+40 | 36.1 | 10.6 | 120 | 25.5 | 0 | 42 | 16.5 | 16.5 | available | 92 | Yuzhnaya 110/35/6 | 40+40 | 27.34 | 63.44 | 12.89 | 120 | 50.55 | 0 | 42 | -8.55 | -8.55 | unavailable
| Nom. capacity MV, МVА | 40+40 | 9.76 | 4.88 |  | 4.88 | 0 | 42 | 37.12 |  |  |  | Nom. capacity MV, МVА | 40+40 | 4.58 | 14.34 | 7.17 |  | 7.17 | 0 | 42 | 34.83
| Nom. capacity LV, МVА | 40+40 | 26.34 | 5.72 | 120 | 20.62 | 0 | 42 | 21.38 |  |  |  | Nom. capacity LV, МVА | 40+40 | 22.76 | 49.1 | 5.72 | 120 | 43.38 | 0 | 42 | -1.38
93 | Karyernaya 110/35/6 | 16+16 | 5.7 | 5.13 | 120 | 0.57 | 0 | 16.8 | 16.23 | 16.23 | available | 93 | Karyernaya 110/35/6 | 16+16 | 3.38 | 9.08 | 8.48 | 120 | 0.6 | 0 | 16.8 | 16.2 | 16.2 | available
| Nom. capacity MV, МВА | 16+16 | 5.13 | 5.13 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МВА | 16+16 | 3.35 | 8.48 | 8.48 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0.57 | 0 | 120 | 0.57 | 0 | 16.8 | 16.23 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.03 | 0.6 | 0 | 120 | 0.6 | 0 | 16.8 | 16.2
94 | Koshchino 35/10 | 4+4 | 0.55 | 0.11 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | available | 94 | Koshchino 35/10 | 4+4 | 0.22 | 0.77 | 0.11 | 120 | 0.66 | 0 | 4.2 | 3.54 | 3.54 | available
95 | Kommunar 35/10 | 2,5+2,5 | 0.44 | 0.03 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | available | 95 | Kommunar 35/10 | 2,5+2,5 | 0.13 | 0.57 | 0.03 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available
96 | Kasplya 110/35/10 | 10+10 | 3.6 | 3.33 | 120 | 0.27 | 0 | 10.5 | 10.23 | 10.23 | available | 96 | Kasplya 110/35/10 | 10+10 | 7.43 | 11.03 | 10.47 | 120 | 0.56 | 0 | 10.5 | 9.94 | 9.94 | available
| Nom. capacity MV, МVА | 10+10 | 2.47 | 2.47 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 7.14 | 9.61 | 9.61 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.13 | 0.86 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.29 | 1.42 | 0.86 | 120 | 0.56 | 0 | 10.5 | 9.94
97 | Apolye 35/10 | 2,5+2,5 | 0.71 | 0.17 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 97 | Apolye 35/10 | 2,5+2,5 | 0.07 | 0.78 | 0.17 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | available
98 | Zhukovskaya 35/10 | 4+4 | 2.01 | 0.19 | 120 | 1.82 | 0 | 4.2 | 2.38 | 2.38 | available | 98 | Zhukovskaya 35/10 | 4+4 | 5.82 | 7.83 | 0.19 | 120 | 7.64 | 0 | 4.2 | -3.44 | -3.44 | unavailable
99 | Mazaltsevo 110/35/10 | 10+10 | 6.01 | 5.6 | 120 | 0.41 | 0 | 10.5 | 10.09 | 10.09 | available | 99 | Mazaltsevo 110/35/10 | 10+10 | 11.03 | 17.04 | 16.53 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.99 | available
| Nom. capacity MV, МVА | 10+10 | 5.34 | 5.34 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 10.93 | 16.27 | 16.27 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.67 | 0.26 | 120 | 0.41 | 0 | 10.5 | 10.09 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.1 | 0.77 | 0.26 | 120 | 0.51 | 0 | 10.5 | 9.99
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 100 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available
101 | Krasny 110/35/10 | 10+10 | 3.52 | 1.06 | 120 | 2.46 | 0 | 10.5 | 8.04 | 8.04 | available | 101 | Krasny 110/35/10 | 10+10 | 2.09 | 5.61 | 2.27 | 120 | 3.34 | 0 | 10.5 | 7.16 | 7.16 | available
| Nom. capacity MV, МVА | 10+10 | 0.6 | 0.6 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.21 | 1.81 | 1.81 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.92 | 0.46 | 120 | 2.46 | 0 | 10.5 | 8.04 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.88 | 3.8 | 0.46 | 120 | 3.34 | 0 | 10.5 | 7.16
102 | Voloelovo 35/10 | 2,5+2,5 | 0.33 | 0.01 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available | 102 | Voloelovo 35/10 | 2,5+2,5 | 0.02 | 0.35 | 0.01 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | available | 103 | Kryukovo 35/10 | 2,5+2,5 | 0.4 | 0.52 | 0.26 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available
104 | Miganovo 35/10 | 2,5+2,5 | 1.51 | 0.49 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | available | 104 | Miganovo 35/10 | 2,5+2,5 | 1.19 | 2.7 | 0.49 | 120 | 2.21 | 0 | 2.625 | 0.415 | 0.415 | available
105 | Velizh 110/35/10 | 10+10 | 5.7 | 1.59 | 120 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | available | 105 | Velizh 110/35/10 | 10+10 | 3.36 | 9.06 | 1.78 | 120 | 7.28 | 0 | 10.5 | 3.22 | 3.22 | available
| Nom. capacity MV, МVА | 10+10 | 0.92 | 0.92 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.19 | 1.11 | 1.11 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.78 | 0.67 | 120 | 4.11 | 0 | 10.5 | 6.39 |  |  |  | Nom. capacity LV, МVА | 10+10 | 3.17 | 7.95 | 0.67 | 120 | 7.28 | 0 | 10.5 | 3.22
106 | Chepli 35/10 | 2,5+2,5 | 0.37 | 0.09 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 106 | Chepli 35/10 | 2,5+2,5 | 0.01 | 0.38 | 0.09 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available
107 | Demidov 110/35/10 | 10+16 | 5.78 | 1.47 | 120 | 4.31 | 0 | 10.5 | 6.19 | 6.19 | available | 107 | Demidov 110/35/10 | 10+16 | 2.14 | 7.92 | 1.91 | 120 | 6.01 | 0 | 10.5 | 4.49 | 4.49 | available
| Nom. capacity MV, МVА | 10+16 | 1.29 | 1.29 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.44 | 1.73 | 1.73 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.49 | 0.18 | 120 | 4.31 | 0 | 10.5 | 6.19 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.7 | 6.19 | 0.18 | 120 | 6.01 | 0 | 10.5 | 4.49
108 | Staroe selo 35/10 | 2,5+2,5 | 0.4 | 0.17 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 108 | Staroe selo 35/10 | 2,5+2,5 | 0.13 | 0.53 | 0.17 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available
109 | Zakrutye 35/10 | 2,5+2,5 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 109 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available
110 | Zaborye 35/10 | 1,6+2,5 | 0.39 | 0.21 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 110 | Zaborye 35/10 | 1,6+2,5 | 0.02 | 0.41 | 0.21 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available
111 | Mikhailovskoe 110/35/10 | 10+10 | 2.35 | 1.24 | 120 | 1.11 | 0 | 10.5 | 9.39 | 9.39 | available | 111 | Mikhailovskoe 110/35/10 | 10+10 | 0.96 | 3.31 | 1.84 | 120 | 1.47 | 0 | 10.5 | 9.03 | 9.03 | available
| Nom. capacity MV, МVА | 10+10 | 0.82 | 0.82 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.6 | 1.42 | 1.42 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.53 | 0.42 | 120 | 1.11 | 0 | 10.5 | 9.39 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.36 | 1.89 | 0.42 | 120 | 1.47 | 0 | 10.5 | 9.03
112 | Kardymovo 110/35/10 | 10+16 | 5.84 | 3.24 | 120 | 2.6 | 0 | 10.5 | 7.9 | 7.9 | available | 112 | Kardymovo 110/35/10 | 10+16 | 11.69 | 17.53 | 7.12 | 120 | 10.41 | 0 | 10.5 | 0.09 | 0.09 | available
| Nom. capacity MV, МVА | 10+16 | 2.62 | 2.62 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 3.88 | 6.5 | 6.5 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 3.22 | 0.62 | 120 | 2.6 | 0 | 10.5 | 7.9 |  |  |  | Nom. capacity LV, МVА | 10+16 | 7.81 | 11.03 | 0.62 | 120 | 10.41 | 0 | 10.5 | 0.09
113 | Sinkovo 35/6 | 4+2,5 | 1.54 | 0.16 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | available | 113 | Sinkovo 35/6 | 4+2,5 | 0.06 | 1.6 | 0.16 | 120 | 1.44 | 0 | 2.625 | 1.185 | 1.185 | available
114 | Kamenka 35/10 | 2,5+2,5 | 1.56 | 0.42 | 120 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | available | 114 | Kamenka 35/10 | 2,5+2,5 | 1.37 | 2.93 | 0.42 | 120 | 2.51 | 0 | 2.625 | 0.115 | 0.115 | available
115 | Solovyevo 35/10 | 4+4 | 0.45 | 0.04 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | available | 115 | Solovyevo 35/10 | 4+4 | 0.22 | 0.67 | 0.04 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | available
116 | Rudnya (FGC) 110/35/10 | 10+16 | 8.56 | 2.37 | 120 | 6.19 | 0 | 10.5 | 4.31 | 4.31 | available | 116 | Rudnya (FGC) 110/35/10 | 10+16 | 1.88 | 10.44 | 2.86 | 120 | 7.58 | 0 | 10.5 | 2.92 | 2.92 | available
| Nom. capacity MV, МVА | 10+16 | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.49 | 1.93 | 1.93 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.12 | 0.93 | 120 | 6.19 | 0 | 10.5 | 4.31 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.39 | 8.51 | 0.93 | 120 | 7.58 | 0 | 10.5 | 2.92
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.19 | 0.75 | 120 | -0.56 | 0 | 2.625 | 3.185 | 3.185 | available | 117 | Zhichitsy 35/10 | 2,5+2,5 | 0.05 | 0.24 | 0.75 | 120 | -0.51 | 0 | 2.625 | 3.135 | 3.135 | available
118 | Mikulino 35/10 | 6,3+6,3 | 0.98 | 1.1 | 120 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | available | 118 | Mikulino 35/10 | 6,3+6,3 | 0.18 | 1.16 | 1.1 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | available
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.62 | 0.74 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 119 | Lyubavichi 35/10 | 2,5+2,5 | 0.29 | 0.91 | 0.74 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available
120 | Kazimirovo 35/10 | 4+4 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | available | 120 | Kazimirovo 35/10 | 4+4 | 0 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | available
121 | Golynki 110/35/6 | 25+25 | 3.35 | 1.81 | 120 | 1.54 | 0 | 26.25 | 24.71 | 24.71 | available | 121 | Golynki 110/35/6 | 25+25 | 5.41 | 8.76 | 7.07 | 120 | 1.69 | 0 | 26.25 | 24.56 | 24.56 | available
| Nom. Capacity MV, МVА | 25+25 | 1.65 | 1.65 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, МVА | 25+25 | 5.26 | 6.91 | 6.91 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.7 | 0.16 | 120 | 1.54 | 0 | 26.25 | 24.71 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.15 | 1.85 | 0.16 | 120 | 1.69 | 0 | 26.25 | 24.56
122 | Belei 35/10 | 2,5+2,5 | 1.78 | 0.75 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | available | 122 | Belei 35/10 | 2,5+2,5 | 4.03 | 5.81 | 0.75 | 120 | 5.06 | 0 | 2.625 | -2.435 | -2.435 | unavailable
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.27 | 2.35 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | available | 123 | Ponizovye 110/35/10 | 6,3+6,3 | 0.3 | 3.57 | 2.65 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 2.29 | 2.29 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.3 | 2.59 | 2.59 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 124 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available
125 | Safonovo 110/6 | 15+20 | 11.46 | 0.06 | 120 | 11.4 | 0 | 15.75 | 4.35 | 4.35 | available | 125 | Safonovo 110/6 | 15+20 | 3.73 | 15.19 | 0.06 | 120 | 15.13 | 0 | 15.75 | 0.62 | 0.62 | available
126 | Gornaya 110/35/6 | 25+25 | 16.12 | 15.14 | 120 | 0.98 | 0 | 26.25 | 25.27 | 25.27 | available | 126 | Gornaya 110/35/6 | 25+25 | 5.68 | 21.8 | 19.59 | 120 | 2.21 | 0 | 26.25 | 24.04 | 24.04 | available
| Nom. capacity MV, МVА | 25+25 | 10.47 | 10.47 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.45 | 14.92 | 14.92 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 5.65 | 4.67 | 120 | 0.98 | 0 | 26.25 | 25.27 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.23 | 6.88 | 4.67 | 120 | 2.21 | 0 | 26.25 | 24.04
127 | Water intake 35/6 | 6,3+4 | 3.1 | 0.69 | 120 | 2.41 | 0 | 4.2 | 1.79 | 1.79 | available | 127 | Water intake 35/6 | 6,3+4 | 1.16 | 4.26 | 0.69 | 120 | 3.57 | 0 | 4.2 | 0.63 | 0.63 | available
128 | Vadino 35/10 | 4+4 | 1.78 | 0 | 120 | 1.78 | 0 | 4.2 | 2.42 | 2.42 | available | 128 | Vadino 35/10 | 4+4 | 2.18 | 3.96 | 0 | 120 | 3.96 | 0 | 4.2 | 0.24 | 0.24 | available
129 | ZSSK 35/6 | 4+4 | 1.81 | 0.75 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | available | 129 | ZSSK 35/6 | 4+4 | 1.03 | 2.84 | 0.75 | 120 | 2.09 | 0 | 4.2 | 2.11 | 2.11 | available
130 | Yanovo 35/10 | 4+6,3 | 0.37 | 0.05 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | available | 130 | Yanovo 35/10 | 4+6,3 | 0 | 0.37 | 0.05 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | available
131 | Kapyrevshchina 35/10 | 4+4 | 1.35 | 0.22 | 120 | 1.13 | 0 | 4.2 | 3.07 | 3.07 | available | 131 | Kapyrevshchina 35/10 | 4+4 | 0.02 | 1.37 | 0.22 | 120 | 1.15 | 0 | 4.2 | 3.05 | 3.05 | available
132 | Miropolye 35/10 | 2,5+2,5 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | available | 132 | Miropolye 35/10 | 2,5+2,5 | 0.01 | 0.68 | 0 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 4.8 | 2.63 | 120 | 2.17 | 0 | 5.88 | 3.71 | 3.71 | available | 133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.52 | 6.32 | 3.55 | 120 | 2.77 | 0 | 5.88 | 3.11 | 3.11 | available
| Nom. capacity MV, МVА | 5,6+6,3 | 2.2 | 2.2 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 0.92 | 3.12 | 3.12 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.6 | 0.43 | 120 | 2.17 | 0 | 5.88 | 3.71 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.6 | 3.2 | 0.43 | 120 | 2.77 | 0 | 5.88 | 3.11
134 | Alferovo 35/10 | 2,5+2,5 | 0.75 | 0.2 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | available | 134 | Alferovo 35/10 | 2,5+2,5 | 0.13 | 0.88 | 0.2 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available
135 | Kasulino 35/10 | 2,5+2,5 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available | 135 | Kasulino 35/10 | 2,5+2,5 | 0.06 | 0.38 | 0 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.6 | 0.15 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | available | 136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.05 | 0.65 | 0.15 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | available
137 | Glinka 110/35/10 | 10+6,3 | 2.13 | 0.56 | 120 | 1.57 | 0 | 6.615 | 5.045 | 5.045 | available | 137 | Glinka 110/35/10 | 10+6,3 | 0.45 | 2.58 | 0.99 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | available
| Nom. capacity MV, МVА | 10+6,3 | 0.45 | 0.45 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.43 | 0.88 | 0.88 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.68 | 0.11 | 120 | 1.57 | 0 | 6.615 | 5.045 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.02 | 1.7 | 0.11 | 120 | 1.59 | 0 | 6.615 | 5.025
138 | Dobromino 35/10 | 2,5+2,5 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | available | 138 | Dobromino 35/10 | 2,5+2,5 | 0.14 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | available
139 | Bely kholm 35/10 | 1,6+1,6 | 0.18 | 0 | 120 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | available | 139 | Bely kholm 35/10 | 1,6+1,6 | 0.1 | 0.28 | 0 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available
140 | Dukhovshchina 110/35/10 | 10+10 | 3.65 | 1.99 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | available | 140 | Dukhovshchina 110/35/10 | 10+10 | 2.73 | 6.38 | 3.86 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | available
| Nom. capacity MV, МVА | 10+10 | 1.73 | 1.73 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.87 | 3.6 | 3.6 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.92 | 0.26 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.86 | 2.78 | 0.26 | 120 | 2.52 | 0 | 10.5 | 7.98
141 | Zimets 35/10 | 4+4 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | available | 141 | Zimets 35/10 | 4+4 | 0 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | available
142 | Beresnevo 35/10 | 1,6+1,6 | 0.53 | 0.01 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | available | 142 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.53 | 0.01 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | available
143 | Prechistoe 110/35/10 | 6,3+6,3 | 2.02 | 0.14 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | available | 143 | Prechistoe 110/35/10 | 6,3+6,3 | 0.56 | 2.58 | 0.14 | 120 | 2.44 | 0 | 6.615 | 4.175 | 4.175 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 1.5 | 0 |  | 1.5 | 0 | 6.615 | 5.115 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.35 | 1.85 | 0 |  | 1.85 | 0 | 6.615 | 4.765
| Nom. capacity LV, МVА | 6,3+6,3 | 0.52 | 0.14 | 120 | 0.38 | 0 | 6.615 | 6.235 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.21 | 0.73 | 0.14 | 120 | 0.59 | 0 | 6.615 | 6.025
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.24 | 0.07 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 144 | Vorontsovo 35/10 | 2,5+2,5 | 0.05 | 0.29 | 0.07 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available
145 | Ozyorny 35/10 | 6,3+6,3 | 1.58 | 0.01 | 120 | 1.57 | 0 | 6.615 | 5.045 | 5.045 | available | 145 | Ozyorny 35/10 | 6,3+6,3 | 0.24 | 1.82 | 0.01 | 120 | 1.81 | 0 | 6.615 | 4.805 | 4.805 | available
146 | Igorevskaya 110/10 | 10+10 | 7.93 | 0 | 120 | 7.93 | 0 | 10.5 | 2.57 | 2.57 | available | 146 | Igorevskaya 110/10 | 10+10 | 0.24 | 8.17 | 0 | 120 | 8.17 | 0 | 10.5 | 2.33 | 2.33 | available
147 | Kanyutino 110/35/10 | 5,6+6,3 | 3.4 | 1.68 | 120 | 1.72 | 0 | 5.88 | 4.16 | 4.16 | available | 147 | Kanyutino 110/35/10 | 5,6+6,3 | 1.74 | 5.14 | 4.94 | 120 | 0.2 | 0 | 5.88 | 5.68 | 5.68 | available
| Nom. capacity LV, МVА | 5,6+6,3 | 2.99 | 2.99 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 1.74 | 4.73 | 4.73 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.11 | 0.25 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | available | 148 | Bogolyubovo 35/10 | 2,5+2,5 | 0.12 | 1.23 | 0.25 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | available
149 | Kholm-Zhirki 35/10 | 2,5+4 | 2.73 | 0.5 | 120 | 2.23 | 0 | 2.625 | 0.395 | 0.395 | available | 149 | Kholm-Zhirki 35/10 | 2,5+4 | 1.4 | 4.13 | 0.5 | 120 | 3.63 | 0 | 2.625 | -1.005 | -1.005 | unavailable
150 | Dorogobuzh 1 110/35/10 | 16+16 | 10.38 | 4.87 | 120 | 5.51 | 0 | 16.8 | 11.29 | 11.29 | available | 150 | Dorogobuzh 1 110/35/10 | 16+16 | 2.69 | 13.07 | 6.09 | 120 | 6.98 | 0 | 16.8 | 9.82 | 9.82 | available
| Nom. capacity MV, МVА | 16+16 | 4.35 | 4.35 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.22 | 5.57 | 5.57 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 6.03 | 0.52 | 120 | 5.51 | 0 | 16.8 | 11.29 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.47 | 7.5 | 0.52 | 120 | 6.98 | 0 | 16.8 | 9.82
151 | Kaskovo 35/10 | 1,6+4 | 0.84 | 0.09 | 120 | 0.75 | 0 | 1.68 | 0.93 | 0.93 | available | 151 | Kaskovo 35/10 | 1,6+4 | 0.18 | 1.02 | 0.09 | 120 | 0.93 | 0 | 1.68 | 0.75 | 0.75 | available
152 | Usvyatye 35/10 | 2,5+4 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 152 | Usvyatye 35/10 | 2,5+4 | 0.68 | 1.47 | 0 | 120 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | available
153 | Ushakovo 35/10 | 1,6+2,5 | 0.84 | 0 | 120 | 0.84 | 0 | 1.68 | 0.84 | 0.84 | available | 153 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.84 | 0 | 120 | 0.84 | 0 | 1.68 | 0.84 | 0.84 | available
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | available | 154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | available
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | available | 155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | available
156 | Elnya 110/35/10 | 16+16 | 4.43 | 2.7 | 120 | 1.73 | 0 | 16.8 | 15.07 | 15.07 | available | 156 | Elnya 110/35/10 | 16+16 | 0.53 | 4.96 | 2.88 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | available
| Nom. capacity MV, МVА | 16+16 | 2.16 | 2.16 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.18 | 2.34 | 2.34 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.27 | 0.54 | 10 | 1.73 | 0 | 16.8 | 15.07 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.35 | 2.62 | 0.54 | 120 | 2.08 | 0 | 16.8 | 14.72
157 | Pavlovo 35/10 | 2,5+2,5 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 157 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available
158 | Sharapovo 35/10 | 4+4 | 0.48 | 1 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | available | 158 | Sharapovo 35/10 | 4+4 | 0 | 0.48 | 1 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | available
159 | Korobets 35/10 | 2,5+2,5 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | available | 159 | Korobets 35/10 | 2,5+2,5 | 0 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | available
160 | Baltutino 35/10 | 2,5+2,5 | 0.54 | 0 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 160 | Baltutino 35/10 | 2,5+2,5 | 0.15 | 0.69 | 0 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | available
161 | Lapino 110/35/10 | 5,6+5,6 | 1.13 | 0.72 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | available | 161 | Lapino 110/35/10 | 5,6+5,6 | 0.02 | 1.15 | 0.74 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | available
| Nom. capacity MV, МVА | 5,6+5,6 | 0.72 | 0.72 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0.02 | 0.74 | 0.74 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47
162 | Mutishche 35/10 | 1,6+2,5 | 0.14 | 0.08 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | available | 162 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.14 | 0.08 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | available
163 | Suetovo 110/35/10 | 6,3+6,3 | 3.12 | 2.33 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | available | 163 | Suetovo 110/35/10 | 6,3+6,3 | 1.32 | 4.44 | 3.41 | 120 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 1.75 | 1.75 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1.08 | 2.83 | 2.83 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.37 | 0.58 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.61 | 0.58 | 120 | 1.03 | 0 | 6.615 | 5.585
164 | Pushkino 35/10 | 2,5+2,5 | 0.97 | 0.04 | 120 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | available | 164 | Pushkino 35/10 | 2,5+2,5 | 1.08 | 2.05 | 0.04 | 120 | 2.01 | 0 | 2.625 | 0.615 | 0.615 | available
165 | Yartsevo 1 110/10 | 40+40 | 17.99 | 5.34 | 120 | 12.65 | 0 | 42 | 29.35 | 29.35 | available | 165 | Yartsevo 1 110/10 | 40+40 | 3.02 | 21.01 | 5.34 | 120 | 15.67 | 0 | 42 | 26.33 | 26.33 | available
166 | Yartsevo 2 110/10 | 16+16 | 12.7 | 0.75 | 120 | 11.95 | 0 | 16.8 | 4.85 | 4.85 | available | 166 | Yartsevo 2 110/10 | 16+16 | 10.59 | 23.29 | 0.75 | 120 | 22.54 | 0 | 16.8 | -5.74 | -5.74 | unavailable
167 | Saprykino 110/35/10 | 6,3+6,3 | 1.72 | 0.87 | 120 | 0.85 | 0 | 6.615 | 5.765 | 5.765 | available | 167 | Saprykino 110/35/10 | 6,3+6,3 | 0.33 | 2.05 | 0.87 | 120 | 1.18 | 0 | 6.615 | 5.435 | 5.435 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.25 | 0.4 | 120 | 0.85 | 0 | 6.615 | 5.765 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.33 | 1.58 | 0.4 | 120 | 1.18 | 0 | 6.615 | 5.435
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.87 | 0 | 120 | 2.87 | 0 | 6.615 | 3.745 | 3.745 | available | 168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.79 | 3.66 | 0 | 120 | 3.66 | 0 | 6.615 | 2.955 | 2.955 | available
169 | Egoryevo 35/10 | 6,3+6,3 | 5.39 | 0 | 120 | 5.39 | 0 | 6.615 | 1.225 | 1.225 | available | 169 | Egoryevo 35/10 | 6,3+6,3 | 0.92 | 6.31 | 0 | 120 | 6.31 | 0 | 6.615 | 0.305 | 0.305 | available
170 | Shalomino 35/10 | 1,6+2,5 | 0.65 | 0.13 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | available | 170 | Shalomino 35/10 | 1,6+2,5 | 0.02 | 0.67 | 0.13 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available
171 | Roslavl 110/35/6 | 25+40 | 24.09 | 1.4 | 120 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | available | 171 | Roslavl 110/35/6 | 25+40 | 4.63 | 28.72 | 3.91 | 120 | 24.81 | 0 | 26.25 | 1.44 | 1.44 | available
| Nom. capacity MV, МVА | 25+40 | 11.48 | 1.4 |  | 10.08 | 0 | 26.25 | 16.17 |  |  |  | Nom. capacity MV, МVА | 25+40 | 2.11 | 13.59 | 3.91 |  | 9.68 | 0 | 26.25 | 16.57
| Nom. сapacity LV, МVА | 25+40 | 12.61 | 0 | 120 | 12.61 | 0 | 26.25 | 13.64 |  |  |  | Nom. сapacity LV, МVА | 25+40 | 2.52 | 15.13 | 0 | 120 | 15.13 | 0 | 26.25 | 11.12
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.69 | 0 | 120 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | available | 172 | Meet processing plant 35/6 | 6,3+6,3 | 0.11 | 1.8 | 0 | 120 | 1.8 | 0 | 6.615 | 4.815 | 4.815 | available
173 | Perenka 35/10 | 4+4 | 0.4 | 0 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | available | 173 | Perenka 35/10 | 4+4 | 0.01 | 0.41 | 0 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | available
174 | Khoroshevo 35/10 | 2,5+4 | 1.03 | 0 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | available | 174 | Khoroshevo 35/10 | 2,5+4 | 0.35 | 1.38 | 0 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | available
175 | Lipovka 35/10 | 2,5+2,5 | 0.43 | 0 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | available | 175 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.43 | 0 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | available
176 | Kirilly 35/10 | 2,5+2,5 | 0.76 | 0 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available | 176 | Kirilly 35/10 | 2,5+2,5 | 1.34 | 2.1 | 0 | 120 | 2.1 | 0 | 2.625 | 0.525 | 0.525 | available
177 | Desnogorsk 110/35/10 | 25+25 | 18.65 | 5.42 | 120 | 13.23 | 0 | 26.25 | 13.02 | 13.02 | available | 177 | Desnogorsk 110/35/10 | 25+25 | 1.79 | 20.44 | 3.16 | 120 | 17.28 | 0 | 26.25 | 8.97 | 8.97 | available
| Nom. capacity MV, МVА | 25+25 | 5.42 | 5.42 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 1.78 | 7.2 | 3.16 |  | 4.04 | 0 | 26.25 | 22.21
| Nom. capacidty LV, МVА | 25+25 | 13.23 | 0 | 120 | 13.23 | 0 | 26.25 | 13.02 |  |  |  | Nom. capacidty LV, МVА | 25+25 | 0.01 | 13.24 | 0 | 120 | 13.24 | 0 | 26.25 | 13.01
178 | Ekimovichi 35/10 | 4+4 | 2.3 | 0.24 | 120 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | available | 178 | Ekimovichi 35/10 | 4+4 | 0.32 | 2.62 | 0.24 | 120 | 2.38 | 0 | 4.2 | 1.82 | 1.82 | available
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.21 | 0.07 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 179 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.21 | 0.07 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available
180 | Kokhany 35/10 | 1,6+1,6 | 0.35 | 0.09 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 180 | Kokhany 35/10 | 1,6+1,6 | 0.09 | 0.44 | 0.09 | 120 | 0.35 | 0 | 1.68 | 1.33 | 1.33 | available
181 | Koski 35/10 | 4+4 | 0.39 | 0 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | available | 181 | Koski 35/10 | 4+4 | 0.03 | 0.42 | 0 | 120 | 0.42 | 0 | 4.2 | 3.78 | 3.78 | available
182 | Industrialnaya 110/35/6 | 16+16 | 4.62 | 1.33 | 120 | 3.29 | 0 | 16.8 | 13.51 | 5.565 | available | 182 | Industrialnaya 110/35/6 | 16+16 | 2.08 | 6.7 | 1.43 | 120 | 5.27 | 0 | 16.8 | 11.53 | 5.565 | available
| Nom. capacity MV, МVА | 16,3+5,3 | 1.33 | 1.33 |  | 0 | 0 | 5.565 | 5.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0.1 | 1.43 | 1.43 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 3.29 | 0 | 120 | 3.29 | 0 | 11.235 | 7.945 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 1.98 | 5.27 | 0 | 120 | 5.27 | 0 | 11.235 | 5.965
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.83 | 0 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | available | 183 | Astapkovichi 35/10 | 2,5+2,5 | 0.07 | 0.9 | 0 | 120 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | available
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.14 | 0.86 | 120 | 0.28 | 0 | 6.615 | 6.335 | 6.335 | available | 184 | Barsuki 110/35/10 | 6,3+6,3 | 0.046 | 1.186 | 1.02 | 120 | 0.166 | 0 | 6.615 | 6.449 | 6.335 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 0.86 | 0.86 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.16 | 1.02 | 1.02 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335
185 | Bogdanovo 35/10 | 4+4 | 0.26 | 0 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | available | 185 | Bogdanovo 35/10 | 4+4 | 0.02 | 0.28 | 0 | 120 | 0.28 | 0 | 4.2 | 3.92 | 3.92 | available
186 | Prigorye 110/35/10 | 10+2,5 | 0.94 | 0.66 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 186 | Prigorye 110/35/10 | 10+2,5 | 0.01 | 0.95 | 0.67 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available
| Nom. capacity MV, МVА | 10+2,5 | 0.66 | 0.66 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0.01 | 0.67 | 0.67 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 |  |  |  | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345
187 | Bekhovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 187 | Bekhovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available
188 | Pochinok 110/35/10 | 10+16 | 9.02 | 3.12 | 120 | 5.9 | 0 | 10.5 | 4.6 | 4.6 | available | 188 | Pochinok 110/35/10 | 10+16 | 2.23 | 11.25 | 3.88 | 120 | 7.37 | 0 | 10.5 | 3.13 | 3.13 | available
| Nom. capacidty MV, МVА | 10+16 | 3.04 | 3.04 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacidty MV, МVА | 10+16 | 0.76 | 3.8 | 3.8 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.98 | 0.08 | 120 | 5.9 | 0 | 10.5 | 4.6 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.47 | 7.45 | 0.08 | 120 | 7.37 | 0 | 10.5 | 3.13
189 | Divinskaya 35/10 | 4+4 | 1.19 | 0.17 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | available | 189 | Divinskaya 35/10 | 4+4 | 0.04 | 1.23 | 0.17 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | available
190 | Shatalovo 35/10 | 2,5+2,5 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | available | 190 | Shatalovo 35/10 | 2,5+2,5 | 0 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | available
191 | Panskaya 35/10 | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | available | 191 | Panskaya 35/10 | 6,3+6,3 | 0.69 | 2.05 | 0 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | available
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.41 | 1.82 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | available | 192 | Stodolishche 110/35/10 | 6,3+6,3 | 2.78 | 6.19 | 2.3 | 120 | 3.89 | 0 | 6.615 | 2.725 | 2.725 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 1.37 | 1.37 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.48 | 1.85 | 1.85 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.04 | 0.45 | 120 | 1.59 | 0 | 6.615 | 5.025 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.3 | 4.34 | 0.45 | 120 | 3.89 | 0 | 6.615 | 2.725
193 | Belik 35/10 | 2,5+2,5 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | available | 193 | Belik 35/10 | 2,5+2,5 | 0 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | available
194 | Pervomayskaya 35/10 | 4+4 | 1.52 | 0 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | available | 194 | Pervomayskaya 35/10 | 4+4 | 0.07 | 1.59 | 0 | 120 | 1.59 | 0 | 4.2 | 2.61 | 2.61 | available
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.85 | 2.07 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.355 | available | 195 | Vaskovo 110/35/10 | 6,3+6,3 | 0.77 | 2.62 | 2.32 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.315 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 1.38 | 1.38 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.73 | 2.11 | 2.11 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.47 | 0.21 | 120 | 0.26 | 0 | 6.615 | 6.355 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.04 | 0.51 | 0.21 | 120 | 0.3 | 0 | 6.615 | 6.315
196 | Strigino 35/10 | 2,5+2,5 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 196 | Strigino 35/10 | 2,5+2,5 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available
197 | Komintern 35/10 | 2,5+2,5 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available | 197 | Komintern 35/10 | 2,5+2,5 | 0 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available
198 | Monastyrshchina 110/35/10 | 10+10 | 6.21 | 1.77 | 120 | 4.44 | 0 | 10.5 | 6.06 | 6.06 | available | 198 | Monastyrshchina 110/35/10 | 10+10 | 0.22 | 6.43 | 1.87 | 120 | 4.56 | 0 | 10.5 | 5.94 | 5.94 | available
| Nom. capacity MV, МVА | 10+10 | 1.77 | 1.77 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.1 | 1.87 | 1.87 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.44 | 0 | 120 | 4.44 | 0 | 10.5 | 6.06 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.12 | 4.56 | 0 | 120 | 4.56 | 0 | 10.5 | 5.94
199 | N.Mikhailov 35/10 | 4+4 | 0.57 | 0 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available | 199 | N.Mikhailov 35/10 | 4+4 | 0 | 0.57 | 0 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available
200 | Tatarsk 35/10 | 3,2+4 | 0.94 | 0 | 120 | 0.94 | 0 | 3.36 | 2.42 | 2.42 | available | 200 | Tatarsk 35/10 | 3,2+4 | 0.07 | 1.01 | 0 | 120 | 1.01 | 0 | 3.36 | 2.35 | 2.35 | available
201 | Turki 35/10 | 1,6+1,6 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | available | 201 | Turki 35/10 | 1,6+1,6 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | available
202 | Sozh 35/10 | 4+4 | 0.4 | 0 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | available | 202 | Sozh 35/10 | 4+4 | 0.02 | 0.42 | 0 | 120 | 0.42 | 0 | 4.2 | 3.78 | 3.78 | available
203 | Khislavichi 110/35/10 | 16+16 | 3.95 | 1.62 | 120 | 2.33 | 0 | 16.8 | 14.47 | 14.47 | available | 203 | Khislavichi 110/35/10 | 16+16 | 0.89 | 4.84 | 1.88 | 120 | 2.96 | 0 | 16.8 | 13.84 | 13.84 | available
| Nom. capacity MV, МVА | 16+16 | 1.44 | 1.44 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.26 | 1.7 | 1.7 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.51 | 0.18 | 120 | 2.33 | 0 | 16.8 | 14.47 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.63 | 3.14 | 0.18 | 120 | 2.96 | 0 | 16.8 | 13.84
204 | Gorodishche 35/10 | 1,8+2,5 | 0.73 | 0 | 120 | 0.73 | 0 | 1.89 | 1.16 | 1.16 | available | 204 | Gorodishche 35/10 | 1,8+2,5 | 0.08 | 0.81 | 0 | 120 | 0.81 | 0 | 1.89 | 1.08 | 1.08 | available
205 | Komarovka 35/10 | 4+4 | 0.15 | 0.02 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | available | 205 | Komarovka 35/10 | 4+4 | 0.09 | 0.24 | 0.02 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | available
206 | Cherepovo 35/10 | 2,5+2,5 | 0.26 | 0 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available | 206 | Cherepovo 35/10 | 2,5+2,5 | 0.05 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available
207 | Studenets 35/10 | 1,6+2,5 | 0.29 | 0.01 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 207 | Studenets 35/10 | 1,6+2,5 | 0 | 0.29 | 0.01 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available
208 | Shumyachi 110/35/10 | 10+10 | 4.78 | 2.84 | 120 | 1.94 | 0 | 10.5 | 8.56 | 8.56 | available | 208 | Shumyachi 110/35/10 | 10+10 | 0.88 | 5.66 | 3.36 | 120 | 2.3 | 0 | 10.5 | 8.2 | 8.2 | available
| Nom. capacity MV, МVА | 10+10 | 2.2 | 2.2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.52 | 2.72 | 2.72 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.58 | 0.64 | 120 | 1.94 | 0 | 10.5 | 8.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.36 | 2.94 | 0.64 | 120 | 2.3 | 0 | 10.5 | 8.2
209 | Ershichi 110/35/10 | 10+10 | 2.26 | 0.42 | 120 | 1.84 | 0 | 10.5 | 8.66 | 8.66 | available | 209 | Ershichi 110/35/10 | 10+10 | 0.6 | 2.86 | 0.42 | 120 | 2.44 | 0 | 10.5 | 8.06 | 8.06 | available
| Nom. capacity MV, МVА | 10+10 | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.06 | 0.22 | 120 | 1.84 | 0 | 10.5 | 8.66 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.6 | 2.66 | 0.22 | 120 | 2.44 | 0 | 10.5 | 8.06
210 | Rukhan 35/10 | 2,5+2,5 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available | 210 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available
211 | Vyazma 1 110/35/10 | 40+40 | 41.71 | 2.515 | 120 | 39.195 | 0 | 42 | 2.805 | 2.805 | available | 211 | Vyazma 1 110/35/10 | 40+40 | 22.58 | 64.29 | 5.5 | 120 | 58.79 | 0 | 42 | -16.79 | -16.79 | unavailable
| Nom. capacity MV, МVА | 40+40 | 26.3 | 1.955 | 121 | 24.345 | 0 | 42 | 17.655 |  |  |  | Nom. capacity MV, МVА | 40+40 | 11.99 | 38.29 | 4.94 |  | 33.35 | 0 | 42 | 8.65
| Nom. capacity LV, МVА | 40+40 | 15.41 | 0.56 | 122 | 14.85 | 0 | 42 | 27.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 10.59 | 26 | 0.56 | 120 | 25.44 | 0 | 42 | 16.56
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.38 | 0 | 120 | 2.38 | 0 | 6.615 | 4.235 | 4.235 | available | 212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 0.94 | 3.32 | 0 | 120 | 3.32 | 0 | 6.615 | 3.295 | 3.295 | available
213 | Khmelita 35/10 | 1,6+2,5 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | available | 213 | Khmelita 35/10 | 1,6+2,5 | 0.35 | 0.73 | 0.11 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | available
214 | Isakovo 35/10 | 2,5+4 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 214 | Isakovo 35/10 | 2,5+4 | 0.01 | 0.59 | 0.3 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available
215 | Rizskoe 35/10 | 2,5+2,5 | 0.73 | 0.01 | 120 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | available | 215 | Rizskoe 35/10 | 2,5+2,5 | 0.2 | 0.93 | 0.01 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | available
216 | Beryozka 35/10 | 4+4 | 0.97 | 0 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | available | 216 | Beryozka 35/10 | 4+4 | 0.69 | 1.66 | 0 | 120 | 1.66 | 0 | 4.2 | 2.54 | 2.54 | available
217 | Shimanovo 35/10 | 1,8+4 | 0.47 | 0.32 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | available | 217 | Shimanovo 35/10 | 1,8+4 | 0.1 | 0.57 | 0.32 | 120 | 0.25 | 0 | 1.89 | 1.64 | 1.64 | available
218 | Kaydakovo 35/10 | 4+4 | 1.04 | 0.2 | 120 | 0.84 | 0 | 4.2 | 3.36 | 3.36 | available | 218 | Kaydakovo 35/10 | 4+4 | 0.35 | 1.39 | 0.2 | 120 | 1.19 | 0 | 4.2 | 3.01 | 3.01 | available
219 | Flour mill 35/10 | 10+10 | 7.89 | 0.13 | 120 | 7.76 | 0 | 10.5 | 2.74 | 2.74 | available | 219 | Flour mill 35/10 | 10+10 | 9.23 | 17.12 | 0.13 | 120 | 16.99 | 0 | 10.5 | -6.49 | -6.49 | unavailable
220 | Kikino 35/10 | 2,5+2,5 | 0.56 | 0.41 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 220 | Kikino 35/10 | 2,5+2,5 | 0.13 | 0.69 | 0.41 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available
221 | Vyazma 2 110/10 | 16+16 | 15.6 | 0 | 120 | 15.6 | 0 | 16.8 | 1.2 | 1.2 | available | 221 | Vyazma 2 110/10 | 16+16 | 6.89 | 22.49 | 0 | 120 | 22.49 | 0 | 16.8 | -5.69 | -5.69 | unavailable
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.19 | 1.22 | 120 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | available | 222 | Tumanovo 110/35/10 | 6,3+6,3 | 0.3 | 2.49 | 1.38 | 120 | 1.11 | 0 | 6.615 | 5.505 | 5.505 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 0.88 | 0.88 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.16 | 1.04 | 1.04 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.31 | 0.34 | 120 | 0.97 | 0 | 6.615 | 5.645 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.14 | 1.45 | 0.34 | 120 | 1.11 | 0 | 6.615 | 5.505
223 | Rossiya 110/35/10 | 10+16 | 2.38 | 1.82 | 120 | 0.56 | 0 | 10.5 | 9.94 | 9.94 | available | 223 | Rossiya 110/35/10 | 10+16 | 1.65 | 4.03 | 3.45 | 120 | 0.58 | 0 | 10.5 | 9.92 | 9.92 | available
| Nom. capacity MV, МVА | 10+16 | 1.5 | 1.5 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 1.63 | 3.13 | 3.13 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 0.88 | 0.32 | 120 | 0.56 | 0 | 10.5 | 9.94 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.02 | 0.9 | 0.32 | 120 | 0.58 | 0 | 10.5 | 9.92
224 | Semlevo 35/10 | 2,5+4 | 0.87 | 0 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | available | 224 | Semlevo 35/10 | 2,5+4 | 0.71 | 1.58 | 0 | 120 | 1.58 | 0 | 2.625 | 1.045 | 1.045 | available
225 | Artyomovo 35/10 | 2,5+2,5 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | available | 225 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | available
226 | Gagarin 110/35/10 | 25+25 | 23.41 | 4.78 | 120 | 18.63 | 0 | 26.25 | 7.62 | 7.62 | available | 226 | Gagarin 110/35/10 | 25+25 | 14.59 | 38 | 6.82 | 120 | 31.18 | 0 | 26.25 | -4.93 | -4.93 | unavailable
| Nom. capacity MV, МVА | 25+25 | 8.21 | 3.06 |  | 5.15 | 0 | 26.25 | 21.1 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.88 | 14.09 | 5.1 |  | 8.99 | 0 | 26.25 | 17.26
| Nom. capacity LV, МVА | 25+25 | 15.2 | 1.72 | 120 | 13.48 | 0 | 26.25 | 12.77 |  |  |  | Nom. capacity LV, МVА | 25+25 | 8.71 | 23.91 | 1.72 | 120 | 22.19 | 0 | 26.25 | 4.06
227 | Rodomanovo 35/10 | 4+4 | 0.91 | 1.18 | 120 | -0.27 | 0 | 4.2 | 4.47 | 4.47 | available | 227 | Rodomanovo 35/10 | 4+4 | 2.41 | 3.32 | 1.18 | 120 | 2.14 | 0 | 4.2 | 2.06 | 2.06 | available
228 | Klushino 35/10 | 4+4 | 0.78 | 0.57 | 120 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | available | 228 | Klushino 35/10 | 4+4 | 0.46 | 1.24 | 0.57 | 120 | 0.67 | 0 | 4.2 | 3.53 | 3.53 | available
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 229 | Ivino 35/10 | 1,6+1,6 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available
230 | Karmanovo 35/10 | 4+4 | 3.56 | 0.21 | 120 | 3.35 | 0 | 4.2 | 0.85 | 0.85 | available | 230 | Karmanovo 35/10 | 4+4 | 1.42 | 4.98 | 0.21 | 120 | 4.77 | 0 | 4.2 | -0.57 | -0.57 | unavailable
231 | Sverchkovo 35/10 | 2,5+2,5 | 2.04 | 0.75 | 120 | 1.29 | 0 | 2.625 | 1.335 | 1.335 | available | 231 | Sverchkovo 35/10 | 2,5+2,5 | 0.1 | 2.14 | 0.75 | 120 | 1.39 | 0 | 2.625 | 1.235 | 1.235 | available
232 | Lesnaya 35/10 | 4+4 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available | 232 | Lesnaya 35/10 | 4+4 | 0 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available
233 | Tesovo 35/10 | 1,6+2,5 | 0.52 | 0.48 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | available | 233 | Tesovo 35/10 | 1,6+2,5 | 0.09 | 0.61 | 0.48 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available
234 | Svetotekhnika 110/10 | 16+16 | 4.5 | 0.97 | 120 | 3.53 | 0 | 16.8 | 13.27 | 13.27 | available | 234 | Svetotekhnika 110/10 | 16+16 | 2.42 | 6.92 | 0.97 | 120 | 5.95 | 0 | 16.8 | 10.85 | 10.85 | available
235 | Mishino 110/35/10 | 10+10 | 3.81 | 3.17 | 120 | 0.64 | 0 | 10.5 | 9.86 | 9.86 | available | 235 | Mishino 110/35/10 | 10+10 | 3 | 6.81 | 4.52 | 120 | 2.29 | 0 | 10.5 | 8.21 | 8.21 | available
| Nom. capacity MV, МVА | 10+10 | 2.53 | 2.53 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.35 | 3.88 | 3.88 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.28 | 0.64 | 120 | 0.64 | 0 | 10.5 | 9.86 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.65 | 2.93 | 0.64 | 120 | 2.29 | 0 | 10.5 | 8.21
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.71 | 0.59 | 120 | 1.12 | 0 | 6.615 | 5.495 | 5.495 | available | 236 | Nikolskoe 35/10 | 6,3+6,3 | 1.03 | 2.74 | 0.59 | 120 | 2.15 | 0 | 6.615 | 4.465 | 4.465 | available
237 | Bekrino 35/10 | 2,5+2,5 | 0.51 | 0.09 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available | 237 | Bekrino 35/10 | 2,5+2,5 | 0.23 | 0.74 | 0.09 | 120 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | available
238 | Trubnaya 110/10 | 25+25 | 6.49 | 1.57 | 120 | 4.92 | 0 | 26.25 | 21.33 | 21.33 | available | 238 | Trubnaya 110/10 | 25+25 | 5.29 | 11.78 | 1.57 | 120 | 10.21 | 0 | 26.25 | 16.04 | 16.04 | available
239 | Temkino 110/35/10 | 10+10 | 3.66 | 1.65 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | available | 239 | Temkino 110/35/10 | 10+10 | 2.06 | 5.72 | 2.05 | 120 | 3.67 | 0 | 10.5 | 6.83 | 6.83 | available
| Nom. capacity MV, МVА | 10+10 | 1.4 | 1.4 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.4 | 1.8 | 1.8 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.26 | 0.25 | 120 | 2.01 | 0 | 10.5 | 8.49 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.66 | 3.92 | 0.25 | 120 | 3.67 | 0 | 10.5 | 6.83
240 | Narytka 35/10 | 2,5+2,5 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 240 | Narytka 35/10 | 2,5+2,5 | 0 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available
241 | Novodugino 110/35/10 | 10+10 | 3.9 | 1.89 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | available | 241 | Novodugino 110/35/10 | 10+10 | 1.21 | 5.11 | 2.88 | 120 | 2.23 | 0 | 10.5 | 8.27 | 8.27 | available
| Nom. capacity MV, МVА | 10+10 | 1.41 | 1.41 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.99 | 2.4 | 2.4 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.49 | 0.48 | 120 | 2.01 | 0 | 10.5 | 8.49 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 2.71 | 0.48 | 120 | 2.23 | 0 | 10.5 | 8.27
242 | Vysokoe 35/10 | 1,6+4 | 0.57 | 0.42 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | available | 242 | Vysokoe 35/10 | 1,6+4 | 0.85 | 1.42 | 0.42 | 120 | 1 | 0 | 1.68 | 0.68 | 0.68 | available
243 | Khotkovo 35/10 | 4+4 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | available | 243 | Khotkovo 35/10 | 4+4 | 0 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | available
244 | Dneprovsk 110/35/10 | 10+10 | 2.57 | 1.88 | 120 | 0.69 | 0 | 10.5 | 9.81 | 9.81 | available | 244 | Dneprovsk 110/35/10 | 10+10 | 2.55 | 5.12 | 4.41 | 120 | 0.71 | 0 | 10.5 | 9.79 | 9.79 | available
| Nom. capacity MV, МVА | 10+10 | 1.72 | 1.72 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.53 | 4.25 | 4.25 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.85 | 0.16 | 120 | 0.69 | 0 | 10.5 | 9.81 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.02 | 0.87 | 0.16 | 120 | 0.71 | 0 | 10.5 | 9.79
245 | Lipetsy 35/10 | 2,5+2,5 | 0.24 | 0.75 | 120 | -0.51 | 0 | 2.625 | 3.135 | 3.135 | available | 245 | Lipetsy 35/10 | 2,5+2,5 | 0.03 | 0.27 | 0.75 | 120 | -0.48 | 0 | 2.625 | 3.105 | 3.105 | available
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.66 | 0.7 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.02 | 0.68 | 0.7 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available
247 | Sychevka 110/35/10 | 16+25 | 8.8 | 1.47 | 120 | 7.33 | 0 | 16.8 | 9.47 | 9.47 | available | 247 | Sychevka 110/35/10 | 16+25 | 6.63 | 15.43 | 1.78 | 120 | 13.65 | 0 | 16.8 | 3.15 | 3.15 | available
| Nom. capacity MV, МVА | 16+25 | 3.43 | 0.7 |  | 2.73 | 0 | 16.8 | 14.07 |  |  |  | Nom. capacity MV, МVА | 16+25 | 3.94 | 7.37 | 1.01 |  | 6.36 | 0 | 16.8 | 10.44
| Nom. capacfity LV, МVА | 16+25 | 5.37 | 0.77 | 120 | 4.6 | 0 | 16.8 | 12.2 |  |  |  | Nom. capacfity LV, МVА | 16+25 | 2.69 | 8.06 | 0.77 | 120 | 7.29 | 0 | 16.8 | 9.51
248 | Sutormino 35/10 | 1,8+4 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | available | 248 | Sutormino 35/10 | 1,8+4 | 0 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | available
249 | Karavaevo 35/10 | 4+4 | 1.29 | 0.29 | 120 | 1 | 0 | 4.2 | 3.2 | 3.2 | available | 249 | Karavaevo 35/10 | 4+4 | 0.43 | 1.72 | 0.29 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available
250 | Lukino 35/10 | 4+1,6 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | available | 250 | Lukino 35/10 | 4+1,6 | 0 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | available
251 | Subbotniki 110/10 | 6,3+6,3 | 0.75 | 0 | 120 | 0.75 | 0 | 6.615 | 5.865 | 5.865 | available | 251 | Subbotniki 110/10 | 6,3+6,3 | 0.24 | 0.99 | 0 | 120 | 0.99 | 0 | 6.615 | 5.625 | 5.625 | available
252 | Ugra 110/10 | 6,3+6,3 | 3.64 | 0 | 120 | 3.64 | 0 | 6.615 | 2.975 | 2.975 | available | 252 | Ugra 110/10 | 6,3+6,3 | 0.61 | 4.25 | 0 | 120 | 4.25 | 0 | 6.615 | 2.365 | 2.365 | available
253 | Znamenka 110/35/10 | 10+10 | 3.58 | 2.35 | 120 | 1.23 | 0 | 10.5 | 9.27 | 9.27 | available | 253 | Znamenka 110/35/10 | 10+10 | 3.56 | 7.14 | 2.77 | 120 | 4.37 | 0 | 10.5 | 6.13 | 6.13 | available
| Nom. capacity MV, МVА | 10+10 | 2.32 | 2.32 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.42 | 2.74 | 2.74 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.26 | 0.03 | 120 | 1.23 | 0 | 10.5 | 9.27 |  |  |  | Nom. capacity LV, МVА | 10+10 | 3.14 | 4.4 | 0.03 | 120 | 4.37 | 0 | 10.5 | 6.13
254 | Losmino 35/10 | 2,5+2,5 | 1.5 | 0.4 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | available | 254 | Losmino 35/10 | 2,5+2,5 | 0.07 | 1.57 | 0.4 | 120 | 1.17 | 0 | 2.625 | 1.455 | 1.455 | available
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.41 | 0.37 | 120 | 1.04 | 0 | 6.615 | 5.575 | 5.575 | available | 255 | Vskhody 110/35/10 | 6,3+6,3 | 0.22 | 1.63 | 0.37 | 120 | 1.26 | 0 | 6.615 | 5.355 | 5.355 | available
| Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 0.36 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.36 | 0.36 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.05 | 0.01 | 120 | 1.04 | 0 | 6.615 | 5.575 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.22 | 1.27 | 0.01 | 120 | 1.26 | 0 | 6.615 | 5.355
| Total: | 3150.6 | 578.51 | [8 empty] | 2: Total:; 3: 3150.6; 4: 318.83; 5: 897.34
| deficit | [8 empty] | -0.06 |  | 2: deficit; Min 12: -115.48
| proficit | [8 empty] | 1033.96 |  | 2: proficit; Min 12: 783.24