## Tambovenergo
Transmission capacity calculation of supply centers of IDGC of Centre - Tambovenergo division following the results of measurements of peak loads as at December 1, 2011
[9 empty] | table 1 | [11 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA |  |  |  | Installed transformer capacity, Sinst.
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS of 110 kV | [11 empty] | 1: SS of 110 kV
1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 21.45 |  |  | 21.45 | 0 | 26.25 | 4.8 | 4.8 | available | 1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 0 | 21.45 |  |  | 21.45 | 0 | 26.25 | 4.8 | 4.8 | available |  |  | 65
2 | SS 110/6 Tambovskaya No.3 | 2*25 | 14.6 |  |  | 14.6 | 0 | 26.25 | 11.65 | 11.65 | available | 2 | SS 110/6 Tambovskaya No.3 | 2*25 | 0 | 14.6 |  |  | 14.6 | 0 | 26.25 | 11.65 | 11.65 | available |  |  | 50
3 | SS 110/6 Tambovskaya No.5 | 2*25 | 14.71 |  |  | 14.71 | 0 | 26.25 | 11.54 | 11.54 | available | 3 | SS 110/6 Tambovskaya No.5 | 2*25 | 0 | 14.71 |  |  | 14.71 | 0 | 26.25 | 11.54 | 11.54 | available |  |  | 50
4 | SS 110/6 Tambovskaya No.7 | 2*25 | 16.7 |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | available | 4 | SS 110/6 Tambovskaya No.7 | 2*25 | 0 | 16.7 |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | available |  |  | 50
5 | SS 110/35/6 Pigment | 2*63 | 32.2 | 27.68 | 80 | 4.52 | 0 | 66.15 | 61.63 | 61.63 | available | 5 | SS 110/35/6 Pigment | 2*63 | 0 | 32.2 | 27.68 | 80 | 4.52 | 0 | 66.15 | 61.63 | 61.63 | available |  |  | 126
6 | SS 110/6 Tambovskaya No.8 | 40+16 | 9.33 |  |  | 9.33 | 0 | 16.8 | 7.47 | 7.47 | available | 6 | SS 110/6 Tambovskaya No.8 | 2*40 | 13.46 | 22.79 |  |  | 22.79 | 0 | 42 | 19.21 | 19.21 | available | Scheduled reconstruction works (replacement of a transformer capacity of 16 MVA to 40 MVA) |  | 56
7 | SS 110/35/6 Malinovskaya | 2*40 | 16.9 | 4.75 | 120 | 12.15 | 0 | 42 | 29.85 | 29.85 | available | 7 | SS 110/35/6 Malinovskaya | 2*40 | 0 | 16.9 | 4.75 | 120 | 12.15 | 0 | 42 | 29.85 | 29.85 | available |  |  | 80
8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 8.84 | 1.25 | 120 | 7.59 | 0 | 10.5 | 2.91 | 2.91 | available | 8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 2.35 | 11.19 | 1.25 | 120 | 9.94 | 0 | 10.5 | 0.56 | 0.56 | available |  |  | 26
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5.28 | 0.62 | 120 | 4.66 | 0 | 6.615 | 1.955 | 1.955 | available | 9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 0.08 | 5.36 | 0.62 | 120 | 4.74 | 0 | 6.615 | 1.875 | 1.875 | available |  |  | 16.3
10 | SS 110/35/10 Komsomolskaya | 2*10 | 7.87 | 2 | 80 | 5.87 | 0 | 10.5 | 4.63 | 4.63 | available | 10 | SS 110/35/10 Komsomolskaya | 2*10 | 1.76 | 9.63 | 2 | 80 | 7.63 | 0 | 10.5 | 2.87 | 2.87 | available |  |  | 20
11 | SS 110/10 М.Talinskaya | 10 | 0.62 | 0.52 | 1 day and night | 0.1 | 0 | 10.5 | 10.4 | 10.4 | available | 11 | SS 110/10 М.Talinskaya | 10 | 0 | 0.62 | 0.52 | 1 day and night | 0.1 | 0 | 10.5 | 10.4 | 10.4 | available |  |  | 10
12 | SS 110/35/10 Promyshlennaya | 2*40 | 19.62 | 5 | 120 | 14.62 | 0 | 42 | 27.38 | 27.38 | available | 12 | SS 110/35/10 Promyshlennaya | 2*40 | 1.94 | 21.56 | 5 | 120 | 16.56 | 0 | 42 | 25.44 | 25.44 | available |  |  | 80
13 | SS 110/35/10 Arzhenskaya | 2*10 | 4.23 | 1.5 | 80 | 2.73 | 0 | 10.5 | 7.77 | 7.77 | available | 13 | SS 110/35/10 Arzhenskaya | 2*10 | 0 | 4.23 | 1.5 | 80 | 2.73 | 0 | 10.5 | 7.77 | 7.77 | available |  |  | 20
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available | 14 | SS 110/10 Teleshovskaya | 2*2,5 | 0 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available |  |  | 5
15 | SS 110/6 Oktyabrskaya | 2*25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 | 22.35 | available | 15 | SS 110/6 Oktyabrskaya | 2*25 | 0 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 | 22.35 | available |  |  | 50
16 | SS 110/10 Spasskaya | 2*6,3 | 2.31 |  |  | 2.31 | 0 | 6.615 | 4.305 | 4.305 | available | 16 | SS 110/10 Spasskaya | 2*6,3 | 2.8 | 5.11 |  |  | 5.11 | 0 | 6.615 | 1.505 | 1.505 | available |  |  | 12.6
17 | SS 110/35/10 Kuzminskaya | 2*10 | 6.41 | 2 | 45 | 4.41 | 0 | 10.5 | 6.09 | 6.09 | available | 17 | SS 110/35/10 Kuzminskaya | 2*10 | 0 | 6.41 | 2 | 45 | 4.41 | 0 | 10.5 | 6.09 | 6.09 | available |  |  | 20
18 | SS 110/35/10 Sampurskaya | 10+16 | 5.8 | 2 | 80 | 3.8 | 0 | 10.5 | 6.7 | 6.7 | available | 18 | SS 110/35/10 Sampurskaya | 10+16 | 6.67 | 12.47 | 2 | 80 | 10.47 | 0 | 10.5 | 0.03 | 0.03 | available |  |  | 26
19 | SS 110/6 Leather plant | 2*10 | 1.19 |  |  | 1.19 | 0 | 10.5 | 9.31 | 9.31 | available | 19 | SS 110/6 Leather plant | 2*10 | 0 | 1.19 |  |  | 1.19 | 0 | 10.5 | 9.31 | 9.31 | available |  |  | 20
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 14.21 | 1.5 | 120 | 12.71 | 0 | 21 | 8.29 | 8.29 | available | 20 | SS 110/35/6 Rasskazovskaya | 25+20 | 0 | 14.21 | 1.5 | 120 | 12.71 | 0 | 21 | 8.29 | 8.29 | available |  |  | 45
21 | SS 110/35/10 Volchkovskaya | 2*10 | 2.16 | 0.95 | 120 | 1.21 | 0 | 10.5 | 9.29 | 9.29 | available | 21 | SS 110/35/10 Volchkovskaya | 2*10 | 0 | 2.16 | 0.95 | 120 | 1.21 | 0 | 10.5 | 9.29 | 9.29 | available |  |  | 20
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 3.33 | 1 | 120 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | available | 22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 0.53 | 3.86 | 1 | 120 | 2.86 | 0 | 6.615 | 3.755 | 3.755 | available |  |  | 22.3
23 | SS 110/35/10 Khmelevskaya | 2*10 | 4.21 | 0.5 | 120 | 3.71 | 0 | 10.5 | 6.79 | 6.79 | available | 23 | SS 110/35/10 Khmelevskaya | 2*10 | 0 | 4.21 | 0.5 | 120 | 3.71 | 0 | 10.5 | 6.79 | 6.79 | available |  |  | 20
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.09 | 1 | 80 | 4.09 | 0 | 6.615 | 2.525 | 2.525 | available | 24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 0.15 | 5.24 | 1 | 80 | 4.24 | 0 | 6.615 | 2.375 | 2.375 | available |  |  | 12.6
25 | SS 110/35/10 Nikiforovskaya | 10+16 | 3.22 | 1.5 | 120 | 1.72 | 0 | 10.5 | 8.78 | 8.78 | available | 25 | SS 110/35/10 Nikiforovskaya | 10+16 | 0.07 | 3.29 | 1.5 | 120 | 1.79 | 0 | 10.5 | 8.71 | 8.71 | available |  |  | 26
26 | SS 110/10 N.Seslavinskaya | 2.5 | 0.37 | 0.37 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 26 | SS 110/10 N.Seslavinskaya | 2.5 | 0 | 0.37 | 0.37 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available |  |  | 2.5
27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.33 | 0.33 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0 | 0.33 | 0.33 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available |  |  | 2.5
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.25 | 0.27 |  |  | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available |  |  | 5
29 | SS 110/35/10 Yuzhnaya | 16 | 7.4 | 3 | 1 day and night | 4.4 | 0 | 16.8 | 12.4 | 12.4 | available | 29 | SS 110/35/10 Yuzhnaya | 16 | 0 | 7.4 | 3 | 1 day and night | 4.4 | 0 | 16.8 | 12.4 | 12.4 | available |  |  | 16
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 21.19 | 3 | 120 | 18.19 | 0 | 33.075 | 14.885 | 14.885 | available | 30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 0.24 | 21.43 | 3 | 120 | 18.43 | 0 | 33.075 | 14.645 | 14.645 | available |  |  | 63
31 | SS 110/35/10 Sosnovskaya | 2*16 | 8.08 | 2 | 80 | 6.08 | 0 | 16.8 | 10.72 | 10.72 | available | 31 | SS 110/35/10 Sosnovskaya | 2*16 | 0 | 8.08 | 2 | 80 | 6.08 | 0 | 16.8 | 10.72 | 10.72 | available |  |  | 32
32 | SS 110/35/10 Pichaevskaya | 2*10 | 4.16 | 2 | 80 | 2.16 | 0 | 10.5 | 8.34 | 8.34 | available | 32 | SS 110/35/10 Pichaevskaya | 2*10 | 0.21 | 4.37 | 2 | 80 | 2.37 | 0 | 10.5 | 8.13 | 8.13 | available |  |  | 20
33 | SS 110/35/10 Algasovskaya | 2*40 | 12.85 | 2.92 | 120 | 9.93 | 0 | 42 | 32.07 | 32.07 | available | 33 | SS 110/35/10 Algasovskaya | 2*40 | 0 | 12.85 | 2.92 | 120 | 9.93 | 0 | 42 | 32.07 | 32.07 | available |  |  | 80
34 | SS 110/35/6 Morshanskaya | 40+25 | 19.29 | 3 | 120 | 16.29 | 0 | 26.25 | 9.96 | 9.96 | available | 34 | SS 110/35/6 Morshanskaya | 40+25 | 0 | 19.29 | 3 | 120 | 16.29 | 0 | 26.25 | 9.96 | 9.96 | available |  |  | 65
35 | SS 110/35/6 Kamvolnaya | 16+25 | 7.86 | 5 | 80 | 2.86 | 0 | 16.8 | 13.94 | 13.94 | available | 35 | SS 110/35/6 Kamvolnaya | 16+25 | 0 | 7.86 | 5 | 80 | 2.86 | 0 | 16.8 | 13.94 | 13.94 | available |  |  | 41
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 2.54 | 0.63 | 120 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | available | 36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 1.79 | 4.33 | 0.63 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | available |  |  | 20
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 2.52 | 1 | 120 | 1.52 | 0 | 10.5 | 8.98 | 8.98 | available | 37 | SS 110/35/10 Nashchekinskaya | 2*10 | 0 | 2.52 | 1 | 120 | 1.52 | 0 | 10.5 | 8.98 | 8.98 | available |  |  | 20
38 | SS 110/10 Shachinskaya | 2.5 | 0.06 | 0.05 | 1 day and night | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available | 38 | SS 110/10 Shachinskaya | 2.5 | 0 | 0.06 | 0.05 | 1 day and night | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available |  |  | 2.5
39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 8.85 | 3 | 45 | 5.85 | 0 | 16.8 | 10.95 | 10.95 | available | 39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 0 | 8.85 | 3 | 45 | 5.85 | 0 | 16.8 | 10.95 | 10.95 | available |  |  | 32
40 | SS 110/35/10 Muchkapskaya | 2*10 | 2.92 | 0.5 | 120 | 2.42 | 0 | 10.5 | 8.08 | 8.08 | available | 40 | SS 110/35/10 Muchkapskaya | 2*10 | 2.33 | 5.25 | 0.5 | 120 | 4.75 | 0 | 10.5 | 5.75 | 5.75 | available |  |  | 20
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.71 | 1.29 | 0.3 | 120 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | available |  |  | 5
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.78 | 0.6 | 120 | 1.18 | 0 | 10.5 | 9.32 | 9.32 | available | 42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 0.71 | 2.49 | 0.6 | 120 | 1.89 | 0 | 10.5 | 8.61 | 8.61 | available |  |  | 26
43 | SS 110/10 Shpikulovskaya | 6,3+2,5 | 0.68 | 0.61 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 43 | SS 110/10 Shpikulovskaya | 6,3+2,5 | 0.21 | 0.89 | 0.61 | 120 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | available |  |  | 8.8
44 | SS 110/35/10 Zherdevskaya | 2*16 | 6.27 | 3.5 | 80 | 2.77 | 0 | 16.8 | 14.03 | 14.03 | available | 44 | SS 110/35/10 Zherdevskaya | 2*16 | 13.81 | 20.08 | 3.5 | 80 | 16.58 | 0 | 16.8 | 0.22 | 0.22 | available |  |  | 32
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.52 | 0.4 | 120 | 4.12 | 0 | 10.5 | 6.38 | 6.38 | available | 45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 0.07 | 4.59 | 0.4 | 120 | 4.19 | 0 | 10.5 | 6.31 | 6.31 | available |  |  | 20
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available | 46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.37 | 0.76 | 0.2 | 120 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | available |  |  | 5
47 | SS 110/35/10 Tokarevskaya | 2*25 | 6.75 | 3 | 120 | 3.75 | 0 | 26.25 | 22.5 | 22.5 | available | 47 | SS 110/35/10 Tokarevskaya | 2*25 | 2.35 | 9.1 | 3 | 120 | 6.1 | 0 | 26.25 | 20.15 | 20.15 | available |  |  | 50
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0.76 | 0.91 | 120 | -0.15 | 0 | 6.615 | 6.765 | 6.765 | available | 48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0 | 0.76 | 0.91 | 120 | -0.15 | 0 | 6.615 | 6.765 | 6.765 | available |  |  | 16.3
49 | SS 110/35/10 Mordovskaya | 2*10 | 3.65 | 1 | 120 | 2.65 | 0 | 10.5 | 7.85 | 7.85 | available | 49 | SS 110/35/10 Mordovskaya | 2*10 | 0.47 | 4.12 | 1 | 120 | 3.12 | 0 | 10.5 | 7.38 | 7.38 | available |  |  | 20
50 | SS 110/35/10 Pavlovskaya | 10 | 1.14 | 1 | 1 day and night | 0.14 | 0 | 10.5 | 10.36 | 10.36 | available | 50 | SS 110/35/10 Pavlovskaya | 10 | 0 | 1.14 | 1 | 1 day and night | 0.14 | 0 | 10.5 | 10.36 | 10.36 | available |  |  | 10
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 13.92 | 3 | 120 | 10.92 | 0 | 26.25 | 15.33 | 15.33 | available | 51 | SS 110/35/10 Kirsanovskaya | 2*25 | 0.18 | 14.1 | 3 | 120 | 11.1 | 0 | 26.25 | 15.15 | 15.15 | available |  |  | 50
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 7.59 | 1 | 120 | 6.59 | 0 | 16.8 | 10.21 | 10.21 | available | 52 | SS 110/35/10 Inzhavinskaya | 2*16 | 6.84 | 14.43 | 1 | 120 | 13.43 | 0 | 16.8 | 3.37 | 3.37 | available |  |  | 32
53 | SS 110/35/10 Umyotskaya | 2*10 | 1.51 | 2 | 80 | -0.49 | 0 | 10.5 | 10.99 | 10.99 | available | 53 | SS 110/35/10 Umyotskaya | 2*10 | 0 | 1.51 | 2 | 80 | -0.49 | 0 | 10.5 | 10.99 | 10.99 | available |  |  | 20
54 | SS 110/35/10 Kovylskaya | 2*10 | 0.8 | 1 | 120 | -0.2 | 0 | 10.5 | 10.7 | 10.7 | available | 54 | SS 110/35/10 Kovylskaya | 2*10 | 0.22 | 1.02 | 1 | 120 | 0.02 | 0 | 10.5 | 10.48 | 10.48 | available |  |  | 20
55 | SS 110/10 Inokovskaya | 2.5 | 0.16 | 0.18 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available | 55 | SS 110/10 Inokovskaya | 2.5 | 0 | 0.16 | 0.18 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available |  |  | 2.5
56 | SS 110/10 PTF | 2*16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 | 16.8 | available | 56 | SS 110/10 PTF | 2*16 | 13.56 | 13.56 |  |  | 13.56 | 0 | 16.8 | 3.24 | 3.24 | available |  |  | 32
SS of 35 kV | [11 empty] | 1: SS of 35 kV |  | TOTAL for 110kV | 1699.9
57 | SS 35/6 Elevatornaya | 2*2,5 | 1.87 |  |  | 1.87 | 0 | 2.625 | 0.755 | 0.755 | available | 57 | SS 35/6 Elevatornaya | 2*2,5 | 0 | 1.87 |  |  | 1.87 | 0 | 2.625 | 0.755 | 0.755 | available |  |  | 5
58 | SS 35/10 Picherskaya | 2*2,5 | 0.36 |  |  | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 58 | SS 35/10 Picherskaya | 2*2,5 | 0 | 0.36 |  |  | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available |  |  | 5
59 | SS 35/10 Osinovskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available | 59 | SS 35/10 Osinovskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available |  |  | 5
60 | SS 35/10 Koptevskaya | 2*2,5 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available | 60 | SS 35/10 Koptevskaya | 2*2,5 | 0 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available |  |  | 5
61 | SS 35/10 Sayukinskaya | 2,5+4 | 0.53 | 0.2 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 61 | SS 35/10 Sayukinskaya | 2,5+4 | 0 | 0.53 | 0.2 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available |  |  | 6.5
62 | SS 35/10 Zelyonaya-1 | 2*4 | 1.84 |  |  | 1.84 | 0 | 4.2 | 2.36 | 2.36 | available | 62 | SS 35/10 Zelyonaya-1 | 2*4 | 0 | 1.84 |  |  | 1.84 | 0 | 4.2 | 2.36 | 2.36 | available |  |  | 8
63 | SS 35/10 Pyatiletka | 2*4 | 0.28 |  |  | 0.28 | 0 | 4.2 | 3.92 | 3.92 | available | 63 | SS 35/10 Pyatiletka | 2*4 | 0 | 0.28 |  |  | 0.28 | 0 | 4.2 | 3.92 | 3.92 | available |  |  | 8
64 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.82 |  |  | 0.82 | 0 | 2.625 | 1.805 | 1.805 | available | 64 | SS 35/10 Yaroslavskaya | 2*2,5 | 1.74 | 2.56 |  |  | 2.56 | 0 | 2.625 | 0.065 | 0.065 | available |  |  | 5
65 | SS 35/10 Platonovskaya | 2*6,3 | 2.25 | 0.24 | 120 | 2.01 | 0 | 6.615 | 4.605 | 4.605 | available | 65 | SS 35/10 Platonovskaya | 2*6,3 | 0 | 2.25 | 0.24 | 120 | 2.01 | 0 | 6.615 | 4.605 | 4.605 | available |  |  | 12.6
66 | SS 35/10 Znamenskaya | 2*4 | 2.81 | 1.54 | 120 | 1.27 | 0 | 4.2 | 2.93 | 2.93 | available | 66 | SS 35/10 Znamenskaya | 2*4 | 0.33 | 3.14 | 1.54 | 120 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | available |  |  | 8
67 | SS 35/10 Sukhotinskaya | 2.5 | 0.34 |  |  | 0.34 | 0 | 0 | -0.34 | -0.34 | unavailable | 67 | SS 35/10 Sukhotinskaya | 2*2,5 | 0 | 0.34 |  |  | 0.34 | 0 | 2.63 | 2.29 | 2.29 | available | Scheduled reconstruction works (installation of 2-nd transformer 2,5 MVA) |  | 2.5
68 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.97 |  |  | 0.97 | 0 | 1.68 | 0.71 | 0.71 | available | 68 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0 | 0.97 |  |  | 0.97 | 0 | 1.68 | 0.71 | 0.71 | available |  |  | 4.1
69 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.48 | 0.29 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 69 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0 | 0.48 | 0.29 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available |  |  | 4.1
70 | SS 35/10 Stepnaya | 2*4 | 1.41 | 0.7 | 80 | 0.71 | 0 | 4.2 | 3.49 | 3.49 | available | 70 | SS 35/10 Stepnaya | 2*4 | 0 | 1.41 | 0.7 | 80 | 0.71 | 0 | 4.2 | 3.49 | 3.49 | available |  |  | 8
71 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 0.94 | 0.5 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | available | 71 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 3.73 | 4.67 | 0.5 | 120 | 4.17 | 0 | 4.2 | 0.03 | 0.03 | available |  |  | 8
72 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.32 | 0.2 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | available | 72 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0 | 0.32 | 0.2 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | available |  |  | 4.1
73 | SS 35/10 Gorelskaya | 4+6,3 | 1.69 | 0.7 | 80 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | available | 73 | SS 35/10 Gorelskaya | 4+6,3 | 0.83 | 2.52 | 0.7 | 80 | 1.82 | 0 | 4.2 | 2.38 | 2.38 | available |  |  | 10.3
74 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | available | 74 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | available |  |  | 5
75 | SS 35/10 Avangardskaya | 2*2,5 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available | 75 | SS 35/10 Avangardskaya | 2*2,5 | 0 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available |  |  | 5
76 | SS 35/10 Suravskaya | 1,6+2,5 | 0.62 | 0.2 | 120 | 0.42 | 0 | 1.68 | 1.26 | 1.26 | available | 76 | SS 35/10 Suravskaya | 1,6+2,5 | 0 | 0.62 | 0.2 | 120 | 0.42 | 0 | 1.68 | 1.26 | 1.26 | available |  |  | 4.1
77 | SS 35/10 Seleznzyovskaya | 3*4 | 3.64 |  |  | 3.64 | 0 | 8.4 | 4.76 | 4.76 | available | 77 | SS 35/10 Seleznzyovskaya | 3*4 | 0.11 | 3.75 |  |  | 3.75 | 0 | 8.4 | 4.65 | 4.65 | available |  |  | 12
78 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.56 | 0.3 | 80 | 1.26 | 0 | 1.68 | 0.42 | 0.42 | available | 78 | SS 35/10 Chernyanskaya | 1,6+2,5 | 0.16 | 1.72 | 0.3 | 80 | 1.42 | 0 | 1.68 | 0.26 | 0.26 | available |  |  | 4.1
79 | SS 35/10 Viktorskaya | 2.5 | 0.42 |  |  | 0.42 | 0 | 0 | -0.42 | -0.42 | unavailable | 79 | SS 35/10 Viktorskaya | 2.5 | 0 | 0.42 |  |  | 0.42 | 0 | 0 | -0.42 | -0.42 | unavailable |  |  | 2.5
80 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.69 |  |  | 0.69 | 0 | 1.68 | 0.99 | 0.99 | available | 80 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0 | 0.69 |  |  | 0.69 | 0 | 1.68 | 0.99 | 0.99 | available |  |  | 3.2
81 | SS 35/10 Avdeevskaya | 2*2,5 | 0.69 |  |  | 0.69 | 0 | 2.625 | 1.935 | 1.935 | available | 81 | SS 35/10 Avdeevskaya | 2*2,5 | 0 | 0.69 |  |  | 0.69 | 0 | 2.625 | 1.935 | 1.935 | available |  |  | 5
82 | SS 35/10 Tatanovskaya | 2*2,5 | 2.6 |  |  | 2.6 | 0 | 2.625 | 0.025 | 0.025 | available | 82 | SS 35/10 Tatanovskaya | 2*2,5 | 0 | 2.6 |  | 120 | 2.6 | 0 | 2.625 | 0.025 | 0.025 | available |  |  | 5
83 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 2.94 | 0.3 | 60 | 2.64 | 0 | 5.25 | 2.61 | 2.61 | available | 83 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 0.1 | 3.04 | 0.3 | 60 | 2.74 | 0 | 5.25 | 2.51 | 2.51 | available |  |  | 9
84 | SS 35/10 P.Prigorodnaya | 2*6,3 | 4.18 |  |  | 4.18 | 0 | 6.615 | 2.435 | 2.435 | available | 84 | SS 35/10 P.Prigorodnaya | 2*6,3 | 0.05 | 4.23 |  |  | 4.23 | 0 | 6.615 | 2.385 | 2.385 | available |  |  | 12.6
85 | SS 35/10 Bokinskaya | 2*6,3 | 1.95 | 0.3 | 30 | 1.65 | 0 | 6.615 | 4.965 | 4.965 | available | 85 | SS 35/10 Bokinskaya | 2*6,3 | 0.09 | 2.04 | 0.3 | 30 | 1.74 | 0 | 6.615 | 4.875 | 4.875 | available |  |  | 12.6
86 | SS 35/10 Stolovskaya | 4 | 0.55 | 0.2 | 1 day and night | 0.35 | 0 | 4.2 | 3.85 | 3.85 | available | 86 | SS 35/10 Stolovskaya | 4 | 0 | 0.55 | 0.2 | 1 day and night | 0.35 | 0 | 4.2 | 3.85 | 3.85 | available |  |  | 4
87 | SS 35/10 Tulinovskaya | 2*2,5 | 1.36 |  |  | 1.36 | 0 | 2.625 | 1.265 | 1.265 | available | 87 | SS 35/10 Tulinovskaya | 2*2,5 | 0 | 1.36 |  |  | 1.36 | 0 | 2.625 | 1.265 | 1.265 | available |  |  | 5
88 | SS 35/6 Macaroni factory | 1.6 | 0.08 |  |  | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available | 88 | SS 35/6 Macaroni factory | 1.6 | 0 | 0.08 |  |  | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available |  |  | 1.6
89 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | available | 89 | SS 35/10 Serebryakovskaya | 2*1,6 | 0 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | available |  |  | 3.2
90 | SS 35/10 B.Doroga | 2*1,6 | 0.28 | 0.2 | 60 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available | 90 | SS 35/10 B.Doroga | 2*1,6 | 0 | 0.28 | 0.2 | 60 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available |  |  | 3.2
91 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.57 |  |  | 0.57 | 0 | 2.625 | 2.055 | 2.055 | available | 91 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0 | 0.57 |  |  | 0.57 | 0 | 2.625 | 2.055 | 2.055 | available |  |  | 5
92 | SS 35/10 Vishnevskaya | 2*2,5 | 0.48 | 0.26 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available | 92 | SS 35/10 Vishnevskaya | 2*2,5 | 0 | 0.48 | 0.26 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available |  |  | 5
93 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.31 | 0.32 | 50 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 93 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.12 | 0.43 | 0.32 | 50 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available |  |  | 5
94 | SS 35/10 Glazkovskaya | 2*4 | 0.84 | 0.4 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | available | 94 | SS 35/10 Glazkovskaya | 2*4 | 0 | 0.84 | 0.4 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | available |  |  | 8
95 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 95 | SS 35/10 Dmitirievskaya | 2*2,5 | 0 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available |  |  | 5
96 | SS 35/6 Donskaya | 6,3+10 | 4.07 | 2 | 1 day and night | 2.07 | 0 | 6.615 | 4.545 | 4.545 | available | 96 | SS 35/6 Donskaya | 6,3+10 | 0 | 4.07 | 2 | 1 day and night | 2.07 | 0 | 6.615 | 4.545 | 4.545 | available |  |  | 16.3
97 | SS 35/10 Druzhba | 2.5 | 0.23 | 0.16 | 1 day and night | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 97 | SS 35/10 Druzhba | 2.5 | 0.08 | 0.31 | 0.16 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available |  |  | 2.5
98 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.13 | 0.23 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | available | 98 | SS 35/10 Ekaterininskaya | 2*2,5 | 0 | 0.13 | 0.23 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | available |  |  | 5
99 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.31 | 0.25 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | available | 99 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.06 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | available |  |  | 4.1
100 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.4 | 0.4 | 80 | 1 | 0 | 2.625 | 1.625 | 1.625 | available | 100 | SS 35/10 Izosimovskaya | 6,3+2,5 | 0.06 | 1.46 | 0.4 | 80 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | available |  |  | 8.8
101 | SS 35/10 KIM | 2,5+4 | 1.24 | 0.3 | 120 | 0.94 | 0 | 2.625 | 1.685 | 1.685 | available | 101 | SS 35/10 KIM | 2,5+4 | 0.06 | 1.3 | 0.3 | 120 | 1 | 0 | 2.625 | 1.625 | 1.625 | available |  |  | 6.5
102 | SS 35/10 Klenskaya | 2*2,5 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 102 | SS 35/10 Klenskaya | 2*2,5 | 0 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available |  |  | 5
103 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.59 | 0.3 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available | 103 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0 | 0.59 | 0.3 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available |  |  | 5
104 | SS 35/10 Komintern | 2*2,5 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 104 | SS 35/10 Komintern | 2*2,5 | 0.29 | 0.6 | 0.22 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available |  |  | 5
105 | SS 35/10 Kochetovskaya | 6.3 | 0.42 | 0.2 | 1 day and night | 0.22 | 0 | 6.615 | 6.395 | 6.395 | available | 105 | SS 35/10 Kochetovskaya | 6.3 | 0 | 0.42 | 0.2 | 1 day and night | 0.22 | 0 | 6.615 | 6.395 | 6.395 | available |  |  | 6.3
106 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.3 | 0.14 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 106 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0 | 0.3 | 0.14 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available |  |  | 5
107 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 1.08 | 0.3 | 1 day and night | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available | 107 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 0 | 1.08 | 0.3 | 1 day and night | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available |  |  | 2.5
108 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.38 | 0.28 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | available | 108 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0 | 0.38 | 0.28 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | available |  |  | 3.2
109 | SS 35/10 Petrovskaya | 2*4 | 3.23 | 0.5 | 120 | 2.73 | 0 | 4.2 | 1.47 | 1.47 | available | 109 | SS 35/10 Petrovskaya | 2*4 | 0.41 | 3.64 | 0.5 | 120 | 3.14 | 0 | 4.2 | 1.06 | 1.06 | available |  |  | 8
110 | SS 35/10 Prigorodnaya | 2*2,5 | 0.7 | 0.4 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 110 | SS 35/10 Prigorodnaya | 2*2,5 | 0.16 | 0.86 | 0.4 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available |  |  | 5
111 | SS 35/6 Progress | 2*10 | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | available | 111 | SS 35/6 Progress | 2*10 | 0 | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | available |  |  | 20
112 | SS 35/10 Raninskaya | 1.6 | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | available | 112 | SS 35/10 Raninskaya | 1.6 | 0 | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | available |  |  | 1.6
113 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.4 |  |  | 0.4 | 0 | 1.68 | 1.28 | 1.28 | available | 113 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0 | 0.4 |  |  | 0.4 | 0 | 1.68 | 1.28 | 1.28 | available |  |  | 3.2
114 | SS 35/10 Saburovskaya | 2*5,6 | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | available | 114 | SS 35/10 Saburovskaya | 2*5,6 | 0 | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | available |  |  | 11.2
115 | SS 35/10 Sestryonskaya | 1,6+2,5 | 0.11 |  |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available | 115 | SS 35/10 Sestryonskaya | 1,6+2,5 | 0 | 0.11 |  |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available |  |  | 4.1
116 | SS 35/10 Sitovskaya | 1.6 | 0.45 | 0.5 | 1 day and night | -0.05 | 0 | 1.68 | 1.73 | 1.73 | available | 116 | SS 35/10 Sitovskaya | 1.6 | 0 | 0.45 | 0.5 | 1 day and night | -0.05 | 0 | 1.68 | 1.73 | 1.73 | available |  |  | 1.6
117 | SS 35/10 Skobelevskaya | 1.6 | 0.21 | 0.24 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 117 | SS 35/10 Skobelevskaya | 1.6 | 0 | 0.21 | 0.24 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available |  |  | 1.6
118 | SS 35/10 Ustyinskaya | 2.5 | 1.08 | 0.4 | 1 day and night | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available | 118 | SS 35/10 Ustyinskaya | 2.5 | 0 | 1.08 | 0.4 | 1 day and night | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available |  |  | 2.5
119 | SS 35/10 Yurlovskaya | 2*2,5 | 0.49 |  |  | 0.49 | 0 | 2.625 | 2.135 | 2.135 | available | 119 | SS 35/10 Yurlovskaya | 2*2,5 | 0 | 0.49 |  |  | 0.49 | 0 | 2.625 | 2.135 | 2.135 | available |  |  | 5
120 | SS 35/10 Yablonovetskaya | 2*2,5 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | available | 120 | SS 35/10 Yablonovetskaya | 2*2,5 | 0 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | available |  |  | 5
121 | SS 35/10 Agroprom | 2*4 | 1.55 |  |  | 1.55 | 0 | 4.2 | 2.65 | 2.65 | available | 121 | SS 35/10 Agroprom | 2*4 | 0 | 1.55 |  |  | 1.55 | 0 | 4.2 | 2.65 | 2.65 | available |  |  | 8
122 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.2 |  |  | 0.2 | 0 | 1.68 | 1.48 | 1.48 | available | 122 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0 | 0.2 |  |  | 0.2 | 0 | 1.68 | 1.48 | 1.48 | available |  |  | 4.1
123 | SS 35/10 Vanovskaya | 2*2,5 | 0.12 | 0.07 | 80 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 123 | SS 35/10 Vanovskaya | 2*2,5 | 0 | 0.12 | 0.07 | 80 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available |  |  | 5
124 | SS 35/10 Vyazhlinskaya | 1.8 | 0.42 | 0.3 | 1 day and night | 0.12 | 0 | 1.89 | 1.77 | 1.77 | available | 124 | SS 35/10 Vyazhlinskaya | 1.8 | 0 | 0.42 | 0.3 | 1 day and night | 0.12 | 0 | 1.89 | 1.77 | 1.77 | available |  |  | 1.8
125 | SS 35/10 Zarechnaya | 2*2,5 | 0.93 |  |  | 0.93 | 0 | 2.625 | 1.695 | 1.695 | available | 125 | SS 35/10 Zarechnaya | 2*2,5 | 0 | 0.93 |  |  | 0.93 | 0 | 2.625 | 1.695 | 1.695 | available |  |  | 5
126 | SS 35/10 Kryukovskaya | 2*2,5 | 0.72 | 0.3 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available | 126 | SS 35/10 Kryukovskaya | 2*2,5 | 0.11 | 0.83 | 0.3 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | available |  |  | 5
127 | SS 35/6 Korshunovskaya | 2*2,5 | 0.47 |  |  | 0.47 | 0 | 2.625 | 2.155 | 2.155 | available | 127 | SS 35/6 Korshunovskaya | 2*2,5 | 1.96 | 2.43 |  |  | 2.43 | 0 | 2.625 | 0.195 | 0.195 | available |  |  | 5
128 | SS 35/6 Lugovaya | 4 | 0.63 | 0.4 | 1 day and night | 0.23 | 0 | 4.2 | 3.97 | 3.97 | available | 128 | SS 35/6 Lugovaya | 4 | 0 | 0.63 | 0.4 | 1 day and night | 0.23 | 0 | 4.2 | 3.97 | 3.97 | available |  |  | 4
129 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.25 | 0.15 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 129 | SS 35/10 Lyubvinskaya | 2*2,5 | 0 | 0.25 | 0.15 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available |  |  | 5
130 | SS 35/10 Morshanskaya | 2*4 | 2.28 |  |  | 2.28 | 0 | 4.2 | 1.92 | 1.92 | available | 130 | SS 35/10 Morshanskaya | 2*4 | 0.22 | 2.5 |  |  | 2.5 | 0 | 4.2 | 1.7 | 1.7 | available |  |  | 8
131 | SS 35/10 Piterskaya | 2.5 | 0.84 | 0.4 | 1 day and night | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 131 | SS 35/10 Piterskaya | 2.5 | 0.07 | 0.91 | 0.4 | 1 day and night | 0.51 | 0 | 2.625 | 2.115 | 2.115 | available |  |  | 2.5
132 | SS 35/10 Rakshinskaya | 2*4 | 1.3 | 0.6 | 80 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | available | 132 | SS 35/10 Rakshinskaya | 2*4 | 0.08 | 1.38 | 0.6 | 80 | 0.78 | 0 | 4.2 | 3.42 | 3.42 | available |  |  | 8
133 | SS 35/10 Rybinskaya | 2*2,5 | 0.69 | 0.5 | 80 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available | 133 | SS 35/10 Rybinskaya | 2*2,5 | 0.07 | 0.76 | 0.5 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available |  |  | 5
134 | SS 35/10 Serpovskaya | 2*2,5 | 0.68 | 0.3 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available | 134 | SS 35/10 Serpovskaya | 2*2,5 | 0 | 0.68 | 0.3 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available |  |  | 5
135 | SS 35/10 St.Tomnikovskaya | 1 | 0.14 | 0.09 | 1 day and night | 0.05 | 0 | 1.05 | 1 | 1 | available | 135 | SS 35/10 St.Tomnikovskaya | 1 | 0 | 0.14 | 0.09 | 1 day and night | 0.05 | 0 | 1.05 | 1 | 1 | available |  |  | 1
136 | SS 35/10 Chernitovskaya | 2.5 | 0.44 | 0.2 | 1 day and night | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 136 | SS 35/10 Chernitovskaya | 2.5 | 0 | 0.44 | 0.2 | 1 day and night | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available |  |  | 2.5
137 | SS 35/10 Bondarskaya | 2*2,5 | 1.02 | 0.3 | 80 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | available | 137 | SS 35/10 Bondarskaya | 2*2,5 | 0.47 | 1.49 | 0.3 | 80 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | available |  |  | 5
138 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.36 | 0.25 | 80 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available | 138 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0 | 0.36 | 0.25 | 80 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available |  |  | 4.1
139 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.18 | 0.15 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | available | 139 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.41 | 0.59 | 0.15 | 120 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | available |  |  | 4.1
140 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.66 | 0.3 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 140 | SS 35/10 Egorovskaya | 2,5+3,2 | 0 | 0.66 | 0.3 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available |  |  | 5.7
141 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.18 |  |  | 0.18 | 0 | 1.68 | 1.5 | 1.5 | available | 141 | SS 35/10 Kershinskaya | 1,6+2,5 | 0 | 0.18 |  |  | 0.18 | 0 | 1.68 | 1.5 | 1.5 | available |  |  | 4.1
142 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.15 | 0.05 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | available | 142 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.89 | 1.04 | 0.05 | 120 | 0.99 | 0 | 1.68 | 0.69 | 0.69 | available |  |  | 3.2
143 | SS 35/10 Lipovskaya | 2.5 | 0.2 | 0.27 | 1 day and night | -0.07 | 0 | 2.625 | 2.695 | 2.695 | available | 143 | SS 35/10 Lipovskaya | 2.5 | 0 | 0.2 | 0.27 | 1 day and night | -0.07 | 0 | 2.625 | 2.695 | 2.695 | available |  |  | 2.5
144 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.12 | 0.11 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available | 144 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0 | 0.12 | 0.11 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available |  |  | 5.7
145 | SS 35/10 Mitropolskaya | 2.5 | 0.18 | 0.28 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | available | 145 | SS 35/10 Mitropolskaya | 2.5 | 0 | 0.18 | 0.28 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | available |  |  | 2.5
146 | SS 35/10 P.Uglovskaya | 1.6 | 0.28 | 0.15 | 1 day and night | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available | 146 | SS 35/10 P.Uglovskaya | 1.6 | 0 | 0.28 | 0.15 | 1 day and night | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available |  |  | 1.6
147 | SS 35/10 Rudovskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available | 147 | SS 35/10 Rudovskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available |  |  | 5
148 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.32 | 0.23 | 1 day and night | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 148 | SS 35/10 V.Yaroslavskaya | 2.5 | 2 | 2.32 | 0.23 | 1 day and night | 2.09 | 0 | 2.625 | 0.535 | 0.535 | available |  |  | 2.5
149 | SS 35/10 Degtyanskaya | 2.5 | 1.24 | 0.4 | 1 day and night | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 149 | SS 35/10 Degtyanskaya | 2.5 | 0.98 | 2.22 | 0.4 | 1 day and night | 1.82 | 0 | 2.625 | 0.805 | 0.805 | available |  |  | 2.5
150 | SS 35/10 Zelenaya-2 | 1.6 | 0.15 | 0.18 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 150 | SS 35/10 Zelenaya-2 | 1.6 | 0 | 0.15 | 0.18 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available |  |  | 1.6
151 | SS 35/10 Kulevatovskaya | 2*4 | 1.76 | 0.5 | 80 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | available | 151 | SS 35/10 Kulevatovskaya | 2*4 | 0 | 1.76 | 0.5 | 80 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | available |  |  | 8
152 | SS 35/10 Lamskaya | 4+2,5 | 0.52 | 0.2 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available | 152 | SS 35/10 Lamskaya | 4+2,5 | 2 | 2.52 | 0.2 | 120 | 2.32 | 0 | 2.625 | 0.305 | 0.305 | available |  |  | 6.5
153 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 153 | SS 35/10 Gryaznovskaya | 2*2,5 | 0 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available |  |  | 5
154 | SS 35/10 Otyasskaya | 2*2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 154 | SS 35/10 Otyasskaya | 2*2,5 | 0 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available |  |  | 5
155 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.15 | 0.19 | 1 day and night | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 155 | SS 35/10 P.Vasilyevskaya | 1.6 | 0 | 0.15 | 0.19 | 1 day and night | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available |  |  | 1.6
156 | SS 35/10 Podlesnaya | 2*2,5 | 0.52 | 0.22 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 156 | SS 35/10 Podlesnaya | 2*2,5 | 0 | 0.52 | 0.22 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available |  |  | 5
157 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 157 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available |  |  | 5
158 | SS 35/10 Zherdevskaya | 4 | 2.37 | 0.5 | 1 day and night | 1.87 | 0 | 4.2 | 2.33 | 2.33 | available | 158 | SS 35/10 Zherdevskaya | 4 | 0 | 2.37 | 0.5 | 1 day and night | 1.87 | 0 | 4.2 | 2.33 | 2.33 | available |  |  | 4
159 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.37 |  |  | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available | 159 | SS 35/10 Sukmanovskaya | 2*2,5 | 0 | 0.37 |  |  | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available |  |  | 5
160 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.32 | 0.29 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | available | 160 | SS 35/10 Tugolukovskaya | 2,5+4 | 0 | 0.32 | 0.29 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | available |  |  | 6.5
161 | SS 35/10 Artemovskaya | 2*2,5 | 0.5 | 0.35 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 161 | SS 35/10 Artemovskaya | 2*4 | 2.95 | 3.45 | 0.35 | 120 | 3.1 | 0 | 4.2 | 1.1 | 1.1 | available | Scheduled reconstruction works (replacement of a transformer capacity of 2,5 MVA to 4 MVA) |  | 5
162 | SS 35/10 RSKhO | 2,5+4 | 1.36 | 1.16 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 162 | SS 35/10 RSKhO | 2,5+4 | 2.4 | 3.76 | 1.16 | 80 | 2.6 | 0 | 2.625 | 0.025 | 0.025 | available |  |  | 6.5
163 | SS 35/10 Maksimovskaya | 2*1,6 | 0.34 | 0.18 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | available | 163 | SS 35/10 Maksimovskaya | 2*1,6 | 0 | 0.34 | 0.18 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | available |  |  | 3.2
164 | SS 35/10 Burnakskaya | 5,6+6,3 | 2.15 |  |  | 2.15 | 0 | 5.88 | 3.73 | 3.73 | available | 164 | SS 35/10 Burnakskaya | 5,6+6,3 | 0.24 | 2.39 |  |  | 2.39 | 0 | 5.88 | 3.49 | 3.49 | available |  |  | 11.9
165 | SS 35/10 Poletaevskaya | 2*4 | 0.21 | 0.19 | 120 | 0.02 | 2.18 | 4.2 | 2 | 2 | available | 165 | SS 35/10 Poletaevskaya | 2*4 | 0 | 0.21 | 0.19 | 120 | 0.02 | 2.18 | 4.2 | 2 | 2 | available |  |  | 8
166 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.83 |  |  | 0.83 | 0 | 4.2 | 3.37 | 3.37 | available | 166 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0 | 0.83 |  |  | 0.83 | 0 | 4.2 | 3.37 | 3.37 | available |  |  | 6.5
167 | SS 35/10 Pioner | 1,6+2,5 | 1.04 | 0.3 | 60 | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available | 167 | SS 35/10 Pioner | 1,6+2,5 | 0 | 1.04 | 0.3 | 60 | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available |  |  | 4.1
168 | SS 35/10 Lvovskaya | 2*2,5 | 0.34 | 0.2 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 168 | SS 35/10 Lvovskaya | 2*2,5 | 0 | 0.34 | 0.2 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available |  |  | 5
169 | SS 35/10 Nadezhdinskaya | 1.6 | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available | 169 | SS 35/10 Nadezhdinskaya | 1.6 | 0 | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available |  |  | 1.6
170 | SS 35/10 Kuleshovskaya | 2.5 | 0.36 | 0.26 | 1 day and night | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 170 | SS 35/10 Kuleshovskaya | 2.5 | 0 | 0.36 | 0.26 | 1 day and night | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available |  |  | 2.5
171 | SS 35/10 Chernyaevskaya | 2*4 | 1.3 |  |  | 1.3 | 0 | 4.2 | 2.9 | 2.9 | available | 171 | SS 35/10 Chernyaevskaya | 2*4 | 0 | 1.3 |  |  | 1.3 | 0 | 4.2 | 2.9 | 2.9 | available |  |  | 8
172 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available | 172 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available |  |  | 5
173 | SS 35/10 Shulginskaya | 2*4 | 0.62 | 0.02 | 120 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | available | 173 | SS 35/10 Shulginskaya | 2*4 | 0 | 0.62 | 0.02 | 120 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | available |  |  | 8
174 | SS 35/10 Lavrovskaya | 2*2,5 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available | 174 | SS 35/10 Lavrovskaya | 2*2,5 | 0 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available |  |  | 5
175 | SS 35/10 N.Sergievskaya | 3.2 | 0.42 | 0.3 | 1 day and night | 0.12 | 0 | 3.36 | 3.24 | 3.24 | available | 175 | SS 35/10 N.Sergievskaya | 3.2 | 0 | 0.42 | 0.3 | 1 day and night | 0.12 | 0 | 3.36 | 3.24 | 3.24 | available |  |  | 3.2
176 | SS 35/10 Kamenskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available | 176 | SS 35/10 Kamenskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available |  |  | 5
177 | SS 35/10 Protasovskaya | 4+2,5 | 0.35 |  |  | 0.35 | 0 | 2.625 | 2.275 | 2.275 | available | 177 | SS 35/10 Protasovskaya | 4+2,5 | 0 | 0.35 |  |  | 0.35 | 0 | 2.625 | 2.275 | 2.275 | available |  |  | 6.5
178 | SS 35/10 Chakinskaya | 4 | 0.64 |  |  | 0.64 | 0 | 0 | -0.64 | -0.64 | unavailable | 178 | SS 35/10 Chakinskaya | 4 | 0 | 0.64 |  |  | 0.64 | 0 | 0 | -0.64 | -0.64 | unavailable |  |  | 4
179 | SS 35/10 Lukinskaya | 2.5 | 0.26 | 0.22 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 179 | SS 35/10 Lukinskaya | 2.5 | 0 | 0.26 | 0.22 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available |  |  | 2.5
180 | SS 35/10 Zolotovskaya | 2.5 | 0.52 | 0.2 | 1 day and night | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available | 180 | SS 35/10 Zolotovskaya | 2.5 | 0 | 0.52 | 0.2 | 1 day and night | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available |  |  | 2.5
181 | SS 35/10 Mozdokskaya | 2.5 | 0.28 |  |  | 0.28 | 0 | 0 | -0.28 | -0.28 | unavailable | 181 | SS 35/10 Mozdokskaya | 2.5 | 0 | 0.28 |  |  | 0.28 | 0 | 0 | -0.28 | -0.28 | unavailable |  |  | 2.5
182 | SS 35/10 Oblovskaya | 2*2,5 | 0.34 | 0.25 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 182 | SS 35/10 Oblovskaya | 2*2,5 | 0 | 0.34 | 0.25 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available |  |  | 5
183 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.42 | 0.07 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | available | 183 | SS 35/10 V.Vershinskaya | 2,5+4 | 0 | 0.42 | 0.07 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | available |  |  | 6.5
184 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 184 | SS 35/10 Luchevskaya | 2,5+1,6 | 0 | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available |  |  | 4.1
185 | SS 35/10 Olshanskaya | 4+2,5 | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | available | 185 | SS 35/10 Olshanskaya | 4+2,5 | 0 | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | available |  |  | 6.5
186 | SS 35/10 Pavlodarskaya | 2.5 | 0.08 | 0.1 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available | 186 | SS 35/10 Pavlodarskaya | 2.5 | 0 | 0.08 | 0.1 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available |  |  | 2.5
187 | SS 35/10 Berezovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available | 187 | SS 35/10 Berezovskaya | 2*2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available |  |  | 5
188 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.37 | 0.29 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available | 188 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0 | 0.37 | 0.29 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available |  |  | 3.2
189 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available | 189 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available |  |  | 4.1
190 | SS 35/10 Shapkinskaya | 2*4 | 0.52 |  |  | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available | 190 | SS 35/10 Shapkinskaya | 2*4 | 0 | 0.52 |  |  | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available |  |  | 8
191 | SS 35/10 Maryinskaya | 2*1,6 | 0.16 | 0.25 | 120 | -0.09 | 0 | 1.68 | 1.77 | 1.77 | available | 191 | SS 35/10 Maryinskaya | 2*1,6 | 0 | 0.16 | 0.25 | 120 | -0.09 | 0 | 1.68 | 1.77 | 1.77 | available |  |  | 3.2
192 | SS 35/10 Irskaya | 1,6+2,5 | 0.17 | 0.35 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | available | 192 | SS 35/10 Irskaya | 1,6+2,5 | 0 | 0.17 | 0.35 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | available |  |  | 4.1
193 | SS 35/10 Zavodskaya | 2*4 | 1.22 | 0.3 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | available | 193 | SS 35/10 Zavodskaya | 2*4 | 0 | 1.22 | 0.3 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | available |  |  | 8
194 | SS 35/10 Kalaisskaya | 2.5 | 0.47 | 0.28 | 1 day and night | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available | 194 | SS 35/10 Kalaisskaya | 2.5 | 0 | 0.47 | 0.28 | 1 day and night | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available |  |  | 2.5
195 | SS 35/10 Sokolovskaya | 2*2,5 | 0.92 | 0.3 | 80 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | available | 195 | SS 35/10 Sokolovskaya | 2*2,5 | 0 | 0.92 | 0.3 | 80 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | available |  |  | 5
196 | SS 35/10 Veterinarnaya | 2.5 | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | available | 196 | SS 35/10 Veterinarnaya | 2.5 | 0 | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | available |  |  | 2.5
197 | SS 35/10 Glukhovskaya | 2.5 | 0.23 | 0.09 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 197 | SS 35/10 Glukhovskaya | 2.5 | 0 | 0.23 | 0.09 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available |  |  | 2.5
198 | SS 35/10 Orzhevskaya | 2.5 | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 198 | SS 35/10 Orzhevskaya | 2.5 | 0 | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available |  |  | 2.5
199 | SS 35/10 Umyotskaya | 2*4 | 1.34 | 0.4 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | available | 199 | SS 35/10 Umyotskaya | 2*4 | 0 | 1.34 | 0.4 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | available |  |  | 8
200 | SS 35/10 Gavrilovskaya | 2*4 | 1.42 | 0.5 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | available | 200 | SS 35/10 Gavrilovskaya | 2*4 | 0.89 | 2.31 | 0.5 | 120 | 1.81 | 0 | 4.2 | 2.39 | 2.39 | available |  |  | 8
201 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.66 | 0.3 | 80 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 201 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.89 | 1.55 | 0.3 | 80 | 1.25 | 0 | 2.625 | 1.375 | 1.375 | available |  |  | 5
202 | SS 35/10 Annenskaya | 2*2,5 | 1.29 | 0.3 | 80 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | available | 202 | SS 35/10 Annenskaya | 2*2,5 | 1.11 | 2.4 | 0.3 | 80 | 2.1 | 0 | 2.625 | 0.525 | 0.525 | available |  |  | 5
203 | SS 35/10 Filatovskaya | 2*2,5 | 0.44 | 0.33 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 203 | SS 35/10 Filatovskaya | 2*2,5 | 0 | 0.44 | 0.33 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available |  |  | 5
204 | SS 35/10 Nikitinskaya | 2*4 | 0.73 | 0.14 | 120 | 0.59 | 0 | 1.68 | 1.09 | 1.09 | available | 204 | SS 35/10 Nikitinskaya | 2*4 | 3.6 | 4.33 | 0.14 | 120 | 4.19 | 0 | 4.2 | 0.01 | 0.01 | available |  |  | 8
205 | SS 35/10 Balykleyskaya | 2*2,5 | 0.96 | 0.2 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available | 205 | SS 35/10 Balykleyskaya | 2*2,5 | 0 | 0.96 | 0.2 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available |  |  | 5
206 | SS 35/10 Karavainskaya | 2*1,6 | 0.43 | 0.3 | 80 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available | 206 | SS 35/10 Karavainskaya | 2*1,6 | 0 | 0.43 | 0.3 | 80 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available |  |  | 3.2
207 | SS 35/10 Pavlovskaya | 3.2 | 0.26 | 0.28 | 1 day and night | -0.02 | 0 | 3.36 | 3.38 | 3.38 | available | 207 | SS 35/10 Pavlovskaya | 3.2 | 0 | 0.26 | 0.28 | 1 day and night | -0.02 | 0 | 3.36 | 3.38 | 3.38 | available |  |  | 3.2
| Total: | 2486.9 | 498.61 | [8 empty] | 2: Total:; 3: 2516.4; 5: 602.46 |  | TOTAL 35kV | 787
| deficit | [8 empty] | -1.68 |  | 2: deficit; Min 12: -1.34
| proficit | [8 empty] | 921.18 |  | 2: proficit; Min 12: 848.92 |  | TOTAL 35+110 | 2486.9

## Св. тек. дефицит ноябрь 2011 (hidden)
Перечень закрытых центров питания филиала ОАО "МРСК Центра" - "Тамбовэнерго" по зимним замерам нагрузкам по состоянию на 1 декабря 2011 года (текущий дефицит мощности).
№ п/п | Наименование объекта центра питания, класс напряжения |  | Текущий дефицит , МВА
Тамбовэнерго
1 | ПС 35/10 Сухотинская | 2.5 | -0.34
2 | ПС 35/10 Викторская | 2.5 | -0.42
3 | ПС 35/10 Чакинская | 4 | -0.64
4 | ПС 35/10 Моздокская | 2.5 | -0.28
Итого текущий дефицит (01.12.11) |  |  | -1.68

## Св. ожид. дефицит ноябрь 2011 (hidden)
Перечень закрытых центров питания филиала ОАО "МРСК Центра" - "Тамбовэнерго" по ожидаемым нагрузкам с учетом подключения новых мощностей по технологическому присоединению и др.развития э/сетевого комплекса по состоянию на 1 декабря 2011 года (ожидаемый дефицит мощности).
№ п/п | Наименование объекта центра питания, класс напряжения |  | Ожидаемый дефицит , МВА
Тамбовэнерго
1 | ПС 35/10 Викторская | 2.5 | -0.42
2 | ПС 35/10 Чакинская | 4 | -0.64
3 | ПС 35/10 Моздокская | 2.5 | -0.28
Итого ожидаемый дефицит (01.12.11) |  |  | -1.34