## Summary
Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2011 | [13 empty] | Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2011
[11 empty] | Table 1 | [14 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note |  |  | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA | [5 empty] | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [13 empty] | MVA | Min
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Однотрансформаторные ПС | [13 empty] | 1: Однотрансформаторные ПС
| СЭС | [12 empty] | 2: СЭС
1 | No. 44 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 | No. 44 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110/6
2 | Stupino | 6.3 | 0.78 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.2575 | 0.2575 |  |  |  | 2 | Stupino | 6.3 | 1.51 | 2.29 | 1.0375 | 120 | 1.2525 | 0 | 1.0375 | -1.2525 | -1.2525 | 110/10
3 | P.Kommuna | 6.3 | 0.5 | 0.5 | 120 | 0.5 | 0 | 0.5 | 0 | 0 |  |  |  | 3 | P.Kommuna | 6.3 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 0.5 | 0 | 0 | 110/10
4 | No. 38 | 2.5 | 0.55 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.25 | 0.25 |  |  |  | 4 | No. 38 | 2.5 | 0 | 0.55 | 0.8 | 120 | -0.25 | 0 | 0.8 | 0.25 | 0.25 | 35/10
5 | No. 46 | 4 | 0.11 | 0 | 0 | 0 | 0 | 0 | -0.11 | -0.11 |  |  |  | 5 | No. 46 | 4 | 0 | 0.11 | 0 | 0 | 0.11 | 0 | 0 | -0.11 | -0.11 | 35/6
6 | Istobnoe | 4 | 0.33 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.03 | 0.03 |  |  |  | 6 | Istobnoe | 4 | 0.29 | 0.62 | 0.36 | 120 | 0.26 | 0 | 0.36 | -0.26 | -0.26 | 35/10
7 | Rodina | 2.5 | 0 | 2.2 | 120 | 2.2 | 0 | 2.2 | 2.2 | 2.2 |  |  |  | 7 | Rodina | 2.5 | 0.17 | 0.17 | 2.2 | 120 | -2.03 | 0 | 2.2 | 2.03 | 2.03 | 35/10
8 | Vyaznovatovka | 2.5 | 0.87 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.63 | 0.63 |  |  |  | 8 | Vyaznovatovka | 2.5 | 0.01 | 0.88 | 1.5 | 120 | -0.62 | 0 | 1.5 | 0.62 | 0.62 | 35/10
9 | V.Turovo-1 | 3.2 | 1.25 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.15 | 0.15 |  |  |  | 9 | V.Turovo-1 | 3.2 | 0.19 | 1.44 | 1.4 | 120 | 0.04 | 0 | 1.4 | -0.04 | -0.04 | 35/10
10 | Semidesyatnoe | 2.5 | 0.24 | 0 | 0 | 0 | 0 | 0 | -0.24 | -0.24 |  |  |  | 10 | Semidesyatnoe | 2.5 | 0.12 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | -0.36 | -0.36 | 35/10
11 | Khokhol-2 | 2.5 | 1.33 | 0 | 0 | 0 | 0 | 0 | -1.33 | -1.33 |  |  |  | 12 | Khokhol-2 | 2.5 | 0.42 | 1.75 | 0 | 0 | 1.75 | 0 | 0 | -1.75 | -1.75 | 35/10
12 | N.Olshanka | 4 | 0.98 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | -0.2226 | -0.2226 |  |  |  | 13 | N.Olshanka | 4 | 0.09 | 1.07 | 0.7574 | 120 | 0.3126 | 0 | 0.7574 | -0.3126 | -0.3126 | 35/10
13 | Troitskoe | 2.5 | 0.27 | 0 | 0 | 0 | 0 | 0 | -0.27 | -0.27 |  |  |  | 14 | Troitskoe | 2.5 | 0.01 | 0.28 | 0 | 0 | 0.28 | 0 | 0 | -0.28 | -0.28 | 35/10
14 | Zemlyansk | 4 | 0.66 | 0 | 0 | 0 | 0 | 0 | -0.66 | -0.66 |  |  |  | 15 | Zemlyansk | 4 | 0.67 | 1.33 | 0 | 0 | 1.33 | 0 | 0 | -1.33 | -1.33 | 35/10
15 | Losevo SPS | 2.5 | 0.55 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.4036 | 0.4036 |  |  |  | 16 | Losevo SPS | 2.5 | 0 | 0.55 | 0.9536 | 120 | -0.4036 | 0 | 0.9536 | 0.4036 | 0.4036 | 35/10
16 | Verny | 2.5 | 1.53 | 2.15 | 120 | 2.15 | 0 | 2.15 | 0.62 | 0.62 |  |  |  | 17 | Verny | 2.5 | 0.13 | 1.66 | 2.15 | 120 | -0.49 | 0 | 2.15 | 0.49 | 0.49 | 35/10
17 | Elevator | 2.5 | 1.37 | 1.1 | 120 | 1.1 | 0 | 1.1 | -0.27 | -0.27 |  |  |  | 18 | Elevator | 2.5 | 0.03 | 1.4 | 1.1 | 120 | 0.3 | 0 | 1.1 | -0.3 | -0.3 | 35/10
18 | Yubileynaya | 4 | 1.16 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.44 | 0.44 |  |  |  | 19 | Yubileynaya | 4 | 0.07 | 1.23 | 1.6 | 120 | -0.37 | 0 | 1.6 | 0.37 | 0.37 | 35/10
19 | Parusnoe | 4 | 2.63 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.5284 | 0.5284 |  |  |  | 20 | Parusnoe | 4 | 0.18 | 2.81 | 3.1584 | 120 | -0.3484 | 0 | 3.1584 | 0.3484 | 0.3484 | 35/10
20 | Rogachyovka | 4 | 1.6 | 2.05 | 120 | 2.05 | 0 | 2.05 | 0.45 | 0.45 |  |  |  | 21 | Rogachyovka | 4 | 0.09 | 1.69 | 2.05 | 120 | -0.36 | 0 | 2.05 | 0.36 | 0.36 | 35/10
21 | Poultry farm Rassvet | 2.5 | 0.08 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.22 | 0.22 |  |  |  | 22 | Poultry farm Rassvet | 2.5 | 0 | 0.08 | 0.3 | 120 | -0.22 | 0 | 0.3 | 0.22 | 0.22 | 35/10
22 | Alena | 6.3 | 1.37 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.03 | 0.03 |  |  |  | 23 | Alena | 6.3 | 0 | 1.37 | 1.4 | 120 | -0.03 | 1 | 1.4 | 0.03 | 0.03 | 35/10
23 | Dankovo | 2.5 | 0.8 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.099 | 0.099 |  |  |  | 24 | Dankovo | 2.5 | 0.02 | 0.82 | 0.899 | 120 | -0.079 | 0 | 0.899 | 0.079 | 0.079 | 35/10
24 | ЛЭС | [12 empty] | 2: ЛЭС
25 | Bugaevka | 16 | 7.84 | 14 | 90 | 14 | 0 | 14 | 6.16 | 1.56 |  |  |  | 25 | Bugaevka | 16 | 0.28 | 8.12 | 14 | 90 | -5.88 | 0 | 14 | 5.88 | 1.28
| Sн. MV, МVА | 16 | 5.4 | 10 | 90 | 10 | 0 | 10 | 4.6 | [5 empty] | Sн. MV, МVА | 16 | 0 | 5.4 | 10 | 90 | -4.6 | 0 | 10 | 4.6 |  | 110/35/10
| Sн. LV, МVА | 16 | 2.44 | 4 | 90 | 4 | 0 | 4 | 1.56 | [5 empty] | Sн. LV, МVА | 16 | 0.28 | 2.72 | 4 | 90 | -1.28 | 0 | 4 | 1.28
26 | Dobrino | 10 | 2.07 | 8.9 | 90 | 8.9 | 0 | 8.9 | 6.83 | 1.12 |  |  |  | 26 | Dobrino | 10 | 0.23 | 2.3 | 6.6 | 90 | -4.3 | 0 | 6.6 | 4.3 | 0.89
| Sн. MV, МVА | 10 | 0 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.8 | [5 empty] | Sн. MV, МVА | 10 | 0 | 0 | 5.8 | 90 | -5.8 | 0 | 5.8 | 5.8 |  | 110/35/10
| Sн. LV, МVА | 10 | 2 | 3.12 | 90 | 3.12 | 0 | 3.12 | 1.12 | [5 empty] | Sн. LV, МVА | 10 | 0.23 | 2.23 | 3.12 | 90 | -0.89 | 0 | 3.12 | 0.89
27 | N. Kalitva | 6.3 | 1.43 | 2 | 240 | 2 | 0 | 2 | 0.57 | 0.57 |  |  |  | 27 | N. Kalitva | 6.3 | 0.59 | 2.02 | 2 | 240 | 0.02 | 0 | 2 | -0.02 | -0.02 | 110/10
28 | Shishovka | 6.3 | 0.69 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.65 | 1.65 |  |  |  | 28 | Shishovka | 6.3 | 0.37 | 1.06 | 2.34 | 180 | -1.28 | 0 | 2.34 | 1.28 | 1.28 | 110/10
29 | Azovka | 10 | 1.91 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.21 | 1.21 |  |  |  | 29 | Azovka | 10 | 0.47 | 2.38 | 3.12 | 180 | -0.74 | 0 | 3.12 | 0.74 | 0.74 | 110/10
30 | Yurasovka | 2.5 | 0.84 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.72 | 0.72 |  |  |  | 30 | Yurasovka | 2.5 | 0.03 | 0.87 | 1.56 | 120 | -0.69 | 0 | 1.56 | 0.69 | 0.69 | 35/10
31 | Nerovnovka | 2.5 | 0.28 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.5 | 0.5 |  |  |  | 31 | Nerovnovka | 2.5 | 0.02 | 0.3 | 0.78 | 240 | -0.48 | 0 | 0.78 | 0.48 | 0.48 | 35/10
32 | Saprino | 1.8 | 0.4 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.4 | 1.4 |  |  |  | 32 | Saprino | 1.8 | 0.03 | 0.43 | 1.8 | 120 | -1.37 | 0 | 1.8 | 1.37 | 1.37 | 35/10
33 | Sergeevka | 4 | 0.53 | 0 | 0 | 0 | 0 | 0 | -0.53 | -0.53 |  |  |  | 33 | Sergeevka | 4 | 0.06 | 0.59 | 0 | 0 | 0.59 | 0 | 0 | -0.59 | -0.59 | 35/10
34 | Stepanovka | 4 | 0.32 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.24 | 1.24 |  |  |  | 34 | Stepanovka | 4 | 0.04 | 0.36 | 1.56 | 240 | -1.2 | 0 | 1.56 | 1.2 | 1.2 | 35/10
35 | Kolodezhanskaya | 2.5 | 0.24 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.54 | 0.54 |  |  |  | 35 | Kolodezhanskaya | 2.5 | 0.08 | 0.32 | 0.78 | 180 | -0.46 | 0 | 0.78 | 0.46 | 0.46 | 35/10
36 | Andreevka | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 36 | Andreevka | 2.5 | 0.02 | 0.02 | 0 | 0 | 0.02 | 0 | 0 | -0.02 | -0.02 | 35/10
37 | Kulikovka | 4 | 1.75 | 0 | 0 | 0 | 0 | 0 | -1.75 | -1.75 |  |  |  | 37 | Kulikovka | 4 | 0.44 | 2.19 | 0 | 0 | 2.19 | 0 | 0 | -2.19 | -2.19 | 35/10
38 | Lizinovka | 2.5 | 0.87 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.63 | 1.63 |  |  |  | 38 | Lizinovka | 2.5 | 0.07 | 0.94 | 2.5 | 240 | -1.56 | 0 | 2.5 | 1.56 | 1.56 | 35/10
39 | Sotnitskaya | 4 | 1.45 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.85 | 0.85 |  |  |  | 39 | Sotnitskaya | 4 | 0.16 | 1.61 | 2.3 | 120 | -0.69 | 0 | 2.3 | 0.69 | 0.69 | 35/10
40 | Kr. Polyana | 2.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 |  |  |  | 40 | Kr. Polyana | 2.5 | 0.04 | 0.39 | 0 | 0 | 0.39 | 0 | 0 | -0.39 | -0.39 | 35/10
41 | Gumny | 4 | 0.8 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.76 | 0.76 |  |  |  | 41 | Gumny | 4 | 0.19 | 0.99 | 1.56 | 180 | -0.57 | 0 | 1.56 | 0.57 | 0.57 | 35/10
42 | Uryv | 2.5 | 0.67 | 0 | 0 | 0 | 0 | 0 | -0.67 | -0.67 |  |  |  | 42 | Uryv | 2.5 | 0.11 | 0.78 | 0 | 0 | 0.78 | 0 | 0 | -0.78 | -0.78 | 35/10
43 | Shubnoe | 2.5 | 1.18 | 1.17 | 180 | 1.17 | 0 | 1.17 | -0.01 | -0.01 |  |  |  | 43 | Shubnoe | 2.5 | 0.19 | 1.37 | 1.17 | 180 | 0.2 | 0 | 1.17 | -0.2 | -0.2 | 35/10
44 | Zaluzhnoe | 2.5 | 2.16 | 2 | 240 | 2 | 0 | 2 | -0.16 | -0.16 |  |  |  | 44 | Zaluzhnoe | 2.5 | 0.52 | 2.68 | 2 | 240 | 0.68 | 0 | 2 | -0.68 | -0.68 | 35/10
45 | БЭС | [12 empty] | 2: БЭС
46 | Anna-2 | 25 | 6.18 | 7.8 | 90 | 7.8 | 0 | 7.8 | 1.62 | 0.31 |  |  |  | 45 | Anna-2 | 25 | 3.55 | 9.73 | 7.8 | 90 | 1.93 | 0 | 7.8 | -1.93 | -2.24
| Sн. MV, МVА | 25 | 1.93 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.31 | [5 empty] | Sн. MV, МVА | 25 | 0 | 1.93 | 2.24 | 90 | -0.31 | 0 | 2.24 | 0.31 |  | 110/35/10
| Sн. LV, МVА | 25 | 4.25 | 5.56 | 90 | 5.56 | 0 | 5.56 | 1.31 | [5 empty] | Sн. LV, МVА | 25 | 3.55 | 7.8 | 5.56 | 90 | 2.24 | 0 | 5.56 | -2.24
47 | Vostochnaya | 10 | 3.62 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.18 | 1.18 |  |  |  | 46 | Vostochnaya | 10 | 1.14 | 4.76 | 4.8 | 30 | -0.04 | 0 | 4.8 | 0.04 | 0.04 | 35/6
48 | BolshevikBPS | 6.3 | 0.9 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.56 | 0.56 |  |  |  | 47 | BolshevikBPS | 6.3 | 0.06 | 0.96 | 1.46 | 60 | -0.5 | 0 | 1.46 | 0.5 | 0.5 | 110/10
49 | Rozhdestvo | 6.3 | 0.66 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.09 | 0.09 |  |  |  | 48 | Rozhdestvo | 6.3 | 0.26 | 0.92 | 0.75 | 60 | 0.17 | 0 | 0.75 | -0.17 | -0.17 | 110/10
50 | V. Toyda | 6.3 | 1 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.4 | 0.4 |  |  |  | 49 | V. Toyda | 6.3 | 0.01 | 1.01 | 1.4 | 90 | -0.39 | 0 | 1.4 | 0.39 | 0.39 | 110/10
51 | Vostochnaya-1 | 40 | 7.63 | 8.13 | 60 | 8.13 | 0 | 8.13 | 0.5 | -0.54 |  |  |  | 50 | Vostochnaya-1 | 40 | 1.3 | 8.93 | 8.13 | 60 | 0.8 | 0 | 8.13 | -0.8 | -0.8
| Sн. MV, МVА | 40 | 6.21 | 5.67 | 60 | 5.67 | 0 | 5.67 | -0.54 | [5 empty] | Sн. MV, МVА | 40 | 0 | 6.21 | 5.67 | 60 | 0.54 | 0 | 5.67 | -0.54 |  | 110/35/6
| Sн. LV, МVА | 40 | 2.19 | 3.1 | 60 | 3.1 | 0 | 3.1 | 0.91 | [5 empty] | Sн. LV, МVА | 40 | 1.3 | 3.49 | 3.1 | 60 | 0.39 | 0 | 3.1 | -0.39
52 | Makashevka | 2.5 | 0.36 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.12 | 0.12 |  |  |  | 51 | Makashevka | 2.5 | 0.12 | 0.48 | 0.48 | 180 | 0 | 0 | 0.48 | 0 | 0 | 35/10
53 | Mirolyubie | 4 | 0.31 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.19 | 0.19 |  |  |  | 52 | Mirolyubie | 4 | 0.03 | 0.34 | 0.5 | 60 | -0.16 | 0 | 0.5 | 0.16 | 0.16 | 35/10
54 | V. Zaton | 2.5 | 0 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0.01 | 0.01 |  |  |  | 53 | V. Zaton | 2.5 | 0 | 0 | 0.01 | 60 | -0.01 | 0 | 0.01 | 0.01 | 0.01 | 35/10
55 | Oktyabrskoe | 2.5 | 0.59 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.08 | 0.08 |  |  |  | 54 | Oktyabrskoe | 2.5 | 0.13 | 0.72 | 0.67 | 30 | 0.05 | 0 | 0.67 | -0.05 | -0.05 | 35/10
56 | Ilmen | 2.5 | 0.24 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.14 | 0.14 |  |  |  | 55 | Ilmen | 2.5 | 0.05 | 0.29 | 0.38 | 60 | -0.09 | 0 | 0.38 | 0.09 | 0.09 | 35/10
57 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 |  |  |  | 56 | Vikhlyaevka | 2.5 | 0 | 0.1 | 0.12 | 120 | -0.02 | 0 | 0.12 | 0.02 | 0.02 | 35/10
58 | N. Elan | 2.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | -0.5 | -0.5 |  |  |  | 57 | N. Elan | 2.5 | 0.02 | 0.52 | 0 | 0 | 0.52 | 0 | 0 | -0.52 | -0.52 | 35/10
59 | B. Alabukhi | 2.5 | 0.83 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.1 | 0.1 |  |  |  | 58 | B. Alabukhi | 2.5 | 0.17 | 1 | 0.93 | 90 | 0.07 | 0 | 0.93 | -0.07 | -0.07 | 35/10
60 | Pykhovka | 2.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | -0.25 | -0.25 |  |  |  | 59 | Pykhovka | 2.5 | 0 | 0.25 | 0 | 0 | 0.25 | 0 | 0 | -0.25 | -0.25 | 35/10
61 | Е. Koleno | 4 | 2.96 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.37 | 0.37 |  |  |  | 60 | Е. Koleno | 4 | 0.1 | 3.06 | 3.33 | 120 | -0.27 | 0 | 3.33 | 0.27 | 0.27 | 35/10
62 | Podgornoe BPS | 2.5 | 0.41 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.05 | 0.05 |  |  |  | 61 | Podgornoe BPS | 2.5 | 0.01 | 0.42 | 0.46 | 180 | -0.04 | 0 | 0.46 | 0.04 | 0.04 | 35/10
63 | Mikhailovka-1 | 4 | 0.3 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.06 | 0.06 |  |  |  | 62 | Mikhailovka-1 | 4 | 0 | 0.3 | 0.36 | 60 | -0.06 | 0 | 0.36 | 0.06 | 0.06 | 35/10
64 | Mikhailovka | 2.5 | 0.31 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.19 | 0.19 |  |  |  | 63 | Mikhailovka | 2.5 | 0.01 | 0.32 | 0.5 | 60 | -0.18 | 0 | 0.5 | 0.18 | 0.18 | 35/10
65 | Gnilusha | 4 | 0.74 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.18 | 0.18 |  |  |  | 64 | Gnilusha | 4 | 0 | 0.74 | 0.92 | 180 | -0.18 | 0 | 0.92 | 0.18 | 0.18 | 35/10
66 | Mayskaya | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 |  |  |  | 65 | Mayskaya | 2.5 | 0 | 0.42 | 0 | 0 | 0.42 | 0 | 0 | -0.42 | -0.42 | 35/10
67 | Khleborodnoe | 2.5 | 0.49 | 0 | 0 | 0 | 0 | 0 | -0.49 | -0.49 |  |  |  | 66 | Khleborodnoe | 2.5 | 0.09 | 0.58 | 0 | 0 | 0.58 | 0 | 0 | -0.58 | -0.58 | 35/10
68 | N. Kurlak | 4 | 0.42 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.18 | 0.18 |  |  |  | 67 | N. Kurlak | 4 | 0 | 0.42 | 0.6 | 120 | -0.18 | 0 | 0.6 | 0.18 | 0.18 | 35/10
69 | Nikolaevka | 4 | 1.33 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.17 | 0.17 |  |  |  | 68 | Nikolaevka | 4 | 0.04 | 1.37 | 1.5 | 120 | -0.13 | 0 | 1.5 | 0.13 | 0.13 | 35/10
70 | Vasilyevka BPS | 2.5 | 0.48 | 0.39 | 180 | 0.39 | 0 | 0.39 | -0.09 | -0.09 |  |  |  | 69 | Vasilyevka BPS | 2.5 | 0.09 | 0.57 | 0.39 | 180 | 0.18 | 0 | 0.39 | -0.18 | -0.18 | 35/10
71 | Avangard | 2.5 | 0.9 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.01 | 0.01 |  |  |  | 70 | Avangard | 2.5 | 0.07 | 0.97 | 0.91 | 120 | 0.06 | 0 | 0.91 | -0.06 | -0.06 | 35/10
72 | Orlovka | 2.5 | 0.57 | 0.48 | 90 | 0.48 | 0 | 0.48 | -0.09 | -0.09 |  |  |  | 71 | Orlovka | 2.5 | 0.05 | 0.62 | 0.48 | 90 | 0.14 | 0 | 0.48 | -0.14 | -0.14 | 35/10
73 | N. Chigla | 2.5 | 0.59 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.31 | 0.31 |  |  |  | 72 | N. Chigla | 2.5 | 0.11 | 0.7 | 0.9 | 120 | -0.2 | 0 | 0.9 | 0.2 | 0.2 | 35/10
74 | Troitskoe-1 | 1.6 | 0.12 | 0.11 | 120 | 0.11 | 0 | 0.11 | -0.01 | -0.01 |  |  |  | 73 | Troitskoe-1 | 1.6 | 0 | 0.12 | 0.11 | 120 | 0.01 | 0 | 0.11 | -0.01 | -0.01 | 35/10
75 | Tishanka | 2.5 | 1.02 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.49 | 0.49 |  |  |  | 74 | Tishanka | 2.5 | 0.05 | 1.07 | 1.51 | 120 | -0.44 | 0 | 1.51 | 0.44 | 0.44 | 35/10
76 | КЭС | [12 empty] | 2: КЭС
77 | Kalacheevskaya | 6.3 | 0.55 | 1 | 1 сутки | 1 | 0 | 1 | 0.45 | 0.45 |  |  |  | 75 | Kalacheevskaya | 6.3 | 1.55 | 2.1 | 1 | 1 сутки | 1.1 | 0 | 1 | -1.1 | -1.1 | 110/10
78 | B.Kazinka | 6.3 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 | -0.51 |  |  |  | 76 | B.Kazinka | 6.3 | 3.09 | 3.6 | 0 | 0 | 3.6 | 0 | 0 | -3.6 | -3.6
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110/35/10
| Sн. LV, МVА | 6.3 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 | [5 empty] | Sн. LV, МVА | 6.3 | 3.09 | 3.6 | 0 | 0 | 3.6 | 0 | 0 | -3.6
79 | Derezovka | 6.3 | 0.36 | 0 | 0 | 0 | 0 | 0 | -0.36 | -0.36 |  |  |  | 77 | Derezovka | 6.3 | 0.07 | 0.43 | 0 | 0 | 0.43 | 0 | 0 | -0.43 | -0.43 | 110/10
80 | Osetrovka | 6.3 | 0.88 | 1.5 | 1 сутки | 1.5 | 0 | 1.5 | 0.62 | 0.62 |  |  |  | 78 | Osetrovka | 6.3 | 2.22 | 3.1 | 1.5 | 1 сутки | 1.6 | 0 | 1.5 | -1.6 | -1.6 | 110/10
81 | sovkhoz Radchensky | 10 | 2.79 | 2 | 1 сутки | 2 | 0 | 2 | -0.79 | -2.64 |  |  |  | 79 | sovkhoz Radchensky | 10 | 0.03 | 2.82 | 2 | 1 сутки | 0.82 | 0 | 2 | -0.82 | -2.64
| Sн. MV, МVА | 10 | 2.64 | 0 | 1 сутки | 0 | 0 | 0 | -2.64 | [5 empty] | Sн. MV, МVА | 10 | 0 | 2.64 | 0 | 0 | 2.64 | 0 | 0 | -2.64 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.15 | 2 | 1 сутки | 2 | 0 | 2 | 1.85 | [5 empty] | Sн. LV, МVА | 10 | 0.03 | 0.18 | 2 | 1 сутки | -1.82 | 0 | 2 | 1.82
82 | Klepovka | 4 | 1.16 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.44 | 0.44 |  |  |  | 80 | Klepovka | 4 | 0.13 | 1.29 | 1.6 | 120 | -0.31 | 0 | 1.6 | 0.31 | 0.31 | 35/10
83 | Krasnopolye | 4 | 0.31 | 1 | 120 | 1 | 0 | 1 | 0.69 | 0.69 |  |  |  | 81 | Krasnopolye | 4 | 0.02 | 0.33 | 1 | 120 | -0.67 | 0 | 1 | 0.67 | 0.67 | 35/10
84 | Nikolskoe | 2.5 | 0.4 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.1 | 1.1 |  |  |  | 82 | Nikolskoe | 2.5 | 0 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
85 | N. Liman | 2.5 | 0.35 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.15 | 1.15 |  |  |  | 83 | N. Liman | 2.5 | 0.09 | 0.44 | 1.5 | 45 | -1.06 | 0 | 1.5 | 1.06 | 1.06 | 35/10
86 | Bereznyagi | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 |  |  |  | 84 | Bereznyagi | 2.5 | 0.13 | 0.43 | 1.5 | 45 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | 35/10
87 | Kr.Flot | 2.5 | 0.27 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.23 | 1.23 |  |  |  | 85 | Kr.Flot | 2.5 | 0.11 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
88 | R. Zhuravka | 2.5 | 0.72 | 0 | 0 | 0 | 0 | 0 | -0.72 | -0.72 |  |  |  | 86 | R. Zhuravka | 2.5 | 0.08 | 0.8 | 0 | 0 | 0.8 | 0 | 0 | -0.8 | -0.8 | 35/10
89 | Gorokhovka | 2.5 | 0.55 | 1.5 | 45 | 1.5 | 0 | 1.5 | 0.95 | 0.95 |  |  |  | 87 | Gorokhovka | 2.5 | 0.11 | 0.66 | 1.5 | 45 | -0.84 | 0 | 1.5 | 0.84 | 0.84 | 35/10
90 | Livenka | 2.5 | 0.42 | 0.5 | 1 сутки | 0.5 | 0 | 0.5 | 0.08 | 0.08 |  |  |  | 88 | Livenka | 2.5 | 0.05 | 0.47 | 0.5 | 1 сутки | -0.03 | 0 | 0.5 | 0.03 | 0.03 | 35/10
91 | R.Buylovka | 2.5 | 0.5 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1 | 1 |  |  |  | 89 | R.Buylovka | 2.5 | 0.06 | 0.56 | 1.5 | 45 | -0.94 | 0 | 1.5 | 0.94 | 0.94 | 35/10
92 | Shurinovka | 2.5 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 |  |  |  | 90 | Shurinovka | 2.5 | 0.03 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | 35/10
93 | Tvyordokhlebovka | 4 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  |  | 91 | Tvyordokhlebovka | 4 | 0.05 | 0.34 | 0 | 0 | 0.34 | 0 | 0 | -0.34 | -0.34 | 35/10
94 | Krinitsa | 2.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | -0.12 | -0.12 |  |  |  | 92 | Krinitsa | 2.5 | 0.05 | 0.17 | 0 | 0 | 0.17 | 0 | 0 | -0.17 | -0.17 | 35/10
95 | Krasnogorovka | 2.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | -0.12 | -0.12 |  |  |  | 93 | Krasnogorovka | 2.5 | 0.01 | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | 35/10
96 | Двух- и более трансформаторные ПС | [12 empty] | 2: Двух- и более трансформаторные ПС
97 | СЭС | [12 empty] | 2: СЭС
98 | No. 2 | 25+25 | 22.86 | 2.94 | 120 | 19.92 | 0 | 26.25 | 6.33 | 6.33 |  | 1.05 | 25 | 94 | No. 2 | 25+25 | 4.87 | 27.73 | 2.94 | 120 | 24.79 | 0 | 26.25 | 1.46 | 1.46 | 110/6
99 | No.3 | 6,3 + 10 | 9.41 | 2.5 | 120 | 6.91 | 0 | 6.615 | -0.295 | -0.295 |  | 1.05 | 6.3 | 95 | No.3 | 6,3 + 10 | 0.13 | 9.54 | 2.5 | 120 | 7.04 | 0 | 6.615 | -0.425 | -0.425 | 35/6
100 | No. 4 | 10+10+15 | 15.86 | 0 | 0 | 15.86 | 0 | 21 | 5.14 | 5.14 |  | 1.05 | 20 | 96 | No. 4 | 10+10+15 | 0.09 | 15.95 | 0 | 0 | 15.95 | 0 | 21 | 5.05 | 5.05 | 35/6
101 | No. 6 | 25+32 | 15.82 | 1.6 | 120 | 14.22 | 0 | 26.25 | 12.03 | 12.03 |  | 1.05 | 25 | 97 | No. 6 | 25+32 | 4.21 | 20.03 | 1.6 | 120 | 18.43 | 0 | 26.25 | 7.82 | 7.82 | 110/6
102 | No. 7 | 2,5+4 | 0.72 | 2.5 | 0 | -1.78 | 0 | 2.625 | 4.405 | 4.405 |  | 1.05 | 2.5 | 98 | No. 7 | 2,5+4 | 2.22 | 2.94 | 2.5 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | 35/10/6
103 | No. 8 | 4+4+4 | 6.11 | 0 | 0 | 6.11 | 0 | 8.4 | 2.29 | 2.29 |  | 1.05 | 8 | 99 | No. 8 | 4+4+4 | 1.91 | 8.02 | 0 | 0 | 8.02 | 0 | 8.4 | 0.38 | 0.38 | 35/6
104 | No. 9 | 40+40 | 21.99 | 3.3 | 120 | 18.69 | 0 | 42 | 23.31 | 23.31 |  | 1.05 | 40 | 100 | No. 9 | 40+40 | 1.92 | 23.91 | 3.3 | 120 | 20.61 | 0 | 42 | 21.39 | 21.39 | 110/6
105 | No. 10 | 63+63 | 31.86 | 13.3 | 120 | 18.56 | 0 | 66.15 | 47.59 | 47.59 |  | 1.05 | 63 | 101 | No. 10 | 63+63 | 15.3 | 47.16 | 13.3 | 120 | 33.86 | 0 | 66.15 | 32.29 | 32.29 | 35/6
106 | No. 13 | 6,3+6,3 | 9.47 | 3.7 | 120 | 5.77 | 0 | 6.615 | 0.845 | 0.845 |  | 1.05 | 6.3 | 102 | No. 13 | 6,3+6,3 | 5.09 | 14.56 | 3.7 | 120 | 10.86 | 0 | 6.615 | -4.245 | -4.245 | 35/10
107 | No. 14 | 31,5+31,5 | 12.75 | 1.3 | 120 | 11.45 | 0 | 33.075 | 21.625 | 21.625 |  | 1.05 | 31.5 | 103 | No. 14 | 31,5+31,5 | 3.36 | 16.11 | 1.3 | 120 | 14.81 | 0 | 33.075 | 18.265 | 18.265
| Sн. MV, МVА | 31,5+31,5 |  | 0 | 0 | 0 | 0 | 33.075 | 33.075 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 0 | 0 | 0 | 0 | 0 | 33.075 | 33.075 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5 | 12.75 | 1.3 | 120 | 11.45 | 0 | 33.075 | 21.625 |  |  | 1.05 | 31.5 |  | Sн. LV, МVА | 31,5+31,5 | 3.36 | 16.11 | 1.3 | 120 | 14.81 | 0 | 33.075 | 18.265
108 | No. 15 | 40,5+40,5+63,0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 | 85.05 |  | 1.05 | 81 | 104 | No. 15 | 40,5+40,5+63,0 | 0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 | 85.05
| Sн. MV, МVА | 40,5+40,5+63,0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 |  |  | 1.05 | 81 |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  | 1.05 | 81 |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05
109 | No. 16 | 31,5+31,5+40,0 | 59.48 | 4 | 120 | 55.48 | 0 | 66.15 | 10.67 | 10.67 |  | 1.05 | 63 | 105 | No. 16 | 31,5+31,5+40,0 | 17.07 | 76.55 | 4 | 120 | 72.55 | 0 | 66.15 | -6.4 | -6.4
| Sн. MV, МVА | 31,5+31,5 | 4.5 | 0 | 0 | 4.5 | 0 | 33.075 | 28.575 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 4.5 | 0 | 0 | 4.5 | 0 | 33.075 | 28.575 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5+40,0 | 54.98 | 4 | 120 | 50.98 | 0 | 66.15 | 15.17 |  |  | 1.05 | 63 |  | Sн. LV, МVА | 31,5+31,5+40,0 | 17.07 | 72.05 | 4 | 120 | 68.05 | 0 | 66.15 | -1.9
110 | No. 18 | 6,3+6,3 | 2.81 | 0 | 0 | 2.81 | 0 | 6.615 | 3.805 | 3.805 |  | 1.05 | 6.3 | 106 | No. 18 | 6,3+6,3 | 1.73 | 4.54 | 0 | 0 | 4.54 | 0 | 6.615 | 2.075 | 2.075 | 110/10
111 | No. 20 | 25+25 | 22.03 | 9.6 | 120 | 12.43 | 0 | 26.25 | 13.82 | 13.82 |  | 1.05 | 25 | 107 | No. 20 | 25+25 | 10.49 | 32.52 | 9.6 | 120 | 22.92 | 0 | 26.25 | 3.33 | 3.33
| Sн. MV, МVА | 25+25 | 7.55 | 4 | 0 | 3.55 | 0 | 26.25 | 22.7 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 7.55 | 4 | 0 | 3.55 | 0 | 26.25 | 22.7 |  | 110/10/6
| Sн. LV, МVА | 25+25 | 14.48 | 5.6 | 120 | 8.88 | 0 | 26.25 | 17.37 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 10.49 | 24.97 | 5.6 | 120 | 19.37 | 0 | 26.25 | 6.88
112 | No. 21 | 25,0+20,0+40,0 | 42.3 | 4.6 | 120 | 37.7 | 0 | 47.25 | 9.55 | 9.55 |  | 1.05 | 45 | 108 | No. 21 | 25,0+20,0+40,0 | 6.49 | 48.79 | 4.6 | 180 | 44.19 | 0 | 49.6125 | 5.4225 | 5.4225 | 110/35/6
113 | No. 23 | 7,5+6,3 | 6.46 | 0.8 | 120 | 5.66 | 0 | 6.615 | 0.955 | 0.955 |  | 1.05 | 6.3 | 110 | No. 23 | 7,5+6,3 | 0 | 6.46 | 0.8 | 120 | 5.66 | 0 | 6.615 | 0.955 | 0.955 | 35/6
114 | No. 24 | 3,2+4,0 | 1.75 | 0 | 0 | 1.75 | 0 | 3.36 | 1.61 | 1.61 |  | 1.05 | 3.2 | 111 | No. 24 | 3,2+4,0 | 0.04 | 1.79 | 0 | 0 | 1.79 | 0 | 3.36 | 1.57 | 1.57 | 35/6
115 | No. 25 | 40+40+40 | 45.58 | 3.8 | 120 | 41.78 | 0 | 84 | 42.22 | 42.22 |  | 1.05 | 80 | 112 | No. 25 | 40+40+40 | 5.28 | 50.86 | 3.8 | 120 | 47.06 | 0 | 84 | 36.94 | 36.94 | 110/6
116 | No. 27 | 32,0+32,0+63,0 | 44.43 | 3.3 | 180 | 41.13 | 0 | 67.2 | 26.07 | 26.07 |  | 1.05 | 64 | 113 | No. 27 | 32,0+32,0+63,0 | 24.07 | 68.5 | 3.3 | 180 | 65.2 | 0 | 67.2 | 2 | 2 | 110/6
117 | No. 28 | 10+10 | 14.23 | 0 | 0 | 14.23 | 0 | 10.5 | -3.73 | -3.73 |  | 1.05 | 10 | 114 | No. 28 | 10+10 | 1.58 | 15.81 | 0 | 0 | 15.81 | 0 | 10.5 | -5.31 | -5.31 | 110/10
118 | No.29 | 25+25 | 27.87 | 8.4 | 120 | 19.47 | 0 | 26.25 | 6.78 | 6.78 |  | 1.05 | 25 | 115 | No.29 | 25+25 | 5.91 | 33.78 | 5.1 | 120 | 28.68 | 0 | 26.25 | -2.43 | -2.43
| Sн. MV, МVА | 25+25 | 10.54 | 4.2 | 120 | 6.34 | 0 | 26.25 | 19.91 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 10.54 | 4.02 | 120 | 6.52 | 0 | 26.25 | 19.73 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 17.33 | 4.2 | 120 | 13.13 | 0 | 26.25 | 13.12 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 5.91 | 23.24 | 1.09 | 120 | 22.15 | 0 | 26.25 | 4.1
119 | No. 30 | 40+40+63 | 67.69 | 5.1 | 120 | 62.59 | 0 | 108.15 | 45.56 | 30.34 |  | 1.05 | 103 | 116 | No. 30 | 40+40+63 | 15.79 | 83.48 | 5.1 | 120 | 78.38 | 0 | 108.15 | 29.77 | 29.77
| Sн. MV, МVА | 40+40 | 11.66 | 0 | 0 | 11.66 | 0 | 42 | 30.34 |  |  | 1.05 | 40 |  | Sн. MV, МVА | 40+40 | 0 | 11.66 | 0 | 0 | 11.66 | 0 | 42 | 30.34 |  | 110/35/10
| Sн. LV, МVА | 40+40+63 | 56.03 | 5.1 | 120 | 50.93 | 0 | 108.15 | 57.22 |  |  | 1.05 | 103 |  | Sн. LV, МVА | 40+40+63 | 15.79 | 71.82 | 5.1 | 120 | 66.72 | 0 | 108.15 | 41.43
120 | No. 32 | 25+25 | 8.16 | 8 | 120 | 0.16 | 0 | 26.25 | 26.09 | 23.39 |  | 1.05 | 25 | 117 | No. 32 | 25+25 | 20.4 | 28.56 | 8 | 120 | 20.56 | 0 | 26.25 | 5.69 | 2.99
| Sн. MV, МVА | 25+25 | 5.3 | 8 | 120 | -2.7 | 0 | 26.25 | 28.95 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 5.3 | 8 | 120 | -2.7 | 0 | 26.25 | 28.95 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 2.86 | 0 | 0 | 2.86 | 0 | 26.25 | 23.39 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 20.4 | 23.26 | 0 | 0 | 23.26 | 0 | 26.25 | 2.99
121 | No. 33 | 4,0+4,0 | 3.8 | 0 | 0 | 3.8 | 0 | 4.2 | 0.4 | 0.4 |  | 1.05 | 4 | 118 | No. 33 | 4,0+4,0 | 1.98 | 5.78 | 0 | 0 | 5.78 | 0 | 4.2 | -1.58 | -1.58 | 35/10
122 | No. 34 | 2,5+1,8 | 2.09 | 0 | 0 | 2.09 | 0 | 1.89 | -0.2 | -0.2 |  | 1.05 | 1.8 | 119 | No. 34 | 2,5+1,8 | 0.35 | 2.44 | 0 | 0 | 2.44 | 0 | 1.89 | -0.55 | -0.55 | 35/6
123 | No.35 | 10+10 | 12.27 | 2.4 | 120 | 9.87 | 0 | 10.5 | 0.63 | 0.63 |  | 1.05 | 10 | 120 | No.35 | 10+10 | 1.4 | 13.67 | 2.4 | 120 | 11.27 | 0 | 10.5 | -0.77 | -0.77 | 35/6
124 | No. 36 | 25+25 | 3.81 | 0 | 0 | 3.81 | 0 | 26.25 | 22.44 | 22.44 |  | 1.05 | 25 | 121 | No. 36 | 25+25 | 6.6 | 10.41 | 0 | 0 | 10.41 | 0 | 26.25 | 15.84 | 15.84 | 110/35/10
125 | No. 39 | 25+25 | 26.38 | 7.08 | 120 | 19.3 | 0 | 26.25 | 6.95 | 6.95 |  | 1.05 | 25 | 122 | No. 39 | 25+25 | 5.07 | 31.45 | 7.08 | 120 | 24.37 | 0 | 26.25 | 1.88 | 1.88 | 110/6
126 | No. 41 | 10+10 | 8.58 | 0 | 0 | 8.58 | 0 | 10.5 | 1.92 | 1.92 |  | 1.05 | 10 | 123 | No. 41 | 10+10 | 0.18 | 8.76 | 0 | 0 | 8.76 | 0 | 10.5 | 1.74 | 1.74 | 35/6
127 | No. 42 | 25+40 | 18.46 | 1.6 | 120 | 16.86 | 0 | 26.25 | 9.39 | 9.39 |  | 1.05 | 25 | 124 | No. 42 | 25+40 | 7.65 | 26.11 | 1.6 | 120 | 24.51 | 0 | 26.25 | 1.74 | 1.74 | 110/6
128 | No. 43 | 63+25 | 15.69 | 1.6 | 60 | 14.09 | 0 | 26.25 | 12.16 | 12.16 |  | 1.05 | 25 | 125 | No. 43 | 63+25 | 5.46 | 21.15 | 1.6 | 60 | 19.55 | 0 | 26.25 | 6.7 | 6.7 | 110/6
129 | No. 45 | 63+63 | 44.43 | 7.1 | 120 | 37.33 | 0 | 66.15 | 28.82 | 28.82 |  | 1.05 | 63 | 126 | No. 45 | 63+63 | 22.44 | 66.87 | 7.1 | 120 | 59.77 | 0 | 66.15 | 6.38 | 6.38 | 110/6
130 | No. 47 | 25+25 | 12.35 | 0 | 0 | 12.35 | 0 | 26.25 | 13.9 | 13.9 |  | 1.05 | 25 | 127 | No. 47 | 25+25 | 1.92 | 14.27 | 0 | 0 | 14.27 | 0 | 26.25 | 11.98 | 11.98
| Sн. MV, МVА | 25+25 | 5.17 | 0 | 0 | 5.17 | 0 | 26.25 | 21.08 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 5.17 | 0 | 0 | 5.17 | 0 | 26.25 | 21.08 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 7.23 | 0 | 0 | 7.23 | 0 | 26.25 | 19.02 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 1.92 | 9.15 | 0 | 0 | 9.15 | 0 | 26.25 | 17.1
131 | Panino | 16+16 | 10.99 | 5.2 | 120 | 5.79 | 0 | 16.8 | 11.01 | 11.01 |  | 1.05 | 16 | 128 | Panino | 16+16 | 2.38 | 13.37 | 5.2 | 120 | 8.17 | 0 | 16.8 | 8.63 | 8.63
| Sн. MV, МVА | 16+16 | 5.07 | 5 | 120 | 0.07 | 0 | 16.8 | 16.73 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 5.07 | 5 | 120 | 0.07 | 0 | 16.8 | 16.73 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.92 | 0.2 | 120 | 5.72 | 0 | 16.8 | 11.08 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.38 | 8.3 | 0.2 | 120 | 8.1 | 0 | 16.8 | 8.7
132 | Kriusha | 2,5+2,5 | 0.33 | 0 | 0 | 0.33 | 0 | 2.625 | 2.295 | 2.295 |  | 1.05 | 2.5 | 129 | Kriusha | 2,5+2,5 | 0.13 | 0.46 | 0 | 0 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | 35/10
133 | Seed plant | 4+4 | 1.76 | 0 | 0 | 1.76 | 0 | 4.2 | 2.44 | 2.44 |  | 1.05 | 4 | 130 | Seed plant | 4+4 | 0.07 | 1.83 | 0 | 0 | 1.83 | 0 | 4.2 | 2.37 | 2.37 | 35/10
134 | Progress | 2,5+10 | 0.53 | 0.5315 | 120 | -0.0015 | 0 | 2.625 | 2.6265 | 2.6265 |  | 1.05 | 2.5 | 131 | Progress | 2,5+10 | 0.01 | 0.54 | 0.5315 | 120 | 0.0085 | 0 | 2.625 | 2.6165 | 2.6165 | 110/35/10
135 | Katukhovka | 2,5+2,5 | 0.36 | 0.385 | 120 | -0.025 | 0 | 2.625 | 2.65 | 2.65 |  | 1.05 | 2.5 | 132 | Katukhovka | 2,5+2,5 | 0.02 | 0.38 | 0.385 | 120 | -0.005 | 0 | 2.625 | 2.63 | 2.63 | 35/10
136 | Kr.Liman | 2,5+4,0 | 0.76 | 0 | 0 | 0.76 | 0 | 2.625 | 1.865 | 1.865 |  | 1.05 | 2.5 | 133 | Kr.Liman | 2,5+4,0 | 0.02 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | 35/10
137 | Ivanovka | 1,8+1,6 | 0.2 | 0.36 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 |  | 1.05 | 1.6 | 134 | Ivanovka | 1,8+1,6 | 0.09 | 0.29 | 0.36 | 120 | -0.07 | 0 | 1.68 | 1.75 | 1.75 | 35/10
138 | Don | 2,5+2,5 | 2.82 | 0 | 0 | 2.82 | 0 | 2.625 | -0.195 | -0.195 |  | 1.05 | 2.5 | 135 | Don | 2,5+2,5 | 1.59 | 4.41 | 0 | 0 | 4.41 | 0 | 2.625 | -1.785 | -1.785 | 35/10
139 | Yablochnoe | 4+4 | 0.36 | 0 | 0 | 0.36 | 0 | 4.2 | 3.84 | 3.84 |  | 1.05 | 4 | 136 | Yablochnoe | 4+4 | 0.09 | 0.45 | 0 | 0 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | 35/10
140 | St.Nikolskoe | 2,5+2,5 | 0.76 | 1.227 | 120 | -0.467 | 0 | 2.625 | 3.092 | 3.092 |  | 1.05 | 2.5 | 137 | St.Nikolskoe | 2,5+2,5 | 0.36 | 1.12 | 1.227 | 120 | -0.107 | 0 | 2.625 | 2.732 | 2.732 | 35/10
141 | Rudkino | 4,0+4,0 | 2.2 | 0 | 0 | 2.2 | 0 | 4.2 | 2 | 2 |  | 1.05 | 4 | 138 | Rudkino | 4,0+4,0 | 0.37 | 2.57 | 0 | 0 | 2.57 | 0 | 4.2 | 1.63 | 1.63 | 35/10
142 | Khokhol-1 | 6,3+6,3 | 3.82 | 0 | 0 | 3.82 | 0 | 6.615 | 2.795 | 2.795 |  | 1.05 | 6.3 | 139 | Khokhol-1 | 6,3+6,3 | 0.86 | 4.68 | 0 | 0 | 4.68 | 0 | 6.615 | 1.935 | 1.935 | 35/6
143 | No. 11 | 5,6+6,3 | 3.22 | 0.5 | 120 | 2.72 | 0 | 5.88 | 3.16 | 3.16 |  | 1.05 | 5.6 | 140 | No. 11 | 5,6+6,3 | 0 | 3.22 | 0.5 | 120 | 2.72 | 0 | 5.88 | 3.16 | 3.16
| Sн. MV, МVА | 5,6+6,3 | 0.53 | 0.5 | 120 | 0.03 | 0 | 5.88 | 5.85 |  |  | 1.05 | 5.6 |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.53 | 0.5 | 120 | 0.03 | 0 | 5.88 | 5.85 |  | 110/35/6
| Sн. LV, МVА | 5,6+6,3 | 2.69 | 0 | 0 | 2.69 | 0 | 5.88 | 3.19 |  |  | 1.05 | 5.6 |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.69 | 0 | 0 | 2.69 | 0 | 5.88 | 3.19
144 | Beryozovka | 4+4 | 4.15 | 0 | 0 | 4.15 | 0 | 4.2 | 0.05 | 0.05 |  | 1.05 | 4 | 141 | Beryozovka | 4+4 | 1.12 | 5.27 | 0 | 0 | 5.27 | 0 | 4.2 | -1.07 | -1.07 | 35/10
145 | N.Zhivotinnoe | 6,3+6,3 | 4.84 | 1 | 120 | 3.84 | 0 | 6.615 | 2.775 | 2.775 |  | 1.05 | 6.3 | 142 | N.Zhivotinnoe | 6,3+6,3 | 5.77 | 10.61 | 1 | 120 | 9.61 | 0 | 6.615 | -2.995 | -2.995 | 35/10
146 | Ramon-1 | 4+4+4 | 4.58 | 6.85 | 120 | -2.27 | 0 | 8.4 | 10.67 | 10.67 |  | 1.05 | 8 | 143 | Ramon-1 | 4+4+4 | 0.79 | 5.37 | 6.85 | 120 | -1.48 | 0 | 8.4 | 9.88 | 9.88 | 35/10/6
147 | Ramon-2 | 16,0+16,0 | 20.17 | 10.48 | 120 | 9.69 | 0 | 16.8 | 7.11 | 7.11 |  | 1.05 | 16 | 144 | Ramon-2 | 16,0+16,0 | 0.74 | 20.91 | 10.48 | 120 | 10.43 | 0 | 16.8 | 6.37 | 6.37
| Sн. MV, МVА | 16,0+16,0 | 16.21 | 6.85 | 0 | 9.36 | 0 | 16.8 | 7.44 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 16.21 | 6.85 | 0 | 9.36 | 0 | 16.8 | 7.44 |  | 110/35/10
| Sн. LV, МVА | 16,0+16,0 | 3.96 | 3.63 | 120 | 0.33 | 0 | 16.8 | 16.47 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.74 | 4.7 | 3.63 | 120 | 1.07 | 0 | 16.8 | 15.73
148 | Vereyka | 2,5+2,5 | 1.11 | 0 | 0 | 1.11 | 0 | 2.625 | 1.515 | 1.515 |  | 1.05 | 2.5 | 145 | Vereyka | 2,5+2,5 | 0.01 | 1.12 | 0 | 0 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | 35/10
149 | Complex | 10+10 | 5.19 | 3.4 | 180 | 1.79 | 0 | 10.5 | 8.71 | 8.09 |  | 1.05 | 10 | 146 | Complex | 10+10 | 0 | 5.19 | 3.4 | 180 | 1.79 | 0 | 10.5 | 8.71 | 8.09
| Sн. MV, МVА | 10+10 | 2.48 | 3.1 | 180 | -0.62 | 0 | 10.5 | 11.12 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.48 | 3.1 | 180 | -0.62 | 0 | 10.5 | 11.12 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.71 | 0.3 | 180 | 2.41 | 0 | 10.5 | 8.09 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0 | 2.71 | 0.3 | 180 | 2.41 | 0 | 10.5 | 8.09
150 | N.Veduga | 16+16 | 3.3 | 2.9 | 120 | 0.4 | 0 | 16.8 | 16.4 | 15.68 |  | 1.05 | 16 | 147 | N.Veduga | 16+16 | 0 | 3.3 | 2.9 | 120 | 0.4 | 0 | 16.8 | 16.4 | 15.68
| Sн. MV, МVА | 16+16 | 2.18 | 2.9 | 120 | -0.72 | 0 | 16.8 | 17.52 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 2.18 | 2.9 | 120 | -0.72 | 0 | 16.8 | 17.52 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.12 | 0 | 0 | 1.12 | 0 | 16.8 | 15.68 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0 | 1.12 | 0 | 0 | 1.12 | 0 | 16.8 | 15.68
151 | Golosnovka | 2,5+2,5 | 0.45 | 0.512 | 120 | -0.062 | 0 | 2.625 | 2.687 | 2.687 |  | 1.05 | 2.5 | 148 | Golosnovka | 2,5+2,5 | 0.02 | 0.47 | 0.512 | 120 | -0.042 | 0 | 2.625 | 2.667 | 2.667 | 35/10
152 | Medvezhye | 3,2+4,0 | 1.09 | 0 | 0 | 1.09 | 0 | 3.36 | 2.27 | 2.27 |  | 1.05 | 3.2 | 149 | Medvezhye | 3,2+4,0 | 0.11 | 1.2 | 0 | 0 | 1.2 | 0 | 3.36 | 2.16 | 2.16 | 35/10
153 | St.Veduga | 4+4 | 0.93 | 0 | 0 | 0.93 | 0 | 4.2 | 3.27 | 3.27 |  | 1.05 | 4 | 150 | St.Veduga | 4+4 | 0.03 | 0.96 | 0 | 0 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | 35/10
154 | M.Pokrovka | 2,5+2,5 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 |  | 1.05 | 2.5 | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | 35/10
155 | V.Turovo-2 | 2,5+2,5 | 0.71 | 0.7 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 |  | 1.05 | 2.5 | 152 | V.Turovo-2 | 2,5+2,5 | 0.28 | 0.99 | 0.7 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | 35/10
156 | S.Lipyagi | 3,2+2,5 | 1.53 | 2.9638 | 120 | -1.4338 | 0 | 2.625 | 4.0588 | 4.0588 |  | 1.05 | 2.5 | 153 | S.Lipyagi | 3,2+2,5 | 1.92 | 3.45 | 2.9638 | 120 | 0.4862 | 0 | 2.625 | 2.1388 | 2.1388 | 35/10
157 | N.Devitsk | 25+16 | 7.14 | 8.2225 | 180 | -1.0825 | 0 | 16.8 | 17.8825 | 15.81 |  | 1.05 | 16 | 154 | N.Devitsk | 25+16 | 1.1 | 8.24 | 8.2225 | 180 | 0.0175 | 0 | 16.8 | 16.7825 | 15.81
| Sн. MV, МVА | 25+16 | 3.79 | 2.8 | 180 | 0.99 | 0 | 16.8 | 15.81 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 25+16 | 0 | 3.79 | 2.8 | 180 | 0.99 | 0 | 16.8 | 15.81 |  | 110/35/10
| Sн. LV, МVА | 25+16 | 3.35 | 5.393 | 180 | -2.043 | 0 | 16.8 | 18.843 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 25+16 | 1.1 | 4.45 | 5.393 | 180 | -0.943 | 0 | 16.8 | 17.743
158 | Repyevka | 4+4 | 2.53 | 0.5 | 120 | 2.03 | 0 | 4.2 | 2.17 | 2.17 |  | 1.05 | 4 | 155 | Repyevka | 4+4 | 0.12 | 2.65 | 0.5 | 120 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | 35/10
159 | Krasnolipye | 16+16 | 11.07 | 2.9 | 120 | 8.17 | 0 | 16.8 | 8.63 | 8.63 |  | 1.05 | 16 | 156 | Krasnolipye | 16+16 | 0.25 | 11.32 | 2.9 | 120 | 8.42 | 0 | 16.8 | 8.38 | 8.38
| Sн. MV, МVА | 16+16 | 9.73 | 2.7 | 120 | 7.03 | 0 | 16.8 | 9.77 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 9.73 | 2.7 | 120 | 7.03 | 0 | 16.8 | 9.77 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.34 | 0.2 | 120 | 1.14 | 0 | 16.8 | 15.66 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.25 | 1.59 | 0.2 | 120 | 1.39 | 0 | 16.8 | 15.41
160 | Ulyanovka | 6,3+6,3 | 0.44 | 0.04 | 60 | 0.4 | 0 | 6.615 | 6.215 | 6.215 |  | 1.05 | 6.3 | 157 | Ulyanovka | 6,3+6,3 | 0.11 | 0.55 | 0.04 | 60 | 0.51 | 0 | 6.615 | 6.105 | 6.105 | 110/10
161 | МОB | 4+2,5 | 1.39 | 0.6 | 60 | 0.79 | 0 | 2.625 | 1.835 | 1.835 |  | 1.05 | 2.5 | 158 | МОB | 4+2,5 | 0.21 | 1.6 | 0.6 | 60 | 1 | 0 | 2.625 | 1.625 | 1.625 | 35/10
162 | L.Rossosh | 6,3+6,3 | 6.26 | 0 | 0 | 6.26 | 0 | 6.615 | 0.355 | 0.355 |  | 1.05 | 6.3 | 159 | L.Rossosh | 6,3+6,3 | 1.34 | 7.6 | 0 | 0 | 7.6 | 0 | 6.615 | -0.985 | -0.985 | 35/10
163 | Kashirskoe | 2,5+2,5 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 |  | 1.05 | 2.5 | 160 | Kashirskoe | 2,5+2,5 | 0.05 | 0.74 | 0 | 0 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | 35/10
164 | Zaprudskoe | 2,5+2,5 | 1.67 | 0 | 0 | 1.67 | 0 | 2.625 | 0.955 | 0.955 |  | 1.05 | 2.5 | 161 | Zaprudskoe | 2,5+2,5 | 0.31 | 1.98 | 0 | 0 | 1.98 | 0 | 2.625 | 0.645 | 0.645 | 35/10
165 | Moskovskoe | 10+10 | 9.96 | 1.8 | 120 | 8.16 | 0 | 10.5 | 2.34 | 1.44 |  | 1.05 | 10 | 162 | Moskovskoe | 10+10 | 0.19 | 10.15 | 1.8 | 120 | 8.35 | 0 | 10.5 | 2.15 | 1.44
| Sн. MV, МVА | 10+10 | 9.06 | 0 | 0 | 9.06 | 0 | 10.5 | 1.44 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 9.06 | 0 | 0 | 9.06 | 0 | 10.5 | 1.44 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.9 | 1.8 | 120 | -0.9 | 0 | 10.5 | 11.4 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.19 | 1.09 | 1.8 | 120 | -0.71 | 0 | 10.5 | 11.21
166 | SemenovkaSPS | 2,5+4,0 | 2.04 | 0 | 0 | 2.04 | 0 | 2.625 | 0.585 | 0.585 |  | 1.05 | 2.5 | 163 | SemenovkaSPS | 2,5+4,0 | 0.01 | 2.05 | 0 | 0 | 2.05 | 0 | 2.625 | 0.575 | 0.575 | 35/10
167 | N. Baygora | 2,5+2,5 | 0.82 | 1.03 | 60 | -0.21 | 0 | 2.625 | 2.835 | 2.835 |  | 1.05 | 2.5 | 164 | N. Baygora | 2,5+2,5 | 0.02 | 0.84 | 1.03 | 60 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | 35/10
168 | Shukavka | 2,5+2,5 | 0.78 | 0.1 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 |  | 1.05 | 2.5 | 165 | Shukavka | 2,5+2,5 | 0.03 | 0.81 | 0.1 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | 35/10
169 | Uglyanets | 4+2,5 | 2.36 | 0.8 | 120 | 1.56 | 0 | 2.625 | 1.065 | 1.065 |  | 1.05 | 2.5 | 166 | Uglyanets | 4+2,5 | 3.68 | 6.04 | 0.8 | 120 | 5.24 | 0 | 2.625 | -2.615 | -2.615 | 35/10
170 | V.Khava | 16+16 | 14.73 | 0.4 | 120 | 14.33 | 0 | 16.8 | 2.47 | 2.47 |  | 1.05 | 16 | 167 | V.Khava | 16+16 | 2.98 | 17.71 | 0.4 | 120 | 17.31 | 0 | 16.8 | -0.51 | -0.51
| Sн. MV, МVА | 16+16 | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 8.86 | 0.4 | 120 | 8.46 | 0 | 16.8 | 8.34 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.98 | 11.84 | 0.4 | 120 | 11.44 | 0 | 16.8 | 5.36
171 | Usman-1 | 25+25 | 11.43 | 0 | 0 | 11.43 | 0 | 26.25 | 14.82 | 14.82 |  | 1.05 | 25 | 168 | Usman-1 | 25+25 | 2.7 | 14.13 | 0 | 0 | 14.13 | 0 | 26.25 | 12.12 | 12.12 | 35/10
172 | Usman-2 | 10+6,3 | 10.56 | 0 | 0 | 10.56 | 0 | 6.615 | -3.945 | -3.945 |  | 1.05 | 6.3 | 169 | Usman-2 | 10+6,3 | 4.29 | 14.85 | 0 | 0 | 14.85 | 0 | 6.615 | -8.235 | -8.235 | 35/10
173 | R.Khava | 4+4 | 3.62 | 0.2 | 120 | 3.42 | 0 | 4.2 | 0.78 | 0.78 |  | 1.05 | 4 | 170 | R.Khava | 4+4 | 0.08 | 3.7 | 0.2 | 120 | 3.5 | 0 | 4.2 | 0.7 | 0.7 | 35/10
174 | No. 31 | 16+25 | 23.02 | 5.6 | 120 | 17.42 | 0 | 16.8 | -0.62 | -0.62 |  | 1.05 | 16 | 171 | No. 31 | 16+25 | 1.17 | 24.19 | 5.6 | 120 | 18.59 | 0 | 16.8 | -1.79 | -1.79
| Sн. MV, МVА | 16+25 | 13.67 | 5.6 | 120 | 8.07 | 0 | 16.8 | 8.73 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+25 | 0 | 13.67 | 5.6 | 120 | 8.07 | 0 | 16.8 | 8.73 |  | 110/35/10
| Sн. LV, МVА | 16+25 | 9.35 | 0 | 0 | 9.35 | 0 | 16.8 | 7.45 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+25 | 1.17 | 10.52 | 0 | 0 | 10.52 | 0 | 16.8 | 6.28
175 | Maslovka | 4+4 | 4.02 | 0 | 0 | 4.02 | 0 | 4.2 | 0.18 | 0.18 |  | 1.05 | 4 | 172 | Maslovka | 4+4 | 1.59 | 5.61 | 0 | 0 | 5.61 | 0 | 4.2 | -1.41 | -1.41 | 35/10
| ЛЭС | [12 empty] | 2: ЛЭС
176 | Podgornaya - district Line Maintenance Service | 16+16 | 4.11 | 1.6 | 180 | 2.51 | 0 | 16.8 | 14.29 | 13.24 |  | 1.05 | 16 | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 2.69 | 6.8 | 1.6 | 180 | 5.2 | 0 | 16.8 | 11.6 | 10.55
| Sн. MV, МVА | 16+16 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 4.11 | 0.55 | 180 | 3.56 | 0 | 16.8 | 13.24 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.69 | 6.8 | 0.55 | 180 | 6.25 | 0 | 16.8 | 10.55
177 | Kantemirovka | 10+10 | 9.57 | 1.6 | 60 | 7.97 | 0 | 10.5 | 2.53 | 2.53 |  | 1.05 | 10 | 174 | Kantemirovka | 10+10 | 0.52 | 10.09 | 1.6 | 60 | 8.49 | 0 | 10.5 | 2.01 | 2.01
| Sн. СН, МВА | 10+10 | 5.88 | 1.4 | 60 | 4.48 | 0 | 10.5 | 6.02 |  |  | 1.05 | 10 |  | Sн. СН, МВА | 10+10 | 0 | 5.88 | 1.4 | 60 | 4.48 | 0 | 10.5 | 6.02 |  | 110/35/10
| Sн. НН, МВА | 10+10 | 3.69 | 0.2 | 60 | 3.49 | 0 | 10.5 | 7.01 |  |  | 1.05 | 10 |  | Sн. НН, МВА | 10+10 | 0.52 | 4.21 | 0.2 | 60 | 4.01 | 0 | 10.5 | 6.49
178 | Rossosh | 16+16+40 | 24.2 | 2.68 | 120 | 21.52 | 0 | 33.6 | 12.08 | 12.08 |  | 1.05 | 32 | 175 | Rossosh | 16+16+40 | 1.56 | 25.76 | 2.68 | 120 | 23.08 | 0 | 33.6 | 10.52 | 10.52
| Sн. MV, МVА | 16+16+40 | 4 | 1.9 | 120 | 2.1 | 0 | 33.6 | 31.5 |  |  | 1.05 | 32 |  | Sн. MV, МVА | 16+16+40 | 0 | 4 | 1.9 | 120 | 2.1 | 0 | 33.6 | 31.5 |  | 110/35/10/6
| Sн. LV, МVА | 16+16+40 | 20.2 | 0.78 | 120 | 19.42 | 0 | 33.6 | 14.18 |  |  | 1.05 | 32 |  | Sн. LV, МVА | 16+16+40 | 1.56 | 21.76 | 0.78 | 120 | 20.98 | 0 | 33.6 | 12.62
179 | Kamenka r-naya LPS | 16+16 | 3.75 | 0.97 | 120 | 2.78 | 0 | 16.8 | 14.02 | 14.02 |  | 1.05 | 16 | 176 | Kamenka r-naya LPS | 16+16 | 1.08 | 4.83 | 0.97 | 120 | 3.86 | 0 | 16.8 | 12.94 | 12.94
| Sн. MV, МVА | 16+16 | 0.67 | 0 | 120 | 0.67 | 0 | 16.8 | 16.13 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0.03 | 0.7 | 0 | 120 | 0.7 | 0 | 16.8 | 16.1 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 3.08 | 0.97 | 120 | 2.11 | 0 | 16.8 | 14.69 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 1.05 | 4.13 | 0.97 | 120 | 3.16 | 0 | 16.8 | 13.64
180 | Korotoyak | 6,3+10 | 3.77 | 0.47 | 180 | 3.3 | 0 | 6.615 | 3.315 | 3.315 |  | 1.05 | 6.3 | 177 | Korotoyak | 6,3+10 | 0.72 | 4.49 | 0.47 | 180 | 4.02 | 0 | 6.615 | 2.595 | 2.595
| Sн. MV, МVА | 6,3+10 | 0 | 0 | 180 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+10 | 0 | 0 | 0 | 180 | 0 | 0 | 6.615 | 6.615 |  | 110/35/10
| Sн. LV, МVА | 6,3+10 | 3.77 | 0.47 | 180 | 3.3 | 0 | 6.615 | 3.315 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+10 | 0.72 | 4.49 | 0.47 | 180 | 4.02 | 0 | 6.615 | 2.595
181 | Ostrogozhsk | 40,5+40,5 | 19.78 | 2.4 | 60 | 17.38 | 0 | 42.525 | 25.145 | 25.145 |  | 1.05 | 40.5 | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 19.78 | 2.4 | 60 | 17.38 | 0 | 42.525 | 25.145 | 25.145
| Sн. MV, МVА | 40,5+40,5 | 16.81 | 2.4 | 60 | 14.41 | 0 | 42.525 | 28.115 |  |  | 1.05 | 40.5 |  | Sн. MV, МVА | 40,5+40,5 | 0 | 16.81 | 2.4 | 60 | 14.41 | 0 | 42.525 | 28.115 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5 | 2.97 | 0 | 60 | 2.97 | 0 | 42.525 | 39.555 |  |  | 1.05 | 40.5 |  | Sн. LV, МVА | 40,5+40,5 | 0 | 2.97 | 0 | 60 | 2.97 | 0 | 42.525 | 39.555
182 | Khrenovoe | 16+6,3 | 4.09 | 0 | 0 | 4.09 | 0 | 6.615 | 2.525 | 2.525 |  | 1.05 | 6.3 | 179 | Khrenovoe | 16+6,3 | 1.07 | 5.16 | 0 | 0 | 5.16 | 0 | 6.615 | 1.455 | 1.455
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 16+6,3 | 0.34 | 0.34 | 0 | 0 | 0.34 | 0 | 6.615 | 6.275 |  | 110/35/10
| Sн. LV, МVА | 16+6,3 | 4.09 | 0 | 0 | 4.09 | 0 | 6.615 | 2.525 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 16+6,3 | 0.73 | 4.82 | 0 | 0 | 4.82 | 0 | 6.615 | 1.795
183 | Oil extraction plant | 25+25 | 23.52 | 7.9 | 120 | 15.62 | 0 | 26.25 | 10.63 | 10.63 |  | 1.05 | 25 | 180 | Oil extraction plant | 25+25 | 0.3 | 23.82 | 7.9 | 120 | 15.92 | 0 | 26.25 | 10.33 | 10.33
| Sн. MV, МVА | 25+25 | 9.01 | 7.9 | 120 | 1.11 | 0 | 26.25 | 25.14 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 9.01 | 7.9 | 120 | 1.11 | 0 | 26.25 | 25.14 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 14.51 | 0 | 0 | 14.51 | 0 | 26.25 | 11.74 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.3 | 14.81 | 0 | 0 | 14.81 | 0 | 26.25 | 11.44
184 | ANP | 6,3+6,3 | 3.09 | 0.39 | 120 | 2.7 | 0 | 6.615 | 3.915 | 3.915 |  | 1.05 | 6.3 | 181 | ANP | 6,3+6,3 | 4.7 | 4.39 | 0.39 | 120 | 4 | 0 | 6.615 | 2.615 | 2.615 | 110/6
185 | St. Kalitva | 6,3+6,3 | 1.62 | 0.86 | 240 | 0.76 | 0 | 6.615 | 5.855 | 5.855 |  | 1.05 | 6.3 | 182 | St. Kalitva | 6,3+6,3 | 0.2 | 1.82 | 0.86 | 240 | 0.96 | 0 | 6.615 | 5.655 | 5.655 | 110/10
186 | Nikanorovka | 2,5+6,3 | 0.67 | 0.5 | 240 | 0.17 | 0 | 2.625 | 2.455 | 2.455 |  | 1.05 | 2.5 | 183 | Nikanorovka | 2,5+6,3 | 0.59 | 1.26 | 0.5 | 240 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | 110/10
187 | Poultry plant | 10+10 | 3.37 | 1 | 120 | 2.37 | 0 | 10.5 | 8.13 | 8.13 |  | 1.05 | 10 | 184 | Poultry plant | 10+10 | 0.78 | 4.15 | 1 | 120 | 3.15 | 0 | 10.5 | 7.35 | 7.35 | 110/10
188 | Korshevo | 6,3+6,3 | 0.89 | 0.56 | 120 | 0.33 | 0 | 6.615 | 6.285 | 6.285 |  | 1.05 | 6.3 | 185 | Korshevo | 6,3+6,3 | 2.55 | 3.44 | 0.56 | 120 | 2.88 | 0 | 6.615 | 3.735 | 3.735 | 110/10
189 | Davydovka | 6,3+6,3 | 6.25 | 2.11 | 240 | 4.14 | 0 | 6.615 | 2.475 | 2.475 |  | 1.05 | 6.3 | 186 | Davydovka | 6,3+6,3 | 2.46 | 8.71 | 2.11 | 240 | 6.6 | 0 | 6.615 | 0.015 | 0.015 | 110/10
190 | the 2nd Pyatiletka | 6,3+6,3 | 1.28 | 0.66 | 120 | 0.62 | 0 | 6.615 | 5.995 | 5.995 |  | 1.05 | 6.3 | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.67 | 1.95 | 0.66 | 120 | 1.29 | 0 | 6.615 | 5.325 | 5.325 | 110/10
191 | Liskinskaya | 10+16 | 7.22 | 0.72 | 120 | 6.5 | 0 | 10.5 | 4 | 4 |  | 1.05 | 10 | 188 | Liskinskaya | 10+16 | 1.52 | 8.74 | 0.72 | 120 | 8.02 | 0 | 10.5 | 2.48 | 2.48 | 110/6
192 | Olkhovatka | 4+4 | 3.55 | 2.55 | 180 | 1 | 0 | 4.2 | 3.2 | 3.2 |  | 1.05 | 4 | 189 | Olkhovatka | 4+4 | 1.06 | 4.61 | 2.55 | 180 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | 35/10
193 | Shaposhnikovka | 2,5+2,5 | 1.23 | 0.86 | 180 | 0.37 | 0 | 2.625 | 2.255 | 2.255 |  | 1.05 | 2.5 | 190 | Shaposhnikovka | 2,5+2,5 | 0.27 | 1.5 | 0.86 | 180 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | 35/10
194 | Karayashnik | 2,5+2,5 | 0.6 | 0.2875 | 180 | 0.3125 | 0 | 2.625 | 2.3125 | 2.3125 |  | 1.05 | 2.5 | 191 | Karayashnik | 2,5+2,5 | 0.05 | 0.65 | 0.2875 | 180 | 0.3625 | 0 | 2.625 | 2.2625 | 2.2625 | 35/10
195 | Saguny | 2,5+2,5 | 1.02 | 0.91 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 |  | 1.05 | 2.5 | 192 | Saguny | 2,5+2,5 | 0.16 | 1.18 | 0.91 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | 35/10
196 | Belogorye | 2,5+2,5 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 |  | 1.05 | 2.5 | 193 | Belogorye | 2,5+2,5 | 0.25 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | 35/10
197 | Taly | 4+4 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 |  | 1.05 | 4 | 194 | Taly | 4+4 | 0.36 | 1.66 | 0 | 0 | 1.66 | 0 | 4.2 | 2.54 | 2.54 | 35/10
198 | Titarevka | 2,5+2,5 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 |  | 1.05 | 2.5 | 195 | Titarevka | 2,5+2,5 | 0.32 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | 35/10
199 | Mitrofanovka | 4+4 | 2.67 | 0 | 0 | 2.67 | 0 | 4.2 | 1.53 | 1.53 |  | 1.05 | 4 | 196 | Mitrofanovka | 4+4 | 0.75 | 3.42 | 0 | 0 | 3.42 | 0 | 4.2 | 0.78 | 0.78 | 35/10
200 | Druzhba | 4+4 | 2.11 | 0.44 | 150 | 1.67 | 0 | 4.2 | 2.53 | 2.53 |  | 1.05 | 4 | 197 | Druzhba | 4+4 | 0.51 | 2.62 | 0.44 | 150 | 2.18 | 0 | 4.2 | 2.02 | 2.02 | 35/10
201 | AlexandrovkaLPS | 4+4 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 |  | 1.05 | 4 | 198 | AlexandrovkaLPS | 4+4 | 0.22 | 2.85 | 0 | 0 | 2.85 | 0 | 4.2 | 1.35 | 1.35 | 35/10
202 | Tkhorevka | 4+4 | 0.82 | 0.78 | 180 | 0.04 | 0 | 4.2 | 4.16 | 4.16 |  | 1.05 | 4 | 199 | Tkhorevka | 4+4 | 0.17 | 0.99 | 0.78 | 180 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | 35/10
203 | Marki | 2,5+2,5 | 0.42 | 0.27 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 |  | 1.05 | 2.5 | 200 | Marki | 2,5+2,5 | 0.14 | 0.56 | 0.27 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | 35/10
204 | Olkhov Log | 2,5+2,5 | 0.69 | 0.58 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 |  | 1.05 | 2.5 | 201 | Olkhov Log | 2,5+2,5 | 0 | 0.69 | 0.58 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | 35/10
205 | Boldyrevka | 2,5+2,5 | 1 | 0 | 0 | 1 | 0 | 2.625 | 1.625 | 1.625 |  | 1.05 | 2.5 | 202 | Boldyrevka | 2,5+2,5 | 0.26 | 1.26 | 0 | 0 | 1.26 | 0 | 2.625 | 1.365 | 1.365 | 35/10
206 | Pobeda | 4+4 | 0.61 | 0 | 0 | 0.61 | 0 | 4.2 | 3.59 | 3.59 |  | 1.05 | 4 | 203 | Pobeda | 4+4 | 0.08 | 0.69 | 0 | 0 | 0.69 | 0 | 4.2 | 3.51 | 3.51 | 35/10
207 | Lipovka | 4+4 | 1.64 | 0 | 0 | 1.64 | 0 | 4.2 | 2.56 | 2.56 |  | 1.05 | 4 | 204 | Lipovka | 4+4 | 2.8 | 4.44 | 0 | 0 | 4.44 | 0 | 4.2 | -0.24 | -0.24 | 35/10
208 | Yudanovka | 2,5+2,5 | 0.96 | 0.81 | 180 | 0.15 | 0 | 2.625 | 2.475 | 2.475 |  | 1.05 | 2.5 | 205 | Yudanovka | 2,5+2,5 | 2.44 | 3.4 | 0.81 | 180 | 2.59 | 0 | 2.625 | 0.035 | 0.035 | 35/10
209 | Mechetka | 2,5+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 |  | 1.05 | 1.6 | 206 | Mechetka | 2,5+1,6 | 0.06 | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | 35/10
210 | Petrovskaya | 4+4 | 2.31 | 0.03 | 180 | 2.28 | 0 | 4.2 | 1.92 | 1.92 |  | 1.05 | 4 | 207 | Petrovskaya | 4+4 | 1.44 | 3.75 | 0.03 | 180 | 3.72 | 0 | 4.2 | 0.48 | 0.48 | 35/10
211 | Sr. Ikorets | 4+4 | 3.64 | 0.06 | 120 | 3.58 | 0 | 4.2 | 0.62 | 0.62 |  | 1.05 | 4 | 208 | Sr. Ikorets | 4+4 | 1.8 | 5.44 | 0.06 | 120 | 5.38 | 0 | 4.2 | -1.18 | -1.18 | 35/10
212 | the 2nd Storozhevoe | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 |  | 1.05 | 2.5 | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.39 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | 35/10
213 | Purification facilities | 2,5+2,5 | 2.23 | 0.42 | 120 | 1.81 | 0 | 2.625 | 0.815 | 0.815 |  | 1.05 | 2.5 | 210 | Purification facilities | 2,5+2,5 | 2.17 | 4.4 | 0.6 | 120 | 3.8 | 0 | 2.625 | -1.175 | -1.175 | 35/6
214 | БЭС | [12 empty] | 2: БЭС
214 | Borisoglebsk | 25+25 | 28.11 | 15.05 | 240 | 13.06 | 0 | 26.25 | 13.19 | 13.19 |  | 1.05 | 25 | 211 | Borisoglebsk | 25+25 | 0 | 28.11 | 24.9 | 240 | 3.21 | 0 | 26.25 | 23.04 | 22.14
| Sн. MV, МVА | 25+25 | 20.61 | 10.9 | 240 | 9.71 | 0 | 26.25 | 16.54 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 20.61 | 16.5 | 240 | 4.11 | 0 | 26.25 | 22.14 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 7.5 | 4.15 | 240 | 3.35 | 0 | 26.25 | 22.9 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0 | 7.5 | 8.4 | 240 | -0.9 | 0 | 26.25 | 27.15
215 | KamenkaBPS | 10+10 | 5.85 | 2.79 | 180 | 3.06 | 0 | 10.5 | 7.44 | 7.44 |  | 1.05 | 10 | 212 | KamenkaBPS | 10+10 | 0.06 | 5.91 | 6.01 | 180 | -0.1 | 0 | 10.5 | 10.6 | 10.19
| Sн. MV, МVА | 10+10 | 4.94 | 2.54 | 180 | 2.4 | 0 | 10.5 | 8.1 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 4.94 | 5.35 | 180 | -0.41 | 0 | 10.5 | 10.91 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.91 | 0.25 | 180 | 0.66 | 0 | 10.5 | 9.84 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.06 | 0.97 | 0.66 | 180 | 0.31 | 0 | 10.5 | 10.19
216 | Talovaya | 16+16 | 6.1 | 3.6 | 180 | 2.5 | 0 | 16.8 | 14.3 | 14.3 |  | 1.05 | 16 | 213 | Talovaya | 16+16 | 0.4 | 6.5 | 6.39 | 180 | 0.11 | 0 | 16.8 | 16.69 | 15.31
| Sн. MV, МVА | 16+16 | 5.01 | 3.6 | 180 | 1.41 | 0 | 16.8 | 15.39 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 5.01 | 6.39 | 180 | -1.38 | 0 | 16.8 | 18.18 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.09 | 0 | 0 | 1.09 | 0 | 16.8 | 15.71 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.4 | 1.49 | 0 | 0 | 1.49 | 0 | 16.8 | 15.31
217 | Anna | 25+25 | 16.6 | 7.8 | 150 | 8.8 | 0 | 26.25 | 17.45 | 17.45 |  | 1.05 | 25 | 214 | Anna | 25+25 | 1.03 | 17.63 | 14.11 | 150 | 3.52 | 0 | 26.25 | 22.73 | 22.73
| Sн. MV, МVА | 25+25 | 6.75 | 2.39 | 150 | 4.36 | 0 | 26.25 | 21.89 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 6.75 | 5.37 | 150 | 1.38 | 0 | 26.25 | 24.87 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 9.85 | 5.4 | 150 | 4.45 | 0 | 26.25 | 21.8 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 1.03 | 10.88 | 8.74 | 150 | 2.14 | 0 | 26.25 | 24.11
218 | ArkhangelskoeBPS | 10+10 | 6.76 | 0.88 | 90 | 5.88 | 0 | 10.5 | 4.62 | 4.62 |  | 1.05 | 10 | 215 | ArkhangelskoeBPS | 10+10 | 0.01 | 6.77 | 3.02 | 90 | 3.75 | 0 | 10.5 | 6.75 | 6.75
| Sн. MV, МVА | 10+10 | 3.75 | 0.88 | 90 | 2.87 | 0 | 10.5 | 7.63 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 3.75 | 3.02 | 90 | 0.73 | 0 | 10.5 | 9.77 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.01 | 0 | 0 | 3.01 | 0 | 10.5 | 7.49 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.01 | 3.02 | 0 | 0 | 3.02 | 0 | 10.5 | 7.48
219 | Listopadovka | 10+10 | 2.55 | 1.63 | 90 | 0.92 | 0 | 10.5 | 9.58 | 9.28 |  | 1.05 | 10 | 216 | Listopadovka | 10+10 | 0.37 | 2.92 | 3.08 | 90 | -0.16 | 0 | 10.5 | 10.66 | 8.91
| Sн. MV, МVА | 10+10 | 1.33 | 1.63 | 90 | -0.3 | 0 | 10.5 | 10.8 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.33 | 3.08 | 90 | -1.75 | 0 | 10.5 | 12.25 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.37 | 1.59 | 0 | 0 | 1.59 | 0 | 10.5 | 8.91
220 | V. Karachan | 10+10 | 1.9 | 0.81 | 90 | 1.09 | 0 | 10.5 | 9.41 | 8.73 |  | 1.05 | 10 | 217 | V. Karachan | 10+10 | 0.3 | 2.2 | 1.18 | 90 | 1.02 | 0 | 10.5 | 9.48 | 8.43
| Sн. MV, МVА | 10+10 | 0.13 | 0.81 | 90 | -0.68 | 0 | 10.5 | 11.18 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 0.13 | 1.18 | 90 | -1.05 | 0 | 10.5 | 11.55 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.77 | 0 | 0 | 1.77 | 0 | 10.5 | 8.73 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.3 | 2.07 | 0 | 0 | 2.07 | 0 | 10.5 | 8.43
221 | Ternovka | 10+10 | 3.89 | 0.66 | 60 | 3.23 | 0 | 10.5 | 7.27 | 7.27 |  | 1.05 | 10 | 218 | Ternovka | 10+10 | 0.06 | 3.95 | 1.03 | 60 | 2.92 | 0 | 10.5 | 7.58 | 7.58
| Sн. MV, МVА | 10+10 | 1.2 | 0.66 | 60 | 0.54 | 0 | 10.5 | 9.96 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.2 | 1.03 | 60 | 0.17 | 0 | 10.5 | 10.33 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.69 | 0 | 0 | 2.69 | 0 | 10.5 | 7.81 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.06 | 2.75 | 0 | 0 | 2.75 | 0 | 10.5 | 7.75
222 | Narodnoe | 16+10 | 3.35 | 0.6 | 90 | 2.75 | 0 | 10.5 | 7.75 | 7.68 |  | 1.05 | 10 | 219 | Narodnoe | 16+10 | 0.47 | 3.82 | 0.93 | 90 | 2.89 | 0 | 10.5 | 7.61 | 7.21
| Sн. MV, МVА | 16+10 | 0.53 | 0.6 | 90 | -0.07 | 0 | 10.5 | 10.57 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 0.53 | 0.93 | 90 | -0.4 | 0 | 10.5 | 10.9 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 2.82 | 0 | 0 | 2.82 | 0 | 10.5 | 7.68 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 0.47 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21
223 | N. Khopersk | 10+16 | 8.13 | 1.7 | 120 | 6.43 | 0 | 10.5 | 4.07 | 4.07 |  | 1.05 | 10 | 220 | N. Khopersk | 10+16 | 1.83 | 9.96 | 1.95 | 120 | 8.01 | 0 | 10.5 | 2.49 | 2.49
| Sн. MV, МVА | 10+16 | 2.52 | 1.7 | 120 | 0.82 | 0 | 10.5 | 9.68 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 2.52 | 1.95 | 120 | 0.57 | 0 | 10.5 | 9.93 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 5.61 | 0 | 0 | 5.61 | 0 | 10.5 | 4.89 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 1.83 | 7.44 | 0 | 0 | 7.44 | 0 | 10.5 | 3.06
224 | Ertil | 16+16 | 8.64 | 2.92 | 180 | 5.72 | 0 | 16.8 | 11.08 | 7.35 |  | 1.05 | 16 | 221 | Ertil | 16+16 | 0.08 | 8.72 | 1.4 | 180 | 7.32 | 0 | 16.8 | 9.48 | 5.83
| Sн. MV, МVА | 10+16 | 6.07 | 2.92 | 180 | 3.15 | 0 | 10.5 | 7.35 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 6.07 | 1.4 | 180 | 4.67 | 0 | 10.5 | 5.83 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 2.57 | 0.08 | 0 | 2.49 | 0 | 10.5 | 8.01 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 0.08 | 2.65 | 0 | 0 | 2.65 | 0 | 10.5 | 7.85
225 | Shchuchye | 6,3+6,3 | 2.06 | 1.09 | 180 | 0.97 | 0 | 6.615 | 5.645 | 5.475 |  | 1.05 | 6.3 | 222 | Shchuchye | 6,3+6,3 | 0.78 | 2.84 | 2.33 | 180 | 0.51 | 0 | 6.615 | 6.105 | 4.965
| Sн. MV, МVА | 6,3+6,3 | 0.67 | 0.84 | 180 | -0.17 | 0 | 6.615 | 6.785 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 0.67 | 1.81 | 180 | -1.14 | 0 | 6.615 | 7.755 |  | 110/35/10
| Sн.LV, МVА | 6,3+6,3 | 1.39 | 0.25 | 180 | 1.14 | 0 | 6.615 | 5.475 |  |  | 1.05 | 6.3 |  | Sн.LV, МVА | 6,3+6,3 | 0.78 | 2.17 | 0.52 | 180 | 1.65 | 0 | 6.615 | 4.965
226 | Dokuchaevo | 10+10 | 2.32 | 0.12 | 120 | 2.2 | 0 | 10.5 | 8.3 | 8.3 |  | 1.05 | 10 | 223 | Dokuchaevo | 10+10 | 0.08 | 2.4 | 0.45 | 120 | 1.95 | 0 | 10.5 | 8.55 | 8.55 | 110/10
227 | B. Gribanovka | 16+16 | 9.24 | 0.11 | 30 | 9.13 | 0 | 16.8 | 7.67 | 7.67 |  | 1.05 | 16 | 224 | B. Gribanovka | 16+16 | 1.8 | 11.04 | 0.24 | 30 | 10.8 | 0 | 16.8 | 6 | 6 | 110/10
228 | Khimmash | 16+16 | 6.66 | 4.47 | 240 | 2.19 | 0 | 16.8 | 14.61 | 14.61 |  | 1.05 | 16 | 225 | Khimmash | 16+16 | 0 | 6.66 | 7.1 | 240 | -0.44 | 0 | 16.8 | 17.24 | 17.24 | 110/6
229 | Chigorak | 2,5+4 | 0.9 | 0.74 | 90 | 0.16 | 0 | 2.625 | 2.465 | 2.465 |  | 1.05 | 2.5 | 226 | Chigorak | 2,5+4 | 0.44 | 1.34 | 0.96 | 90 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | 35/10
230 | Tretyaki | 4+4 | 1.21 | 0 | 0 | 1.21 | 0 | 4.2 | 2.99 | 2.99 |  | 1.05 | 4 | 227 | Tretyaki | 4+4 | 1.34 | 2.55 | 0 | 0 | 2.55 | 0 | 4.2 | 1.65 | 1.65 | 35/10
231 | Gubari | 2,5+2,5 | 0.31 | 0.06 | 180 | 0.25 | 0 | 2.625 | 2.375 | 2.375 |  | 1.05 | 2.5 | 228 | Gubari | 2,5+2,5 | 0.15 | 0.46 | 0.43 | 180 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | 35/10
232 | Tantsyrey | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 |  | 1.05 | 2.5 | 229 | Tantsyrey | 2,5+2,5 | 0.26 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | 35/10
233 | Peski | 4+4 | 3.17 | 0 | 0 | 3.17 | 0 | 4.2 | 1.03 | 1.03 |  | 1.05 | 4 | 230 | Peski | 4+4 | 1.16 | 4.33 | 0 | 0 | 4.33 | 0 | 4.2 | -0.13 | -0.13 | 35/10
234 | M. Gribanovka | 1,6+1,6 | 0.38 | 0.31 | 30 | 0.07 | 0 | 1.68 | 1.61 | 1.61 |  | 1.05 | 1.6 | 231 | M. Gribanovka | 1,6+1,6 | 0.31 | 0.69 | 0.87 | 30 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | 35/10
235 | N. Karachan | 2,5+2,5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 |  | 1.05 | 2.5 | 232 | N. Karachan | 2,5+2,5 | 0.07 | 0.62 | 0 | 0 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | 35/10
236 | Kozlovka BPS | 4+2,5 | 1.04 | 0 | 0 | 1.04 | 0 | 2.625 | 1.585 | 1.585 |  | 1.05 | 2.5 | 233 | Kozlovka BPS | 4+2,5 | 0.03 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | 35/10
237 | K. Otdelets | 2,5+2,5 | 0.4 | 0 | 30 | 0.4 | 0 | 2.625 | 2.225 | 2.225 |  | 1.05 | 2.5 | 234 | K. Otdelets | 2,5+2,5 | 0 | 0.4 | 0.63 | 30 | -0.23 | 0 | 2.625 | 2.855 | 2.855 | 35/10
238 | Esipovo | 2,5+2,5 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 |  | 1.05 | 2.5 | 235 | Esipovo | 2,5+2,5 | 0.02 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 35/10
239 | Kiselnov | 2,5+2,5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 |  | 1.05 | 2.5 | 236 | Kiselnov | 2,5+2,5 | 0 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | 35/10
240 | Krasnoe | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 |  | 1.05 | 4 | 237 | Krasnoe | 4+4 | 1.55 | 2.15 | 0 | 0 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | 35/10
241 | Troitskoe | 2,5+2,5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 |  | 1.05 | 2.5 | 238 | Troitskoe | 2,5+2,5 | 0.01 | 0.49 | 0 | 0 | 0.49 | 0 | 2.625 | 2.135 | 2.135 | 35/10
242 | Ertil-gorod | 6,3+6,3 | 3.48 | 2.45 | 240 | 1.03 | 0 | 6.615 | 5.585 | 5.585 |  | 1.05 | 6.3 | 239 | Ertil-gorod | 6,3+6,3 | 0.2 | 3.68 | 5 | 240 | -1.32 | 0 | 6.615 | 7.935 | 7.935 | 35/10
243 | Rostoshi | 4+4 | 1.32 | 0 | 0 | 1.32 | 0 | 4.2 | 2.88 | 2.88 |  | 1.05 | 4 | 240 | Rostoshi | 4+4 | 0 | 1.32 | 0 | 0 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | 35/10
244 | Vvedenka | 2,5+2,5 | 0.16 | 0 | 60 | 0.16 | 0 | 2.625 | 2.465 | 2.465 |  | 1.05 | 2.5 | 241 | Vvedenka | 2,5+2,5 | 0 | 0.16 | 0.48 | 60 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | 35/10
245 | Sadovoe | 4+4 | 2.23 | 0 | 0 | 2.23 | 0 | 4.2 | 1.97 | 1.97 |  | 1.05 | 4 | 242 | Sadovoe | 4+4 | 0.28 | 2.51 | 0 | 0 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | 35/10
246 | Rubashevka | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 |  | 1.05 | 2.5 | 243 | Rubashevka | 2,5+2,5 | 0.03 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 35/10
247 | N. Nadezhdenka | 2,5+2,5 | 0.46 | 0.22 | 180 | 0.24 | 0 | 2.625 | 2.385 | 2.385 |  | 1.05 | 2.5 | 244 | N. Nadezhdenka | 2,5+2,5 | 0 | 0.46 | 0.75 | 180 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | 35/10
248 | Abramovka | 6,3+4 | 2.77 | 0.29 | 120 | 2.48 | 0 | 4.2 | 1.72 | 1.72 |  | 1.05 | 4 | 245 | Abramovka | 6,3+4 | 0.22 | 2.99 | 0.52 | 120 | 2.47 | 0 | 4.2 | 1.73 | 1.73 | 35/10
249 | Alexandrovka BPS | 2,5+2,5 | 0.87 | 0.64 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 |  | 1.05 | 2.5 | 246 | Alexandrovka BPS | 2,5+2,5 | 0.05 | 0.92 | 1.17 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | 35/10
250 | N. Troitskaya | 4+4 | 0.38 | 0.2 | 120 | 0.18 | 0 | 4.2 | 4.02 | 4.02 |  | 1.05 | 4 | 247 | N. Troitskaya | 4+4 | 0 | 0.38 | 0.34 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | 35/10
251 | КЭС | [12 empty] | 2: КЭС
251 | Kalach-1 | 25+25 | 13.87 | 2.2 | 120 | 11.67 | 0 | 26.25 | 14.58 | 14.58 |  | 1.05 | 25 | 248 | Kalach-1 | 25+25 | 2.36 | 16.23 | 2.2 | 120 | 14.03 | 0 | 26.25 | 12.22 | 12.22
| Sн. MV, МVА | 25+25 | 6.32 | 1 | 120 | 5.32 | 0 | 26.25 | 20.93 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 6.32 | 1 | 120 | 5.32 | 0 | 26.25 | 20.93 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.55 | 1.2 | 120 | 6.35 | 0 | 26.25 | 19.9 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 2.36 | 9.91 | 1.2 | 120 | 8.71 | 0 | 26.25 | 17.54
252 | Kalach-2 | 16+16 | 7.66 | 2 | 1 сутки | 5.66 | 0 | 16.8 | 11.14 | 11.14 |  | 1.05 | 16 | 249 | Kalach-2 | 16+16 | 2.31 | 9.97 | 2 | 1 сутки | 7.97 | 0 | 16.8 | 8.83 | 8.83 | 110/10
253 | Buturlinovka-1 | 16+16 | 13.48 | 2 | 120 | 11.48 | 0 | 16.8 | 5.32 | 5.32 |  | 1.05 | 16 | 250 | Buturlinovka-1 | 16+16 | 0.31 | 13.79 | 2 | 120 | 11.79 | 0 | 16.8 | 5.01 | 5.01
| Sн. MV, МVА | 16+16 | 3.12 | 0 | 0 | 3.12 | 0 | 16.8 | 13.68 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.12 | 0 | 0 | 3.12 | 0 | 16.8 | 13.68 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 10.36 | 2 | 120 | 8.36 | 0 | 16.8 | 8.44 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.31 | 10.67 | 2 | 120 | 8.67 | 0 | 16.8 | 8.13
254 | Buturlinovka-2 | 6,3+6,3 | 4.42 | 1.5 | 120 | 2.92 | 0 | 6.615 | 3.695 | 3.695 |  | 1.05 | 6.3 | 251 | Buturlinovka-2 | 6,3+6,3 | 0.01 | 4.43 | 1.5 | 120 | 2.93 | 0 | 6.615 | 3.685 | 3.685 | 110/10
255 | N.Kislyai | 10+10 | 5.61 | 1.5 | 120 | 4.11 | 0 | 10.5 | 6.39 | 6.39 |  | 1.05 | 10 | 252 | N.Kislyai | 10+10 | 0.8 | 6.41 | 1.5 | 120 | 4.91 | 0 | 10.5 | 5.59 | 5.59
| Sн. MV, МVА | 10+10 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.69 | 1.5 | 120 | 1.19 | 0 | 10.5 | 9.31 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.8 | 3.49 | 1.5 | 120 | 1.99 | 0 | 10.5 | 8.51
256 | Kozlovka CPS | 2,5+6,3 | 1.17 | 1.5 | 45 | -0.33 | 0 | 2.625 | 2.955 | 2.955 |  | 1.05 | 2.5 | 253 | Kozlovka CPS | 2,5+6,3 | 0.18 | 1.35 | 1.5 | 45 | -0.15 | 0 | 2.625 | 2.775 | 2.775 | 110/10
257 | Filippenkovo | 6,3+6,3 | 1.14 | 1.5 | 120 | -0.36 | 0 | 6.615 | 6.975 | 6.975 |  | 1.05 | 6.3 | 254 | Filippenkovo | 6,3+6,3 | 0.05 | 1.19 | 1.5 | 120 | -0.31 | 0 | 6.615 | 6.925 | 6.925 | 110/10
258 | Vorobyovka | 16+16 | 7.48 | 1.5 | 120 | 5.98 | 0 | 16.8 | 10.82 | 10.82 |  | 1.05 | 16 | 255 | Vorobyovka | 16+16 | 0.43 | 7.91 | 1.5 | 120 | 6.41 | 0 | 16.8 | 10.39 | 10.39
| Sн. MV, МVА | 16+16 | 4.88 | 0.5 | 120 | 4.38 | 0 | 16.8 | 12.42 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 4.88 | 0.5 | 120 | 4.38 | 0 | 16.8 | 12.42 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.6 | 1 | 120 | 1.6 | 0 | 16.8 | 15.2 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.43 | 3.03 | 1 | 120 | 2.03 | 0 | 16.8 | 14.77
259 | Solontsy | 6,3+6,3 | 0.95 | 1 | 1 сутки | -0.05 | 0 | 6.615 | 6.665 | 5.885 |  | 1.05 | 6.3 | 256 | Solontsy | 6,3+6,3 | 0.03 | 0.98 | 1 | 1 сутки | -0.02 | 0 | 6.615 | 6.635 | 5.855
| Sн. MV, МVА | 6,3+6,3 | 0.22 | 1 | 1 сутки | -0.78 | 0 | 6.615 | 7.395 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 0.22 | 1 | 1 сутки | -0.78 | 0 | 6.615 | 7.395 |  | 110/35/10
| Sн. LV, МVА | 6,3+6,3 | 0.73 | 0 | 0 | 0.73 | 0 | 6.615 | 5.885 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+6,3 | 0.03 | 0.76 | 0 | 0 | 0.76 | 0 | 6.615 | 5.855
260 | Manino | 16+16 | 1.22 | 1.5 | 1 сутки | -0.28 | 0 | 16.8 | 17.08 | 16.58 |  | 1.05 | 16 | 257 | Manino | 16+16 | 0.04 | 1.26 | 1.5 | 1 сутки | -0.24 | 0 | 16.8 | 17.04 | 16.54
| Sн. MV, МVА | 16+16 | 0 | 0.5 | 1 сутки | -0.5 | 0 | 16.8 | 17.3 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0 | 0.5 | 1 сутки | -0.5 | 0 | 16.8 | 17.3 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.22 | 1 | 1 сутки | 0.22 | 0 | 16.8 | 16.58 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.04 | 1.26 | 1 | 1 сутки | 0.26 | 0 | 16.8 | 16.54
261 | Petropavlovka | 10+10 | 4.83 | 2 | 120 | 2.83 | 0 | 10.5 | 7.67 | 7.67 |  | 1.05 | 10 | 258 | Petropavlovka | 10+10 | 1.42 | 6.25 | 2 | 120 | 4.25 | 0 | 10.5 | 6.25 | 6.25
| Sн. MV, МVА | 10+10 | 1.92 | 1 | 120 | 0.92 | 0 | 10.5 | 9.58 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2 | 1 | 120 | 1 | 0 | 10.5 | 9.5 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.91 | 1 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 1.42 | 4.33 | 1 | 120 | 3.33 | 0 | 10.5 | 7.17
262 | V.Mamon | 16+10 | 5.68 | 2 | 120 | 3.68 | 0 | 10.5 | 6.82 | 6.82 |  | 1.05 | 10 | 259 | V.Mamon | 16+10 | 1.61 | 7.29 | 2 | 120 | 5.29 | 0 | 10.5 | 5.21 | 5.21
| Sн. MV, МVА | 16+10 | 2.14 | 0 | 0 | 2.14 | 0 | 10.5 | 8.36 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 2.14 | 0 | 0 | 2.14 | 0 | 10.5 | 8.36 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 3.54 | 2 | 120 | 1.54 | 0 | 10.5 | 8.96 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 1.61 | 5.15 | 2 | 120 | 3.15 | 0 | 10.5 | 7.35
263 | N.Mamon | 2,5+6,3 | 1.28 | 0 | 0 | 1.28 | 0 | 2.625 | 1.345 | 1.345 |  | 1.05 | 2.5 | 260 | N.Mamon | 2,5+6,3 | 0.08 | 1.36 | 0 | 0 | 1.36 | 0 | 2.625 | 1.265 | 1.265 | 110/10
264 | Pavlovsk-2 | 25+25 | 20.78 | 1.5 | 120 | 19.28 | 0 | 26.25 | 6.97 | 6.97 |  | 1.05 | 25 | 261 | Pavlovsk-2 | 25+25 | 0.14 | 20.92 | 1.5 | 120 | 19.42 | 0 | 26.25 | 6.83 | 6.83
| Sн. MV, МVА | 25+25 | 13.01 | 1.5 | 120 | 11.51 | 0 | 26.25 | 14.74 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 13.01 | 1.5 | 120 | 11.51 | 0 | 26.25 | 14.74 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.77 | 0 | 0 | 7.77 | 0 | 26.25 | 18.48 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.14 | 7.91 | 0 | 0 | 7.91 | 0 | 26.25 | 18.34
265 | Bogucharskaya | 16+16 | 9.98 | 2 | 120 | 7.98 | 0 | 16.8 | 8.82 | 8.82 |  | 1.05 | 16 | 262 | Bogucharskaya | 16+16 | 3.32 | 13.3 | 2 | 120 | 11.3 | 0 | 16.8 | 5.5 | 5.5
| Sн. MV, МVА | 16+16 | 4.4 | 1 | 120 | 3.4 | 0 | 16.8 | 13.4 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 1.01 | 5.41 | 1 | 120 | 4.41 | 0 | 16.8 | 12.39 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.58 | 1 | 120 | 4.58 | 0 | 16.8 | 12.22 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.31 | 7.89 | 1 | 120 | 6.89 | 0 | 16.8 | 9.91
266 | Opornaya | 6,3+6,3 | 2.4 | 1.5 | 120 | 0.9 | 0 | 6.615 | 5.715 | 5.715 |  | 1.05 | 6.3 | 263 | Opornaya | 6,3+6,3 | 1.05 | 3.45 | 1.5 | 120 | 1.95 | 0 | 6.615 | 4.665 | 4.665 | 110/10
267 | Podgornaya KPS | 2,5+2,5 | 0.8 | 1 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 |  | 1.05 | 2.5 | 264 | Podgornaya KPS | 2,5+2,5 | 0.07 | 0.87 | 1 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | 35/10
268 | Bolshevik KPS | 4+2,5 | 2.24 | 1.5 | 45 | 0.74 | 0 | 2.625 | 1.885 | 1.885 |  | 1.05 | 2.5 | 265 | Bolshevik KPS | 4+2,5 | 0.46 | 2.7 | 1.5 | 45 | 1.2 | 0 | 2.625 | 1.425 | 1.425 | 35/10
269 | Semenovka KPS | 2,5+1,8 | 0.71 | 1 | 80 | -0.29 | 0 | 1.89 | 2.18 | 2.18 |  | 1.05 | 1.8 | 266 | Semenovka KPS | 2,5+1,8 | 0.09 | 0.8 | 1 | 80 | -0.2 | 0 | 1.89 | 2.09 | 2.09 | 35/10
270 | Popasnoe | 4+4 | 0.34 | 1.5 | 120 | -1.16 | 0 | 4.2 | 5.36 | 5.36 |  | 1.05 | 4 | 267 | Popasnoe | 4+4 | 0.04 | 0.38 | 1.5 | 120 | -1.12 | 0 | 4.2 | 5.32 | 5.32 | 35/10
271 | N.Kriusha | 2,5+2,5 | 0.89 | 1.5 | 45 | -0.61 | 0 | 2.625 | 3.235 | 3.235 |  | 1.05 | 2.5 | 268 | N.Kriusha | 2,5+2,5 | 1.71 | 2.6 | 1.5 | 45 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | 35/10
272 | N.Melovatka | 2,5+2,5 | 1.44 | 1.5 | 45 | -0.06 | 0 | 2.625 | 2.685 | 2.685 |  | 1.05 | 2.5 | 269 | N.Melovatka | 2,5+2,5 | 0.25 | 1.69 | 1.5 | 45 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | 35/10
273 | Vasilyevka KPS | 4+4 | 0.89 | 1.5 | 120 | -0.61 | 0 | 4.2 | 4.81 | 4.81 |  | 1.05 | 4 | 270 | Vasilyevka KPS | 4+4 | 0.08 | 0.97 | 1.5 | 120 | -0.53 | 0 | 4.2 | 4.73 | 4.73 | 35/10
274 | V.Oktyabr | 4+4 | 1.76 | 1.5 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 |  | 1.05 | 4 | 271 | V.Oktyabr | 4+4 | 0.22 | 1.98 | 1.5 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | 35/10
275 | V.Arkhangelskoe | 2,5+2,5 | 0.43 | 1.5 | 45 | -1.07 | 0 | 2.625 | 3.695 | 3.695 |  | 1.05 | 2.5 | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.07 | 0.5 | 1.5 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 | 35/10
276 | Leshchanaya | 2,5+2,5 | 1.82 | 1.5 | 45 | 0.32 | 0 | 2.625 | 2.305 | 2.305 |  | 1.05 | 2.5 | 273 | Leshchanaya | 2,5+2,5 | 0.18 | 2 | 1.5 | 45 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | 35/10
277 | Muzhichye | 4+2,5 | 0.52 | 1.5 | 45 | -0.98 | 0 | 2.625 | 3.605 | 3.605 |  | 1.05 | 2.5 | 274 | Muzhichye | 4+2,5 | 0.11 | 0.63 | 1.5 | 45 | -0.87 | 0 | 2.625 | 3.495 | 3.495 | 35/10
278 | Rudnya | 4+4 | 0.48 | 1.5 | 120 | -1.02 | 0 | 4.2 | 5.22 | 5.22 |  | 1.05 | 4 | 275 | Rudnya | 4+4 | 0.04 | 0.52 | 1.5 | 120 | -0.98 | 0 | 4.2 | 5.18 | 5.18 | 35/10
279 | St. Melovaya | 4+4 | 0.95 | 0 | 0 | 0.95 | 0 | 4.2 | 3.25 | 3.25 |  | 1.05 | 4 | 276 | St. Melovaya | 4+4 | 0.36 | 1.31 | 0 | 0 | 1.31 | 0 | 4.2 | 2.89 | 2.89 | 35/10
280 | St. Kriusha | 2,5+4 | 1.05 | 0 | 0 | 1.05 | 0 | 2.625 | 1.575 | 1.575 |  | 1.05 | 2.5 | 277 | St. Kriusha | 2,5+4 | 0.26 | 1.31 | 0 | 0 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | 35/10
281 | Lozovaya | 4+4 | 0.72 | 0 | 0 | 0.72 | 0 | 4.2 | 3.48 | 3.48 |  | 1.05 | 4 | 278 | Lozovaya | 4+4 | 0.3 | 1.02 | 0 | 0 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | 35/10
282 | Pavlovsk-1 | 4+4 | 3.87 | 1 | 120 | 2.87 | 0 | 4.2 | 1.33 | 1.33 |  | 1.05 | 4 | 279 | Pavlovsk-1 | 4+4 | 0.38 | 4.25 | 1 | 120 | 3.25 | 0 | 4.2 | 0.95 | 0.95 | 35/10
283 | Losevo KPS | 4+4 | 3.2 | 0 | 0 | 3.2 | 0 | 4.2 | 1 | 1 |  | 1.05 | 4 | 280 | Losevo KPS | 4+4 | 0.09 | 3.29 | 0 | 0 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | 35/10
284 | Gavrilsk | 4+4 | 0.55 | 0 | 0 | 0.55 | 0 | 4.2 | 3.65 | 3.65 |  | 1.05 | 4 | 281 | Gavrilsk | 4+4 | 0.03 | 0.58 | 0 | 0 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | 35/10
285 | Pokrovka | 4+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 |  | 1.05 | 2.5 | 282 | Pokrovka | 4+2,5 | 0.02 | 0.82 | 0 | 0 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | 35/10
286 | Vorontsovka | 4+4 | 2.99 | 1.5 | 120 | 1.49 | 0 | 4.2 | 2.71 | 2.71 |  | 1.05 | 4 | 283 | Vorontsovka | 4+4 | 0.7 | 3.69 | 1.5 | 120 | 2.19 | 0 | 4.2 | 2.01 | 2.01 | 35/10
287 | А.Donskaya | 2,5+2,5 | 1.13 | 1.5 | 45 | -0.37 | 0 | 2.625 | 2.995 | 2.995 |  | 1.05 | 2.5 | 284 | А.Donskaya | 2,5+2,5 | 0.14 | 1.27 | 1.5 | 45 | -0.23 | 0 | 2.625 | 2.855 | 2.855 | 35/10
288 | Petrovka | 2,5+4 | 1.79 | 1.5 | 45 | 0.29 | 0 | 2.625 | 2.335 | 2.335 |  | 1.05 | 2.5 | 285 | Petrovka | 2,5+4 | 2.38 | 4.17 | 1.5 | 45 | 2.67 | 0 | 2.625 | -0.045 | -0.045 | 35/10
289 | Monastyrshchina | 4+4 | 0.66 | 1.5 | 120 | -0.84 | 0 | 4.2 | 5.04 | 5.04 |  | 1.05 | 4 | 286 | Monastyrshchina | 4+4 | 0.21 | 0.87 | 1.5 | 120 | -0.63 | 0 | 4.2 | 4.83 | 4.83 | 35/10
290 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 |  | 1.05 | 1.8 | 287 | Zhuravka | 1,8+2,5 | 0.01 | 0.16 | 0 | 0 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | 35/10
291 | Dyachenkovo | 2,5+2,5 | 1.83 | 1.5 | 45 | 0.33 | 0 | 2.625 | 2.295 | 2.295 |  | 1.05 | 2.5 | 288 | Dyachenkovo | 2,5+2,5 | 1.51 | 3.34 | 1.5 | 45 | 1.84 | 0 | 2.625 | 0.785 | 0.785 | 35/10
292 | Radchenskaya | 1,6+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 1.68 | 0.98 | 0.98 |  | 1.05 | 1.6 | 289 | Radchenskaya | 1,6+2,5 | 0.53 | 1.23 | 0 | 0 | 1.23 | 0 | 1.68 | 0.45 | 0.45 | 35/10
293 | Rossiya | 4+4 | 1.4 | 1.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 |  | 1.05 | 4 | 290 | Rossiya | 4+4 | 0.22 | 1.62 | 1.5 | 120 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | 35/10
294 | Pervomayskaya | 4+4 | 0.53 | 1.5 | 120 | -0.97 | 0 | 4.2 | 5.17 | 5.17 |  | 1.05 | 4 | 291 | Pervomayskaya | 4+4 | 0.23 | 0.76 | 1.5 | 120 | -0.74 | 0 | 4.2 | 4.94 | 4.94 | 35/10
295 | Podkolodnovka | 2,5+3,2 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 |  | 1.05 | 2.5 | 292 | Podkolodnovka | 2,5+3,2 | 0.19 | 0.98 | 0 | 0 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | 35/10
296 | Yuzhny | 2,5+2,5 | 0.12 | 0 | 0 | 0.12 | 0 | 2.625 | 2.505 | 2.505 |  | 1.05 | 2.5 | 293 | Yuzhny | 2,5+2,5 |  | 0.12 | 0 | 0 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | 35/10
| TOTAL: | [8 empty] | 1225.8127 |  |  |  | 2: TOTAL:; Min 12: 940.6152
| deficit | [8 empty] | 20.245 |  |  |  | 2: deficit; Min 12: 55.9151
| proficit | [8 empty] | 1205.5677 |  |  |  | 2: proficit; Min 12: 884.7001
Note on S1: не нашел
Note on S2: не нашел
Note on S10: не нашел
Note on S119: не нашел
Note on S418: не нашел
Note on S419: не нашел
Note on S420: не нашел
Note on S421: не нашел
Note on Z155: Ivanov_MA:
Note on S34: не нашел
Note on S59: не нашел
Note on S94: не нашел
Note on S234: не нашел
Note on S289: не нашел
Note on S351: не нашел
Note on S417: не нашел