## Орел
table 1
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit/proficit of Main Substation, MVA |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit / proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kv Almazovo | 2.5 | 0.38 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.45 | 0.45 | opened | 1 | SS 35/10 kv Almazovo | 2.5 | 0.041 | 0.421 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.409 | 0.409 | opened
2 | SS 35/10 kv Voronets | 2.5 | 0.31 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.6 | 0.6 | opened | 2 | SS 35/10 kv Voronets | 2.5 | 0 | 0.31 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.6 | 0.6 | opened
3 | SS 35/10 kv Gostoml | 2.5 | 0.65 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.01 | 0.01 | opened | 3 | SS 35/10 kv Gostoml | 2.5 | 0.059 | 0.709 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.891 | 0.891 | opened
4 | SS 35/10 kv Gubkino | 3.2 | 0.47 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.09 | 1.09 | opened | 4 | SS 35/10 kv Gubkino | 3.2 | 0.038 | 0.508 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.052 | 1.052 | opened
5 | SS 35/10 kv Devyatino | 1.6 | 0.31 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.4 | 0.4 | opened | 5 | SS 35/10 kv Devyatino | 1.6 | 0.012 | 0.322 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.388 | 0.388 | opened
6 | SS 35/10 kv Kamenka | 2.5 | 0.76 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.84 | 0.84 | opened | 6 | SS 35/10 kv Kamenka | 2.5 | 0.025 | 0.785 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.815 | 0.815 | opened
7 | SS 35/10 kv Kozminskaya | 2.5 | 0.28 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.01 | 1.01 | opened | 7 | SS 35/10 kv Kozminskaya | 2.5 | 0.056 | 0.336 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.954 | 0.954 | opened
8 | SS 110/35/10 kv Maloarkhangelskaya | 10 | 5.93 | 6.14 | 60 | 0.21 | 0 | 6.14 | 0.21 | 0.21 | opened | 8 | SS 110/35/10 kv Maloarkhangelskaya | 10 | 3.163 | 9.123 | 6.14 | 60 | 6.14 | 0 | 6.14 | -2.983 | -2.983 | closed
| Nom. capacity MV, MVA | 10 | 2.66 | 1.94 | 60 | [7 empty] | Nom. capacity MV, MVA | 10 | 0.075 | 2.735 | 1.94 | 60 | 1.94 | 0 | 1.94 | -0.795
| Nom. capacity LV, MVA | 10 | 3.3 | 4.2 | 60 | 0.9 | 0 | 4.2 | 0.9 |  |  |  | Nom. capacity LV, MVA | 10 | 3.088 | 6.388 | 4.2 | 60 | 4.2 | 0 | 4.2 | -2.188
9 | SS 110/35/10 kv Novopolevo | 16 | 3.13 | 3.71 | 30 | 3.71 | 0 | 3.71 | 0.58 | -0.27 | closed | 9 | SS 110/35/10 kv Novopolevo | 16 | 0.619 | 3.749 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.039 | -0.694 | closed
| Nom. capacity MV, MVA | 16 | 1.75 | 2.6 | 30 | [7 empty] | Nom. capacity MV, MVA | 16 | 0.195 | 1.945 | 2.6 | 30 | 2.6 | 0 | 2.6 | 0.655
| Nom. capacity LV, MVA | 16 | 1.38 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.27 |  |  |  | Nom. capacity LV, MVA | 16 | 0.424 | 1.804 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.694
10 | SS 35/10 kv Nikolskaya | 2.5 | 0.6 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.73 | 0.73 | opened | 10 | SS 35/10 kv Nikolskaya | 2.5 | 0.093 | 0.693 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.637 | 0.637 | opened
11 | SS 35/10 kv Paramonovo | 1.8 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | opened | 11 | SS 35/10 kv Paramonovo | 1.8 | 0.082 | 0.232 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.248 | 0.248 | opened
12 | SS 35/10 kv Senkovo | 1.6 | 0.31 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.98 | 0.98 | opened | 12 | SS 35/10 kv Senkovo | 1.6 | 0.111 | 0.421 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.869 | 0.869 | opened
13 | SS 35/10 kv Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | opened | 13 | SS 35/10 kv Somovo | 2.5 | 0.004 | 0.344 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.616 | 0.616 | opened
14 | SS 110/35/10 kv Trosna | 16 | 2.53 | 4.16 | 45 | 4.16 | 0 | 4.16 | 1.63 | 0.72 | opened | 14 | SS 110/35/10 kv Trosna | 16 | 0.156 | 2.696 | 4.16 | 45 | 4.16 | 0 | 4.16 | 1.464 | 1.464 | opened
| Nom. capacity MV, MVA | 16 | 1.46 | 2.36 | 45 | [7 empty] | Nom. capacity MV, MVA | 16 | 0.019 | 1.479 | 2.36 | 45 | 2.36 | 0 | 2.36 | 0.881
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.137 | 1.217 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.583
15 | SS 35/10 kv Shablykino | 5.6 | 0.09 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.71 | 0.71 | opened | 15 | SS 35/10 kv Shablykino | 5.6 | 0.015 | 0.105 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.695 | 0.695 | opened
16 | SS 35/10 kv Yuryevo | 2.5 | 0.18 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.89 | 0.89 | opened | 16 | SS 35/10 kv Yuryevo | 2.5 | 0.065 | 0.245 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.825 | 0.825 | opened
17 | SS 110/35/10 kv Region V | 10 | 3.77 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.63 | 1.56 | opened | 17 | SS 110/35/10 kv Region V | 10 | 0.2 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 | 1.36 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | [8 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 3.84 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.56 |  |  |  | Nom. capacity LV, MVA | 10 | 0.2 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36
18 | SS 110/10 kv Pishchevaya | 6.3 | 2.57 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.695 | -0.695 | closed | 18 | SS 110/10 kv Pishchevaya | 6.3 | 2.353 | 4.923 | 1.875 | 60 | 1.875 | 0 | 1.875 | -3.048 | -3.048 | closed
19 | SS 110/10 kv Telchye | 3.2 | 1.65 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.19 | -0.19 | closed | 19 | SS 110/10 kv Telchye | 3.2 | 0.231 | 1.881 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.421 | -0.421 | closed
20 | SS 110/10 kv B.Chern | 2.5 | 0.44 | 1 | 120 | 1 | 0 | 1 | 0.56 | 0.56 | opened | 20 | SS 110/10 kv B.Chern | 2.5 | 0.006 | 0.446 | 1 | 120 | 1 | 0 | 1 | 0.554 | 0.554 | opened
21 | SS 35/10 kv Bashkatovo | 1.6 | 0.37 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.43 | 0.43 | opened | 21 | SS 35/10 kv Bashkatovo | 1.6 | 0.018 | 0.388 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.412 | 0.412 | opened
22 | SS 35/10 kv Vysokoe | 1.6 | 0.28 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.96 | 0.96 | opened | 22 | SS 35/10 kv Vysokoe | 1.6 | 0.033 | 0.313 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.927 | 0.927 | opened
23 | SS 35/10 kv Gladkoe | 2.5 | 0.43 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.03 | 1.03 | opened | 23 | SS 35/10 kv Gladkoe | 2.5 | 0.014 | 0.444 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.016 | 1.016 | opened
24 | SS 35/10 kv Lykovo | 2.5 | 0.82 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.42 | 0.42 | opened | 24 | SS 35/10 kv Lykovo | 2.5 | 0.14 | 0.96 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.28 | 0.28 | opened
25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened | 25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.3 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.38 | 0.38 | opened | 26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.044 | 0.344 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.336 | 0.336 | opened
27 | SS 35/10 kv Koptevo | 2.5 | 0.28 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.16 | 0.16 | opened | 27 | SS 35/10 kv Koptevo | 2.5 | 0 | 0.28 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.16 | 0.16 | opened
28 | SS 110/35/10/6 kv Meat processing factory | 10 | 1.57 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.56 | 0.32 | opened | 28 | SS 110/35/10/6 kv Meat processing factory | 10 | 0.012 | 1.829 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.301 | 0.301 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | [7 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.81 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.32 |  |  |  | Nom. capacity LV, MVA | 10 | 0.019 | 1.829 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.301
29 | SS 110/35/10 kv Shatilovo | 10 | 1.43 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.74 | -0.74 | closed | 29 | SS 110/35/10 kv Shatilovo | 10 | 0.005 | 1.503 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.813 | -0.813 | closed
| Nom. capacity MV, MVA | 10 | 0.53 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.37 |  |  |  | Nom. capacity MV, MVA | 10 | 0.011 | 0.541 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.381
| Nom. capacity LV, MVA | 10 | 0.91 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.38 |  |  |  | Nom. capacity LV, MVA | 10 | 0.052 | 0.962 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.432
30 | SS 110/35/10 kv Sovkhoznaya | 10 | 6.46 | 8.96 | 120 | 8.96 | 0 | 8.96 | 2.5 | 1.23 | opened | 30 | SS 110/35/10 kv Sovkhoznaya | 10 | 1.462 | 7.952 | 8.96 | 120 | 8.96 | 0 | 8.96 | 1.008 | -0.15 | closed
| Nom. capacity MV, MVA | 10 | 5.39 | 6.62 | 120 | 6.62 | 0 | 6.62 | 1.23 |  |  |  | Nom. capacity MV, MVA | 10 | 1.38 | 6.77 | 6.62 | 120 | 6.62 | 0 | 6.62 | -0.15
| Nom. capacity LV, MVA | 10 | 1.1 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.24 |  |  |  | Nom. capacity LV, MVA | 10 | 0.082 | 1.182 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.158
31 | SS 35/10 kv Danilovskaya | 1.6 | 0.45 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.09 | 0.09 | opened | 31 | SS 35/10 kv Danilovskaya | 1.6 | 0 | 0.45 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.09 | 0.09 | opened
32 | SS 35/10 kv Korseevo | 1.8 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | opened | 32 | SS 35/10 kv Korseevo | 1.8 | 0 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | opened
33 | SS 35/10 kv Lipovets | 2.5 | 0.82 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.57 | 0.57 | opened | 33 | SS 35/10 kv Lipovets | 2.5 | 0.022 | 0.842 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.548 | 0.548 | opened
34 | SS 35/10 kv Misaylovo | 1.6 | 0.47 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.13 | 1.13 | opened | 34 | SS 35/10 kv Misaylovo | 1.6 | 0.004 | 0.474 | 1.6 |  | 1.6 | 0 | 1.6 | 1.126 | 1.126 | openedт
35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | opened | 35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.009 | 0.269 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.041 | 0.041 | opened
36 | SS 35/10 kv Pankovo | 1.8 | 0.53 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.07 | 1.07 | opened | 36 | SS 35/10 kv Pankovo | 1.8 | 0.011 | 0.541 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.059 | 1.059 | opened
37 | SS 35/10 kv Sudbishchi | 2.5 | 0.73 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.87 | 0.87 | opened | 38 | SS 35/10 kv Sudbishchi | 2.5 | 0.015 | 0.745 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.855 | 0.855 | opened
38 | SS 35/10 kv Tim | 1.6 | 0.71 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.89 | 0.89 | opened | 39 | SS 35/10 kv Tim | 1.6 | 0.013 | 0.723 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.877 | 0.877 | opened
39 | SS 35/10 kv Topki | 1 | 0.36 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.24 | 1.24 | opened | 40 | SS 35/10 kv Topki | 1 | 0.006 | 0.366 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.234 | 1.234 | opened
40 | SS 35/10 kv Yarishche | 2.5 | 0.4 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.2 | 1.2 | opened | 41 | SS 35/10 kv Yarishche | 2.5 | 0.039 | 0.439 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.161 | 1.161 | opened
41 | SS 110/10 kv Alshanskaya | 10+10 | 6.6 | 3.88 | 30 | 2.72 | 0 | 10.5 | 7.78 | 7.78 | opened | 42 | SS 110/10 kv Alshanskaya | 10+10 | 0.554 | 7.154 | 3.88 | 30 | 3.274 | 0 | 10.5 | 7.226 | 7.226 | opened
42 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | opened | 43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.065 | 0.465 | 0.93 | 90 | -0.465 | 0 | 2.625 | 3.09 | 3.09 | opened
43 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened | 44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.035 | 0.595 | 0 |  | 0.595 | 0 | 1.68 | 1.085 | 1.085 | opened
44 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.9 | 3.06 | 90 | -0.16 | 0 | 10.5 | 10.66 | 10.29 | opened | 45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.128 | 4.998 | 3.06 | 90 | 1.938 | 0 | 10.5 | 8.562 | 8.562 | opened
45 | Nom. capacity MV, MVA | 10+10 | 2.64 | 2.43 | 90 | 0.21 | 0 | 10.5 | 10.29 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.646 | 3.286 | 2.43 | 90 | 0.856 | 0 | 10.5 | 9.644
| Nom. capacity LV, MVA | 10+10 | 0.23 | 0.63 | 90 | -0.4 | 0 | 10.5 | 10.9 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.482 | 1.712 | 0.63 | 90 | 1.082 | 0 | 10.5 | 9.418
| SS 35/10 kv Baklanovo | 1,6+1,6 | 0.83 | 0.64 | 60 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.031 | 0.861 | 0.64 | 60 | 0.221 | 0 | 1.68 | 1.459 | 1.459 | opened
46 | SS 35/10 kv Biofactory | 6,3+6,3 | 2.88 | 2.05 | 90 | 0.83 | 0 | 6.615 | 5.785 | 5.785 | opened | 47 | SS 35/10 kv Biofactory | 6,3+6,3 | 0.566 | 3.446 | 2.05 | 90 | 1.396 | 0 | 6.615 | 5.219 | 5.219 | opened
47 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.85 | 1.46 | 30 | 2.39 | 0 | 2.625 | 0.235 | 0.235 | opened | 48 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.692 | 7.542 | 1.46 | 30 | 6.082 | 0 | 2.625 | -3.457 | -3.457 | closed
48 | SS 110/10 kv Vostochnaya | 15+15 | 14.87 | 5.87 | 120 | 9 | 0 | 15.75 | 6.75 | 6.75 | opened | 49 | SS 110/10 kv Vostochnaya | 15+15 | 0 | 14.87 | 5.87 | 120 | 9 |  | 15.75 | 6.75 | 6.75 | opened
49 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 3.64 | 0.45 | 60 | 3.19 | 0 | 10.5 | 7.31 | 7.31 | opened | 50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 0.177 | 3.807 | 0.45 | 60 | 3.357 | 0 | 10.5 | 7.143 | 7.143 | opened
50 | Nom. capacity MV, MVA | 10+10 | 0.31 | 0 | 0 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.012 | 0.322 | 0 |  | 0.322 | 0 | 10.5 | 10.178
| Nom. capacity LV, MVA | 10+10 | 3.32 | 0.45 | 60 | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.165 | 3.485 | 0.45 | 60 | 3.035 | 0 | 10.5 | 7.465
| SS 110/10 kv Zheleznodorozhnaya | 16+16 | 12.57 | 3.98 | 180 | 8.59 | 0 | 16.8 | 8.21 | 8.21 | opened | 51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 1.942 | 14.512 | 3.98 | 180 | 10.532 | 0 | 16.8 | 6.268 | 6.268 | opened
51 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 1.06 | 0.64 | 60 | 0.42 | 0 | 1.89 | 1.47 | 1.47 | opened | 52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 0.021 | 1.081 | 0.64 | 60 | 0.441 | 0 | 1.89 | 1.449 | 1.449 | opened
52 | SS 110/6 kv Zavodskaya | 40+25 | 16.07 | 4.39 | 150 | 11.68 | 0 | 26.25 | 14.57 | 14.57 | opened | 53 | SS 110/6 kv Zavodskaya | 40+25 | 0 | 16.07 | 4.39 | 150 | 11.68 | 0 | 26.25 | 14.57 | 14.57 | opened
53 | SS 110/6 kv Zapadnaya | 25+25 | 25.03 | 0 | 120 | 25.03 | 0 | 26.25 | 1.22 | 1.22 | opened | 54 | SS 110/6 kv Zapadnaya | 25+25 | 19.118 | 44.148 | 5.37 | 120 | 38.778 | 0 | 26.25 | -12.528 | -12.528 | closed
54 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 2.08 | 1.48 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 0.62 | 2.7 | 1.48 | 60 | 1.22 | 0 | 2.625 | 1.405 | 1.405 | opened
55 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 1.16 | 1.18 | 30 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened | 56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 0.071 | 1.231 | 1.18 | 30 | 0.051 | 0 | 1.68 | 1.629 | 1.629 | opened
56 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.28 | 1.44 | 90 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened | 57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 6.715 | 12.025 | 1.44 | 90 | 10.585 | 0 | 10.5 | -0.085 | -0.085 | closed
57 | Nom. capacity MV, MVA | 10+10 | 1.49 | 1 | 90 | 0.49 | 0 | 10.5 | 10.01 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.49 | 1 | 90 | 0.49 | 0 | 10.5 | 10.01
| Nom. capacity LV, MVA | 10+10 | 3.82 | 0.44 | 90 | 3.38 | 0 | 10.5 | 7.12 |  |  |  | Nom. capacity LV, MVA | 10+10 | 6.715 | 10.535 | 0.44 | 90 | 10.095 | 0 | 10.5 | 0.405
| SS 110/35/10 kv Kromskaya | 16+16 | 8.63 | 6.83 | 45 | 1.8 | 0 | 16.8 | 15 | 14.42 | opened | 58 | SS 110/35/10 kv Kromskaya | 16+16 | 6.674 | 15.884 | 6.83 | 45 | 9.054 | 0 | 16.8 | 7.746 | 7.746 | opened
58 | Nom. capacity MV, MVA | 16+16 | 5 | 5 | 45 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 6.085 | 11.085 | 5 | 45 | 6.085 | 0 | 16.8 | 10.715
| Nom. capacity LV, MVA | 16+16 | 4.21 | 1.83 | 45 | 2.38 | 0 | 16.8 | 14.42 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.589 | 4.799 | 1.83 | 45 | 2.969 | 0 | 16.8 | 13.831
| SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 1.16 | 0.95 | 30 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 0.019 | 1.179 | 0.95 | 30 | 0.229 | 0 | 2.625 | 2.396 | 2.396 | opened
59 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.83 | 0 | - | 0.83 | 0 | 1.68 | 0.85 | 0.85 | opened | 60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.005 | 0.835 | 0 |  | 0.835 | 0 | 1.68 | 0.845 | 0.845 | opened
60 | SS 35/10 kv Kutafino | 1,6+1,6 | 0.27 | 0.83 | 30 | -0.56 | 0 | 1.68 | 2.24 | 2.24 | opened | 61 | SS 35/10 kv Kutafino | 1,6+1,6 | 5.893 | 6.163 | 0.83 | 30 | 5.333 | 0 | 1.68 | -3.653 | -3.653 | closed
61 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.6 | 1.59 | 30 | -0.99 | 0 | 2.625 | 3.615 | 3.615 | opened | 62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.058 | 0.658 | 1.59 | 30 | -0.932 | 0 | 2.625 | 3.557 | 3.557 | opened
62 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.43 | 0.47 | 60 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened | 63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.014 | 0.444 | 0.47 | 60 | -0.026 | 0 | 1.05 | 1.076 | 1.076 | opened
63 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.42 | 0.99 | 90 | -0.57 | 0 | 1.89 | 2.46 | 2.46 | opened | 64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.012 | 0.432 | 0.99 | 90 | -0.558 | 0 | 1.89 | 2.448 | 2.448 | opened
64 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.54 | 1.7 | 30 | -1.16 | 0 | 5.88 | 7.04 | 7.04 | opened | 65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.353 | 0.893 | 1.7 | 30 | -0.807 | 0 | 5.88 | 6.687 | 6.687 | opened
65 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 7.38 | 1.41 | 90 | 5.97 | 0 | 10.5 | 4.53 | 4.53 | opened | 66 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 1.293 | 8.683 | 1.41 | 90 | 7.273 | 0 | 10.5 | 3.227 | 3.227 | opened
66 | Nom. capacity MV, MVA | 10+10 | 1.3 | 0.86 | 90 | 0.44 | 0 | 10.5 | 10.06 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.135 | 1.435 | 0.86 | 90 | 0.575 | 0 | 10.5 | 9.925
| Nom. capacity LV, MVA | 10+10 | 6.09 | 0.55 | 90 | 5.54 | 0 | 10.5 | 4.96 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.158 | 7.248 | 0.55 | 90 | 6.698 | 0 | 10.5 | 3.802
| SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.58 | 1.63 | 45 | -1.05 | 0 | 2.625 | 3.675 | 3.675 | opened | 67 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.021 | 0.601 | 1.63 | 45 | -1.029 | 0 | 2.625 | 3.654 | 3.654 | opened
67 | SS 35/10 kv Novopetrovka | 2,5+1,6 | 0.45 | 0.73 | 60 | -0.28 | 0 | 1.68 | 1.96 | 1.96 | opened | 68 | SS 35/10 kv Novopetrovka | 2,5+1,6 | 0.039 | 0.489 | 0.73 | 60 | -0.241 | 0 | 1.68 | 1.921 | 1.921 | opened
68 | SS 35/10 kv Putimets | 2,5+2,5 | 0.82 | 1.53 | 90 | -0.71 | 0 | 2.625 | 3.335 | 3.335 | opened | 69 | SS 35/10 kv Putimets | 2,5+2,5 | 0.175 | 0.995 | 1.53 | 90 | -0.535 | 0 | 2.625 | 3.16 | 3.16 | opened
69 | SS 110/10 kv Pishchevaya | 40+25 | 6.16 | 2.22 | 60 | 3.94 | 0 | 26.25 | 22.31 | 22.31 | opened | 70 | SS 110/10 kv Pishchevaya | 40+25 | 0.426 | 6.586 | 2.22 | 60 | 4.366 | 0 | 26.25 | 21.884 | 21.884 | opened
70 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.49 | 0.65 | 90 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | opened | 71 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.016 | 0.506 | 0.65 | 90 | -0.144 | 0 | 2.625 | 2.769 | 2.769 | opened
71 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 3.17 | 1.98 | 45 | 1.19 | 0 | 10.5 | 9.31 | 9.21 | opened | 72 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 1.01 | 4.19 | 1.98 | 45 | 2.21 | 0 | 10.5 | 8.29 | 8.29 | opened
72 | Nom. capacity MV, MVA | 10+10 | 1.32 | 1.41 | 45 | -0.09 | 0 | 10.5 | 10.59 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.188 | 1.508 | 1.41 | 45 | 0.098 | 0 | 10.5 | 10.402
| Nom. capacity LV, MVA | 10+10 | 1.86 | 0.57 | 45 | 1.29 | 0 | 10.5 | 9.21 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.822 | 2.682 | 0.57 | 45 | 2.112 | 0 | 10.5 | 8.388
| SS 35/10 kv Streletskaya | 4+4 | 2.24 | 0.91 | 90 | 1.33 | 0 | 4.2 | 2.87 | 2.87 | opened | 73 | SS 35/10 kv Streletskaya | 4+4 | 1.098 | 3.338 | 0.91 | 90 | 2.428 | 0 | 4.2 | 1.772 | 1.772 | opened
73 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 29.48 | 3.86 | 180 | 25.62 | 0 | 68.25 | 42.63 | 19 | opened | 74 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 8.138 | 37.518 | 3.86 | 180 | 33.658 | 0 | 68.25 | 34.592 | 34.592 | opened
74 | Nom. capacity MV, MVA | 20+20 | 7.1 | 5.1 | 90 | 2 | 0 | 21 | 19 |  |  |  | Nom. capacity MV, MVA | 20+20 | 1.798 | 8.898 | 5.1 | 90 | 3.798 | 0 | 21 | 17.202
| Nom. capacity LV, MVA | 20+20+25+40 | 22.28 | 3.86 | 180 | 18.42 | 0 | 68.25 | 49.83 |  |  |  | Nom. capacity LV, MVA | 20+20+25+40 | 6.34 | 28.62 | 3.86 | 180 | 24.76 | 0 | 68.25 | 43.49
| SS 35/10 kv Soskovskaya | 4+3,2 | 1.49 | 0.64 | 90 | 0.85 | 0 | 3.36 | 2.51 | 2.51 | opened | 75 | SS 35/10 kv Soskovskaya | 4+3,2 | 0.068 | 1.558 | 0.64 | 90 | 0.918 | 0 | 3.36 | 2.442 | 2.442 | opened
75 | SS 35/10 kv Trosna | 5,6+3,2 | 0.81 | 1.76 | 30 | -0.95 | 0 | 3.36 | 4.31 | 4.31 | opened | 76 | SS 35/10 kv Trosna | 5,6+3,2 | 0.024 | 0.834 | 1.76 | 30 | -0.926 | 0 | 3.36 | 4.286 | 4.286 | opened
76 | SS 110/10 kv Khimmash | 25+25 | 8.13 | 1.51 | 120 | 6.62 | 0 | 26.25 | 19.63 | 19.63 | opened | 77 | SS 110/10 kv Khimmash | 25+25 | 3.582 | 11.712 | 1.51 | 120 | 10.202 | 0 | 26.25 | 16.048 | 16.048 | opened
77 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 1.12 | 0 | - | 1.12 | 0 | 5.88 | 4.76 | 4.76 | opened | 78 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0 | 1.12 | 0 |  | 1.12 | 0 | 5.88 | 4.76 | 4.76 | opened
78 | SS 35/10 kv Khotynetskaya | 4+2,5 | 2.47 | 1.49 | 80 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened | 79 | SS 35/10 kv Khotynetskaya | 4+2,5 | 0.581 | 3.051 | 1.49 | 80 | 1.561 | 0 | 2.625 | 1.064 | 1.064 | opened
79 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.53 | 1.03 | 80 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened | 80 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.029 | 0.559 | 1.03 | 80 | -0.471 | 0 | 1.68 | 2.151 | 2.151 | opened
80 | SS 110/10/6 kv Tsentralnaya | 25+25 | 13.82 | 3.46 | 135 | 10.36 | 0 | 26.25 | 15.89 | 15.89 | opened | 81 | SS 110/10/6 kv Tsentralnaya | 25+25 | 0 | 13.82 | 3.46 | 135 | 10.36 | 0 | 26.25 | 15.89 | 15.89 | opened
81 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 2.37 | 1.36 | 30 | 1.01 | 0 | 6.615 | 5.605 | 5.605 | opened | 82 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 0.093 | 2.483 | 1.36 | 30 | 1.123 | 0 | 6.615 | 5.492 | 5.492 | opened
82 | Nom. capacity MV, MVA | 6,3+6,3 | 0.97 | 0.54 | 30 | 0.43 | 0 | 6.615 | 6.185 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.048 | 1.018 | 0.54 | 30 | 0.478 | 0 | 6.615 | 6.137
| Nom. capacity LV, MVA | 6,3+6,3 | 1.42 | 0.82 | 30 | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.045 | 1.465 | 0.82 | 30 | 0.645 | 0 | 6.615 | 5.97
| SS 110/35/10 kv Shakhovo | 10+10 | 2.51 | 2.55 | 120 | -0.04 | 0 | 10.5 | 10.54 | 10.07 | opened | 83 | SS 110/35/10 kv Shakhovo | 10+10 | 0.34 | 2.86 | 2.55 | 120 | 0.31 | 0 | 10.5 | 10.19 | 10.19 | opened
83 | Nom. capacity MV, MVA | 10+10 | 0.82 | 0.39 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.175 | 0.995 | 0.39 | 120 | 0.605 | 0 | 10.5 | 9.895
| Nom. capacity LV, MVA | 10+10 | 1.7 | 2.16 | 120 | -0.46 | 0 | 10.5 | 10.96 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.165 | 1.865 | 2.16 | 120 | -0.295 | 0 | 10.5 | 10.795
| SS 35/10 kv Shepino | 2,5+1,6 | 1.4 | 1.1 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 84 | SS 35/10 kv Shepino | 2,5+1,6 | 0.234 | 1.634 | 1.1 | 120 | 0.534 | 0 | 1.68 | 1.146 | 1.146 | opened
84 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 10.72 | 0.74 | 60 | 9.98 | 0 | 26.25 | 16.27 | 16.27 | opened | 85 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 1.176 | 11.896 | 0.74 | 60 | 11.156 | 0 | 26.25 | 15.094 | 15.094 | opened
85 | SS 110/10 kv Yuzhnaya | 10+10 | 9.07 | 1.05 | 90 | 8.02 | 0 | 10.5 | 2.48 | 2.48 | opened | 86 | SS 110/10 kv Yuzhnaya | 10+10 | 2.122 | 11.192 | 1.05 | 90 | 10.142 | 0 | 10.5 | 0.358 | 0.358 | opened
86 | SS 220/110/10 kv Mtsensk | 40+40 | 9.81 | 0 | - | 9.81 | 0 | 42 | 32.19 | 32.19 | opened | 87 | SS 220/110/10 kv Mtsensk | 40+40 | 0.721 | 10.531 | 0 |  | 10.531 | 0 | 42 | 31.469 | 31.469 | opened
87 | SS 110/35/10 kv Kommash | 10+16 | 10.51 | 4.65 | 90 | 5.86 | 0 | 10.5 | 4.64 | 4.64 | opened | 88 | SS 110/35/10 kv Kommash | 10+16 | 0.111 | 10.611 | 4.65 | 90 | 5.961 | 0 | 10.5 | 4.539 | 4.539 | opened
88 | Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.5 | 4.65 | 90 | 5.85 | 0 | 10.5 | 4.65 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.111 | 10.611 | 4.65 | 90 | 5.961 | 0 | 10.5 | 4.539
| SS 110/35/10 kv Novosergievka | 6,3+10 | 2.55 | 4.13 | 120 | -1.58 | 0 | 6.615 | 8.195 | 6.695 | opened | 89 | SS 110/35/10 kv Novosergievka | 6,3+10 | 0.237 | 2.797 | 4.13 | 120 | -1.333 | 0 | 6.615 | 7.948 | 7.948 | opened
89 | Nom. capacity MV, MVA | 6,3+10 | 2.32 | 2.4 | 120 | -0.08 | 0 | 6.615 | 6.695 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.237 | 2.557 | 2.4 | 120 | 0.157 | 0 | 6.615 | 6.458
| Nom. capacity LV, MVA | 6,3+10 | 0.24 | 1.73 | 120 | -1.49 | 0 | 6.615 | 8.105 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.24 | 1.73 | 120 | -1.49 | 0 | 6.615 | 8.105
| SS 110/10 kv 1 Voin | 6,3+6,3 | 2.33 | 1.83 | 120 | 0.5 | 0 | 6.615 | 6.115 | 6.115 | opened | 90 | SS 110/10 kv 1 Voin | 6,3+6,3 | 2.825 | 5.155 | 1.83 | 120 | 3.325 | 0 | 6.615 | 3.29 | 3.29 | opened
90 | SS 110/35/10 kv Zalegoshch | 10+16 | 5.94 | 3.95 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened | 91 | SS 110/35/10 kv Zalegoshch | 10+16 | 0.833 | 6.743 | 3.95 | 120 | 2.793 | 0 | 10.5 | 7.707 | 7.707 | opened
91 | Nom. capacity MV, MVA | 10+16 | 2.48 | 2.39 | 120 | 0.09 | 0 | 10.5 | 10.41 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.078 | 2.558 | 2.39 | 120 | 0.168 | 0 | 10.5 | 10.332
| Nom. capacity LV, MVA | 10+16 | 3.43 | 1.56 | 120 | 1.87 | 0 | 10.5 | 8.63 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.755 | 4.185 | 1.56 | 120 | 2.625 | 0 | 10.5 | 7.875
| SS 110/10 kv Kochety | 2,5+2,5 | 0.34 | 0.66 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened | 92 | SS 110/10 kv Kochety | 2,5+2,5 | 0.165 | 0.505 | 0.66 | 120 | -0.155 | 0 | 2.625 | 2.78 | 2.78 | opened
92 | SS 110/35/10 kv Bolkhov | 10+10 | 8.61 | 4.1 | 120 | 4.51 | 0 | 10.5 | 5.99 | 5.99 | opened | 93 | SS 110/35/10 kv Bolkhov | 10+10 | 0.857 | 9.467 | 4.1 | 120 | 5.367 | 0 | 10.5 | 5.133 | 5.133 | opened
93 | Nom. capacity MV, MVA | 10+10 | 3.01 | 2.45 | 120 | 0.56 | 0 | 10.5 | 9.94 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.802 | 3.812 | 2.45 | 120 | 1.362 | 0 | 10.5 | 9.138
| Nom. capacity LV, MVA | 10+10 | 5.6 | 1.65 | 120 | 3.95 | 0 | 10.5 | 6.55 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.055 | 5.655 | 1.65 | 120 | 4.005 | 0 | 10.5 | 6.495
| SS 110/35/10 kv Novosil | 10+10 | 4.69 | 2.98 | 120 | 1.71 | 0 | 10.5 | 8.79 | 8.79 | opened | 94 | SS 110/35/10 kv Novosil | 10+10 | 0.123 | 4.813 | 2.98 | 120 | 1.833 | 0 | 10.5 | 8.667 | 8.667 | opened
94 | Nom. capacity MV, MVA | 10+10 | 2.4 | 1.46 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.074 | 2.474 | 1.46 | 120 | 1.014 | 0 | 10.5 | 9.486
| Nom. capacity LV, MVA | 10+10 | 2.29 | 1.52 | 120 | 0.77 | 0 | 10.5 | 9.73 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.049 | 2.339 | 1.52 | 120 | 0.819 | 0 | 10.5 | 9.681
| SS 110/35/10 kv Znamenskaya | 10+10 | 2.2 | 1.78 | 120 | 0.42 | 0 | 10.5 | 10.08 | 10.08 | opened | 95 | SS 110/35/10 kv Znamenskaya | 10+10 | 0.096 | 2.296 | 1.78 | 120 | 0.516 | 0 | 10.5 | 9.984 | 9.984 | opened
95 | Nom. capacity MV, MVA | 10+10 | 0.49 | 0.34 | 120 | 0.15 | 0 | 10.5 | 10.35 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.018 | 0.508 | 0.34 | 120 | 0.168 | 0 | 10.5 | 10.332
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.078 | 1.788 | 1.44 | 120 | 0.348 | 0 | 10.5 | 10.152
| SS 35/10 kv Apalkovo | 1,8+1,8 | 0.43 | 0.48 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened | 96 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0.192 | 0.622 | 0.48 | 120 | 0.142 | 0 | 1.89 | 1.748 | 1.748 | opened
96 | SS 35/10 kv Podberyozovo | 4+1 | 0.26 | 0.59 | 120 | -0.33 | 0 | 1.05 | 1.38 | 1.38 | opened | 97 | SS 35/10 kv Podberyozovo | 4+1 | 0.016 | 0.276 | 0.59 | 120 | -0.314 | 0 | 1.05 | 1.364 | 1.364 | opened
97 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.51 | 0 |  | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened | 98 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.006 | 0.516 | 0 |  | 0.516 | 0 | 1.68 | 1.164 | 1.164 | opened
98 | SS 35/10 kv Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened | 99 | SS 35/10 kv Alyoshnya | 1+1 | 0.02 | 0.36 | 0.24 | 120 | 0.12 | 0 | 1.05 | 0.93 | 0.93 | opened
99 | SS 35/10 kv Lomovoe | 2,5+2,5 | 1 | 0 | - | 1 | 0 | 2.625 | 1.625 | 1.625 | opened | 100 | SS 35/10 kv Lomovoe | 2,5+2,5 | 0.023 | 1.023 | 0 |  | 1.023 | 0 | 2.625 | 1.602 | 1.602 | opened
100 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.91 | 0.63 | 120 | 0.28 |  | 2.625 | 2.345 | 2.345 | opened | 101 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.035 | 0.945 | 0.63 | 120 | 0.315 | 0 | 2.625 | 2.31 | 2.31 | opened
101 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | opened | 102 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | opened
102 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.32 | 0 | - | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened | 103 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0 | 0.32 | 0 |  | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
103 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 1.1 | 0.67 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 104 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.516 | 1.616 | 0.67 | 120 | 0.946 | 0 | 2.625 | 1.679 | 1.679 | opened
104 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 105 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.032 | 0.532 | 0.37 | 120 | 0.162 | 0 | 1.68 | 1.518 | 1.518 | opened
105 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.63 | 0.69 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened | 106 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.017 | 0.647 | 0.69 | 120 | -0.043 | 0 | 2.625 | 2.668 | 2.668 | opened
106 | SS 35/10 kv Odinok | 1,6+1,6 | 0.38 | 0 | - | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened | 107 | SS 35/10 kv Odinok | 1,6+1,6 | 0.039 | 0.419 | 0 |  | 0.419 | 0 | 1.68 | 1.261 | 1.261 | opened
107 | SS 35/10 kv Uzkoe | 1,6+1 | 0.21 | 0.25 | 120 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened | 108 | SS 35/10 kv Uzkoe | 1,6+1 | 0.018 | 0.228 | 0.25 | 120 | -0.022 | 0 | 1.05 | 1.072 | 1.072 | opened
108 | SS 35/10 kv Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 109 | SS 35/10 kv Korsakovo | 2,5+4 | 0.072 | 0.832 | 0.69 | 120 | 0.142 | 0 | 2.625 | 2.483 | 2.483 | opened
109 | SS 35/10 kv Paramonovo | 4+2,5 | 0.88 | 0.76 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 110 | SS 35/10 kv Paramonovo | 4+2,5 | 0.018 | 0.898 | 0.76 | 120 | 0.138 | 0 | 2.625 | 2.487 | 2.487 | opened
110 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.22 | 0 | - | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 111 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.034 | 0.254 | 0 |  | 0.254 | 0 | 1.68 | 1.426 | 1.426 | opened
111 | SS 110/35/10 kv Verkhovye I | 16+10 | 8.57 | 3.65 | 120 | 4.92 | 0 | 10.5 | 5.58 | 5.58 | opened | 112 | SS 110/35/10 kv Verkhovye I | 16+10 | 0.218 | 8.848 | 3.65 | 120 | 5.198 | 0 | 10.5 | 5.302 | 5.302 | opened
112 | Nom. capacity MV, MVA | 16+10 | 3.01 | 2.05 | 120 | 0.96 | 0 | 10.5 | 9.54 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.037 | 3.047 | 2.05 | 120 | 0.997 | 0 | 10.5 | 9.503
| Nom. capacity LV, MVA | 16+10 | 5.62 | 1.6 | 120 | 4.02 | 0 | 10.5 | 6.48 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.181 | 5.801 | 1.6 | 120 | 4.201 | 0 | 10.5 | 6.299
| SS 110/35/10 kv Verkhovye II | 40+40 | 16.92 | 0.3 | - | 16.62 | 0 | 42 | 25.38 | 25.38 | opened | 113 | SS 110/35/10 kv Verkhovye II | 40+40 | 0.009 | 16.959 | 0.3 |  | 16.659 | 0 | 42 | 25.341 | 25.341 | opened
113 | Nom. capacity MV, MVA | 40+40 | 0.47 | 0.3 | - | 0.17 | 0 | 42 | 41.83 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.009 | 0.479 | 0.3 |  | 0.179 | 0 | 42 | 41.821
| Nom. capacity LV, MVA | 40+40 | 16.48 | 0 | - | 16.48 | 0 | 42 | 25.52 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 16.48 | 0 |  | 16.48 | 0 | 42 | 25.52
| SS 110/35/10 kv Dolgoe | 16+10 | 7.02 | 3.38 | 120 | 3.64 | 0 | 10.5 | 6.86 | 6.86 | opened | 114 | SS 110/35/10 kv Dolgoe | 16+10 | 0.05 | 7.08 | 3.38 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | opened
114 | Nom. capacity MV, MVA | 16+10 | 2.67 | 2.38 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.025 | 2.695 | 2.38 | 120 | 0.315 | 0 | 10.5 | 10.185
| Nom. capacity LV, MVA | 16+10 | 4.36 | 1 | 120 | 3.36 | 0 | 10.5 | 7.14 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.025 | 4.385 | 1 | 120 | 3.385 | 0 | 10.5 | 7.115
| SS 110/35/10 kv Kolpny-110 | 10+16 | 5.8 | 2.79 | 120 | 3.01 | 0 | 10.5 | 7.49 | 7.49 | opened | 115 | SS 110/35/10 kv Kolpny-110 | 10+16 | 0.099 | 5.879 | 2.79 | 120 | 3.089 | 0 | 10.5 | 7.411 | 7.411 | opened
115 | Nom. capacity MV, MVA | 10+16 | 3.92 | 2.46 | 120 | 1.46 | 0 | 10.5 | 9.04 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.028 | 3.948 | 2.46 | 120 | 1.488 | 0 | 10.5 | 9.012
| Nom. capacity LV, MVA | 10+16 | 1.86 | 0.33 | 120 | 1.53 | 0 | 10.5 | 8.97 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.071 | 1.931 | 0.33 | 120 | 1.601 | 0 | 10.5 | 8.899
| SS 110/35/10 kv Kr. Zarya | 10+10 | 5.24 | 1.54 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | opened | 116 | SS 110/35/10 kv Kr. Zarya | 10+10 | 0.082 | 5.332 | 1.54 | 120 | 3.792 | 0 | 10.5 | 6.708 | 6.708 | opened
116 | Nom. capacity MV, MVA | 10+10 | 1.69 | 1.29 | 120 | 0.4 | 0 | 10.5 | 10.1 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.024 | 1.714 | 1.29 | 120 | 0.424 | 0 | 10.5 | 10.076
| Nom. capacity LV, MVA | 10+10 | 3.56 | 0.25 | 120 | 3.31 | 0 | 10.5 | 7.19 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.058 | 3.618 | 0.25 | 120 | 3.368 | 0 | 10.5 | 7.132
| SS 110/35/10 kv Pokrovskaya | 10+10 | 5.84 | 2.84 | 120 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened | 117 | SS 110/35/10 kv Pokrovskaya | 10+10 | 0.463 | 6.323 | 2.84 | 120 | 3.483 | 0 | 10.5 | 7.017 | 7.017 | opened
117 | Nom. capacity MV, MVA | 10+10 | 2.41 | 2.12 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.135 | 2.545 | 2.12 | 120 | 0.425 | 0 | 10.5 | 10.075
| Nom. capacity LV, MVA | 10+10 | 3.45 | 0.72 | 120 | 2.73 | 0 | 10.5 | 7.77 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.328 | 3.778 | 0.72 | 120 | 3.058 | 0 | 10.5 | 7.442
| SS 110/35/6 kv Cherkasskaya | 40+25 | 29.08 | 13.39 | 120 | 15.69 | 0 | 26.25 | 10.56 | 10.56 | opened | 118 | SS 110/35/6 kv Cherkasskaya | 40+25 | 3.644 | 32.874 | 13.39 | 120 | 19.484 | 0 | 26.25 | 6.766 | 6.766 | opened
118 | Nom. capacity MV, MVA | 40+25 | 13.36 | 10.84 | 120 | 2.52 | 0 | 26.25 | 23.73 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.679 | 16.039 | 10.84 | 120 | 5.199 | 0 | 26.25 | 21.051
| Nom. capacity LV, MVA | 40+25 | 15.87 | 2.55 | 120 | 13.32 | 0 | 26.25 | 12.93 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0.965 | 16.835 | 2.55 | 120 | 14.285 | 0 | 26.25 | 11.965
| SS 110/6 kv Plastmass | 16+16 | 10.73 | 0 | - | 10.73 | 0 | 16.8 | 6.07 | 6.07 | opened | 119 | SS 110/6 kv Plastmass | 16+16 | 0 | 10.73 | 0 |  | 10.73 | 0 | 16.8 | 6.07 | 6.07 | opened
119 | SS 110/10 kv PM | 10+10 | 5.07 | 0 | - | 5.07 | 0 | 10.5 | 5.43 | 5.43 | opened | 120 | SS 110/10 kv PM | 10+10 | 0 | 5.07 | 0 |  | 5.07 | 0 | 10.5 | 5.43 | 5.43 | opened
120 | SS 110/10 kv Rechitsa | 6,3+6,3 | 1.81 | 1.85 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened | 121 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.033 | 1.843 | 1.85 | 120 | -0.007 | 0 | 6.615 | 6.622 | 6.622 | opened
121 | SS 110/10 kv R.Brod | 5,6+10 | 1.69 | 0.29 | 120 | 1.4 | 0 | 5.88 | 4.48 | 4.48 | opened | 122 | SS 110/10 kv R.Brod | 5,6+10 | 0.681 | 2.371 | 0.29 | 120 | 2.081 | 0 | 5.88 | 3.799 | 3.799 | opened
122 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.61 | 0.13 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened | 123 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.054 | 0.664 | 0.13 | 120 | 0.534 | 0 | 1.68 | 1.146 | 1.146 | opened
123 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 1.6 | 0.65 | 120 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened | 124 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 0.052 | 1.652 | 0.65 | 120 | 1.002 | 0 | 2.625 | 1.623 | 1.623 | opened
124 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0.76 | 0.43 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 125 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0 | 0.76 | 0.43 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
125 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 1.1 | 0.56 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | opened | 126 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.027 | 1.127 | 0.56 | 120 | 0.567 | 0 | 1.68 | 1.113 | 1.113 | opened
126 | SS 35/10 kv Droskovo | 4+2,5 | 1.34 | 0 | - | 1.34 | 0 | 2.625 | 1.285 | 1.285 | opened | 127 | SS 35/10 kv Droskovo | 4+2,5 | 0.081 | 1.421 | 0 |  | 1.421 | 0 | 2.625 | 1.204 | 1.204 | opened
127 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 2.44 | 0.39 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | opened | 128 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 0.018 | 2.458 | 0.39 | 120 | 2.068 | 0 | 6.615 | 4.547 | 4.547 | opened
128 | SS 35/10 kv Krutoe | 2,5+1,6 | 1.59 | 0.87 | 120 | 0.72 | 0 | 1.68 | 0.96 | 0.96 | opened | 129 | SS 35/10 kv Krutoe | 2,5+1,6 | 0.126 | 1.716 | 0.87 | 120 | 0.846 | 0 | 1.68 | 0.834 | 0.834 | opened
129 | SS 35/10 kv Mezentsevo | 4+6,3 | 3.15 | 1.11 | 80 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | opened | 130 | SS 35/10 kv Mezentsevo | 4+6,3 | 0.265 | 3.415 | 1.11 | 80 | 2.305 | 0 | 4.2 | 1.895 | 1.895 | opened
130 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.15 | 0 | - | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 131 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.008 | 0.158 | 0 |  | 0.158 | 0 | 1.68 | 1.522 | 1.522 | opened
131 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0.44 | 0.39 | - | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened | 132 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0 | 0.44 | 0.39 |  | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
132 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 1.85 | 0.54 | 80 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened | 133 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 0.087 | 1.937 | 0.54 | 80 | 1.397 | 0 | 2.625 | 1.228 | 1.228 | opened
133 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.47 | 1.67 | 120 | -1.2 | 0 | 3.36 | 4.56 | 4.56 | opened | 134 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.009 | 0.479 | 1.67 | 120 | -1.191 | 0 | 3.36 | 4.551 | 4.551 | opened
134 | SS 35/6 kv Pushkarskaya | 4+4 | 5.27 | 0 |  | 5.27 | 0 | 4.2 | -1.07 | -1.07 | closed | 135 | SS 35/6 kv Pushkarskaya | 4+4 | 0 | 5.27 | 0 |  | 5.27 | 0 | 4.2 | -1.07 | -1.07 | closed
135 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0.68 | 0.25 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 136 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0 | 0.68 | 0.25 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
136 | SS 35/10 kv Rosstani | 2,5+2,5 | 1.28 | 0.7 | 80 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 137 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.113 | 1.393 | 0.7 | 80 | 0.693 | 0 | 2.625 | 1.932 | 1.932 | opened
137 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.4 | 1.5 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 138 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.358 | 2.758 | 1.5 | 120 | 1.258 | 0 | 2.625 | 1.367 | 1.367 | opened
138 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.47 | 0.33 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 139 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.013 | 0.483 | 0.33 | 120 | 0.153 | 0 | 1.68 | 1.527 | 1.527 | opened
139 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0.24 | 0 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 140 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0 | 0.24 | 0 |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
140 | SS 35/10 kv SSK | 1,6+1 | 0.11 | 0 |  | 0.11 | 0 | 1.05 | 0.94 | 0.94 | opened | 37 | SS 35/10 kv SSK | 1,6+1 | 0.012 | 0.122 | 0 |  | 0.122 | 0 | 1.05 | 0.928 | 0.928 | opened
141 | SS 35/10 kv Urynok | 1,6+1,6 | 1.23 | 0.52 | 20 | 0.71 | 0 | 1.68 | 0.97 | 0.97 | opened | 141 | SS 35/10 kv Urynok | 1,6+1,6 | 0.012 | 1.242 | 0.52 | 20 | 0.722 | 0 | 1.68 | 0.958 | 0.958 | opened
142 | SS 35/10 kv Khomutovo | 4+4 | 2.54 | 0.31 | 80 | 2.23 | 0 | 4.2 | 1.97 | 1.97 | opened | 142 | SS 35/10 kv Khomutovo | 4+4 | 0.024 | 2.564 | 0.31 | 80 | 2.254 | 0 | 4.2 | 1.946 | 1.946 | opened
| Total: | [10 empty] | 2: Total:; 4: 132.02; 5: 779.075
| deficit | [8 empty] | -2.965 |  | 2: deficit; Мin. 12: -28.667
| proficit | [8 empty] | 541.735 |  | 2: proficit; Мin. 12: 507.771