## Костромаэнерго
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the N-1 mode, MVA | Transmission capacity, MVA | Deficit/proficit of Main Substation, MVA |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of Main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load calculated in the N-1 mode, MVA | Transmission capacity, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Sandogora 35/6 kv | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | opened | 1 | Sandogora 35/6 kv | 1 | 0.089 | 0.559 | 0.55 | 120 | 0.009 | 0 | 0.55 | -0.009 | -0.009 | closed
2 | Gridino 35/10 kv | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | opened | 2 | Gridino 35/10 kv | 1.8 | 0.262 | 0.992 | 1.2 | 120 | -0.208 | 0 | 1.2 | 0.208 | 0.208 | opened
3 | Novinki 35/10 kv | 1.8 | 0.15 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.29 | 1.29 | opened | 3 | Novinki 35/10 kv | 1.8 | 0.318 | 0.468 | 1.44 | 120 | -0.972 | 0 | 1.44 | 0.972 | 0.972 | opened
4 | Priskokovo 35/10kv | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | opened | 4 | Priskokovo 35/10kv | 2.5 | 0.111 | 1.611 | 1.5 | 120 | 0.111 | 0 | 1.5 | -0.111 | -0.111 | closed
5 | Grigortsevo 110/10 kv | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 5 | Grigortsevo 110/10 kv | 2.5 | 0 | 0.25 | 1.5 | 120 | -1.25 | 0 | 1.5 | 1.25 | 1.25 | opened
6 | Klementyevo 110/10 kv | 6.3 | 0.47 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.23 | 3.23 | opened | 6 | Klementyevo 110/10 kv | 6.3 | 0.029 | 0.499 | 3.7 | 120 | -3.201 | 0 | 3.7 | 3.201 | 3.201 | opened
7 | Rudino 35/10 kv | 2.5 | 0.27 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.23 | 1.23 | opened | 7 | Rudino 35/10 kv | 2.5 | 0.002 | 0.272 | 1.5 | 120 | -1.228 | 0 | 1.5 | 1.228 | 1.228 | opened
8 | Stoyankovo 35/10 kv | 1.6 | 0.14 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.58 | 0.58 | opened | 8 | Stoyankovo 35/10 kv | 1.6 | 0.066 | 0.206 | 0.72 | 120 | -0.514 | 0 | 0.72 | 0.514 | 0.514 | opened
9 | Adishchevo 35/10 kv | 4 | 1.35 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.25 | 1.25 | opened | 9 | Adishchevo 35/10 kv | 4 | 0.903 | 2.253 | 2.6 | 120 | -0.347 | 0 | 2.6 | 0.347 | 0.347 | opened
10 | Stolbovo 110/10 kv | 10 | 0.27 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.33 | 4.33 | opened | 10 | Stolbovo 110/10 kv | 10 | 0.011 | 0.281 | 4.6 | 120 | -4.319 | 0 | 4.6 | 4.319 | 4.319 | opened
11 | Raslovo 35/10 kv | 2.5 | 0.54 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.84 | 0.84 | opened | 11 | Raslovo 35/10 kv | 2.5 | 0.318 | 0.858 | 1.38 | 120 | -0.522 | 0 | 1.38 | 0.522 | 0.522 | opened
12 | Andreevskoe 35/10 kv | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | opened | 12 | Andreevskoe 35/10 kv | 1.6 | 0.018 | 0.198 | 0.93 | 120 | -0.732 | 0 | 0.93 | 0.732 | 0.732 | opened
13 | Popadyino 35/10 kv | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | opened | 13 | Popadyino 35/10 kv | 1.6 | 0.124 | 0.344 | 0.88 | 120 | -0.536 | 0 | 0.88 | 0.536 | 0.536 | opened
14 | Elegino 110/10 kv | 2.5 | 0.15 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.83 | 0.83 | opened | 14 | Elegino 110/10 kv | 2.5 | 0.302 | 0.452 | 0.98 | 120 | -0.528 | 0 | 0.98 | 0.528 | 0.528 | opened
15 | Krenyovo 35/10 kv | 2.5 | 0.47 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.03 | 2.03 | opened | 15 | Krenyovo 35/10 kv | 2.5 | 0.051 | 0.521 | 2.5 | 24 hours | -1.979 | 0 | 2.5 | 1.979 | 1.979 | opened
16 | Semyonovskoe 35/10 kv | 1.6 | 0.09 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.51 | 1.51 | opened | 16 | Semyonovskoe 35/10 kv | 1.6 | 0 | 0.09 | 1.6 | 24 hours | -1.51 | 0 | 1.6 | 1.51 | 1.51 | opened
17 | Khimik 35/10 kv | 3.2 | 0.1 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.34 | 1.34 | opened | 17 | Khimik 35/10 kv | 3.2 | 0 | 0.1 | 1.44 | 120 | -1.34 | 0 | 1.44 | 1.34 | 1.34 | opened
18 | N. Beryozovets 35/10 kv | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | opened | 18 | N. Beryozovets 35/10 kv | 2.5 | 0.006 | 0.336 | 0.43 | 120 | -0.094 | 0 | 0.43 | 0.094 | 0.094 | opened
19 | Stepanovo 35/10 kv | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | opened | 19 | Stepanovo 35/10 kv | 4 | 0.09 | 0.41 | 2.32 | 120 | -1.91 | 0 | 2.32 | 1.91 | 1.91 | opened
20 | Gorbachevo 35/10 kv | 1 | 0.11 | 0.78 | 120 | 0.78 | 0 | 0.78 | 0.67 | 0.67 | opened | 20 | Gorbachevo 35/10 kv | 1 | 0 | 0.11 | 0.78 | 120 | -0.67 | 0 | 0.78 | 0.67 | 0.67 | opened
21 | Kalinino 35/10 kv | 1 | 0.11 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.45 | 0.45 | opened | 21 | Kalinino 35/10 kv | 1 | 0 | 0.11 | 0.56 | 120 | -0.45 | 0 | 0.56 | 0.45 | 0.45 | opened
22 | Kuzemino 35/10 kv | 1.6 | 0.28 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.32 | 1.32 | opened | 22 | Kuzemino 35/10 kv | 1.6 | 0 | 0.28 | 1.6 | 24 hours | -1.32 | 0 | 1.6 | 1.32 | 1.32 | opened
23 | Sovega 35/10 kv | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | opened | 23 | Sovega 35/10 kv | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | opened
24 | Lukovtsino 110/10 kv | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | opened | 24 | Lukovtsino 110/10 kv | 2.5 | 0.023 | 0.213 | 1.38 | 120 | -1.167 | 0 | 1.38 | 1.167 | 1.167 | opened
25 | Fyodorovskoe 110/10 kv | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | opened | 25 | Fyodorovskoe 110/10 kv | 2.5 | 0 | 0.15 | 1.5 | 120 | -1.35 | 0 | 1.5 | 1.35 | 1.35 | opened
26 | Pankratovo 35/10 kv | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | opened | 26 | Pankratovo 35/10 kv | 1 | 0.017 | 0.077 | 0.39 | 120 | -0.313 | 0 | 0.39 | 0.313 | 0.313 | opened
27 | Petrovskoe 35/10 kv | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | opened | 27 | Petrovskoe 35/10 kv | 1.6 | 0 | 0.32 | 0.77 | 120 | -0.45 | 0 | 0.77 | 0.45 | 0.45 | opened
28 | Kotelnikovo 35/10 kv | 1 | 0.13 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.13 | 0.13 | opened | 28 | Kotelnikovo 35/10 kv | 1 | 0 | 0.13 | 0.26 | 120 | -0.13 | 0 | 0.26 | 0.13 | 0.13 | opened
29 | Legitovo 35/10 kv | 2.5 | 0.31 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.79 | 0.79 | opened | 29 | Legitovo 35/10 kv | 2.5 | 0 | 0.31 | 1.1 | 120 | -0.79 | 0 | 1.1 | 0.79 | 0.79 | opened
30 | Sloboda 35/10 kv | 2.5 | 0.05 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 30 | Sloboda 35/10 kv | 2.5 | 0 | 0.05 | 0.85 | 120 | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
31 | Zavrazhye 35/10 kv | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | открыт | 31 | Zavrazhye 35/10 kv | 1.6 | 0.077 | 0.367 | 0.74 | 120 | -0.373 | 0 | 0.74 | 0.373 | 0.373 | opened
32 | Okulovo 35/10 kv | 1.6 | 0.16 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.74 | 0.74 | opened | 32 | Okulovo 35/10 kv | 1.6 | 0.093 | 0.253 | 0.9 | 120 | -0.647 | 0 | 0.9 | 0.647 | 0.647 | opened
33 | Chernyshevo 35/10 kv | 4 | 0.57 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.23 | 1.23 | opened | 33 | Chernyshevo 35/10 kv | 4 | 0.088 | 0.658 | 1.8 | 120 | -1.142 | 0 | 1.8 | 1.142 | 1.142 | opened
34 | Yakovlevo 110/35/10 kv | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 | 5.24 | opened | 34 | Yakovlevo 110/35/10 kv | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234 | 5.234 | opened
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 |  |  |  | Nom. Capacity LV, MVA | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234
35 | Chermenino 35/10 kv | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | opened | 35 | Chermenino 35/10 kv | 1.6 | 0 | 0.07 | 0.86 | 120 | -0.79 | 0 | 0.86 | 0.79 | 0.79 | opened
36 | Nezhitino 35/10 kv | 1 | 0.08 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.46 | 0.46 | opened | 36 | Nezhitino 35/10 kv | 1 | 0.038 | 0.118 | 0.54 | 120 | -0.422 | 0 | 0.54 | 0.422 | 0.422 | opened
37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.45 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.54 | 0.54 | opened | 37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.143 | 0.593 | 0.99 | 120 | -0.397 | 0 | 0.99 | 0.397 | 0.397 | opened
38 | Gusevo 110/10 kv | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | opened | 38 | Gusevo 110/10 kv | 2.5 | 0.018 | 0.308 | 1.63 | 120 | -1.322 | 0 | 1.63 | 1.322 | 1.322 | opened
39 | Medveditsa 35/10 kv | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | opened | 39 | Medveditsa 35/10 kv | 2.5 | 0 | 0.53 | 1.3 | 120 | -0.77 | 0 | 1.3 | 0.77 | 0.77 | opened
40 | Novinskoe 110/10 kv | 2.5 | 0.03 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.2 | 1.2 | opened | 40 | Novinskoe 110/10 kv | 2.5 | 0 | 0.03 | 1.23 | 120 | -1.2 | 0 | 1.23 | 1.2 | 1.2 | opened
41 | Filino 35/10 kv | 1.6 | 0.25 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.71 | 0.71 | opened | 41 | Filino 35/10 kv | 1.6 | 0.098 | 0.348 | 0.96 | 120 | -0.612 | 0 | 0.96 | 0.612 | 0.612 | opened
42 | Dyakonovo 110/10 kv | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | opened | 42 | Dyakonovo 110/10 kv | 2.5 | 0 | 0.28 | 1.13 | 120 | -0.85 | 0 | 1.13 | 0.85 | 0.85 | opened
43 | Oktyabrskaya 110/10 kv | 2.5 | 0.91 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.59 | 1.59 | opened | 43 | Oktyabrskaya 110/10 kv | 2.5 | 0.012 | 0.922 | 2.5 | 24 hours | -1.578 | 0 | 2.5 | 1.578 | 1.578 | opened
44 | Kuzhbal 35/10 kv | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | opened | 44 | Kuzhbal 35/10 kv | 2.5 | 0.017 | 0.417 | 1.48 | 120 | -1.063 | 0 | 1.48 | 1.063 | 1.063 | opened
45 | Nikolo-Poloma 110/10 kv | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | opened | 45 | Nikolo-Poloma 110/10 kv | 2.5 | 0.069 | 1.109 | 1.13 | 120 | -0.021 | 0 | 1.13 | 0.021 | 0.021 | opened
46 | Nikola 110/35/10 kv | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87 | 2.87 | opened | 46 | Nikola 110/35/10 kv | 6.3 | 0 | 0.28 | 3.15 | 120 | -2.87 | 0 | 3.15 | 2.87 | 2.87 | opened
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0 | 0.28 | 3.15 | 120 | -2.87 | 0 | 3.15 | 2.87
47 | Zavetluzhye 35/10 kv | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | opened | 47 | Zavetluzhye 35/10 kv | 1.6 | 0 | 0.11 | 0.67 | 120 | -0.56 | 0 | 0.67 | 0.56 | 0.56 | opened
48 | Talitsa 35/10 kv | 1.6 | 0.26 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.34 | 1.34 | opened | 48 | Talitsa 35/10 kv | 1.6 | 0 | 0.26 | 1.6 | 24 hours | -1.34 | 0 | 1.6 | 1.34 | 1.34 | opened
49 | Khoroshaya 35/10 kv | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | opened | 49 | Khoroshaya 35/10 kv | 2.5 | 0 | 0.06 | 1.95 | 120 | -1.89 | 0 | 1.95 | 1.89 | 1.89 | opened
50 | Zabegaevo 35/10 kv | 1.6 | 0.11 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.77 | 0.77 | opened | 50 | Zabegaevo 35/10 kv | 1.6 | 0 | 0.11 | 0.88 | 120 | -0.77 | 0 | 0.88 | 0.77 | 0.77 | opened
51 | Ilyinskoe 35/10 kv | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | opened | 51 | Ilyinskoe 35/10 kv | 1.6 | 0 | 0.04 | 0.9 | 120 | -0.86 | 0 | 0.9 | 0.86 | 0.86 | opened
52 | Luptyug 35/10 kv | 2.5 | 0.11 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.24 | 1.24 | opened | 52 | Luptyug 35/10 kv | 2.5 | 0 | 0.11 | 1.35 | 120 | -1.24 | 0 | 1.35 | 1.24 | 1.24 | opened
53 | Solovetskoe 35/10 kv | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | opened | 53 | Solovetskoe 35/10 kv | 1.6 | 0 | 0.09 | 0.72 | 120 | -0.63 | 0 | 0.72 | 0.63 | 0.63 | opened
54 | Gudkovo 110/10 kv | 2.5 | 0.06 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.32 | 1.32 | opened | 54 | Gudkovo 110/10 kv | 2.5 | 0 | 0.06 | 1.38 | 120 | -1.32 | 0 | 1.38 | 1.32 | 1.32 | opened
55 | Shortyug 110/10 kv | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | opened | 55 | Shortyug 110/10 kv | 6.3 | 0.006 | 0.526 | 3.47 | 120 | -2.944 | 0 | 3.47 | 2.944 | 2.944 | opened
56 | Yakshanga 110/10 kv | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | opened | 56 | Yakshanga 110/10 kv | 6.3 | 0.083 | 1.493 | 3.47 | 120 | -1.977 | 0 | 3.47 | 1.977 | 1.977 | opened
57 | Katunino 35/10 kv | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | opened | 57 | Katunino 35/10 kv | 2.5 | 0 | 0.17 | 1.33 | 120 | -1.16 | 0 | 1.33 | 1.16 | 1.16 | opened
58 | Konyovo 35/10 kv | 1.6 | 0.33 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.55 | 0.55 | opened | 58 | Konyovo 35/10 kv | 1.6 | 0.017 | 0.347 | 0.88 | 120 | -0.533 | 0 | 0.88 | 0.533 | 0.533 | opened
59 | Shekshema 110/10 kv | 6.3 | 0.58 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.92 | 1.92 | opened | 59 | Shekshema 110/10 kv | 6.3 | 0.041 | 0.621 | 2.5 | 24 hours | -1.879 | 0 | 2.5 | 1.879 | 1.879 | opened
60 | Golovino 35/10 kv | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | opened | 60 | Golovino 35/10 kv | 1 | 0 | 0.06 | 0.12 | 120 | -0.06 | 0 | 0.12 | 0.06 | 0.06 | opened
61 | Pishchyovka 35/10 kv | 1 | 0.19 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.26 | 0.26 | opened | 61 | Pishchyovka 35/10 kv | 1 | 0.063 | 0.253 | 0.45 | 120 | -0.197 | 0 | 0.45 | 0.197 | 0.197 | opened
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
62 | Vasilyovo 110/35/10 kv | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | opened | 62 | Vasilyovo 110/35/10 kv | 10+10 | 3.671 | 5.801 | 0.86 | 120 | 4.941 | 0 | 10.5 | 5.559 | 5.559 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 3.671 | 5.211 | 0.86 | 120 | 4.351 | 0 | 10.5 | 6.149
63 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 7.21 | opened | 63 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 0.355 | 6.475 | 1.15 | 120 | 5.325 | 0 | 12.18 | 6.855 | 6.855 | opened
| Nom. Capacity MV, MVA | 10+10+1,6 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.53 | 1.15 | 120 | 0.38 | 0 | 12.18 | 11.8 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.355 | 1.885 | 1.15 | 120 | 0.735 | 0 | 12.18 | 11.445
64 | Apraksino 35/10 kv | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | opened | 64 | Apraksino 35/10 kv | 2,5+2,5 | 0.769 | 2.499 | 0.425 | 120 | 2.074 | 0 | 2.625 | 0.551 | 0.551 | opened
65 | Borshchino 35/10 kv | 4+4 | 0.63 | 0.62 | 120 | 0.01 | 0 | 4.2 | 4.19 | 4.19 | opened | 65 | Borshchino 35/10 kv | 4+4 | 0.457 | 1.087 | 0.62 | 120 | 0.467 | 0 | 4.2 | 3.733 | 3.733 | opened
66 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.2 | 0.11 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 66 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.039 | 0.239 | 0.11 | 120 | 0.129 | 0 | 1.68 | 1.551 | 1.551 | opened
67 | Ilyinskoe 35/10 kv | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | opened | 67 | Ilyinskoe 35/10 kv | 2,5+2,5 | 0.41 | 2.74 | 0.55 | 120 | 2.19 | 0 | 2.625 | 0.435 | 0.435 | opened
68 | Kuznetsovo 35/10 kv | 2,5+2,5 | 1.1 | 0.4 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 68 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.174 | 1.274 | 0.4 | 120 | 0.874 | 0 | 2.625 | 1.751 | 1.751 | opened
69 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.72 | 0.29 | 120 | 0.43 | 0 | 1.68 | 1.25 | 1.25 | opened | 69 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.131 | 0.851 | 0.29 | 120 | 0.561 | 0 | 1.68 | 1.119 | 1.119 | opened
70 | Minskoe 35/10 kv | 2,5+2,5 | 1.3 | 0.43 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | opened | 70 | Minskoe 35/10 kv | 2,5+2,5 | 0.594 | 1.894 | 0.43 | 120 | 1.464 | 0 | 2.625 | 1.161 | 1.161 | opened
71 | Miskovo 35/6 kv | 1,8+1,8 | 0.35 | 0.2 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | opened | 71 | Miskovo 35/6 kv | 1,8+1,8 | 0.056 | 0.406 | 0.2 | 120 | 0.206 | 0 | 1.89 | 1.684 | 1.684 | opened
72 | Nikolskoe 35/6 kv | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | opened | 72 | Nikolskoe 35/6 kv | 4+4 | 0.606 | 3.106 | 0.92 | 120 | 2.186 | 0 | 4.2 | 2.014 | 2.014 | opened
73 | Samet 35/6 kv | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | opened | 73 | Samet 35/6 kv | 1,6+4 | 0.247 | 1.677 | 0 | 0 | 1.677 | 0 | 1.68 | 0.003 | 0.003 | opened
74 | Sukhonogovo 35/10 kv | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | opened | 74 | Sukhonogovo 35/10 kv | 3,2+4 | 0.578 | 3.288 | 0 | 0 | 3.288 | 0 | 3.36 | 0.072 | 0.072 | opened
75 | Sushchevo 35/10 kv | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | opened | 75 | Sushchevo 35/10 kv | 4+4 | 0.306 | 3.986 | 0.76 | 120 | 3.226 | 0 | 4.2 | 0.974 | 0.974 | opened
76 | EMZ 35/6 kv | 1+1 | 0.76 | 0 | 0 | 0.76 | 0 | 1.05 | 0.29 | 0.29 | opened | 76 | EMZ 35/6 kv | 1+1 | 0 | 0.76 | 0 | 0 | 0.76 | 0 | 1.05 | 0.29 | 0.29 | opened
77 | Krasnoe 110/35/10 kv | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | opened | 77 | Krasnoe 110/35/10 kv | 16+16 | 2.22 | 14.63 | 0 | 0 | 14.63 | 0 | 16.8 | 2.17 | 2.17 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.22 | 13.86 | 0 | 0 | 13.86 | 0 | 16.8 | 2.94
78 | Isaevo 35/10 kv | 4+4 | 0.92 | 1.03 | 120 | -0.11 | 0 | 4.2 | 4.31 | 4.31 | opened | 78 | Isaevo 35/10 kv | 4+4 | 2.649 | 3.569 | 1.03 | 120 | 2.539 | 0 | 4.2 | 1.661 | 1.661 | opened
79 | Chapaevo 35/10 kv | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 79 | Chapaevo 35/10 kv | 2,5+2,5 | 0.107 | 1.377 | 0.43 | 120 | 0.947 | 0 | 2.625 | 1.678 | 1.678 | opened
80 | Chernevo 35/10 kv | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | opened | 80 | Chernevo 35/10 kv | 1,8+1,8 | 0.023 | 0.393 | 0.43 | 120 | -0.037 | 0 | 1.89 | 1.927 | 1.927 | opened
81 | Nerekhta-1 110/35/10 kv | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | opened | 81 | Nerekhta-1 110/35/10 kv | 25+25 | 0.551 | 19.061 | 2.75 | 120 | 16.311 | 0 | 26.25 | 9.939 | 9.939 | opened
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.551 | 12.541 | 2.75 | 120 | 9.791 | 0 | 26.25 | 16.459
| Nerekhta-1 110/10 kv | 16+16 | 2.41 | 2.2 | 120 | 0.21 | 0 | 16.8 | 16.59 |  |  |  | Nerekhta-1 110/10 kv | 16+16 | 0 | 2.41 | 2.2 | 120 | 0.21 | 0 | 16.8 | 16.59
82 | Nerekhta-2 110/10/6 kv | 5,6+10 | 0.93 | 1.55 | 120 | -0.62 | 0 | 5.88 | 6.5 | 6.5 | opened | 82 | Nerekhta-2 110/10/6 kv | 10+10 | 5.736 | 6.666 | 1.55 | 120 | 5.116 | 0 | 10.5 | 5.384 | 5.384 | opened
83 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.57 | 0.41 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 83 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.087 | 0.657 | 0.41 | 120 | 0.247 | 0 | 1.68 | 1.433 | 1.433 | opened
84 | Tatarskoe 35/10 kv | 1,6+1,6 | 0.36 | 0.23 | 120 | 0.13 | 0 | 6.615 | 6.485 | 6.485 | opened | 84 | Tatarskoe 35/10 kv | 1,6+1,6 | 0.002 | 0.362 | 0.23 | 120 | 0.132 | 0 | 6.615 | 6.483 | 6.483 | opened
85 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 3.89 | 0.76 | 120 | 3.13 | 0 | 6.615 | 3.485 | 3.305 | opened | 85 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 0.112 | 4.002 | 0.76 | 120 | 3.242 | 0 | 6.615 | 3.373 | 3.305 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 3.31 | 0 | 120 | 3.31 | 0 | 6.615 | 3.305 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 3.31 | 0 | 120 | 3.31 | 0 | 6.615 | 3.305
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.58 | 0.76 | 120 | -0.18 | 0 | 6.615 | 6.795 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.112 | 0.692 | 0.76 | 120 | -0.068 | 0 | 6.615 | 6.683
86 | Krasnaya Polyana 110/35/10 kv | 10+10 | 3.91 | 1.28 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | opened | 86 | Krasnaya Polyana 110/35/10 kv | 10+10 | 1.149 | 5.059 | 1.28 | 120 | 3.779 | 0 | 10.5 | 6.721 | 6.721 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78
| Nom. Capacity LV, MVA | 10+10 | 3.19 | 1.28 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.149 | 4.339 | 1.28 | 120 | 3.059 | 0 | 10.5 | 7.441
87 | Igodovo 35/10 kv | 1,6+1,6 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 87 | Igodovo 35/10 kv | 1,6+1,6 | 0.087 | 0.457 | 0.25 | 120 | 0.207 | 0 | 1.68 | 1.473 | 1.473 | opened
88 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 88 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.017 | 0.817 | 0.56 | 120 | 0.257 | 0 | 1.68 | 1.423 | 1.423 | opened
89 | Ostrovskoe 35/10 kv | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 89 | Ostrovskoe 35/10 kv | 2,5+2,5 | 0.045 | 1.365 | 0.52 | 120 | 0.845 | 0 | 2.625 | 1.78 | 1.78 | opened
90 | Sudislavl 110/10 kv | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | opened | 90 | Sudislavl 110/10 kv | 10+10 | 1.351 | 9.491 | 1.8 | 120 | 7.691 | 0 | 10.5 | 2.809 | 2.809 | opened
91 | Voronye 35/10 kv | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 91 | Voronye 35/10 kv | 1,8+1,8 | 0.093 | 0.583 | 0.4 | 120 | 0.183 | 0 | 1.89 | 1.707 | 1.707 | opened
92 | Susanino 110/35/10 kv | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | opened | 92 | Susanino 110/35/10 kv | 10+10 | 0.603 | 4.533 | 1.89 | 120 | 2.643 | 0 | 10.5 | 7.857 | 7.857 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.603 | 4.153 | 1.89 | 120 | 2.263 | 0 | 10.5 | 8.237
93 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.25 | 0.07 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 93 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.025 | 0.275 | 0.07 | 120 | 0.205 | 0 | 2.625 | 2.42 | 2.42 | opened
94 | Airport 110/35/6 kv | 16+16 | 5.31 | 2.88 | 120 | 2.43 | 0 | 16.8 | 14.37 | 14.37 | opened | 94 | Airport 110/35/6 kv | 16+16 | 0.753 | 6.063 | 2.88 | 120 | 3.183 | 0 | 16.8 | 13.617 | 13.617 | opened
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.31 | 2.88 | 120 | 2.43 | 0 | 16.8 | 14.37 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 0.753 | 6.063 | 2.88 | 120 | 3.183 | 0 | 16.8 | 13.617
95 | Vostochnaya-2 110/35/10 kv | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | opened | 95 | Vostochnaya-2 110/35/10 kv | 25+25 | 1.344 | 24.384 | 0.02 | 120 | 24.364 | 0 | 26.25 | 1.886 | 1.886 | opened
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 1.344 | 5.144 | 0.02 | 120 | 5.124 | 0 | 26.25 | 21.126
96 | Kostroma-3 110/35/10 kv | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | closed | 96 | Kostroma-3 110/35/10 kv | 10+16 | 1.013 | 12.503 | 0 | 120 | 12.503 | 0 | 10.5 | -2.003 | -8.773 | closed
| Nom. Capacity MV, MVA | 10+16 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82
| Nom. Capacity LV, MVA | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.013 | 9.823 | 0 | 120 | 9.823 | 0 | 1.05 | -8.773
97 | Yuzhnaya 110/35/10 kv | 25+25 | 10.9 | 0 | 120 | 10.9 | 0 | 26.25 | 15.35 | 15.35 | opened | 97 | Yuzhnaya 110/35/10 kv | 25+25 | 11.185 | 22.085 | 0 | 120 | 22.085 | 0 | 26.25 | 4.165 | 4.165 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8
| Nom. Capacity LV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 11.185 | 16.635 | 0 | 120 | 16.635 | 0 | 26.25 | 9.615
98 | Davydovskaya 110/10 kv | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | opened | 98 | Davydovskaya 110/10 kv | 25+25 | 4.653 | 13.563 | 0.02 | 120 | 13.543 | 0 | 26.25 | 12.707 | 12.707 | opened | introduced in September, 2009.
99 | Kostroma-1 110/6 kv | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | opened | 99 | Kostroma-1 110/6 kv | 10+10 | 0.794 | 11.174 | 0 | 0 | 11.174 | 0 | 10.5 | -0.674 | -0.674 | closed
100 | Severnaya 110/6 kv | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | opened | 100 | Severnaya 110/6 kv | 20+25 | 1.651 | 20.891 | 0 | 0 | 20.891 | 0 | 21 | 0.109 | 0.109 | opened
101 | Strommashina 110/6 kv | 40+40 | 9.03 | 0 | 0 | 9.03 | 0 | 42 | 32.97 | 32.97 | opened | 101 | Strommashina 110/6 kv | 40+40 | 4.332 | 13.362 | 0 | 0 | 13.362 | 0 | 42 | 28.638 | 28.638 | opened
102 | Tsentralnaya 110/10/6 kv | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | opened | 102 | Tsentralnaya 110/10/6 kv | 25+25 | 5.519 | 21.959 | 0 | 0 | 21.959 | 0 | 26.25 | 4.291 | 4.291 | opened
103 | Baydarka 35/6 kv | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | opened | 103 | Baydarka 35/6 kv | 6,3+6,3 | 0.745 | 2.735 | 1.2 | 120 | 1.535 | 0 | 6.615 | 5.08 | 5.08 | opened
104 | Volzhskaya 35/6 kv | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 104 | Volzhskaya 35/6 kv | 4+4 | 0.23 | 1.52 | 0.76 | 120 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened
105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 22.36 | 0 | 0 | 22.36 | 0 | 17.115 | -5.245 | -5.245 | closed | 105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 1.9 | 24.26 | 0 | 0 | 24.26 | 0 | 17.115 | -7.145 | -7.145 | closed
106 | Karavaevo 35/10 kv | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | opened | 106 | Karavaevo 35/10 kv | 6,3+6,3 | 1.542 | 5.002 | 0 | 0 | 5.002 | 0 | 6.615 | 1.613 | 1.613 | opened
107 | Korkino 35/10 kv | 2,5+2,5 | 1.67 | 0.85 | 120 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | opened | 107 | Korkino 35/10 kv | 2,5+2,5 | 0.379 | 2.049 | 0.85 | 120 | 1.199 | 0 | 2.625 | 1.426 | 1.426 | opened
108 | KPD 110/35/10 kv | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | opened | 108 | KPD 110/35/10 kv | 25+25 | 11.047 | 18.587 | 1.44 | 120 | 17.147 | 0 | 26.25 | 9.103 | 9.103 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 11.047 | 11.667 | 0 | 120 | 11.667 | 0 | 26.25 | 14.583
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 6.92 | 1.44 | 120 | 5.48 | 0 | 26.25 | 20.77
109 | SM State district power station 110/35/6 kv | 10+16 | 6.48 | 0 | 0 | 6.48 | 0 | 10.5 | 4.02 | 4.02 | opened | 109 | SM State district power station 110/35/6 kv | 10+16 | 2.908 | 9.388 | 0 | 0 | 9.388 | 0 | 10.5 | 1.112 | 1.112 | opened
| Nom. Capacity MV, MVA | 10+16 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88
| Nom. Capacity LV, MVA | 10+16 | 5.86 | 0 | 0 | 5.86 | 0 | 10.5 | 4.64 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 2.908 | 8.768 | 0 | 0 | 8.768 | 0 | 10.5 | 1.732
110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.76 | 0.82 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened | 110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.145 | 0.905 | 0.82 | 120 | 0.085 | 0 | 2.625 | 2.54 | 2.54 | opened
111 | Buy (r) 110/35/10 kv | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | opened | 111 | Buy (r) 110/35/10 kv | 4+10 | 0.296 | 2.166 | 0 | 120 | 2.166 | 0 | 4.2 | 2.034 | 2.034 | opened
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 0 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0.296 | 0.296 | 0 | 120 | 0.296 | 0 | 4.2 | 3.904
112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | opened | 112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 0.493 | 6.743 | 1.2 | 120 | 5.543 | 0 | 6.615 | 1.072 | 1.072 | opened
113 | Zapadnaya 110/10 kv | 10+10 | 5.08 | 2.63 | 120 | 2.45 | 0 | 10.5 | 8.05 | 8.05 | opened | 113 | Zapadnaya 110/10 kv | 10+10 | 0.03 | 5.11 | 2.63 | 120 | 2.48 | 0 | 10.5 | 8.02 | 8.02 | opened
114 | Dor 35/10 kv | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened | 114 | Dor 35/10 kv | 1,6+1,6 | 0.023 | 0.483 | 0.06 | 120 | 0.423 | 0 | 1.68 | 1.257 | 1.257 | opened
115 | Dyakonovo 35/10 kv | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened | 115 | Dyakonovo 35/10 kv | 1+1 | 0 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened
116 | Likurga 35/10 kv | 1,8+1,6 | 0.2 | 0.12 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened | 116 | Likurga 35/10 kv | 1,8+1,6 | 0.001 | 0.201 | 0.12 | 120 | 0.081 | 0 | 1.68 | 1.599 | 1.599 | opened
117 | Shushkodom 35/10 kv | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | opened | 117 | Shushkodom 35/10 kv | 1+1 | 0.012 | 0.302 | 0.06 | 120 | 0.242 | 0 | 1.05 | 0.808 | 0.808 | opened
118 | Novaya 110/35/10 kv | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | opened | 118 | Novaya 110/35/10 kv | 6,3+6,3 | 0.636 | 3.566 | 0.64 | 120 | 2.926 | 0 | 6.615 | 3.689 | 3.689 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.636 | 1.736 | 0.64 | 120 | 1.096 | 0 | 6.615 | 5.519
119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | opened | 119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 0.152 | 1.512 | 0 | 120 | 1.512 | 0 | 6.615 | 5.103 | 5.103 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.152 | 0.982 | 0 | 120 | 0.982 | 0 | 6.615 | 5.633
120 | Loparevo 110/10 kv | 2,5+2,5 | 0.36 | 0.55 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 120 | Loparevo 110/10 kv | 2,5+2,5 | 0.237 | 0.597 | 0.55 | 120 | 0.047 | 0 | 2.625 | 2.578 | 2.578 | opened
121 | Poultry farm 35/10 kv | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened | 121 | Poultry farm 35/10 kv | 4+4 | 0.045 | 1.775 | 1.28 | 120 | 0.495 | 0 | 4.2 | 3.705 | 3.705 | opened
122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.28 | 0.22 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened | 122 | Kabanovo 35/10 kv | 2,5+2,5 | 0 | 0.28 | 0.22 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
123 | Levkovo 35/10 kv | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | opened | 123 | Levkovo 35/10 kv | 1,6+1,6 | 0.006 | 0.226 | 0.74 | 120 | -0.514 | 0 | 1.68 | 2.194 | 2.194 | opened
124 | Pronino 35/10 kv | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 124 | Pronino 35/10 kv | 4+2,5 | 0.01 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.2 | 0.13 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.352 | 0.552 | 0.13 | 120 | 0.422 | 0 | 2.625 | 2.203 | 2.203 | opened
126 | Soligalich 110/35/10 kv | 10+10 | 5.27 | 1.7 | 120 | 3.57 | 0 | 10.5 | 6.93 | 6.93 | opened | 126 | Soligalich 110/35/10 kv | 10+10 | 0.843 | 6.113 | 1.7 | 120 | 4.413 | 0 | 10.5 | 6.087 | 6.087 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.94 | 0 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.94 | 0 | 120 | 0.94 | 0 | 10.5 | 9.56
| Nom. Capacity LV, MVA | 10+10 | 4.33 | 1.7 | 120 | 2.63 | 0 | 10.5 | 7.87 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.843 | 5.173 | 1.7 | 120 | 3.473 | 0 | 10.5 | 7.027
127 | Pochinok 35/10 kv | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 127 | Pochinok 35/10 kv | 1,6+2,5 | 0.017 | 0.547 | 0.34 | 120 | 0.207 | 0 | 1.68 | 1.473 | 1.473 | opened
128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | opened | 128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 0.551 | 4.521 | 2.06 | 120 | 2.461 | 0 | 6.615 | 4.154 | 4.154 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.551 | 3.401 | 2.06 | 120 | 1.341 | 0 | 6.615 | 5.274
129 | Suday 35/10 kv | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened | 129 | Suday 35/10 kv | 1,6+1,6 | 0.083 | 1.093 | 0.49 | 120 | 0.603 | 0 | 1.68 | 1.077 | 1.077 | opened
130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 6.09 | 0.38 | 120 | 5.71 | 0 | 6.615 | 0.905 | 0.905 | opened | 130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 0.144 | 6.234 | 0.38 | 120 | 5.854 | 0 | 6.615 | 0.761 | 0.761 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 3.53 | 0 | 120 | 3.53 | 0 | 6.615 | 3.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 3.53 | 0 | 120 | 3.53 | 0 | 6.615 | 3.085
| Nom. Capacity LV, MVA | 6,3+16 | 2.56 | 0.38 | 120 | 2.18 | 0 | 6.615 | 4.435 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.144 | 2.704 | 0.38 | 120 | 2.324 | 0 | 6.615 | 4.291
131 | Palkino 35/10 kv | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened | 131 | Palkino 35/10 kv | 2,5+4 | 0.031 | 0.731 | 0.45 | 120 | 0.281 | 0 | 2.625 | 2.344 | 2.344 | opened
132 | Slovinka 35/10 kv | 1,6+1,6 | 0.13 | 0.1 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 132 | Slovinka 35/10 kv | 1,6+1,6 | 0.006 | 0.136 | 0.1 | 120 | 0.036 | 0 | 1.68 | 1.644 | 1.644 | opened
133 | Kady 110/35/10 kv | 10+10 | 3.48 | 0.69 | 120 | 2.79 | 0 | 10.5 | 7.71 | 7.71 | opened | 133 | Kady 110/35/10 kv | 10+10 | 0.381 | 3.861 | 0.69 | 120 | 3.171 | 0 | 10.5 | 7.329 | 7.329 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.23 | 0 | 120 | 1.23 | 0 | 10.5 | 9.27 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.23 | 0 | 120 | 1.23 | 0 | 10.5 | 9.27
| Nom. Capacity LV, MVA | 10+10 | 2.25 | 0.69 | 120 | 1.56 | 0 | 10.5 | 8.94 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.381 | 2.631 | 0.69 | 120 | 1.941 | 0 | 10.5 | 8.559
134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | opened | 134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | opened
135 | Ilyinskoe 110/35/10 kv | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | opened | 135 | Ilyinskoe 110/35/10 kv | 10+10 | 0 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43
136 | Kologriv 35/10 kv | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | opened | 136 | Kologriv 35/10 kv | 4+4 | 0.162 | 2.282 | 1.42 | 120 | 0.862 | 0 | 4.2 | 3.338 | 3.338 | opened
137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.23 | 0.08 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.007 | 0.237 | 0.08 | 120 | 0.157 | 0 | 1.68 | 1.523 | 1.523 | opened
138 | Makaryev-1 110/35/10 kv | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | opened | 138 | Makaryev-1 110/35/10 kv | 10+10 | 0.064 | 7.604 | 0.8 | 120 | 6.804 | 0 | 10.5 | 3.696 | 3.696 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.064 | 2.244 | 0.8 | 120 | 1.444 | 0 | 10.5 | 9.056
139 | Gorchukha 35/10 kv | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened | 139 | Gorchukha 35/10 kv | 2,5+2,5 | 0.034 | 1.224 | 0 | 0 | 1.224 | 0 | 2.625 | 1.401 | 1.401 | opened
140 | Makaryev-2 35/10 kv | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened | 140 | Makaryev-2 35/10 kv | 4+4 | 0.161 | 3.161 | 1.58 | 120 | 1.581 | 0 | 4.2 | 2.619 | 2.619 | opened
141 | Timoshino 35/10 kv | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | opened | 141 | Timoshino 35/10 kv | 1+1 | 0.077 | 0.257 | 0 | 0 | 0.257 | 0 | 1.05 | 0.793 | 0.793 | opened
142 | Unzha 35/10 kv | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | opened | 142 | Unzha 35/10 kv | 1+1,6 | 0 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | opened
143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | opened | 143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.004 | 0.394 | 0.32 | 120 | 0.074 | 0 | 1.68 | 1.606 | 1.606 | opened
144 | BKhZ 110/6 kv | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | opened | 144 | BKhZ 110/6 kv | 25+25 | 0.189 | 2.769 | 0 | 0 | 2.769 | 0 | 26.25 | 23.481 | 23.481 | opened
145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.077 | 0.517 | 0.15 | 120 | 0.367 | 0 | 1.68 | 1.313 | 1.313 | opened
146 | Georgievskoe 35/10 kv | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 146 | Georgievskoe 35/10 kv | 2,5+2,5 | 0.099 | 2.249 | 1.23 | 120 | 1.019 | 0 | 2.625 | 1.606 | 1.606 | opened
147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | opened | 147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 0.562 | 16.612 | 3.6 | 120 | 13.012 | 0 | 48.615 | 35.603 | 35.603 | opened
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.562 | 8.082 | 3.6 | 120 | 4.482 | 0 | 48.615 | 44.133
148 | Vozherovo 35/10 kv | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 148 | Vozherovo 35/10 kv | 1,6+1,6 | 0 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
149 | Matveevo 35/10 kv | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 149 | Matveevo 35/10 kv | 1,8+4 | 0 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened
150 | Parfenyevo 35/10 kv | 4+4 | 2.32 | 1.89 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened | 150 | Parfenyevo 35/10 kv | 4+4 | 0.036 | 2.356 | 1.89 | 120 | 0.466 | 0 | 4.2 | 3.734 | 3.734 | opened
151 | Vokhma 110/35/10 kv | 6,3+16 | 5.42 | 0 | 0 | 5.42 | 0 | 6.615 | 1.195 | 1.195 | opened | 151 | Vokhma 110/35/10 kv | 6,3+16 | 0.19 | 5.61 | 0 | 0 | 5.61 | 0 | 6.615 | 1.005 | 1.005 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085
| Nom. Capacity LV, MVA | 6,3+16 | 3.89 | 0 | 0 | 3.89 | 0 | 6.615 | 2.725 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.19 | 4.08 | 0 | 0 | 4.08 | 0 | 6.615 | 2.535
152 | Lapshino 35/10 kv | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 152 | Lapshino 35/10 kv | 2,5+2,5 | 0 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
153 | Spass 35/10 kv | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 153 | Spass 35/10 kv | 1,6+2,5 | 0.006 | 0.356 | 0.35 | 120 | 0.006 | 0 | 1.68 | 1.674 | 1.674 | opened
154 | Bogovarovo 35/10 kv | 2,5+4 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 154 | Bogovarovo 35/10 kv | 2,5+4 | 0.07 | 1.66 | 1 | 120 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | opened
155 | Pavino 110/35/10 kv | 10+6,3 | 1.69 | 0 | 0 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | opened | 155 | Pavino 110/35/10 kv | 10+6,3 | 0.101 | 1.791 | 0 | 0 | 1.791 | 0 | 6.615 | 4.824 | 4.824 | opened
| Nom. Capacity MV, MVA | 10+6,3 | 0.18 | 0 | 0 | 0.18 | 0 | 6.615 | 6.435 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.18 | 0 | 0 | 0.18 | 0 | 6.615 | 6.435
| Nom. Capacity LV, MVA | 10+6,3 | 1.51 | 0 | 0 | 1.51 | 0 | 6.615 | 5.105 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.101 | 1.611 | 0 | 0 | 1.611 | 0 | 6.615 | 5.004
156 | Ledengskaya 35/10 kv | 1,6+4 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 156 | Ledengskaya 35/10 kv | 1,6+4 | 0 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | opened | 157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 0.22 | 2.64 | 0 | 0 | 2.64 | 0 | 6.615 | 3.975 | 3.975 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.22 | 2.52 | 0 | 0 | 2.52 | 0 | 6.615 | 4.095
158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened | 158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 0.116 | 1.886 | 0.75 | 120 | 1.136 | 0 | 4.2 | 3.064 | 3.064 | opened
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.116 | 1.196 | 0.75 | 120 | 0.446 | 0 | 4.2 | 3.754
159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.37 | 0.27 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | opened | 159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.014 | 0.384 | 0.27 | 120 | 0.114 | 0 | 1.68 | 1.566 | 1.566 | opened
160 | Sharya (r) 110/35/6 kv | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | opened | 160 | Sharya (r) 110/35/6 kv | 20+25 | 0.393 | 19.413 | 2 | 120 | 17.413 | 0 | 21 | 3.587 | 3.587 | opened
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.393 | 7.213 | 2 | 120 | 5.213 | 0 | 21 | 15.787
161 | Industrial hub 110/6/6 kv | 25+25 | 3.32 | 2.5 | 120 | 0.82 | 0 | 26.25 | 25.43 | 25.43 | opened | 161 | Industrial hub 110/6/6 kv | 25+25 | 0.129 | 3.449 | 2.5 | 120 | 0.949 | 0 | 26.25 | 25.301 | 25.301 | opened
162 | Krivyachka 35/10 kv | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | opened | 162 | Krivyachka 35/10 kv | 1,6+1 | 0.015 | 0.835 | 0.57 | 120 | 0.265 | 0 | 1.05 | 0.785 | 0.785 | opened
163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.89 | 0 | 0 | 0.89 | 0 | 1.68 | 0.79 | 0.79 | opened | 163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.196 | 1.086 | 0 | 0 | 1.086 | 0 | 1.68 | 0.594 | 0.594 | opened
164 | Tsentralnaya 35/6 kv | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | opened | 164 | Tsentralnaya 35/6 kv | 10+10 | 1.665 | 10.625 | 3 | 120 | 7.625 | 0 | 10.5 | 2.875 | 2.875 | opened
| Total over Kostromaenergo | 1705 | 403.61 | [8 empty] | 2: Total over Kostromaenergo; 3: 1705; 5: 489.545
| deficit | [8 empty] | -6.235 |  | 2: deficit; Min 12: -16.712
| proficit | [8 empty] | 523.32 |  | 2: proficit; Min 12: 455.274