## брянск
[9 empty] | table 1 | [12 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
|  |  | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kV Lopandino | 6.3 | 0.231 | 1.2 | 1 day and night | -0.969 | 0 | 6.615 | 7.584 | 7.584 | open | 1 | SS 110/10 kV Lopandino | 6.3 | 0 | 0.231 | 1.2 | 1 day and night | -0.969 | 0 | 6.615 | 7.584 | 7.584 | open
2 | SS 110/35/10 kV Nerussa | 16 | 2.904 | 3.4 | 1 day and night | -0.496 | 0 | 16.8 | 17.296 | 14.787 | open | 2 | SS 110/35/10 kV Nerussa | 16 | 0.0508 | 2.9548 | 2.6 | 1 day and night | 0.3548 | 0 | 16.8 | 16.4452 | 14.787 | open
| Nom. capacity MV, MVA | 16 | 2.013 | 1.5 | 1 day and night | 0.513 | 0 | 16.8 | 14.787 |  |  |  | Nom. capacity MV, MVA | 16 |  | 2.013 | 1.5 | 1 day and night | 0.513 | 0 | 16.8 | 14.787
| Nom. capacity LV, MVA | 16 | 0.891 | 1.9 | 1 day and night | -1.009 | 0 | 16.8 | 17.809 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0508 | 0.9418 | 1.1 | 1 day and night | -0.1582 | 0 | 16.8 | 16.9582
3 | SS 110/6 kV Svenskaya | 6.3 | 1.327 | 1.5 | 1 day and night | -0.173 | 0 | 6.615 | 6.788 | 6.788 | open | 3 | SS 110/6 kV Svenskaya | 6.3 | 0.2035 | 1.5305 | 1.5 | 1 day and night | 0.0305 | 0 | 6.615 | 6.5845 | 6.5845 | open
4 | SS 110/10 kV Khmelevskaya | 6.3 | 0.366 | 0.361 | 1 day and night | 0.005 | 0 | 6.615 | 6.61 | 6.61 | open | 4 | SS 110/10 kV Khmelevskaya | 6.3 | 0.0662 | 0.4322 | 0.361 | 1 day and night | 0.0712 | 0 | 6.615 | 6.5438 | 6.5438 | open
5 | SS 110/6 kV Energoremont | 10 | 5.456 | 6.4 | 1 day and night | -0.944 | 0 | 10.5 | 11.444 | 11.444 | open | 5 | SS 110/6 kV Energoremont | 10 | 0 | 5.456 | 6.4 | 1 day and night | -0.944 | 0 | 10.5 | 11.444 | 11.444 | open
1 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.805 | 0.671 | 1 day and night | 0.134 | 0 | 10.5 | 10.366 | 10.366 | open | 1 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.0276 | 0.8326 | 0.671 | 1 day and night | 0.1616 | 0 | 10.5 | 10.3384 | 10.3384 | open
2 | SS 110/10 kV Glybochka | 2.5 | 0.215 | 1.225 | 1 day and night | -1.01 | 0 | 2.625 | 3.635 | 3.635 | open | 2 | SS 110/10 kV Glybochka | 2.5 | 0.5191 | 0.7341 | 1.225 | 1 day and night | -0.4909 | 0 | 2.625 | 3.1159 | 3.1159 | open
3 | SS 110/10 kV Desyatukha | 6.3 | 0.885 | 1.187 | 1 day and night | -0.302 | 0 | 6.615 | 6.917 | 6.917 | open | 3 | SS 110/10 kV Desyatukha | 6.3 | 0.0258 | 0.9108 | 1.187 | 1 day and night | -0.2762 | 0 | 6.615 | 6.8912 | 6.8912 | open
4 | SS 110/35/10 kV Ivaytenki | 6.3 | 1.309 | 1.6 | 1 day and night | -0.291 | 0 | 6.615 | 6.906 | 5.972 | open | 4 | SS 110/35/10 kV Ivaytenki | 6.3 | 0.0562 | 1.3652 | 1.6 | 1 day and night | -0.2348 | 0 | 6.615 | 6.8498 | 5.972 | open
| Nom. capacity MV, MVA | 6.3 | 0.643 | 0.9 | 1 day and night | 0 | 0 | 6.615 | 5.972 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.643 | 0.9 | 1 day and night | 0 | 0 | 6.615 | 5.972
| Nom. capacity LV, MVA | 6.3 | 0.666 | 0.7 | 1 day and night | -0.034 | 0 | 6.615 | 6.649 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.0562 | 0.7222 | 0.7 | 1 day and night | 0.0222 | 0 | 6.615 | 6.5928
5 | SS 110/35/10 kV Lugovaya | 16 | 5.093 | 4.7 | 1 day and night | 0.393 | 0 | 16.8 | 16.407 | 12.45 | open | 5 | SS 110/35/10 kV Lugovaya | 16 | 0.0668 | 5.1598 | 4.7 | 1 day and night | 0.4598 | 0 | 16.8 | 16.3402 | 12.45 | open
| Nom. capacity MV, MVA | 16 | 4.35 | 3.8 | 1 day and night | 0.55 | 0 | 16.8 | 12.45 |  |  |  | Nom. capacity MV, MVA | 16 |  | 4.35 | 3.8 | 1 day and night | 0.55 | 0 | 16.8 | 12.45
| Nom. capacity LV, MVA | 16 | 0.743 | 0.9 | 1 day and night | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0668 | 0.8098 | 0.9 | 1 day and night | 0 | 0 | 16.8 | 16.8
6 | SS 110/35/10 kV Plyuskovo | 6.3 | 1.967 | 2.1 | 1 day and night | -0.133 | 0 | 6.615 | 6.748 | 5.385 | open | 6 | SS 110/35/10 kV Plyuskovo | 6.3 | 0.5018 | 2.4688 | 2.1 | 1 day and night | 0.3688 | 0 | 6.615 | 6.2462 | 5.385 | open
| Nom. capacity MV, MVA | 6.3 | 1.23 | 1.1 | 1 day and night | 0 | 0 | 6.615 | 5.385 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1.23 | 1.1 | 1 day and night | 0 | 0 | 6.615 | 5.385
| Nom. capacity LV, MVA | 6.3 | 0.737 | 1 | 1 day and night | -0.263 | 0 | 6.615 | 6.878 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.5018 | 1.2388 | 1 | 1 day and night | 0.2388 | 0 | 6.615 | 6.3762
7 | SS 35/10 kV Aleshinskaya | 2.5 | 0.338 | 0.338 | 1 day and night | 0.338 | 0 | 0.338 | 0 | 0 | open | 7 | SS 35/10 kV Aleshinskaya | 2.5 | 0.0757 | 0.4137 | 0.4137 | 1 day and night | 0.4137 | 0 | 0.4137 | 0 | 0 | open
8 | SS 35/10 kV Altukhovskaya | 1.6 | 0.375 | 0.375 | 1 day and night | 0.375 | 0 | 0.375 | 0 | 0 | open | 8 | SS 35/10 kV Altukhovskaya | 1.6 | 0 | 0.375 | 0.375 | 1 day and night | 0.375 | 0 | 0.375 | 0 | 0 | open
9 | SS 35/10 kV Domashovo | 2.5 | 0.354 | 0.354 | 1 day and night | 0.354 | 0 | 0.354 | 0 | 0 | open | 9 | SS 35/10 kV Domashovo | 2.5 | 0.6923 | 1.0463 | 1.0463 | 1 day and night | 1.0463 | 0 | 1.0463 | 0 | 0 | open
10 | SS 35/6 kV Dronovskaya | 2.5 | 0.354 | 0.354 | 1 day and night | 0.354 | 0 | 0.354 | 0 | 0 | open | 10 | SS 35/6 kV Dronovskaya | 2.5 | 0.0432 | 0.3972 | 0.3972 | 1 day and night | 0.3972 | 0 | 0.3972 | 0 | 0 | open
11 | SS 35/10 kV Kokorevskaya | 4 | 0.851 | 0.851 | 1 day and night | 0.851 | 0 | 0.851 | 0 | 0 | open | 11 | SS 35/10 kV Kokorevskaya | 4 | 0.003 | 0.854 | 0.854 | 1 day and night | 0.854 | 0 | 0.854 | 0 | 0 | open
12 | SS 35/6 kV Malopolpinskaya | 4 | 0.819 | 0.819 | 1 day and night | 0.819 | 0 | 0.819 | 0 | 0 | open | 12 | SS 35/6 kV Malopolpinskaya | 4 | 0.091 | 0.91 | 0.91 | 1 day and night | 0.91 | 0 | 0.91 | 0 | 0 | open
13 | SS 35/10 kV Morachevskaya | 1.6 | 0.332 | 0.332 | 1 day and night | 0.332 | 0 | 0.332 | 0 | 0 | open | 13 | SS 35/10 kV Morachevskaya | 1.6 | 0.632 | 0.964 | 0.964 | 1 day and night | 0.964 | 0 | 0.964 | 0 | 0 | open
14 | SS 35/10 kV Saltanovskaya | 2.5 | 0.591 | 0.591 | 1 day and night | 0.591 | 0 | 0.591 | 0 | 0 | open | 14 | SS 35/10 kV Saltanovskaya | 2.5 | 0.005 | 0.596 | 0.596 | 1 day and night | 0.596 | 0 | 0.596 | 0 | 0 | open
15 | SS 35/10 kV Svetovo | 2.5 | 0.328 | 0.328 | 1 day and night | 0.328 | 0 | 0.328 | 0 | 0 | open | 15 | SS 35/10 kV Svetovo | 2.5 | 0.0211 | 0.3491 | 0.3491 | 1 day and night | 0.3491 | 0 | 0.3491 | 0 | 0 | open
16 | SS 35/10 kV Seshcha | 2.5 | 0.789 | 0.789 | 1 day and night | 0.789 | 0 | 0.789 | 0 | 0 | open | 16 | SS 35/10 kV Seshcha | 2.5 | 0.01 | 0.799 | 0.799 | 1 day and night | 0.799 | 0 | 0.799 | 0 | 0 | open
17 | SS 35/10 kV Sovkhoznaya | 4 | 0.3 | 0.3 | 1 day and night | 0.3 | 0 | 0.3 | 0 | 0 | open | 17 | SS 35/10 kV Sovkhoznaya | 4 | 0.0071 | 0.3071 | 0.3071 | 1 day and night | 0.3071 | 0 | 0.3071 | 0 | 0 | open
18 | SS 35/10 kV Strachevskaya | 2.5 | 0.494 | 0.494 | 1 day and night | 0.494 | 0 | 0.494 | 0 | 0 | open | 18 | SS 35/10 kV Strachevskaya | 2.5 | 0.0572 | 0.5512 | 0.5512 | 1 day and night | 0.5512 | 0 | 0.5512 | 0 | 0 | open
19 | SS 35/10 kV Strashevichi | 4 | 0.772 | 0.772 | 1 day and night | 0.772 | 0 | 0.772 | 0 | 0 | open | 19 | SS 35/10 kV Strashevichi | 4 | 0.8407 | 1.6127 | 1.6127 | 1 day and night | 1.6127 | 0 | 1.6127 | 0 | 0 | open
20 | SS 35/10 kV Usozhskaya | 2.5 | 0.685 | 0.685 | 1 day and night | 0.685 | 0 | 0.685 | 0 | 0 | open | 20 | SS 35/10 kV Usozhskaya | 2.5 | 0.046 | 0.731 | 0.731 | 1 day and night | 0.731 | 0 | 0.731 | 0 | 0 | open
21 | SS 35/10 kV Kharinovskaya | 1 | 0.085 | 0.085 | 1 day and night | 0.085 | 0 | 0.085 | 0 | 0 | open | 21 | SS 35/10 kV Kharinovskaya | 1 | 0 | 0.085 | 0.085 | 1 day and night | 0.085 | 0 | 0.085 | 0 | 0 | open
22 | SS 35/10 kV Kharitonovskaya | 4 | 0.667 | 0.667 | 1 day and night | 0.667 | 0 | 0.667 | 0 | 0 | open | 22 | SS 35/10 kV Kharitonovskaya | 4 | 0.1138 | 0.7808 | 0.7808 | 1 day and night | 0.7808 | 0 | 0.7808 | 0 | 0 | open
23 | SS 35/10 kV Divovka | 2.5 | 0.624 | 0.624 | 1 day and night | 0.624 | 0 | 0.624 | 0 | 0 | open | 23 | SS 35/10 kV Divovka | 2.5 | 0.013 | 0.637 | 0.637 | 1 day and night | 0.637 | 0 | 0.637 | 0 | 0 | open
24 | SS 35/10 kV Molodkovo | 1 | 0.179 | 0.179 | 1 day and night | 0.179 | 0 | 0.179 | 0 | 0 | open | 24 | SS 35/10 kV Molodkovo | 1 | 0 | 0.179 | 0.179 | 1 day and night | 0.179 | 0 | 0.179 | 0 | 0 | open
25 | SS 35/10 kV Papsuevskaya | 2.5 | 0.434 | 0.434 | 1 day and night | 0.434 | 0 | 0.434 | 0 | 0 | open | 25 | SS 35/10 kV Papsuevskaya | 2.5 | 0.0054 | 0.4394 | 0.4394 | 1 day and night | 0.4394 | 0 | 0.4394 | 0 | 0 | open
26 | SS 35/10 kV Radutinskaya | 1.6 | 0.651 | 0.651 | 1 day and night | 0.651 | 0 | 0.651 | 0 | 0 | open | 26 | SS 35/10 kV Radutinskaya | 1.6 | 0.0774 | 0.7284 | 0.7284 | 1 day and night | 0.7284 | 0 | 0.7284 | 0 | 0 | open
27 | SS 35/6 kV Ushchepye | 1.6 | 0.155 | 0.155 | 1 day and night | 0.155 | 0 | 0.155 | 0 | 0 | open | 27 | SS 35/6 kV Ushchepye | 1.6 | 0.0322 | 0.1872 | 0.1872 | 1 day and night | 0.1872 | 0 | 0.1872 | 0 | 0 | open
28 | SS 35/10 kV Ushchepye | 1.6 | 0.049 | 0.049 | 1 day and night | 0.049 | 0 | 0.049 | 0 | 0 | open | 28 | SS 35/10 kV Ushchepye | 1.6 | 0 | 0.049 | 0.049 | 1 day and night | 0.049 | 0 | 0.049 | 0 | 0 | open
29 | SS 35/10 kV Yakovskaya | 2.5 | 0.58 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0 | 0 | open | 29 | SS 35/10 kV Yakovskaya | 2.5 | 0.0337 | 0.6137 | 0.6137 | 1 day and night | 0.6137 | 0 | 0.6137 | 0 | 0 | open
30 | SS 110/35/6 kV Aksinino | 40+40 | 21.1 | 0 | 0 | 21.1 | 0 | 42 | 20.9 | 20.9 | open | 30 | SS 110/35/6 kV Aksinino | 40+40 | 0.019 | 21.119 | 0 | 0 | 21.119 | 0 | 42 | 20.881 | 20.881 | open
| Nom. capacity MV, MVA | 40+40 | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5
| Nom. capacity LV, MVA | 40+40 | 17.6 | 0 | 0 | 17.6 | 0 | 42 | 24.4 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.019 | 17.619 | 0 | 0 | 17.619 | 0 | 42 | 24.381
31 | SS 110/10 kV Airport | 6,3+6,3 | 0.736 | 0 | 0 | 0.736 | 0 | 6.615 | 5.879 | 5.879 | open | 31 | SS 110/10 kV Airport | 6,3+6,3 | 0.0603 | 0.7963 | 0 | 0 | 0.7963 | 0 | 6.615 | 5.8187 | 5.8187 | open
32 | SS 110/6 kV Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed | 32 | SS 110/6 kV Bezhitskaya | 25+40 | 3.811 | 38.381 | 0 | 0 | 38.381 | 0 | 26.25 | -12.131 | -12.131 | closed
33 | SS 110/6 kV Water intake | 6,3+6,3 | 2.11 | 0 | 0 | 2.11 | 0 | 6.615 | 4.505 | 4.505 | open | 33 | SS 110/6 kV Water intake | 6,3+6,3 | 0.8442 | 2.9542 | 0 | 0 | 2.9542 | 0 | 6.615 | 3.6608 | 3.6608 | open
34 | SS 110/6 kV Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 час | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed | 34 | SS 110/6 kV Gorodishchenskaya | 16+16 | 1.0481 | 26.6081 | 1.5 | 12 час | 25.1081 | 0 | 16.8 | -8.3081 | -8.3081 | closed
35 | SS 110/10 kV Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138 | -0.138 | closed | 35 | SS 110/10 kV Dobrunskaya | 6,3+4 | 1.8685 | 6.2065 | 0 | 0 | 6.2065 | 0 | 4.2 | -2.0065 | -2.0065 | closed
36 | SS 110/35/6 kV Dormashevskaya | 40+63 | 44.35 | 0 | 0 | 44.35 | 0 | 42 | -2.35 | -2.35 | closed | 36 | SS 110/35/6 kV Dormashevskaya | 40+63 | 3.4765 | 47.8265 | 0 | 0 | 47.8265 | 0 | 42 | -5.8265 | -5.8265 | closed
| Nom. capacity MV, MVA | 40+63 | 25.76 | 0 | 0 | 25.76 | 0 | 42 | 16.24 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 25.76 | 0 | 0 | 25.76 | 0 | 42 | 16.24
| Nom. capacity LV, MVA | 40+63 | 18.59 | 0 | 0 | 18.59 | 0 | 42 | 23.41 |  |  |  | Nom. capacity LV, MVA | 40+63 | 3.4765 | 22.0665 | 0 | 0 | 22.0665 | 0 | 42 | 19.9335
37 | SS 110/35/10 kV Dubrovskaya | 16+16 | 8.741 | 0 | 0 | 8.741 | 0 | 16.8 | 8.059 | 8.059 | open | 37 | SS 110/35/10 kV Dubrovskaya | 16+16 | 0.1001 | 8.8411 | 0 | 0 | 8.8411 | 0 | 16.8 | 7.9589 | 7.9589 | open
| Nom. capacity MV, MVA | 16+16 | 5.239 | 0 | 0 | 5.239 | 0 | 16.8 | 11.561 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.239 | 0 | 0 | 5.239 | 0 | 16.8 | 11.561
| Nom. capacity LV, MVA | 16+16 | 3.502 | 0 | 0 | 3.502 | 0 | 16.8 | 13.298 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1001 | 3.6021 | 0 | 0 | 3.6021 | 0 | 16.8 | 13.1979
38 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 37.17 | 7.92 | 12 час | 29.25 | 0 | 26.25 | -3 | -3 | closed | 38 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 0.0129 | 37.1829 | 8.9 | 12 час | 28.2829 | 0 | 26.25 | -2.0329 | -3.0129 | closed
| Nom. capacity MV, MVA | 25+25 | 7.92 | 7.92 | 12 час | 0 | 0 | 26.25 | 18.33 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 7.92 | 8.9 | 12 час | -0.98 | 0 | 26.25 | 18.33
| Nom. capacity LV, MVA | 25+25 | 29.25 | 0 | 0 | 29.25 | 0 | 26.25 | -3 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.0129 | 29.2629 | 0 | 0 | 29.2629 | 0 | 26.25 | -3.0129
39 | SS 110/35/10 kV Zhukovskaya | 16+25 | 12.76 | 5.2 | 6 час | 7.56 | 0 | 16.8 | 9.24 | 9.24 | open | 39 | SS 110/35/10 kV Zhukovskaya | 16+25 | 0.1791 | 12.9391 | 5.2 | 6 час | 7.7391 | 0 | 16.8 | 9.0609 | 9.0609 | open
| Nom. capacity MV, MVA | 16+25 | 5.9 | 5.2 | 6 час | 0.7 | 0 | 16.8 | 10.9 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 5.9 | 5.2 | 6 час | 0.7 | 0 | 16.8 | 10.9
| Nom. capacity LV, MVA | 16+25 | 6.86 | 0 | 0 | 6.86 | 0 | 16.8 | 9.94 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.1791 | 7.0391 | 0 | 0 | 7.0391 | 0 | 16.8 | 9.7609
40 | SS 110/6 kV Zarechnaya | 10+10 | 8.27 | 0 | 0 | 8.27 | 0 | 10.5 | 2.23 | 2.23 | open | 40 | SS 110/6 kV Zarechnaya | 10+10 | 1.398 | 9.668 | 0 | 0 | 9.668 | 0 | 10.5 | 0.832 | 0.832 | open
41 | SS 110/35/6 kV Ivotskaya | 25+25 | 15.72 | 2.68 | 6 час | 13.04 | 0 | 26.25 | 13.21 | 13.21 | open | 41 | SS 110/35/6 kV Ivotskaya | 25+25 | 0 | 15.72 | 2.4 | 6 час | 13.32 | 0 | 26.25 | 12.93 | 12.93 | open
| Nom. capacity MV, MVA | 25+25 | 6.07 | 2.68 | 6 час | 3.39 | 0 | 26.25 | 20.18 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.07 | 2.4 | 6 час | 3.67 | 0 | 26.25 | 20.18
| Nom. capacity LV, MVA | 25+25 | 9.65 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 9.65 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kV Kamvolnaya | 25+25 | 17.92 | 0 | 0 | 17.92 | 0 | 26.25 | 8.33 | 8.33 | open | 42 | SS 110/6 kV Kamvolnaya | 25+25 | 1.7811 | 19.7011 | 0 | 0 | 19.7011 | 0 | 26.25 | 6.5489 | 6.5489 | open
43 | SS 110/6 kV Karachevskaya | 16+25 | 11.684 | 0 | 0 | 11.684 | 0 | 16.8 | 5.116 | 5.116 | open | 43 | SS 110/6 kV Karachevskaya | 16+25 | 0.3493 | 12.0333 | 0 | 0 | 12.0333 | 0 | 16.8 | 4.7667 | 4.7667 | open
44 | SS 110/6 kV Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed | 44 | SS 110/6 kV Karachizhskaya | 10+10 | 2.7528 | 21.0328 | 0 | 0 | 21.0328 | 0 | 10.5 | -10.5328 | -10.5328 | closed
45 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 7.056 | 1.4 | 6 час | 5.656 | 0 | 10.5 | 4.844 | 4.844 | open | 45 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 0.5655 | 7.6215 | 1.4 | 6 час | 6.2215 | 0 | 10.5 | 4.2785 | 4.2785 | open
| Nom. capacity MV, MVA | 10+16 | 2.234 | 1.4 | 6 час | 0.834 | 0 | 10.5 | 8.266 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 2.234 | 1.4 | 6 час | 0.834 | 0 | 10.5 | 8.266
| Nom. capacity LV, MVA | 10+16 | 4.822 | 0 | 0 | 4.822 | 0 | 10.5 | 5.678 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.5655 | 5.3875 | 0 | 0 | 5.3875 | 0 | 10.5 | 5.1125
46 | SS 110/35/10 kV Komarichi | 16+16 | 10.253 | 3.7 | 6 час | 6.553 | 0 | 16.8 | 10.247 | 10.247 | open | 46 | SS 110/35/10 kV Komarichi | 16+16 | 0.0603 | 10.3133 | 3.7 | 6 час | 6.6133 | 0 | 16.8 | 10.1867 | 10.1867 | open
| Nom. capacity MV, MVA | 16+16 | 4.997 | 3.7 | 6 час | 1.297 | 0 | 16.8 | 11.803 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.997 | 3.7 | 6 час | 1.297 | 0 | 16.8 | 11.803
| Nom. capacity LV, MVA | 16+16 | 5.256 | 0 | 0 | 5.256 | 0 | 16.8 | 11.544 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.0603 | 5.3163 | 0 | 0 | 5.3163 | 0 | 16.8 | 11.4837
47 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.717 | 0 | 0 | 0.717 | 0 | 2.625 | 1.908 | 1.908 | open | 47 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.0442 | 0.7612 | 0 | 0 | 0.7612 | 0 | 2.625 | 1.8638 | 1.8638 | open
48 | SS 110/6 kV Mamonovskaya | 16+16 | 15.29 | 0 | 0 | 15.29 | 0 | 16.8 | 1.51 | 1.51 | open | 48 | SS 110/6 kV Mamonovskaya | 16+16 | 0.6366 | 15.9266 | 0 | 0 | 15.9266 | 0 | 16.8 | 0.8734 | 0.8734 | open
49 | SS 110/35/10 kV Maritskaya | 10+16 | 5.796 | 4.5 | 6 час | 1.296 | 0 | 10.5 | 9.204 | 5.362 | open | 49 | SS 110/35/10 kV Maritskaya | 10+16 | 0.1489 | 5.9449 | 4.5 | 6 час | 1.4449 | 0 | 10.5 | 9.0551 | 5.362 | open
| Nom. capacity MV, MVA | 10+16 | 5.138 | 4.5 | 6 час | 0 | 0 | 10.5 | 5.362 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 5.138 | 4.5 | 6 час | 0 | 0 | 10.5 | 5.362
| Nom. capacity LV, MVA | 10+16 | 0.658 | 0 | 0 | 0.658 | 0 | 10.5 | 9.842 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.1489 | 0.8069 | 0 | 0 | 0.8069 | 0 | 10.5 | 9.6931
50 | SS 110/6 kV Michurinskaya | 10+10 | 3.457 | 0 | 0 | 3.457 | 0 | 6.615 | 3.158 | 3.158 | open | 50 | SS 110/6 kV Michurinskaya | 10+10 | 0.9677 | 4.4247 | 0 | 0 | 4.4247 | 0 | 6.615 | 2.1903 | 2.1903 | open
51 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 2.438 | 0 | 0 | 2.438 | 0 | 6.615 | 4.177 | 4.177 | open | 51 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 0.1876 | 2.6256 | 0 | 0 | 2.6256 | 0 | 6.615 | 3.9894 | 3.9894 | open
52 | SS 110/10 kV Polpinskaya | 16+16 | 5.734 | 0 | 0 | 5.734 | 0 | 16.8 | 11.066 | 11.066 | open | 52 | SS 110/10 kV Polpinskaya | 16+16 | 0.0967 | 5.8307 | 0 | 0 | 5.8307 | 0 | 16.8 | 10.9693 | 10.9693 | open
53 | SS 110/6 kV Sovetskaya | 16+16+25+40 | 36.96 | 0 | 0 | 36.96 | 0 | 59.85 | 22.89 | 22.89 | open | 53 | SS 110/6 kV Sovetskaya | 16+16+25+40 | 18.6429 | 55.6029 | 0 | 0 | 55.6029 | 0 | 59.85 | 4.2471 | 4.2471 | open
54 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 46.85 | 0 | 0 | 46.85 | 0 | 75.075 | 28.225 | 28.225 | open | 54 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 0.178 | 47.028 | 0 | 0 | 47.028 | 0 | 75.075 | 28.047 | 28.047 | open
55 | SS 110/10 kV Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | open | 55 | SS 110/10 kV Teplichnaya | 10+10 | 0.5453 | 5.4453 | 0 | 0 | 5.4453 | 0 | 10.5 | 5.0547 | 5.0547 | open
56 | SS 110/6 kV Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | open | 56 | SS 110/6 kV Uritskaya | 20+20 | 0 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | open
57 | SS 110/35/10 kV Tsentralnaya | 16+16 | 10.488 | 4.8 | 6 час | 5.688 | 0 | 16.8 | 11.112 | 10.032 | open | 57 | SS 110/35/10 kV Tsentralnaya | 16+16 | 0.1727 | 10.6607 | 4.8 | 6 час | 5.8607 | 0 | 16.8 | 10.9393 | 9.8593 | open
| Nom. capacity MV, MVA | 16+16 | 3.72 | 4.8 | 6 час | -1.08 | 0 | 16.8 | 13.08 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.72 | 4.8 | 6 час | -1.08 | 0 | 16.8 | 13.08
| Nom. capacity LV, MVA | 16+16 | 6.768 | 0 | 0 | 6.768 | 0 | 16.8 | 10.032 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1727 | 6.9407 | 0 | 0 | 6.9407 | 0 | 16.8 | 9.8593
58 | SS 110/6 kV Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed | 58 | SS 110/6 kV Yuzhnaya | 16+25 | 0.238 | 19.668 | 0 | 0 | 19.668 | 0 | 16.8 | -2.868 | -2.868 | closed
59 | SS 110/10 kV Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | open | 59 | SS 110/10 kV Bobovichi | 6,3+2,5 | 0.0226 | 1.5196 | 0 | 0 | 1.5196 | 0 | 2.625 | 1.1054 | 1.1054 | open
60 | SS 110/6 kV Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | open | 60 | SS 110/6 kV Belaya Berezka | 16+25 | 0 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | open
61 | SS 110/10 kV Valuets | 4+6,3 | 1.239 | 0 | 0 | 1.239 | 0 | 4.2 | 2.961 | 2.961 | open | 61 | SS 110/10 kV Valuets | 4+6,3 | 0.1009 | 1.3399 | 0 | 0 | 1.3399 | 0 | 4.2 | 2.8601 | 2.8601 | open
62 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 1.873 | 0.54 | 3 час | 1.333 | 0 | 6.615 | 5.282 | 4.984 | open | 62 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 0.0161 | 1.8891 | 0.54 | 3 час | 1.3491 | 0 | 6.615 | 5.2659 | 4.9679 | open
| Nom. capacity MV, MVA | 10+6,3 | 0.242 | 0.54 | 3 час | 0 | 0 | 6.615 | 6.373 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.242 | 0.54 | 3 час | 0 | 0 | 6.615 | 6.373
| Nom. capacity LV, MVA | 10+6,3 | 1.631 | 0 | 0 | 1.631 | 0 | 6.615 | 4.984 |  |  |  | Nom. capacity LV, MVA | 10+6,3 | 0.0161 | 1.6471 | 0 | 0 | 1.6471 | 0 | 6.615 | 4.9679
63 | SS 110/6 kV Vysokoe | 40+40 | 31.467 | 0 | 0 | 31.467 | 0 | 42 | 10.533 | 10.533 | open | 63 | SS 110/6 kV Vysokoe | 40+40 | 0.0676 | 31.5346 | 0 | 0 | 31.5346 | 0 | 42 | 10.4654 | 10.4654 | open
64 | SS 110/10 kV Zalineynaya | 10+6,3 | 2.493 | 0 | 0 | 2.493 | 0 | 6.615 | 4.122 | 4.122 | open | 64 | SS 110/10 kV Zalineynaya | 10+6,3 | 0.2939 | 2.7869 | 0 | 0 | 2.7869 | 0 | 6.615 | 3.8281 | 3.8281 | open
65 | SS 110/6 kV Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | closed | 65 | SS 110/6 kV Zapadnaya | 10+10 | 0.0747 | 10.5747 | 0 | 0 | 10.5747 | 0 | 10.5 | -0.0747 | -0.0747 | closed
66 | SS 110/35/10 kV Klimovo | 16+16 | 10.535 | 1.64 | 6 час | 8.895 | 0 | 16.8 | 7.905 | 7.905 | open | 66 | SS 110/35/10 kV Klimovo | 16+16 | 0.1955 | 10.7305 | 1.64 | 6 час | 9.0905 | 0 | 16.8 | 7.7095 | 7.7095 | open
| Nom. capacity MV, MVA | 16+16 | 3.301 | 1.64 | 6 час | 1.661 | 0 | 16.8 | 13.499 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.301 | 1.64 | 6 час | 1.661 | 0 | 16.8 | 13.499
| Nom. capacity LV, MVA | 16+16 | 7.234 | 0 | 0 | 7.234 | 0 | 16.8 | 9.566 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1955 | 7.4295 | 0 | 0 | 7.4295 | 0 | 16.8 | 9.3705
67 | SS 110/35/6 kV Kozhany | 10+10 | 3.521 | 3.12 | 6 час | 0.401 | 0 | 10.5 | 10.099 | 7.795 | open | 67 | SS 110/35/6 kV Kozhany | 10+10 | 0.019 | 3.54 | 3.12 | 6 час | 0.42 | 0 | 10.5 | 10.08 | 7.795 | open
| Nom. capacity MV, MVA | 10+10 | 2.705 | 3.12 | 6 час | -0.415 | 0 | 10.5 | 7.795 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 2.705 | 3.12 | 6 час | -0.415 | 0 | 10.5 | 7.795
| Nom. capacity LV, MVA | 10+10 | 0.816 | 0 | 0 | 0.816 | 0 | 10.5 | 9.684 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.019 | 0.835 | 0 | 0 | 0.835 | 0 | 10.5 | 9.665
68 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 0.668 | 0 | 0 | 0.668 | 0 | 2.625 | 1.957 | 1.957 | open | 68 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 0.1713 | 0.8393 | 0 | 0 | 0.8393 | 0 | 2.625 | 1.7857 | 1.7857 | open
69 | SS 110/35/10 kV Pogar | 16+16+16 | 9.411 | 1.8 | 6 час | 7.611 | 0 | 33.6 | 25.989 | 25.989 | open | 69 | SS 110/35/10 kV Pogar | 16+16+16 | 1.2608 | 10.6718 | 1.8 | 6 час | 8.8718 | 0 | 33.6 | 24.7282 | 24.7282 | open
| Nom. capacity MV, MVA | 16+16 | 1.952 | 1.8 | 6 час | 0.152 | 0 | 33.6 | 31.648 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.952 | 1.8 | 6 час | 0.152 | 0 | 33.6 | 31.648
| Nom. capacity LV, MVA | 16+16 | 7.459 | 0 | 0 | 7.459 | 0 | 33.6 | 26.141 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.2608 | 8.7198 | 0 | 0 | 8.7198 | 0 | 33.6 | 24.8802
70 | SS 110/35/10 kV Pochepskaya | 25+25 | 11.182 | 2.21 | 3 час | 8.972 | 0 | 26.25 | 17.278 | 16.497 | open | 70 | SS 110/35/10 kV Pochepskaya | 25+25 | 3.2383 | 14.4203 | 2.21 | 3 час | 12.2103 | 0 | 26.25 | 14.0397 | 13.2587 | open
| Nom. capacity MV, MVA | 25+25 | 1.429 | 2.21 | 3 час | -0.781 | 0 | 26.25 | 24.821 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 1.429 | 2.21 | 3 час | -0.781 | 0 | 26.25 | 24.821
| Nom. capacity LV, MVA | 25+25 | 9.753 | 0 | 0 | 9.753 | 0 | 26.25 | 16.497 |  |  |  | Nom. capacity LV, MVA | 25+25 | 3.2383 | 12.9913 | 0 | 0 | 12.9913 | 0 | 26.25 | 13.2587
71 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.279 | 0 | 0 | 0.279 | 0 | 2.625 | 2.346 | 2.346 | open | 71 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.006 | 0.285 | 0 | 0 | 0.285 | 0 | 2.625 | 2.34 | 2.34 | open
72 | SS 110/35/10 kV Starodub | 16+16 | 12.564 | 7.34 | 6 час | 5.224 | 0 | 16.8 | 11.576 | 9.465 | open | 72 | SS 110/35/10 kV Starodub | 16+16 | 0.025 | 12.589 | 7.34 | 6 час | 5.249 | 0 | 16.8 | 11.551 | 9.465 | open
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 час | -0.005 | 0 | 16.8 | 9.465 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 час | -0.005 | 0 | 16.8 | 9.465
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 16.8 | 11.571 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.025 | 5.254 | 0 | 0 | 5.254 | 0 | 16.8 | 11.546
73 | SS 110/10 kV Staroselye | 6,3+6,3 | 1.116 | 0 | 0 | 1.116 | 0 | 6.615 | 5.499 | 5.499 | open | 73 | SS 110/10 kV Staroselye | 6,3+6,3 | 0.0544 | 1.1704 | 0 | 0 | 1.1704 | 0 | 6.615 | 5.4446 | 5.4446 | open
74 | SS 110/35/6 kV Surazh | 16+16 | 19.433 | 3.04 | 6 час | 16.393 | 0 | 16.8 | 0.407 | 0.185 | open | 74 | SS 110/35/6 kV Surazh | 16+16 | 0 | 19.433 | 3.04 | 6 час | 16.393 | 0 | 16.8 | 0.407 | 0.185 | open
| Nom. capacity MV, MVA | 16+16 | 2.818 | 3.04 | 6 час | -0.222 | 0 | 16.8 | 13.982 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 2.818 | 3.04 | 6 час | -0.222 | 0 | 16.8 | 13.982
| Nom. capacity LV, MVA | 16+16 | 16.615 | 0 | 0 | 16.615 | 0 | 16.8 | 0.185 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 16.615 | 0 | 0 | 16.615 | 0 | 16.8 | 0.185
75 | SS 110/10 kV Trubchevsk | 16+10 | 7.977 | 0 | 0 | 7.977 | 0 | 10.5 | 2.523 | 2.523 | open | 75 | SS 110/10 kV Trubchevsk | 16+10 | 0.7107 | 8.6877 | 0 | 0 | 8.6877 | 0 | 10.5 | 1.8123 | 1.8123 | open
76 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.819 | 0 | 0 | 0.819 | 0 | 6.615 | 5.796 | 5.796 | open | 76 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.0229 | 0.8419 | 0 | 0 | 0.8419 | 0 | 6.615 | 5.7731 | 5.7731 | open
77 | SS 110/35/6 kV Yubileynaya | 16+16 | 13.228 | 6.45 | 3 час | 6.778 | 0 | 16.8 | 10.022 | 9.905 | open | 77 | SS 110/35/6 kV Yubileynaya | 16+16 | 1.9292 | 15.1572 | 6.45 | 3 час | 8.7072 | 0 | 16.8 | 8.0928 | 7.9758 | open
| Nom. capacity MV, MVA | 16+16 | 6.333 | 6.45 | 3 час | 0 | 0 | 16.8 | 10.467 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.333 | 6.45 | 3 час | 0 | 0 | 16.8 | 10.467
| Nom. capacity LV, MVA | 16+16 | 6.895 | 0 | 0 | 6.895 | 0 | 16.8 | 9.905 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.9292 | 8.8242 | 0 | 0 | 8.8242 | 0 | 16.8 | 7.9758
78 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 3.334 | 0 | 0 | 3.334 | 0 | 6.615 | 3.281 | 3.281 | open | 78 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 0.043 | 3.377 | 0 | 0 | 3.377 | 0 | 6.615 | 3.238 | 3.238 | open
79 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 3.119 | 0 | 0 | 3.119 | 0 | 6.615 | 3.496 | 3.496 | open | 79 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 0.0187 | 3.1377 | 0 | 0 | 3.1377 | 0 | 6.615 | 3.4773 | 3.4773 | open
80 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.708 | 0 | 0 | 0.708 | 0 | 1.68 | 0.972 | 0.972 | open | 80 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.0078 | 0.7158 | 0 | 0 | 0.7158 | 0 | 1.68 | 0.9642 | 0.9642 | open
81 | SS 35/6 kV Bytosh | 3,2+6,3 | 2.533 | 0 | 0 | 2.533 | 0 | 3.36 | 0.827 | 0.827 | open | 81 | SS 35/6 kV Bytosh | 3,2+6,3 | 0 | 2.533 | 0 | 0 | 2.533 | 0 | 3.36 | 0.827 | 0.827 | open
82 | SS 35/6 kV Velyaminovskaya | 4+4 | 1.217 | 0 | 0 | 1.217 | 0 | 4.2 | 2.983 | 2.983 | open | 82 | SS 35/6 kV Velyaminovskaya | 4+4 | 0.0803 | 1.2973 | 0 | 0 | 1.2973 | 0 | 4.2 | 2.9027 | 2.9027 | open
83 | SS 35/6 kV Vetma | 2,5+2,5 | 0.425 | 0 | 0 | 0.425 | 0 | 2.625 | 2.2 | 2.2 | open | 83 | SS 35/6 kV Vetma | 2,5+2,5 | 0.0315 | 0.4565 | 0 | 0 | 0.4565 | 0 | 2.625 | 2.1685 | 2.1685 | open
84 | SS 35/6 kV Volodarskaya | 10+6,3 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed | 84 | SS 35/6 kV Volodarskaya | 10+6,3 | 0 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed
85 | SS 35/10 kV Glodnevskaya | 4+2,5 | 1.099 | 0 | 0 | 1.099 | 0 | 2.625 | 1.526 | 1.526 | open | 85 | SS 35/10 kV Glodnevskaya | 4+2,5 | 0.0519 | 1.1509 | 0 | 0 | 1.1509 | 0 | 2.625 | 1.4741 | 1.4741 | open
86 | SS 35/6 kV Gorodskaya | 10+10 | 12.37 | 0 | 0 | 12.37 | 0 | 10.5 | -1.87 | -1.87 | closed | 86 | SS 35/6 kV Gorodskaya | 10+10 | 0 | 12.37 | 0 | 0 | 12.37 | 0 | 10.5 | -1.87 | -1.87 | closed
87 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.833 | 0 | 0 | 0.833 | 0 | 4.2 | 3.367 | 3.367 | open | 87 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.0536 | 0.8866 | 0 | 0 | 0.8866 | 0 | 4.2 | 3.3134 | 3.3134 | open
88 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0.253 | 0 | 0 | 0.253 | 0 | 1.68 | 1.427 | 1.427 | open | 88 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0 | 0.253 | 0 | 0 | 0.253 | 0 | 1.68 | 1.427 | 1.427 | open
89 | SS 35/10 kV Zhiryatinskaya | 4+4 | 1.101 | 0 | 0 | 1.101 | 0 | 4.2 | 3.099 | 3.099 | open | 89 | SS 35/10 kV Zhiryatinskaya | 4+4 | 0.0824 | 1.1834 | 0 | 0 | 1.1834 | 0 | 4.2 | 3.0166 | 3.0166 | open
90 | SS 35/10 kV Igritskaya | 4+6,3 | 1.379 | 0 | 0 | 1.379 | 0 | 4.2 | 2.821 | 2.821 | open | 90 | SS 35/10 kV Igritskaya | 4+6,3 | 0.101 | 1.48 | 0 | 0 | 1.48 | 0 | 4.2 | 2.72 | 2.72 | open
91 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.168 | 0 | 0 | 0.168 | 0 | 1.05 | 0.882 | 0.882 | open | 91 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.0188 | 0.1868 | 0 | 0 | 0.1868 | 0 | 1.05 | 0.8632 | 0.8632 | open
92 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.258 | 0 | 0 | 0.258 | 0 | 2.625 | 2.367 | 2.367 | open | 92 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.01 | 0.268 | 0 | 0 | 0.268 | 0 | 2.625 | 2.357 | 2.357 | open
93 | SS 35/10 kV Krupets | 2,5+2,5 | 0.805 | 0 | 0 | 0.805 | 0 | 2.625 | 1.82 | 1.82 | open | 93 | SS 35/10 kV Krupets | 2,5+2,5 | 0.7261 | 1.5311 | 0 | 0 | 1.5311 | 0 | 2.625 | 1.0939 | 1.0939 | open
94 | SS 35/10 kV Luna | 1,6+1,6 | 0.638 | 0 | 0 | 0.638 | 0 | 1.68 | 1.042 | 1.042 | open | 94 | SS 35/10 kV Luna | 1,6+1,6 | 0 | 0.638 | 0 | 0 | 0.638 | 0 | 1.68 | 1.042 | 1.042 | open
95 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 5.144 | 0 | 0 | 5.144 | 0 | 6.615 | 1.471 | 1.471 | open | 95 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 0.0285 | 5.1725 | 0 | 0 | 5.1725 | 0 | 6.615 | 1.4425 | 1.4425 | open
96 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.86 | 0 | 0 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | open | 96 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.0935 | 0.9535 | 0 | 0 | 0.9535 | 0 | 1.68 | 0.7265 | 0.7265 | open
97 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.155 | 0 | 0 | 0.155 | 0 | 1.68 | 1.525 | 1.525 | open | 97 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.0052 | 0.1602 | 0 | 0 | 0.1602 | 0 | 1.68 | 1.5198 | 1.5198 | open
98 | SS 35/10 kV Norinskaya | 4+4 | 0.512 | 0 | 0 | 0.512 | 0 | 4.2 | 3.688 | 3.688 | open | 98 | SS 35/10 kV Norinskaya | 4+4 | 0.0704 | 0.5824 | 0 | 0 | 0.5824 | 0 | 4.2 | 3.6176 | 3.6176 | open
99 | SS 35/6 kV Paltso | 4+2,5 | 0.468 | 0 | 0 | 0.468 | 0 | 2.625 | 2.157 | 2.157 | open | 99 | SS 35/6 kV Paltso | 4+2,5 | 0.018 | 0.486 | 0 | 0 | 0.486 | 0 | 2.625 | 2.139 | 2.139 | open
100 | SS 35/6 kV Pobeda | 4+4 | 2.399 | 0 | 0 | 2.399 | 0 | 4.2 | 1.801 | 1.801 | open | 100 | SS 35/6 kV Pobeda | 4+4 | 0.0264 | 2.4254 | 0 | 0 | 2.4254 | 0 | 4.2 | 1.7746 | 1.7746 | open
101 | SS 35/10 kV Pogreby | 4+4 | 0.915 | 0 | 0 | 0.915 | 0 | 4.2 | 3.285 | 3.285 | open | 101 | SS 35/10 kV Pogreby | 4+4 | 0.057 | 0.972 | 0 | 0 | 0.972 | 0 | 4.2 | 3.228 | 3.228 | open
102 | SS 35/10 kV Privolskaya | 2,5+1,6 | 1.329 | 0 | 0 | 1.329 | 0 | 1.68 | 0.351 | 0.351 | open | 102 | SS 35/10 kV Privolskaya | 2,5+1,6 | 0.3078 | 1.6368 | 0 | 0 | 1.6368 | 0 | 1.68 | 0.0432 | 0.0432 | open
103 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0.711 | 0 | 0 | 0.711 | 0 | 2.625 | 1.914 | 1.914 | open | 103 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0 | 0.711 | 0 | 0 | 0.711 | 0 | 2.625 | 1.914 | 1.914 | open
104 | SS 35/10 kV Rognedinskaya | 4+6,3 | 1.511 | 0 | 0 | 1.511 | 0 | 4.2 | 2.689 | 2.689 | open | 104 | SS 35/10 kV Rognedinskaya | 4+6,3 | 0.0153 | 1.5263 | 0 | 0 | 1.5263 | 0 | 4.2 | 2.6737 | 2.6737 | open
105 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.835 | 0 | 0 | 0.835 | 0 | 4.2 | 3.365 | 3.365 | open | 105 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.02 | 0.855 | 0 | 0 | 0.855 | 0 | 4.2 | 3.345 | 3.345 | open
106 | SS 35/10 kV Sevskaya | 6,3+6,3 | 3.607 | 0 | 0 | 3.607 | 0 | 6.615 | 3.008 | 3.008 | open | 106 | SS 35/10 kV Sevskaya | 6,3+6,3 | 0.2569 | 3.8639 | 0 | 0 | 3.8639 | 0 | 6.615 | 2.7511 | 2.7511 | open
107 | SS 35/6 kc Seshcha | 1,6+4 | 2.1 | 0 | 0 | 2.1 | 0 | 1.68 | -0.42 | -0.42 | closed | 107 | SS 35/6 kc Seshcha | 1,6+4 | 0.0554 | 2.1554 | 0 | 0 | 2.1554 | 0 | 1.68 | -0.4754 | -0.4754 | closed
108 | SS 35/6 kV Star | 10+10 | 2.806 | 0 | 0 | 2.806 | 0 | 10.5 | 7.694 | 7.694 | open | 108 | SS 35/6 kV Star | 10+10 | 0 | 2.806 | 0 | 0 | 2.806 | 0 | 10.5 | 7.694 | 7.694 | open
109 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.578 | 0 | 0 | 0.578 | 0 | 2.625 | 2.047 | 2.047 | open | 109 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.4702 | 1.0482 | 0 | 0 | 1.0482 | 0 | 2.625 | 1.5768 | 1.5768 | open
110 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.493 | 0 | 0 | 0.493 | 0 | 1.68 | 1.187 | 1.187 | open | 110 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.0338 | 0.5268 | 0 | 0 | 0.5268 | 0 | 1.68 | 1.1532 | 1.1532 | open
111 | SS 35/6 kV Fokinskaya | 16+16+16 | 19.71 | 0 | 0 | 19.71 | 0 | 33.6 | 13.89 | 13.89 | open | 111 | SS 35/6 kV Fokinskaya | 16+16+16 | 1.226 | 20.936 | 0 | 0 | 20.936 | 0 | 33.6 | 12.664 | 12.664 | open
112 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | open | 112 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 3.8008 | 12.1008 | 0 | 0 | 12.1008 | 0 | 12.495 | 0.3942 | 0.3942 | open
113 | SS 35/10 kV Khvoshchevskaya | 2,5+2,5 | 1.288 | 0 | 0 | 1.288 | 0 | 2.625 | 1.337 | 1.337 | open | 113 | SS 35/10 kV Khvoshchevskaya | 2,5+2,5 | 0.1628 | 1.4508 | 0 | 0 | 1.4508 | 0 | 2.625 | 1.1742 | 1.1742 | open
114 | SS 35/10 kV Abarinskaya | 4+4 | 0.643 | 0 | 0 | 0.643 | 0 | 4.2 | 3.557 | 3.557 | open | 114 | SS 35/10 kV Abarinskaya | 4+4 | 0.101 | 0.744 | 0 | 0 | 0.744 | 0 | 4.2 | 3.456 | 3.456 | open
115 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 1.023 | 0 | 0 | 1.023 | 0 | 2.625 | 1.602 | 1.602 | open | 115 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 0.0795 | 1.1025 | 0 | 0 | 1.1025 | 0 | 2.625 | 1.5225 | 1.5225 | open
116 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.933 | 0 | 0 | 0.933 | 0 | 1.68 | 0.747 | 0.747 | open | 116 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.046 | 0.979 | 0 | 0 | 0.979 | 0 | 1.68 | 0.701 | 0 | open
117 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.537 | 0 | 0 | 0.537 | 0 | 1.68 | 1.143 | 1.143 | open | 117 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.0303 | 0.5673 | 0 | 0 | 0.5673 | 0 | 1.68 | 1.1127 | 1.1127 | open
118 | SS 35/6 kV Water intake | 2,5+2,5 | 0.242 | 0 | 0 | 0.242 | 0 | 2.625 | 2.383 | 2.383 | open | 118 | SS 35/6 kV Water intake | 2,5+2,5 | 0 | 0.242 | 0 | 0 | 0.242 | 0 | 2.625 | 2.383 | 2.383 | open
119 | SS 35/10 kV Voronok | 2,5+3,2 | 1.517 | 0 | 0 | 1.517 | 0 | 2.625 | 1.108 | 1.108 | open | 119 | SS 35/10 kV Voronok | 2,5+3,2 | 0.0437 | 1.5607 | 0 | 0 | 1.5607 | 0 | 2.625 | 1.0643 | 1.0643 | open
120 | SS 35/10 kV Gordeevka | 4+4 | 2.201 | 0 | 0 | 2.201 | 0 | 4.2 | 1.999 | 1.999 | open | 120 | SS 35/10 kV Gordeevka | 4+4 | 0.12 | 2.321 | 0 | 0 | 2.321 | 0 | 4.2 | 1.879 | 1.879 | open
121 | SS 35/10 kV Gridenki | 2,5+3,2 | 1.167 | 0 | 0 | 1.167 | 0 | 2.625 | 1.458 | 1.458 | open | 121 | SS 35/10 kV Gridenki | 2,5+3,2 | 0.1144 | 1.2814 | 0 | 0 | 1.2814 | 0 | 2.625 | 1.3436 | 1.3436 | open
122 | SS 35/10 kV Zavodskaya | 4+2,5 | 1.428 | 0 | 0 | 1.428 | 0 | 2.625 | 1.197 | 1.197 | open | 122 | SS 35/10 kV Zavodskaya | 4+2,5 | 0.0048 | 1.4328 | 0 | 0 | 1.4328 | 0 | 2.625 | 1.1922 | 1.1922 | open
123 | SS 35/10 kV Istopki | 1,6+1,6 | 1.251 | 0 | 0 | 1.251 | 0 | 1.68 | 0.429 | 0.429 | open | 123 | SS 35/10 kV Istopki | 1,6+1,6 | 0.0049 | 1.2559 | 0 | 0 | 1.2559 | 0 | 1.68 | 0.4241 | 0.4241 | open
124 | SS 35/10 kV Katashin | 1,6+1,6 | 1.017 | 0 | 0 | 1.017 | 0 | 1.68 | 0.663 | 0.663 | open | 124 | SS 35/10 kV Katashin | 1,6+1,6 | 0.0261 | 1.0431 | 0 | 0 | 1.0431 | 0 | 1.68 | 0.6369 | 0.6369 | open
125 | SS 35/10 kV Kivay | 2,5+2,5 | 1.33 | 0 | 0 | 1.33 | 0 | 2.625 | 1.295 | 1.295 | open | 125 | SS 35/10 kV Kivay | 2,5+2,5 | 0.0701 | 1.4001 | 0 | 0 | 1.4001 | 0 | 2.625 | 1.2249 | 1.2249 | open
126 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.806 | 0 | 0 | 0.806 | 0 | 1.68 | 0.874 | 0.874 | open | 126 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.0039 | 0.8099 | 0 | 0 | 0.8099 | 0 | 1.68 | 0.8701 | 0.8701 | open
127 | SS 35/10 kV Logovatoe | 2,5+1,6 | 0.939 | 0 | 0 | 0.939 | 0 | 1.68 | 0.741 | 0.741 | open | 127 | SS 35/10 kV Logovatoe | 2,5+1,6 | 0.0107 | 0.9497 | 0 | 0 | 0.9497 | 0 | 1.68 | 0.7303 | 0.7303 | open
128 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.268 | 0 | 0 | 0.268 | 0 | 2.625 | 2.357 | 2.357 | open | 128 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.025 | 0.293 | 0 | 0 | 0.293 | 0 | 2.625 | 2.332 | 2.332 | open
129 | SS 35/10 kV Mglinskaya | 4+4 | 3.559 | 0 | 0 | 3.559 | 0 | 4.2 | 0.641 | 0.641 | open | 129 | SS 35/10 kV Mglinskaya | 4+4 | 0.019 | 3.578 | 0 | 0 | 3.578 | 0 | 4.2 | 0.622 | 0.622 | open
130 | SS 35/10 kV Mishkovka | 2,5+1,6 | 0.531 | 0 | 0 | 0.531 | 0 | 1.68 | 1.149 | 1.149 | open | 130 | SS 35/10 kV Mishkovka | 2,5+1,6 | 0.0247 | 0.5557 | 0 | 0 | 0.5557 | 0 | 1.68 | 1.1243 | 1.1243 | open
131 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.563 | 0 | 0 | 0.563 | 0 | 2.625 | 2.062 | 2.062 | open | 131 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.008 | 0.571 | 0 | 0 | 0.571 | 0 | 2.625 | 2.054 | 2.054 | open
132 | SS 35/10 kV Putevaya | 6,3+6,3 | 5.093 | 0 | 0 | 5.093 | 0 | 6.615 | 1.522 | 1.522 | open | 132 | SS 35/10 kV Putevaya | 6,3+6,3 | 0.072 | 5.165 | 0 | 0 | 5.165 | 0 | 6.615 | 1.45 | 1.45 | open
133 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 0.797 | 0 | 0 | 0.797 | 0 | 2.625 | 1.828 | 1.828 | open | 133 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 0.1019 | 0.8989 | 0 | 0 | 0.8989 | 0 | 2.625 | 1.7261 | 1.7261 | open
134 | SS 35/10 kV Slava | 2,5+1,6 | 1.271 | 0 | 0 | 1.271 | 0 | 1.68 | 0.409 | 0.409 | open | 134 | SS 35/10 kV Slava | 2,5+1,6 | 0.0544 | 1.3254 | 0 | 0 | 1.3254 | 0 | 1.68 | 0.3546 | 0.3546 | open
135 | SS 35/10 kV Smolevichi | 6,3+6,3 | 2.692 | 0 | 0 | 2.692 | 0 | 6.615 | 3.923 | 3.923 | open | 135 | SS 35/10 kV Smolevichi | 6,3+6,3 | 0.2757 | 2.9677 | 0 | 0 | 2.9677 | 0 | 6.615 | 3.6473 | 3.6473 | open
136 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.387 | 0 | 0 | 0.387 | 0 | 1.68 | 1.293 | 1.293 | open | 136 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.005 | 0.392 | 0 | 0 | 0.392 | 0 | 1.68 | 1.288 | 1.288 | open
137 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open | 137 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.0137 | 0.4137 | 0 | 0 | 0.4137 | 0 | 2.625 | 2.2113 | 2.2113 | open
138 | SS 35/6 kV Tembr | 4+4+3,2 | 6.43 | 0 | 0 | 6.43 | 0 | 7.56 | 1.13 | 1.13 | open | 138 | SS 35/6 kV Tembr | 4+4+3,2 | 0.1094 | 6.5394 | 0 | 0 | 6.5394 | 0 | 7.56 | 1.0206 | 1.0206 | open
139 | SS 35/10 kV Churovichi | 2,5+4 | 0.726 | 0 | 0 | 0.726 | 0 | 2.625 | 1.899 | 1.899 | open | 139 | SS 35/10 kV Churovichi | 2,5+4 | 0.0822 | 0.8082 | 0 | 0 | 0.8082 | 0 | 2.625 | 1.8168 | 1.8168 | open
140 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 0.999 | 0 | 0 | 0.999 | 0 | 2.625 | 1.626 | 1.626 | open | 140 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 0.0659 | 1.0649 | 0 | 0 | 1.0649 | 0 | 2.625 | 1.5601 | 1.5601 | open
| Total: | 2302.5 | 756.754 | [8 empty] | 2: Total:; 3: 2302.5; 4: 62.0972; 5: 818.8512
| deficit | [8 empty] | -38.503 |  | 2: deficit; Min 12: -51.8409
| proficit | [8 empty] | 416.533 |  | 2: proficit; Min 12: 408.7198

## Свод тек.деф.зима
The list of closed supply centers of IDGC of Centre (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA | [5 empty] | Current deficit, MVA
Bryanskenergo
1 | SS 110/6 kV Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32
2 | SS 110/6 kV Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 час | 24.06 | 0 | 16.8 | -7.26
3 | SS 110/10 kV Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138
4 | SS 110/35/6 kV Dormashevskaya | 40+63 | 44.04 | 0 | 0 | 44.04 | 0 | 42 | -2.35
| Nom. capacity MV, MVA | 40+63 | 22.42 | 0 | 0 | 22.42 | 0 | 42
| Nom. capacity LV, MVA | 40+63 | 21.62 | 0 | 0 | 21.62 | 0 | 42
5 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 36.72 | 8.9 | 12 час | 27.82 | 0 | 26.25 | -3
| Nom. capacity MV, MVA | 25+25 | 8.85 | 8.9 | 12 час | -0.05 | 0 | 26.25
| Nom. capacity LV, MVA | 25+25 | 27.87 | 0 | 0 | 27.87 | 0 | 26.25
6 | SS 110/6 kV Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78
7 | SS 110/6 kV Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63
8 | SS 35/6 kV Volodarskaya | 10+6,3 | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.735
9 | SS 35/6 kV Gorodskaya | 10+10 | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -1.87
10 | SS 35/6 kc Seshcha | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.42
Total current deficit (winter) |  | 363.2 | [6 empty] | -38.503

## Свод.ожид.тек.зима
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Bryanskenergo
1 | SS 110/6 kV Bezhitskaya | 25+40 | 3.182 | #REF! | 0 | 0 | #REF! | 0 | 26.25 | #REF! | -12.131 | closed
2 | SS 110/6 kV Gorodishchenskaya | 16+16 | 0.806 | #REF! | 1.5 | 12 час | #REF! | 0 | 16.8 | #REF! | -8.308 | closed
3 | SS 110/10 kV Dobrunskaya | 6,3+4 | 0.524 | #REF! | 0 | 0 | #REF! | 0 | 4.2 | #REF! | -2.0065 | closed
4 | SS 110/35/6 kV Dormashevskaya | 40+63 | 3.226 | 42.736 | 0 | 0 | 42.736 | 0 | 42 | -0.736 | -5.8265 | closed
| Nom. capacity MV, MVA | 40+63 |  | #REF! | 0 | 0 | #REF! | 0 | 42 | #REF!
| Nom. capacity LV, MVA | 40+63 | 3.226 | #REF! | 0 | 0 | #REF! | 0 | 42 | #REF!
5 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 0 | 36.72 | 8.9 | 12 час | 27.82 | 0 | 26.25 | -1.57 | -3.013 | closed
| Nom. capacity MV, MVA | 25+25 |  | #REF! | 8.9 | 12 час | #REF! | 0 | 26.25 | #REF!
| Nom. capacity LV, MVA | 25+25 |  | #REF! | 0 | 0 | #REF! | 0 | 26.25 | #REF!
6 | SS 110/6 kV Karachizhskaya | 10+10 | 0.457 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -10.533 | closed
7 | SS 110/6 kV Zapadnaya | 10+10 | 1.472 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -0.075 | closed
8 | SS 110/6 kV Yuzhnaya | 16+25 | 0.238 | #REF! | 0 | 0 | #REF! | 0 | 16.8 | #REF! | -2.868 | closed
9 | SS 35/6 kV Volodarskaya | 10+6,3 | 0 | #REF! | 0 | 0 | #REF! | 0 | 6.615 | #REF! | -4.735 | closed
10 | SS 35/6 kV Gorodskaya | 10+10 | 0 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -1.87 | closed
11 | SS 35/6 kc Seshcha | 1,6+4 | 0.037 | #REF! | 0 | 0 | #REF! | 0 | 1.68 | #REF! | -0.475 | closed
| Total: | 383.2 | [8 empty] | -51.841