## Тамбовэнерго
[9 empty] | Table 1 | [11 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS of 110 kV | [11 empty] | 1: SS of 110 kV
1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 21.45 |  |  | 21.45 | 0 | 26.25 | 4.8 | 4.8 | open | 1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 0 | 21.45 |  |  | 21.45 | 0 | 26.25 | 4.8 | 4.8 | open
2 | SS 110/6 Tambovskaya No.3 | 2*25 | 14.6 |  |  | 14.6 | 0 | 26.25 | 11.65 | 11.65 | open | 2 | SS 110/6 Tambovskaya No.3 | 2*25 | 0 | 14.6 |  |  | 14.6 | 0 | 26.25 | 11.65 | 11.65 | open
3 | SS 110/6 Tambovskaya No.5 | 2*25 | 14.71 |  |  | 14.71 | 0 | 26.25 | 11.54 | 11.54 | open | 3 | SS 110/6 Tambovskaya No.5 | 2*25 | 0 | 14.71 |  |  | 14.71 | 0 | 26.25 | 11.54 | 11.54 | open
4 | SS 110/6 Tambovskaya No.7 | 2*25 | 16.7 |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | open | 4 | SS 110/6 Tambovskaya No.7 | 2*25 | 0 | 16.7 |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | open
5 | SS 110/35/6 Pigment | 2*63 | 32.2 | 27.68 | 80 | 4.52 | 0 | 66.15 | 61.63 | 61.63 | open | 5 | SS 110/35/6 Pigment | 2*63 | 0 | 32.2 | 27.68 | 80 | 4.52 | 0 | 66.15 | 61.63 | 61.63 | open
6 | SS 110/6 Tambovskaya No.8 | 40+16 | 9.33 |  |  | 9.33 | 0 | 16.8 | 7.47 | 7.47 | open | 6 | SS 110/6 Tambovskaya No.8 | 2*40 | 8.71 | 18.04 |  |  | 18.04 | 0 | 42 | 23.96 | 23.96 | open | Scheduled reconstruction works (replacement of a transformer capacity of 16 MVA to 40 MVA)
7 | SS 110/35/6 Malinovskaya | 2*40 | 16.9 | 4.75 | 120 | 12.15 | 0 | 42 | 29.85 | 29.85 | open | 7 | SS 110/35/6 Malinovskaya | 2*40 | 0 | 16.9 | 4.75 | 120 | 12.15 | 0 | 42 | 29.85 | 29.85 | open
8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 8.84 | 1.25 | 120 | 7.59 | 0 | 10.5 | 2.91 | 2.91 | open | 8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 1.86 | 10.7 | 1.25 | 120 | 9.45 | 0 | 10.5 | 1.05 | 1.05 | open
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5.28 | 1.62 | 120 | 3.66 | 0 | 6.615 | 2.955 | 2.955 | open | 9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 0.08 | 5.36 | 7.18 | 120 | -1.82 | 0 | 6.615 | 8.435 | 8.435 | open
10 | SS 110/35/10 Komsomolskaya | 2*10 | 7.87 | 4 | 80 | 3.87 | 0 | 10.5 | 6.63 | 6.63 | open | 10 | SS 110/35/10 Komsomolskaya | 2*10 | 0 | 7.87 | 4 | 80 | 3.87 | 0 | 10.5 | 6.63 | 6.63 | open
11 | SS 110/10 М.Talinskaya | 10 | 0.62 | 0.52 | 1 day and night | 0.1 | 0 | 10.5 | 10.4 | 10.4 | open | 11 | SS 110/10 М.Talinskaya | 10 | 0 | 0.62 | 0.52 | 1 day and night | 0.1 | 0 | 10.5 | 10.4 | 10.4 | open
12 | SS 110/35/10 Promyshlennaya | 2*40 | 19.62 | 10.2 | 120 | 9.42 | 0 | 42 | 32.58 | 32.58 | open | 12 | SS 110/35/10 Promyshlennaya | 2*40 | 1.63 | 21.25 | 10.2 | 120 | 11.05 | 0 | 42 | 30.95 | 30.95 | open
13 | SS 110/35/10 Arzhenskaya | 2*10 | 4.23 | 3.92 | 80 | 0.31 | 0 | 10.5 | 10.19 | 10.19 | open | 13 | SS 110/35/10 Arzhenskaya | 2*10 | 0 | 4.23 | 3.92 | 80 | 0.31 | 0 | 10.5 | 10.19 | 10.19 | open
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | open | 14 | SS 110/10 Teleshovskaya | 2*2,5 | 0 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | open
15 | SS 110/6 Oktyabrskaya | 2*25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 | 22.35 | open | 15 | SS 110/6 Oktyabrskaya | 2*25 | 0 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 | 22.35 | open
16 | SS 110/10 Spasskaya | 2*6,3 | 2.31 |  |  | 2.31 | 0 | 6.615 | 4.305 | 4.305 | open | 16 | SS 110/10 Spasskaya | 2*6,3 | 2.8 | 5.11 |  |  | 5.11 | 0 | 6.615 | 1.505 | 1.505 | open
17 | SS 110/35/10 Kuzminskaya | 2*10 | 6.41 | 5.02 | 45 | 1.39 | 0 | 10.5 | 9.11 | 9.11 | open | 17 | SS 110/35/10 Kuzminskaya | 2*10 | 0 | 6.41 | 5.02 | 45 | 1.39 | 0 | 10.5 | 9.11 | 9.11 | open
18 | SS 110/35/10 Sampurskaya | 10+16 | 5.8 | 4.33 | 80 | 1.47 | 0 | 10.5 | 9.03 | 9.03 | open | 18 | SS 110/35/10 Sampurskaya | 10+16 | 2.94 | 8.74 | 4.33 | 80 | 4.41 | 0 | 10.5 | 6.09 | 6.09 | open
19 | SS 110/6 Leather plant | 2*10 | 1.19 |  |  | 1.19 | 0 | 10.5 | 9.31 | 9.31 | open | 19 | SS 110/6 Leather plant | 2*10 | 0 | 1.19 |  |  | 1.19 | 0 | 10.5 | 9.31 | 9.31 | open
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 14.21 | 3.04 | 120 | 11.17 | 0 | 21 | 9.83 | 9.83 | open | 20 | SS 110/35/6 Rasskazovskaya | 25+20 | 0 | 14.21 | 3.04 | 120 | 11.17 | 0 | 21 | 9.83 | 9.83 | open
21 | SS 110/35/10 Volchkovskaya | 2*10 | 2.16 | 0.95 | 120 | 1.21 | 0 | 10.5 | 9.29 | 9.29 | open | 21 | SS 110/35/10 Volchkovskaya | 2*10 | 0 | 2.16 | 0.95 | 120 | 1.21 | 0 | 10.5 | 9.29 | 9.29 | open
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 3.33 | 1.66 | 120 | 1.67 | 0 | 6.615 | 4.945 | 4.945 | open | 22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 0 | 3.33 | 1.66 | 120 | 1.67 | 0 | 6.615 | 4.945 | 4.945 | open
23 | SS 110/35/10 Khmelevskaya | 2*10 | 4.21 | 0.92 | 120 | 3.29 | 0 | 10.5 | 7.21 | 7.21 | open | 23 | SS 110/35/10 Khmelevskaya | 2*10 | 0 | 4.21 | 0.92 | 120 | 3.29 | 0 | 10.5 | 7.21 | 7.21 | open
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.09 | 2.84 | 80 | 2.25 | 0 | 6.615 | 4.365 | 4.365 | open | 24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 0.15 | 5.24 | 2.84 | 80 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | open
25 | SS 110/35/10 Nikiforovskaya | 10+16 | 3.22 | 2.81 | 120 | 0.41 | 0 | 10.5 | 10.09 | 10.09 | open | 25 | SS 110/35/10 Nikiforovskaya | 10+16 | 0 | 3.22 | 2.81 | 120 | 0.41 | 0 | 10.5 | 10.09 | 10.09 | open
26 | SS 110/10 N.Seslavinskaya | 2.5 | 0.37 | 0.47 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open | 26 | SS 110/10 N.Seslavinskaya | 2.5 | 0 | 0.37 | 0.47 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.33 | 0.19 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open | 27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0 | 0.33 | 0.19 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | open | 28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.25 | 0.27 |  |  | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open
29 | SS 110/35/10 Yuzhnaya | 16 | 7.4 | 8.51 | 1 day and night | -1.11 | 0 | 16.8 | 17.91 | 17.91 | open | 29 | SS 110/35/10 Yuzhnaya | 16 | 0 | 7.4 | 8.51 | 1 day and night | -1.11 | 0 | 16.8 | 17.91 | 17.91 | open
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 21.19 | 9.45 | 120 | 11.74 | 0 | 33.075 | 21.335 | 21.335 | open | 30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 0.24 | 21.43 | 9.45 | 120 | 11.98 | 0 | 33.075 | 21.095 | 21.095 | open
31 | SS 110/35/10 Sosnovskaya | 2*16 | 8.08 | 6.6 | 80 | 1.48 | 0 | 16.8 | 15.32 | 15.32 | open | 31 | SS 110/35/10 Sosnovskaya | 2*16 | 0 | 8.08 | 6.6 | 80 | 1.48 | 0 | 16.8 | 15.32 | 15.32 | open
32 | SS 110/35/10 Pichaevskaya | 2*10 | 4.16 | 4.19 | 80 | -0.03 | 0 | 10.5 | 10.53 | 10.53 | open | 32 | SS 110/35/10 Pichaevskaya | 2*10 | 0 | 4.16 | 4.19 | 80 | -0.03 | 0 | 10.5 | 10.53 | 10.53 | open
33 | SS 110/35/10 Algasovskaya | 2*40 | 12.85 | 2.9168 | 120 | 9.9332 | 0 | 42 | 32.0668 | 32.0668 | open | 33 | SS 110/35/10 Algasovskaya | 2*40 | 0 | 12.85 | 2.9168 | 120 | 9.9332 | 0 | 42 | 32.0668 | 32.0668 | open
34 | SS 110/35/6 Morshanskaya | 40+25 | 19.29 | 7.2005 | 120 | 12.0895 | 0 | 26.25 | 14.1605 | 14.1605 | open | 34 | SS 110/35/6 Morshanskaya | 40+25 | 0 | 19.29 | 7.2005 | 120 | 12.0895 | 0 | 26.25 | 14.1605 | 14.1605 | open
35 | SS 110/35/6 Kamvolnaya | 16+25 | 7.86 | 7.2 | 80 | 0.66 | 0 | 16.8 | 16.14 | 16.14 | open | 35 | SS 110/35/6 Kamvolnaya | 16+25 | 0 | 7.86 | 7.2 | 80 | 0.66 | 0 | 16.8 | 16.14 | 16.14 | open
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 2.54 | 0.63 | 120 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | open | 36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 1.79 | 4.33 | 0.63 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | open
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 2.52 | 2.05 | 120 | 0.47 | 0 | 10.5 | 10.03 | 10.03 | open | 37 | SS 110/35/10 Nashchekinskaya | 2*10 | 0 | 2.52 | 2.05 | 120 | 0.47 | 0 | 10.5 | 10.03 | 10.03 | open
38 | SS 110/10 Shachinskaya | 2.5 | 0.06 | 0.054495 | 1 day and night | 0.005505 | 0 | 2.625 | 2.6195 | 2.6195 | open | 38 | SS 110/10 Shachinskaya | 2.5 | 0 | 0.06 | 0.054495 | 1 day and night | 0.005505 | 0 | 2.625 | 2.6195 | 2.6195 | open
39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 8.85 | 9.027 | 45 | -0.17699 | 0 | 16.8 | 16.977 | 16.977 | open | 39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 0 | 8.85 | 9.027 | 45 | -0.17699 | 0 | 16.8 | 16.977 | 16.977 | open
40 | SS 110/35/10 Muchkapskaya | 2*10 | 2.92 | 1.3519 | 120 | 1.5681 | 0 | 10.5 | 8.9319 | 8.9319 | open | 40 | SS 110/35/10 Muchkapskaya | 2*10 | 0 | 2.92 | 1.3519 | 120 | 1.5681 | 0 | 10.5 | 8.9319 | 8.9319 | open
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.58 | 0.66667 | 120 | -0.086667 | 0 | 2.625 | 2.7117 | 2.7117 | open | 41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.71 | 1.29 | 0.66667 | 120 | 0.62333 | 0 | 2.625 | 2.0017 | 2.0017 | open
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.78 | 1.2921 | 120 | 0.48795 | 0 | 10.5 | 10.0121 | 10.0121 | open | 42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 0.71 | 2.49 | 1.2921 | 120 | 1.1979 | 0 | 10.5 | 9.3021 | 9.3021 | open
43 | SS 110/10 Shpikulovskaya | 6,3+2,5 | 0.68 | 0.61404 | 120 | 0.065965 | 0 | 2.625 | 2.559 | 2.559 | open | 43 | SS 110/10 Shpikulovskaya | 6,3+2,5 | 0.21 | 0.89 | 0.61404 | 120 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 | open
44 | SS 110/35/10 Zherdevskaya | 2*16 | 6.27 | 5.6533 | 80 | 0.61675 | 0 | 16.8 | 16.1833 | 16.1833 | open | 44 | SS 110/35/10 Zherdevskaya | 2*16 | 0 | 6.27 | 5.6533 | 80 | 0.61675 | 0 | 16.8 | 16.1833 | 16.1833 | open
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.52 | 0.58824 | 120 | 3.9318 | 0 | 10.5 | 6.5682 | 6.5682 | open | 45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 0.07 | 4.59 | 0.58824 | 120 | 4.0018 | 0 | 10.5 | 6.4982 | 6.4982 | open
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.39 | 0.42105 | 120 | -0.031053 | 0 | 2.625 | 2.6561 | 2.6561 | open | 46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.37 | 0.76 | 0.42105 | 120 | 0.33895 | 0 | 2.625 | 2.2861 | 2.2861 | open
47 | SS 110/35/10 Tokarevskaya | 2*25 | 6.75 | 6.0846 | 120 | 0.66538 | 0 | 26.25 | 25.5846 | 25.5846 | open | 47 | SS 110/35/10 Tokarevskaya | 2*25 | 0 | 6.75 | 6.0846 | 120 | 0.66538 | 0 | 26.25 | 25.5846 | 25.5846 | open
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0.76 | 0.90918 | 120 | -0.14918 | 0 | 6.615 | 6.7642 | 6.7642 | open | 48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0 | 0.76 | 0.90918 | 120 | -0.14918 | 0 | 6.615 | 6.7642 | 6.7642 | open
49 | SS 110/35/10 Mordovskaya | 2*10 | 3.65 | 1.8937 | 120 | 1.7563 | 0 | 10.5 | 8.7437 | 8.7437 | open | 49 | SS 110/35/10 Mordovskaya | 2*10 | 0.47 | 4.12 | 1.8937 | 120 | 2.2263 | 0 | 10.5 | 8.2737 | 8.2737 | open
50 | SS 110/35/10 Pavlovskaya | 10 | 1.14 | 1.56 | 1 day and night | -0.42 | 0 | 10.5 | 10.92 | 10.92 | open | 50 | SS 110/35/10 Pavlovskaya | 10 | 0 | 1.14 | 1.56 | 1 day and night | -0.42 | 0 | 10.5 | 10.92 | 10.92 | open
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 13.92 | 5.989 | 120 | 7.931 | 0 | 26.25 | 18.319 | 18.319 | open | 51 | SS 110/35/10 Kirsanovskaya | 2*25 | 0.18 | 14.1 | 5.989 | 120 | 8.111 | 0 | 26.25 | 18.139 | 18.139 | open
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 7.59 | 2.01 | 120 | 5.58 | 0 | 16.8 | 11.22 | 11.22 | open | 52 | SS 110/35/10 Inzhavinskaya | 2*16 | 6.84 | 14.43 | 2.01 | 120 | 12.42 | 0 | 16.8 | 4.38 | 4.38 | open
53 | SS 110/35/10 Umyotskaya | 2*10 | 1.51 | 4.5 | 80 | -2.99 | 0 | 10.5 | 13.49 | 13.49 | open | 53 | SS 110/35/10 Umyotskaya | 2*10 | 0 | 1.51 | 4.5 | 80 | -2.99 | 0 | 10.5 | 13.49 | 13.49 | open
54 | SS 110/35/10 Kovylskaya | 2*10 | 0.8 | 1.347 | 120 | -0.547 | 0 | 10.5 | 11.047 | 11.047 | open | 54 | SS 110/35/10 Kovylskaya | 2*10 | 0 | 0.8 | 1.347 | 120 | -0.547 | 0 | 10.5 | 11.047 | 11.047 | open
55 | SS 110/10 Inokovskaya | 2.5 | 0.16 | 0.184 | 1 day and night | -0.024 | 0 | 2.625 | 2.649 | 2.649 | open | 55 | SS 110/10 Inokovskaya | 2.5 | 0 | 0.16 | 0.184 | 1 day and night | -0.024 | 0 | 2.625 | 2.649 | 2.649 | open
SS of 35 kV | [11 empty] | 1: SS of 35 kV
56 | SS 35/6 Pervomayskaya | 2*2,5 | 1.87 |  |  | 1.87 | 0 | 2.625 | 0.755 | 0.755 | open | 56 | SS 35/6 Pervomayskaya | 2*2,5 | 0 | 1.87 |  |  | 1.87 | 0 | 2.625 | 0.755 | 0.755 | open
57 | SS 35/10 Picherskaya | 2*2,5 | 0.36 |  |  | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open | 57 | SS 35/10 Picherskaya | 2*2,5 | 0 | 0.36 |  |  | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open
58 | SS 35/10 Osinovskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open | 58 | SS 35/10 Osinovskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open
59 | SS 35/10 Koptevskaya | 2*2,5 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | open | 59 | SS 35/10 Koptevskaya | 2*2,5 | 0 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | open
60 | SS 35/10 Sayukinskaya | 2,5+4 | 0.53 | 0.5 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open | 60 | SS 35/10 Sayukinskaya | 2,5+4 | 0 | 0.53 | 0.5 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open
61 | SS 35/10 Zelyonaya-1 | 2*4 | 1.84 |  |  | 1.84 | 0 | 4.2 | 2.36 | 2.36 | open | 61 | SS 35/10 Zelyonaya-1 | 2*4 | 0 | 1.84 |  |  | 1.84 | 0 | 4.2 | 2.36 | 2.36 | open
62 | SS 35/10 Pyatiletka | 2*4 | 0.28 |  |  | 0.28 | 0 | 4.2 | 3.92 | 3.92 | open | 62 | SS 35/10 Pyatiletka | 2*4 | 0 | 0.28 |  |  | 0.28 | 0 | 4.2 | 3.92 | 3.92 | open
63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.82 |  |  | 0.82 | 0 | 2.625 | 1.805 | 1.805 | open | 63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0 | 0.82 |  |  | 0.82 | 0 | 2.625 | 1.805 | 1.805 | open
64 | SS 35/10 Platonovskaya | 2*6,3 | 2.25 | 0.24 | 120 | 2.01 | 0 | 6.615 | 4.605 | 4.605 | open | 64 | SS 35/10 Platonovskaya | 2*6,3 | 0 | 2.25 | 0.24 | 120 | 2.01 | 0 | 6.615 | 4.605 | 4.605 | open
65 | SS 35/10 Znamenskaya | 2*4 | 2.81 | 1.54 | 120 | 1.27 | 0 | 4.2 | 2.93 | 2.93 | open | 65 | SS 35/10 Znamenskaya | 2*4 | 0.33 | 3.14 | 1.54 | 120 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | open
66 | SS 35/10 Sukhotinskaya | 2.5 | 0.34 | 0 | 1 day and night | 0.34 | 0 | 0 | -0.34 | -0.34 | closed | 66 | SS 35/10 Sukhotinskaya | 2.5 | 0 | 0.34 | 0 | 1 day and night | 0.34 | 0 | 0 | -0.34 | -0.34 | closed
67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.97 |  |  | 0.97 | 0 | 1.68 | 0.71 | 0.71 | open | 67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0 | 0.97 |  |  | 0.97 | 0 | 1.68 | 0.71 | 0.71 | open
68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.48 | 0.29 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0 | 0.48 | 0.29 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open
69 | SS 35/10 Stepnaya | 2*4 | 1.41 | 1.7 | 80 | -0.29 | 0 | 4.2 | 4.49 | 4.49 | open | 69 | SS 35/10 Stepnaya | 2*4 | 0 | 1.41 | 1.7 | 80 | -0.29 | 0 | 4.2 | 4.49 | 4.49 | open
70 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 0.94 | 0.97 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | open | 70 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 0 | 0.94 | 0.97 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | open
71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.32 | 0.47 | 120 | -0.15 | 0 | 1.68 | 1.83 | 1.83 | open | 71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0 | 0.32 | 0.47 | 120 | -0.15 | 0 | 1.68 | 1.83 | 1.83 | open
72 | SS 35/10 Gorelskaya | 4+6,3 | 1.69 | 1.71 | 80 | -0.02 | 0 | 4.2 | 4.22 | 4.22 | open | 72 | SS 35/10 Gorelskaya | 4+6,3 | 0.83 | 2.52 | 1.71 | 80 | 0.81 | 0 | 4.2 | 3.39 | 3.39 | open
73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | open | 73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | open
74 | SS 35/10 Avangardskaya | 2*2,5 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open | 74 | SS 35/10 Avangardskaya | 2*2,5 | 0 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open
75 | SS 35/10 Suravskaya | 1,6+2,5 | 0.62 | 0.45 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | open | 75 | SS 35/10 Suravskaya | 1,6+2,5 | 0 | 0.62 | 0.45 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | open
76 | SS 35/10 Seleznzyovskaya | 3*4 | 3.64 |  |  | 3.64 | 0 | 8.4 | 4.76 | 4.76 | open | 76 | SS 35/10 Seleznzyovskaya | 3*4 | 0 | 3.64 |  |  | 3.64 | 0 | 8.4 | 4.76 | 4.76 | closed
77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.56 | 0.68 | 80 | 0.88 | 0 | 1.68 | 0.8 | 0.8 | open | 77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 0 | 1.56 | 0.68 | 80 | 0.88 | 0 | 1.68 | 0.8 | 0.8 | open
78 | SS 35/10 Viktorskaya | 2.5 | 0.42 |  |  | 0.42 | 0 | 0 | -0.42 | -0.42 | closed | 78 | SS 35/10 Viktorskaya | 2.5 | 0 | 0.42 |  |  | 0.42 | 0 | 0 | -0.42 | -0.42 | closed
79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.69 |  |  | 0.69 | 0 | 1.68 | 0.99 | 0.99 | open | 79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0 | 0.69 |  |  | 0.69 | 0 | 1.68 | 0.99 | 0.99 | open
80 | SS 35/10 Avdeevskaya | 2*2,5 | 0.69 |  |  | 0.69 | 0 | 2.625 | 1.935 | 1.935 | open | 80 | SS 35/10 Avdeevskaya | 2*2,5 | 0 | 0.69 |  |  | 0.69 | 0 | 2.625 | 1.935 | 1.935 | open
81 | SS 35/10 Tatanovskaya | 2*2,5 | 2.6 |  |  | 2.6 | 0 | 2.625 | 0.025 | 0.025 | open | 81 | SS 35/10 Tatanovskaya | 2*2,5 | 0 | 2.6 |  | 120 | 2.6 | 0 | 2.625 | 0.025 | 0.025 | open
82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 2.94 | 0.63 | 60 | 2.31 | 0 | 5.25 | 2.94 | 2.94 | open | 82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 0.1 | 3.04 | 0.63 | 60 | 2.41 | 0 | 5.25 | 2.84 | 2.84 | open
83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 4.18 |  |  | 4.18 | 0 | 6.615 | 2.435 | 2.435 | open | 83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 0 | 4.18 |  |  | 4.18 | 0 | 6.615 | 2.435 | 2.435 | open
84 | SS 35/10 Bokinskaya | 2*6,3 | 1.95 | 0.92 | 30 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | open | 84 | SS 35/10 Bokinskaya | 2*6,3 | 0 | 1.95 | 0.92 | 30 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | open
85 | SS 35/10 Stolovskaya | 4 | 0.55 | 0.52 | 1 day and night | 0.03 | 0 | 4.2 | 4.17 | 4.17 | open | 85 | SS 35/10 Stolovskaya | 4 | 0 | 0.55 | 0.52 | 1 day and night | 0.03 | 0 | 4.2 | 4.17 | 4.17 | open
86 | SS 35/10 Tulinovskaya | 2*2,5 | 1.36 |  |  | 1.36 | 0 | 2.625 | 1.265 | 1.265 | open | 86 | SS 35/10 Tulinovskaya | 2*2,5 | 0 | 1.36 |  |  | 1.36 | 0 | 2.625 | 1.265 | 1.265 | open
87 | SS 35/6 Macaroni factory | 1.6 | 0.08 |  |  | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open | 87 | SS 35/6 Macaroni factory | 1.6 | 0 | 0.08 |  |  | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open
88 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | open | 88 | SS 35/10 Serebryakovskaya | 2*1,6 | 0 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | open
89 | SS 35/10 B.Doroga | 2*1,6 | 0.28 | 0.34 | 60 | -0.06 | 0 | 1.68 | 1.74 | 1.74 | open | 89 | SS 35/10 B.Doroga | 2*1,6 | 0 | 0.28 | 0.34 | 60 | -0.06 | 0 | 1.68 | 1.74 | 1.74 | open
90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.57 |  |  | 0.57 | 0 | 2.625 | 2.055 | 2.055 | open | 90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0 | 0.57 |  |  | 0.57 | 0 | 2.625 | 2.055 | 2.055 | open
91 | SS 35/10 Vishnevskaya | 2*2,5 | 0.48 | 0.26 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | open | 91 | SS 35/10 Vishnevskaya | 2*2,5 | 0 | 0.48 | 0.26 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | open
92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.31 | 0.32 | 50 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.12 | 0.43 | 0.32 | 50 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open
93 | SS 35/10 Glazkovskaya | 2*4 | 0.84 | 0.71 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | open | 93 | SS 35/10 Glazkovskaya | 2*4 | 0 | 0.84 | 0.71 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | open
94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open
95 | SS 35/6 Donskaya | 6,3+10 | 4.07 | 3.65 | 1 day and night | 0.42 | 0 | 6.615 | 6.195 | 6.195 | open | 95 | SS 35/6 Donskaya | 6,3+10 | 0 | 4.07 | 3.65 | 1 day and night | 0.42 | 0 | 6.615 | 6.195 | 6.195 | open
96 | SS 35/10 Druzhba | 2.5 | 0.23 | 0.16 | 1 day and night | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 96 | SS 35/10 Druzhba | 2.5 | 0.08 | 0.31 | 0.16 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open
97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.13 | 0.23 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open | 97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0 | 0.13 | 0.23 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.31 | 0.25 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | open | 98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.06 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open
99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.4 | 1.08 | 80 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | open | 99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 0.06 | 1.46 | 1.08 | 80 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
100 | SS 35/10 KIM | 2,5+4 | 1.24 | 0.74 | 120 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | open | 100 | SS 35/10 KIM | 2,5+4 | 0.06 | 1.3 | 0.74 | 120 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | open
101 | SS 35/10 Klenskaya | 2*2,5 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 101 | SS 35/10 Klenskaya | 2*2,5 | 0 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open
102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.59 | 0.6 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0 | 0.59 | 0.6 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open
103 | SS 35/10 Komintern | 2*2,5 | 0.31 | 0.22 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 103 | SS 35/10 Komintern | 2*2,5 | 0.29 | 0.6 | 0.22 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
104 | SS 35/10 Kochetovskaya | 6.3 | 0.42 | 0.2 | 1 day and night | 0.22 | 0 | 6.615 | 6.395 | 6.395 | open | 104 | SS 35/10 Kochetovskaya | 6.3 | 0 | 0.42 | 0.2 | 1 day and night | 0.22 | 0 | 6.615 | 6.395 | 6.395 | open
105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.3 | 0.14 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0 | 0.3 | 0.14 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 1.08 | 0.66 | 1 day and night | 0.42 | 0 | 2.625 | 2.205 | 2.205 | open | 106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 0 | 1.08 | 0.66 | 1 day and night | 0.42 | 0 | 2.625 | 2.205 | 2.205 | open
107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.38 | 0.28 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | open | 107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0 | 0.38 | 0.28 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | open
108 | SS 35/10 Petrovskaya | 2*4 | 3.23 | 1.2 | 120 | 2.03 | 0 | 4.2 | 2.17 | 2.17 | open | 108 | SS 35/10 Petrovskaya | 2*4 | 0.08 | 3.31 | 1.2 | 120 | 2.11 | 0 | 4.2 | 2.09 | 2.09 | open
109 | SS 35/10 Prigorodnaya | 2*2,5 | 0.7 | 0.62 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | open | 109 | SS 35/10 Prigorodnaya | 2*2,5 | 0 | 0.7 | 0.62 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | open
110 | SS 35/6 Progress | 2*10 | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | open | 110 | SS 35/6 Progress | 2*10 | 0 | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | open
111 | SS 35/10 Raninskaya | 1.6 | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | open | 111 | SS 35/10 Raninskaya | 1.6 | 0 | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | open
112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.4 |  |  | 0.4 | 0 | 1.68 | 1.28 | 1.28 | open | 112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0 | 0.4 |  |  | 0.4 | 0 | 1.68 | 1.28 | 1.28 | open
113 | SS 35/10 Saburovskaya | 2*5,6 | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | open | 113 | SS 35/10 Saburovskaya | 2*5,6 | 0 | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | open
114 | SS 35/10 Sestryonskaya | 1.6 | 0.11 |  |  | 0.11 | 0 | 0 | -0.11 | -0.11 | closed | 114 | SS 35/10 Sestryonskaya | 1.6 | 0 | 0.11 |  |  | 0.11 | 0 | 0 | -0.11 | -0.11 | closed
115 | SS 35/10 Sitovskaya | 1.6 | 0.45 | 0.5 | 1 day and night | -0.05 | 0 | 1.68 | 1.73 | 1.73 | open | 115 | SS 35/10 Sitovskaya | 1.6 | 0 | 0.45 | 0.5 | 1 day and night | -0.05 | 0 | 1.68 | 1.73 | 1.73 | open
116 | SS 35/10 Skobelevskaya | 1.6 | 0.21 | 0.24 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open | 116 | SS 35/10 Skobelevskaya | 1.6 | 0 | 0.21 | 0.24 | 1 day and night | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open
117 | SS 35/10 Ustyinskaya | 2.5 | 1.08 | 1.06 | 1 day and night | 0.02 | 0 | 2.625 | 2.605 | 2.605 | open | 117 | SS 35/10 Ustyinskaya | 2.5 | 0 | 1.08 | 1.06 | 1 day and night | 0.02 | 0 | 2.625 | 2.605 | 2.605 | open
118 | SS 35/10 Yurlovskaya | 2*2,5 | 0.49 |  |  | 0.49 | 0 | 2.625 | 2.135 | 2.135 | open | 118 | SS 35/10 Yurlovskaya | 2*2,5 | 0 | 0.49 |  |  | 0.49 | 0 | 2.625 | 2.135 | 2.135 | open
119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | open | 119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | open
120 | SS 35/10 Agroprom | 2*4 | 1.55 |  |  | 1.55 | 0 | 4.2 | 2.65 | 2.65 | open | 120 | SS 35/10 Agroprom | 2*4 | 0 | 1.55 |  |  | 1.55 | 0 | 4.2 | 2.65 | 2.65 | open
121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.2 |  |  | 0.2 | 0 | 1.68 | 1.48 | 1.48 | open | 121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0 | 0.2 |  |  | 0.2 | 0 | 1.68 | 1.48 | 1.48 | open
122 | SS 35/10 Vanovskaya | 2*2,5 | 0.12 | 0.07 | 80 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | open | 122 | SS 35/10 Vanovskaya | 2*2,5 | 0 | 0.12 | 0.07 | 80 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | open
123 | SS 35/10 Vyazhlinskaya | 1.8 | 0.42 | 0.81 | 1 day and night | -0.39 | 0 | 1.89 | 2.28 | 2.28 | open | 123 | SS 35/10 Vyazhlinskaya | 1.8 | 0 | 0.42 | 0.81 | 1 day and night | -0.39 | 0 | 1.89 | 2.28 | 2.28 | open
124 | SS 35/10 Zarechnaya | 2*2,5 | 0.93 |  |  | 0.93 | 0 | 2.625 | 1.695 | 1.695 | open | 124 | SS 35/10 Zarechnaya | 2*2,5 | 0 | 0.93 |  |  | 0.93 | 0 | 2.625 | 1.695 | 1.695
125 | SS 35/10 Kryukovskaya | 2*2,5 | 0.72 | 0.6593 | 120 | 0.060697 | 0 | 2.625 | 2.5643 | 2.5643 | open | 125 | SS 35/10 Kryukovskaya | 2*2,5 | 0.11 | 0.83 | 0.6593 | 120 | 0.1707 | 0 | 2.625 | 2.4543 | 2.4543 | open
126 | SS 35/6 Korshunovskaya | 2*2,5 | 0.47 |  |  | 0.47 | 0 | 2.625 | 2.155 | 2.155 | open | 126 | SS 35/6 Korshunovskaya | 2*2,5 | 0 | 0.47 |  |  | 0.47 | 0 | 2.625 | 2.155 | 2.155 | open
127 | SS 35/6 Lugovaya | 4 | 0.63 | 0.94977 | 1 day and night | -0.31977 | 0 | 4.2 | 4.5198 | 4.5198 | open | 127 | SS 35/6 Lugovaya | 4 | 0 | 0.63 | 0.94977 | 1 day and night | -0.31977 | 0 | 4.2 | 4.5198 | 4.5198 | open
128 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.25 | 0.1467 | 120 | 0.1033 | 0 | 2.625 | 2.5217 | 2.5217 | open | 128 | SS 35/10 Lyubvinskaya | 2*2,5 | 0 | 0.25 | 0.1467 | 120 | 0.1033 | 0 | 2.625 | 2.5217 | 2.5217 | open
129 | SS 35/10 Morshanskaya | 2*4 | 2.28 |  |  | 2.28 | 0 | 4.2 | 1.92 | 1.92 | open | 129 | SS 35/10 Morshanskaya | 2*4 | 0.22 | 2.5 |  |  | 2.5 | 0 | 4.2 | 1.7 | 1.7 | open
130 | SS 35/10 Piterskaya | 2.5 | 0.84 | 0.93 | 1 day and night | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 130 | SS 35/10 Piterskaya | 2.5 | 0.07 | 0.91 | 0.93 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
131 | SS 35/10 Rakshinskaya | 2*4 | 1.3 | 1.6137 | 80 | -0.31374 | 0 | 4.2 | 4.5137 | 4.5137 | open | 131 | SS 35/10 Rakshinskaya | 2*4 | 0.08 | 1.38 | 1.6137 | 80 | -0.23374 | 0 | 4.2 | 4.4337 | 4.4337 | open
132 | SS 35/10 Rybinskaya | 2*2,5 | 0.69 | 1.0536 | 80 | -0.36357 | 0 | 2.625 | 2.9886 | 2.9886 | open | 132 | SS 35/10 Rybinskaya | 2*2,5 | 0 | 0.69 | 1.0536 | 80 | -0.36357 | 0 | 2.625 | 2.9886 | 2.9886 | open
133 | SS 35/10 Serpovskaya | 2*2,5 | 0.68 | 0.7 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open | 133 | SS 35/10 Serpovskaya | 2*2,5 | 0 | 0.68 | 0.7 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
134 | SS 35/10 St.Tomnikovskaya | 1 | 0.14 | 0.092555 | 1 day and night | 0.047445 | 0 | 1.05 | 1.0026 | 1.0026 | open | 134 | SS 35/10 St.Tomnikovskaya | 1 | 0 | 0.14 | 0.092555 | 1 day and night | 0.047445 | 0 | 1.05 | 1.0026 | 1.0026 | open
135 | SS 35/10 Chernitovskaya | 2.5 | 0.44 | 0.39963 | 1 day and night | 0.04037 | 0 | 2.625 | 2.5846 | 2.5846 | open | 135 | SS 35/10 Chernitovskaya | 2.5 | 0 | 0.44 | 0.39963 | 1 day and night | 0.04037 | 0 | 2.625 | 2.5846 | 2.5846 | open
136 | SS 35/10 Bondarskaya | 2*2,5 | 1.02 | 0.93 | 80 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 136 | SS 35/10 Bondarskaya | 2*2,5 | 0.47 | 1.49 | 0.93 | 80 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | open
137 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.36 | 0.53457 | 80 | -0.17457 | 0 | 1.68 | 1.8546 | 1.8546 | open | 137 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0 | 0.36 | 0.53457 | 80 | -0.17457 | 0 | 1.68 | 1.8546 | 1.8546 | open
138 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.18 | 0.14532 | 120 | 0.03468 | 0 | 1.68 | 1.6453 | 1.6453 | open | 138 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.41 | 0.59 | 0.14532 | 120 | 0.44468 | 0 | 1.68 | 1.2353 | 1.2353 | open
139 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.66 | 0.71276 | 120 | -0.05276 | 0 | 2.625 | 2.6778 | 2.6778 | open | 139 | SS 35/10 Egorovskaya | 2,5+3,2 | 0 | 0.66 | 0.71276 | 120 | -0.05276 | 0 | 2.625 | 2.6778 | 2.6778 | open
140 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.18 |  |  | 0.18 | 0 | 1.68 | 1.5 | 1.5 | open | 140 | SS 35/10 Kershinskaya | 1,6+2,5 | 0 | 0.18 |  |  | 0.18 | 0 | 1.68 | 1.5 | 1.5 | open
141 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.15 | 0.054495 | 120 | 0.095505 | 0 | 1.68 | 1.5845 | 1.5845 | open | 141 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.89 | 1.04 | 0.054495 | 120 | 0.98551 | 0 | 1.68 | 0.69449 | 0.69449 | open
142 | SS 35/10 Lipovskaya | 2.5 | 0.2 | 0.26988 | 1 day and night | -0.06988 | 0 | 2.625 | 2.6949 | 2.6949 | open | 142 | SS 35/10 Lipovskaya | 2.5 | 0 | 0.2 | 0.26988 | 1 day and night | -0.06988 | 0 | 2.625 | 2.6949 | 2.6949 | open
143 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.12 | 0.11 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | open | 143 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0 | 0.12 | 0.11 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | open
144 | SS 35/10 Mitropolskaya | 2.5 | 0.18 | 0.28 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open | 144 | SS 35/10 Mitropolskaya | 2.5 | 0 | 0.18 | 0.28 | 1 day and night | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
145 | SS 35/10 P.Uglovskaya | 1.6 | 0.28 | 0.35292 | 1 day and night | -0.07292 | 0 | 1.68 | 1.7529 | 1.7529 | open | 145 | SS 35/10 P.Uglovskaya | 1.6 | 0 | 0.28 | 0.35292 | 1 day and night | -0.07292 | 0 | 1.68 | 1.7529 | 1.7529 | open
146 | SS 35/10 Rudovskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open | 146 | SS 35/10 Rudovskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open
147 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.32 | 0.23 | 1 day and night | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 147 | SS 35/10 V.Yaroslavskaya | 2.5 | 2 | 2.32 | 0.23 | 1 day and night | 2.09 | 0 | 2.625 | 0.535 | 0.535 | open
148 | SS 35/10 Degtyanskaya | 2.5 | 1.24 | 0.9 | 1 day and night | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open | 148 | SS 35/10 Degtyanskaya | 2.5 | 0 | 1.24 | 0.9 | 1 day and night | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open
149 | SS 35/10 Zelenaya-2 | 1.6 | 0.15 | 0.17992 | 1 day and night | -0.02992 | 0 | 1.68 | 1.7099 | 1.7099 | open | 149 | SS 35/10 Zelenaya-2 | 1.6 | 0 | 0.15 | 0.17992 | 1 day and night | -0.02992 | 0 | 1.68 | 1.7099 | 1.7099 | open
150 | SS 35/10 Kulevatovskaya | 2*4 | 1.76 | 1.81 | 80 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | open | 150 | SS 35/10 Kulevatovskaya | 2*4 | 0 | 1.76 | 1.81 | 80 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | open
151 | SS 35/10 Lamskaya | 4+2,5 | 0.52 | 0.20362 | 120 | 0.31638 | 0 | 2.625 | 2.3086 | 2.3086 | open | 151 | SS 35/10 Lamskaya | 4+2,5 | 2 | 2.52 | 0.20362 | 120 | 2.3164 | 0 | 2.625 | 0.30862 | 0.30862 | open
152 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 152 | SS 35/10 Gryaznovskaya | 2*2,5 | 0 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
153 | SS 35/10 Otyasskaya | 2*2,5 | 0.36 | 0.39963 | 120 | -0.03963 | 0 | 2.625 | 2.6646 | 2.6646 | open | 153 | SS 35/10 Otyasskaya | 2*2,5 | 0 | 0.36 | 0.39963 | 120 | -0.03963 | 0 | 2.625 | 2.6646 | 2.6646 | open
154 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.15 | 0.1903 | 1 day and night | -0.0403 | 0 | 1.68 | 1.7203 | 1.7203 | open | 154 | SS 35/10 P.Vasilyevskaya | 1.6 | 0 | 0.15 | 0.1903 | 1 day and night | -0.0403 | 0 | 1.68 | 1.7203 | 1.7203 | open
155 | SS 35/10 Podlesnaya | 2*2,5 | 0.52 | 0.41935 | 120 | 0.10065 | 0 | 2.625 | 2.5244 | 2.5244 | open | 155 | SS 35/10 Podlesnaya | 2*2,5 | 0 | 0.52 | 0.41935 | 120 | 0.10065 | 0 | 2.625 | 2.5244 | 2.5244 | open
156 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0.43 | 0.38146 | 120 | 0.048535 | 0 | 2.625 | 2.5765 | 2.5765 | open | 156 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0 | 0.43 | 0.38146 | 120 | 0.048535 | 0 | 2.625 | 2.5765 | 2.5765 | open
157 | SS 35/10 Zherdevskaya | 4 | 2.37 | 2.25 | 1 day and night | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open | 157 | SS 35/10 Zherdevskaya | 4 | 0 | 2.37 | 2.25 | 1 day and night | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open
158 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.37 |  |  | 0.37 | 0 | 2.625 | 2.255 | 2.255 | open | 158 | SS 35/10 Sukmanovskaya | 2*2,5 | 0 | 0.37 |  |  | 0.37 | 0 | 2.625 | 2.255 | 2.255 | open
159 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.32 | 0.29 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open | 159 | SS 35/10 Tugolukovskaya | 2,5+4 | 0 | 0.32 | 0.29 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open
160 | SS 35/10 Artemovskaya | 2*2,5 | 0.5 | 0.35 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open | 160 | SS 35/10 Artemovskaya | 2*2,5 | 0 | 0.5 | 0.35 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open
161 | SS 35/10 RSKhO | 2,5+4 | 1.36 | 1.16 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 161 | SS 35/10 RSKhO | 2,5+4 | 0 | 1.36 | 1.16 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open
162 | SS 35/10 Maksimovskaya | 2*1,6 | 0.34 | 0.18 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | open | 162 | SS 35/10 Maksimovskaya | 2*1,6 | 0 | 0.34 | 0.18 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | open
163 | SS 35/10 Burnakskaya | 5,6+6,3 | 2.15 |  |  | 2.15 | 0 | 5.88 | 3.73 | 3.73 | open | 163 | SS 35/10 Burnakskaya | 5,6+6,3 | 0 | 2.15 |  |  | 2.15 | 0 | 5.88 | 3.73 | 3.73 | open
164 | SS 35/10 Poletaevskaya | 2*4 | 0.21 | 0.19 | 120 | 0.02 | 2.18 | 4.2 | 2 | 2 | open | 164 | SS 35/10 Poletaevskaya | 2*4 | 0 | 0.21 | 0.19 | 120 | 0.02 | 2.18 | 4.2 | 2 | 2 | open
165 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.83 |  |  | 0.83 | 0 | 4.2 | 3.37 | 3.37 | open | 165 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0 | 0.83 |  |  | 0.83 | 0 | 4.2 | 3.37 | 3.37 | open
166 | SS 35/10 Pioner | 1,6+2,5 | 1.04 | 0.72 | 60 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 166 | SS 35/10 Pioner | 1,6+2,5 | 0 | 1.04 | 0.72 | 60 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open
167 | SS 35/10 Lvovskaya | 2*2,5 | 0.34 | 0.47 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | open | 167 | SS 35/10 Lvovskaya | 2*2,5 | 0 | 0.34 | 0.47 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | open
168 | SS 35/10 Nadezhdinskaya | 1.6 | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | open | 168 | SS 35/10 Nadezhdinskaya | 1.6 | 0 | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | open
169 | SS 35/10 Kuleshovskaya | 2.5 | 0.36 | 0.26 | 1 day and night | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open | 169 | SS 35/10 Kuleshovskaya | 2.5 | 0 | 0.36 | 0.26 | 1 day and night | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open
170 | SS 35/10 Chernyaevskaya | 4+2,5 | 1.3 |  |  | 1.3 | 0 | 2.625 | 1.325 | 1.325 | open | 170 | SS 35/10 Chernyaevskaya | 4+2,5 | 0 | 1.3 |  |  | 1.3 | 0 | 2.625 | 1.325 | 1.325 | open
171 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open | 171 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open
172 | SS 35/10 Shulginskaya | 2*4 | 0.62 | 0.02 | 120 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | open | 172 | SS 35/10 Shulginskaya | 2*4 | 0 | 0.62 | 0.02 | 120 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | open
173 | SS 35/10 Lavrovskaya | 2*2,5 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | open | 173 | SS 35/10 Lavrovskaya | 2*2,5 | 0 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | open
174 | SS 35/10 N.Sergievskaya | 3.2 | 0.42 | 0.49 | 1 day and night | -0.07 | 0 | 3.36 | 3.43 | 3.43 | open | 174 | SS 35/10 N.Sergievskaya | 3.2 | 0 | 0.42 | 0.49 | 1 day and night | -0.07 | 0 | 3.36 | 3.43 | 3.43 | open
175 | SS 35/10 Kamenskaya | 2*2,5 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open | 175 | SS 35/10 Kamenskaya | 2*2,5 | 0 | 0.46 |  |  | 0.46 | 0 | 2.625 | 2.165 | 2.165 | open
176 | SS 35/10 Protasovskaya | 4+2,5 | 0.35 |  |  | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open | 176 | SS 35/10 Protasovskaya | 4+2,5 | 0 | 0.35 |  |  | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open
177 | SS 35/10 Chakinskaya | 4 | 0.64 |  |  | 0.64 | 0 | 0 | -0.64 | -0.64 | closed | 177 | SS 35/10 Chakinskaya | 4 | 0 | 0.64 |  |  | 0.64 | 0 | 0 | -0.64 | -0.64 | closed
178 | SS 35/10 Lukinskaya | 2.5 | 0.26 | 0.22 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | open | 178 | SS 35/10 Lukinskaya | 2.5 | 0 | 0.26 | 0.22 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | open
179 | SS 35/10 Zolotovskaya | 2.5 | 0.52 | 0.37 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open | 179 | SS 35/10 Zolotovskaya | 2.5 | 0 | 0.52 | 0.37 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open
180 | SS 35/10 Mozdokskaya | 2.5 | 0.28 |  |  | 0.28 | 0 | 0 | -0.28 | -0.28 | closed | 180 | SS 35/10 Mozdokskaya | 2.5 | 0 | 0.28 |  |  | 0.28 | 0 | 0 | -0.28 | -0.28 | closed
181 | SS 35/10 Oblovskaya | 2*2,5 | 0.34 | 0.65 | 120 | -0.31 | 0 | 2.625 | 2.935 | 2.935 | open | 181 | SS 35/10 Oblovskaya | 2*2,5 | 0 | 0.34 | 0.65 | 120 | -0.31 | 0 | 2.625 | 2.935 | 2.935 | open
182 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.42 | 0.07 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open | 182 | SS 35/10 V.Vershinskaya | 2,5+4 | 0 | 0.42 | 0.07 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open
183 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | open | 183 | SS 35/10 Luchevskaya | 2,5+1,6 | 0 | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | open
184 | SS 35/10 Olshanskaya | 4+2,5 | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | open | 184 | SS 35/10 Olshanskaya | 4+2,5 | 0 | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | open
185 | SS 35/10 Pavlodarskaya | 2.5 | 0.08 | 0.1 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open | 185 | SS 35/10 Pavlodarskaya | 2.5 | 0 | 0.08 | 0.1 | 1 day and night | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
186 | SS 35/10 Berezovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | open | 186 | SS 35/10 Berezovskaya | 2*2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | open
187 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.37 | 0.29 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open | 187 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0 | 0.37 | 0.29 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open
188 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | open | 188 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | open
189 | SS 35/10 Shapkinskaya | 2*4 | 0.52 |  |  | 0.52 | 0 | 4.2 | 3.68 | 3.68 | open | 189 | SS 35/10 Shapkinskaya | 2*4 | 0 | 0.52 |  |  | 0.52 | 0 | 4.2 | 3.68 | 3.68 | open
190 | SS 35/10 Maryinskaya | 2*1,6 | 0.16 | 0.25 | 120 | -0.09 | 0 | 1.68 | 1.77 | 1.77 | open | 190 | SS 35/10 Maryinskaya | 2*1,6 | 0 | 0.16 | 0.25 | 120 | -0.09 | 0 | 1.68 | 1.77 | 1.77 | open
191 | SS 35/10 Irskaya | 1,6+2,5 | 0.17 | 0.345 | 120 | -0.175 | 0 | 1.68 | 1.855 | 1.855 | open | 191 | SS 35/10 Irskaya | 1,6+2,5 | 0 | 0.17 | 0.345 | 120 | -0.175 | 0 | 1.68 | 1.855 | 1.855 | open
192 | SS 35/10 Zavodskaya | 2*4 | 1.22 | 1.25 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | open | 192 | SS 35/10 Zavodskaya | 2*4 | 0 | 1.22 | 1.25 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | open
193 | SS 35/10 Kalaisskaya | 2.5 | 0.47 | 0.58 | 1 day and night | -0.11 | 0 | 2.625 | 2.735 | 2.735 | open | 193 | SS 35/10 Kalaisskaya | 2.5 | 0 | 0.47 | 0.58 | 1 day and night | -0.11 | 0 | 2.625 | 2.735 | 2.735 | open
194 | SS 35/10 Sokolovskaya | 2*2,5 | 0.92 | 1.02 | 80 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open | 194 | SS 35/10 Sokolovskaya | 2*2,5 | 0 | 0.92 | 1.02 | 80 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
195 | SS 35/10 Veterinarnaya | 2.5 | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | open | 195 | SS 35/10 Veterinarnaya | 2.5 | 0 | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | open
196 | SS 35/10 Glukhovskaya | 2.5 | 0.23 | 0.09 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open | 196 | SS 35/10 Glukhovskaya | 2.5 | 0 | 0.23 | 0.09 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open
197 | SS 35/10 Orzhevskaya | 2.5 | 0.4 | 0.47 | 1 day and night | -0.07 | 0 | 2.625 | 2.695 | 2.695 | open | 197 | SS 35/10 Orzhevskaya | 2.5 | 0 | 0.4 | 0.47 | 1 day and night | -0.07 | 0 | 2.625 | 2.695 | 2.695 | open
198 | SS 35/10 Umyotskaya | 2*4 | 1.34 | 1.54 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | open | 198 | SS 35/10 Umyotskaya | 2*4 | 0 | 1.34 | 1.54 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | open
199 | SS 35/10 Gavrilovskaya | 2*4 | 1.42 | 0.996 | 120 | 0.424 | 0 | 4.2 | 3.776 | 3.776 | open | 199 | SS 35/10 Gavrilovskaya | 2*4 | 0 | 1.42 | 0.996 | 120 | 0.424 | 0 | 4.2 | 3.776 | 3.776 | open
200 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.66 | 0.76 | 80 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open | 200 | SS 35/10 Peresypkinskaya | 2*2,5 | 0 | 0.66 | 0.76 | 80 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
201 | SS 35/10 Annenskaya | 2*2,5 | 1.29 | 0.806 | 80 | 0.484 | 0 | 2.625 | 2.141 | 2.141 | open | 201 | SS 35/10 Annenskaya | 2*2,5 | 0.11 | 1.4 | 0.806 | 80 | 0.594 | 0 | 2.625 | 2.031 | 2.031 | open
202 | SS 35/10 Filatovskaya | 2*2,5 | 0.44 | 0.33 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open | 202 | SS 35/10 Filatovskaya | 2*2,5 | 0 | 0.44 | 0.33 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open
203 | SS 35/10 Nikitinskaya | 2,5+1,6 | 0.73 | 0.135 | 120 | 0.595 | 0 | 1.68 | 1.085 | 1.085 | open | 203 | SS 35/10 Nikitinskaya | 2*4 | 3.6 | 4.33 | 0.135 | 120 | 4.195 | 0 | 4.2 | 0.005 | 0.005 | open
204 | SS 35/10 Balykleyskaya | 2*2,5 | 0.96 | 0.414 | 120 | 0.546 | 0 | 2.625 | 2.079 | 2.079 | open | 204 | SS 35/10 Balykleyskaya | 2*2,5 | 0 | 0.96 | 0.414 | 120 | 0.546 | 0 | 2.625 | 2.079 | 2.079 | open
205 | SS 35/10 Karavainskaya | 2*1,6 | 0.43 | 0.548 | 80 | -0.118 | 0 | 1.68 | 1.798 | 1.798 | open | 205 | SS 35/10 Karavainskaya | 2*1,6 | 0 | 0.43 | 0.548 | 80 | -0.118 | 0 | 1.68 | 1.798 | 1.798 | open
206 | SS 35/10 Poultry plant | 2*2,5 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open | 206 | SS 35/10 Poultry plant | 2*2,5 | 0 | 0.26 |  |  | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open
207 | SS 35/10 Pavlovskaya | 3.2 | 0.26 | 0.28 | 1 day and night | -0.02 | 0 | 3.36 | 3.38 | 3.38 | open | 207 | SS 35/10 Pavlovskaya | 3.2 | 0 | 0.26 | 0.28 | 1 day and night | -0.02 | 0 | 3.36 | 3.38 | 3.38 | open
| Total: | 2452 | 498.87 | [8 empty] | 2: Total:; 3: 2479.9; 4: 0; 5: 540.85
| deficit | [8 empty] | -1.79 |  | 2: deficit; 4: 0; Min 12: -1.79
| proficit | [8 empty] | 1000.337 |  | 2: proficit; 4: 0; Min 12: 991.637

## Св. тек. дефицит март 2011
The list of closed supply centers of IDGC of Centre - Tambovenergo division based on winter load measurements as of March 1, 2011 (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA
Tambovenergo
1 | SS 35/10 Sukhotinskaya | 2.5 | -0.34
2 | SS 35/10 Viktorskaya | 2.5 | -0.42
3 | SS 35/10 Sestryonskaya | 1.6 | -0.11
4 | SS 35/10 Chakinskaya | 4 | -0.64
5 | SS 35/10 Mozdokskaya | 2.5 | -0.28
Total current deficit (1.03.11) |  |  | -1.79

## Св. ожид. дефицит март 2011
The list of closed supply centers of IDGC of Centre - Tambovenergo division with expected load taking into account new connections and other development of the electical networks as of March 1, 2011 (expected deficit of capacity).
No. | Name of supply center, voltage class |  | Expected deficit, MVA
Tambovenergo
1 | ПС 35/10 Сухотинская | 2.5 | -0.34
2 | ПС 35/10 Викторская | 2.5 | -0.42
3 | ПС 35/10 Сестрёнская | 1.6 | -0.11
4 | ПС 35/10 Чакинская | 4 | -0.64
5 | ПС 35/10 Моздокская | 2.5 | -0.28
Total expected deficit (01.03.11) |  |  | -1.79