## Липецк
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [12 empty] | MVA | Min
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [12 empty] | 1: One-transformer substations
1 | SS 110/10 kV Lev Tolstoy | 10 |  | 3 | 1.6 | 30 | 1.4 | 0 | 1.6 | -1.4 | -1.4 | closed | 1 | SS 110/10 kV Lev Tolstoy | 10 | 0.053 | 3.053 | 1.6 | 30 | 1.453 | 0 | 1.6 | -1.453 | -1.453 | closed
2 | SS 110/10 kV Dvurechki | 6.3 |  | 2.16 | 0.1 | 70 | 2.06 | 0 | 0.1 | -2.06 | -2.06 | closed | 2 | SS 110/10 kV Dvurechki | 6.3 | 0.218 | 2.378 | 0.1 | 70 | 2.278 | 0 | 0.1 | -2.278 | -2.278 | closed
3 | SS 110/10 kV Manezhnaya | 40 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | closed | 3 | SS 110/10 kV Manezhnaya | 40 | 37.457 | 37.457 | 0 | 0 | 37.457 | 0 | 0 | -37.457 | -37.457 | closed
4 | SS 35/10 kV Vesyoloe | 2.5 |  | 0.07 | 0.8 | 100 | -0.73 | 0 | 0.8 | 0.73 | 0.73 | open | 4 | SS 35/10 kV Vesyoloe | 2.5 | 0.015 | 0.085 | 0.8 | 100 | -0.715 | 0 | 0.8 | 0.715 | 0.715 | open
5 | SS 35/10 kV Kr.Palna | 3.2 |  | 0.72 | 1.2 | 70 | -0.48 | 0 | 1.2 | 0.48 | 0.48 | open | 5 | SS 35/10 kV Kr.Palna | 3.2 | 0.02 | 0.74 | 1.2 | 70 | -0.46 | 0 | 1.2 | 0.46 | 0.46 | open
6 | SS 35/10 kV Kamenka | 2.5 |  | 0.78 | 1.5 | 60 | -0.72 | 0 | 1.5 | 0.72 | 0.72 | open | 6 | SS 35/10 kV Kamenka | 2.5 | 0.188 | 0.968 | 1.5 | 60 | -0.532 | 0 | 1.5 | 0.532 | 0.532 | open
7 | SS 35/10 kV Krasotynovka | 2.5 |  | 0.33 | 1.5 | 50 | -1.17 | 0 | 1.5 | 1.17 | 1.17 | open | 7 | SS 35/10 kV Krasotynovka | 2.5 | 0.005 | 0.335 | 1.5 | 50 | -1.165 | 0 | 1.5 | 1.165 | 1.165 | open
8 | SS 35/10 kV Ozyorki | 2.5 |  | 0.09 | 0 | 0 | 0.09 | 0 | 0 | -0.09 | -0.09 | closed | 8 | SS 35/10 kV Ozyorki | 2.5 |  | 0.09 | 0 | 0 | 0.09 | 0 | 0 | -0.09 | -0.09 | closed
9 | SS 35/10 kV Pankratovka | 2.5 |  | 0.55 | 1.2 | 90 | -0.65 | 0 | 1.2 | 0.65 | 0.65 | open | 9 | SS 35/10 kV Pankratovka | 2.5 |  | 0.55 | 1.2 | 90 | -0.65 | 0 | 1.2 | 0.65 | 0.65 | open
10 | SS 35/10 kV Preobrazhenye | 2.5 |  | 0.39 | 0 | 0 | 0.39 | 0 | 0 | -0.39 | -0.39 | closed | 10 | SS 35/10 kV Preobrazhenye | 2.5 | 0.03 | 0.42 | 0 | 0 | 0.42 | 0 | 0 | -0.42 | -0.42 | closed
11 | SS 35/10 kV Yakovlevo | 2.5 |  | 0.83 | 0 | 0 | 0.83 | 0 | 0 | -0.83 | -0.83 | closed | 11 | SS 35/10 kV Yakovlevo | 2.5 | 0.511 | 1.341 | 0 | 0 | 1.341 | 0 | 0 | -1.341 | -1.341 | closed
12 | SS 110/10 kV Terbunsky gonchar | 25 |  | без нагрузки | [8 empty] | 1: 12; 2: SS 110/10 kV Terbunsky gonchar; 3: 25; 4: 9.95; 5: 9.95
13 | SS 35/10 kV Pervomayskaya | 2.5 |  | 0.82 | 0.3 | 60 | 0.52 | 0 | 0.3 | -0.52 | -0.52 | closed | 13 | SS 35/10 kV Pervomayskaya | 2.5 | 0.008 | 0.828 | 0.3 | 60 | 0.528 | 0 | 0.3 | -0.528 | -0.528 | closed
14 | SS 35/10 kV Kamennaya Lubna | 2.5 |  | 0.93 | 0.9 | 90 | 0.03 | 0 | 0.9 | -0.03 | -0.03 | closed | 14 | SS 35/10 kV Kamennaya Lubna | 2.5 | 0.06 | 0.99 | 0.9 | 90 | 0.09 | 0 | 0.9 | -0.09 | -0.09 | closed
15 | SS 35/10 kV Znamenka | 2.5 |  | 0.71 | 0.4 | 8 hours | 0.31 | 0 | 0.4 | -0.31 | -0.31 | closed | 15 | SS 35/10 kV Znamenka | 2.5 |  | 0.71 | 0.4 | 8 hours | 0.31 | 0 | 0.4 | -0.31 | -0.31 | closed
16 | SS 35/10 kV Pikovo | 2.5 |  | 0.5 | 0.5 | 60 | 0 | 0 | 0.5 | 0 | 0 | closed | 16 | SS 35/10 kV Pikovo | 2.5 | 0.008 | 0.508 | 0.5 | 60 | 0.008 | 0 | 0.5 | -0.008 | -0.008 | closed
17 | SS 35/10 kV Nikolskoe | 4 |  | 0.27 | 0.8 | 150 | -0.53 | 0 | 0.8 | 0.53 | 0.53 | open | 17 | SS 35/10 kV Nikolskoe | 4 | 0.02 | 0.29 | 0.8 | 150 | -0.51 | 0 | 0.8 | 0.51 | 0.51 | open
18 | SS 35/10 kV Peskovatka | 1.6 |  | 0.49893 | 0.24 | 70 | 0.25893 | 0 | 0.24 | -0.25893 | -0.25893 | closed | 18 | SS 35/10 kV Peskovatka | 1.6 |  | 0.49893 | 0.24 | 70 | 0.25893 | 0 | 0.24 | -0.25893 | -0.25893 | closed
19 | SS 35/6 kV Druzhba | 5.6 |  | КРУНН-6кВ не наши | [7 empty] | open | 1: 19; 2: SS 35/6 kV Druzhba; 3: 5.6; 5: 0
20 | SS 35/10 kV SOM | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | closed | 20 | SS 35/10 kV SOM | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | closed
21 | SS 35/6 kV Novonikolaevka | 4 |  | 0.32178 | 0 | 0 | 0.32178 | 0 | 0 | -0.32178 | -0.32178 | closed | 21 | SS 35/6 kV Novonikolaevka | 4 |  | 0.32178 | 0 | 0 | 0.32178 | 0 | 0 | -0.32178 | -0.32178 | closed
22 | SS 35/10 kV Sindyakino | 2.5 |  | 0.14809 | 0.4 | 90 | -0.25191 | 0 | 0.4 | 0.25191 | 0.25191 | open | 22 | SS 35/10 kV Sindyakino | 2.5 |  | 0.14809 | 0.4 | 90 | -0.25191 | 0 | 0.4 | 0.25191 | 0.25191 | open
23 | SS 35/10 kV Kurino | 2.5 |  | 0.47679 | 0 | 0 | 0.47679 | 0 | 0 | -0.47679 | -0.47679 | closed | 23 | SS 35/10 kV Kurino | 2.5 | 0.096 | 0.57279 | 0 | 0 | 0.57279 | 0 | 0 | -0.57279 | -0.57279 | closed
24 | SS 35/10 kV Novodubovoe | 2.5 |  | 0.90825 | 0 | 0 | 0.90825 | 0 | 0 | -0.90825 | -0.90825 | closed | 24 | SS 35/10 kV Novodubovoe | 2.5 | 0.046 | 0.95425 | 0 | 0 | 0.95425 | 0 | 0 | -0.95425 | -0.95425 | closed
25 | SS 35/10 kV Beryozovka | 2.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | closed | 25 | SS 35/10 kV Beryozovka | 2.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | closed
26 | SS 35/6 kV Karyer | 4 |  | 0.32 | [8 empty] | 1: 26; 2: SS 35/6 kV Karyer; 3: 4; 5: 0
Two- and more transformer substations (for two voltage levels) | [12 empty] | 1: Two- and more transformer substations (for two voltage levels)
27 | SS 110/6 kV Agregatnaya | 16+16 | 32 | 12.7 | 0 | 0 | 12.7 | 0 | 16.8 | 4.1 | 4.1 | open | 27 | SS 110/6 kV Agregatnaya | 16+16 | 0.555 | 13.255 | 0 | 0 | 13.255 | 0 | 16.8 | 3.545 | 3.545 | open
28 | SS 110/6 kV Zapadnaya | 40+40 | 80 | 14.93 | 0 | 0 | 14.93 | 0 | 42 | 27.07 | 27.07 | open | 28 | SS 110/6 kV Zapadnaya | 40+40 | 3.624 | 18.554 | 0 | 0 | 18.554 | 0 | 42 | 23.446 | 23.446 | open
29 | SS 110/10 kV Kashary | 2,5+6,3 | 8.8 | 1.28 | 2.3 | 100 | -1.02 | 0 | 2.625 | 3.645 | 3.645 | open | 29 | SS 110/10 kV Kashary | 2,5+6,3 | 0.353 | 1.633 | 2.3 | 100 | -0.667 | 0 | 2.625 | 3.292 | 3.292 | open
30 | SS 110/6 kV Tabak | 16+16 | 32 | 7.72 | 3.2 | 20 | 4.52 | 0 | 16.8 | 12.28 | 12.28 | open | 30 | SS 110/6 kV Tabak | 16+16 | 0.03 | 7.75 | 3.2 | 20 | 4.55 | 0 | 16.8 | 12.25 | 12.25 | open
31 | SS 110/10 kV Lukoshkino | 10+2,5 | 12.5 | 0.14 | 0 | 0 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open | 31 | SS 110/10 kV Lukoshkino | 10+2,5 | 0.014 | 0.154 | 0 | 0 | 0.154 | 0 | 2.625 | 2.471 | 2.471 | open
32 | SS 110/10kV Niva | 10+10 | 20 | 5.09 | 1 | 100 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | open | 32 | SS 110/10kV Niva | 10+10 | 0.05 | 5.14 | 1 | 100 | 4.14 | 0 | 10.5 | 6.36 | 6.36 | open
33 | SS 110/10 kV Olkhovets | 2,5+2,5 | 5 | 1.4 | 0.8 | 100 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open | 33 | SS 110/10 kV Olkhovets | 2,5+2,5 | 0.09 | 1.49 | 0.8 | 100 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | open
34 | SS 110/10 kV Kuyman | 2,5+2,5 | 5 | 0.8 | 1 | 100 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | * | 34 | SS 110/10 kV Kuyman | 2,5+2,5 | 0.037 | 0.837 | 1 | 100 | -0.163 | 0 | 2.625 | 2.788 | 2.788 | open
35 | SS 110/10 kV Lutoshkino | 2,5+2,5 | 5 | 0.38 | 0.5 | 60 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open | 35 | SS 110/10 kV Lutoshkino | 2,5+2,5 |  | 0.38 | 0.5 | 60 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open
36 | SS 110/10 kV Krugloe | 2,5+2,5 | 5 | 0.59 | 0.5 | 60 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 36 | SS 110/10 kV Krugloe | 2,5+2,5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open
37 | SS 110/10/6 kV Yugo-Zapadnaya | 40+40 | 80 | 42.99 | 4.5 | 30 | 38.49 | 0 | 42 | 3.51 | 3.51 | * | 37 | SS 110/10/6 kV Yugo-Zapadnaya | 40+40 | 13.23 | 56.22 | 4.5 | 30 | 51.72 | 0 | 42 | -9.72 | -9.72 | closed
38 | SS 110/6 kV Privokzalnaya | 20+20+25 | 65 | 42.27 | 1.38 | 30 | 40.89 | 0 | 42 | 1.11 | 1.11 | open | 38 | SS 110/6 kV Privokzalnaya | 20+20+25 | 0.978 | 43.248 | 1.38 | 30 | 41.868 | 0 | 42 | 0.132 | 0.132 | open
39 | SS 110/10/6 kV Yuzhnaya | 40+40 | 80 | 41 | 6 | 30 | 35 | 0 | 42 | 7 | 7 | * | 39 | SS 110/10/6 kV Yuzhnaya | 40+40 | 4.435 | 45.435 | 6 | 30 | 39.435 | 0 | 42 | 2.565 | 2.565 | *
40 | SS 110/6 kV Sitovka | 10+10 | 20 | 3.79 | 1.29 | 30 | 2.5 | 0 | 10.5 | 8 | 8 | * | 40 | SS 110/6 kV Sitovka | 10+10 |  | 3.79 | 1.29 | 30 | 2.5 | 0 | 10.5 | 8 | 8 | *
41 | SS 110/6 kV LTP | 6,3+10 | 16.3 | 2.54 | 0 | 0 | 2.54 | 0 | 6.615 | 4.075 | 4.075 | * | 41 | SS 110/6 kV LTP | 6,3+10 |  | 2.54 | 0 | 0 | 2.54 | 0 | 6.615 | 4.075 | 4.075 | *
42 | SS 110/6 kV KPD | 10+10 | 20 | 2.43 | 0 | 0 | 2.43 | 0 | 10.5 | 8.07 | 8.07 | * | 42 | SS 110/6 kV KPD | 10+10 | 1.6 | 4.03 | 0 | 0 | 4.03 | 0 | 10.5 | 6.47 | 6.47 | *
43 | SS 110/10 kV Oktyabskaya | 40+40 | 80 | 19.02 | 4 | 30 | 15.02 | 0 | 42 | 26.98 | 26.98 | * | 43 | SS 110/10 kV Oktyabskaya | 40+40 | 13.301 | 32.321 | 4 | 30 | 28.321 | 0 | 42 | 13.679 | 13.679 | *
44 | SS 110/10 kV Universitetskaya | 40+40 | 80 | 0 | 0 | 0 | 0 | 0 | 42 | 42 | 42 | open | 44 | SS 110/10 kV Universitetskaya | 40+40 | 52.8 | 52.8 | 0 | 0 | 52.8 | 0 | 42 | -10.8 | -10.8 | closed
45 | SS 110/6 kV Teplichnaya | 15+15 | 30 | 6.28 | 0 | 0 | 6.28 | 0 | 15.75 | 9.47 | 9.47 | * | 45 | SS 110/6 kV Teplichnaya | 15+15 | 0.014 | 6.294 | 0 | 0 | 6.294 | 0 | 15.75 | 9.456 | 9.456 | *
46 | SS 110/6 kV Trubnaya-2 | 25+25 | 50 | 5.22 | 0 | 0 | 5.22 | 0 | 26.25 | 21.03 | 21.03 | * | 46 | SS 110/6 kV Trubnaya-2 | 25+25 | 0.065 | 5.285 | 0 | 0 | 5.285 | 0 | 26.25 | 20.965 | 20.965 | *
47 | SS 110/6 kV GPP-2 LTZ | 63+63 | 126 | 6.89 | 0 | 0 | 6.89 | 0 | 66.15 | 59.26 | 59.26 | * | 47 | SS 110/6 kV GPP-2 LTZ | 63+63 | 1.6 | 8.49 | 0 | 0 | 8.49 | 0 | 66.15 | 57.66 | 57.66 | *
48 | SS 35/10 kV Avangard | 4+4 | 8 | 1.05 | 1.2 | 110 | -0.15 | 0 | 4.2 | 4.35 | 4.35 | open | 48 | SS 35/10 kV Avangard | 4+4 | 0.178 | 1.228 | 1.2 | 110 | 0.028 | 0 | 4.2 | 4.172 | 4.172 | open
49 | SS 35/10 kV Afanasysevo | 2,5+2,5 | 5 | 1.33 | 0 | 0 | 1.33 | 0 | 2.625 | 1.295 | 1.295 | open | 49 | SS 35/10 kV Afanasysevo | 2,5+2,5 | 0.095 | 1.425 | 0 | 0 | 1.425 | 0 | 2.625 | 1.2 | 1.2 | open
50 | SS 35/10 kV Babarykino | 2,5+2,5 | 5 | 0.26 | 1.4 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | open | 50 | SS 35/10 kV Babarykino | 2,5+2,5 | 0.01 | 0.27 | 1.4 | 120 | -1.13 | 0 | 2.625 | 3.755 | 3.755 | open
51 | SS 35/10 kV Avrora | 2,5+2,5 | 5 | 0.66 | 1.2 | 110 | -0.54 | 0 | 2.625 | 3.165 | 3.165 | open | 51 | SS 35/10 kV Avrora | 2,5+2,5 | 0.229 | 0.889 | 1.2 | 110 | -0.311 | 0 | 2.625 | 2.936 | 2.936 | open
52 | SS 35/10 kV B.Boyovka | 2,5+2,5 | 5 | 0.38 | 1.5 | 120 | -1.12 | 0 | 2.625 | 3.745 | 3.745 | open | 52 | SS 35/10 kV B.Boyovka | 2,5+2,5 |  | 0.38 | 1.5 | 120 | -1.12 | 0 | 2.625 | 3.745 | 3.745 | open
53 | SS 35/10 kV Borki | 2,5+2,5 | 5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | open | 53 | SS 35/10 kV Borki | 2,5+2,5 |  | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | open
54 | SS 35/6kV Vostochnaya | 10+16 | 26 | 6.9 | 4.8 | 20 | 2.1 | 0 | 10.5 | 8.4 | 8.4 | open | 54 | SS 35/6kV Vostochnaya | 10+16 | 2.388 | 9.288 | 4.8 | 20 | 4.488 | 0 | 10.5 | 6.012 | 6.012 | open
55 | SS 35/10 kV Vasilyevka | 2,5+2,5 | 5 | 0.51 | 1.5 | 90 | -0.99 | 0 | 2.625 | 3.615 | 3.615 | open | 55 | SS 35/10 kV Vasilyevka | 2,5+2,5 |  | 0.51 | 1.5 | 90 | -0.99 | 0 | 2.625 | 3.615 | 3.615 | open
56 | SS 35/10 kV Voronets | 4+4 | 8 | 1.41 | 1.2 | 110 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | open | 56 | SS 35/10 kV Voronets | 4+4 | 0.022 | 1.432 | 1.2 | 110 | 0.232 | 0 | 4.2 | 3.968 | 3.968 | open
57 | SS 35/6 kV Golikovo | 1,8+1,6 | 3.4 | 1.41 | 0 | 0 | 1.41 | 0 | 1.68 | 0.27 | 0.27 | open | 57 | SS 35/6 kV Golikovo | 1,8+1,6 |  | 1.41 | 0 | 0 | 1.41 | 0 | 1.68 | 0.27 | 0.27 | open
58 | SS 35/10 kV Gatishche | 2,5+2,5 | 5 | 0.28 | 0 | 0 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open | 58 | SS 35/10 kV Gatishche | 2,5+2,5 |  | 0.28 | 0 | 0 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open
59 | SS 35/10 kV Gnilusha | 6,3+6,3 | 12.6 | 0.7 | 1.2 | 120 | -0.5 | 0 | 6.615 | 7.115 | 7.115 | open | 59 | SS 35/10 kV Gnilusha | 6,3+6,3 | 0.085 | 0.785 | 1.2 | 120 | -0.415 | 0 | 6.615 | 7.03 | 7.03 | open
60 | SS 35/10kV Gryzlovo | 2,5+2,5 | 5 | 0.47 | 0.8 | 110 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | open | 60 | SS 35/10kV Gryzlovo | 2,5+2,5 | 0.025 | 0.495 | 0.8 | 110 | -0.305 | 0 | 2.625 | 2.93 | 2.93 | open
61 | SS 35/10 kV Zhernovnoe | 2,5+2,5 | 5 | 0.37 | 1.5 | 100 | -1.13 | 0 | 2.625 | 3.755 | 3.755 | open | 61 | SS 35/10 kV Zhernovnoe | 2,5+2,5 | 0.352 | 0.722 | 1.5 | 100 | -0.778 | 0 | 2.625 | 3.403 | 3.403 | open
62 | SS 35/10 kV Zadonsk-selsk. | 3,2+1,6 | 4.8 | 1.95 | 0 | 0 | 1.95 | 0 | 1.68 | -0.27 | -0.27 | closed | 62 | SS 35/10 kV Zadonsk-selsk. | 3,2+1,6 | 0.27 | 2.22 | 0 | 0 | 2.22 | 0 | 1.68 | -0.54 | -0.54 | closed
63 | SS 35/10 kV Zakharovka | 2,5+2,5 | 5 | 0.4 | 0.8 | 60 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | open | 63 | SS 35/10 kV Zakharovka | 2,5+2,5 |  | 0.4 | 0.8 | 60 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | open
64 | SS 35/10 kV Kazaki | 4+4 | 8 | 0.68 | 0 | 0 | 0.68 | 0 | 4.2 | 3.52 | 3.52 | open | 64 | SS 35/10 kV Kazaki | 4+4 | 0.008 | 0.688 | 0 | 0 | 0.688 | 0 | 4.2 | 3.512 | 3.512 | open
65 | SS 35/10 kV Kolesovo | 6,3+6,3 | 12.6 | 1.71 | 1.5 | 90 | 0.21 | 0 | 6.615 | 6.405 | 6.405 | open | 65 | SS 35/10 kV Kolesovo | 6,3+6,3 | 0.097 | 1.807 | 1.5 | 90 | 0.307 | 0 | 6.615 | 6.308 | 6.308 | open
66 | SS 35/10 kV Knyazevo | 2,5+2,5 | 5 | 0.35 | 0 | 0 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open | 66 | SS 35/10 kV Knyazevo | 2,5+2,5 |  | 0.35 | 0 | 0 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | open
67 | SS 35/10 kV Kirillovo | 2,5+2,5 | 5 | 0.31 | 1.5 | 70 | -1.19 | 0 | 2.625 | 3.815 | 3.815 | open | 67 | SS 35/10 kV Kirillovo | 2,5+2,5 |  | 0.31 | 1.5 | 70 | -1.19 | 0 | 2.625 | 3.815 | 3.815 | open
68 | SS 35/10 kV Ksizovo | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | open | 68 | SS 35/10 kV Ksizovo | 2,5+2,5 | 0.005 | 0.295 | 0 | 0 | 0.295 | 0 | 2.625 | 2.33 | 2.33 | open
69 | SS 35/10 kV Lamskoe | 2,5+2,5 | 5 | 1.75 | 1.2 | 100 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | open | 69 | SS 35/10 kV Lamskoe | 2,5+2,5 | 0.022 | 1.772 | 1.2 | 100 | 0.572 | 0 | 2.625 | 2.053 | 2.053 | open
70 | SS 35/10 kV Kazachye | 2,5+2,5 | 5 | 0.37 | 0 | 0 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | open | 70 | SS 35/10 kV Kazachye | 2,5+2,5 | 0.029 | 0.399 | 0 | 0 | 0.399 | 0 | 2.625 | 2.226 | 2.226 | open
71 | SS 35/10 kV Lebyazhye | 2,5+1,6 | 4.1 | 0.35 | 0 | 0 | 0.35 | 0 | 1.68 | 1.33 | 1.33 | open | 71 | SS 35/10 kV Lebyazhye | 2,5+1,6 |  | 0.35 | 0 | 0 | 0.35 | 0 | 1.68 | 1.33 | 1.33 | open
72 | SS 35/10 kV Lomovets | 1,6+2,5 | 4.1 | 0.48 | 0 | 0 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | open | 72 | SS 35/10 kV Lomovets | 1,6+2,5 | 0.005 | 0.485 | 0 | 0 | 0.485 | 0 | 1.68 | 1.195 | 1.195 | open
73 | SS 35/10 kV Olshanets | 2,5+4 | 6.5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | open | 73 | SS 35/10 kV Olshanets | 2,5+4 |  | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | open
74 | SS 35/10 kV Ploskoe | 4+4 | 8 | 3.63 | 3 | 70 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | open | 74 | SS 35/10 kV Ploskoe | 4+4 | 1.252 | 4.882 | 3 | 70 | 1.882 | 0 | 4.2 | 2.318 | 2.318 | open
75 | SS 35/10 kV Stegalovka | 2,5+3,2 | 5.7 | 0.48 | 1.1 | 70 | -0.62 | 0 | 2.625 | 3.245 | 3.245 | open | 75 | SS 35/10 kV Stegalovka | 2,5+3,2 | 0.023 | 0.503 | 1.1 | 70 | -0.597 | 0 | 2.625 | 3.222 | 3.222 | open
76 | SS 35/10 kV Solidarnost | 4+4 | 8 | 1.16 | 1.2 | 70 | -0.04 | 0 | 4.2 | 4.24 | 4.24 | open | 76 | SS 35/10 kV Solidarnost | 4+4 | 0.024 | 1.184 | 1.2 | 70 | -0.016 | 0 | 4.2 | 4.216 | 4.216 | open
77 | SS 35/10 kV Timiryazevo | 4+4 | 8 | 0.77 | 0.8 | 45 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | open | 77 | SS 35/10 kV Timiryazevo | 4+4 | 0.033 | 0.803 | 0.8 | 45 | 0.003 | 0 | 4.2 | 4.197 | 4.197 | open
78 | SS 35/10 kV Talitsa | 2,5+2,5 | 5 | 1.18 | 1.5 | 110 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | open | 78 | SS 35/10 kV Talitsa | 2,5+2,5 | 0.346 | 1.526 | 1.5 | 110 | 0.026 | 0 | 2.625 | 2.599 | 2.599 | open
79 | SS 35/10 kV the II Terbuny | 2,5+2,5 | 5 | 0.98 | 0 | 0 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | open | 79 | SS 35/10 kV the II Terbuny | 2,5+2,5 | 1.07 | 2.05 | 0 | 0 | 2.05 | 0 | 2.625 | 0.575 | 0.575 | open
80 | SS 35/10 kV Tikhii Don | 4+4 | 8 | 0.49 | 0.8 | 50 | -0.31 | 0 | 4.2 | 4.51 | 4.51 | open | 80 | SS 35/10 kV Tikhii Don | 4+4 | 0.083 | 0.573 | 0.8 | 50 | -0.227 | 0 | 4.2 | 4.427 | 4.427 | open
81 | SS 35/10 kV Khitrovo | 6,3+6,3 | 12.6 | 0.41 | 0 | 0 | 0.41 | 0 | 6.615 | 6.205 | 6.205 | open | 81 | SS 35/10 kV Khitrovo | 6,3+6,3 | 0.014 | 0.424 | 0 | 0 | 0.424 | 0 | 6.62 | 6.196 | 6.196 | open
82 | SS 35/10 kV Chernava | 2,5+2,5 | 5 | 1.46 | 0 | 0 | 1.46 | 0 | 2.625 | 1.165 | 1.165 | open | 82 | SS 35/10 kV Chernava | 2,5+2,5 | 0.029 | 1.489 | 0 | 0 | 1.489 | 0 | 2.625 | 1.136 | 1.136 | open
83 | SS 35/10 kV Chernoles | 2,5+2,5 | 5 | 0.23 | 0 | 0 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | open | 83 | SS 35/10 kV Chernoles | 2,5+2,5 | 0.007 | 0.237 | 0 | 0 | 0.237 | 0 | 2.625 | 2.388 | 2.388 | open
84 | SS 35/6 kV SS No. 5 | 6,3+3,2 | 9.5 | 1.07 | 0 | 0 | 1.07 | 0 | 3.36 | 2.29 | 2.29 | open | 84 | SS 35/6 kV SS No. 5 | 6,3+3,2 |  | 1.07 | 0 | 0 | 1.07 | 0 | 3.36 | 2.29 | 2.29 | open
85 | SS 35/10 kV Krasnoe | 4+4 | 8 | 3.4 | 1 | 120 | 2.4 | 0 | 4.2 | 1.8 | 1.8 | open | 85 | SS 35/10 kV Krasnoe | 4+4 | 0.059 | 3.459 | 1 | 120 | 2.459 | 0 | 4.2 | 1.741 | 1.741 | open
86 | SS 35/10 kV Tyoploe | 2,5+2,5 | 5 | 1.01 | 1 | 60 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | open | 86 | SS 35/10 kV Tyoploe | 2,5+2,5 |  | 1.01 | 1 | 60 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | open
87 | SS 35/10 kV Dankov-selskaya | 6,3+4 | 10.3 | 4.28 | 2 | 120 | 2.28 | 0 | 4.2 | 1.92 | 1.92 | open | 87 | SS 35/10 kV Dankov-selskaya | 6,3+4 | 0.724 | 5.004 | 2 | 120 | 3.004 | 0 | 4.2 | 1.196 | 1.196 | open
88 | SS 35/10 kV Kolybelskaya | 2,5+2,5 | 5 | 0.91 | 0 | 0 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | open | 88 | SS 35/10 kV Kolybelskaya | 2,5+2,5 | 0.03 | 0.94 | 0 | 0 | 0.94 | 0 | 2.625 | 1.685 | 1.685 | open
89 | SS 35/10 kV Topki | 2,5+2,5 | 5 | 0.58 | 0.5 | 60 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | open | 89 | SS 35/10 kV Topki | 2,5+2,5 | 0.76 | 1.34 | 0.5 | 60 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | open
90 | SS 35/10 kV Agronom | 4+6,3 | 10.3 | 1.48 | 1 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | open | 90 | SS 35/10 kV Agronom | 4+6,3 | 0.036 | 1.516 | 1 | 120 | 0.516 | 0 | 4.2 | 3.684 | 3.684 | open
91 | SS 35/10 kV Troekurovo-sovkhoznaya | 2,5+2,5 | 5 | 1.78 | 0.5 | 60 | 1.28 | 0 | 2.625 | 1.345 | 1.345 | open | 91 | SS 35/10 kV Troekurovo-sovkhoznaya | 2,5+2,5 | 0.93 | 2.71 | 0.5 | 60 | 2.21 | 0 | 2.625 | 0.415 | 0.415 | open
92 | SS 35/10 kV Gagarino | 1,8+1,8 | 3.6 | 0.46 | 0.5 | 120 | -0.04 | 0 | 1.89 | 1.93 | 1.93 | open | 92 | SS 35/10 kV Gagarino | 1,8+1,8 |  | 0.46 | 0.5 | 120 | -0.04 | 0 | 1.89 | 1.93 | 1.93 | open
93 | SS 35/10 kV Ranenburg | 1,6+1,6 | 3.2 | 1.76 | 0.5 | 60 | 1.26 | 0 | 1.68 | 0.42 | 0.42 | open | 93 | SS 35/10 kV Ranenburg | 1,6+1,6 | 0.131 | 1.891 | 0.5 | 60 | 1.391 | 0 | 1.68 | 0.289 | 0.289 | open
94 | SS 35/10 kV Sergievka | 2,5+2,5 | 5 | 0.49 | 0.5 | 60 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 94 | SS 35/10 kV Sergievka | 2,5+2,5 |  | 0.49 | 0.5 | 60 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open
95 | SS 35/10 kV Drezgalovo | 1,6+1,6 | 3.2 | 0.57 | 0.5 | 60 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 95 | SS 35/10 kV Drezgalovo | 1,6+1,6 |  | 0.57 | 0.5 | 60 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open
96 | SS 35/10 kV Dolgoe | 2,5+2,5 | 5 | 0.26 | 0 | 0 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open | 96 | SS 35/10 kV Dolgoe | 2,5+2,5 |  | 0.26 | 0 | 0 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open
97 | SS 35/10 kV Voskresenovka | 1,6+1,6 | 3.2 | 0.57 | 0 | 0 | 0.57 | 0 | 1.68 | 1.11 | 1.11 | open | 97 | SS 35/10 kV Voskresenovka | 1,6+1,6 | 0.01 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | open
98 | SS 35/10 kV Saprykino | 1,6+2,5 | 4.1 | 0.52 | 0 | 0 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open | 98 | SS 35/10 kV Saprykino | 1,6+2,5 | 0.03 | 0.55 | 0 | 0 | 0.55 | 0 | 1.68 | 1.13 | 1.13 | open
99 | SS 35/10 kV Nopolyanye | 2,5+2,5 | 5 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | open | 99 | SS 35/10 kV Nopolyanye | 2,5+2,5 |  | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | open
100 | SS 35/10 kV Vednoe | 2,5+2,5 | 5 | 0.56 | 0.5 | 180 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | open | 100 | SS 35/10 kV Vednoe | 2,5+2,5 | 0.009 | 0.569 | 0.5 | 180 | 0.069 | 0 | 2.625 | 2.556 | 2.556 | open
101 | SS 35/10 kV Bigildino | 2,5+2,5 | 5 | 0.86 | 0.5 | 60 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open | 101 | SS 35/10 kV Bigildino | 2,5+2,5 |  | 0.86 | 0.5 | 60 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open
102 | SS 35/10 kV Kultura | 2,5+2,5 | 5 | 0.89 | 0.5 | 60 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | open | 102 | SS 35/10 kV Kultura | 2,5+2,5 | 0.029 | 0.919 | 0.5 | 60 | 0.419 | 0 | 2.625 | 2.206 | 2.206 | open
103 | SS 35/10 kV Boryatino | 2,5+2,5 | 5 | 0.38 | 0 | 0 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open | 103 | SS 35/10 kV Boryatino | 2,5+2,5 |  | 0.38 | 0 | 0 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
104 | SS 35/10 kV B.Popovo | 2,5+2,5 | 5 | 1.64 | 0.5 | 60 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | open | 104 | SS 35/10 kV B.Popovo | 2,5+2,5 | 0.037 | 1.677 | 0.5 | 60 | 1.177 | 0 | 2.625 | 1.448 | 1.448 | open
105 | SS 35/10 kV B. Izbishchi | 2,5+2,5 | 5 | 1.41 | 0.5 | 60 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | open | 105 | SS 35/10 kV B. Izbishchi | 2,5+2,5 | 0.755 | 2.165 | 0.5 | 60 | 1.665 | 0 | 2.625 | 0.96 | 0.96 | open
106 | SS 35/10 kV Polibino | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | open | 106 | SS 35/10 kV Polibino | 2,5+2,5 |  | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | open
107 | SS 35/10 kV Dubrava | 2,5+2,5 | 5 | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open | 107 | SS 35/10 kV Dubrava | 2,5+2,5 |  | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open
108 | SS 35/10 kV Khrushchevo | 2,5+2,5 | 5 | 0.34 | 0 | 0 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open | 108 | SS 35/10 kV Khrushchevo | 2,5+2,5 | 0.006 | 0.346 | 0 | 0 | 0.346 | 0 | 2.625 | 2.279 | 2.279 | open
109 | SS 35/10 kV B. Verkh | 2,5+2,5 | 5 | 0.7 | 0.5 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 109 | SS 35/10 kV B. Verkh | 2,5+2,5 | 0.042 | 0.742 | 0.5 | 120 | 0.242 | 0 | 2.625 | 2.383 | 2.383 | open
110 | SS 35/10 kV Golovinshchino | 2,5+2,5 | 5 | 0.52 | 0 | 0 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | open | 110 | SS 35/10 kV Golovinshchino | 2,5+2,5 | 0.015 | 0.535 | 0 | 0 | 0.535 | 0 | 2.625 | 2.09 | 2.09 | open
111 | SS 35/10 kV Yablonevoe | 2,5+2,5 | 5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | open | 111 | SS 35/10 kV Yablonevoe | 2,5+2,5 | 0.04 | 0.52 | 0 | 0 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | open
112 | SS 35/10 kV Politovo | 2,5+2,5 | 5 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | open | 112 | SS 35/10 kV Politovo | 2,5+2,5 |  | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | open
113 | SS 35/10 kV Complex | 4+4 | 8 | 0.92 | 1 | 120 | -0.08 | 0 | 4.2 | 4.28 | 4.28 | open | 113 | SS 35/10 kV Complex | 4+4 |  | 0.92 | 1 | 120 | -0.08 | 0 | 4.2 | 4.28 | 4.28 | open
114 | SS 35/10 kV No.1 | 4+4 | 8 | 3.68 | 0 | 0 | 3.68 | 0 | 4.2 | 0.52 | 0.52 | open | 114 | SS 35/10 kV No.1 | 4+4 | 0.676 | 4.356 | 0 | 0 | 4.356 | 0 | 4.2 | -0.156 | -0.156 | closed
115 | SS 35/6 kV No. 2 | 1+1+1 | 3 | 1.8217 | 0 | 0 | 1.8217 | 0 | 1.05 | -0.77169 | -0.77169 | closed | 115 | SS 35/6 kV No. 2 | 1+1+1 | 0.334 | 2.1557 | 0 | 0 | 2.1557 | 0 | 1.05 | -1.1057 | -1.1057 | closed
116 | SS 35/10 kV No. 3 | 2,5+2,5 | 5 | 0.95 | 0.46 | 90 | 0.49 | 0 | 2.625 | 2.135 | 2.135 | * | 116 | SS 35/10 kV No. 3 | 2,5+2,5 | 0.21 | 1.16 | 0.46 | 90 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | *
117 | SS 35/6 kV No. 4 | 4+4 | 8 | 2.24 | 0 | 0 | 2.24 | 0 | 4.2 | 1.96 | 1.96 | * | 117 | SS 35/6 kV No. 4 | 4+4 | 0.236 | 2.476 | 0 | 0 | 2.476 | 0 | 4.2 | 1.724 | 1.724 | *
118 | SS 35/6 kV Gryazi-gorod | 6,3+5,6 | 11.9 | 4.38 | 0 | 0 | 4.38 | 0 | 5.88 | 1.5 | 1.5 | open | 118 | SS 35/6 kV Gryazi-gorod | 6,3+5,6 | 0.408 | 4.788 | 0 | 0 | 4.788 | 0 | 5.88 | 1.092 | 1.092 | open
119 | SS 35/10 kV Butyrki | 5,6+4 | 9.6 | 6.15 | 0 | 0 | 6.15 | 0 | 4.2 | -1.95 | -1.95 | closed | 119 | SS 35/10 kV Butyrki | 5,6+4 | -1.063 | 5.087 | 0 | 0 | 5.087 | 0 | 4.2 | -0.887 | -0.887 | closed
120 | SS 35/10 kV Yarlukovo | 3,2+4 | 7.2 | 3.51 | 1.5 | 80 | 2.01 | 0 | 3.36 | 1.35 | 1.35 | open | 120 | SS 35/10 kV Yarlukovo | 3,2+4 | 0.422 | 3.932 | 1.5 | 80 | 2.432 | 0 | 3.36 | 0.928 | 0.928 | open
121 | SS 35/10 kV Knyazhya Baygora | 1,6+1,6 | 3.2 | 0.44 | 0.22 | 70 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open | 121 | SS 35/10 kV Knyazhya Baygora | 1,6+1,6 |  | 0.44 | 0.22 | 70 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open
122 | SS 35/10 kV Pravda | 4+2,5 | 6.5 | 0.96 | 2.06 | 100 | -1.1 | 0 | 2.625 | 3.725 | 3.725 | open | 122 | SS 35/10 kV Pravda | 4+2,5 |  | 0.96 | 2.06 | 100 | -1.1 | 0 | 2.625 | 3.725 | 3.725 | open
123 | SS 35/10 kV Krasnaya Dubrava | 2,5+2,5 | 5 | 0.35 | 0.18 | 70 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 123 | SS 35/10 kV Krasnaya Dubrava | 2,5+2,5 |  | 0.35 | 0.18 | 70 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
124 | SS 35/10 kV Matyra | 4+3,2 | 7.2 | 3.67 | 0 | 0 | 3.67 | 0 | 3.36 | -0.31 | -0.31 | closed | 124 | SS 35/10 kV Matyra | 4+3,2 | 0.183 | 3.853 | 0 | 0 | 3.853 | 0 | 3.36 | -0.493 | -0.493 | closed
125 | SS 35/10 kV Vperyod | 4+4 | 8 | 0.83 | 0.32 | 80 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | open | 125 | SS 35/10 kV Vperyod | 4+4 | 0.05 | 0.88 | 0.32 | 80 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | open
126 | SS 35/10 kV Maley | 4+2,5 | 6.5 | 0.56 | 0.12 | 70 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | open | 126 | SS 35/10 kV Maley | 4+2,5 |  | 0.56 | 0.12 | 70 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | open
127 | SS 35/10 kV SKhТ | 2,5+1,6 | 4.1 | 1.49 | 0 | 0 | 1.49 | 0 | 1.68 | 0.19 | 0.19 | open | 127 | SS 35/10 kV SKhТ | 2,5+1,6 | 0.685 | 2.175 | 0 | 0 | 2.175 | 0 | 1.68 | -0.495 | -0.495 | closed
128 | SS 35/10 kV Soshki | 4+4 | 8 | 0.49 | 0.2 | 80 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | open | 128 | SS 35/10 kV Soshki | 4+4 | 0.005 | 0.495 | 0.2 | 80 | 0.295 | 0 | 4.2 | 3.905 | 3.905 | open
129 | SS 35/6 kV Tavolzhanka | 4+4 | 8 | 4.35 | 0 | 0 | 4.35 | 0 | 4.2 | -0.15 | -0.15 | closed | 129 | SS 35/6 kV Tavolzhanka | 4+4 | 0.965 | 5.315 | 0 | 0 | 5.315 | 0 | 4.2 | -1.115 | -1.115 | closed
130 | SS 35/10 kV Trubetchino | 2,5+2,5 | 5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | * | 130 | SS 35/10 kV Trubetchino | 2,5+2,5 | 0.025 | 1.215 | 0 | 0 | 1.215 | 0 | 2.625 | 1.41 | 1.41 | open
131 | SS 35/10 kV Ratchino | 2,5+2,5 | 5 | 1.08 | 0.12 | 70 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | * | 131 | SS 35/10 kV Ratchino | 2,5+2,5 | 0.018 | 1.098 | 0.12 | 70 | 0.978 | 0 | 2.625 | 1.647 | 1.647 | *
132 | SS 35/10 kV Kalikino | 3,2+3,2 | 6.4 | 2.1 | 0.42 | 80 | 1.68 | 0 | 3.36 | 1.68 | 1.68 | * | 132 | SS 35/10 kV Kalikino | 3,2+3,2 | 0.005 | 2.105 | 0.42 | 80 | 1.685 | 0 | 3.36 | 1.675 | 1.675 | *
133 | SS 35/10 kV Borisovka | 4+2,5 | 6.5 | 2.67 | 0 | 0 | 2.67 | 0 | 2.625 | -0.045 | -0.045 | closed | 133 | SS 35/10 kV Borisovka | 4+2,5 | 0.828 | 3.498 | 0 | 0 | 3.498 | 0 | 2.625 | -0.873 | -0.873 | closed
134 | SS 35/10 kV Vvedenka | 4+4 | 8 | 1.96 | 0.14 | 70 | 1.82 | 0 | 4.2 | 2.38 | 2.38 | * | 134 | SS 35/10 kV Vvedenka | 4+4 | 1.506 | 3.466 | 0.14 | 70 | 3.326 | 0 | 4.2 | 0.874 | 0.874 | open
135 | SS 35/10 kV Gryaznoe | 4+4 | 8 | 1.1 | 0 | 0 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | * | 135 | SS 35/10 kV Gryaznoe | 4+4 | 0.58 | 1.68 | 0 | 0 | 1.68 | 0 | 4.2 | 2.52 | 2.52 | *
136 | SS 35/10 kV Borino | 4+4 | 8 | 3.92 | 1.2 | 90 | 2.72 | 0 | 4.2 | 1.48 | 1.48 | * | 136 | SS 35/10 kV Borino | 4+4 | 0.106 | 4.026 | 1.2 | 90 | 2.826 | 0 | 4.2 | 1.374 | 1.374 | *
137 | SS 35/10 kV Chastaya Dubrava | 2,5+2,5 | 5 | 1.54 | 1.88 | 100 (45) | -0.34 | 0 | 2.625 | 2.965 | 2.965 | * | 137 | SS 35/10 kV Chastaya Dubrava | 2,5+2,5 | 0.723 | 2.263 | 1.88 | 100 (45) | 0.383 | 0 | 2.625 | 2.242 | 2.242 | open
138 | SS 35/10 kV Troitskaya | 2,5+4 | 6.5 | 2.23 | 0.6 | 70 | 1.63 | 0 | 2.625 | 0.995 | 0.995 | * | 138 | SS 35/10 kV Troitskaya | 2,5+4 | 0.465 | 2.695 | 0.6 | 70 | 2.095 | 0 | 2.625 | 0.53 | 0.53 | *
139 | SS 35/6 kV Veshalovka | 2,5+2,5 | 5 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | * | 139 | SS 35/6 kV Veshalovka | 2,5+2,5 | 0.075 | 0.925 | 0 | 0 | 0.925 | 0 | 2.625 | 1.7 | 1.7 | *
140 | SS 35/10 kV Pruzhinki | 2,5+2,5 | 5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | * | 140 | SS 35/10 kV Pruzhinki | 2,5+2,5 | 0.03 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | *
141 | SS 35/10 kV Stebaevo | 2,5+2,5 | 5 | 0.64 | 0.28 | 80 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | * | 141 | SS 35/10 kV Stebaevo | 2,5+2,5 | 0.04 | 0.68 | 0.28 | 80 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | *
142 | SS 35/10 kV Khleboprodukty | 6,3+6,3 | 12.6 | 3.51 | 0.6 | 100 | 2.91 | 0 | 6.615 | 3.705 | 3.705 | * | 142 | SS 35/10 kV Khleboprodukty | 6,3+6,3 | 0.38 | 3.89 | 0.6 | 100 | 3.29 | 0 | 6.615 | 3.325 | 3.325 | *
143 | SS 35/10 kV Sentsovo | 10+10 | 20 | 5.9 | 0 | 0 | 5.9 | 0 | 10.5 | 4.6 | 4.6 | * | 143 | SS 35/10 kV Sentsovo | 10+10 | 1.822 | 7.722 | 0 | 0 | 7.722 | 0 | 10.5 | 2.778 | 2.778 | *
144 | SS 35/10 kV Meet processing plant | 6,3+6,3 | 12.6 | 4.56 | 1.6 | 110 | 2.96 | 0 | 6.62 | 3.66 | 3.66 | * | 144 | SS 35/10 kV Meet processing plant | 6,3+6,3 | 0.24 | 4.8 | 1.6 | 110 | 3.2 | 0 | 6.62 | 3.42 | 3.42 | *
145 | SS 35/6 kV Poultry plant | 4+4 | 8 | 1.41 | 0 | 0 | 1.41 | 0 | 4.2 | 2.79 | 2.79 | * | 145 | SS 35/6 kV Poultry plant | 4+4 | 0.052 | 1.462 | 0 | 0 | 1.462 | 0 | 4.2 | 2.738 | 2.738 | *
146 | SS 35/6 kV Water intake | 10+10 | 20 | 0.64 | 0 | 0 | 0.64 | 0 | 10.5 | 9.86 | 9.86 | * | 146 | SS 35/6 kV Water intake | 10+10 | 0.062 | 0.702 | 0 | 0 | 0.702 | 0 | 10.5 | 9.798 | 9.798 | *
147 | SS 35/10 kV Petrovskaya | 2,5+4 | 6.5 | 0.97 | 1.06 | 90 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 147 | SS 35/10 kV Petrovskaya | 2,5+4 |  | 0.97 | 1.06 | 90 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open
148 | SS 35/10 kV Lebedyanka | 2,5+2,5 | 5 | 0.61 | 0.68 | 90 | -0.07 | 0 | 2.625 | 2.695 | 2.695 | open | 148 | SS 35/10 kV Lebedyanka | 2,5+2,5 | 0.005 | 0.615 | 0.68 | 90 | -0.065 | 0 | 2.625 | 2.69 | 2.69 | open
149 | SS 35/10 kV Novocherkutino | 4+4 | 8 | 0.89 | 1.02 | 100 | -0.13 | 0 | 4.2 | 4.33 | 4.33 | open | 149 | SS 35/10 kV Novocherkutino | 4+4 | 0.005 | 0.895 | 1.02 | 100 | -0.125 | 0 | 4.2 | 4.325 | 4.325 | open
150 | SS 35/10 kV Ivanovka | 2,5+2,5 | 5 | 1.01 | 0 | 0 | 1.01 | 0 | 2.625 | 1.615 | 1.615 | open | 150 | SS 35/10 kV Ivanovka | 2,5+2,5 | 0.05 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | open
151 | SS 35/10 kV Poddubrovka | 2,5+2,5 | 5 | 1.04 | 0 | 0 | 1.04 | 0 | 2.625 | 1.585 | 1.585 | open | 151 | SS 35/10 kV Poddubrovka | 2,5+2,5 | 0.033 | 1.073 | 0 | 0 | 1.073 | 0 | 2.625 | 1.552 | 1.552 | open
152 | SS 35/10 kV Plavitsa | 1,6+1,6 | 3.2 | 1.05 | 0.46 | 90 | 0.59 | 0 | 1.68 | 1.09 | 1.09 | open | 152 | SS 35/10 kV Plavitsa | 1,6+1,6 |  | 1.05 | 0.46 | 90 | 0.59 | 0 | 1.68 | 1.09 | 1.09 | open
153 | SS 35/10 kV Parshinovka | 1,6+2,5 | 4.1 | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | open | 153 | SS 35/10 kV Parshinovka | 1,6+2,5 | 0.007 | 0.517 | 0 | 0 | 0.517 | 0 | 1.68 | 1.163 | 1.163 | open
154 | SS 35/10 kV Talitsky Chamlyk | 3,2+4 | 7.2 | 2.18 | 1.28 | 100 | 0.9 | 0 | 3.36 | 2.46 | 2.46 | open | 154 | SS 35/10 kV Talitsky Chamlyk | 3,2+4 | 0.025 | 2.205 | 1.28 | 100 | 0.925 | 0 | 3.36 | 2.435 | 2.435 | open
155 | SS 35/10 kV Demshinka | 2,5+2,5 | 5 | 0.17 | 0 | 0 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 155 | SS 35/10 kV Demshinka | 2,5+2,5 | 0.012 | 0.182 | 0 | 0 | 0.182 | 0 | 2.625 | 2.443 | 2.443 | open
156 | SS 35/10 kV Bereznyagovka | 1,6+1,6 | 3.2 | 0.87 | 0.46 | 80 | 0.41 | 0 | 1.68 | 1.27 | 1.27 | open | 156 | SS 35/10 kV Bereznyagovka | 1,6+1,6 | 0.015 | 0.885 | 0.46 | 80 | 0.425 | 0 | 1.68 | 1.255 | 1.255 | open
157 | SS 35/10 kV Dmitrievka | 2,5+2,5 | 5 | 0.73 | 0 | 0 | 0.73 | 0 | 2.625 | 1.895 | 1.895 | open | 157 | SS 35/10 kV Dmitrievka | 2,5+2,5 | 0.025 | 0.755 | 0 | 0 | 0.755 | 0 | 2.625 | 1.87 | 1.87 | open
158 | SS 35/10 kV Pashkovo | 2,5+2,5 | 5 | 1.41 | 0 | 0 | 1.41 | 0 | 2.625 | 1.215 | 1.215 | open | 158 | SS 35/10 kV Pashkovo | 2,5+2,5 | 0.008 | 1.418 | 0 | 0 | 1.418 | 0 | 2.625 | 1.207 | 1.207 | open
159 | SS 35/10 kV Moskovka | 1,6+1,6 | 3.2 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | open | 159 | SS 35/10 kV Moskovka | 1,6+1,6 | 0.01 | 0.68 | 0 | 0 | 0.68 | 0 | 1.68 | 1 | 1 | open
160 | SS 35/10 kV Bochinovka | 4+4 | 8 | 2.4 | 1.18 | 90 | 1.22 | 0 | 4.2 | 2.98 | 2.98 | open | 160 | SS 35/10 kV Bochinovka | 4+4 | 0.164 | 2.564 | 1.18 | 90 | 1.384 | 0 | 4.2 | 2.816 | 2.816 | open
161 | SS 35/10 kV Fyodorovka | 2,5+2,5 | 5 | 0.77 | 0.5 | 70 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open | 161 | SS 35/10 kV Fyodorovka | 2,5+2,5 |  | 0.77 | 0.5 | 70 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open
162 | SS 35/10 kV Kulikovo | 2,5+2,5 | 5 | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open | 162 | SS 35/10 kV Kulikovo | 2,5+2,5 |  | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open
163 | SS 35/10 kV Kon-Kolodez | 2,5+2,5 | 5 | 1.21 | 0 | 0 | 1.21 | 0 | 2.625 | 1.415 | 1.415 | * | 163 | SS 35/10 kV Kon-Kolodez | 2,5+2,5 | 0.475 | 1.685 | 0 | 0 | 1.685 | 0 | 2.625 | 0.94 | 0.94 | *
164 | SS 35/10 kV Dmitryashevka | 2,5+2,5 | 5 | 0.33 | 0 | 0 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | * | 164 | SS 35/10 kV Dmitryashevka | 2,5+2,5 | 0.005 | 0.335 | 0 | 0 | 0.335 | 0 | 2.625 | 2.29 | 2.29 | *
165 | SS 35/10 kV Rechnaya | 4+4 | 8 | 1.65 | 1.06 | 100 | 0.59 | 0 | 4.2 | 3.61 | 3.61 | * | 165 | SS 35/10 kV Rechnaya | 4+4 | 0.033 | 1.683 | 1.06 | 100 | 0.623 | 0 | 4.2 | 3.577 | 3.577 | *
166 | SS 35/10 kV Negachevka | 2,5+2,5 | 5 | 0.42 | 0.22 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | * | 166 | SS 35/10 kV Negachevka | 2,5+2,5 |  | 0.42 | 0.22 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | *
167 | SS 35/10 kV Karamyshevo | 10+10 | 20 | 1.02 | 0.1 | 70 | 0.92 | 0 | 10.5 | 9.58 | 9.58 | open | 167 | SS 35/10 kV Karamyshevo | 10+10 | 0.058 | 1.078 | 0.1 | 70 | 0.978 | 0 | 10.5 | 9.522 | 9.522 | open
168 | SS 35/10 kV Tyushevka | 1,6+1,6 | 3.2 | 0.81 | 0.1 | 70 | 0.71 | 0 | 1.68 | 0.97 | 0.97 | * | 168 | SS 35/10 kV Tyushevka | 1,6+1,6 | 0.007 | 0.817 | 0.1 | 70 | 0.717 | 0 | 1.68 | 0.963 | 0.963 | *
169 | SS 35/10 kV Sselki | 10+10 | 20 | 0.28 | 0 | 0 | 0.28 | 0 | 10.5 | 10.22 | 10.22 | open | 169 | SS 35/10 kV Sselki | 10+10 | 6.29 | 6.57 | 0 | 0 | 6.57 | 0 | 10.5 | 3.93 | 3.93 | open
Two- and more transformer substations (for three voltage levels) | [12 empty] | 1: Two- and more transformer substations (for three voltage levels)
170 | SS 110/35/10 kV Terbuny-110 | 10+10 | 20 | 8.54 | 3.5 |  | 5.04 | 0 | 10.5 | 5.46 | 4.94 | open | 170 | SS 110/35/10 kV Terbuny-110 | 10+10 | 1.034 | 9.574 | 3.5 |  | 6.074 | 0 | 10.5 | 4.426 | 4.417 | open
| Nom. Capacity MV, МVA | 10+10 |  | 2.98 | 3.5 | 30 | -0.52 | 0 | 10.5 | 11.02 |  |  |  | Nom. Capacity MV, МVA | 10+10 | 0.511 | 3.491 | 3.5 | 30 | -0.009 | 0 | 10.5 | 10.509
| Nom. capacity LV, МVA | 10+10 |  | 5.56 | 0 | 0 | 5.56 | 0 | 10.5 | 4.94 |  |  |  | Nom. capacity LV, МVA | 10+10 | 0.523 | 6.083 | 0 | 0 | 6.083 | 0 | 10.5 | 4.417
171 | SS 110/35/10 kV Dolgorukovo | 6,3+10 | 16.3 | 6.98 | 4 |  | 2.98 | 0 | 6.615 | 3.635 | 3.635 | open | 171 | SS 110/35/10 kV Dolgorukovo | 6,3+10 | 0.645 | 7.625 | 4 |  | 3.625 | 0 | 6.615 | 2.99 | 2.99 | open
| Nom. capacity MV, МVA | 6,3+10 |  | 4.25 | 4 | 45 | 0.25 | 0 | 6.615 | 6.365 |  |  |  | Nom. capacity MV, МVA | 6,3+10 | 0.458 | 4.708 | 4 | 45 | 0.708 | 0 | 6.615 | 5.907
| Nom. capacity LV, МVA | 6,3+10 |  | 2.73 | 0 | 0 | 2.73 | 0 | 6.615 | 3.885 |  |  |  | Nom. capacity LV, МVA | 6,3+10 | 0.187 | 2.917 | 0 | 0 | 2.917 | 0 | 6.615 | 3.698
172 | SS 110/35/10 kV Volovo | 10+10 | 20 | 2 | 0.89 |  | 1.11 | 0 | 10.5 | 9.39 | 9.39 | open | 172 | SS 110/35/10 kV Volovo | 10+10 | 0.164 | 2.164 | 0.89 |  | 1.274 | 0 | 10.5 | 9.226 | 9.226 | open
| Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 |  | 2 | 0.89 | 60 | 1.11 | 0 | 10.5 | 9.39 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.164 | 2.164 | 0.89 | 60 | 1.274 | 0 | 10.5 | 9.226
173 | SS 110/35/10 kV Izmalkovo | 10+10 | 20 | 10.18 | 1.2 |  | 8.98 | 0 | 10.5 | 1.52 | 1.52 | open | 173 | SS 110/35/10 kV Izmalkovo | 10+10 | 0.081 | 10.261 | 1.2 |  | 9.061 | 0 | 10.5 | 1.439 | 1.439 | open
| Nom. capacity MV, МVА | 10+10 |  | 6.29 | 1.2 | 30 | 5.09 | 0 | 10.5 | 5.41 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.03 | 6.32 | 1.2 | 30 | 5.12 | 0 | 10.5 | 5.38
| Nom. capacity LV, МVА | 10+10 |  | 3.89 | 0 | 0 | 3.89 | 0 | 10.5 | 6.61 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.051 | 3.941 | 0 | 0 | 3.941 | 0 | 10.5 | 6.559
174 | SS 110/35/10 kV Gorokhovskaya | 16+16 | 32 | 12.2 | 7.2 |  | 5 | 0 | 16.8 | 11.8 | 11.8 | open | 174 | SS 110/35/10 kV Gorokhovskaya | 16+16 | 2.088 | 14.288 | 7.2 |  | 7.088 | 0 | 16.8 | 9.712 | 9.712 | open
| Nom. capacity MV, МVА | 16+16 |  | 9 | 6 | 30 | 3 | 0 | 16.8 | 13.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.715 | 9.715 | 6 | 30 | 3.715 | 0 | 16.8 | 13.085
| Nom. capacity LV, МVА | 16+16 |  | 3.2 | 1.2 | 120 | 2 | 0 | 16.8 | 14.8 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.373 | 4.573 | 1.2 | 120 | 3.373 | 0 | 16.8 | 13.427
175 | SS 110/35/10 kV Donskaya | 10+10 | 20 | 4.65 | 4.89 |  | -0.24 | 0 | 10.5 | 10.74 | 8.44 | open | 175 | SS 110/35/10 kV Donskaya | 10+10 | 0.186 | 4.836 | 4.89 |  | -0.054 | 0 | 10.5 | 10.554 | 8.397 | open
| Nom. capacity MV, МVА | 10+10 |  | 1.7 | 4 | 30 | -2.3 | 0 | 10.5 | 12.8 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.143 | 1.843 | 4 | 30 | -2.157 | 0 | 10.5 | 12.657
| Nom. capacity LV, МVА | 10+10 |  | 2.95 | 0.89 | 120 | 2.06 | 0 | 10.5 | 8.44 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.043 | 2.993 | 0.89 | 120 | 2.103 | 0 | 10.5 | 8.397
176 | SS 110/35/10 kV Lebedyan | 16+16 | 32 | 11.78 | 9 |  | 2.78 | 0 | 16.8 | 14.02 | 12.69 | open | 176 | SS 110/35/10 kV Lebedyan | 16+16 | 1.505 | 13.285 | 9 |  | 4.285 | 0 | 16.8 | 12.515 | 12.23 | open
| Nom. capacity MV, МVА | 16+16 |  | 4.67 | 6 | 60 | -1.33 | 0 | 16.8 | 18.13 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.045 | 5.715 | 6 | 60 | -0.285 | 0 | 16.8 | 17.085
| Nom. capacity LV, МVА | 16+16 |  | 7.11 | 3 | 120 | 4.11 | 0 | 16.8 | 12.69 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.46 | 7.57 | 3 | 120 | 4.57 | 0 | 16.8 | 12.23
177 | SS 110/35/10 kV Chaplygin-novaya | 16+16 | 32 | 6.32 | 4.5 |  | 1.82 | 0 | 16.8 | 14.98 | 14.98 | open | 177 | SS 110/35/10 kV Chaplygin-novaya | 16+16 | 0.884 | 7.204 | 4.5 |  | 2.704 | 0 | 16.8 | 14.096 | 14.096 | open
| Nom. capacity MV, МVА | 16+16 |  | 2.83 | 2.5 | 20 | 0.33 | 0 | 16.8 | 16.47 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.768 | 3.598 | 2.5 | 20 | 1.098 | 0 | 16.8 | 15.702
| Nom. capacity LV, МVА | 16+16 |  | 3.49 | 2 | 100 | 1.49 | 0 | 16.8 | 15.31 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.116 | 3.606 | 2 | 100 | 1.606 | 0 | 16.8 | 15.194
178 | SS 110/35/10 kV Kompressornaya | 16+16 | 32 | 3.05 | 3.2 |  | -0.15 | 0 | 16.8 | 16.95 | 15.84 | open | 178 | SS 110/35/10 kV Kompressornaya | 16+16 | 0.2615 | 3.3115 | 3.2 |  | 0.1115 | 0 | 16.8 | 16.6885 | 15.764 | open
| Nom. Capacity MV, МVА | 16+16 |  | 1.09 | 2.2 | 20 | -1.11 | 0 | 16.8 | 17.91 |  |  |  | Nom. Capacity MV, МVА | 16+16 | 0.1855 | 1.2755 | 2.2 | 20 | -0.9245 | 0 | 16.8 | 17.7245
| Nom. capacity LV, МVА | 16+16 |  | 1.96 | 1 | 60 | 0.96 | 0 | 16.8 | 15.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.076 | 2.036 | 1 | 60 | 1.036 | 0 | 16.8 | 15.764
179 | SS 110/35/10 kV Rossiya | 16+16 | 32 | 4.8 | 3.8 |  | 1 | 0 | 16.8 | 15.8 | 15.8 | open | 179 | SS 110/35/10 kV Rossiya | 16+16 | 0.137 | 4.937 | 3.8 |  | 1.137 | 0 | 16.8 | 15.663 | 15.663 | open
| Nom. capacity MV, МVА | 16+16 |  | 3.93 | 3 | 60 | 0.93 | 0 | 16.8 | 15.87 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.129 | 4.059 | 3 | 60 | 1.059 | 0 | 16.8 | 15.741
| Nom. capacity LV, МVА | 16+16 |  | 0.87 | 0.8 | 100 | 0.07 | 0 | 16.8 | 16.73 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.008 | 0.878 | 0.8 | 100 | 0.078 | 0 | 16.8 | 16.722
180 | SS 110/35/10 kV Beryozovka | 16+10 | 26 | 1.45 | 3 |  | -1.55 | 0 | 10.5 | 12.05 | 9.6 | open | 180 | SS 110/35/10 kV Beryozovka | 16+10 | 0 | 1.45 | 3 |  | -1.55 | 0 | 10.5 | 12.05 | 9.6 | open
| Nom. capacity MV, МVА | 16+10 |  | 0.55 | 3 | 60 | -2.45 | 0 | 10.5 | 12.95 |  |  |  | Nom. capacity MV, МVА | 16+10 | 0 | 0.55 | 3 | 60 | -2.45 | 0 | 10.5 | 12.95
| Nom. capacity LV, МVА | 16+10 |  | 0.9 | 0 | 0 | 0.9 | 0 | 10.5 | 9.6 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0 | 0.9 | 0 | 0 | 0.9 | 0 | 10.5 | 9.6
181 | SS 110/35/10 kV Astapovo | 16+16 | 32 | 3.76 | 3 |  | 0.76 | 0 | 16.8 | 16.04 | 16.04 | open | 181 | SS 110/35/10 kV Astapovo | 16+16 | 0.146 | 3.906 | 3 |  | 0.906 | 0 | 16.8 | 15.894 | 15.894 | open
| Nom. capacity MV, МVА | 16+16 |  | 2.34 | 2 | 60 | 0.34 | 0 | 16.8 | 16.46 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.015 | 2.355 | 2 | 60 | 0.355 | 0 | 16.8 | 16.445
| Nom. capacity LV, МVА | 16+16 |  | 1.42 | 1 | 60 | 0.42 | 0 | 16.8 | 16.38 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.131 | 1.551 | 1 | 60 | 0.551 | 0 | 16.8 | 16.249
182 | SS 110/35/10 kV Khimicheskaya | 16+16 | 32 | 5.11 | 5.5 |  | -0.39 | 0 | 16.8 | 17.19 | 16.24 | open | 182 | SS 110/35/10 kV Khimicheskaya | 16+16 | 0.885 | 5.995 | 5.5 |  | 0.495 | 0 | 16.8 | 16.305 | 15.5 | open
| Nom. capacity MV, МVА | 16+16 |  | 5.06 | 4.5 | 60 | 0.56 | 0 | 16.8 | 16.24 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.74 | 5.8 | 4.5 | 60 | 1.3 | 0 | 16.8 | 15.5
| Nom. capacity LV, МVА | 16+16 |  | 0.05 | 1 | 60 | -0.95 | 0 | 16.8 | 17.75 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.145 | 0.195 | 1 | 60 | -0.805 | 0 | 16.8 | 17.605
183 | SS 110/35/6 kV Bugor | 15+15+25 | 55 | 32.14 | 0.5 |  | 31.64 | 1 | 31.5 | -1.14 | -1.14 | closed | 183 | SS 110/35/6 kV Bugor | 15+15+25 | 12.035 | 44.175 | 0.5 |  | 43.675 | 1 | 31.5 | -13.175 | -13.175 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.11 | 0 | 0 | 9.11 | 0 | 31.5 | 22.39 |  |  |  | Nom. capacity MV, МVА | 15+15+25 | 10.4 | 19.51 | 0 | 0 | 19.51 | 0 | 31.5 | 11.99
| Nom. capacity LV, МVА | 15+15+25 |  | 23.03 | 0.5 | 40 | 22.53 | 1 | 31.5 | 7.97 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 1.635 | 24.665 | 0.5 | 40 | 24.165 | 1 | 31.5 | 6.335
184 | SS 110/35/6 kVВ Tsementnaya | 63+32+20 | 115 | 30.55 | 0 |  | 30.55 | 0 | 54.6 | 24.05 | 9.14 | open | 184 | SS 110/35/6 kVВ Tsementnaya | 63+32+20 | 0.89 | 31.44 | 0 |  | 31.44 | 0 | 54.6 | 23.16 | 8.25 | open
| Nom. capacity MV, МVА | 63+20 |  | 11.86 | 0 | 0 | 11.86 | 0 | 21 | 9.14 |  |  |  | Nom. capacity MV, МVА | 63+20 | 0.89 | 12.75 | 0 | 0 | 12.75 | 0 | 21 | 8.25
| Nom. capacity LV, МVА | 63+32+20 |  | 18.69 | 0 | 30 | 18.69 | 0 | 54.6 | 35.91 |  |  |  | Nom. capacity LV, МVА | 63+32+20 | 0 | 18.69 | 0 | 30 | 18.69 | 0 | 54.6 | 35.91
185 | SS 110/35/10/60 kV Gidrooborudovanie | 25+25+31,5 | 81.5 | 16.78 | 2.5 |  | 14.28 | 0 | 52.5 | 38.22 | -5.97 | closed | 185 | SS 110/35/10/60 kV Gidrooborudovanie | 25+25+31,5 | 0.916 | 17.696 | 2.5 |  | 15.196 | 0 | 52.5 | 37.304 | -6.378 | closed
| Nom. capacity MV, МVА | 31.5 |  | 7.97 | 2 | 10 | 5.97 | 0 | 2 | -5.97 |  |  |  | Nom. capacity MV, МVА | 31.5 | 0.408 | 8.378 | 2 | 10 | 6.378 | 0 | 2 | -6.378
| Nom. capacity LV, МVА | 25+25 |  | 8.81 | 0.5 | 80 | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.508 | 9.318 | 0.5 | 80 | 8.818 | 0 | 26.25 | 17.432
186 | SS 110/35/10 kV Usman | 16+16 | 32 | 13.66 | 6.5 |  | 7.16 | 0 | 16.8 | 9.64 | 8.74 | open | 186 | SS 110/35/10 kV Usman | 16+16 | 0.522 | 14.182 | 6.5 |  | 7.682 | 0 | 16.8 | 9.118 | 8.39 | open
| Nom. capacity MV, МVА | 16+16 |  | 4.1 | 5 | 20 | -0.9 | 0 | 16.8 | 17.7 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.172 | 4.272 | 5 | 20 | -0.728 | 0 | 16.8 | 17.528
| Nom. Capacity LV, МVА | 16+16 |  | 9.56 | 1.5 | 100 | 8.06 | 0 | 16.8 | 8.74 |  |  |  | Nom. Capacity LV, МVА | 16+16 | 0.35 | 9.91 | 1.5 | 100 | 8.41 | 0 | 16.8 | 8.39
187 | SS 110/35/10 kV Aksai | 10+10 | 20 | 7.39 | 1.12 |  | 6.27 | 0 | 10.5 | 4.23 | 4.23 | open | 187 | SS 110/35/10 kV Aksai | 10+10 | 0.1045 | 7.4945 | 1.12 |  | 6.3745 | 0 | 10.5 | 4.1255 | 4.1255 | open
| Nom. Capacity MV, МVА | 10+10 |  | 5.11 | 0.5 | 20 | 4.61 | 0 | 10.5 | 5.89 |  |  |  | Nom. Capacity MV, МVА | 10+10 | 0.0855 | 5.1955 | 0.5 | 20 | 4.6955 | 0 | 10.5 | 5.8045
| Nom. capacity LV, МVА | 10+10 |  | 2.28 | 0.62 | 80 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.019 | 2.299 | 0.62 | 80 | 1.679 | 0 | 10.5 | 8.821
188 | SS 110/35/10 kV Nikolskaya | 6,3+6,3 | 12.6 | 4.05 | 3.34 |  | 0.71 | 0 | 6.615 | 5.905 | 5.905 | open | 188 | SS 110/35/10 kV Nikolskaya | 6,3+6,3 | 0.0555 | 4.1055 | 3.34 |  | 0.7655 | 0 | 6.615 | 5.8495 | 5.8495 | open
| Nom. capacity MV, МVА | 6,3+6,3 |  | 3.36 | 3 | 10 | 0.36 | 0 | 6.615 | 6.255 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.0505 | 3.4105 | 3 | 10 | 0.4105 | 0 | 6.615 | 6.2045
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.69 | 0.34 | 80 | 0.35 | 0 | 6.615 | 6.265 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.005 | 0.695 | 0.34 | 80 | 0.355 | 0 | 6.615 | 6.26
189 | SS 110/35/10 kV Khvorostyanka | 10+16 | 26 | 8.31 | 6.72 |  | 1.59 | 0 | 10.5 | 8.91 | 8.09 | open | 189 | SS 110/35/10 kV Khvorostyanka | 10+16 | 1.1885 | 9.4985 | 6.72 |  | 2.7785 | 0 | 10.5 | 7.7215 | 7.674 | open
| Nom. capacity MV, МVА | 10+16 |  | 5.68 | 6.5 | 20 | -0.82 | 0 | 10.5 | 11.32 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.7725 | 6.4525 | 6.5 | 20 | -0.0475 | 0 | 10.5 | 10.5475
| Nom. capacity LV, МVА | 10+16 |  | 2.63 | 0.22 | 80 | 2.41 | 0 | 10.5 | 8.09 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.416 | 3.046 | 0.22 | 80 | 2.826 | 0 | 10.5 | 7.674
190 | SS 110/35/10 kV Dobrinka | 16+10 | 26 | 8.56 | 5.68 |  | 2.88 | 0 | 10.5 | 7.62 | 7.62 | open | 190 | SS 110/35/10 kV Dobrinka | 16+10 | 0.134 | 8.694 | 5.68 |  | 3.014 | 0 | 10.5 | 7.486 | 7.486 | open
| Nom. capacity СН, МВА | 16+10 |  | 4.97 | 4 | 80 | 0.97 | 0 | 10.5 | 9.53 |  |  |  | Nom. capacity СН, МВА | 16+10 | 0.037 | 5.007 | 4 | 80 | 1.007 | 0 | 10.5 | 9.493
| Nom. capacity LV, МVА | 16+10 |  | 3.59 | 1.68 | 100 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.097 | 3.687 | 1.68 | 100 | 2.007 | 0 | 10.5 | 8.493
191 | SS 110/35/10 kV Verkhnyaya Matryonka | 6,3+6,3 | 12.6 | 1.58 | 0.4 |  | 1.18 | 0 | 6.615 | 5.435 | 5.435 | open | 191 | SS 110/35/10 kV Verkhnyaya Matryonka | 6,3+6,3 | 0.012 | 1.592 | 0.4 |  | 1.192 | 0 | 6.615 | 5.423 | 5.423 | open
| Nom. capacity MV, МVА | 6,3+6,3 |  | 0.87 | 0 | 0 | 0.87 | 0 | 6.615 | 5.745 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.012 | 0.882 | 0 | 0 | 0.882 | 0 | 6.615 | 5.733
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.71 | 0.4 | 90 | 0.31 | 0 | 6.615 | 6.305 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.71 | 0.4 | 90 | 0.31 | 0 | 6.615 | 6.305
192 | SS 110/35/10 kV Kazinka | 16+16 | 32 | 13.75 | 0 |  | 13.75 | 0 | 16.8 | 3.05 | 3.05 | open | 192 | SS 110/35/10 kV Kazinka | 16+16 | 2.426 | 16.176 | 0 |  | 16.176 | 0 | 16.8 | 0.624 | 0.624 | open
| Nom. capacity MV, МVА | 16+16 |  | 5.06 | 0 | 0 | 5.06 | 0 | 16.8 | 11.74 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.725 | 6.785 | 0 | 0 | 6.785 | 0 | 16.8 | 10.015
| Nom. capacity LV, МVА | 16+16 |  | 8.69 | 0 | 0 | 8.69 | 0 | 16.8 | 8.11 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.701 | 9.391 | 0 | 0 | 9.391 | 0 | 16.8 | 7.409
193 | SS 110/35/10 kV Dobroe | 16+16 | 32 | 10.68 | 3 |  | 7.68 | 0 | 16.8 | 9.12 | 9.12 | * | 193 | SS 110/35/10 kV Dobroe | 16+16 | 1.421 | 12.101 | 3 |  | 9.101 | 0 | 16.8 | 7.699 | 7.699 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.4 | 3 | 20 | 3.4 | 0 | 16.8 | 13.4 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.851 | 7.251 | 3 | 20 | 4.251 | 0 | 16.8 | 12.549
| Nom. capacity LV, МVА | 16+16 |  | 4.28 | 0 | 0 | 4.28 | 0 | 16.8 | 12.52 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.57 | 4.85 | 0 | 0 | 4.85 | 0 | 16.8 | 11.95
194 | SS 110/35/6 kV Novaya Derevnya | 10+6,3 | 16.3 | 8.05 | 5 |  | 3.05 | 0 | 6.615 | 3.565 | 3.565 | * | 194 | SS 110/35/6 kV Novaya Derevnya | 10+6,3 | 0.578 | 8.628 | 5 |  | 3.628 | 0 | 6.615 | 2.987 | 2.987 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 5.33 | 5 | 10 | 0.33 | 0 | 6.615 | 6.285 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.374 | 5.704 | 5 | 10 | 0.704 | 0 | 6.615 | 5.911
| Nom. capacity LV, МVА | 10+6,3 |  | 2.72 | 0 | 0 | 2.72 | 0 | 6.615 | 3.895 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.204 | 2.924 | 0 | 0 | 2.924 | 0 | 6.615 | 3.691
195 | SS 110/35/6 kV Verbilovo | 10+6,3 | 16.3 | 3.51 | 0 |  | 3.51 | 0 | 6.62 | 3.11 | 3.11 | * | 195 | SS 110/35/6 kV Verbilovo | 10+6,3 | 0.725 | 4.235 | 0 |  | 4.235 | 0 | 6.62 | 2.385 | 2.385 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 2.51 | 0 | 0 | 2.51 | 0 | 6.62 | 4.11 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.62 | 3.13 | 0 | 0 | 3.13 | 0 | 6.62 | 3.49
| Nom. capacity LV, МVА | 10+6,3 |  | 1 | 0 | 0 | 1 | 0 | 6.62 | 5.62 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.105 | 1.105 | 0 | 0 | 1.105 | 0 | 6.62 | 5.515
196 | SS 110/35/10 kV Khlevnoe | 16+16 | 32 | 11.16 | 0 |  | 11.16 | 0 | 16.8 | 5.64 | 5.64 | * | 196 | SS 110/35/10 kV Khlevnoe | 16+16 | 2.53 | 13.69 | 0 |  | 13.69 | 0 | 16.8 | 3.11 | 3.11 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.54 | 0 | 0 | 6.54 | 0 | 16.8 | 10.26 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.655 | 7.195 | 0 | 0 | 7.195 | 0 | 16.8 | 9.605
| Nom. capacity LV, МVА | 16+16 |  | 4.62 | 0 | 0 | 4.62 | 0 | 16.8 | 12.18 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.875 | 6.495 | 0 | 0 | 6.495 | 0 | 16.8 | 10.305
197 | SS 110/35/10 kV Naberezhnoe | 6,3+10 | 16.3 | 2.35 | 4.5 |  | -2.15 | 0 | 6.62 | 8.77 | 5.98 | open | 197 | SS 110/35/10 kV Naberezhnoe | 6,3+10 | 1.085 | 3.435 | 4.5 |  | -1.065 | 0 | 6.62 | 7.685 | 5.965 | open
| Nom. capacity MV, МVА | 6,3+10 |  | 1.71 | 4.5 | 10 | -2.79 | 0 | 6.62 | 9.41 |  |  |  | Nom. capacity MV, МVА | 6,3+10 | 1.07 | 2.78 | 4.5 | 10 | -1.72 | 0 | 6.62 | 8.34
| Nom. capacity LV, МVА | 6,3+10 |  | 0.64 | 0 | 0 | 0.64 | 0 | 6.62 | 5.98 |  |  |  | Nom. capacity LV, МVА | 6,3+10 | 0.015 | 0.655 | 0 | 0 | 0.655 | 0 | 6.62 | 5.965
198 | SS 110/35/10 kV Chaplygin | 7,5+6,3 | 13.8 | 4.4 | 4.5 |  | -0.1 | 0 | 6.62 | 6.72 | 6.62 | open | 198 | SS 110/35/10 kV Chaplygin | 7,5+6,3 | 0.102 | 4.502 | 4.5 |  | 0.002 | 0 | 6.62 | 6.618 | 6.618 | open
| Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 7,5+6,3 |  | 4.4 | 4.5 | 30 | -0.1 | 0 | 6.62 | 6.72 |  |  |  | Nom. capacity LV, МVА | 7,5+6,3 | 0.102 | 4.502 | 4.5 | 30 | 0.002 | 0 | 6.62 | 6.618
199 | SS 110/35/10 kV Troekurovo | 10+6,3 | 16.3 | 0.55 | 0.5 |  | 0.05 | 0 | 6.62 | 6.57 | 6.57 | open | 199 | SS 110/35/10 kV Troekurovo | 10+6,3 | 0.0045 | 0.5545 | 0.5 |  | 0.0545 | 0 | 6.62 | 6.5655 | 6.5655 | open
| Nom. capacity MV, МVА | 10+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.0045 | 0.0045 | 0 | 0 | 0.0045 | 0 | 6.62 | 6.6155
| Nom. capacity LV, МVА | 10+6,3 |  | 0.55 | 0.5 | 120 | 0.05 | 0 | 6.62 | 6.57 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0 | 0.55 | 0.5 | 120 | 0.05 | 0 | 6.62 | 6.57
| Total: | 2709.6 | 2709.6 | 650.7555 | [6 empty] | 789.5445 |  | 2: Total:; 3: 2709.6; 5: 852.281; Min 12: 602.306
| deficit | [9 empty] | -18.2024 |  | 2: deficit; Min 12: -32.8674
| proficit | [9 empty] | 559.647 | taken into account * | 2: proficit; Min 12: 401.9035; Min 13: taken into account *
* Ограничение на присоединяемую мощность по режиму работы сети 110, 220 кВ (по данным Липецкого РДУ)
Note on S31: krutko_eg: нагрузка 1 МВт, введена в сентябре