## Орел
Table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kV Almazovo | 2.5 | 0.49 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.34 | 0.34 | open | 1 | SS 35/10 kV Almazovo | 2.5 | 0.035 | 0.525 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.305 | 0.305 | open
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | open | 2 | SS 35/10 kV Voronets | 2.5 | 0 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | open
3 | SS 35/10 kV Gostoml | 2.5 | 0.79 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.81 | 0.81 | open | 3 | SS 35/10 kV Gostoml | 2.5 | 0.059 | 0.849 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.751 | 0.751 | open
4 | SS 35/10 kV Gubkino | 3.2 | 0.39 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.17 | 1.17 | open | 4 | SS 35/10 kV Gubkino | 3.2 | 0.014 | 0.404 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.156 | 1.156 | open
5 | SS 35/10 kV Devyatino | 1.6 | 0.21 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.5 | 0.5 | open | 5 | SS 35/10 kV Devyatino | 1.6 | 0.012 | 0.222 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.488 | 0.488 | open
6 | SS 35/10 kV Kamenka | 2.5 | 0.89 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.71 | 0.71 | open | 6 | SS 35/10 kV Kamenka | 2.5 | 0.025 | 0.915 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.685 | 0.685 | open
7 | SS 35/10 kV Kozminskaya | 2.5 | 0.33 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.96 | 0.96 | open | 7 | SS 35/10 kV Kozminskaya | 2.5 | 0.053 | 0.383 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.907 | 0.907 | open
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.23 | 6.14 | 60 | 1.91 | 0 | 6.14 | 1.91 | 0.04 | open | 8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 3.045 | 7.275 | 6.14 | 60 | 6.14 | 0 | 6.14 | -1.135 | -1.135 | closed
| Nom. capacity MV, MVA | 10 | 1.9 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.04 |  |  |  | Nom. capacity MV, MVA | 10 | 0.051 | 1.951 | 1.94 | 60 | 1.94 | 0 | 1.94 | -0.011
| Nom. capacity LV, MVA | 10 | 2.33 | 4.2 | 60 | 1.87 | 0 | 4.2 | 1.87 |  |  |  | Nom. capacity LV, MVA | 10 | 2.994 | 5.324 | 4.2 | 60 | 4.2 | 0 | 4.2 | -1.124
9 | SS 110/35/10 kV Novopolevo | 16 | 4.5 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.79 | -0.79 | closed | 9 | SS 110/35/10 kV Novopolevo | 16 | 0.663 | 5.163 | 3.71 | 30 | 3.71 | 0 | 3.71 | -1.453 | -1.453 | closed
| Nom. capacity MV, MVA | 16 | 3.2 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.248 | 3.448 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.848
| Nom. capacity LV, MVA | 16 | 1.3 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.19 |  |  |  | Nom. capacity LV, MVA | 16 | 0.415 | 1.715 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.605
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.51 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.82 | 0.82 | open | 10 | SS 35/10 kV Nikolskaya | 2.5 | 0.053 | 0.563 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.767 | 0.767 | open
11 | SS 35/10 kV Paramonovo | 1.8 | 0.34 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.14 | 0.14 | open | 11 | SS 35/10 kV Paramonovo | 1.8 | 0.081 | 0.421 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.059 | 0.059 | open
12 | SS 35/10 kV Senkovo | 1.6 | 0.42 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.87 | 0.87 | open | 12 | SS 35/10 kV Senkovo | 1.6 | 0.115 | 0.535 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.755 | 0.755 | open
13 | SS 35/10 kV Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | open | 13 | SS 35/10 kV Somovo | 2.5 | 0.004 | 0.344 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.616 | 0.616 | open
14 | SS 110/35/10 kV Trosna | 16 | 3.74 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.42 | -0.3 | closed | 14 | SS 110/35/10 kV Trosna | 16 | 0.826 | 4.566 | 4.16 | 45 | 4.16 | 0 | 4.16 | -0.406 | -0.406 | closed
| Nom. capacity MV, MVA | 16 | 2.66 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.012 | 2.672 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.312
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.814 | 1.894 | 1.8 | 45 | 1.8 | 0 | 1.8 | -0.094
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | open | 15 | SS 35/10 kV Shablykino | 5.6 | 0 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | open
16 | SS 35/10 kV Yuryevo | 2.5 | 0.17 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.9 | 0.9 | open | 16 | SS 35/10 kV Yuryevo | 2.5 | 0.029 | 0.199 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.871 | 0.871 | open
17 | SS 110/35/10 kV Region V | 10 | 4.48 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.92 | 0 | open | 17 | SS 110/35/10 kV Region V | 10 | 0.2 | 4.424 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.976 | 0.976 | open
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 |  |  |  | Nom. capacity LV, MVA | 10 | 0.384 | 4.424 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.976
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.79 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.085 | 0.085 | open | 18 | SS 110/10 kV Pishchevaya | 6.3 | 2.588 | 4.378 | 1.875 | 60 | 1.875 | 0 | 1.875 | -2.503 | -2.503 | closed
19 | SS 110/10 kV Telchye | 3.2 | 1.56 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.1 | -0.1 | closed | 19 | SS 110/10 kV Telchye | 3.2 | 0.054 | 1.614 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.154 | -0.154 | closed
20 | SS 110/10 kV B.Chern | 2.5 | 0.43 | 1 | 120 | 1 | 0 | 1 | 0.57 | 0.57 | open | 20 | SS 110/10 kV B.Chern | 2.5 | 0.256 | 0.686 | 1 | 120 | 1 | 0 | 1 | 0.314 | 0.314 | open
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.46 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.34 | 0.34 | open | 21 | SS 35/10 kV Bashkatovo | 1.6 | 0.018 | 0.478 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.322 | 0.322 | open
22 | SS 35/10 kV Vysokoe | 1.6 | 0.2 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.04 | 1.04 | open | 22 | SS 35/10 kV Vysokoe | 1.6 | 0.016 | 0.216 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.024 | 1.024 | open
23 | SS 35/10 kV Gladkoe | 2.5 | 0.32 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.14 | 1.14 | open | 23 | SS 35/10 kV Gladkoe | 2.5 | 0.018 | 0.338 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.122 | 1.122 | open
24 | SS 35/10 kV Lykovo | 2.5 | 0.72 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.52 | 0.52 | open | 24 | SS 35/10 kV Lykovo | 2.5 | 0.14 | 0.86 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.38 | 0.38 | open
25 | SS 35/6 kV Sugar mill | 4 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | open | 25 | SS 35/6 kV Sugar mill | 4 | 0 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | open
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.38 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.3 | 0.3 | open | 26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.014 | 0.394 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.286 | 0.286 | open
27 | SS 35/10 kV Koptevo | 2.5 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | open | 27 | SS 35/10 kV Koptevo | 2.5 | 0 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | open
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 | 0 | open | 28 | SS 110/35/10/6 kV Meat processing factory | 10 | 0.012 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221 | 0.221 | open
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 |  |  |  | Nom. capacity LV, MVA | 10 | 0.019 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221
29 | SS 110/35/10 kV Shatilovo | 10 | 1.21 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.52 | -0.52 | closed | 29 | SS 110/35/10 kV Shatilovo | 10 | 0.005 | 1.258 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.568 | -0.568 | closed
| Nom. capacity MV, MVA | 10 | 0.52 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.36 |  |  |  | Nom. capacity MV, MVA | 10 | 0.006 | 0.526 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.366
| Nom. capacity LV, MVA | 10 | 0.68 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.15 |  |  |  | Nom. capacity LV, MVA | 10 | 0.052 | 0.732 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.202
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.33 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.63 | 1.06 | open | 30 | SS 110/35/10 kV Sovkhoznaya | 10 | 1.849 | 5.189 | 8.96 | 120 | 8.96 | 0 | 8.96 | 3.771 | 0.985 | open
| Nom. capacity MV, MVA | 10 | 2.06 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.56 |  |  |  | Nom. capacity MV, MVA | 10 | 1.774 | 3.834 | 6.62 | 120 | 6.62 | 0 | 6.62 | 2.786
| Nom. capacity LV, MVA | 10 | 1.28 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.06 |  |  |  | Nom. capacity LV, MVA | 10 | 0.075 | 1.355 | 2.34 | 120 | 2.34 | 0 | 2.34 | 0.985
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | open | 31 | SS 35/10 kV Danilovskaya | 1.6 | 0 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | open
32 | SS 35/10 kV Korseevo | 1.8 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | open | 32 | SS 35/10 kV Korseevo | 1.8 | 0 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | open
33 | SS 35/10 kV Lipovets | 2.5 | 0.74 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.65 | 0.65 | open | 33 | SS 35/10 kV Lipovets | 2.5 | 0.316 | 1.056 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.334 | 0.334 | open
34 | SS 35/10 kV Misaylovo | 1.6 | 0.3 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.3 | 1.3 | open | 34 | SS 35/10 kV Misaylovo | 1.6 | 0 | 0.3 | 1.6 |  | 1.6 | 0 | 1.6 | 1.3 | 1.3 | open
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | open | 35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.009 | 0.269 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.041 | 0.041 | open
36 | SS 35/10 kV Pankovo | 1.8 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open | 36 | SS 35/10 kV Pankovo | 1.8 | 0.006 | 0.526 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.074 | 1.074 | open
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.65 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.95 | 0.95 | open | 37 | SS 35/10 kV Sudbishchi | 2.5 | 0.015 | 0.665 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.935 | 0.935 | open
38 | SS 35/10 kV Tim | 1.6 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open | 38 | SS 35/10 kV Tim | 1.6 | 0.006 | 0.526 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.074 | 1.074 | open
39 | SS 35/10 kV Topki | 1 | 0.19 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.41 | 1.41 | open | 39 | SS 35/10 kV Topki | 1 | 0.006 | 0.196 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.404 | 1.404 | open
40 | SS 35/10 kV Yarishche | 2.5 | 0.29 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.31 | 1.31 | open | 40 | SS 35/10 kV Yarishche | 2.5 | 0.032 | 0.322 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.278 | 1.278 | open
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.06 | 3.88 | 30 | 0.18 | 0 | 10.5 | 10.32 | 10.32 | open | 41 | SS 110/10 kV Alshanskaya | 10+10 | 0.414 | 4.474 | 3.88 | 30 | 0.594 | 0 | 10.5 | 9.906 | 9.906 | open
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | open | 42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.018 | 0.418 | 0.93 | 90 | -0.512 | 0 | 2.625 | 3.137 | 3.137 | open
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | open | 43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.376 | 1.076 | 0 |  | 1.076 | 0 | 1.68 | 0.604 | 0.604 | open
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.64 | 3.06 | 90 | -0.42 | 0 | 10.5 | 10.92 | 10.51 | open | 44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 0.763 | 3.403 | 3.06 | 90 | 0.343 | 0 | 10.5 | 10.157 | 10.157 | open
| Nom. capacity MV, MVA | 10+10 | 2.42 | 2.43 | 90 | -0.01 | 0 | 10.5 | 10.51 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.763 | 3.183 | 2.43 | 90 | 0.753 | 0 | 10.5 | 9.747
| Nom. capacity LV, MVA | 10+10 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 1.01 | 0.64 | 60 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open | 45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.048 | 1.058 | 0.64 | 60 | 0.418 | 0 | 1.68 | 1.262 | 1.262 | open
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.07 | 2.05 | 90 | 1.02 | 0 | 6.615 | 5.595 | 5.595 | open | 46 | SS 35/10 kV Biofactory | 6,3+6,3 | 0.518 | 3.588 | 2.05 | 90 | 1.538 | 0 | 6.615 | 5.077 | 5.077 | open
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.19 | 1.46 | 30 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | open | 47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 2.841 | 6.031 | 1.46 | 30 | 4.571 | 0 | 2.625 | -1.946 | -1.946 | closed
48 | SS 110/10 kV Vostochnaya | 15+15 | 13.63 | 5.87 | 120 | 7.76 | 0 | 15.75 | 7.99 | 7.99 | open | 48 | SS 110/10 kV Vostochnaya | 15+15 | 0.471 | 14.101 | 5.87 | 120 | 8.231 |  | 15.75 | 7.519 | 7.519 | open
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.26 | 0.45 | 60 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | open | 49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 0.196 | 3.456 | 0.45 | 60 | 3.006 | 0 | 10.5 | 7.494 | 7.494 | open
| Nom. capacity MV, MVA | 10+10 | 0.25 | 0 | 0 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.012 | 0.262 | 0 |  | 0.262 | 0 | 10.5 | 10.238
| Nom. capacity LV, MVA | 10+10 | 3.01 | 0.45 | 60 | 2.56 | 0 | 10.5 | 7.94 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.184 | 3.194 | 0.45 | 60 | 2.744 | 0 | 10.5 | 7.756
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.84 | 3.98 | 180 | 7.86 | 0 | 16.8 | 8.94 | 8.94 | open | 50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 0.306 | 12.146 | 3.98 | 180 | 8.166 | 0 | 16.8 | 8.634 | 8.634 | open
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.98 | 0.64 | 60 | 0.34 | 0 | 1.89 | 1.55 | 1.55 | open | 51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.018 | 0.998 | 0.64 | 60 | 0.358 | 0 | 1.89 | 1.532 | 1.532 | open
52 | SS 110/6 kV Zavodskaya | 40+25 | 11.83 | 4.39 | 150 | 7.44 | 0 | 26.25 | 18.81 | 18.81 | open | 52 | SS 110/6 kV Zavodskaya | 40+25 | 1.612 | 13.442 | 4.39 | 150 | 9.052 | 0 | 26.25 | 17.198 | 17.198 | open
53 | SS 110/6 kV Zapadnaya | 63+63 | 25.39 | 5.37 | 120 | 20.02 | 19 | 66.15 | 27.13 | 27.13 | open | 53 | SS 110/6 kV Zapadnaya | 63+63 | 15.235 | 40.625 | 5.37 | 120 | 35.255 | 19 | 66.15 | 11.895 | 11.895 | open
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.87 | 1.48 | 60 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | open | 54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 0.814 | 2.684 | 1.48 | 60 | 1.204 | 0 | 2.625 | 1.421 | 1.421 | open
55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.84 | 1.18 | 30 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | open | 55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.071 | 0.911 | 1.18 | 30 | -0.269 | 0 | 1.68 | 1.949 | 1.949 | open
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 5.59 | 1.44 | 90 | 4.15 | 0 | 10.5 | 6.35 | 6.35 | open | 56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 5.556 | 11.146 | 1.44 | 90 | 9.706 | 0 | 10.5 | 0.794 | 0.794 | open
| Nom. capacity MV, MVA | 10+10 | 1.76 | 1 | 90 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.76 | 1 | 90 | 0.76 | 0 | 10.5 | 9.74
| Nom. capacity LV, MVA | 10+10 | 3.83 | 0.44 | 90 | 3.39 | 0 | 10.5 | 7.11 |  |  |  | Nom. capacity LV, MVA | 10+10 | 5.556 | 9.386 | 0.44 | 90 | 8.946 | 0 | 10.5 | 1.554
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.68 | 6.83 | 45 | -0.15 | 0 | 16.8 | 16.95 | 15.28 | open | 57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.976 | 13.656 | 6.83 | 45 | 6.826 | 0 | 16.8 | 9.974 | 9.974 | open
| Nom. capacity MV, MVA | 16+16 | 3.33 | 5 | 45 | -1.67 | 0 | 16.8 | 18.47 |  |  |  | Nom. capacity MV, MVA | 16+16 | 6.408 | 9.738 | 5 | 45 | 4.738 | 0 | 16.8 | 12.062
| Nom. capacity LV, MVA | 16+16 | 3.35 | 1.83 | 45 | 1.52 | 0 | 16.8 | 15.28 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.568 | 3.918 | 1.83 | 45 | 2.088 | 0 | 16.8 | 14.712
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.63 | 0.95 | 30 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | open | 58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 0.012 | 1.642 | 0.95 | 30 | 0.692 | 0 | 2.625 | 1.933 | 1.933 | open
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | open | 59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.02 | 0.58 | 0 |  | 0.58 | 0 | 1.68 | 1.1 | 1.1 | open
60 | SS 35/10 kV Kutafino | 1,6+1,6 | 0.66 | 0.83 | 30 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | open | 60 | SS 35/10 kV Kutafino | 1,6+1,6 | 5.893 | 6.553 | 0.83 | 30 | 5.723 | 0 | 1.68 | -4.043 | -4.043 | closed
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.89 | 1.59 | 30 | -0.7 | 0 | 2.625 | 3.325 | 3.325 | open | 61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.092 | 0.982 | 1.59 | 30 | -0.608 | 0 | 2.625 | 3.233 | 3.233 | open
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.48 | 0.47 | 60 | 0.01 | 0 | 1.05 | 1.04 | 1.04 | open | 62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.02 | 0.5 | 0.47 | 60 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | open
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.33 | 0.99 | 90 | -0.66 | 0 | 1.89 | 2.55 | 2.55 | open | 63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.012 | 0.342 | 0.99 | 90 | -0.648 | 0 | 1.89 | 2.538 | 2.538 | open
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.47 | 1.7 | 30 | -1.23 | 0 | 5.88 | 7.11 | 7.11 | open | 64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0 | 0.47 | 1.7 | 30 | -1.23 | 0 | 5.88 | 7.11 | 7.11 | open
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 9.2 | 1.41 | 90 | 7.79 | 0 | 10.5 | 2.71 | 2.71 | open | 65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 0.941 | 10.141 | 1.41 | 90 | 8.731 | 0 | 10.5 | 1.769 | 1.769 | open
| Nom. capacity MV, MVA | 10+10 | 2.76 | 0.86 | 90 | 1.9 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.117 | 2.877 | 0.86 | 90 | 2.017 | 0 | 10.5 | 8.483
| Nom. capacity LV, MVA | 10+10 | 6.44 | 0.55 | 90 | 5.89 | 0 | 10.5 | 4.61 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.824 | 7.264 | 0.55 | 90 | 6.714 | 0 | 10.5 | 3.786
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.68 | 1.63 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | open | 66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.021 | 0.701 | 1.63 | 45 | -0.929 | 0 | 2.625 | 3.554 | 3.554 | open
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.52 | 0.73 | 60 | -0.21 | 0 | 1.68 | 1.89 | 1.89 | open | 67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.054 | 0.574 | 0.73 | 60 | -0.156 | 0 | 1.68 | 1.836 | 1.836 | open
68 | SS 35/10 kV Putimets | 2,5+2,5 | 1.31 | 1.53 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.175 | 1.485 | 1.53 | 90 | -0.045 | 0 | 2.625 | 2.67 | 2.67 | open
69 | SS 110/10 kV Pishchevaya | 40+25 | 5.38 | 2.22 | 60 | 3.16 | 0 | 26.25 | 23.09 | 23.09 | open | 69 | SS 110/10 kV Pishchevaya | 40+25 | 0.232 | 5.612 | 2.22 | 60 | 3.392 | 0 | 26.25 | 22.858 | 22.858 | open
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.43 | 0.65 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.016 | 0.446 | 0.65 | 90 | -0.204 | 0 | 2.625 | 2.829 | 2.829 | open
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.69 | 1.98 | 45 | 0.71 | 0 | 10.5 | 9.79 | 9.74 | open | 71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 0.711 | 3.401 | 1.98 | 45 | 1.421 | 0 | 10.5 | 9.079 | 9.079 | open
| Nom. capacity MV, MVA | 10+10 | 1.36 | 1.41 | 45 | -0.05 | 0 | 10.5 | 10.55 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.16 | 1.52 | 1.41 | 45 | 0.11 | 0 | 10.5 | 10.39
| Nom. capacity LV, MVA | 10+10 | 1.33 | 0.57 | 45 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.551 | 1.881 | 0.57 | 45 | 1.311 | 0 | 10.5 | 9.189
72 | SS 35/10 kV Streletskaya | 4+4 | 1.66 | 0.91 | 90 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | open | 72 | SS 35/10 kV Streletskaya | 4+4 | 1.481 | 3.141 | 0.91 | 90 | 2.231 | 0 | 4.2 | 1.969 | 1.969 | open
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 27.61 | 3.86 | 180 | 23.75 | 0 | 68.25 | 44.5 | 19.36 | open | 73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 8.486 | 28.766 | 3.86 | 180 | 24.906 | 0 | 68.25 | 43.344 | 17.214 | open
| Nom. capacity MV, MVA | 20+20 | 6.74 | 5.1 | 90 | 1.64 | 0 | 21 | 19.36 |  |  |  | Nom. capacity MV, MVA | 20+20 | 2.146 | 8.886 | 5.1 | 90 | 3.786 | 0 | 21 | 17.214
| Nom. capacity LV, MVA | 25+40 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72 |  |  |  | Nom. capacity LV, MVA | 25+40 | 0 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72
| SS 35/10 kV Soskovskaya | 20+20+40 | 13.54 | 3.86 | 180 | 9.68 | 0 | 42 | 32.32 |  |  |  | SS 35/10 kV Soskovskaya | 20+20+40 | 6.34 | 19.88 | 3.86 | 180 | 16.02 | 0 | 42 | 25.98
74 | SS 35/10 kV Trosna | 4+3,2 | 1.13 | 0.64 | 90 | 0.49 | 0 | 3.36 | 2.87 | 2.87 | open | 74 | SS 35/10 kV Trosna | 4+3,2 | 0.044 | 1.174 | 0.64 | 90 | 0.534 | 0 | 3.36 | 2.826 | 2.826 | open
75 | SS 110/10 kV Khimmash | 5,6+3,2 | 0.69 | 1.76 | 30 | -1.07 | 0 | 3.36 | 4.43 | 4.43 | open | 75 | SS 110/10 kV Khimmash | 5,6+3,2 | 0.029 | 0.719 | 1.76 | 30 | -1.041 | 0 | 3.36 | 4.401 | 4.401 | open
76 | SS 35/10kV Khleboprodukty | 25+25 | 6.32 | 1.51 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | open | 76 | SS 35/10kV Khleboprodukty | 25+25 | 7.694 | 14.014 | 1.51 | 120 | 12.504 | 0 | 26.25 | 13.746 | 13.746 | open
77 | SS 35/10 kV Khotynetskaya | 5,6+6,3 | 0.97 | 0 | - | 0.97 | 0 | 5.88 | 4.91 | 4.91 | open | 77 | SS 35/10 kV Khotynetskaya | 5,6+6,3 | 0 | 0.97 | 0 |  | 0.97 | 0 | 5.88 | 4.91 | 4.91 | open
78 | SS 35/10 kV Khotkovo | 4+2,5 | 2.2 | 1.49 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | open | 78 | SS 35/10 kV Khotkovo | 4+2,5 | 0.734 | 2.934 | 1.49 | 80 | 1.444 | 0 | 2.625 | 1.181 | 1.181 | open
79 | SS 110/10/6 kV Tsentralnaya | 1,6+1,6 | 0.58 | 1.03 | 80 | -0.45 | 0 | 1.68 | 2.13 | 2.13 | open | 79 | SS 110/10/6 kV Tsentralnaya | 1,6+1,6 | 0.064 | 0.644 | 1.03 | 80 | -0.386 | 0 | 1.68 | 2.066 | 2.066 | open
80 | SS 110/35/10 kV Shablykino | 25+25 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | open | 80 | SS 110/35/10 kV Shablykino | 25+25 | 0 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | open
81 | Nom. capacity MV, MVA | 6,3+6,3 | 2.68 | 1.36 | 30 | 1.32 | 0 | 6.615 | 5.295 | 5.295 | open | 81 | Nom. capacity MV, MVA | 6,3+6,3 | 0.077 | 2.757 | 1.36 | 30 | 1.397 | 0 | 6.615 | 5.218 | 5.218 | open
| Nom. capacity LV, MVA | 6,3+6,3 | 1.08 | 0.54 | 30 | 0.54 | 0 | 6.615 | 6.075 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.068 | 1.148 | 0.54 | 30 | 0.608 | 0 | 6.615 | 6.007
| SS 110/35/10 kV Shakhovo | 6,3+6,3 | 1.6 | 0.82 | 30 | 0.78 | 0 | 6.615 | 5.835 |  |  |  | SS 110/35/10 kV Shakhovo | 6,3+6,3 | 0.009 | 1.609 | 0.82 | 30 | 0.789 | 0 | 6.615 | 5.826
82 | Nom. capacity MV, MVA | 10+10 | 4.21 | 2.55 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | open | 82 | Nom. capacity MV, MVA | 10+10 | 0.446 | 4.656 | 2.55 | 120 | 2.106 | 0 | 10.5 | 8.394 | 8.394 | open
| Nom. capacity LV, MVA | 10+10 | 1.33 | 0.39 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.175 | 1.505 | 0.39 | 120 | 1.115 | 0 | 10.5 | 9.385
| SS 35/10 kV Shepino | 10+10 | 2.88 | 2.16 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | SS 35/10 kV Shepino | 10+10 | 0.271 | 3.151 | 2.16 | 120 | 0.991 | 0 | 10.5 | 9.509
83 | SS 110/10/6 kV Yugo-Vostochnaya | 2,5+1,6 | 1.6 | 1.1 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 83 | SS 110/10/6 kV Yugo-Vostochnaya | 2,5+1,6 | 0.338 | 1.938 | 1.1 | 120 | 0.838 | 0 | 1.68 | 0.842 | 0.842 | open
84 | SS 110/10 kV Yuzhnaya | 25+25 | 9.8 | 0.74 | 60 | 9.06 | 0 | 26.25 | 17.19 | 17.19 | open | 84 | SS 110/10 kV Yuzhnaya | 25+25 | 1.176 | 10.976 | 0.74 | 60 | 10.236 | 0 | 26.25 | 16.014 | 16.014 | open
85 | SS 220/110/10 kV Mtsensk | 10+10 | 7.42 | 1.05 | 90 | 6.37 | 0 | 10.5 | 4.13 | 4.13 | open | 85 | SS 220/110/10 kV Mtsensk | 10+10 | 1.444 | 8.864 | 1.05 | 90 | 7.814 | 0 | 10.5 | 2.686 | 2.686 | open
86 | SS 110/35/10 kV Kommash | 40+40 | 9.57 | 0 | - | 9.57 | 0 | 42 | 32.43 | 32.43 | open | 86 | SS 110/35/10 kV Kommash | 40+40 | 0.379 | 9.949 | 0 |  | 9.949 | 0 | 42 | 32.051 | 32.051 | open
87 | Nom. capacity MV, MVA | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 | 4.89 | open | 87 | Nom. capacity MV, MVA | 10+16 | 3.868 | 14.128 | 4.65 | 90 | 9.478 | 0 | 10.5 | 1.022 | 1.022 | open
| Nom. capacity LV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| SS 110/35/10 kV Novosergievka | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 |  |  |  | SS 110/35/10 kV Novosergievka | 10+16 | 3.868 | 14.128 | 4.65 | 90 | 9.478 | 0 | 10.5 | 1.022
88 | Nom. capacity MV, MVA | 6,3+10 | 1.84 | 4.13 | 120 | -2.29 | 0 | 6.615 | 8.905 | 7.365 | open | 88 | Nom. capacity MV, MVA | 6,3+10 | 0.254 | 2.064 | 4.13 | 120 | -2.066 | 0 | 6.615 | 8.681 | 7.111 | open
| Nom. capacity LV, MVA | 6,3+10 | 1.65 | 2.4 | 120 | -0.75 | 0 | 6.615 | 7.365 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0.254 | 1.904 | 2.4 | 120 | -0.496 | 0 | 6.615 | 7.111
| SS 110/10 kV 1 Voin | 6,3+10 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185 |  |  |  | SS 110/10 kV 1 Voin | 6,3+10 | 0 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185
89 | SS 110/35/10 kV Zalegoshch | 6,3+6,3 | 2.52 | 1.83 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | open | 89 | SS 110/35/10 kV Zalegoshch | 6,3+6,3 | 0.055 | 2.575 | 1.83 | 120 | 0.745 | 0 | 6.615 | 5.87 | 5.87 | open
90 | Nom. capacity MV, MVA | 10+16 | 6 | 3.95 | 120 | 2.05 | 0 | 10.5 | 8.45 | 8.45 | open | 90 | Nom. capacity MV, MVA | 10+16 | 0.145 | 6.145 | 3.95 | 120 | 2.195 | 0 | 10.5 | 8.305 | 8.305 | open
| Nom. capacity LV, MVA | 10+16 | 2.71 | 2.39 | 120 | 0.32 | 0 | 10.5 | 10.18 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.05 | 2.76 | 2.39 | 120 | 0.37 | 0 | 10.5 | 10.13
| SS 110/10 kV Kochety | 10+16 | 3.29 | 1.56 | 120 | 1.73 | 0 | 10.5 | 8.77 |  |  |  | SS 110/10 kV Kochety | 10+16 | 0.095 | 3.385 | 1.56 | 120 | 1.825 | 0 | 10.5 | 8.675
91 | SS 110/35/10 kV Bolkhov | 2,5+2,5 | 0.26 | 0.66 | 120 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | open | 91 | SS 110/35/10 kV Bolkhov | 2,5+2,5 | 0.011 | 0.271 | 0.66 | 120 | -0.389 | 0 | 2.625 | 3.014 | 3.014 | open
92 | Nom. capacity MV, MVA | 10+10 | 7.69 | 4.1 | 120 | 3.59 | 0 | 10.5 | 6.91 | 6.88 | open | 92 | Nom. capacity MV, MVA | 10+10 | 0.263 | 7.943 | 4.1 | 120 | 3.843 | 0 | 10.5 | 6.657 | 6.657 | open
| Nom. capacity LV, MVA | 10+10 | 2.41 | 2.45 | 120 | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.208 | 2.618 | 2.45 | 120 | 0.168 | 0 | 10.5 | 10.332
| SS 110/35/10 kV Novosil | 10+10 | 5.27 | 1.65 | 120 | 3.62 | 0 | 10.5 | 6.88 |  |  |  | SS 110/35/10 kV Novosil | 10+10 | 0.055 | 5.325 | 1.65 | 120 | 3.675 | 0 | 10.5 | 6.825
93 | Nom. capacity MV, MVA | 10+10 | 4.98 | 2.98 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | open | 93 | Nom. capacity MV, MVA | 10+10 | 0.1 | 5.12 | 2.98 | 120 | 2.14 | 0 | 10.5 | 8.36 | 8.36 | open
| Nom. capacity LV, MVA | 10+10 | 2.53 | 1.46 | 120 | 1.07 | 0 | 10.5 | 9.43 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.055 | 2.585 | 1.46 | 120 | 1.125 | 0 | 10.5 | 9.375
| SS 110/35/10 kV Znamenskaya | 10+10 | 2.49 | 1.52 | 120 | 0.97 | 0 | 10.5 | 9.53 |  |  |  | SS 110/35/10 kV Znamenskaya | 10+10 | 0.045 | 2.535 | 1.52 | 120 | 1.015 | 0 | 10.5 | 9.485
94 | Nom. capacity MV, MVA | 10+10 | 2.14 | 1.78 | 120 | 0.36 | 0 | 10.5 | 10.14 | 10.14 | open | 94 | Nom. capacity MV, MVA | 10+10 | 0.052 | 2.152 | 1.78 | 120 | 0.372 | 0 | 10.5 | 10.128 | 10.128 | open
| Nom. capacity LV, MVA | 10+10 | 0.39 | 0.34 | 120 | 0.05 | 0 | 10.5 | 10.45 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 0.39 | 0.34 | 120 | 0.05 | 0 | 10.5 | 10.45
| SS 35/10 kV Apalkovo | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | SS 35/10 kV Apalkovo | 10+10 | 0.052 | 1.762 | 1.44 | 120 | 0.322 | 0 | 10.5 | 10.178
95 | SS 35/10 kV Podberyozovo | 1,8+1,8 | 0.29 | 0.48 | 120 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | open | 95 | SS 35/10 kV Podberyozovo | 1,8+1,8 | 0.004 | 0.294 | 0.48 | 120 | -0.186 | 0 | 1.89 | 2.076 | 2.076 | open
96 | SS 35/10 kV Protasovo | 4+1 | 0.14 | 0.59 | 120 | -0.45 | 0 | 1.05 | 1.5 | 1.5 | open | 96 | SS 35/10 kV Protasovo | 4+1 | 0.016 | 0.156 | 0.59 | 120 | -0.434 | 0 | 1.05 | 1.484 | 1.484 | open
97 | SS 35/10 kV Alyoshnya | 2,5+1,6 | 0.54 | 0 |  | 0.54 | 0 | 1.68 | 1.14 | 1.14 | open | 97 | SS 35/10 kV Alyoshnya | 2,5+1,6 | 0.018 | 0.558 | 0 |  | 0.558 | 0 | 1.68 | 1.122 | 1.122 | open
98 | SS 35/10 kV Lomovoe | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | open | 98 | SS 35/10 kV Lomovoe | 1+1 | 0 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | open
99 | SS 35/10 kV Mokhovoe | 2,5+2,5 | 1.25 | 0 | - | 1.25 | 0 | 2.625 | 1.375 | 1.375 | open | 99 | SS 35/10 kV Mokhovoe | 2,5+2,5 | 0.023 | 1.273 | 0 |  | 1.273 | 0 | 2.625 | 1.352 | 1.352 | open
100 | SS 35/10 kV Mishkovo 2 | 2,5+4 | 0.89 | 0.63 | 120 | 0.26 |  | 2.625 | 2.365 | 2.365 | open | 100 | SS 35/10 kV Mishkovo 2 | 2,5+4 | 0.027 | 0.917 | 0.63 | 120 | 0.287 | 0 | 2.625 | 2.338 | 2.338 | open
101 | SS 35/10 kV Vyazovoe | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | open | 101 | SS 35/10 kV Vyazovoe | 1,6+1,6 | 0 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | open
102 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.33 | 0 | - | 0.33 | 0 | 2.625 | 2.295 | 2.295 | open | 102 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0 | 0.33 | 0 |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | open
103 | SS 35/10 kV Fatnevo | 2,5+2,5 | 0.66 | 0.67 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 103 | SS 35/10 kV Fatnevo | 2,5+2,5 | 0.152 | 0.812 | 0.67 | 120 | 0.142 | 0 | 2.625 | 2.483 | 2.483 | open
104 | SS 35/10 kV Varvarinka | 1,6+1,6 | 0.59 | 0.37 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open | 104 | SS 35/10 kV Varvarinka | 1,6+1,6 | 0.02 | 0.61 | 0.37 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | open
105 | SS 35/10 kV Odinok | 2,5+2,5 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 105 | SS 35/10 kV Odinok | 2,5+2,5 | 0 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open
106 | SS 35/10 kV Uzkoe | 1,6+1,6 | 0.36 | 0 | - | 0.36 | 0 | 1.68 | 1.32 | 1.32 | open | 106 | SS 35/10 kV Uzkoe | 1,6+1,6 | 0.039 | 0.399 | 0 |  | 0.399 | 0 | 1.68 | 1.281 | 1.281 | open
107 | SS 35/10 kV Korsakovo | 1,6+1 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open | 107 | SS 35/10 kV Korsakovo | 1,6+1 | 0 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open
108 | SS 35/10 kV Paramonovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 108 | SS 35/10 kV Paramonovo | 2,5+4 | 0.048 | 0.808 | 0.69 | 120 | 0.118 | 0 | 2.625 | 2.507 | 2.507 | open
109 | SS 35/10 kV Speshnevo | 4+2,5 | 1.06 | 0.76 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | open | 109 | SS 35/10 kV Speshnevo | 4+2,5 | 0.016 | 1.076 | 0.76 | 120 | 0.316 | 0 | 2.625 | 2.309 | 2.309 | open
110 | SS 110/35/10 kV Verkhovye I | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 110 | SS 110/35/10 kV Verkhovye I | 1,6+1,6 | 0.064 | 0.254 | 0 |  | 0.254 | 0 | 1.68 | 1.426 | 1.426 | open
111 | Nom. capacity MV, MVA | 16+10 | 7.34 | 3.65 | 120 | 3.69 | 0 | 10.5 | 6.81 | 6.81 | open | 111 | Nom. capacity MV, MVA | 16+10 | 0.203 | 7.543 | 3.65 | 120 | 3.893 | 0 | 10.5 | 6.607 | 6.607 | open
| Nom. capacity LV, MVA | 16+10 | 2.25 | 2.05 | 120 | 0.2 | 0 | 10.5 | 10.3 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.025 | 2.275 | 2.05 | 120 | 0.225 | 0 | 10.5 | 10.275
| SS 110/35/10 kV Verkhovye II | 16+10 | 5.09 | 1.6 | 120 | 3.49 | 0 | 10.5 | 7.01 |  |  |  | SS 110/35/10 kV Verkhovye II | 16+10 | 0.178 | 5.268 | 1.6 | 120 | 3.668 | 0 | 10.5 | 6.832
112 | Nom. capacity MV, MVA | 40+40 | 7.05 | 0.3 | - | 6.75 | 0 | 42 | 35.25 | 35.25 | open | 112 | Nom. capacity MV, MVA | 40+40 | 0.009 | 7.099 | 0.3 |  | 6.799 | 0 | 42 | 35.201 | 35.201 | open
| Nom. capacity LV, MVA | 40+40 | 0.37 | 0.3 | - | 0.07 | 0 | 42 | 41.93 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.009 | 0.379 | 0.3 |  | 0.079 | 0 | 42 | 41.921
| SS 110/35/10 kV Dolgoe | 40+40 | 6.72 | 0 | - | 6.72 | 0 | 42 | 35.28 |  |  |  | SS 110/35/10 kV Dolgoe | 40+40 | 0 | 6.72 | 0 |  | 6.72 | 0 | 42 | 35.28
113 | Nom. capacity MV, MVA | 16+10 | 4.82 | 3.38 | 120 | 1.44 | 0 | 10.5 | 9.06 | 8.55 | open | 113 | Nom. capacity MV, MVA | 16+10 | 0.071 | 4.891 | 3.38 | 120 | 1.511 | 0 | 10.5 | 8.989 | 8.497 | open
| Nom. capacity LV, MVA | 16+10 | 1.87 | 2.38 | 120 | -0.51 | 0 | 10.5 | 11.01 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.018 | 1.888 | 2.38 | 120 | -0.492 | 0 | 10.5 | 10.992
| SS 110/35/10 kV Kolpny-110 | 16+10 | 2.95 | 1 | 120 | 1.95 | 0 | 10.5 | 8.55 |  |  |  | SS 110/35/10 kV Kolpny-110 | 16+10 | 0.053 | 3.003 | 1 | 120 | 2.003 | 0 | 10.5 | 8.497
114 | Nom. capacity MV, MVA | 10+16 | 3.73 | 2.79 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.35 | open | 114 | Nom. capacity MV, MVA | 10+16 | 0.148 | 3.878 | 2.79 | 120 | 1.088 | 0 | 10.5 | 9.412 | 9.278 | open
| Nom. capacity LV, MVA | 10+16 | 2.25 | 2.46 | 120 | -0.21 | 0 | 10.5 | 10.71 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.076 | 2.326 | 2.46 | 120 | -0.134 | 0 | 10.5 | 10.634
| SS 110/35/10 kV Kr. Zarya | 10+16 | 1.48 | 0.33 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | SS 110/35/10 kV Kr. Zarya | 10+16 | 0.072 | 1.552 | 0.33 | 120 | 1.222 | 0 | 10.5 | 9.278
115 | Nom. capacity MV, MVA | 10+10 | 3.69 | 1.54 | 120 | 2.15 | 0 | 10.5 | 8.35 | 8.35 | open | 115 | Nom. capacity MV, MVA | 10+10 | 0.07 | 3.78 | 1.54 | 120 | 2.24 | 0 | 10.5 | 8.26 | 8.26 | open
| Nom. capacity LV, MVA | 10+10 | 1.6 | 1.29 | 120 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.024 | 1.624 | 1.29 | 120 | 0.334 | 0 | 10.5 | 10.166
| SS 110/35/10 kV Pokrovskaya | 10+10 | 2.11 | 0.25 | 120 | 1.86 | 0 | 10.5 | 8.64 |  |  |  | SS 110/35/10 kV Pokrovskaya | 10+10 | 0.046 | 2.156 | 0.25 | 120 | 1.906 | 0 | 10.5 | 8.594
116 | Nom. capacity MV, MVA | 10+10 | 5.36 | 2.84 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | open | 116 | Nom. capacity MV, MVA | 10+10 | 0.547 | 5.917 | 2.84 | 120 | 3.077 | 0 | 10.5 | 7.423 | 7.423 | open
| Nom. capacity LV, MVA | 10+10 | 2.47 | 2.12 | 120 | 0.35 | 0 | 10.5 | 10.15 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.187 | 2.657 | 2.12 | 120 | 0.537 | 0 | 10.5 | 9.963
| SS 110/35/6 kV Cherkasskaya | 10+10 | 2.9 | 0.72 | 120 | 2.18 | 0 | 10.5 | 8.32 |  |  |  | SS 110/35/6 kV Cherkasskaya | 10+10 | 0.36 | 3.26 | 0.72 | 120 | 2.54 | 0 | 10.5 | 7.96
117 | Nom. capacity MV, MVA | 40+25 | 21.65 | 13.39 | 120 | 8.26 | 0 | 26.25 | 17.99 | 17.99 | open | 117 | Nom. capacity MV, MVA | 40+25 | 3.63 | 25.3 | 13.39 | 120 | 11.91 | 0 | 26.25 | 14.34 | 14.34 | open
| Nom. capacity LV, MVA | 40+25 | 15.2 | 10.84 | 120 | 4.36 | 0 | 26.25 | 21.89 |  |  |  | Nom. capacity LV, MVA | 40+25 | 2.665 | 17.865 | 10.84 | 120 | 7.025 | 0 | 26.25 | 19.225
| SS 110/6 kV Plastmass | 40+25 | 6.47 | 2.55 | 120 | 3.92 | 0 | 26.25 | 22.33 |  |  |  | SS 110/6 kV Plastmass | 40+25 | 0.965 | 7.435 | 2.55 | 120 | 4.885 | 0 | 26.25 | 21.365
118 | SS 110/10 kV PM | 16+16 | 9.77 | 0 | - | 9.77 | 0 | 16.8 | 7.03 | 7.03 | open | 118 | SS 110/10 kV PM | 16+16 | 0 | 9.77 | 0 |  | 9.77 | 0 | 16.8 | 7.03 | 7.03 | open
119 | SS 110/10 kV Rechitsa | 10+10 | 3.48 | 0 | - | 3.48 | 0 | 10.5 | 7.02 | 7.02 | open | 119 | SS 110/10 kV Rechitsa | 10+10 | 0 | 3.48 | 0 |  | 3.48 | 0 | 10.5 | 7.02 | 7.02 | open
120 | SS 110/10 kV R.Brod | 6,3+6,3 | 0.95 | 1.85 | 120 | -0.9 | 0 | 6.615 | 7.515 | 7.515 | open | 120 | SS 110/10 kV R.Brod | 6,3+6,3 | 0.033 | 0.983 | 1.85 | 120 | -0.867 | 0 | 6.615 | 7.482 | 7.482 | open
121 | SS 35/10 kV Alekseevskaya | 5,6+10 | 1.6 | 0.29 | 120 | 1.31 | 0 | 5.88 | 4.57 | 4.57 | open | 121 | SS 35/10 kV Alekseevskaya | 5,6+10 | 0.135 | 1.735 | 0.29 | 120 | 1.445 | 0 | 5.88 | 4.435 | 4.435 | open
122 | SS 35/10 kV V.Dubrava | 1,6+1,6 | 0.63 | 0.13 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 122 | SS 35/10 kV V.Dubrava | 1,6+1,6 | 0.079 | 0.709 | 0.13 | 120 | 0.579 | 0 | 1.68 | 1.101 | 1.101 | open
123 | SS 35/10 kV V.Olshanoe | 2,5+2,5 | 0.85 | 0.65 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 123 | SS 35/10 kV V.Olshanoe | 2,5+2,5 | 0.061 | 0.911 | 0.65 | 120 | 0.261 | 0 | 2.625 | 2.364 | 2.364 | open
124 | SS 35/10 kV Vvedenskoe | 4+2,5 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 124 | SS 35/10 kV Vvedenskoe | 4+2,5 | 0 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open
125 | SS 35/10 kV Droskovo | 1,6+1,8 | 0.68 | 0.56 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open | 125 | SS 35/10 kV Droskovo | 1,6+1,8 | 0.027 | 0.707 | 0.56 | 120 | 0.147 | 0 | 1.68 | 1.533 | 1.533 | open
126 | SS 35/10 kV Kolpny-35 | 4+2,5 | 1.57 | 0 | - | 1.57 | 0 | 2.625 | 1.055 | 1.055 | open | 126 | SS 35/10 kV Kolpny-35 | 4+2,5 | 0.108 | 1.678 | 0 |  | 1.678 | 0 | 2.625 | 0.947 | 0.947 | open
127 | SS 35/10 kV Krutoe | 6,3+6,3 | 0.96 | 0.39 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | open | 127 | SS 35/10 kV Krutoe | 6,3+6,3 | 0.035 | 0.995 | 0.39 | 120 | 0.605 | 0 | 6.615 | 6.01 | 6.01 | open
128 | SS 35/10 kV Mezentsevo | 2,5+2,5 | 1.41 | 0.87 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open | 128 | SS 35/10 kV Mezentsevo | 2,5+2,5 | 0.126 | 1.536 | 0.87 | 120 | 0.666 | 0 | 2.625 | 1.959 | 1.959 | open
129 | SS 35/10 kV N.Zhernovets | 4+6,3 | 1.66 | 1.11 | 80 | 0.55 | 0 | 4.2 | 3.65 | 3.65 | open | 129 | SS 35/10 kV N.Zhernovets | 4+6,3 | 0.259 | 1.919 | 1.11 | 80 | 0.809 | 0 | 4.2 | 3.391 | 3.391 | open
130 | SS 35/10 kV Netrubezh | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 130 | SS 35/10 kV Netrubezh | 1,6+1,6 | 0.008 | 0.198 | 0 |  | 0.198 | 0 | 1.68 | 1.482 | 1.482 | open
131 | SS 35/10 kV Nikolskaya | 2,5+2,5 | 0.55 | 0.39 | - | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 131 | SS 35/10 kV Nikolskaya | 2,5+2,5 | 0 | 0.55 | 0.39 |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
132 | SS 35/10 kV Pesochnaya | 2,5+3,2 | 1.14 | 0.54 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open | 132 | SS 35/10 kV Pesochnaya | 2,5+3,2 | 0.066 | 1.206 | 0.54 | 80 | 0.666 | 0 | 2.625 | 1.959 | 1.959 | open
133 | SS 35/6 kV Pushkarskaya | 3,2+3,2 | 0.37 | 1.67 | 120 | -1.3 | 0 | 3.36 | 4.66 | 4.66 | open | 133 | SS 35/6 kV Pushkarskaya | 3,2+3,2 | 0.009 | 0.379 | 1.67 | 120 | -1.291 | 0 | 3.36 | 4.651 | 4.651 | open
134 | SS 35/10 kV Rakhmanovo | 4+4 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | closed | 134 | SS 35/10 kV Rakhmanovo | 4+4 | 0 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | closed
135 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open | 135 | SS 35/10 kV Rosstani | 2,5+2,5 | 0 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open
136 | SS 35/10 kV Sergievskaya | 2,5+2,5 | 0.97 | 0.7 | 80 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open | 136 | SS 35/10 kV Sergievskaya | 2,5+2,5 | 0.124 | 1.094 | 0.7 | 80 | 0.394 | 0 | 2.625 | 2.231 | 2.231 | open
137 | SS 35/10 kV Skorodnoe | 4+2,5 | 1.31 | 1.5 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | open | 137 | SS 35/10 kV Skorodnoe | 4+2,5 | 1.458 | 2.768 | 1.5 | 120 | 1.268 | 0 | 2.625 | 1.357 | 1.357 | open
138 | SS 35/10 kV Spasskaya | 1,6+1,6 | 0.3 | 0.33 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open | 138 | SS 35/10 kV Spasskaya | 1,6+1,6 | 0.025 | 0.325 | 0.33 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | open
139 | SS 35/10 kV SSK | 2,5+1,6 | 0.25 | 0 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | open | 139 | SS 35/10 kV SSK | 2,5+1,6 | 0.035 | 0.285 | 0 |  | 0.285 | 0 | 1.68 | 1.395 | 1.395 | open
140 | SS 35/10 kV Urynok | 1,6+1,6 | 0.07 | 0 |  | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 140 | SS 35/10 kV Urynok | 1,6+1,6 | 0.012 | 0.082 | 0 |  | 0.082 | 0 | 1.68 | 1.598 | 1.598 | open
141 | SS 35/10 kV Khomutovo | 1,6+1,6 | 0.84 | 0.52 | 20 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 141 | SS 35/10 kV Khomutovo | 1,6+1,6 | 0.012 | 0.852 | 0.52 | 20 | 0.332 | 0 | 1.68 | 1.348 | 1.348 | open
142 | Total: | 4+4 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | open | 142 | Total: | 4+4 | 0 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | open
| deficit | [10 empty] | 2: deficit; 4: 130.219; 5: 683.003
| proficit | [8 empty] | -2.51 |  | 2: proficit; Min 12: -13.008
| профицит | [8 empty] | 618.475 |  | 2: профицит; Min 12: 486.85

## Недозагрузка сктевых активов
Table 4
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | Supply Station Load, % | Supply Station Underload, MVA | The total maximum-allowed power of substation in n-1 mode | The total maximum-allowed power of substation | Installed capacity of supply centers of Orelenergo, S supply centers, MVA
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA
|  |  | MVA | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
1 | SS 35/10 kV Almazovo | 2.5 | 0.49 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.34 | 0.34 | open |  |  | 2.625 | 2.625 | 2.5
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | open |  |  | 2.625 | 2.625 | 2.5
3 | SS 35/10 kV Gostoml | 2.5 | 0.79 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.81 | 0.81 | open |  |  | 2.625 | 2.625 | 2.5
4 | SS 35/10 kV Gubkino | 3.2 | 0.39 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.17 | 1.17 | open |  |  | 3.36 | 3.36 | 3.2
5 | SS 35/10 kV Devyatino | 1.6 | 0.21 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.5 | 0.5 | open |  |  | 1.68 | 1.68 | 1.6
6 | SS 35/10 kV Kamenka | 2.5 | 0.89 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.71 | 0.71 | open |  |  | 2.625 | 2.625 | 2.5
7 | SS 35/10 kV Kozminskaya | 2.5 | 0.33 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.96 | 0.96 | open |  |  | 2.625 | 2.625 | 2.5
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.23 | 6.14 | 60 | 1.91 | 0 | 6.14 | 1.91 | 0.04 | open |  |  | 10.5 | 10.5 | 10
| Nom. capacity MV, MVA | 10 | 1.9 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.04
| Nom. capacity LV, MVA | 10 | 2.33 | 4.2 | 60 | 1.87 | 0 | 4.2 | 1.87
9 | SS 110/35/10 kV Novopolevo | 16 | 4.5 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.79 | -0.79 | closed |  |  | 16.8 | 16.8 | 16
| Nom. capacity MV, MVA | 16 | 3.2 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.6
| Nom. capacity LV, MVA | 16 | 1.3 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.19
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.51 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.82 | 0.82 | open |  |  | 2.625 | 2.625 | 2.5
11 | SS 35/10 kV Paramonovo | 1.8 | 0.34 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.14 | 0.14 | open |  |  | 1.89 | 1.89 | 1.8
12 | SS 35/10 kV Senkovo | 1.6 | 0.42 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.87 | 0.87 | open |  |  | 1.68 | 1.68 | 1.6
13 | SS 35/10 kV Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | open |  |  | 2.625 | 2.625 | 2.5
14 | SS 110/35/10 kV Trosna | 16 | 3.74 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.42 | -0.3 | closed |  |  | 16.8 | 16.8 | 16
| Nom. capacity MV, MVA | 16 | 2.66 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.3
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | open |  |  | 5.88 | 5.88 | 5.6
16 | SS 35/10 kV Yuryevo | 2.5 | 0.17 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.9 | 0.9 | open |  |  | 2.625 | 2.625 | 2.5
17 | SS 110/35/10 kV Region V | 10 | 4.48 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.92 | 0 | open |  |  | 10.5 | 10.5 | 10
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.79 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.085 | 0.085 | open |  |  | 6.615 | 6.615 | 6.3
19 | SS 110/10 kV Telchye | 3.2 | 1.56 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.1 | -0.1 | closed |  |  | 3.36 | 3.36 | 3.2
20 | SS 110/10 kV B.Chern | 2.5 | 0.43 | 1 | 120 | 1 | 0 | 1 | 0.57 | 0.57 | open |  |  | 2.625 | 2.625 | 2.5
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.46 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.34 | 0.34 | open |  |  | 1.68 | 1.68 | 1.6
22 | SS 35/10 kV Vysokoe | 1.6 | 0.2 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.04 | 1.04 | open |  |  | 1.68 | 1.68 | 1.6
23 | SS 35/10 kV Gladkoe | 2.5 | 0.32 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.14 | 1.14 | open |  |  | 2.625 | 2.625 | 2.5
24 | SS 35/10 kV Lykovo | 2.5 | 0.72 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.52 | 0.52 | open |  |  | 2.625 | 2.625 | 2.5
25 | SS 35/6 kV Sugar mill | 4 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | open |  |  | 4.2 | 4.2 | 4
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.38 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.3 | 0.3 | open |  |  | 1.68 | 1.68 | 1.6
27 | SS 35/10 kV Koptevo | 2.5 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | open |  |  | 2.625 | 2.625 | 2.5
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 | 0 | open |  |  | 10.5 | 10.5 | 10
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24
29 | SS 110/35/10 kV Shatilovo | 10 | 1.21 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.52 | -0.52 | closed |  |  | 10.5 | 10.5 | 10
| Nom. capacity MV, MVA | 10 | 0.52 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.36
| Nom. capacity LV, MVA | 10 | 0.68 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.15
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.33 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.63 | 1.06 | open |  |  | 10.5 | 10.5 | 10
| Nom. capacity MV, MVA | 10 | 2.06 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.56
| Nom. capacity LV, MVA | 10 | 1.28 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.06
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | open |  |  | 1.68 | 1.68 | 1.6
32 | SS 35/10 kV Korseevo | 1.8 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | open |  |  | 1.89 | 1.89 | 1.8
33 | SS 35/10 kV Lipovets | 2.5 | 0.74 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.65 | 0.65 | open |  |  | 2.625 | 2.625 | 2.5
34 | SS 35/10 kV Misaylovo | 1.6 | 0.3 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.3 | 1.3 | open |  |  | 1.68 | 1.68 | 1.6
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | open |  |  | 2.625 | 2.625 | 2.5
36 | SS 35/10 kV Pankovo | 1.8 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open |  |  | 1.89 | 1.89 | 1.8
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.65 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.95 | 0.95 | open |  |  | 2.625 | 2.625 | 2.5
38 | SS 35/10 kV Tim | 1.6 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open |  |  | 1.68 | 1.68 | 1.6
39 | SS 35/10 kV Topki | 1 | 0.19 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.41 | 1.41 | open |  |  | 1.05 | 1.05 | 1
40 | SS 35/10 kV Yarishche | 2.5 | 0.29 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.31 | 1.31 | open |  |  | 2.625 | 2.625 | 2.5
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.06 | 3.88 | 30 | 0.18 | 0 | 10.5 | 10.32 | 10.32 | open | 38.6667 | 6.44 | 10.5 | 21 | 20
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | open | 15.2381 | 2.225 | 2.625 | 5.25 | 5
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | open | 41.6667 | 0.98 | 1.68 | 4.305 | 4.1
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.64 | 3.06 | 90 | -0.42 | 0 | 10.5 | 10.92 | 10.51 | open | 25.1429 | 7.86 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 2.42 | 2.43 | 90 | -0.01 | 0 | 10.5 | 10.51
| Nom. capacity LV, MVA | 10+10 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 1.01 | 0.64 | 60 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open | 60.119 | 0.67 | 1.68 | 3.36 | 3.2
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.07 | 2.05 | 90 | 1.02 | 0 | 6.615 | 5.595 | 5.595 | open | 46.4097 | 3.545 | 6.615 | 13.23 | 12.6
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.19 | 1.46 | 30 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | open | 121.5238 | -0.565 | 2.625 | 9.24 | 8.8
48 | SS 110/10 kV Vostochnaya | 15+15 | 13.63 | 5.87 | 120 | 7.76 | 0 | 15.75 | 7.99 | 7.99 | open | 86.5397 | 2.12 | 15.75 | 31.5 | 30
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.26 | 0.45 | 60 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | open | 31.0476 | 7.24 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 0.25 | 0 | 0 | 0.25 | 0 | 10.5 | 10.25
| Nom. capacity LV, MVA | 10+10 | 3.01 | 0.45 | 60 | 2.56 | 0 | 10.5 | 7.94
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.84 | 3.98 | 180 | 7.86 | 0 | 16.8 | 8.94 | 8.94 | open | 70.4762 | 4.96 | 16.8 | 33.6 | 32
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.98 | 0.64 | 60 | 0.34 | 0 | 1.89 | 1.55 | 1.55 | open | 51.8519 | 0.91 | 1.89 | 3.78 | 3.6
52 | SS 110/6 kV Zavodskaya | 40+25 | 11.83 | 4.39 | 150 | 7.44 | 0 | 26.25 | 18.81 | 18.81 | open | 45.0667 | 14.42 | 26.25 | 68.25 | 65
53 | SS 110/6 kV Zapadnaya | 63+63 | 25.39 | 5.37 | 120 | 20.02 | 19 | 66.15 | 27.13 | 27.13 | open | 38.3825 | 21.76 | 47.15 | 132.3 | 126
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.87 | 1.48 | 60 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | open | 71.2381 | 0.755 | 2.625 | 5.25 | 5
55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.84 | 1.18 | 30 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | open | 50 | 0.84 | 1.68 | 5.04 | 4.8
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 5.59 | 1.44 | 90 | 4.15 | 0 | 10.5 | 6.35 | 6.35 | open | 53.2381 | 4.91 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 1.76 | 1 | 90 | 0.76 | 0 | 10.5 | 9.74
| Nom. capacity LV, MVA | 10+10 | 3.83 | 0.44 | 90 | 3.39 | 0 | 10.5 | 7.11
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.68 | 6.83 | 45 | -0.15 | 0 | 16.8 | 16.95 | 15.28 | open | 39.7619 | 10.12 | 16.8 | 33.6 | 32
| Nom. capacity MV, MVA | 16+16 | 3.33 | 5 | 45 | -1.67 | 0 | 16.8 | 18.47 | [6 empty] | 0
| Nom. capacity LV, MVA | 16+16 | 3.35 | 1.83 | 45 | 1.52 | 0 | 16.8 | 15.28 | [6 empty] | 0
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.63 | 0.95 | 30 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | open | 62.0952 | 0.995 | 2.625 | 5.25 | 5
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | open | 33.3333 | 1.12 | 1.68 | 3.57 | 3.4
60 | SS 35/10 kV Kutafino | 1,6+1,6 | 0.66 | 0.83 | 30 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | open | 39.2857 | 1.02 | 1.68 | 3.36 | 3.2
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.89 | 1.59 | 30 | -0.7 | 0 | 2.625 | 3.325 | 3.325 | open | 33.9048 | 1.735 | 2.625 | 5.25 | 5
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.48 | 0.47 | 60 | 0.01 | 0 | 1.05 | 1.04 | 1.04 | open | 45.7143 | 0.57 | 1.05 | 2.73 | 2.6
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.33 | 0.99 | 90 | -0.66 | 0 | 1.89 | 2.55 | 2.55 | open | 17.4603 | 1.56 | 1.89 | 4.515 | 4.3
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.47 | 1.7 | 30 | -1.23 | 0 | 5.88 | 7.11 | 7.11 | open | 7.9932 | 5.41 | 5.88 | 11.76 | 11.2
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 9.2 | 1.41 | 90 | 7.79 | 0 | 10.5 | 2.71 | 2.71 | open | 87.619 | 1.3 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 2.76 | 0.86 | 90 | 1.9 | 0 | 10.5 | 8.6 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 6.44 | 0.55 | 90 | 5.89 | 0 | 10.5 | 4.61 | [6 empty] | 0
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.68 | 1.63 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | open | 25.9048 | 1.945 | 2.625 | 8.505 | 8.1
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.52 | 0.73 | 60 | -0.21 | 0 | 1.68 | 1.89 | 1.89 | open | 30.9524 | 1.16 | 1.68 | 4.305 | 4.1
68 | SS 35/10 kV Putimets | 2,5+2,5 | 1.31 | 1.53 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 49.9048 | 1.315 | 2.625 | 5.25 | 5
69 | SS 110/10 kV Pishchevaya* | 40+25 | 5.38 | 2.22 | 60 | 3.16 | 0 | 26.25 | 23.09 | 23.09 | open | 20.4952
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.43 | 0.65 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 16.381 | 2.195 | 2.625 | 5.25 | 5
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.69 | 1.98 | 45 | 0.71 | 0 | 10.5 | 9.79 | 9.74 | open | 25.619 | 7.81 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 1.36 | 1.41 | 45 | -0.05 | 0 | 10.5 | 10.55 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 1.33 | 0.57 | 45 | 0.76 | 0 | 10.5 | 9.74 | [6 empty] | 0
72 | SS 35/10 kV Streletskaya | 4+4 | 1.66 | 0.91 | 90 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | open | 39.5238 | 2.54 | 4.2 | 8.4 | 8
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 27.61 | 3.86 | 180 | 23.75 | 0 | 68.25 | 44.5 | 19.36 | open | 40.4542 | 40.64 | 68.25 | 110.25 | 105
| Nom. capacity MV -35kV; MVA | 20+20 | 6.74 | 5.1 | 90 | 1.64 | 0 | 21 | 19.36
| Nom. capacity LV-10kV; MVA | 25+40 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72
| Nom. capacity LV-6kV; MVA | 20+20+40 | 13.54 | 3.86 | 180 | 9.68 | 0 | 42 | 32.32
74 | SS 35/10 kV Soskovskaya | 4+3,2 | 1.13 | 0.64 | 90 | 0.49 | 0 | 3.36 | 2.87 | 2.87 | open | 33.631 | 2.23 | 3.36 | 7.56 | 7.2
75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.69 | 1.76 | 30 | -1.07 | 0 | 3.36 | 4.43 | 4.43 | open | 20.5357 | 2.67 | 3.36 | 9.24 | 8.8
76 | SS 110/10 kV Khimmash | 25+25 | 6.32 | 1.51 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | open | 24.0762 | 19.93 | 26.25 | 52.5 | 50
77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.97 | 0 | - | 0.97 | 0 | 5.88 | 4.91 | 4.91 | open | 16.4966 | 4.91 | 5.88 | 12.495 | 11.9
78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 2.2 | 1.49 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | open | 83.8095 | 0.425 | 2.625 | 6.825 | 6.5
79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.58 | 1.03 | 80 | -0.45 | 0 | 1.68 | 2.13 | 2.13 | open | 34.5238 | 1.1 | 1.68 | 3.36 | 3.2
80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | open | 47.5429 | 13.77 | 26.25 | 52.5 | 50
81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 2.68 | 1.36 | 30 | 1.32 | 0 | 6.615 | 5.295 | 5.295 | open | 40.514 | 3.935 | 6.615 | 13.23 | 12.6
| Nom. capacity MV, MVA | 6,3+6,3 | 1.08 | 0.54 | 30 | 0.54 | 0 | 6.615 | 6.075 | [6 empty] | 0
| Nom. capacity LV, MVA | 6,3+6,3 | 1.6 | 0.82 | 30 | 0.78 | 0 | 6.615 | 5.835 | [6 empty] | 0
82 | SS 110/35/10 kV Shakhovo | 10+10 | 4.21 | 2.55 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | open | 40.0952 | 6.29 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 1.33 | 0.39 | 120 | 0.94 | 0 | 10.5 | 9.56 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 2.88 | 2.16 | 120 | 0.72 | 0 | 10.5 | 9.78 | [6 empty] | 0
83 | SS 35/10 kV Shepino | 2,5+1,6 | 1.6 | 1.1 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 95.2381 | 0.08 | 1.68 | 4.305 | 4.1
84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 9.8 | 0.74 | 60 | 9.06 | 0 | 26.25 | 17.19 | 17.19 | open | 37.3333 | 16.45 | 26.25 | 52.5 | 50
85 | SS 110/10 kV Yuzhnaya | 10+10 | 7.42 | 1.05 | 90 | 6.37 | 0 | 10.5 | 4.13 | 4.13 | open | 70.6667 | 3.08 | 10.5 | 21 | 20
86 | SS 220/110/10 kV Mtsensk | 40+40 | 9.57 | 0 | - | 9.57 | 0 | 42 | 32.43 | 32.43 | open | 22.7857
87 | SS 110/35/10 kV Kommash | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 | 4.89 | open | 97.7143 | 0.24 | 10.5 | 27.3 | 26
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 | [6 empty] | 0
88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 1.84 | 4.13 | 120 | -2.29 | 0 | 6.615 | 8.905 | 7.365 | open | 27.8156 | 4.775 | 6.615 | 17.115 | 16.3
| Nom. capacity MV, MVA | 6,3+10 | 1.65 | 2.4 | 120 | -0.75 | 0 | 6.615 | 7.365 | [6 empty] | 0
| Nom. capacity LV, MVA | 6,3+10 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185 | [6 empty] | 0
89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 2.52 | 1.83 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | open | 38.0952 | 4.095 | 6.615 | 13.23 | 12.6
90 | SS 110/35/10 kV Zalegoshch | 10+16 | 6 | 3.95 | 120 | 2.05 | 0 | 10.5 | 8.45 | 8.45 | open | 57.1429 | 4.5 | 10.5 | 27.3 | 26
| Nom. capacity MV, MVA | 10+16 | 2.71 | 2.39 | 120 | 0.32 | 0 | 10.5 | 10.18 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+16 | 3.29 | 1.56 | 120 | 1.73 | 0 | 10.5 | 8.77 | [6 empty] | 0
91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.26 | 0.66 | 120 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | open | 9.9048 | 2.365 | 2.625 | 5.25 | 5
92 | SS 110/35/10 kV Bolkhov | 10+10 | 7.69 | 4.1 | 120 | 3.59 | 0 | 10.5 | 6.91 | 6.88 | open | 73.2381 | 2.81 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 2.41 | 2.45 | 120 | -0.04 | 0 | 10.5 | 10.54 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 5.27 | 1.65 | 120 | 3.62 | 0 | 10.5 | 6.88 | [6 empty] | 0
93 | SS 110/35/10 kV Novosil | 10+10 | 4.98 | 2.98 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | open | 47.4286 | 5.52 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 2.53 | 1.46 | 120 | 1.07 | 0 | 10.5 | 9.43 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 2.49 | 1.52 | 120 | 0.97 | 0 | 10.5 | 9.53 | [6 empty] | 0
94 | SS 110/35/10 kV Znamenskaya | 10+10 | 2.14 | 1.78 | 120 | 0.36 | 0 | 10.5 | 10.14 | 10.14 | open | 20.381 | 8.36 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 0.39 | 0.34 | 120 | 0.05 | 0 | 10.5 | 10.45 | [6 empty] | 0
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 | [6 empty] | 0
95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.29 | 0.48 | 120 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | open | 15.3439 | 1.6 | 1.89 | 3.78 | 3.6
96 | SS 35/10 kV Podberyozovo | 4+1 | 0.14 | 0.59 | 120 | -0.45 | 0 | 1.05 | 1.5 | 1.5 | open | 13.3333 | 0.91 | 1.05 | 5.25 | 5
97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0.54 | 0 |  | 0.54 | 0 | 1.68 | 1.14 | 1.14 | open | 32.1429 | 1.14 | 1.68 | 4.305 | 4.1
98 | SS 35/10 kV Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | open | 32.381 | 0.71 | 1.05 | 2.1 | 2
99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 1.25 | 0 | - | 1.25 | 0 | 2.625 | 1.375 | 1.375 | open | 47.619 | 1.375 | 2.625 | 5.25 | 5
100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.89 | 0.63 | 120 | 0.26 |  | 2.625 | 2.365 | 2.365 | open | 33.9048 | 1.735 | 2.625 | 6.825 | 6.5
101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | open | 13.6905 | 1.45 | 1.68 | 3.36 | 3.2
102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.33 | 0 | - | 0.33 | 0 | 2.625 | 2.295 | 2.295 | open | 12.5714 | 2.295 | 2.625 | 5.25 | 5
103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.66 | 0.67 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 25.1429 | 1.965 | 2.625 | 5.25 | 5
104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.59 | 0.37 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open | 35.119 | 1.09 | 1.68 | 3.36 | 3.2
105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 22.8571 | 2.025 | 2.625 | 5.25 | 5
106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.36 | 0 | - | 0.36 | 0 | 1.68 | 1.32 | 1.32 | open | 21.4286 | 1.32 | 1.68 | 3.36 | 3.2
107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open | 17.1429 | 0.87 | 1.05 | 2.73 | 2.6
108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 28.9524 | 1.865 | 2.625 | 6.825 | 6.5
109 | SS 35/10 kV Paramonovo | 4+2,5 | 1.06 | 0.76 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | open | 40.381 | 1.565 | 2.625 | 6.825 | 6.5
110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 11.3095 | 1.49 | 1.68 | 3.36 | 3.2
111 | SS 110/35/10 kV Verkhovye I | 16+10 | 7.34 | 3.65 | 120 | 3.69 | 0 | 10.5 | 6.81 | 6.81 | open | 69.9048 | 3.16 | 10.5 | 27.3 | 26
| Nom. capacity MV, MVA | 16+10 | 2.25 | 2.05 | 120 | 0.2 | 0 | 10.5 | 10.3 | [6 empty] | 0
| Nom. capacity LV, MVA | 16+10 | 5.09 | 1.6 | 120 | 3.49 | 0 | 10.5 | 7.01 | [6 empty] | 0
112 | SS 110/35/10 kV Verkhovye II | 40+40 | 7.05 | 0.3 | - | 6.75 | 0 | 42 | 35.25 | 35.25 | open | 16.7857 | 34.95 | 42 | 84 | 80
| Nom. capacity MV, MVA | 40+40 | 0.37 | 0.3 | - | 0.07 | 0 | 42 | 41.93
| Nom. capacity LV, MVA | 40+40 | 6.72 | 0 | - | 6.72 | 0 | 42 | 35.28
113 | SS 110/35/10 kV Dolgoe | 16+10 | 4.82 | 3.38 | 120 | 1.44 | 0 | 10.5 | 9.06 | 8.55 | open | 45.9048 | 5.68 | 10.5 | 27.3 | 26
| Nom. capacity MV, MVA | 16+10 | 1.87 | 2.38 | 120 | -0.51 | 0 | 10.5 | 11.01
| Nom. capacity LV, MVA | 16+10 | 2.95 | 1 | 120 | 1.95 | 0 | 10.5 | 8.55
114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 3.73 | 2.79 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.35 | open | 35.5238 | 6.77 | 10.5 | 27.3 | 26
| Nom. capacity MV, MVA | 10+16 | 2.25 | 2.46 | 120 | -0.21 | 0 | 10.5 | 10.71
| Nom. capacity LV, MVA | 10+16 | 1.48 | 0.33 | 120 | 1.15 | 0 | 10.5 | 9.35
115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 3.69 | 1.54 | 120 | 2.15 | 0 | 10.5 | 8.35 | 8.35 | open | 35.1429 | 6.81 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 1.6 | 1.29 | 120 | 0.31 | 0 | 10.5 | 10.19
| Nom. capacity LV, MVA | 10+10 | 2.11 | 0.25 | 120 | 1.86 | 0 | 10.5 | 8.64
116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 5.36 | 2.84 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | open | 51.0476 | 5.14 | 10.5 | 21 | 20
| Nom. capacity MV, MVA | 10+10 | 2.47 | 2.12 | 120 | 0.35 | 0 | 10.5 | 10.15
| Nom. capacity LV, MVA | 10+10 | 2.9 | 0.72 | 120 | 2.18 | 0 | 10.5 | 8.32
117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 21.65 | 13.39 | 120 | 8.26 | 0 | 26.25 | 17.99 | 17.99 | open | 82.4762 | 4.6 | 26.25 | 68.25 | 65
| Nom. capacity MV, MVA | 40+25 | 15.2 | 10.84 | 120 | 4.36 | 0 | 26.25 | 21.89
| Nom. capacity LV, MVA | 40+25 | 6.47 | 2.55 | 120 | 3.92 | 0 | 26.25 | 22.33
118 | SS 110/6 kV Plastmass | 16+16 | 9.77 | 0 | - | 9.77 | 0 | 16.8 | 7.03 | 7.03 | open | 58.1548 | 7.03 | 16.8 | 33.6 | 32
119 | SS 110/10 kV PM | 10+10 | 3.48 | 0 | - | 3.48 | 0 | 10.5 | 7.02 | 7.02 | open | 33.1429 | 7.02 | 10.5 | 21 | 20
120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.95 | 1.85 | 120 | -0.9 | 0 | 6.615 | 7.515 | 7.515 | open | 14.3613 | 5.665 | 6.615 | 13.23 | 12.6
121 | SS 110/10 kV R.Brod | 5,6+10 | 1.6 | 0.29 | 120 | 1.31 | 0 | 5.88 | 4.57 | 4.57 | open | 27.2109 | 4.28 | 5.88 | 16.38 | 15.6
122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.63 | 0.13 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 37.5 | 1.05 | 1.68 | 3.36 | 3.2
123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.85 | 0.65 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 32.381 | 1.775 | 2.625 | 5.25 | 5
124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 19.8095 | 2.105 | 2.625 | 6.825 | 6.5
125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.68 | 0.56 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open | 40.4762 | 1 | 1.68 | 3.57 | 3.4
126 | SS 35/10 kV Droskovo | 4+2,5 | 1.57 | 0 | - | 1.57 | 0 | 2.625 | 1.055 | 1.055 | open | 59.8095 | 1.055 | 2.625 | 6.825 | 6.5
127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.96 | 0.39 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | open | 14.5125 | 5.655 | 6.615 | 13.23 | 12.6
128 | SS 35/10 kV Krutoe | 2,5+2,5 | 1.41 | 0.87 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open | 53.7143 | 1.215 | 2.625 | 5.25 | 5
129 | SS 35/10 kV Mezentsevo | 4+6,3 | 1.66 | 1.11 | 80 | 0.55 | 0 | 4.2 | 3.65 | 3.65 | open | 39.5238 | 2.54 | 4.2 | 10.815 | 10.3
130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 11.3095 | 1.49 | 1.68 | 3.36 | 3.2
131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.55 | 0.39 | - | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 20.9524 | 2.075 | 2.625 | 5.25 | 5
132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 1.14 | 0.54 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open | 43.4286 | 1.485 | 2.625 | 5.985 | 5.7
133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.37 | 1.67 | 120 | -1.3 | 0 | 3.36 | 4.66 | 4.66 | open | 11.0119 | 2.99 | 3.36 | 6.72 | 6.4
134 | SS 35/6 kV Pushkarskaya | 4+4 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | closed | 119.0476 | -0.8 | 4.2 | 8.4 | 8
135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open | 24.7619 | 1.975 | 2.625 | 5.25 | 5
136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.97 | 0.7 | 80 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open | 36.9524 | 1.655 | 2.625 | 5.25 | 5
137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.31 | 1.5 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | open | 49.9048 | 1.315 | 2.625 | 6.825 | 6.5
138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.3 | 0.33 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open | 17.8571 | 1.38 | 1.68 | 3.36 | 3.2
139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.25 | 0 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | open | 14.881 | 1.43 | 1.68 | 4.305 | 4.1
140 | SS 35/10 kV SSK | 1,6+1,6 | 0.07 | 0 |  | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 4.1667 | 1.61 | 1.68 | 3.36 | 3.2
141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.84 | 0.52 | 20 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 50 | 0.84 | 1.68 | 3.36 | 3.2
142 | SS 35/10 kV Khomutovo | 4+4 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | open | 46.6667 | 2.24 | 4.2 | 8.4 | 8
Total:
| deficit | [8 empty] | -2.51
| proficit | [8 empty] | 618.475
| total underload in the current month | [10 empty] | 38.6592 | 419.995 | 921.905 | 1792.875 | 1707.5
| Underload percentage in the current month | [12 empty] | 45.5573 | 23.4258
| total underload in the previous month | [12 empty] | 46.605
| Underload percentage in the previous month | [12 empty] | 2.248
Decrease of network assests underload
| Capacity deficit in nodes | [14 empty] | 0.147

## Сводтек.деф.
The list of closed supply centers of IDGC of Centre - Orelenergo division with winter load (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA | [5 empty] | Current deficit, MVA
Orelenergo
1 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | -0.79
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
2 | SS 110/35/10 kV Trosna | 16 | [6 empty] | -0.3
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.1
4 | SS 35/6 kV Pushkarskaya | 4+4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.8
5 | SS 110/35/10 kV Shatilovo | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.52
| Nom. capacity MV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Nom. capacity LV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total current deficit | [8 empty] | -2.51

## Свод.ожид.деф.
The list of closed supply centers of IDGC of Centre - Orelenergo division with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 4 | 5
Orelenergo
1 | SS 110/35/10 kV Maloarkhangelskaya | 10 | [6 empty] | #REF! |  | -1.135
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
2 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | #REF! |  | -1.453
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Pishchevaya | 6.3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -2.503
4 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.154
5 | SS 110/35/10 kV Shatilovo | 10 | [6 empty] | #REF! |  | -0.568
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
6 | SS 110/10 kV Volodarskaya | 2,5+6,3 | [8 empty] | -1.946
7 | SS 35/10 kV Kutafino | 1,6+1,6 | [8 empty] | -4.043
8 | SS 35/6 kV Pushkarskaya | 4+4 | [8 empty] | -0.8
9 | SS 110/35/10 kV Trosna | 16 | [8 empty] | -0.406
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
| Total: | [9 empty] | -13.008