## ярославль
[9 empty] | table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Дефицит/профицит ЦП, МВА |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Deficit /proficit of main substation, MVA
|  |  |  | МВА | Мин. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 0.35 | 0.837 | 1 сутки | 0.837 | 0 | 0.837 | 0.487 | 0.487 | opened | 1 | SS 35/10 Matveevo | 1.6 | 0.025 | 0.375 | 0.837 | 1 сутки | 0.837 | 0 | 0.837 | 0.462 | 0.462 | opened
2 | SS 35/10 Mikhailovskoe | 6.3 | 1.34 | 6.62 | 1 сутки | 6.62 | 0 | 6.62 | 5.28 | 5.28 | opened | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.343 | 6.62 | 1 сутки | 6.62 | 0 | 6.62 | 5.277 | 5.277 | opened
3 | SS 35/10 Shirinye | 2.5 | 2.56 | 0.762 | 1 сутки | 0.762 | 0 | 0.762 | -1.798 | -1.798 | closed | 3 | SS 35/10 Shirinye | 2.5 | 0.259 | 2.819 | 0.762 | 1 сутки | 0.762 | 0 | 0.762 | -2.057 | -2.057 | closed
4 | SS 110/10 Pokrov | 2.5 | 0.29 | 0.945 | 1 сутки | 0.945 | 0 | 0.945 | 0.655 | 0.655 | opened | 4 | SS 110/10 Pokrov | 2.5 | 0.025 | 0.315 | 0.945 | 1 сутки | 0.945 | 0 | 0.945 | 0.63 | 0.63 | opened
5 | SS 35/10 Obnora | 1.6 | 0.4 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.7 | 0.7 | opened | 5 | SS 35/10 Obnora | 1.6 | 0.045 | 0.445 | 1.1 | 1 сутки | 1.1 | 0 | 1.1 | 0.655 | 0.655 | opened
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 11.1 |  |  | 11.1 | 0 | 10.5 | -0.6 | -0.6 | closed | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 16.0176 |  |  | 16.0176 | 0 | 10.5 | -5.5176 | -5.5176 | closed
| Nom. capacity MV, МVА | 10+10 | 8.84 |  |  | 8.84 | 0 | 10.5 | 1.66 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 13.4179; Мин. 8: 13.4179; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: -2.9179
| Nom. capacity LV, МVА | 10+10 | 2.26 |  |  | 2.26 | 0 | 10.5 | 8.24 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.3397 | 2.5997 |  |  | 2.5997 | 0 | 10.5 | 7.9003
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.49 |  |  | 1.49 | 0 | 1.68 | 0.19 | 0.19 | opened | 7 | SS 35/10 Ananyino | 1,6+1,6 | 1.079 | 2.569 |  |  | 2.569 | 0 | 1.68 | -0.889 | -0.889 | closed
8 | SS 110/10/10 Bragino | 40+40 | 35.09 | 1.937 | 120 | 33.153 | 0 | 42 | 8.847 | 8.847 | opened | 8 | SS 110/10/10 Bragino | 40+40 | 6.6167 | 41.7067 | 1.937 | 120 | 39.7697 | 0 | 42 | 2.2303 | 2.2303 | opened
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 2.85 | 0.843 | 120 | 2.007 | 0 | 4.2 | 2.193 | 2.193 | opened | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.524 | 3.374 | 0.843 | 120 | 2.531 | 0 | 4.2 | 1.669 | 1.669 | opened
10 | SS 35/10 Vatolino | 2,5+4,0 | 3.52 |  |  | 3.52 | 0 | 2.63 | -0.89 | -0.89 | closed | 10 | SS 35/10 Vatolino | 2,5+4,0 | 0.706 | 4.226 |  |  | 4.226 | 0 | 2.63 | -1.596 | -1.596 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 4.85 |  |  | 4.85 | 0 | 6.62 | 1.77 | 1.77 | opened | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.3241 | 5.1741 |  |  | 5.1741 | 0 | 6.62 | 1.4459 | 1.4459 | opened
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 2.28 |  |  | 2.28 | 0 | 4.2 | 1.92 | 1.92 | opened | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.1444 | 2.4244 |  |  | 2.4244 | 0 | 4.2 | 1.7756 | 1.7756 | opened
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.76 |  |  | 0.76 | 0 | 1.68 | 0.92 | 0.92 | opened | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.062 | 0.822 |  |  | 0.822 | 0 | 1.68 | 0.858 | 0.858 | opened
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.66 |  |  | 1.66 | 0 | 4.2 | 2.54 | 2.54 | opened | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.7479 | 3.4079 |  |  | 3.4079 | 0 | 4.2 | 0.7921 | 0.7921 | opened
15 | SS 35/10 Volna | 2,5+2,5 | 3.06 |  |  | 3.06 | 0 | 2.63 | -0.43 | -0.43 | closed | 15 | SS 35/10 Volna | 2,5+2,5 | 0.216 | 3.276 |  |  | 3.276 | 0 | 2.63 | -0.646 | -0.646 | closed
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 1.89 | 0.2 | 120 | 1.69 | 0 | 2.63 | 0.94 | 0.94 | opened | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.092 | 1.982 | 0.2 | 120 | 1.782 | 0 | 2.63 | 0.848 | 0.848 | opened
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.52 | 0.22 | 120 | 0.3 | 0 | 2.63 | 2.33 | 2.33 | opened | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.021 | 0.541 | 0.22 | 120 | 0.321 | 0 | 2.63 | 2.309 | 2.309 | opened
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 3.05 | 0.674 | 120 | 2.376 | 0 | 4.2 | 1.824 | 1.824 | opened | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.4296 | 3.4796 | 0.674 | 120 | 2.8056 | 0 | 4.2 | 1.3944 | 1.3944 | opened
19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.91 | 1.02 | 120 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.2749 | 5.1849 | 1.02 | 120 | 4.1649 | 0 | 4.2 | 0.0351 | 0.0351 | opened
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 1.75 |  |  | 1.75 | 0 | 6.62 | 4.87 | 4.87 | opened | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 1.75 |  |  | 1.75 | 0 | 6.62 | 4.87 | 4.87 | opened
21 | SS 110/6 Depo | 16+16 | 8.33 |  |  | 8.33 | 0 | 16.8 | 8.47 | 8.47 | opened | 21 | SS 110/6 Depo | 16+16 | 8.3294 | 16.6594 |  |  | 16.6594 | 0 | 16.8 | 0.14062 | 0.14062 | opened
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.23 | 0.956 | 120 | 0.274 | 0 | 1.68 | 1.406 | 1.406 | opened | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.489 | 1.719 | 0.956 | 120 | 0.763 | 0 | 1.68 | 0.917 | 0.917 | opened
23 | SS 110/10 Druzhba | 16+16 | 6.33 | 0.16 | 120 | 6.17 | 0 | 16.8 | 10.63 | 10.63 | opened | 23 | SS 110/10 Druzhba | 16+16 | 0.4563 | 6.7863 | 0.16 | 120 | 6.6263 | 0 | 16.8 | 10.1737 | 10.1737 | opened
24 | SS 35/10 Dubki | 6,3+6,3 | 4.62 | 0.787 | 120 | 3.833 | 0 | 6.62 | 2.787 | 2.787 | opened | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.3735 | 4.9935 | 0.787 | 120 | 4.2065 | 0 | 6.62 | 2.4135 | 2.4135 | opened
25 | SS 35/10 Dybino | 2,5+2,5 | 1.22 |  |  | 1.22 | 0 | 2.63 | 1.41 | 1.41 | opened | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.386 | 1.606 |  |  | 1.606 | 0 | 2.63 | 1.024 | 1.024 | opened
26 | SS 35/6 Zavolzhskaya | 10+10 | 12.43 |  |  | 12.43 | 0 | 10.5 | -1.93 | -1.93 | closed | 26 | SS 35/6 Zavolzhskaya | 10+10 | 2.4153 | 14.8453 |  |  | 14.8453 | 0 | 10.5 | -4.3453 | -4.3453 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 38.2 |  |  | 38.2 | 0 | 42 | 3.8 | 3.8 | opened | 27 | SS 110/6/6 Institutskaya | 40+40 | 4.2411 | 42.4411 |  |  | 42.4411 | 0 | 42 | -0.44114 | -0.44114 | closed
28 | SS 35/10 Koza | 1,6+1,6 | 0.41 | 0.179 | 120 | 0.231 | 0 | 1.68 | 1.449 | 1.449 | opened | 28 | SS 35/10 Koza | 1,6+1,6 | 0.007 | 0.417 | 0.179 | 120 | 0.238 | 0 | 1.68 | 1.442 | 1.442 | opened
29 | SS 110/35/6 Konstantinovo | 20+20 | 13.99 | 0.1 | 120 | 13.89 | 0 | 21 | 7.11 | 7.11 | opened | 29 | SS 110/35/6 Konstantinovo | 20+20 |  | 15.4253 | 0.1 | 120 | 15.3253 | 0 | 21 | 5.6747 | 5.6747 | opened
| Nom. capacity MV, МVА | 20+20 | 9.73 |  |  | 9.73 | 0 | 21 | 11.27 |  |  | 2: Nom. capacity MV, МVА; 3: 20+20; 5: 10.4878; Мин. 8: 10.4878; Мин. 9: 0; Мин. 10: 21; Мин. 11: 10.5122
| Nom. capacity LV, МVА | 20+20 | 4.26 | 0.1 | 120 | 4.16 | 0 | 21 | 16.84 |  |  |  | Nom. capacity LV, МVА | 20+20 | 0.6775 | 4.9375 | 0.1 | 120 | 4.8375 | 0 | 21 | 16.1625
30 | SS 35/10 Kurba | 2,5+2,5 | 2.58 | 1.71 | 120 | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.113 | 2.693 | 1.71 | 120 | 0.983 | 0 | 2.63 | 1.647 | 1.647 | opened
31 | SS 35/10 Lesnye Polyany | 10+10 | 6.92 | 0.48 | 120 | 6.44 | 0 | 10.5 | 4.06 | 4.06 | opened | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.1375 | 8.0575 | 0.48 | 120 | 7.5775 | 0 | 10.5 | 2.9225 | 2.9225 | opened
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 7.16 | 3.69 | 120 | 3.47 | 0 | 6.62 | 3.15 | 3.15 | opened | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 3.3945 | 10.5545 | 3.69 | 120 | 6.8645 | 0 | 6.62 | -0.2445 | -0.2445 | closed
33 | SS 35/10 Nekrasovo | 10+10 | 9.86 |  |  | 9.86 | 0 | 10.5 | 0.64 | 0.64 | opened | 33 | SS 35/10 Nekrasovo | 10+10 | 1.5544 | 11.4144 |  |  | 11.4144 | 0 | 10.5 | -0.91437 | -0.91437 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 1.049 | 0.38 | 120 | 0.669 | 0 | 2.63 | 1.961 | 1.961 | opened | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.067 | 1.116 | 0.38 | 120 | 0.736 | 0 | 2.63 | 1.894 | 1.894 | opened
35 | SS 110/35/6 Oil refinary plant | 25+25 | 16.28 |  |  | 16.28 | 0 | 26.25 | 9.97 | 9.97 | opened | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 23.6791 |  |  | 23.6791 | 0 | 26.25 | 2.5709 | 2.5709 | opened
| Nom. capacity MV, МVА | 25+25 | 8.4 |  |  | 8.4 | 0 | 26.25 | 17.85 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 8.7241; Мин. 8: 8.7241; Мин. 9: 0; Мин. 10: 26.25; Мин. 11: 17.5259
| Nom. capacity LV, МVА | 25+25 | 7.88 |  |  | 7.88 | 0 | 26.25 | 18.37 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.075 | 14.955 |  |  | 14.955 | 0 | 26.25 | 11.295
36 | SS 110/6/6 Orion | 40+40 | 14.32 |  |  | 14.32 | 0 | 42 | 27.68 | 27.68 | opened | 36 | SS 110/6/6 Orion | 40+40 | 1.5303 | 15.8503 |  |  | 15.8503 | 0 | 42 | 26.1497 | 26.1497 | opened
37 | SS 110/35/6 Pavlovskaya | 20+25 | 21.5 |  |  | 21.5 | 0 | 21 | -0.5 | -0.5 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 21.8898 |  |  | 21.8898 | 0 | 21 | -0.8898 | -0.8898 | closed
| Nom. capacity MV, МVА | 20+25 | 7.1 |  |  | 7.1 | 0 | 21 | 13.9 |  |  | 2: Nom. capacity MV, МVА; 3: 20+25; 5: 7.3148; Мин. 8: 7.3148; Мин. 9: 0; Мин. 10: 21; Мин. 11: 13.6852
| Nom. capaity LV, МVА | 20+25 | 14.4 |  |  | 14.4 | 0 | 21 | 6.6 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.175 | 14.575 |  |  | 14.575 | 0 | 21 | 6.425
38 | SS 110/10 Pereval | 16+16 | 8.6 |  |  | 8.6 | 0 | 16.8 | 8.2 | 8.2 | opened | 38 | SS 110/10 Pereval | 16+16 | 10.483 | 19.083 |  |  | 19.083 | 0 | 16.8 | -2.283 | -2.283 | closed
39 | SS 110/6/6 Perekop | 25+25 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74 | 12.74 | opened | 39 | SS 110/6/6 Perekop | 25+25 | 0.7252 | 14.2352 |  |  | 14.2352 | 0 | 26.25 | 12.0148 | 12.0148 | opened
40 | SS 110/6/6 Poligraf | 40+40 | 40.327 |  |  | 40.327 | 0 | 42 | 1.673 | 1.673 | opened | 40 | SS 110/6/6 Poligraf | 40+40 | 5.0838 | 45.4108 |  |  | 45.4108 | 0 | 42 | -3.4108 | -3.4108 | closed
41 | SS 110/35/10 Prechistoe | 10+10 | 5.37 | 0.213 | 120 | 5.157 | 0 | 10.5 | 5.343 | 5.343 | opened | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 5.8781 | 0.213 | 120 | 5.6651 | 0 | 10.5 | 4.8349 | 4.8349 | opened
| Nom. capacity MV, МVА | 10+10 | 1.79 |  |  | 1.79 | 0 | 10.5 | 8.71 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 1.8742; Мин. 8: 1.8742; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 8.6258
| Nom. capacity LV, МVА | 10+10 | 3.58 | 0.213 | 120 | 3.367 | 0 | 10.5 | 7.133 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.4239 | 4.0039 | 0.213 | 120 | 3.7909 | 0 | 10.5 | 6.7091
42 | SS 35/10 Preventorium | 2,5+2,5 | 0.61 | 0.316 | 120 | 0.294 | 0 | 2.63 | 2.336 | 2.336 | opened | 42 | SS 35/10 Preventorium | 2,5+2,5 | 3.0343 | 3.6443 | 0.316 | 120 | 3.3283 | 0 | 2.63 | -0.6983 | -0.6983 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.12 | 0.044 | 120 | 0.076 | 0 | 2.63 | 2.554 | 2.554 | opened | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.015 | 0.135 | 0.044 | 120 | 0.091 | 0 | 2.63 | 2.539 | 2.539 | opened
44 | SS 110/6/6 Severnaya | 63+63 | 39.51 |  |  | 39.51 | 0 | 66.15 | 26.64 | 26.64 | opened | 44 | SS 110/6/6 Severnaya | 63+63 | 10.4319 | 49.9419 |  |  | 49.9419 | 0 | 66.15 | 16.2081 | 16.2081 | opened
45 | SS 35/10 Sereda | 2,5+2,5 | 1.36 | 0.108 | 120 | 1.252 | 0 | 2.63 | 1.378 | 1.378 | opened | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.3655 | 1.7255 | 0.108 | 120 | 1.6175 | 0 | 2.63 | 1.0125 | 1.0125 | opened
46 | SS 110/6 Tormoznaya | 16+16 | 16.63 |  |  | 16.63 | 0 | 16.8 | 0.17 | 0.17 | opened | 46 | SS 110/6 Tormoznaya | 16+16 | 0.673 | 17.303 |  |  | 17.303 | 0 | 16.8 | -0.503 | -0.503 | closed
47 | SS 110/6 Petrol station pump | 16+16 | 4.52 |  |  | 4.52 | 0 | 16.8 | 12.28 | 12.28 | opened | 47 | SS 110/6 Petrol station pump | 16+16 | 0.6 | 5.12 |  |  | 5.12 | 0 | 16.8 | 11.68 | 11.68 | opened
48 | SS 35/10 Troitsa | 2,5+2,5 | 0.5 | 0.108 | 120 | 0.392 | 0 | 2.63 | 2.238 | 2.238 | opened | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.005 | 0.505 | 0.108 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | opened
49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.61 | 0.01 | 120 | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.111 | 0.721 | 0.01 | 120 | 0.711 | 0 | 2.63 | 1.919 | 1.919 | opened
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 7.54 |  |  | 7.54 | 0 | 6.62 | -0.92 | -0.92 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.35 | 7.89 |  |  | 7.89 | 0 | 6.62 | -1.27 | -1.27 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.78 |  |  | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.041 | 0.821 |  |  | 0.821 | 0 | 2.63 | 1.809 | 1.809 | opened
52 | SS 35/10 Urozhay | 4,0+4,0 | 3.2 | 0.825 | 120 | 2.375 | 0 | 4.2 | 1.825 | 1.825 | opened | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.635 | 3.835 | 0.825 | 120 | 3.01 | 0 | 4.2 | 1.19 | 1.19 | opened
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.75 | 0.134 | 120 | 0.31 | 0 | 3.36 | 3.05 | 2.054 | opened | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 1.4595 | 0.134 | 120 | 1.3255 | 0 | 3.36 | 2.0345 | 2.0345 | opened
| Nom. capacity MV, МVА | 6.3 | 2.31 | [8 empty] | 2: Nom. capacity MV, МVА; 3: 6.3
| Nom. capacity LV, МVА | 6.3 | 1.44 | 0.134 | 120 | 1.306 | 0 | 3.36 | 2.054 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.0195 | 1.4595 | 0.134 | 120 | 1.3255 | 0 | 3.36 | 2.0345
54 | SS 110/10 Chayka | 25+25 | 22.04 |  |  | 22.04 | 0 | 26.25 | 4.21 | 4.21 | opened | 54 | SS 110/10 Chayka | 25+25 | 3.7936 | 25.8336 |  |  | 25.8336 | 0 | 26.25 | 0.41639 | 0.41639 | opened
55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.78 | 0.19 | 120 | 1.59 | 0 | 2.63 | 1.04 | 1.04 | opened | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 0.327 | 2.107 | 0.19 | 120 | 1.917 | 0 | 2.63 | 0.713 | 0.713 | opened
56 | SS 35/10 Shchedrino | 4,0+4,0 | 2.19 |  |  | 2.19 | 0 | 4.2 | 2.01 | 2.01 | opened | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.552 | 2.742 |  |  | 2.742 | 0 | 4.2 | 1.458 | 1.458 | opened
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 32.63 |  |  | 32.63 | 0 | 42 | 9.37 | 9.37 | opened | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 6.6665 | 39.2965 |  |  | 39.2965 | 0 | 42 | 2.7035 | 2.7035 | opened
58 | SS 110/10/6 Yartsevo | 25+25 | 10.32 |  |  | 10.32 | 0 | 26.25 | 15.93 | 15.93 | opened | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.603 | 10.923 |  |  | 10.923 | 0 | 26.25 | 15.327 | 15.327 | opened
59 | SS 110/10 Altynovo | 6,3+6,3 | 3.512 |  |  | 3.512 | 0 | 6.62 | 3.108 | 3.108 | opened | 59 | SS 110/10 Altynovo | 6,3+6,3 | 0.3965 | 3.9085 |  |  | 3.9085 | 0 | 6.62 | 2.7115 | 2.7115 | opened
60 | SS 110/35/10 Borisogleb | 10+16 | 7.938 |  |  | 7.938 | 0 | 10.5 | 2.562 | 2.562 | opened | 60 | SS 110/35/10 Borisogleb | 10+16 |  | 9.5462 |  |  | 9.5462 | 0 | 10.5 | 0.95385 | 0.95385 | opened
| Nom. capacity MV, МVА | 10+16 | 2.72 |  |  | 2.72 | 0 | 10.5 | 7.78 |  |  | 2: Nom. capacity MV, МVА; 3: 10+16; 5: 3.1966; Мин. 8: 3.1966; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 7.3034
| Nom. capacity LV, МVА | 10+16 | 5.218 |  |  | 5.218 | 0 | 10.5 | 5.282 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.1316 | 6.3496 |  |  | 6.3496 | 0 | 10.5 | 4.1504
61 | SS 110/35/10 Vasilkovo | 10+10 | 2.78 | 0.472 | 120 | 2.308 | 0 | 10.5 | 8.192 | 8.192 | opened | 61 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.222 | 0.472 | 120 | 2.75 | 0 | 10.5 | 7.75 | 7.75 | opened
| Nom. capacity MV, МVА | 10+10 | 1.732 |  |  | 1.732 | 0 | 10.5 | 8.768 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 2.09; Мин. 8: 2.09; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 8.41
| Nom. capacity LV, МVА | 10+10 | 1.048 | 0.472 | 120 | 0.576 | 0 | 10.5 | 9.924 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.084 | 1.132 | 0.472 | 120 | 0.66 | 0 | 10.5 | 9.84
62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.28 | 0.07 | 120 | 0.21 | 0 | 6.62 | 6.41 | 6.41 | opened | 62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0 | 0.28 | 0.07 | 120 | 0.21 | 0 | 6.62 | 6.41 | 6.41 | opened
63 | SS 110/6 Gavrilov Yam | 16+16 | 13.286 |  |  | 13.286 | 0 | 16.8 | 3.514 | 3.514 | opened | 63 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 13.286 |  |  | 13.286 | 0 | 16.8 | 3.514 | 3.514 | opened
64 | SS 110/6 Kinoplyonka | 6,3+10 | 6.814 |  |  | 6.814 | 0 | 6.62 | -0.194 | -0.194 | closed | 64 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 9.668 |  |  | 9.668 | 0 | 6.62 | -3.048 | -3.048 | closed
65 | SS 110/35/10 Klimatino | 6,3+6,3 | 1.257 |  |  | 1.257 | 0 | 6.62 | 5.363 | 5.363 | opened | 65 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.288 |  |  | 1.288 | 0 | 6.62 | 5.332 | 5.332 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.313 |  |  | 0.313 | 0 | 6.62 | 6.307 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 0.313; Мин. 8: 0.313; Мин. 9: 0; Мин. 10: 6.62; Мин. 11: 6.307
| Nom. capacity LV, МVА | 6,3+6,3 | 0.944 |  |  | 0.944 | 0 | 6.62 | 5.676 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.031 | 0.975 |  |  | 0.975 | 0 | 6.62 | 5.645
66 | SS 110/35/10 Nila | 6,3+6,3 | 11.107 | 0.45 | 120 | 10.657 | 0 | 6.62 | -4.037 | -4.037 | closed | 66 | SS 110/35/10 Nila | 6,3+6,3 |  | 21.2632 | 0.45 | 120 | 20.8132 | 0 | 6.62 | -14.1932 | -14.1932 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 8.33 |  |  | 8.33 | 0 | 6.62 | -1.71 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 11.5292; Мин. 8: 11.5292; Мин. 9: 0; Мин. 10: 6.62; Мин. 11: -4.9092
| Nom. capacity LV, МVА | 6,3+6,3 | 2.777 | 0.45 | 120 | 2.327 | 0 | 6.62 | 4.293 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 6.957 | 9.734 | 0.45 | 120 | 9.284 | 0 | 6.62 | -2.664
67 | SS 110/35/6 Pereslavl | 25+25 | 26.546 |  |  | 26.546 | 0 | 26.25 | -0.296 | -0.296 | closed | 67 | SS 110/35/6 Pereslavl | 25+25 |  | 35.395 |  |  | 35.395 | 0 | 26.25 | -9.145 | -9.145 | closed
| Nom. capacity MV, МVА | 25+25 | 11.941 |  |  | 11.941 | 0 | 26.25 | 14.309 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 19.958; Мин. 8: 19.958; Мин. 9: 0; Мин. 10: 26.25; Мин. 11: 6.292
| Nom. capacity LV, МVА | 25+25 | 14.605 |  |  | 14.605 | 0 | 26.25 | 11.645 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.832 | 15.437 |  |  | 15.437 | 0 | 26.25 | 10.813
68 | SS 110/10 Ploski | 2,5+2,5 | 1.778 |  |  | 1.778 | 0 | 2.63 | 0.852 | 0.852 | opened | 68 | SS 110/10 Ploski | 2,5+2,5 | 0.6395 | 2.4175 |  |  | 2.4175 | 0 | 2.63 | 0.2125 | 0.2125 | opened
69 | SS 110/35/10 Rostov | 25+20 | 21.343 |  |  | 21.343 | 0 | 21 | -0.343 | -0.343 | closed | 69 | SS 110/35/10 Rostov | 25+20 |  | 24.263 |  |  | 24.263 | 0 | 21 | -3.263 | -3.263 | closed
| Nom. capacity MV, МVА | 25+20 | 1.894 |  |  | 1.894 | 0 | 21 | 19.106 |  |  | 2: Nom. capacity MV, МVА; 3: 25+20; 5: 2.317; Мин. 8: 2.317; Мин. 9: 0; Мин. 10: 21; Мин. 11: 18.683
| Nom. Capacity LV, МVА | 25+20 | 19.449 |  |  | 19.449 | 0 | 21 | 1.551 |  |  |  | Nom. Capacity LV, МVА | 25+20 | 2.497 | 21.946 |  |  | 21.946 | 0 | 21 | -0.946
70 | SS 110/35/10 Technical school | 6,3+6,3 | 8.359 |  |  | 8.359 | 0 | 6.62 | -1.739 | -1.739 | closed | 70 | SS 110/35/10 Technical school | 6,3+6,3 |  | 12.9273 |  |  | 12.9273 | 0 | 6.62 | -6.3073 | -6.3073 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 4.041 |  |  | 4.041 | 0 | 6.62 | 2.579 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 6.4168; Мин. 8: 6.4168; Мин. 9: 0; Мин. 10: 6.62; Мин. 11: 0.20325
| Nom. capacity LV, МVА | 6,3+6,3 | 4.318 |  |  | 4.318 | 0 | 6.62 | 2.302 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.1925 | 6.5105 |  |  | 6.5105 | 0 | 6.62 | 0.1095
71 | SS 110/35/10 Uglich | 25+25 | 24.206 |  |  | 24.206 | 0 | 26.25 | 2.044 | 2.044 | opened | 71 | SS 110/35/10 Uglich | 25+25 |  | 26.6445 |  |  | 26.6445 | 0 | 26.25 | -0.3945 | -0.3945 | closed
| Nom. capacidty MV, МVА | 25+25 | 18.6 |  |  | 18.6 | 0 | 26.25 | 7.65 |  |  | 2: Nom. capacidty MV, МVА; 3: 25+25; 5: 18.7555; Мин. 8: 18.7555; Мин. 9: 0; Мин. 10: 26.25; Мин. 11: 7.4945
| Nom. capacity LV, МVА | 25+25 | 5.606 |  |  | 5.606 | 0 | 26.25 | 20.644 |  |  |  | Nom. capacity LV, МVА | 25+25 | 2.283 | 7.889 |  |  | 7.889 | 0 | 26.25 | 18.361
72 | SS 110/10 Ustye | 10+10 | 4.915 | 0.32 | 120 | 4.595 | 0 | 10.5 | 5.905 | 5.905 | opened | 72 | SS 110/10 Ustye | 10+10 | 0.33 | 5.245 | 0.32 | 120 | 4.925 | 0 | 10.5 | 5.575 | 5.575 | opened
73 | SS 110/10 Shurskol | 10+10 | 1.976 | 1.18 | 120 | 0.796 | 0 | 10.5 | 9.704 | 9.704 | opened | 73 | SS 110/10 Shurskol | 10+10 | 0.138 | 2.114 | 1.18 | 120 | 0.934 | 0 | 10.5 | 9.566 | 9.566 | opened
74 | SS 110/10 Yur.Sloboda | 10+10 | 9.319 | 0.173 | 120 | 9.146 | 0 | 10.5 | 1.354 | 1.354 | opened | 74 | SS 110/10 Yur.Sloboda | 10+10 | 0.8515 | 10.1705 | 0.173 | 120 | 9.9975 | 0 | 10.5 | 0.5025 | 0.5025 | opened
75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.47 |  |  | 0.47 | 0 | 2.63 | 2.16 | 2.16 | opened | 75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.042 | 0.512 |  |  | 0.512 | 0 | 2.63 | 2.118 | 2.118 | opened
76 | SS 35/6 Batki | 1,6+1,6 | 1.548 |  |  | 1.548 | 0 | 1.68 | 0.132 | 0.132 | opened | 76 | SS 35/6 Batki | 1,6+1,6 | 0.1238 | 1.6718 |  |  | 1.6718 | 0 | 1.68 | 0.0082 | 0.0082 | opened
77 | SS 35/10 Beregovaya | 1.6 | 0.25 | 1.71 | 1 сутки | 1.71 | 0 | 1.71 | 1.46 | 1.46 | opened | 77 | SS 35/10 Beregovaya | 1.6 | 0.005 | 0.255 | 1.71 | 1 сутки | 1.71 | 0 | 1.71 | 1.455 | 1.455 | opened
78 | SS 35/10 Berendeevo | 2,5+2,5 | 1.428 | 2.625 | 1 сутки | 2.625 | 0 | 2.625 | 1.197 | 1.197 | opened | 78 | SS 35/10 Berendeevo | 2,5+2,5 | 0.372 | 1.8 | 2.625 |  | 2.625 | 0 | 2.625 | 0.825 | 0.825 | opened
79 | SS 35/10 Vorzha | 1,8+1,8 | 0.524 | 0.454 | 120 | 0.07 | 0 | 1.89 | 1.82 | 1.82 | opened | 79 | SS 35/10 Vorzha | 1,8+1,8 | 0.278 | 0.802 | 0.454 | 120 | 0.348 | 0 | 1.89 | 1.542 | 1.542 | opened
80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.09 | 0.182 | 120 | 0.908 | 0 | 1.68 | 0.772 | 0.772 | opened | 80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.165 | 1.255 | 0.182 | 120 | 1.073 | 0 | 1.68 | 0.607 | 0.607 | opened
81 | SS 35/10 Glebovo | 2,5+2,5 | 2.049 |  |  | 2.049 | 0 | 2.63 | 0.581 | 0.581 | opened | 81 | SS 35/10 Glebovo | 2,5+2,5 | 1.4891 | 3.5381 |  |  | 3.5381 | 0 | 2.63 | -0.9081 | -0.9081 | closed
82 | SS 35/10 Gorki | 2,5+2,5 | 1.021 |  |  | 1.021 | 0 | 2.63 | 1.609 | 1.609 | opened | 82 | SS 35/10 Gorki | 2,5+2,5 | 0.2595 | 1.2805 |  |  | 1.2805 | 0 | 2.63 | 1.3495 | 1.3495 | opened
83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.165 |  |  | 1.165 | 0 | 1.68 | 0.515 | 0.515 | opened | 83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.049 | 1.214 |  |  | 1.214 | 0 | 1.68 | 0.466 | 0.466 | opened
84 | SS 35/10 Zaozerye | 2,5+1,6 | 1.199 |  |  | 1.199 | 0 | 1.68 | 0.481 | 0.481 | opened | 84 | SS 35/10 Zaozerye | 2,5+1,6 | 0.076 | 1.275 |  |  | 1.275 | 0 | 1.68 | 0.405 | 0.405 | opened
85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 1.511 |  |  | 1.511 | 0 | 2.63 | 1.119 | 1.119 | opened | 85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0635 | 1.5745 |  |  | 1.5745 | 0 | 2.63 | 1.0555 | 1.0555 | opened
86 | SS 35/10 Kibernetik | 6,3+6,3 | 1.835 |  |  | 1.835 | 0 | 6.62 | 4.785 | 4.785 | opened | 86 | SS 35/10 Kibernetik | 6,3+6,3 | 3.0165 | 4.8515 |  |  | 4.8515 | 0 | 6.62 | 1.7685 | 1.7685 | opened
87 | SS 35/10 Klementyevo | 2.5 | 0.342 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.418 | 0.418 | opened | 87 | SS 35/10 Klementyevo | 2.5 | 0.016 | 0.358 | 0.76 | 1 сутки | 0.76 | 0 | 0.76 | 0.402 | 0.402 | opened
88 | SS 35/10 Krasnoe | 4,0+4,0 | 1.74 | 0.81 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | opened | 88 | SS 35/10 Krasnoe | 4,0+4,0 | 1.148 | 2.888 | 0.81 | 120 | 2.078 | 0 | 4.2 | 2.122 | 2.122 | opened
89 | SS 35/10 Kulakovo | 2,5+2,5 | 1.675 |  |  | 1.675 | 0 | 2.63 | 0.955 | 0.955 | opened | 89 | SS 35/10 Kulakovo | 2,5+2,5 | 0.239 | 1.914 |  |  | 1.914 | 0 | 2.63 | 0.716 | 0.716 | opened
90 | SS 35/6 Kupan | 2,5+2,5 | 2.398 |  |  | 2.398 | 0 | 2.63 | 0.232 | 0.232 | opened | 90 | SS 35/6 Kupan | 2,5+2,5 | 1.1187 | 3.5167 |  |  | 3.5167 | 0 | 2.63 | -0.88674 | -0.88674 | closed
91 | SS 35/10 Markovo | 2,5+2,5 | 1.224 | 0.36 | 120 | 0.864 | 0 | 2.63 | 1.766 | 1.766 | opened | 91 | SS 35/10 Markovo | 2,5+2,5 | 0.4 | 1.624 | 0.36 | 120 | 1.264 | 0 | 2.63 | 1.366 | 1.366 | opened
92 | SS 35/10 Nagorye | 4,0+4,0 | 3.343 |  |  | 3.343 | 0 | 4.2 | 0.857 | 0.857 | opened | 92 | SS 35/10 Nagorye | 4,0+4,0 | 0.942 | 4.285 |  |  | 4.285 | 0 | 4.2 | -0.085 | -0.085 | closed
93 | SS 35/10 Porechye | 6,3+6,3 | 1.911 | 0.036 | 120 | 1.875 | 0 | 6.62 | 4.745 | 4.745 | opened | 93 | SS 35/10 Porechye | 6,3+6,3 | 0.15 | 2.061 | 0.036 | 120 | 2.025 | 0 | 6.62 | 4.595 | 4.595 | opened
94 | SS 35/10 Pruzhinino | 2,5+2,5 | 1.254 |  |  | 1.254 | 0 | 2.63 | 1.376 | 1.376 | opened | 94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.2135 | 1.4675 |  |  | 1.4675 | 0 | 2.63 | 1.1625 | 1.1625 | opened
95 | SS 35/10 Ramenye | 2,5+2,5 | 0.839 | 0.087 | 120 | 0.752 | 0 | 2.63 | 1.878 | 1.878 | opened | 95 | SS 35/10 Ramenye | 2,5+2,5 | 0.031 | 0.87 | 0.087 | 120 | 0.783 | 0 | 2.63 | 1.847 | 1.847 | opened
96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 1.853 |  |  | 1.853 | 0 | 1.68 | -0.173 | -0.173 | closed | 96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 0.115 | 1.968 |  |  | 1.968 | 0 | 1.68 | -0.288 | -0.288 | closed
97 | SS 35/10 Saraevo | 1+1,6 | 1.291 |  |  | 1.291 | 0 | 1.05 | -0.241 | -0.241 | closed | 97 | SS 35/10 Saraevo | 1+1,6 | 0.75 | 2.041 |  |  | 2.041 | 0 | 1.05 | -0.991 | -0.991 | closed
98 | SS 35/10 Selifontovo | 2,5+2,5 | 1.399 | 0.182 | 120 | 1.217 | 0 | 2.63 | 1.413 | 1.413 | opened | 98 | SS 35/10 Selifontovo | 2,5+2,5 | 0.274 | 1.673 | 0.182 | 120 | 1.491 | 0 | 2.63 | 1.139 | 1.139 | opened
99 | SS 35/10 Semibratovo | 4,0+4,0 | 1.206 | 0.25 | 120 | 0.956 | 0 | 4.2 | 3.244 | 3.244 | opened | 99 | SS 35/10 Semibratovo | 4,0+4,0 | 0.04 | 1.246 | 0.25 | 120 | 0.996 | 0 | 2.63 | 1.634 | 1.634 | opened
100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.252 |  |  | 1.252 | 0 | 1.68 | 0.428 | 0.428 | opened | 100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.4261 | 1.6781 |  |  | 1.6781 | 0 | 1.68 | 0.0019 | 0.0019 | opened
101 | SS 35/10 Solomidino | 2.5 | 0.612 | 1.18 | 1 сутки | 1.18 | 0 | 1.18 | 0.568 | 0.568 | opened | 101 | SS 35/10 Solomidino | 2.5 | 1.7686 | 2.3806 | 1.18 | 1 сутки | 1.18 | 0 | 1.18 | -1.2006 | -1.2006 | closed
102 | SS 35/10 Stavotino | 4,0+4,0 | 1.336 | 0.445 | 120 | 0.891 | 0 | 4.2 | 3.309 | 3.309 | opened | 102 | SS 35/10 Stavotino | 4,0+4,0 | 0.8725 | 2.2085 | 0.445 | 120 | 1.7635 | 0 | 4.2 | 2.4365 | 2.4365 | opened
103 | SS 35/10 Urusovo | 2,5+2,5 | 0.529 | 0.053 | 120 | 0.476 | 0 | 2.63 | 2.154 | 2.154 | opened | 103 | SS 35/10 Urusovo | 2,5+2,5 | 0.003 | 0.532 | 0.053 | 120 | 0.479 | 0 | 2.63 | 2.151 | 2.151 | opened
104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.522 |  |  | 0.522 | 0 | 2.63 | 2.108 | 2.108 | opened | 104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.802 | 1.324 |  |  | 1.324 | 0 | 2.63 | 1.306 | 1.306 | opened
105 | SS 35/10 Choporovo | 2,5+2,5 | 0.532 |  |  | 0.532 | 0 | 2.63 | 2.098 | 2.098 | opened | 105 | SS 35/10 Choporovo | 2,5+2,5 | 0.131 | 0.663 |  |  | 0.663 | 0 | 2.63 | 1.967 | 1.967 | opened
106 | SS 35/10 Shchurovo | 2,5+2,5 | 1.07 | 0.27 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened | 106 | SS 35/10 Shchurovo | 2,5+2,5 | 0.032 | 1.102 | 0.27 | 120 | 0.832 | 0 | 2.63 | 1.798 | 1.798 | opened
107 | SS 35/10 Neksans | 10+10 | 1.619 |  |  | 1.619 | 0 | 10.5 | 8.881 | 8.881 | opened | 107 | SS 35/10 Neksans | 10+10 | 0 | 1.619 |  |  | 1.619 | 0 | 10.5 | 8.881 | 8.881 | opened
108 | SS 35/6 Pribrezhnaya | 10+10 | 13.006 |  |  | 13.006 | 0 | 10.5 | -2.506 | -2.506 | closed | 108 | SS 35/6 Pribrezhnaya | 10+10 | 0 | 13.006 |  |  | 13.006 | 0 | 10.5 | -2.506 | -2.506 | closed
109 | SS 110/10 Product pipeline | 6,3+6,3 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened | 109 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened
110 | SS 110/10 Nekouz | 6,3+6,3 | 2.82 | 0.084 | 120 | 2.736 | 0 | 6.62 | 3.884 | 3.884 | opened | 110 | SS 110/10 Nekouz | 6,3+6,3 | 0.03 | 2.85 | 0.084 | 120 | 2.766 | 0 | 6.62 | 3.854 | 3.854 | opened
111 | SS 110/6 Yuzhnaya | 25+25 | 19.89 |  |  | 19.89 | 0 | 26.25 | 6.36 | 6.36 | opened | 111 | SS 110/6 Yuzhnaya | 25+25 | 0.20826 | 20.0983 |  |  | 20.0983 | 0 | 26.25 | 6.1517 | 6.1517 | opened
112 | SS 110/10 Optika | 10+10 | 4.97 | 1.18 | 120 | 3.79 | 0 | 10.5 | 6.71 | 6.71 | opened | 112 | SS 110/10 Optika | 10+10 | 0.366 | 5.336 | 1.18 | 120 | 4.156 | 0 | 10.5 | 6.344 | 6.344 | opened
113 | SS 110/6 Poligrafmash | 16+16 | 8.54 |  |  | 8.54 | 0 | 16.8 | 8.26 | 8.26 | opened | 113 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 8.6 |  |  | 8.6 | 0 | 16.8 | 8.2 | 8.2 | opened
114 | SS 110/6/6 Zapadnaya | 63+63 | 56.01 |  |  | 56.01 | 0 | 66.15 | 10.14 | 10.14 | opened | 114 | SS 110/6/6 Zapadnaya | 63+63 | 1.359 | 57.369 |  |  | 57.369 | 0 | 66.15 | 8.781 | 8.781 | opened
115 | SS 110/35/6 Volzhskaya | 40+40 | 8.3 |  |  | 8.3 | 0 | 42 | 33.7 | 33.7 | opened | 115 | SS 110/35/6 Volzhskaya | 40+40 |  | 8.3828 |  |  | 8.3828 | 0 | 42 | 33.6172 | 33.6172 | opened
| Nom. capacity MV, МVА | 40+40 | [9 empty] | 2: Nom. capacity MV, МVА; 3: 40+40
| Nom. capacity LV, МVА | 40+40 | 8.3 |  |  | 7.9 | 0 | 42 | 34.1 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.0828 | 8.3828 |  |  | 8.3828 | 0 | 42 | 33.6172
116 | SS 110/35/6 Levoberezhnaya | 16+16 | 14.456 |  |  | 14.456 | 0 | 16.8 | 2.344 | 2.344 | opened | 116 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.659 |  |  | 15.659 | 0 | 16.8 | 1.141 | 1.141 | opened
| Nom. capacity MV, МVА | 16+16 | 9.321 |  |  | 9.321 | 0 | 16.8 | 7.479 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.6 | 10.126 |  |  | 10.126 | 0 | 16.8 | 6.674
| Nom. capacity LV, МVА | 16+16 | 5.135 |  |  | 5.135 | 0 | 16.8 | 11.665 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.398 | 5.533 |  |  | 5.533 | 0 | 16.8 | 11.267
117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 2.2 |  |  | 2.2 | 0 | 7.88 | 5.68 | 5.68 | opened | 117 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 2.21 |  |  | 2.21 | 0 | 7.88 | 5.67 | 5.67 | opened
| Nom. capacity MV, МVА | 7,5+7,5 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43 |  |  | 2: Nom. capacity MV, МVА; 3: 7,5+7,5; 5: 1.45; Мин. 8: 1.45; Мин. 9: 0; Мин. 10: 7.88; Мин. 11: 6.43
| Nom. capacity LV, МVА | 7,5+7,5 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0.01 | 0.76 |  |  | 0.76 | 0 | 7.88 | 7.12
118 | SS 110/6 Dock yard | 10+10 | 4.43 |  |  | 4.43 | 0 | 10.5 | 6.07 | 6.07 | opened | 118 | SS 110/6 Dock yard | 10+10 | 0.056 | 4.486 |  |  | 4.486 | 0 | 10.5 | 6.014 | 6.014 | opened
119 | SS 110/6 Selekhovo | 6,3+6,3 | 4.27 |  |  | 4.27 | 0 | 6.62 | 2.35 | 2.35 | opened | 119 | SS 110/6 Selekhovo | 6,3+6,3 | 0.172 | 4.442 |  |  | 4.442 | 0 | 6.62 | 2.178 | 2.178 | opened
120 | SS 35/6 Kamenniki | 4,0+4,0 | 1.74 |  |  | 1.74 | 0 | 4.2 | 2.46 | 2.46 | opened | 120 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 1.889 |  |  | 1.889 | 0 | 4.2 | 2.311 | 2.311 | opened
121 | SS 35/10 Shashkovo | 1,6+1,6 | 1.03 | 0.532 | 120 | 0.498 | 0 | 1.68 | 1.182 | 1.182 | opened | 121 | SS 35/10 Shashkovo | 1,6+1,6 | 0.318 | 1.348 | 0.532 | 120 | 0.816 | 0 | 1.68 | 0.864 | 0.864 | opened
122 | SS 110/6 Veretye | 25+25 | 19.05 |  |  | 19.05 | 0 | 26.25 | 7.2 | 7.2 | opened | 122 | SS 110/6 Veretye | 25+25 | 1.205 | 20.255 |  |  | 20.255 | 0 | 26.25 | 5.995 | 5.995 | opened
123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.53 | 0.83 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 0.953 | 3.483 | 0.83 | 120 | 2.653 | 0 | 4.2 | 1.547 | 1.547 | opened
124 | SS 35/10 Arefino | 2,5+2,5 | 0.95 | 0.361 | 120 | 0.589 | 0 | 2.63 | 2.041 | 2.041 | opened | 124 | SS 35/10 Arefino | 2,5+2,5 | 0.124 | 1.074 | 0.361 | 120 | 0.713 | 0 | 2.63 | 1.917 | 1.917 | opened
125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.81 |  |  | 0.81 | 0 | 1.68 | 0.87 | 0.87 | opened | 125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.045 | 0.855 |  |  | 0.855 | 0 | 1.68 | 0.825 | 0.825 | opened
126 | SS 35/10 Pokrov | 1,6+1,6 | 0.71 | 0.34 | 120 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | opened | 126 | SS 35/10 Pokrov | 1,6+1,6 | 0.01 | 0.72 | 0.34 | 120 | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened
127 | SS 35/10 Anikovo | 2,5+2,5 | 1.13 | 0.29 | 120 | 0.84 | 0 | 2.63 | 1.79 | 1.79 | opened | 127 | SS 35/10 Anikovo | 2,5+2,5 | 0.02 | 1.15 | 0.29 | 120 | 0.86 | 0 | 2.63 | 1.77 | 1.77 | opened
128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.05 |  |  | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened | 128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.324 | 0.374 |  |  | 0.374 | 0 | 2.63 | 2.256 | 2.256 | opened
129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 5.2 |  |  | 5.2 | 0 | 6.62 | 1.42 | 1.42 | opened | 129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.6335 | 5.8335 |  |  | 5.8335 | 0 | 6.62 | 0.7865 | 0.7865 | opened
130 | SS 35/10 Breytovo | 4,0+4,0 | 4.2 |  |  | 4.2 | 0 | 4.2 | 0 | 0 | opened | 130 | SS 35/10 Breytovo | 4,0+4,0 | 1.603 | 5.803 |  |  | 5.803 | 0 | 4.2 | -1.603 | -1.603 | closed
131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.83 | 0.27 | 120 | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened | 131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.026 | 0.856 | 0.27 | 120 | 0.586 | 0 | 1.68 | 1.094 | 1.094 | opened
132 | SS 35/10 Znamovo | 2,5+2,5 | 0.82 | 0.82 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened | 132 | SS 35/10 Znamovo | 2,5+2,5 | 0 | 0.82 | 0.82 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened
133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened | 133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened
134 | SS 35/10 Zapolye | 2,5+2,5 | 0.45 |  |  | 0.45 | 0 | 2.63 | 2.18 | 2.18 | opened | 134 | SS 35/10 Zapolye | 2,5+2,5 | 0.1295 | 0.5795 |  |  | 0.5795 | 0 | 2.63 | 2.0505 | 2.0505 | opened
135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.43 | 0.843 | 120 | 0.587 | 0 | 1.68 | 1.093 | 1.093 | opened | 135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.157 | 1.587 | 0.843 | 120 | 0.744 | 0 | 1.68 | 0.936 | 0.936 | opened
136 | SS 35/10 Latskoe | 1,6+2,5 | 0.24 | 0.053 | 120 | 0.187 | 0 | 1.68 | 1.493 | 1.493 | opened | 136 | SS 35/10 Latskoe | 1,6+2,5 | 0.02345 | 0.26345 | 0.053 | 120 | 0.21045 | 0 | 1.68 | 1.4695 | 1.4695 | opened
137 | SS 35/10 Borok | 2,5+4,0 | 1.73 | 0.572 | 120 | 1.158 | 0 | 2.63 | 1.472 | 1.472 | opened | 137 | SS 35/10 Borok | 2,5+4,0 | 0.18875 | 1.9187 | 0.572 | 120 | 1.3468 | 0 | 2.63 | 1.2832 | 1.2832 | opened
138 | SS 35/10 Myshkin | 6,3+6,3 | 4.31 | 0.386 | 120 | 3.924 | 0 | 6.62 | 2.696 | 2.696 | opened | 138 | SS 35/10 Myshkin | 6,3+6,3 | 1.097 | 5.407 | 0.386 | 120 | 5.021 | 0 | 6.62 | 1.599 | 1.599 | opened
139 | SS 110/10 Volga | 6,3+5,6 | 1.85 |  |  | 1.85 | 0 | 5.88 | 4.03 | 4.03 | opened | 139 | SS 110/10 Volga | 6,3+5,6 | 0 | 1.85 |  |  | 1.85 | 0 | 5.88 | 4.03 | 4.03 | opened
140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 2 | 0.309 | 120 | 1.691 | 0 | 2.63 | 0.939 | 0.939 | opened | 140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.257 | 2.257 | 0.309 | 120 | 1.948 | 0 | 2.63 | 0.682 | 0.682 | opened
141 | SS 110/35/6 Vostochnaya | 25+25 | 19.27 |  |  | 19.27 | 0 | 26.25 | 6.98 | 6.98 | opened | 141 | SS 110/35/6 Vostochnaya | 25+25 |  | 20.193 |  |  | 20.193 | 0 | 26.25 | 6.057 | 6.057 | opened
| Nom. capacity MV, МVА | 25+25 | 3.688 |  |  | 3.688 | 0 | 26.25 | 22.562 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 4.551; Мин. 8: 4.551; Мин. 9: 0; Мин. 10: 26.25; Мин. 11: 21.699
| Nom. capacity LV, МVА | 25+25 | 15.582 |  |  | 15.582 | 0 | 26.25 | 10.668 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.06 | 15.642 |  |  | 15.642 | 0 | 26.25 | 10.608
142 | SS 110/35/10 Zalesye | 10+10 | 9.362 | 1.13 | 120 | 8.232 | 0 | 10.5 | 2.268 | 2.268 | opened | 142 | SS 110/35/10 Zalesye | 10+10 |  | 9.446 | 1.13 | 120 | 8.316 | 0 | 10.5 | 2.184 | 2.184 | opened
| Nom. capacity MV, МVА | 10+10 | 2.187 |  |  | 2.187 | 0 | 10.5 | 8.313 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 2.187; Мин. 8: 2.187; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 8.313
| Nom. capacity LV, МVА | 10+10 | 7.175 | 1.13 | 120 | 6.045 | 0 | 10.5 | 4.455 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.084 | 7.259 | 1.13 | 120 | 6.129 | 0 | 10.5 | 4.371
143 | SS 110/10 Lugovaya | 6,3+6,3 | 2.93 |  |  | 2.93 | 0 | 6.62 | 3.69 | 3.69 | opened | 143 | SS 110/10 Lugovaya | 6,3+6,3 | 0.136 | 3.066 |  |  | 3.066 | 0 | 6.62 | 3.554 | 3.554 | opened
144 | SS 110/35/10 Lom | 10+10 | 8.743 | 1.54 | 120 | 7.203 | 0 | 10.5 | 3.297 | 3.297 | opened | 144 | SS 110/35/10 Lom | 10+10 |  | 10.2899 | 1.54 | 120 | 8.7499 | 0 | 10.5 | 1.7501 | 1.7501 | opened
| Nom. capacity MV, МVА | 10+10 | 6.877 |  |  | 6.877 | 0 | 10.5 | 3.623 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 7.9615; Мин. 8: 7.9615; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 2.5385
| Nom. capacity LV, МVА | 10+10 | 1.866 | 1.54 | 120 | 0.326 | 0 | 10.5 | 10.174 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.4624 | 2.3284 | 1.54 | 120 | 0.7884 | 0 | 10.5 | 9.7116
145 | SS 35/10 Varegovo | 2,5+1,6 | 0.88 |  |  | 0.88 | 0 | 1.68 | 0.8 | 0.8 | opened | 145 | SS 35/10 Varegovo | 2,5+1,6 | 0.127 | 1.007 |  |  | 1.007 | 0 | 1.68 | 0.673 | 0.673 | opened
146 | SS 110/35/10 Shestikhino | 10+10 | 8.57 | 0.306 | 120 | 8.264 | 0 | 10.5 | 2.236 | 2.236 | opened | 146 | SS 110/35/10 Shestikhino | 10+10 |  | 10.7188 | 0.306 | 120 | 10.4128 | 0 | 10.5 | 0.08725 | 0.08725 | opened
| Nom. capacity MV, МVА | 10+10 | 7.809 |  |  | 7.809 | 0 | 10.5 | 2.691 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 9.6918; Мин. 8: 9.6918; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 0.80825
| Nom. capacity LV, МVА | 10+10 | 0.761 | 0.306 | 120 | 0.455 | 0 | 10.5 | 10.045 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.266 | 1.027 | 0.306 | 120 | 0.721 | 0 | 10.5 | 9.779
147 | SS 110/35/10 Kryukovo | 6.3 | 2.327 | 0.87 | 1 сутки | 1.457 | 0 | 6.62 | 5.163 | 4.543 | opened | 147 | SS 110/35/10 Kryukovo | 6.3 |  | 2.8755 | 0.87 | 1 сутки | 2.0055 | 0 | 6.62 | 4.6145 | 3.9945 | opened
| Nom. capacidty MV, МVА | 6.3 | 2.077 |  |  | 2.077 | 0 | 6.62 | 4.543 |  |  | 2: Nom. capacidty MV, МVА; 3: 6.3; 5: 2.6255; Мин. 8: 2.6255; Мин. 9: 0; Мин. 10: 6.62; Мин. 11: 3.9945
| Nom. capacity LV, МVА | 6.3 | 0.25 | 0.87 | 1 сутки | -0.62 | 0 | 6.62 | 7.24 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.25 | 0.87 | 1 сутки | -0.62 | 0 | 6.62 | 7.24
148 | SS 35/10 Beloe | 2.5 | 0.74 | 1.58 | 1 сутки | 1.58 | 0 | 1.58 | 0.84 | 0.84 | opened | 148 | SS 35/10 Beloe | 2.5 | 0.015 | 0.755 | 1.58 | 1 сутки | 1.58 | 0 | 1.58 | 0.825 | 0.825 | opened
149 | SS 110/35/10 Glebovo | 10 | 6.473 | 0.654 | 1 сутки | 5.819 | 0 | 10.5 | 4.681 | 4.681 | opened | 149 | SS 110/35/10 Glebovo | 10 |  | 8.2985 | 0.654 | 1 сутки | 7.6445 | 0 | 10.5 | 2.8555 | 2.8555 | opened
| Nom. capacity MV, МVА | 10 | 3.485 |  |  | 3.485 | 0 | 10.5 | 7.015 |  |  | 2: Nom. capacity MV, МVА; 3: 10; 5: 4.1185; Мин. 8: 4.1185; Мин. 9: 0; Мин. 10: 10.5; Мин. 11: 6.3815
| Nom. capacity LV, МVА | 10 | 2.988 | 0.654 | 1 сутки | 2.334 | 0 | 10.5 | 8.166 |  |  |  | Nom. capacity LV, МVА | 10 | 1.192 | 4.18 | 0.654 | 1 сутки | 3.526 | 0 | 10.5 | 6.974
150 | SS 35/10 Ermakovo | 1.6 | 1.02 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 0.66 | 0.66 | opened | 150 | SS 35/10 Ermakovo | 1.6 | 0.129 | 1.149 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 0.531 | 0.531 | opened
151 | SS 35/10 Milyushino | 1.6 | 0.78 | 1.053 | 1 сутки | 1.053 | 0 | 1.053 | 0.273 | 0.273 | opened | 151 | SS 35/10 Milyushino | 1.6 | 0.188 | 0.968 | 1.053 | 1 сутки | 1.053 | 0 | 1.053 | 0.085 | 0.085 | opened
152 | SS 35/10 Sutka | 2.5 | 0.68 | 0.87 | 1 сутки | 0.87 | 0 | 0.87 | 0.19 | 0.19 | opened | 152 | SS 35/10 Sutka | 2.5 | 0.022 | 0.702 | 0.87 | 1 сутки | 0.87 | 0 | 0.87 | 0.168 | 0.168 | opened
153 | SS 35/10 Sit | 1.6 | 0.55 | 0.55 | 1 сутки | 0.55 | 0 | 0.55 | 0 | 0 | opened | 153 | SS 35/10 Sit | 1.6 | 0.2713 | 0.8213 | 0.55 | 1 сутки | 0.55 | 0 | 0.55 | -0.2713 | -0.2713 | closed
154 | SS 35/10 Gorelovo | 1.6 | 0.67 | 0.78 | 1 сутки | 0.78 | 0 | 0.78 | 0.11 | 0.11 | opened | 154 | SS 35/10 Gorelovo | 1.6 | 0.331 | 1.001 | 0.78 | 1 сутки | 0.78 | 0 | 0.78 | -0.221 | -0.221 | closed
155 | SS 35/6 Pishchalkino | 1.6 | 0.89 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 0.79 | 0.79 | opened | 155 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.89 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 0.79 | 0.79 | opened
156 | SS 35/6 Varegovo | 1.6 | 0.258 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 1.422 | 1.422 | opened | 156 | SS 35/6 Varegovo | 1.6 | 0.013 | 0.271 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 1.409 | 1.409 | opened
157 | SS 35/10 Levoberezhnaya | 4 | 1.822 | 2 | 1 сутки | 2 | 0 | 2 | 0.178 | 0.178 | opened | 157 | SS 35/10 Levoberezhnaya | 4 |  | 1.822 | 2 | 1 сутки | 2 | 0 | 2 | 0.178 | 0.178 | opened
| Total: | 2622.6 | 907.894 | [8 empty] | 2: Total:; 3: 2622.6; 5: 1074.5919
| deficit | [8 empty] | -16.597 |  | 2: deficit; Мин. 12: -71.0177
| proficit | [8 empty] | 513.333 |  | 2: proficit; Мин. 12: 397.1757
Deputy Director fot technical
[13 empty] | issues - chief engineer | [8 empty] | Е.В. Турапин

## Свод тек.деф.зима
List of indoor main substations of IDGC of Centre or Winter loads 2009. (current capacity deficit).
No. | Object of main substation, voltage class | [5 empty] | Current deficit , MVA
Yarenergo
1 | SS 110/35/10 Abbakumtsevo | 10+10 |  |  |  |  | -0.6
2 | SS 110/35/6 Pavlovskaya | 20+25 |  |  |  |  | -0.5
3 | SS 110/35/10 Nila | 6,3+6,3 |  |  |  |  | -4.037
4 | SS 110/35/6 Pereslavl | 25+25 |  |  |  |  | -0.296
5 | SS 110/35/10 Rostov | 25+20 |  |  |  |  | -0.343
6 | SS 110/35/10 Technical school | 6,3+6,3 |  |  |  |  | -1.739
7 | SS 110/6 Kinoplyonka | 6,3+10 |  |  |  |  | -0.194
8 | SS 35/10 Vatolino | 2,5+4,0 |  |  |  |  | -0.89
9 | SS 35/10 Volna | 2,5+2,5 |  |  |  |  | -0.43
10 | SS 35/6 Zavolzhskaya | 10+10 | 3.48 | 3.48 | 0 | 2.63 | -1.93
11 | SS 35/10 Tutaev-35 | 6,3+6,3 | 11.67 | 11.67 | 0 | 10.5 | -0.92
12 | SS 35/10 Ryazantsevo | 1,6+1,6 | 45.91 | 45.91 | 0 | 42 | -0.173
13 | SS 35/10 Saraevo | 1,0+1,6 | 6.83 | 6.83 | 0 | 6.62 | -0.241
14 | SS 35/6 Pribrezhnaya | 10+10 |  |  |  |  | -2.506
15 | SS 35/10 Shirinye | 2.5 | 11.28 | 11.28 | 0 | 10.5 | -1.798
Total current deficit (Winter) | [6 empty] | -16.597

## Свод ожид.деф.зима
List of indoor main substations of IDGC of Centre for expected loads taking into account of new capacities on technological connection and other development of power grid complex.
No. | Object of main substation, voltage class | Expected deficit/proficit |  | Note
|  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Current deficit/ proficit, MVA
1 | 2 | 3 | 12 | 13
Yarenergo
1 | SS 35/10 Shirinye | 2.5 | -2.057 | closed
2 | SS 110/35/10 Abbakumtsevo | 10+10 | -5.518 | closed
3 | SS 35/10 Ananyino | 1,6+1,6 | -0.889 | closed
4 | SS 35/10 Vatolino | 2,5+4,0 | -1.596 | closed
5 | SS 35/10 Volna | 2,5+2,5 | -0.646 | closed
6 | SS 35/6 Zavolzhskaya | 10+10 | -4.345 | closed
7 | SS 110/6/6 Institutskaya | 40+40 | -0.441 | closed
8 | SS 35/10 Modelovo-2 | 6,3+6,3 | -0.245 | closed
9 | SS 35/10 Nekrasovo | 10+10 | -0.91437 | closed
10 | SS 110/35/6 Pavlovskaya | 20+25 | -0.89 | closed
11 | SS 110/10 Pereval | 16+16 | -2.283 | closed
12 | SS 110/6/6 Poligraf | 40+40 | -3.411 | closed
13 | SS 35/10 Preventorium | 2,5+2,5 | -0.6983 | closed
14 | SS 110/6 Tormoznaya | 16+16 | -0.503 | closed
15 | SS 35/10 Tutaev-35 | 6,3+6,3 | -1.27 | closed
16 | SS 110/6 Kinoplyonka | 6,3+10 | -3.048 | closed
17 | SS 110/35/10 Nila | 6,3+6,3 | -14.193 | closed
18 | SS 110/35/6 Pereslavl | 25+25 | -9.145 | closed
19 | SS 110/35/10 Rostov | 25+20 | -3.263 | closed
20 | SS 110/35/10 Technical school | 6,3+6,3 | -6.307 | closed
21 | SS 110/35/10 Uglich | 25+25 | -0.3945 | closed
22 | SS 35/10 Glebovo | 2,5+2,5 | -0.908 | closed
23 | SS 35/6 Kupan | 2,5+2,5 | -0.887 | closed
24 | SS 35/10 Nagorye | 4,0+4,0 | -0.085 | closed
25 | SS 35/10 Ryazantsevo | 1,6+1,6 | -0.288 | closed
26 | SS 35/10 Saraevo | 1+1,6 | -0.991 | closed
27 | SS 35/10 Solomidino | 2.5 | -1.201 | closed
28 | SS 35/6 Pribrezhnaya | 10+10 | -2.506 | closed
29 | SS 35/10 Breytovo | 4,0+4,0 | -1.603 | closed
30 | SS 35/10 Sit | 1.6 | -0.271 | closed
31 | SS 35/10 Gorelovo | 1.6 | -0.221 | closed
| Total: |  | -71.0182