## Summary
Transmission capacity calculation of supply centers of IDGC of Centre - Belgorodenergo division following the results of measurements of peak loads in winter 2011 | [13 empty] | Transmission capacity calculation of supply centers of IDGC of Centre - Belgorodenergo division following the results of measurements of peak loads in winter 2011
[13 empty] | Table 1 | [12 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [10 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | P | Q | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
[5 empty] | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | One-transformer substations
1 | SS-110/35/10kV D.Polyana | 6.3 | 1297 | 572 | 1.4175 | 1.457 | 45 | 1.457 | 0 | 1.457 | 0.039469 | -0.033615 | unavailable | 1 | SS-110/35/10kV D.Polyana | 6.3 | 0 | 1.4175 | 1.457 | 45 | -0.039469 | 0 | 1.457 | 0.039469 | -0.033615 | unavailable
| S nom MV, МVА | 6.3 | 920 | 370 | 0.99161 | 0.958 | 0 | 0.958 | 0 | 0.958 | -0.033615 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0.99161 | 0.958 | 0 | 0.033615 | 0 | 0.958 | -0.033615
| S nom LV, МVА | 6.3 | 377 | 202 | 0.42771 | 0.499 | 0 | 0.499 | 0 | 0.499 | 0.071293 |  |  |  | S nom LV, МVА | 6.3 | 0.005 | 0.43271 | 0.499 | 0 | -0.066293 | 0 | 0.499 | 0.066293
2 | SS-110/35/10kV Konshino | 6.3 | 323 | 171 | 0.36547 | 0.39 | 20 | 0.39 | 0 | 0.39 | 0.024528 | 0 |  | 2 | SS-110/35/10kV Konshino | 6.3 | 0 | 0.36547 | 0.39 | 20 | -0.024528 | 0 | 0.39 | 0.024528 | -0.013472
| S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, МVА | 6.3 | 323 | 171 | 0.36547 | 0.39 | 0 | 0.39 | 0 | 0.39 | 0.024528 |  |  |  | S nom LV, МVА | 6.3 | 0.038 | 0.40347 | 0.39 | 0 | 0.013472 | 0 | 0.39 | -0.013472
3 | SS-110/35/10kV Orositelnaya | 16 | 12776 | 4356 | 13.4982 | 11.607 | 120 | 11.607 | 0 | 11.607 | -1.8912 | -1.8912 | unavailable | 3 | SS-110/35/10kV Orositelnaya | 16 | 0.051 | 13.5492 | 11.607 | 120 | 1.9422 | 0 | 11.607 | -1.9422 | -1.9422 | unavailable
| S nom MV, МVА | 16 | 8266 | 2995 | 8.7919 | 8.606 | 0 | 8.606 | 0 | 8.606 | -0.18586 |  |  |  | S nom MV, МVА | 16 | 0 | 8.7919 | 8.606 | 0 | 0.18586 | 0 | 8.606 | -0.18586
| S nom LV, МVА | 16 | 4510 | 1361 | 4.7109 | 3.001 | 0 | 3.001 | 0 | 3.001 | -1.7099 |  |  |  | S nom LV, МVА | 16 | 0.051 | 4.7619 | 3.001 | 0 | 1.7609 | 0 | 3.001 | -1.7609
4 | SS-110/35/10kV Rovenki | 16 | 2483 | 1113 | 2.721 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.71896 | 0.71896 |  | 4 | SS-110/35/10kV Rovenki | 16 | 0 | 2.721 | 3.44 | 120 | -0.71896 | 0 | 3.44 | 0.71896 | 0.63179
| S nom MV, МVА | 16 | 2 | 0 | 0.002 | 4 | 0 | 4 | 0 | 4 | 3.998 |  |  |  | S nom MV, МVА | 16 | 0 | 0.002 | 4 | 0 | -3.998 | 0 | 4 | 3.998
| S nom LV, МVА | 16 | 2481 | 1113 | 2.7192 | 3.44 | 0 | 3.44 | 0 | 3.44 | 0.72079 |  |  |  | S nom LV, МVА | 16 | 0.089 | 2.8082 | 3.44 | 0 | -0.63179 | 0 | 3.44 | 0.63179
5 | SS-110/35/10kV Serebryanka | 10 | 866 | 344 | 0.93182 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.84818 | 0 |  | 5 | SS-110/35/10kV Serebryanka | 10 | 0 | 0.93182 | 1.78 | 45 | -0.84818 | 0 | 1.78 | 0.84818 | 0
| S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, MVА | 10 | 866 | 344 | 0.93182 | 1.78 | 0 | 1.78 | 0 | 1.78 | 0.84818 |  |  |  | S nom LV, MVА | 10 | 0.045 | 0.97682 | 1.78 | 0 | -0.80318 | 0 | 1.78 | 0.80318
6 | SS-35/10kV Afanasyevka | 2.5 | 880 | 320 | 0.93638 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.28998 | -0.28998 | unavailable | 6 | SS-35/10kV Afanasyevka | 1.6 | 0.005 | 0.94138 | 0.6464 | 45 | 0.29498 | 0 | 0.6464 | -0.29498 | -0.29498 | unavailable
7 | SS-35/10kV Borisovka | 1.6 | 664 | 200 | 0.69347 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | -0.0099667 | -0.0099667 | unavailable | 7 | SS-35/10kV Borisovka | 1.6 | 0 | 0.69347 | 0.6835 | 45 | 0.0099667 | 0 | 0.6835 | -0.0099667 | -0.0099667 | unavailable
8 | SS-35/10kV Borisy | 1.6 | 798 | 366 | 0.87793 | 0 | 20 | 0 | 0 | 0 | -0.87793 | -0.87793 | unavailable | 8 | SS-35/10kV Borisy | 1.6 | 0.01 | 0.88793 | 0 | 20 | 0.88793 | 0 | 0 | -0.88793 | -0.88793 | unavailable
9 | SS-35/10kV Gostishchevo | 4 | 2680 | 1016 | 2.8661 | 2.64 | 80 | 2.64 | 0 | 2.64 | -0.22612 | -0.22612 | unavailable | 9 | SS-35/10kV Gostishchevo | 4 | 0.28 | 3.1461 | 2.64 | 80 | 0.50612 | 0 | 2.64 | -0.50612 | -0.50612 | unavailable
10 | SS-35/10kV Gruzskoe | 1.6 | 612 | 288 | 0.67638 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.37362 | 0.37362 |  | 10 | SS-35/10kV Gruzskoe | 1.6 | 0.005 | 0.68138 | 1.05 | 80 | -0.36862 | 0 | 1.05 | 0.36862 | 0.36862
11 | SS-35/10kV Zemsnaryad | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | SS-35/10kV Zemsnaryad | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 348 | 120 | 0.36811 | 0 | 0 | 0 | 0 | 0 | -0.36811 | -0.36811 | unavailable | 12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 0 | 0.36811 | 0 | 0 | 0.36811 | 0 | 0 | -0.36811 | -0.36811 | unavailable
13 | SS-35/10kV Kamyzino | 2.5 | 1184 | 784 | 1.42 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.87904 | -0.87904 | unavailable | 13 | SS-35/10kV Kamyzino | 2.5 | 0.0443 | 1.4643 | 0.541 | 45 | 0.92334 | 0 | 0.541 | -0.92334 | -0.92334 | unavailable
14 | SS-35/10kV Koloskovo | 2.5 | 1712 | 544 | 1.7964 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.13375 | -0.13375 | unavailable | 14 | SS-35/10kV Koloskovo | 2.5 | 0.0898 | 1.8862 | 1.6626 | 45 | 0.22355 | 0 | 1.6626 | -0.22355 | -0.22355 | unavailable
15 | SS-35/10jkV Kryukovo | 2.5 | 1140 | 468 | 1.2323 | 1.55 | 45 | 1.55 | 0 | 1.55 | 0.31768 | 0.31768 |  | 15 | SS-35/10jkV Kryukovo | 2.5 | 0.057 | 1.2893 | 1.55 | 45 | -0.26068 | 0 | 1.55 | 0.26068 | 0.26068
16 | SS-35/10kV Kushchino | 1.6 | 360 | 132 | 0.38344 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.026663 | 0.026663 |  | 16 | SS-35/10kV Kushchino | 1.6 | 0.029 | 0.41244 | 0.4101 | 80 | 0.0023371 | 0 | 0.4101 | -0.0023371 | -0.0023371
17 | SS-35/10kV Lopukhinka | 2.5 | 304 | 120 | 0.32683 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.080173 | 0.080173 |  | 17 | SS-35/10kV Lopukhinka | 2.5 | 0 | 0.32683 | 0.407 | 20 | -0.080173 | 0 | 0.407 | 0.080173 | 0.080173
18 | SS-35/10kV Malakeevo | 2.5 | 1032 | 564 | 1.1761 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.20394 | 0.20394 |  | 18 | SS-35/10kV Malakeevo | 2.5 | 0.01 | 1.1861 | 1.38 | 120 | -0.19394 | 0 | 1.38 | 0.19394 | 0.19394
19 | SS-35/10kV Murom | 2.5 | 1192 | 512 | 1.2973 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.24269 | 0.24269 |  | 19 | SS-35/10kV Murom | 2.5 | 0.026 | 1.3233 | 1.54 | 45 | -0.21669 | 0 | 1.54 | 0.21669 | 0.21669
20 | SS-35/10kV Nikolaevka | 2.5 | 672 | 304 | 0.73756 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.072864 | -0.072864 | unavailable | 20 | SS-35/10kV Nikolaevka | 2.5 | 0.014 | 0.75156 | 0.6647 | 45 | 0.086864 | 0 | 0.6647 | -0.086864 | -0.086864 | unavailable
21 | SS-35/10kV Nikolskoe | 4 | 1632 | 408 | 1.6822 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.90223 | -0.90223 | unavailable | 21 | SS-35/10kV Nikolskoe | 4 | 0.684 | 2.3662 | 0.78 | 120 | 1.5862 | 0 | 0.78 | -1.5862 | -1.5862 | unavailable
22 | SS-35/10kV Pokrovka | 2.5 | 576 | 204 | 0.61106 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.11094 | 0.11094 |  | 22 | SS-35/10kV Pokrovka | 4 | 0 | 0.61106 | 0.722 | 45 | -0.11094 | 0 | 0.722 | 0.11094 | 0.11094
23 | SS-35/10kV Pyatnitskoe | 4 | 2062 | 834 | 2.2243 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.38428 | -0.38428 | unavailable | 23 | SS-35/10kV Pyatnitskoe | 4 | 0.055 | 2.2793 | 1.84 | 80 | 0.43928 | 0 | 1.84 | -0.43928 | -0.43928 | unavailable
24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 590 | 511 | 0.78053 | 1.676 | 80 | 1.676 | 0 | 1.676 | 0.89547 | 0.89547 |  | 24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 0 | 0.78053 | 1.676 | 80 | -0.89547 | 0 | 1.676 | 0.89547 | 0.89547
25 | SS-35/10kV Svistovka | 2.5 | 488 | 224 | 0.53695 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.15025 | 0.15025 |  | 25 | SS-35/10kV Svistovka | 2.5 | 0.005 | 0.54195 | 0.6872 | 45 | -0.14525 | 0 | 0.6872 | 0.14525 | 0.14525
26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 512 | 176 | 0.54141 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.18239 | 0.18239 |  | 26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 0 | 0.54141 | 0.7238 | 120 | -0.18239 | 0 | 0.7238 | 0.18239 | 0.18239
27 | SS-35/10kV Kharkovskaya | 2.5 | 572 | 244 | 0.62187 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.057832 | 0.057832 |  | 27 | SS-35/10kV Kharkovskaya | 2.5 | 0 | 0.62187 | 0.6797 | 120 | -0.057832 | 0 | 0.6797 | 0.057832 | 0.057832
Two- and more transformer substations | [13 empty] | Two- and more transformer substations
28 | SS-110/6kV Automobile maintenance plant | 16+16 | 11055 | 5112 | 12.1797 | 3.561 | 45 | 8.6187 | 0 | 16.8 | 8.1813 | 8.1813 |  | 28 | SS-110/6kV Automobile maintenance plant | 16+16 | 0.06 | 12.2397 | 3.561 | 45 | 8.6787 | 0 | 16.8 | 8.1213 | 8.1213
29 | SS-110/35/10kV Aydar | 16+10 | 8005 | 3233 | 8.6332 | 8.95 | 120 | -0.31679 | 0 | 10.5 | 10.8168 | 10.5637 |  | 29 | SS-110/35/10kV Aydar | 16+10 | 0 | 8.6332 | 8.95 | 120 | -0.31679 | 0 | 10.5 | 10.8168 | 10.5637
| S nom MV, МVА | 16+10 | 6709 | 2685 | 7.2263 | 7.29 | 0 | -0.063666 | 0 | 10.5 | 10.5637 |  |  |  | S nom MV, МVА | 16+10 | 0 | 7.2263 | 7.29 | 0 | -0.063666 | 0 | 10.5 | 10.5637
| S nom LV, МVА | 16+10 | 1296 | 548 | 1.4071 | 1.66 | 0 | -0.2529 | 0 | 10.5 | 10.7529 |  |  |  | S nom LV, МVА | 16+10 | 0.008 | 1.4151 | 1.66 | 0 | -0.2449 | 0 | 10.5 | 10.7449
30 | SS-110/35/10kV Alexandrovka | 25+25 | 14291 | 5721 | 15.3936 | 8.37 | 80 | 7.0236 | 0 | 26.25 | 19.2264 | 19.2264 |  | 30 | SS-110/35/10kV Alexandrovka | 25+25 | 0 | 15.3936 | 8.37 | 80 | 7.0236 | 0 | 26.25 | 19.2264 | 19.1003
| S nom MV, МVА | 25+25 | 6817 | 2487 | 7.2565 | 6.697 | 0 | 0.55949 | 0 | 26.25 | 25.6905 |  |  |  | S nom MV, МVА | 25+25 | 0 | 7.2565 | 6.697 | 0 | 0.55949 | 0 | 26.25 | 25.6905
| S nom LV, МVА | 25+25 | 7474 | 3234 | 8.1437 | 1.673 | 0 | 6.4707 | 0 | 26.25 | 19.7793 |  |  |  | S nom LV, МVА | 25+25 | 0.679 | 8.8227 | 1.673 | 0 | 7.1497 | 0 | 26.25 | 19.1003
31 | SS-110/35/10kV Alexeevka | 25+25+25 | 39234 | 13535 | 41.503 | 5.322 | 120 | 36.181 | 0 | 52.5 | 16.319 | 16.319 |  | 31 | SS-110/35/10kV Alexeevka | 25+25+25 | 0 | 41.503 | 5.322 | 120 | 36.181 | 0 | 52.5 | 16.319 | 16.319
| S nom MV, МVА | 25+25+25 | 18194 | 4255 | 18.6849 | 3.102 | 0 | 15.5829 | 0 | 52.5 | 36.9171 |  |  |  | S nom MV, МVА | 25+25+25 | 0 | 18.6849 | 3.102 | 0 | 15.5829 | 0 | 52.5 | 36.9171
| S nom LV, МVА | 25+25+25 | 21040 | 9280 | 22.9957 | 2.22 | 0 | 20.7757 | 0 | 52.5 | 31.7243 |  |  |  | S nom LV, МVА | 25+25+25 | 1.231 | 24.2267 | 2.22 | 0 | 22.0067 | 0 | 52.5 | 30.4933
32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 8788 | 3690 | 9.5313 | 8.87 | 45 | 0.66127 | 0 | 10.5 | 9.8387 | 9.8387 |  | 32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 0 | 9.5313 | 8.87 | 45 | 0.66127 | 0 | 10.5 | 9.8387 | 9.8387
| S nom MV, МVА | 10+16 | 8463 | 3599 | 9.1965 | 8.867 | 0 | 0.32948 | 0 | 10.5 | 10.1705 |  |  |  | S nom MV, МVА | 10+16 | 0 | 9.1965 | 8.867 | 0 | 0.32948 | 0 | 10.5 | 10.1705
| S nom LV, МVА | 10+16 | 325 | 91 | 0.3375 | 0 | 0 | 0.3375 | 0 | 10.5 | 10.1625 |  |  |  | S nom LV, МVА | 10+16 | 0.04 | 0.3775 | 0 | 0 | 0.3775 | 0 | 10.5 | 10.1225
33 | SS-110/6kV Belgorod-1 | 40+40+40 | 28766 | 12827 | 31.4963 | 0 | 120 | 31.4963 | 0 | 84 | 52.5037 | 52.5037 |  | 33 | SS-110/6kV Belgorod-1 | 40+40+40 | 1.056 | 32.5523 | 0 | 120 | 32.5523 | 0 | 84 | 51.4477 | 51.4477
34 | SS-110/35/10kV Borisovka | 16+16 | 10972 | 4956 | 12.0394 | 11.433 | 120 | 0.60638 | 0 | 16.8 | 16.1936 | 5.6302 |  | 34 | SS-110/35/10kV Borisovka | 16+16 | 0 | 12.0394 | 11.433 | 120 | 0.60638 | 0 | 16.8 | 16.1936 | 5.4102
| S nom MV, МVА | 16+16 | 5280 | 2848 | 5.9991 | 8.133 | 0 | -2.1339 | 0 | 8.4 | 10.5339 |  |  |  | S nom MV, МVА | 16+8 | 0 | 5.9991 | 8.133 | 0 | -2.1339 | 0 | 8.4 | 10.5339
| S nom LV, МVА | 16+16 | 5692 | 2108 | 6.0698 | 3.3 | 0 | 2.7698 | 0 | 8.4 | 5.6302 |  |  |  | S nom LV, МVА | 16+8 | 0.22 | 6.2898 | 3.3 | 0 | 2.9898 | 0 | 8.4 | 5.4102
35 | SS-110/35/10kV V.Pokrovka | 10+10 | 9963 | 3940 | 10.7138 | 11.5 | 120 | -0.78623 | 0 | 10.5 | 11.2862 | 8.955 |  | 35 | SS-110/35/10kV V.Pokrovka | 10+10 | 0 | 10.7138 | 11.5 | 120 | -0.78623 | 0 | 10.5 | 11.2862 | 8.955
| S nom MV, МVА | 10+10 | 8666 | 3497 | 9.345 | 7.8 | 0 | 1.545 | 0 | 10.5 | 8.955 |  |  |  | S nom MV, МVА | 10+10 | 0 | 9.345 | 7.8 | 0 | 1.545 | 0 | 10.5 | 8.955
| S nom LV, МVА | 10+10 | 1297 | 443 | 1.3706 | 3.7 | 0 | -2.3294 | 0 | 10.5 | 12.8294 |  |  |  | S nom LV, МVА | 10+10 | 0.026 | 1.3966 | 3.7 | 0 | -2.3034 | 0 | 10.5 | 12.8034
36 | SS-110/35/10kV Veydelevka | 10+10 | 7968 | 3078 | 8.5418 | 8.83 | 120 | -0.28816 | 0 | 10.5 | 10.7882 | 9.8726 |  | 36 | SS-110/35/10kV Veydelevka | 10+10 | 0 | 8.5418 | 8.83 | 120 | -0.28816 | 0 | 10.5 | 10.7882 | 9.8726
| S nom MV, МVА | 10+10 | 4277 | 1645 | 4.5824 | 3.955 | 0 | 0.62744 | 0 | 10.5 | 9.8726 |  |  |  | S nom MV, МVА | 10+10 | 0 | 4.5824 | 3.955 | 0 | 0.62744 | 0 | 10.5 | 9.8726
| S nom LV, МVА | 10+10 | 3691 | 1433 | 3.9594 | 4.875 | 0 | -0.91558 | 0 | 10.5 | 11.4156 |  |  |  | S nom LV, МVА | 10+10 | 0.135 | 4.0944 | 4.875 | 0 | -0.78058 | 0 | 10.5 | 11.2806
37 | SS-110/6kV Vitamin plant | 25+25 | 13444 | 5411 | 14.4921 | 1.46 | 45 | 13.0321 | 0 | 26.25 | 13.2179 | 13.2179 |  | 37 | SS-110/6kV Vitamin plant | 25+25 | 3.022 | 17.5141 | 1.46 | 45 | 16.0541 | 0 | 26.25 | 10.1959 | 10.1959
38 | SS-110/35/10kV Volokonovka | 25+25 | 15310 | 7548 | 17.0695 | 10.651 | 120 | 6.4185 | 0 | 26.25 | 19.8315 | 19.8315 |  | 38 | SS-110/35/10kV Volokonovka | 25+25 | 0 | 17.0695 | 10.651 | 120 | 6.4185 | 0 | 26.25 | 19.8315 | 19.8315
| S nom MV, МVА | 25+25 | 7879 | 4389 | 9.019 | 8.576 | 0 | 0.44298 | 0 | 26.25 | 25.807 |  |  |  | S nom MV, МVА | 25+25 | 0 | 9.019 | 8.576 | 0 | 0.44298 | 0 | 26.25 | 25.807
| S nom LV, МVА | 25+25 | 7431 | 3159 | 8.0746 | 2.075 | 0 | 5.9996 | 0 | 26.25 | 20.2504 |  |  |  | S nom LV, МVА | 25+25 | 0.195 | 8.2696 | 2.075 | 0 | 6.1946 | 0 | 26.25 | 20.0554
39 | SS-110/35/6kV Vostochnaya | 25+25 | 36506 | 13922 | 39.0706 | 0 | 120 | 39.0706 | 0 | 26.25 | 4.1794 | 4.179 |  | 39 | SS-110/35/6kV Vostochnaya | 25+25 | 2.8357 | 41.9063 | 17 | 120 | 24.9063 | 0 | 26.25 | 1.3437 | 1.3437
| S nom MV, МVА | 25+25 | 21043 | 7602 | 22.3741 | 0 | 0 | 22.3741 | 0 | 26.25 | 20.8759 |  |  |  | S nom MV, МVА | 25+25 | 0 | 22.3741 | 17 | 30 | 5.3741 | 0 | 26.25 | 20.8759
| S nom LV, МVА | 25+25 | 15463 | 6320 | 16.7047 | 0 | 0 | 16.7047 | 0 | 26.25 | 8.7103 |  |  |  | S nom LV, МVА | 25+25 | 2.8357 | 19.5404 | 0 | 0 | 19.5404 | 0 | 26.25 | 6.7096
40 | SS-110/10/6kV Golofeevka | 16+16 | 1892 | 844 | 2.0717 | 0 | 0 | 2.0717 | 0 | 16.8 | 14.73 | 14.73 |  | 40 | SS-110/10/6kV Golofeevka | 16+16 | 0 | 2.0717 | 0 | 0 | 2.0717 | 0 | 16.8 | 14.7283 | 14.6833
| S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8 |  |  |  | S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8
| S nom LV, МVА | 16+16 | 1892 | 844 | 2.0717 | 0 | 0 | 2.0717 | 0 | 16.8 | 14.73 |  |  |  | S nom LV, МVА | 16+16 | 0.045 | 2.1167 | 0 | 0 | 2.1167 | 0 | 16.8 | 14.6833
41 | SS-110/10kV Gotnya | 16+16 | 7966 | 3934 | 8.8845 | 6.43 | 120 | 2.4545 | 0 | 16.8 | 14.3455 | 14.3455 |  | 41 | SS-110/10kV Gotnya | 16+16 | 0.085 | 8.9695 | 6.43 | 120 | 2.5395 | 0 | 16.8 | 14.2605 | 14.2605
42 | SS-110/35/10kV Grayvoron | 16+16 | 11753 | 5119 | 12.8194 | 13.953 | 80 | -1.1336 | 0 | 16.8 | 17.9336 | 14.7436 |  | 42 | SS-110/35/10kV Grayvoron | 16+16 | 0 | 12.8194 | 13.953 | 80 | -1.1336 | 0 | 16.8 | 17.9336 | 14.5296
| S nom MV, МVА | 16+16 | 7085 | 3049 | 7.7132 | 10.903 | 0 | -3.1898 | 0 | 16.8 | 19.9898 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.7132 | 10.903 | 0 | -3.1898 | 0 | 16.8 | 19.9898
| S nom LV, МVА | 16+16 | 4668 | 2070 | 5.1064 | 3.05 | 0 | 2.0564 | 0 | 16.8 | 14.7436 |  |  |  | S nom LV, МVА | 16+16 | 0.214 | 5.3204 | 3.05 | 0 | 2.2704 | 0 | 16.8 | 14.5296
43 | SS-110/6kV Donets | 40+40 | 24768 | 7776 | 25.96 | 6.73 | 120 | 19.23 | 0 | 42 | 22.77 | 22.77 |  | 43 | SS-110/6kV Donets | 40+40 | 0.923 | 26.883 | 6.73 | 120 | 20.153 | 0 | 42 | 21.847 | 21.847
44 | SS-110/10kV Dubovoe | 40+40 | 14374 | 2966 | 14.6768 | 11.23 | 120 | 3.4468 | 0 | 42 | 38.5532 | 38.5532 |  | 44 | SS-110/10kV Dubovoe | 40+40 | 0.185 | 14.8618 | 11.23 | 120 | 3.6318 | 0 | 42 | 38.3682 | 38.3682
45 | SS-110/35/6kV Zhuravliki | 40+25 | 19168 | 6753 | 20.3228 | 12.4 | 120 | 7.9228 | 0 | 42 | 34.0772 | 32.987 |  | 45 | SS-110/35/6kV Zhuravliki | 40+25 | 0 | 20.3228 | 12.4 | 120 | 7.9228 | 0 | 42 | 34.0772 | 32.987
| S nom MV, МVА | 40+25 | 14146 | 5670 | 15.24 | 6.227 | 0 | 9.013 | 0 | 42 | 32.987 |  |  |  | S nom MV, МVА | 40+25 | 0 | 15.24 | 6.227 | 0 | 9.013 | 0 | 42 | 32.987
| S nom LV, МVА | 40+25 | 5022 | 1083 | 5.1374 | 6.173 | 0 | -1.0356 | 0 | 42 | 43.0356 |  |  |  | S nom LV, МVА | 40+25 | 0.2453 | 5.3827 | 6.173 | 0 | -0.79025 | 0 | 42 | 42.7903
46 | SS-110/10kV Zapadnaya | 16+16 | 15349 | 4383 | 15.9625 | 1.249 | 80 | 14.7135 | 0 | 16.8 | 2.0865 | 2.0865 |  | 46 | SS-110/10kV Zapadnaya | 16+16 | 1.5732 | 17.5357 | 1.249 | 80 | 16.2867 | 0 | 16.8 | 0.51327 | 0.51327
47 | SS-110/35/10kV Ivnya | 10+10 | 5687 | 2849 | 6.3607 | 6.16 | 80 | 0.20072 | 0 | 10.5 | 10.2993 | 10.0222 |  | 47 | SS-110/35/10kV Ivnya | 10+10 | 0 | 6.3607 | 6.16 | 80 | 0.20072 | 0 | 10.5 | 10.2993 | 10.0222
| S nom MV, МVА | 10+10 | 2411 | 1525 | 2.8528 | 2.375 | 0 | 0.47781 | 0 | 10.5 | 10.0222 |  |  |  | S nom MV, МVА | 10+10 | 0 | 2.8528 | 2.375 | 0 | 0.47781 | 0 | 10.5 | 10.0222
| S nom LV, МVА | 10+10 | 3276 | 1324 | 3.5334 | 3.785 | 0 | -0.25157 | 0 | 10.5 | 10.7516 |  |  |  | S nom LV, МVА | 10+10 | 0.2 | 3.7334 | 3.785 | 0 | -0.051567 | 0 | 10.5 | 10.5516
48 | SS-110/35/10kV K.Gvardiya | 16+16 | 12564 | 5234 | 13.6106 | 7.7116 | 120 | 5.899 | 0 | 16.8 | 10.901 | 10.901 |  | 48 | SS-110/35/10kV K.Gvardiya | 16+16 | 0 | 13.6106 | 7.7116 | 120 | 5.899 | 0 | 16.8 | 10.901 | 10.901
| S nom MV, МVА | 16+16 | 6168 | 2716 | 6.7395 | 4.854 | 0 | 1.8855 | 0 | 16.8 | 14.9145 |  |  |  | S nom MV, МVА | 16+16 | 0 | 6.7395 | 4.854 | 0 | 1.8855 | 0 | 16.8 | 14.9145
| S nom LV, МVА | 16+16 | 6396 | 2518 | 6.8738 | 2.8576 | 0 | 4.0162 | 0 | 16.8 | 12.7838 |  |  |  | S nom LV, МVА | 16+16 | 0.1655 | 7.0393 | 2.8576 | 0 | 4.1817 | 0 | 16.8 | 12.6183
49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 10838 | 3920 | 11.5251 | 9.65 | 80 | 1.8751 | 0 | 26.25 | 24.3749 | 20.1687 |  | 49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 0 | 11.5251 | 9.65 | 80 | 1.8751 | 0 | 26.25 | 24.3749 | 19.8907
| S nom MV, МVА | 25+25 | 1372 | 452 | 1.4445 | 1.384 | 0 | 0.060537 | 0 | 26.25 | 26.1895 |  |  |  | S nom MV, МVА | 25+25 | 0 | 1.4445 | 1.384 | 0 | 0.060537 | 0 | 26.25 | 26.1895
| S nom LV, МVА | 25+25 | 9466 | 3468 | 10.0813 | 4 | 0 | 6.0813 | 0 | 26.25 | 20.1687 |  |  |  | S nom LV, МVА | 25+25 | 0.278 | 10.3593 | 4 | 0 | 6.3593 | 0 | 26.25 | 19.8907
50 | SS-110/35/10kV Korocha | 16+16+16 | 20782 | 9337 | 22.7831 | 2.019 | 20 | 20.7641 | 0 | 33.6 | 12.8359 | 12.8359 |  | 50 | SS-110/35/10kV Korocha | 16+16+16 | 0.002 | 22.7851 | 2.019 | 20 | 20.7661 | 0 | 33.6 | 12.8339 | 12.8339
| S nom MV, МVА | 16+16+16 | 7844 | 3297 | 8.5087 | 1.719 | 0 | 6.7897 | 0 | 33.6 | 26.8103 |  |  |  | S nom MV, МVА | 16+16+16 | 0 | 8.5087 | 1.719 | 0 | 6.7897 | 0 | 33.6 | 26.8103
| S nom LV, МVА | 16+16+16 | 12938 | 6040 | 14.2784 | 0.3 | 0 | 13.9784 | 0 | 33.6 | 19.6216 |  |  |  | S nom LV, МVА | 16+16+16 | 0.603 | 14.8814 | 0.3 | 0 | 14.5814 | 0 | 33.6 | 19.0186
51 | SS-110/10kV Krapivenskaya | 16+16 | 3910 | 1344 | 4.1345 | 0 | 0 | 4.1345 | 0 | 16.8 | 12.6655 | 12.6655 |  | 51 | SS-110/10kV Krapivenskaya | 10+10 | 0 | 9.6441 | 9.158 | 120 | 0.48607 | 0 | 10.5 | 10.0139 | 9.7276
52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 8819 | 3903 | 9.6441 | 9.158 | 120 | 0.48607 | 0 | 10.5 | 10.0139 | 9.7276 |  | 52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 0 | 4.2924 | 3.52 | 0 | 0.77239 | 0 | 10.5 | 9.7276
| S nom MV, МVА | 10+10 | 3963 | 1649 | 4.2924 | 3.52 | 0 | 0.77239 | 0 | 10.5 | 9.7276 |  |  |  | S nom MV, МVА | 10+10 | 0.271 | 5.6246 | 5.638 | 0 | -0.01338 | 0 | 10.5 | 10.5134
| S nom LV, МVА | 10+10 | 4856 | 2254 | 5.3536 | 5.638 | 0 | -0.28438 | 0 | 10.5 | 10.7844 |  |  |  | S nom LV, МVА | 16+16 | 0.75 | 4.8845 | 0 | 0 | 4.8845 | 0 | 16.8 | 11.9155 | 11.9155
53 | SS-110/10/10kV Mayskaya | 40+40 | 9072 | 1687 | 9.2275 | 0 | 0 | 9.2275 | 0 | 42 | 32.7725 | 32.7725 |  | 53 | SS-110/10/10kV Mayskaya | 40+40 | 0.7472 | 9.9747 | 0 | 0 | 9.9747 | 0 | 42 | 32.0253 | 32.0253
54 | SS-110/35/10kV Maximovka | 16+16 | 11362 | 6568 | 13.1238 | 11.48 | 45 | 1.6438 | 0 | 16.8 | 15.1562 | 14.6504 |  | 54 | SS-110/35/10kV Maximovka | 16+16 | 0.008 | 13.1318 | 11.48 | 45 | 1.6518 | 0 | 16.8 | 15.1482 | 14.6504
| S nom MV, МVА | 16+16 | 9914 | 6020 | 11.5986 | 9.449 | 0 | 2.1496 | 0 | 16.8 | 14.6504 |  |  |  | S nom MV, МVА | 16+16 | 0 | 11.5986 | 9.449 | 0 | 2.1496 | 0 | 16.8 | 14.6504
| S nom LV, МVА | 16+16 | 1448 | 548 | 1.5482 | 2.031 | 0 | -0.48277 | 0 | 16.8 | 17.2828 |  |  |  | S nom LV, МVА | 16+16 | 0.008 | 1.5562 | 2.031 | 0 | -0.47477 | 0 | 16.8 | 17.2748
55 | SS-110/35/10kV N.Oskol | 25+31,5 | 16135 | 6490 | 17.3913 | 9.119 | 80 | 8.2723 | 0 | 26.25 | 17.9777 | 16.3926 |  | 55 | SS-110/35/10kV N.Oskol | 25+31,5 | 0 | 17.3913 | 9.119 | 80 | 8.2723 | 0 | 26.25 | 17.9777 | 16.1836
| S nom MV, МVА | 25+31,5 | 5615 | 2806 | 6.2771 | 7.83 | 0 | -1.5529 | 0 | 26.25 | 27.8029 |  |  |  | S nom MV, МVА | 25+31,5 | 0 | 6.2771 | 7.83 | 0 | -1.5529 | 0 | 26.25 | 27.8029
| S nom LV, МVА | 25+31,5 | 10520 | 3684 | 11.1464 | 1.289 | 0 | 9.8574 | 0 | 26.25 | 16.3926 |  |  |  | S nom LV, МVА | 25+31,5 | 0.209 | 11.3554 | 1.289 | 0 | 10.0664 | 0 | 26.25 | 16.1836
56 | SS-110/10kV Obukhovskaya | 25+25 | 2046 | 713 | 2.1667 | 0 | 0 | 2.1667 | 0 | 26.25 | 24.0833 | 24.0833 |  | 56 | SS-110/10kV Obukhovskaya | 25+25 | 0.045 | 2.2117 | 0 | 0 | 2.2117 | 0 | 26.25 | 24.0383 | 24.0383
57 | SS-110/6kV Ochistnye | 16+16 | 4472 | 2208 | 4.9874 | 0 | 0 | 4.9874 | 0 | 16.8 | 11.8126 | 11.8126 |  | 57 | SS-110/6kV Ochistnye | 16+16 | 0.018 | 5.0054 | 0 | 0 | 5.0054 | 0 | 16.8 | 11.7946 | 11.7946
58 | SS-110/35/6kV Pishcheprom | 25+25 | 3557 | 1394 | 3.8204 | 6.679 | 120 | 6.679 | 0 | 26.25 | 22.4296 | 22.4296 |  | 58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 3.8204 | 6.679 | 120 | -2.8586 | 0 | 26.25 | 22.4296 | 21.1574
| S nom MV, МVА | 25+25 | 176 | 205 | 0.27019 | 2.022 | 0 | 2.022 | 0 | 26.25 | 25.9798 |  |  |  | S nom MV, МVА | 25+25 | 0 | 0.27019 | 2.022 | 0 | -1.7518 | 0 | 26.25 | 25.9798
| S nom LV, МVА | 25+25 | 3381 | 1189 | 3.584 | 4.657 | 0 | 4.657 | 0 | 26.25 | 22.666 |  |  |  | S nom LV, МVА | 25+25 | 1.5086 | 5.0926 | 4.657 | 0 | 0.43558 | 0 | 26.25 | 21.1574
59 | SS-110/10kV Promyshlennaya | 25+25 | 15211 | 7256 | 16.853 | 0 | 0 | 16.853 | 0 | 26.25 | 9.397 | 9.397 |  | 59 | SS-110/10kV Promyshlennaya | 25+25 | 0.327 | 17.18 | 0 | 0 | 17.18 | 0 | 26.25 | 9.07 | 9.07
60 | SS-110/10kV Poultry plant | 16+16 | 11361 | 6643 | 13.1606 | 1.296 | 80 | 11.8646 | 0 | 16.8 | 4.9354 | 4.9354 |  | 60 | SS-110/10kV Poultry plant | 16+16 | 0.015 | 13.1756 | 1.296 | 80 | 11.8796 | 0 | 16.8 | 4.9204 | 4.9204
61 | SS-110/10kV Pushkarnaya | 40+40 | 28662 | 9012 | 30.0454 | 0 | 60 | 30.0454 | 0 | 42 | 11.9546 | 11.9546 |  | 61 | SS-110/10kV Pushkarnaya | 40+40 | 0.221 | 30.2664 | 0 | 60 | 30.2664 | 0 | 42 | 11.7336 | 11.7336
62 | SS-110/35/10kV Rakitnoe | 10+10 | 9613 | 5415 | 11.0332 | 8.98 | 120 | 2.0532 | 0 | 10.5 | 8.4468 | 8.4468 |  | 62 | SS-110/35/10kV Rakitnoe | 10+10 | 0 | 11.0332 | 8.98 | 120 | 2.0532 | 0 | 10.5 | 8.4468 | 8.4468
| S nom MV, МVА | 10+10 | 6619 | 4137 | 7.8055 | 6.407 | 0 | 1.3985 | 0 | 10.5 | 9.1015 |  |  |  | S nom MV, МVА | 10+10 | 0 | 7.8055 | 6.407 | 0 | 1.3985 | 0 | 10.5 | 9.1015
| S nom LV, МVА | 10+10 | 2994 | 1278 | 3.2554 | 2.573 | 0 | 0.68235 | 0 | 10.5 | 9.8176 |  |  |  | S nom LV, МVА | 10+10 | 0.075 | 3.3304 | 2.573 | 0 | 0.75735 | 0 | 10.5 | 9.7426
63 | SS-110/35/6kV Rudnik | 25+25 | 16522 | 9562 | 19.0895 | 10.46 | 45 | 8.6295 | 0 | 26.25 | 17.6205 | 17.6205 |  | 63 | SS-110/35/6kV Rudnik | 25+25 | 0 | 19.0895 | 10.46 | 45 | 8.6295 | 0 | 26.25 | 17.6205 | 17.6205
| S nom MV, МVА | 25+25 | 10086 | 5369 | 11.426 | 10.46 | 0 | 0.966 | 0 | 26.25 | 25.284 |  |  |  | S nom MV, МVА | 25+25 | 0 | 11.426 | 10.46 | 0 | 0.966 | 0 | 26.25 | 25.284
| S nom LV, МVА | 25+25 | 6436 | 4193 | 7.6814 | 0 | 0 | 7.6814 | 0 | 26.25 | 18.5686 |  |  |  | S nom LV, МVА | 25+25 | 0.305 | 7.9864 | 0 | 0 | 7.9864 | 0 | 26.25 | 18.2636
64 | SS-110/10kV Severnaya | 40+40 | 13031 | 3928 | 13.6101 | 3.312 | 45 | 10.2981 | 0 | 42 | 31.7019 | 31.7019 |  | 64 | SS-110/10kV Severnaya | 40+40 | 1.3145 | 14.9246 | 3.312 | 45 | 11.6126 | 0 | 42 | 30.3874 | 30.3874
65 | SS-110/35/10kV Skorodnoe | 16+16 | 10734 | 4354 | 11.5834 | 10.36 | 120 | 1.2234 | 0 | 16.8 | 15.5766 | 15.4492 |  | 65 | SS-110/35/10kV Skorodnoe | 16+16 | 0 | 11.5834 | 10.36 | 120 | 1.2234 | 0 | 16.8 | 15.5766 | 15.3872
| S nom MV, МVА | 16+16 | 6880 | 2818 | 7.4348 | 7.562 | 0 | -0.12725 | 0 | 16.8 | 16.9272 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.4348 | 7.562 | 0 | -0.12725 | 0 | 16.8 | 16.9272
| S nom LV, МVА | 16+16 | 3854 | 1536 | 4.1488 | 2.798 | 0 | 1.3508 | 0 | 16.8 | 15.4492 |  |  |  | S nom LV, МVА | 16+16 | 0.062 | 4.2108 | 2.798 | 0 | 1.4128 | 0 | 16.8 | 15.3872
66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 28060 | 14706 | 31.6801 | 0 | 0 | 31.6801 | 0 | 47.25 | 15.5699 | 15.5699 |  | 66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 0 | 31.6801 | 0 | 0 | 31.6801 | 0 | 47.25 | 15.5699 | 15.5699
| S nom MV, МVА | 20+25+25 | 8530 | 5342 | 10.0647 | 0 | 0 | 10.0647 | 0 | 47.25 | 37.1853 |  |  |  | S nom MV, МVА | 20+25+25 | 0 | 10.0647 | 0 | 0 | 10.0647 | 0 | 47.25 | 37.1853
| S nom LV, МVА | 20+25+25 | 19530 | 9364 | 21.6588 | 0 | 0 | 21.6588 | 0 | 47.25 | 25.5912 |  |  |  | S nom LV, МVА | 20+25+25 | 0.1965 | 21.8553 | 0 | 0 | 21.8553 | 0 | 47.25 | 25.3947
67 | SS-110/35/10kV Streletskaya | 16+16 | 6219 | 1734 | 6.4562 | 2.23 | 80 | 4.2262 | 0 | 16.8 | 12.5738 | 6.1583 |  | 67 | SS-110/35/10kV Streletskaya | 16+16 | 0 | 6.4562 | 2.23 | 80 | 4.2262 | 0 | 16.8 | 12.5738 | 3.7508
| S nom MV, МVА | 16+8 | 1932 | 462 | 1.9865 | 0 | 0 | 1.9865 | 0 | 8.4 | 6.4135 |  |  |  | S nom MV, МVА | 16+8 | 0 | 1.9865 | 0 | 0 | 1.9865 | 0 | 8.4 | 6.4135
| S nom LV, МVА | 16+8 | 4287 | 1272 | 4.4717 | 2.23 | 0 | 2.2417 | 0 | 8.4 | 6.1583 |  |  |  | S nom LV, МVА | 16+8 | 2.4075 | 6.8792 | 2.23 | 0 | 4.6492 | 0 | 8.4 | 3.7508
68 | SS-110/6kV Stroitel | 15+15 | 11154 | 4901 | 12.1832 | 0 | 0 | 12.1832 | 0 | 15.75 | 3.5668 | 3.5668 |  | 68 | SS-110/6kV Stroitel | 15+15 | 0.5585 | 12.7417 | 0 | 0 | 12.7417 | 0 | 15.75 | 3.0083 | 3.0083
69 | SS-110/35/10kV Tomarovka | 16+16 | 13683 | 6359 | 15.0885 | 3.46 | 45 | 11.6285 | 0 | 16.8 | 5.1715 | 5.1715 |  | 69 | SS-110/35/10kV Tomarovka | 16+16 | 0 | 15.0885 | 3.46 | 45 | 11.6285 | 0 | 16.8 | 5.1715 | 5.1715
| S nom MV, МVА | 16+16 | 6657 | 3175 | 7.3754 | 3.46 | 0 | 3.9154 | 0 | 16.8 | 12.8846 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.3754 | 3.46 | 0 | 3.9154 | 0 | 16.8 | 12.8846
| S nom LV, МVА | 16+16 | 7026 | 3184 | 7.7138 | 0 | 0 | 7.7138 | 0 | 16.8 | 9.0862 |  |  |  | S nom LV, МVА | 16+16 | 0.482 | 8.1958 | 0 | 0 | 8.1958 | 0 | 16.8 | 8.6042
70 | SS-110/6kV Chemical plant | 32+32 | 11768 | 5854 | 13.1436 | 5.56 | 45 | 7.5836 | 0 | 33.6 | 26.0164 | 26.0164 |  | 70 | SS-110/6kV Chemical plant | 32+32 | 0.044 | 13.1876 | 5.56 | 45 | 7.6276 | 0 | 33.6 | 25.9724 | 25.9724
71 | SS-110/10kV Tsentralnaya | 40+40 | 27276 | 5364 | 27.7984 | 0 | 0 | 27.7984 | 0 | 42 | 14.2016 | 14.2016 |  | 71 | SS-110/10kV Tsentralnaya | 40+40 | 2.132 | 29.9304 | 0 | 0 | 29.9304 | 0 | 42 | 12.0696 | 12.0696
72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 15286 | 6193 | 16.4929 | 20.54 | 80 | -4.0471 | 0 | 26.25 | 30.2971 | 24.4172 |  | 72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 0 | 16.4929 | 20.54 | 80 | -4.0471 | 0 | 26.25 | 30.2971 | 24.4022
| S nom MV, МVА | 25+25 | 13793 | 5130 | 14.7161 | 19.676 | 0 | -4.9599 | 0 | 26.25 | 31.2099 |  |  |  | S nom MV, МVА | 25+25 | 0 | 14.7161 | 19.676 | 0 | -4.9599 | 0 | 26.25 | 31.2099
| S nom LV, МVА | 25+25 | 1493 | 1063 | 1.8328 | 0 | 0 | 1.8328 | 0 | 26.25 | 24.4172 |  |  |  | S nom LV, МVА | 25+25 | 0.015 | 1.8478 | 0 | 0 | 1.8478 | 0 | 26.25 | 24.4022
73 | SS-110/35/10kV Chernyanka | 16+16 | 13608 | 5777 | 14.7835 | 5.969 | 120 | 8.8145 | 0 | 16.8 | 7.9855 | 7.7874 |  | 73 | SS-110/35/10kV Chernyanka | 16+16 | 0 | 14.7835 | 5.969 | 120 | 8.8145 | 0 | 16.8 | 7.9855 | 7.2973
| S nom MV, МVА | 16+16 | 5246 | 2415 | 5.7752 | 5.969 | 0 | -0.19382 | 0 | 16.8 | 16.9938 |  |  |  | S nom MV, МVА | 16+16 | 0 | 5.7752 | 5.969 | 0 | -0.19382 | 0 | 16.8 | 16.9938
| S nom LV, МVА | 16+16 | 8362 | 3362 | 9.0126 | 0 | 0 | 9.0126 | 0 | 16.8 | 7.7874 |  |  |  | S nom LV, МVА | 16+16 | 0.4901 | 9.5027 | 0 | 0 | 9.5027 | 0 | 16.8 | 7.2973
74 | SS-110/35/6kV Shebekino | 40+40 | 25120 | 12318 | 27.9776 | 16.65 | 120 | 11.3276 | 0 | 42 | 30.6724 | 30.6724 |  | 74 | SS-110/35/6kV Shebekino | 40+40 | 0 | 27.9776 | 16.65 | 120 | 11.3276 | 0 | 42 | 30.6724 | 30.6724
| S nom MV, МVА | 40+40 | 13436 | 7362 | 15.3207 | 11.682 | 0 | 3.6387 | 0 | 42 | 38.3613 |  |  |  | S nom MV, МVА | 40+40 | 0 | 15.3207 | 11.682 | 0 | 3.6387 | 0 | 42 | 38.3613
| S nom LV, МVА | 40+40 | 11684 | 4956 | 12.6916 | 4.968 | 0 | 7.7236 | 0 | 42 | 34.2764 |  |  |  | S nom LV, МVА | 40+40 | 0.44 | 13.1316 | 4.968 | 0 | 8.1636 | 0 | 42 | 33.8364
75 | SS-110/10kV Sheino | 3,2+10 | 2220 | 795 | 2.3581 | 0 | 0 | 2.3581 | 0 | 3.36 | 1.0019 | 1.0019 |  | 75 | SS-110/10kV Sheino | 3,2+10 | 0.753 | 3.1111 | 0 | 0 | 3.1111 | 0 | 3.36 | 0.24894 | 0.24894
76 | SS-110/10/6kV Yuzhnaya | 40+40 | 36431 | 10427 | 37.8938 | 12.94 | 120 | 24.9538 | 0 | 42 | 17.0462 | 17.0462 |  | 76 | SS-110/10/6kV Yuzhnaya | 40+40 | 0 | 37.8938 | 12.94 | 120 | 24.9538 | 0 | 42 | 17.0462 | 17.0462
| S nom MV, МVА | 40+40 | 5694 | 1164 | 5.8118 | 3.42 | 0 | 2.3918 | 0 | 42 | 39.6082 |  |  |  | S nom MV, МVА | 40+40 | 0 | 5.8118 | 3.42 | 0 | 2.3918 | 0 | 42 | 39.6082
| S nom LV, МVА | 40+40 | 30737 | 9263 | 32.1024 | 9.52 | 0 | 22.5824 | 0 | 42 | 19.4176 |  |  |  | S nom LV, МVА | 40+40 | 0.82635 | 32.9288 | 9.52 | 0 | 23.4088 | 0 | 42 | 18.5912
77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 792 | 304 | 0.84834 | 0.43267 | 120 | 0.41567 | 0 | 2.625 | 2.2093 | 2.2093 |  | 77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 0.0175 | 0.86584 | 0.43267 | 120 | 0.43317 | 0 | 2.625 | 2.1918 | 2.1918
78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 848 | 320 | 0.90637 | 0.46639 | 120 | 0.43998 | 0 | 2.625 | 2.185 | 2.185 |  | 78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 0.017 | 0.92337 | 0.46639 | 120 | 0.45698 | 0 | 2.625 | 2.168 | 2.168
79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 2364 | 1296 | 2.6959 | 0 | 0 | 2.6959 | 0 | 4.2 | 1.5041 | 1.5041 |  | 79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 0.116 | 2.8119 | 0 | 0 | 2.8119 | 0 | 4.2 | 1.3881 | 1.3881
80 | SS-35/10kV Annovka | 2,5+2,5 | 876 | 354 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267 |  | 80 | SS-35/10kV Annovka | 2,5+2,5 | 0.015 | 0.95982 | 0.44652 | 80 | 0.51331 | 0 | 2.625 | 2.1117 | 2.1117
81 | SS-35/10kV Artelnoe | 6,3+6,3 | 5480 | 3788 | 6.6618 | 0.55 | 45 | 6.1118 | 0 | 6.615 | 0.50322 | 0.50322 |  | 81 | SS-35/10kV Artelnoe | 6,3+6,3 | 0.016 | 6.6778 | 0.55 | 45 | 6.1278 | 0 | 6.615 | 0.48722 | 0.48722
82 | SS-35/10kV B.Dvory | 4+4 | 2352 | 960 | 2.5404 | 1.191 | 120 | 1.3494 | 0 | 4.2 | 2.8506 | 2.8506 |  | 82 | SS-35/10kV B.Dvory | 4+4 | 0.119 | 2.6594 | 1.191 | 120 | 1.4684 | 0 | 4.2 | 2.7316 | 2.7316
83 | SS-35/10kV B.Ivanovka | 2,5+2,5 | 976 | 400 | 1.0548 | 0.62488 | 80 | 0.42991 | 0 | 2.6 | 2.17 | 2.17 |  | 83 | SS-35/10kV B.Ivanovka | 2,5+2,5 | 0.015 | 1.0698 | 0.62488 | 80 | 0.44491 | 0 | 2.625 | 2.1801 | 2.1801
84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 756 | 318 | 0.82016 | 0.44779 | 45 | 0.37236 | 0 | 2.625 | 2.2526 | 2.2526 |  | 84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 0.029 | 0.84916 | 0.44779 | 45 | 0.40136 | 0 | 2.625 | 2.2236 | 2.2236
85 | SS-35/10kV B.Ples | 2,5+2,5 | 672 | 280 | 0.728 | 0.606 | 45 | 0.122 | 0 | 2.625 | 2.503 | 2.503 |  | 85 | SS-35/10kV B.Ples | 2,5+2,5 | 0.034 | 0.762 | 0.606 | 45 | 0.156 | 0 | 2.625 | 2.469 | 2.469
86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 2672 | 948 | 2.8352 | 2.83 | 45 | 0.0051875 | 0 | 6.615 | 6.6098 | 6.6098 |  | 86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 0.008 | 2.8432 | 2.83 | 45 | 0.013187 | 0 | 6.615 | 6.6018 | 6.6018
87 | SS-35/10kV Belovskoe | 4+4 | 3408 | 1496 | 3.7219 | 1.21 | 80 | 2.5119 | 0 | 4.2 | 1.6881 | 1.6881 |  | 87 | SS-35/10kV Belovskoe | 4+4 | 0.6938 | 4.4157 | 1.21 | 80 | 3.2057 | 0 | 4.2 | 0.99431 | 0.99431
88 | SS-35/10kV Belyanka | 2,5+4 | 1776 | 928 | 2.0038 | 1.3214 | 45 | 0.68244 | 0 | 2.625 | 1.9426 | 1.9426 |  | 88 | SS-35/10kV Belyanka | 2,5+4 | 0.036 | 2.0398 | 1.3214 | 45 | 0.71844 | 0 | 2.625 | 1.9066 | 1.9066
89 | SS-35/10kV Bessonovka | 6,3+6,3 | 4344 | 2400 | 4.9629 | 0.918 | 120 | 4.0449 | 0 | 6.615 | 2.5701 | 2.5701 |  | 89 | SS-35/10kV Bessonovka | 6,3+6,3 | 0.353 | 5.3159 | 0.918 | 120 | 4.3979 | 0 | 6.615 | 2.2171 | 2.2171
90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 1112 | 376 | 1.1738 | 0.522 | 45 | 0.65185 | 0 | 1.68 | 1.0282 | 1.0282 |  | 90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 0.01 | 1.1838 | 0.522 | 45 | 0.66185 | 0 | 1.68 | 1.0182 | 1.0182
91 | SS-35/10kV V.Mikhailovka | 4+4 | 2508 | 984 | 2.6941 | 1.45 | 80 | 1.2441 | 0 | 4.2 | 2.9559 | 2.9559 |  | 91 | SS-35/10kV V.Mikhailovka | 4+4 | 0 | 2.6941 | 1.45 | 80 | 1.2441 | 0 | 4.2 | 2.9559 | 2.9559
92 | SS-35/10kV Varvarovka | 2,5+2,5 | 1656 | 680 | 1.7902 | 1.0795 | 120 | 0.71063 | 0 | 2.625 | 1.9144 | 1.9144 |  | 92 | SS-35/10kV Varvarovka | 2,5+2,5 | 0.25 | 2.0402 | 1.0795 | 120 | 0.96063 | 0 | 2.625 | 1.6644 | 1.6644
93 | SS-35/10kV Vengerovka | 2,5+2,5 | 1620 | 588 | 1.7234 | 0.4 | 120 | 1.3234 | 0 | 2.625 | 1.3016 | 1.3016 |  | 93 | SS-35/10kV Vengerovka | 2,5+2,5 | 0.01 | 1.7334 | 0.4 | 120 | 1.3334 | 0 | 2.625 | 1.2916 | 1.2916
94 | SS-35/10kV Verkhopenye | 2,5+4 | 1536 | 704 | 1.6896 | 1.0177 | 45 | 0.67199 | 0 | 2.625 | 1.953 | 1.953 |  | 94 | SS-35/10kV Verkhopenye | 2,5+4 | 0.04 | 1.7296 | 1.0177 | 45 | 0.71199 | 0 | 2.625 | 1.913 | 1.913
95 | SS-35/10kV Viktoropol | 2,5+4 | 1376 | 460 | 1.4509 | 0.95536 | 120 | 0.4955 | 0 | 2.625 | 2.1295 | 2.1295 |  | 95 | SS-35/10kV Viktoropol | 2,5+4 | 0.0355 | 1.4864 | 0.95536 | 120 | 0.531 | 0 | 2.625 | 2.094 | 2.094
96 | SS-35/10kV Vislaya Dubrava | 4+4 | 1968 | 564 | 2.0472 | 0.616 | 80 | 1.4312 | 0 | 4.2 | 2.7688 | 2.7688 |  | 96 | SS-35/10kV Vislaya Dubrava | 4+4 | 0.070034 | 2.1173 | 0.616 | 80 | 1.5013 | 0 | 4.2 | 2.6987 | 2.6987
97 | SS-35/10kV Vladimirovka | 4+4 | 520 | 278 | 0.58965 | 0 | 0 | 0.58965 | 0 | 4.2 | 3.6104 | 3.6104 |  | 97 | SS-35/10kV Vladimirovka | 4+4 | 0.005 | 0.59465 | 0 | 0 | 0.59465 | 0 | 4.2 | 3.6054 | 3.6054
98 | SS-35/10kV Water storage | 4+6,3 | 1848 | 660 | 1.9623 | 0.305 | 45 | 1.6573 | 0 | 4.2 | 2.5427 | 2.5427 |  | 98 | SS-35/10kV Water storage | 4+6,3 | 0.036 | 1.9983 | 0.305 | 45 | 1.6933 | 0 | 4.2 | 2.5067 | 2.5067
99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 2895 | 1109 | 3.1001 | 1.43 | 120 | 1.6701 | 0 | 6.615 | 4.9449 | 4.9449 |  | 99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 0.113 | 3.2131 | 1.43 | 120 | 1.7831 | 0 | 6.615 | 4.8319 | 4.8319
100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 1410 | 588 | 1.5277 | 0.99513 | 120 | 0.53256 | 0 | 2.625 | 2.0924 | 2.0924 |  | 100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 0.023 | 1.5507 | 0.99513 | 120 | 0.55556 | 0 | 2.625 | 2.0694 | 2.0694
101 | SS-35/10kV Glinnoe | 6,3+6,3 | 2256 | 1488 | 2.7025 | 1.4036 | 80 | 1.2989 | 0 | 6.615 | 5.3161 | 5.3161 |  | 101 | SS-35/10kV Glinnoe | 6,3+6,3 | 0 | 2.7025 | 1.4036 | 80 | 1.2989 | 0 | 6.615 | 5.3161 | 5.3161
102 | SS-35/10kV Golovchino | 2,5+2,5 | 2232 | 828 | 2.3806 | 0.617 | 45 | 1.7636 | 0 | 2.625 | 0.86137 | 0.86137 |  | 102 | SS-35/10kV Golovchino | 2,5+2,5 | 0.074 | 2.4546 | 0.617 | 45 | 1.8376 | 0 | 2.625 | 0.78737 | 0.78737
103 | SS-35/10kV Gora-Podol | 2,5+4 | 1380 | 540 | 1.4819 | 0.9085 | 45 | 0.57339 | 0 | 2.625 | 2.0516 | 2.0516 |  | 103 | SS-35/10kV Gora-Podol | 2,5+4 | 0.045 | 1.5269 | 0.9085 | 45 | 0.61839 | 0 | 2.625 | 2.0066 | 2.0066
104 | SS-35/10kV Gorodishche | 4+4 | 2576 | 1104 | 2.8026 | 0 | 0 | 2.8026 | 0 | 4.2 | 1.3974 | 1.3974 |  | 104 | SS-35/10kV Gorodishche | 4+4 | 0.043 | 2.8456 | 0 | 0 | 2.8456 | 0 | 4.2 | 1.3544 | 1.3544
105 | SS-35/10kV Dmitrievka | 4+4 | 1152 | 636 | 1.3159 | 0.78237 | 80 | 0.53353 | 0 | 4.2 | 3.6665 | 3.6665 |  | 105 | SS-35/10kV Dmitrievka | 4+4 | 0.515 | 1.8309 | 0.78237 | 80 | 1.0485 | 0 | 4.2 | 3.1515 | 3.1515
106 | SS-35/10kV Dorogoshch | 4+4 | 2288 | 944 | 2.4751 | 1.054 | 45 | 1.4211 | 0 | 4.2 | 2.7789 | 2.7789 |  | 106 | SS-35/10kV Dorogoshch | 4+4 | 0.02822 | 2.5033 | 1.054 | 45 | 1.4493 | 0 | 4.2 | 2.7507 | 2.7507
107 | SS-35/10kV Dragunka | 2,5+2,5 | 320 | 144 | 0.35091 | 0.62999 | 80 | -0.27908 | 0 | 2.625 | 2.9041 | 2.9041 |  | 107 | SS-35/10kV Dragunka | 2,5+2,5 | 0.05 | 0.40091 | 0.62999 | 80 | -0.22908 | 0 | 2.625 | 2.8541 | 2.8541
108 | SS-35/10kV Zhuravlevka | 2,5+4 | 1264 | 336 | 1.3079 | 0.274 | 80 | 1.0339 | 0 | 2.625 | 1.5911 | 1.5911 |  | 108 | SS-35/10kV Zhuravlevka | 2,5+4 | 0.067 | 1.3749 | 0.274 | 80 | 1.1009 | 0 | 2.625 | 1.5241 | 1.5241
109 | SS-35/6kV Zhuravliki | 10+10 | 7104 | 1872 | 7.3465 | 4.051 | 120 | 3.2955 | 0 | 10.5 | 7.2045 | 7.2045 |  | 109 | SS-35/6kV Zhuravliki | 10+10 | 0.1186 | 7.4651 | 4.051 | 120 | 3.4141 | 0 | 10.5 | 7.0859 | 7.0859
110 | SS-35/10kV Zavidovka | 2,5+2,5 | 808 | 584 | 0.99696 | 0.42 | 80 | 0.57696 | 0 | 2.625 | 2.048 | 2.048 |  | 110 | SS-35/10kV Zavidovka | 2,5+2,5 | 0.102 | 1.099 | 0.42 | 80 | 0.67896 | 0 | 2.625 | 1.946 | 1.946
111 | SS-35/6kV Zapadnaya | 10+10+10 | 5664 | 2496 | 6.1896 | 1.707 | 120 | 4.4826 | 0 | 21 | 16.5174 | 16.5174 |  | 111 | SS-35/6kV Zapadnaya | 10+10+10 | 0.0305 | 6.2201 | 1.707 | 120 | 4.5131 | 0 | 21 | 16.4869 | 16.4869
112 | SS-35/10kV Zozuli | 6,3+6,3 | 5808 | 2912 | 6.4971 | 3.88 | 80 | 2.6171 | 0 | 6.615 | 3.9979 | 3.9979 |  | 112 | SS-35/10kV Zozuli | 6,3+6,3 | 0.073 | 6.5701 | 3.88 | 80 | 2.6901 | 0 | 6.615 | 3.9249 | 3.9249
113 | SS-35/10kV Ivitsa | 2,5+2,5 | 976 | 448 | 1.0739 | 0.58603 | 80 | 0.48788 | 0 | 2.625 | 2.1371 | 2.1371 |  | 113 | SS-35/10kV Ivitsa | 2,5+2,5 | 0.01 | 1.0839 | 0.58603 | 80 | 0.49788 | 0 | 2.625 | 2.1271 | 2.1271
114 | SS-35/10kV Ilovka | 4+4 | 2280 | 744 | 2.3983 | 2.056 | 45 | 0.34232 | 0 | 4.2 | 3.8577 | 3.8577 |  | 114 | SS-35/10kV Ilovka | 4+4 | 0.135 | 2.5333 | 2.056 | 45 | 0.47732 | 0 | 4.2 | 3.7227 | 3.7227
115 | SS-35/10kV Istobnoe | 4+2,5 | 1096 | 600 | 1.2495 | 0.93935 | 120 | 0.31013 | 0 | 2.625 | 2.3149 | 2.3149 |  | 115 | SS-35/10kV Istobnoe | 4+2,5 | 0.055 | 1.3045 | 0.93935 | 120 | 0.36513 | 0 | 2.625 | 2.2599 | 2.2599
116 | SS-35/10kV Kazatskaya | 2,5+4 | 1054 | 381 | 1.1207 | 0.87141 | 45 | 0.24934 | 0 | 2.625 | 2.3757 | 2.3757 |  | 116 | SS-35/10kV Kazatskaya | 2,5+4 | 0.015 | 1.1357 | 0.87141 | 45 | 0.26434 | 0 | 2.625 | 2.3607 | 2.3607
117 | SS-35/10kV Kazinka | 4+4 | 2364 | 804 | 2.497 | 0.736 | 120 | 1.761 | 0 | 4.2 | 2.439 | 2.439 |  | 117 | SS-35/10kV Kazinka | 4+4 | 0.024 | 2.521 | 0.736 | 120 | 1.785 | 0 | 4.2 | 2.415 | 2.415
118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 920 | 308 | 0.97019 | 0.712 | 120 | 0.25819 | 0 | 2.625 | 2.3668 | 2.3668 |  | 118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 0.034 | 1.0042 | 0.712 | 120 | 0.29219 | 0 | 2.625 | 2.3328 | 2.3328
119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 2952 | 1404 | 3.2689 | 0.7035 | 120 | 2.5654 | 0 | 6.615 | 4.0496 | 4.0496 |  | 119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 0.034 | 3.3029 | 0.7035 | 120 | 2.5994 | 0 | 6.615 | 4.0156 | 4.0156
120 | SS-35/10kV Kotovo | 2,5+2,5 | 2304 | 720 | 2.4139 | 1.648 | 20 | 0.76587 | 0 | 2.625 | 1.8591 | 1.8591 |  | 120 | SS-35/10kV Kotovo | 2,5+2,5 | 0.235 | 2.6489 | 1.648 | 20 | 1.0009 | 0 | 2.625 | 1.6241 | 1.6241
121 | SS-35/10kV Kochetovka | 2,5+4 | 1224 | 516 | 1.3283 | 0.6286 | 45 | 0.69972 | 0 | 2.625 | 1.9253 | 1.9253 |  | 121 | SS-35/10kV Kochetovka | 2,5+4 | 0 | 1.3283 | 0.6286 | 45 | 0.69972 | 0 | 2.625 | 1.9253 | 1.9253
122 | SS-35/10kV Krasnoe | 4+2,5 | 1016 | 368 | 1.0806 | 1.1395 | 80 | -0.058929 | 0 | 2.625 | 2.6839 | 2.6839 |  | 122 | SS-35/10kV Krasnoe | 4+2,5 | 0.007 | 1.0876 | 1.1395 | 80 | -0.051929 | 0 | 2.625 | 2.6769 | 2.6769
123 | SS-35/10kV Kretovo | 4+2,5 | 1016 | 468 | 1.1186 | 0.67818 | 120 | 0.44043 | 0 | 2.625 | 2.1846 | 2.1846 |  | 123 | SS-35/10kV Kretovo | 4+2,5 | 0.035 | 1.1536 | 0.67818 | 120 | 0.47543 | 0 | 2.625 | 2.1496 | 2.1496
124 | SS-35/10kV Kurasovka | 4+4 | 2640 | 1248 | 2.9201 | 1.797 | 80 | 1.1231 | 0 | 4.2 | 3.0769 | 3.0769 |  | 124 | SS-35/10kV Kurasovka | 4+4 | 0.27165 | 3.1918 | 1.797 | 80 | 1.3948 | 0 | 4.2 | 2.8052 | 2.8052
125 | SS-35/6kV Lebedi | 4+5,6 | 3586 | 1166 | 3.7708 | 0.581 | 120 | 3.1898 | 0 | 4.2 | 1.0102 | 1.0102 |  | 125 | SS-35/6kV Lebedi | 4+5,6 | 0.124 | 3.8948 | 0.581 | 120 | 3.3138 | 0 | 4.2 | 0.8862 | 0.8862
126 | SS-35/6kV Ledovaya | 4+4 | 2549 | 1325 | 2.8728 | 1.321 | 80 | 1.5518 | 0 | 4.2 | 2.6482 | 2.6482 |  | 126 | SS-35/6kV Ledovaya | 4+4 | 0.01 | 2.8828 | 1.321 | 80 | 1.5618 | 0 | 4.2 | 2.6382 | 2.6382
127 | SS-35/10kV Livenka | 4+4 | 3252 | 1452 | 3.5614 | 1.541 | 120 | 2.0204 | 0 | 4.2 | 2.1796 | 2.1796 |  | 127 | SS-35/10kV Livenka | 4+4 | 0.067 | 3.6284 | 1.541 | 120 | 2.0874 | 0 | 4.2 | 2.1126 | 2.1126
128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 732 | 336 | 0.80543 | 0.66672 | 80 | 0.13872 | 0 | 2.625 | 2.4863 | 2.4863 |  | 128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 0 | 0.80543 | 0.66672 | 80 | 0.13872 | 0 | 2.625 | 2.4863 | 2.4863
129 | SS-35/10kV M.Pristan | 10+10 | 6456 | 1992 | 6.7563 | 1.81 | 45 | 4.9463 | 0 | 10.5 | 5.5537 | 5.5537 |  | 129 | SS-35/10kV M.Pristan | 10+10 | 2.3615 | 9.1178 | 1.81 | 45 | 7.3078 | 0 | 10.5 | 3.1922 | 3.1922
130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 744 | 304 | 0.80371 | 0.60716 | 80 | 0.19655 | 0 | 2.625 | 2.4284 | 2.4284 |  | 130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 0.05 | 0.85371 | 0.60716 | 80 | 0.24655 | 0 | 2.625 | 2.3784 | 2.3784
131 | SS-35/10kV Malinovka | 10+10 | 6352 | 3984 | 7.498 | 1.357 | 120 | 6.141 | 0 | 10.5 | 4.359 | 4.359 |  | 131 | SS-35/10kV Malinovka | 10+10 | 0.01 | 7.508 | 1.357 | 120 | 6.151 | 0 | 10.5 | 4.349 | 4.349
132 | SS-35/10kV Mandrovo | 2,5+2,5 | 1188 | 336 | 1.2346 | 0.65565 | 80 | 0.57895 | 0 | 2.625 | 2.046 | 2.046 |  | 132 | SS-35/10kV Mandrovo | 2,5+2,5 | 0.005 | 1.2396 | 0.65565 | 80 | 0.58395 | 0 | 2.625 | 2.041 | 2.041
133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 1266 | 462 | 1.3477 | 0.643 | 80 | 0.70466 | 0 | 2.625 | 1.9203 | 1.9203 |  | 133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 0.152 | 1.4997 | 0.643 | 80 | 0.85666 | 0 | 2.625 | 1.7683 | 1.7683
134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 1158 | 522 | 1.2702 | 0.59315 | 120 | 0.67706 | 0 | 2.625 | 1.9479 | 1.9479 |  | 134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 0.0565 | 1.3267 | 0.59315 | 120 | 0.73356 | 0 | 2.625 | 1.8914 | 1.8914
135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 3168 | 1168 | 3.3765 | 2.78 | 120 | 0.59645 | 0 | 6.615 | 6.0185 | 6.0185 |  | 135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 0.9045 | 4.281 | 2.78 | 120 | 1.501 | 0 | 6.615 | 5.114 | 5.114
136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 3288 | 1200 | 3.5001 | 0.842 | 45 | 2.6581 | 0 | 6.615 | 3.9569 | 3.9569 |  | 136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 0.084 | 3.5841 | 0.842 | 45 | 2.7421 | 0 | 6.615 | 3.8729 | 3.8729
137 | SS-35/10kV N.Ukolovo | 4+2,5 | 1384 | 524 | 1.4799 | 0.57 | 80 | 0.90988 | 0 | 2.625 | 1.7151 | 1.7151 |  | 137 | SS-35/10kV N.Ukolovo | 4+2,5 | 0.02 | 1.4999 | 0.57 | 80 | 0.92988 | 0 | 2.625 | 1.6951 | 1.6951
138 | SS-35/10kV N.Khutornoe | 2,5+4 | 260 | 89 | 0.27481 | 0.19 | 80 | 0.084811 | 0 | 2.625 | 2.5402 | 2.5402 |  | 138 | SS-35/10kV N.Khutornoe | 2,5+4 | 0 | 0.27481 | 0.19 | 80 | 0.084811 | 0 | 2.625 | 2.5402 | 2.5402
139 | SS-35/10kV Neminushchee | 2,5+2,5 | 1732 | 628 | 1.8423 | 0.65147 | 80 | 1.1909 | 0 | 2.625 | 1.4341 | 1.4341 |  | 139 | SS-35/10kV Neminushchee | 2,5+2,5 | 0.007 | 1.8493 | 0.65147 | 80 | 1.1979 | 0 | 2.625 | 1.4271 | 1.4271
140 | SS-35/10kV Nechaevka | 4+4 | 1100 | 400 | 1.1705 | 0.451 | 120 | 0.71947 | 0 | 4.2 | 3.4805 | 3.4805 |  | 140 | SS-35/10kV Nechaevka | 4+4 | 0.044 | 1.2145 | 0.451 | 120 | 0.76347 | 0 | 4.2 | 3.4365 | 3.4365
141 | SS-35/10kV Nikitovka | 2,5+2,5 | 2016 | 768 | 2.1573 | 1.4354 | 80 | 0.7219 | 0 | 2.625 | 1.9031 | 1.9031 |  | 141 | SS-35/10kV Nikitovka | 2,5+2,5 | 0.55 | 2.7073 | 1.4354 | 80 | 1.2719 | 0 | 2.625 | 1.3531 | 1.3531
142 | SS-35/10kV Novenkoe | 4+4 | 1964 | 616 | 2.0583 | 1.7332 | 80 | 0.32513 | 0 | 4.2 | 3.8749 | 3.8749 |  | 142 | SS-35/10kV Novenkoe | 4+4 | 0 | 2.0583 | 1.7332 | 80 | 0.32513 | 0 | 4.2 | 3.8749 | 3.8749
143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 3968 | 1888 | 4.3943 | 0.872 | 80 | 3.5223 | 0 | 6.615 | 3.0927 | 3.0927 |  | 143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 0.4102 | 4.8045 | 0.872 | 80 | 3.9325 | 0 | 6.615 | 2.6825 | 2.6825
144 | SS-35/10kV Orlik | 4+4 | 1728 | 912 | 1.9539 | 0.553 | 80 | 1.4009 | 0 | 4.2 | 2.7991 | 2.7991 |  | 144 | SS-35/10kV Orlik | 4+4 | 1.2659 | 3.2198 | 0.553 | 80 | 2.6668 | 0 | 4.2 | 1.5332 | 1.5332
145 | SS-35/10kV Podolkhi | 2,5+2,5 | 2076 | 740 | 2.2039 | 1.1225 | 45 | 1.0815 | 0 | 2.625 | 1.5435 | 1.5435 |  | 145 | SS-35/10kV Podolkhi | 2,5+2,5 | 0.032 | 2.2359 | 1.1225 | 45 | 1.1135 | 0 | 2.625 | 1.5115 | 1.5115
146 | SS-35/10kV Popovka | 6,3+4 | 2016 | 792 | 2.166 | 0.64636 | 80 | 1.5196 | 0 | 4.2 | 2.6804 | 2.6804 |  | 146 | SS-35/10kV Popovka | 6,3+4 | 0.026 | 2.192 | 0.64636 | 80 | 1.5456 | 0 | 4.2 | 2.6544 | 2.6544
147 | SS-35/10kV Prelestnoe | 4+4 | 1668 | 612 | 1.7767 | 0 | 0 | 1.7767 | 0 | 4.2 | 2.4233 | 2.4233 |  | 147 | SS-35/10kV Prelestnoe | 4+4 | 0.036 | 1.8127 | 0 | 0 | 1.8127 | 0 | 4.2 | 2.3873 | 2.3873
148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 4608 | 2376 | 5.1845 | 0 | 0 | 5.1845 | 0 | 6.615 | 1.4305 | 1.4305 |  | 148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 0.04 | 5.2245 | 0 | 0 | 5.2245 | 0 | 6.615 | 1.3905 | 1.3905
149 | SS-35/10kV Prilepy | 2,5+2,5 | 468 | 274 | 0.54231 | 0.37638 | 80 | 0.16593 | 0 | 2.625 | 2.4591 | 2.4591 |  | 149 | SS-35/10kV Prilepy | 2,5+2,5 | 0 | 0.54231 | 0.37638 | 80 | 0.16593 | 0 | 2.625 | 2.4591 | 2.4591
150 | SS-35/10kV Printsevka | 2,5+2,5 | 1722 | 622 | 1.8309 | 0.352 | 120 | 1.4789 | 0 | 2.625 | 1.1461 | 1.1461 |  | 150 | SS-35/10kV Printsevka | 2,5+2,5 | 0.005 | 1.8359 | 0.352 | 120 | 1.4839 | 0 | 2.625 | 1.1411 | 1.1411
151 | SS-35/10kV Radkovka | 6,3+6,3 | 2576 | 1072 | 2.7902 | 0.164 | 45 | 2.6262 | 0 | 6.615 | 3.9888 | 3.9888 |  | 151 | SS-35/10kV Radkovka | 6,3+6,3 | 0.015 | 2.8052 | 0.164 | 45 | 2.6412 | 0 | 6.615 | 3.9738 | 3.9738
152 | SS-35/10kV Razdornoe | 2,5+2,5 | 1302 | 654 | 1.457 | 0.662 | 80 | 0.79502 | 0 | 2.625 | 1.83 | 1.83 |  | 152 | SS-35/10kV Razdornoe | 2,5+2,5 | 0.005 | 1.462 | 0.662 | 80 | 0.80002 | 0 | 2.625 | 1.825 | 1.825
153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 1728 | 828 | 1.9161 | 0.88491 | 80 | 1.0312 | 0 | 2.625 | 1.5938 | 1.5938 |  | 153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 0.007 | 1.9231 | 0.88491 | 80 | 1.0382 | 0 | 2.625 | 1.5868 | 1.5868
154 | SS-35/10kV Rzhevka | 6,3+6,3 | 3384 | 1824 | 3.8443 | 2.53 | 45 | 1.3143 | 0 | 6.615 | 5.3007 | 5.3007 |  | 154 | SS-35/10kV Rzhevka | 6,3+6,3 | 0.193 | 4.0373 | 2.53 | 45 | 1.5073 | 0 | 6.615 | 5.1077 | 5.1077
155 | SS-35/10kV Rovenki | 4+4 | 3036 | 1116 | 3.2346 | 1.7393 | 120 | 1.4953 | 0 | 4.2 | 2.7047 | 2.7047 |  | 155 | SS-35/10kV Rovenki | 4+4 | 0.049 | 3.2836 | 1.7393 | 120 | 1.5443 | 0 | 4.2 | 2.6557 | 2.6557
156 | SS-35/10kV Rogovatoe | 4+4 | 2208 | 1312 | 2.5684 | 0 | 0 | 2.5684 | 0 | 2.625 | 0.056614 | 0.056614 |  | 156 | SS-35/10kV Rogovatoe | 4+4 | 0.01 | 2.5784 | 0 | 0 | 2.5784 | 0 | 4.2 | 1.6216 | 1.6216
157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 2091 | 1064 | 2.3461 | 0 | 0 | 2.3461 | 0 | 2.625 | 0.27886 | 0.27886 |  | 157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 0 | 0 | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625
158 | SS-35/10kV Saprykino | 2,5+2,5 | 456 | 256 | 0.52295 | 0.22751 | 120 | 0.29543 | 0 | 2.625 | 2.3296 | 2.3296 |  | 158 | SS-35/10kV Saprykino | 2,5+2,5 | 0 | 0.52295 | 0.22751 | 120 | 0.29543 | 0 | 2.625 | 2.3296 | 2.3296
159 | SS-35/6kV Severnaya | 6,3+6,3 | 6739 | 2088 | 7.0551 | 4.8049 | 120 | 2.2502 | 0 | 6.615 | 4.3648 | 4.3648 |  | 159 | SS-35/6kV Severnaya | 6,3+6,3 | 0.22477 | 7.2798 | 4.8049 | 120 | 2.4749 | 0 | 6.615 | 4.1401 | 4.1401
160 | SS-35/10kV Setishche | 2,5+2,5 | 1734 | 628 | 1.8442 | 1.0621 | 80 | 0.7821 | 0 | 2.625 | 1.8429 | 1.8429 |  | 160 | SS-35/10kV Setishche | 2,5+2,5 | 0.005 | 1.8492 | 1.0621 | 80 | 0.7871 | 0 | 2.625 | 1.8379 | 1.8379
161 | SS-35/10kV Slonovka | 4+4 | 2896 | 1680 | 3.348 | 1.1306 | 120 | 2.2174 | 0 | 4.2 | 1.9826 | 1.9826 |  | 161 | SS-35/10kV Slonovka | 4+4 | 0.104 | 3.452 | 1.1306 | 120 | 2.3214 | 0 | 4.2 | 1.8786 | 1.8786
162 | SS-35/6kV St.Oskol -2 | 16+16 | 10140 | 4435 | 11.0675 | 1.21 | 80 | 9.8575 | 0 | 16.8 | 6.9425 | 6.9425 |  | 162 | SS-35/6kV St.Oskol -2 | 16+16 | 0.085 | 11.1525 | 1.21 | 80 | 9.9425 | 0 | 16.8 | 6.8575 | 6.8575
163 | SS-35/10kV Starikovo | 4+4 | 2448 | 624 | 2.5263 | 1.3453 | 45 | 1.181 | 0 | 4.2 | 3.019 | 3.019 |  | 163 | SS-35/10kV Starikovo | 4+4 | 0.039 | 2.5653 | 1.3453 | 45 | 1.22 | 0 | 4.2 | 2.98 | 2.98
164 | SS-35/10kV Tavrovo | 10+10 | 8520 | 1512 | 8.6531 | 0.531 | 45 | 8.1221 | 0 | 10.5 | 2.3779 | 2.3779 |  | 164 | SS-35/10kV Tavrovo | 10+10 | 1.9486 | 10.6017 | 0.531 | 45 | 10.0707 | 0 | 10.5 | 0.42928 | 0.42928
165 | SS-35/10kV Terebrino | 2,5+2,5 | 1020 | 564 | 1.1655 | 0.44978 | 80 | 0.71576 | 0 | 2.625 | 1.9092 | 1.9092 |  | 165 | SS-35/10kV Terebrino | 2,5+2,5 | 0.014 | 1.1795 | 0.44978 | 80 | 0.72976 | 0 | 2.625 | 1.8952 | 1.8952
166 | SS-35/10kV Urazovo | 6,3+6,3 | 3180 | 1080 | 3.3584 | 1.39 | 120 | 1.9684 | 0 | 6.615 | 4.6466 | 4.6466 |  | 166 | SS-35/10kV Urazovo | 6,3+6,3 | 0.056 | 3.4144 | 1.39 | 120 | 2.0244 | 0 | 6.615 | 4.5906 | 4.5906
167 | SS-35/10kV Utochka | 1,6+2,5 | 664 | 248 | 0.7088 | 0.47242 | 80 | 0.23639 | 0 | 1.68 | 1.4436 | 1.4436 |  | 167 | SS-35/10kV Utochka | 1,6+2,5 | 0.015 | 0.7238 | 0.47242 | 80 | 0.25139 | 0 | 1.68 | 1.4286 | 1.4286
168 | SS-35/6kV Fedoseevka | 4+4 | 1594 | 614 | 1.7082 | 0 | 0 | 1.7082 | 0 | 4.2 | 2.4918 | 2.4918 |  | 168 | SS-35/6kV Fedoseevka | 4+4 | 0.02 | 1.7282 | 0 | 0 | 1.7282 | 0 | 4.2 | 2.4718 | 2.4718
169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 752 | 304 | 0.81112 | 0.78681 | 45 | 0.024316 | 0 | 1.68 | 1.6557 | 1.6557 |  | 169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 0.015 | 0.82612 | 0.78681 | 45 | 0.039316 | 0 | 1.68 | 1.6407 | 1.6407
170 | SS-35/10kV Kholodnoe | 4+4 | 1864 | 620 | 1.9644 | 0 | 0 | 1.9644 | 0 | 4.2 | 2.2356 | 2.2356 |  | 170 | SS-35/10kV Kholodnoe | 4+4 | 0.265 | 2.2294 | 0 | 0 | 2.2294 | 0 | 4.2 | 1.9706 | 1.9706
171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 1152 | 768 | 1.3845 | 1.3513 | 20 | 0.033266 | 0 | 6.615 | 6.5817 | 6.5817 |  | 171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 0.015 | 1.3995 | 1.3513 | 20 | 0.048266 | 0 | 6.615 | 6.5667 | 6.5667
172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 1284 | 432 | 1.3547 | 1 | 80 | 0.35473 | 0 | 2.625 | 2.2703 | 2.2703 |  | 172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0.022 | 1.3767 | 1 | 80 | 0.37673 | 0 | 2.625 | 2.2483 | 2.2483
173 | SS-35/10kV Shatalovka | 6,3+6,3 | 1584 | 704 | 1.7334 | 0 | 0 | 1.7334 | 0 | 6.615 | 4.8816 | 4.8816 |  | 173 | SS-35/10kV Shatalovka | 6,3+6,3 | 0.02 | 1.7534 | 0 | 0 | 1.7534 | 0 | 6.615 | 4.8616 | 4.8616
174 | SS-35/10kV Shakhovka | 4+4 | 1518 | 582 | 1.6257 | 0.79066 | 80 | 0.83508 | 0 | 2.625 | 1.7899 | 1.7899 |  | 174 | SS-35/10kV Shakhovka | 2,5+2,5 | 0.035 | 1.6607 | 0.79066 | 80 | 0.87008 | 0 | 2.625 | 1.7549 | 1.7549
175 | SS-35/10kV Shishino | 6,3+6,3 | 3432 | 1008 | 3.577 | 1.03 | 80 | 2.547 | 0 | 6.615 | 4.068 | 4.068 |  | 175 | SS-35/10kV Shishino | 6,3+6,3 | 0.6392 | 4.2162 | 1.03 | 80 | 3.1862 | 0 | 6.615 | 3.4288 | 3.4288
176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 767 | 623 | 0.98814 | 0 | 0 | 0.98814 | 0 | 1.68 | 0.69186 | 0.69186 |  | 176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 1.68 | 1.68
177 | SS-35/10kV Yablonovo | 4+4 | 1440 | 608 | 1.5631 | 1.1284 | 80 | 0.43467 | 0 | 4.2 | 3.7653 | 3.7653 |  | 177 | SS-35/10kV Yablonovo | 4+4 | 0.029 | 1.5921 | 1.1284 | 80 | 0.46367 | 0 | 4.2 | 3.7363 | 3.7363
178 | SS-35/10kV Yarskoe | 2,5+2,5 | 248 | 80 | 0.26058 | 0.14648 | 80 | 0.11411 | 0 | 2.625 | 2.5109 | 2.5109 |  | 178 | SS-35/10kV Yarskoe | 2,5+2,5 | 0.03 | 0.29058 | 0.14648 | 80 | 0.14411 | 0 | 2.625 | 2.4809 | 2.4809
| TOTAL: | 3303.1 |  |  | 2538.0096 | 1078.5217 |  | 1544.3037 | [6 empty] | TOTAL: | 3303.1 | #N/A | #N/A | #N/A |  | #N/A
| deficit | [10 empty] | 6.069 |  |  | deficit | [9 empty] | 7.3022
| proficit | [10 empty] | 1047.929 |  |  | proficit | [9 empty] | 1013.9722

## Current deficit - winter
The list of closed supply centers of IDGC of Centre according to winter load in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class, transformer capacity (installed MVA) |  | Current deficit, MVA | cos | Note
Belgorodenergo |  |  |  | cos
1 | SS-110/35/10kV D.Poljana | 6.3 | -0.033615 | 0.91497 | unavailable
2 | SS-110/35/10kV Irrigating | 16 | -1.8912 | 0.9465 | unavailable
3 | SS-35/10kV Afanasevka | 2.5 | -0.28998 | 0.93979 | unavailable
4 | SS-35/10kV Borisovka | 1.6 | -0.0099667 | 0.95751 | unavailable
5 | SS-35/10kV Borissy | 1.6 | -0.87793 | 0.90896 | unavailable
6 | SS-35/10kV Gostishchevo | 4 | -0.22612 | 0.93506 | unavailable
7 | SS-35/10kV Cossack Fox | 2.5 | -0.36811 | 0.94537 | unavailable
8 | SS-35/10kV Kamyzino | 2.5 | -0.87904 | 0.83378 | unavailable
9 | SS-35/10kV Koloskovo | 2.5 | -0.13375 | 0.95304 | unavailable
10 | SS-35/10kV Nikolaevka | 2.5 | -0.072864 | 0.91111 | unavailable
11 | SS-35/10kV Nikolsky | 4 | -0.90223 | 0.97014 | unavailable
12 | SS-35/10kV Pjatnitsky | 4 | -0.38428 | 0.92704 | unavailable
Total current deficit |  |  | -6.0691

## Expected deficit
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class |  | Current deficit, MVA | cos | Note
cos
cos
Belgorodenergo
1 | SS-110/35/10kV D.Poljana | 6.3 | -0.033615 | 0.91497 | unavailable
2 | SS-110/35/10kV Irrigating | 16 | -1.9422 | 0.9465 | unavailable
3 | SS-35/10kV Afanasevka | 2.5 | -0.29498 | 0.93979 | unavailable
4 | SS-35/10kV Borisovka | 1.6 | -0.0099667 | 0.95751 | unavailable
5 | SS-35/10kV Borissy | 1.6 | -0.88793 | 0.90896 | unavailable
6 | SS-35/10kV Gostishchevo | 4 | -0.50612 | 0.93506 | unavailable
7 | SS-35/10kV Cossack Fox | 2.5 | -0.36811 | 0.94537 | unavailable
8 | SS-35/10kV Kamyzino | 2.5 | -0.92334 | 0.83378 | unavailable
9 | SS-35/10kV Koloskovo | 2.5 | -0.22355 | 0.95304 | unavailable
10 | SS-35/10kV Nikolaevka | 2.5 | -0.086864 | 0.91111 | unavailable
11 | SS-35/10kV Nikolsky | 4 | -1.5862 | 0.97014 | unavailable
12 | SS-35/10kV Pjatnitsky | 4 | -0.43928 | 0.92704 | unavailable
Total current deficit |  |  | -7.3022