## Bryansk September 2011
[9 empty] | Table 1 | [12 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
|  |  | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kV Lopandino | 6.3 | 0.231 | 1.2 | 1 day and night | -0.969 | 0 | 6.615 | 7.584 | 7.584 | available | 1 | SS 110/10 kV Lopandino | 6.3 | 0 | 0.231 | 1.2 | 1 day and night | -0.969 | 0 | 6.615 | 7.584 | 7.584 | available
2 | SS 110/35/10 kV Nerussa | 16 | 2.904 | 3.4 | 1 day and night | -0.496 | 0 | 16.8 | 17.296 | 14.787 | available | 2 | SS 110/35/10 kV Nerussa | 16 | 0.0508 | 2.9548 | 2.6 | 1 day and night | 0.3548 | 0 | 16.8 | 16.4452 | 14.787 | available
| Nom. capacity MV, MVA | 16 | 2.013 | 1.5 | 1 day and night | 0.513 | 0 | 16.8 | 14.787 |  |  |  | Nom. capacity MV, MVA | 16 |  | 2.013 | 1.5 | 1 day and night | 0.513 | 0 | 16.8 | 14.787
| Nom. capacity LV, MVA | 16 | 0.891 | 1.9 | 1 day and night | -1.009 | 0 | 16.8 | 17.809 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0508 | 0.9418 | 1.1 | 1 day and night | -0.1582 | 0 | 16.8 | 16.9582
3 | SS 110/6 kV Svenskaya | 6.3 | 1.327 | 1.5 | 1 day and night | -0.173 | 0 | 6.615 | 6.788 | 6.788 | available | 3 | SS 110/6 kV Svenskaya | 6.3 | 0.2356 | 1.5626 | 1.5 | 1 day and night | 0.0626 | 0 | 6.615 | 6.5524 | 6.5524 | available
4 | SS 110/10 kV Khmelevskaya | 6.3 | 0.366 | 0.361 | 1 day and night | 0.005 | 0 | 6.615 | 6.61 | 6.61 | available | 4 | SS 110/10 kV Khmelevskaya | 6.3 | 2.4316 | 2.7976 | 0.361 | 1 day and night | 2.4366 | 0 | 6.615 | 4.1784 | 4.1784 | available
5 | SS 110/6 kV Energoremont | 10 | 5.456 | 6.4 | 1 day and night | -0.944 | 0 | 10.5 | 11.444 | 11.444 | available | 5 | SS 110/6 kV Energoremont | 10 | 0.9354 | 6.3914 | 6.4 | 1 day and night | -0.0086 | 0 | 10.5 | 10.5086 | 10.5086 | available
1 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.805 | 0.671 | 1 day and night | 0.134 | 0 | 10.5 | 10.366 | 10.366 | available | 1 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.6888 | 1.4938 | 0.671 | 1 day and night | 0.8228 | 0 | 10.5 | 9.6772 | 9.6772 | available
2 | SS 110/10 kV Glybochka | 2.5 | 0.215 | 1.225 | 1 day and night | -1.01 | 0 | 2.625 | 3.635 | 3.635 | available | 2 | SS 110/10 kV Glybochka | 2.5 | 0.5421 | 0.7571 | 1.225 | 1 day and night | -0.4679 | 0 | 2.625 | 3.0929 | 3.0929 | available
3 | SS 110/10 kV Desyatukha | 6.3 | 0.885 | 1.187 | 1 day and night | -0.302 | 0 | 6.615 | 6.917 | 6.917 | available | 3 | SS 110/10 kV Desyatukha | 6.3 | 0.0355 | 0.9205 | 1.187 | 1 day and night | -0.2665 | 0 | 6.615 | 6.8815 | 6.8815 | available
4 | SS 110/35/10 kV Ivaytenki | 6.3 | 1.309 | 1.6 | 1 day and night | -0.291 | 0 | 6.615 | 6.906 | 5.972 | available | 4 | SS 110/35/10 kV Ivaytenki | 6.3 | 0.0776 | 1.3866 | 1.6 | 1 day and night | -0.2134 | 0 | 6.615 | 6.8284 | 5.972 | available
| Nom. capacity MV, MVA | 6.3 | 0.643 | 0.9 | 1 day and night | 0 | 0 | 6.615 | 5.972 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.643 | 0.9 | 1 day and night | 0 | 0 | 6.615 | 5.972
| Nom. capacity LV, MVA | 6.3 | 0.666 | 0.7 | 1 day and night | -0.034 | 0 | 6.615 | 6.649 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.0776 | 0.7436 | 0.7 | 1 day and night | 0.0436 | 0 | 6.615 | 6.5714
5 | SS 110/35/10 kV Lugovaya | 16 | 5.093 | 4.7 | 1 day and night | 0.393 | 0 | 16.8 | 16.407 | 12.45 | available | 5 | SS 110/35/10 kV Lugovaya | 16 | 0.0718 | 5.1648 | 4.7 | 1 day and night | 0.4648 | 0 | 16.8 | 16.3352 | 12.45 | available
| Nom. capacity MV, MVA | 16 | 4.35 | 3.8 | 1 day and night | 0.55 | 0 | 16.8 | 12.45 |  |  |  | Nom. capacity MV, MVA | 16 |  | 4.35 | 3.8 | 1 day and night | 0.55 | 0 | 16.8 | 12.45
| Nom. capacity LV, MVA | 16 | 0.743 | 0.9 | 1 day and night | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0718 | 0.8148 | 0.9 | 1 day and night | 0 | 0 | 16.8 | 16.8
6 | SS 110/35/10 kV Plyuskovo | 6.3 | 1.967 | 2.1 | 1 day and night | -0.133 | 0 | 6.615 | 6.748 | 5.385 | available | 6 | SS 110/35/10 kV Plyuskovo | 6.3 | 0.9743 | 2.9413 | 2.1 | 1 day and night | 0.8413 | 0 | 6.615 | 5.7737 | 5.385 | available
| Nom. capacity MV, MVA | 6.3 | 1.23 | 1.1 | 1 day and night | 0 | 0 | 6.615 | 5.385 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1.23 | 1.1 | 1 day and night | 0 | 0 | 6.615 | 5.385
| Nom. capacity LV, MVA | 6.3 | 0.737 | 1 | 1 day and night | -0.263 | 0 | 6.615 | 6.878 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.9743 | 1.7113 | 1 | 1 day and night | 0.7113 | 0 | 6.615 | 5.9037
7 | SS 35/10 kV Aleshinskaya | 2.5 | 0.338 | 0.338 | 1 day and night | 0.338 | 0 | 0.338 | 0 | 0 | available | 7 | SS 35/10 kV Aleshinskaya | 2.5 | 0.0757 | 0.4137 | 0.4137 | 1 day and night | 0.4137 | 0 | 0.4137 | 0 | 0 | available
8 | SS 35/10 kV Altukhovskaya | 1.6 | 0.375 | 0.375 | 1 day and night | 0.375 | 0 | 0.375 | 0 | 0 | available | 8 | SS 35/10 kV Altukhovskaya | 1.6 | 0 | 0.375 | 0.375 | 1 day and night | 0.375 | 0 | 0.375 | 0 | 0 | available
9 | SS 35/10 kV Domashovo | 2.5 | 0.354 | 0.354 | 1 day and night | 0.354 | 0 | 0.354 | 0 | 0 | available | 9 | SS 35/10 kV Domashovo | 2.5 | 0.6934 | 1.0474 | 1.0474 | 1 day and night | 1.0474 | 0 | 1.0474 | 0 | 0 | available
10 | SS 35/6 kV Dronovskaya | 2.5 | 0.354 | 0.354 | 1 day and night | 0.354 | 0 | 0.354 | 0 | 0 | available | 10 | SS 35/6 kV Dronovskaya | 2.5 | 0.0636 | 0.4176 | 0.4176 | 1 day and night | 0.4176 | 0 | 0.4176 | 0 | 0 | available
11 | SS 35/10 kV Kokorevskaya | 4 | 0.851 | 0.851 | 1 day and night | 0.851 | 0 | 0.851 | 0 | 0 | available | 11 | SS 35/10 kV Kokorevskaya | 4 | 0.003 | 0.854 | 0.854 | 1 day and night | 0.854 | 0 | 0.854 | 0 | 0 | available
12 | SS 35/6 kV Malopolpinskaya | 4 | 0.819 | 0.819 | 1 day and night | 0.819 | 0 | 0.819 | 0 | 0 | available | 12 | SS 35/6 kV Malopolpinskaya | 4 | 0.1206 | 0.9396 | 0.9396 | 1 day and night | 0.9396 | 0 | 0.9396 | 0 | 0 | available
13 | SS 35/10 kV Morachevskaya | 1.6 | 0.332 | 0.332 | 1 day and night | 0.332 | 0 | 0.332 | 0 | 0 | available | 13 | SS 35/10 kV Morachevskaya | 1.6 | 0.632 | 0.964 | 0.964 | 1 day and night | 0.964 | 0 | 0.964 | 0 | 0 | available
14 | SS 35/10 kV Saltanovskaya | 2.5 | 0.591 | 0.591 | 1 day and night | 0.591 | 0 | 0.591 | 0 | 0 | available | 14 | SS 35/10 kV Saltanovskaya | 2.5 | 0.0211 | 0.6121 | 0.6121 | 1 day and night | 0.6121 | 0 | 0.6121 | 0 | 0 | available
15 | SS 35/10 kV Svetovo | 2.5 | 0.328 | 0.328 | 1 day and night | 0.328 | 0 | 0.328 | 0 | 0 | available | 15 | SS 35/10 kV Svetovo | 2.5 | 0.0211 | 0.3491 | 0.3491 | 1 day and night | 0.3491 | 0 | 0.3491 | 0 | 0 | available
16 | SS 35/10 kV Seshcha | 2.5 | 0.789 | 0.789 | 1 day and night | 0.789 | 0 | 0.789 | 0 | 0 | available | 16 | SS 35/10 kV Seshcha | 2.5 | 0.01 | 0.799 | 0.799 | 1 day and night | 0.799 | 0 | 0.799 | 0 | 0 | available
17 | SS 35/10 kV Sovkhoznaya | 4 | 0.3 | 0.3 | 1 day and night | 0.3 | 0 | 0.3 | 0 | 0 | available | 17 | SS 35/10 kV Sovkhoznaya | 4 | 0.0071 | 0.3071 | 0.3071 | 1 day and night | 0.3071 | 0 | 0.3071 | 0 | 0 | available
18 | SS 35/10 kV Strachevskaya | 2.5 | 0.494 | 0.494 | 1 day and night | 0.494 | 0 | 0.494 | 0 | 0 | available | 18 | SS 35/10 kV Strachevskaya | 2.5 | 0.1379 | 0.6319 | 0.6319 | 1 day and night | 0.6319 | 0 | 0.6319 | 0 | 0 | available
19 | SS 35/10 kV Strashevichi | 4 | 0.772 | 0.772 | 1 day and night | 0.772 | 0 | 0.772 | 0 | 0 | available | 19 | SS 35/10 kV Strashevichi | 4 | 1.271 | 2.043 | 2.043 | 1 day and night | 2.043 | 0 | 2.043 | 0 | 0 | available
20 | SS 35/10 kV Usozhskaya | 2.5 | 0.685 | 0.685 | 1 day and night | 0.685 | 0 | 0.685 | 0 | 0 | available | 20 | SS 35/10 kV Usozhskaya | 2.5 | 0.054 | 0.739 | 0.739 | 1 day and night | 0.739 | 0 | 0.739 | 0 | 0 | available
21 | SS 35/10 kV Kharinovskaya | 1 | 0.085 | 0.085 | 1 day and night | 0.085 | 0 | 0.085 | 0 | 0 | available | 21 | SS 35/10 kV Kharinovskaya | 1 | 0 | 0.085 | 0.085 | 1 day and night | 0.085 | 0 | 0.085 | 0 | 0 | available
22 | SS 35/10 kV Kharitonovskaya | 4 | 0.667 | 0.667 | 1 day and night | 0.667 | 0 | 0.667 | 0 | 0 | available | 22 | SS 35/10 kV Kharitonovskaya | 4 | 0.1198 | 0.7868 | 0.7868 | 1 day and night | 0.7868 | 0 | 0.7868 | 0 | 0 | available
23 | SS 35/10 kV Divovka | 2.5 | 0.624 | 0.624 | 1 day and night | 0.624 | 0 | 0.624 | 0 | 0 | available | 23 | SS 35/10 kV Divovka | 2.5 | 0.0286 | 0.6526 | 0.6526 | 1 day and night | 0.6526 | 0 | 0.6526 | 0 | 0 | available
24 | SS 35/10 kV Molodkovo | 1 | 0.179 | 0.179 | 1 day and night | 0.179 | 0 | 0.179 | 0 | 0 | available | 24 | SS 35/10 kV Molodkovo | 1 | 0 | 0.179 | 0.179 | 1 day and night | 0.179 | 0 | 0.179 | 0 | 0 | available
25 | SS 35/10 kV Papsuevskaya | 2.5 | 0.434 | 0.434 | 1 day and night | 0.434 | 0 | 0.434 | 0 | 0 | available | 25 | SS 35/10 kV Papsuevskaya | 2.5 | 0.0054 | 0.4394 | 0.4394 | 1 day and night | 0.4394 | 0 | 0.4394 | 0 | 0 | available
26 | SS 35/10 kV Radutinskaya | 1.6 | 0.651 | 0.651 | 1 day and night | 0.651 | 0 | 0.651 | 0 | 0 | available | 26 | SS 35/10 kV Radutinskaya | 1.6 | 0.0957 | 0.7467 | 0.7467 | 1 day and night | 0.7467 | 0 | 0.7467 | 0 | 0 | available
27 | SS 35/6 kV Ushchepye | 1.6 | 0.155 | 0.155 | 1 day and night | 0.155 | 0 | 0.155 | 0 | 0 | available | 27 | SS 35/6 kV Ushchepye | 1.6 | 0.0419 | 0.1969 | 0.1969 | 1 day and night | 0.1969 | 0 | 0.1969 | 0 | 0 | available
28 | SS 35/10 kV Ushchepye | 1.6 | 0.049 | 0.049 | 1 day and night | 0.049 | 0 | 0.049 | 0 | 0 | available | 28 | SS 35/10 kV Ushchepye | 1.6 | 0 | 0.049 | 0.049 | 1 day and night | 0.049 | 0 | 0.049 | 0 | 0 | available
29 | SS 35/10 kV Yakovskaya | 2.5 | 0.58 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0 | 0 | available | 29 | SS 35/10 kV Yakovskaya | 2.5 | 0.0391 | 0.6191 | 0.6191 | 1 day and night | 0.6191 | 0 | 0.6191 | 0 | 0 | available
30 | SS 110/35/6 kV Aksinino | 40+40 | 21.1 | 0 | 0 | 21.1 | 0 | 42 | 20.9 | 20.9 | available | 30 | SS 110/35/6 kV Aksinino | 40+40 | 0.019 | 21.119 | 0 | 0 | 21.119 | 0 | 42 | 20.881 | 20.881 | available
| Nom. capacity MV, MVA | 40+40 | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5
| Nom. capacity LV, MVA | 40+40 | 17.6 | 0 | 0 | 17.6 | 0 | 42 | 24.4 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.019 | 17.619 | 0 | 0 | 17.619 | 0 | 42 | 24.381
31 | SS 110/10 kV Airport | 6,3+6,3 | 0.736 | 0 | 0 | 0.736 | 0 | 6.615 | 5.879 | 5.879 | available | 31 | SS 110/10 kV Airport | 6,3+6,3 | 0.1044 | 0.8404 | 0 | 0 | 0.8404 | 0 | 6.615 | 5.7746 | 5.7746 | available
32 | SS 110/6 kV Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | unavailable | 32 | SS 110/6 kV Bezhitskaya | 25+40 | 4.7386 | 39.3086 | 0 | 0 | 39.3086 | 0 | 26.25 | -13.0586 | -13.0586 | unavailable
33 | SS 110/6 kV Water intake | 6,3+6,3 | 2.11 | 0 | 0 | 2.11 | 0 | 6.615 | 4.505 | 4.505 | available | 33 | SS 110/6 kV Water intake | 6,3+6,3 | 1.9699 | 4.0799 | 0 | 0 | 4.0799 | 0 | 6.615 | 2.5351 | 2.5351 | available
34 | SS 110/6 kV Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | unavailable | 34 | SS 110/6 kV Gorodishchenskaya | 16+16 | 4.1068 | 29.6668 | 1.5 | 12 hours | 28.1668 | 0 | 16.8 | -11.3668 | -11.3668 | unavailable
35 | SS 110/10 kV Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138 | -0.138 | unavailable | 35 | SS 110/10 kV Dobrunskaya | 6,3+4 | 2.6345 | 6.9725 | 0 | 0 | 6.9725 | 0 | 4.2 | -2.7725 | -2.7725 | unavailable
36 | SS 110/35/6 kV Dormashevskaya | 40+63 | 44.35 | 0 | 0 | 44.35 | 0 | 42 | -2.35 | -2.35 | unavailable | 36 | SS 110/35/6 kV Dormashevskaya | 40+63 | 5.7438 | 50.0938 | 0 | 0 | 50.0938 | 0 | 42 | -8.0938 | -8.0938 | unavailable
| Nom. capacity MV, MVA | 40+63 | 25.76 | 0 | 0 | 25.76 | 0 | 42 | 16.24 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 25.76 | 0 | 0 | 25.76 | 0 | 42 | 16.24
| Nom. capacity LV, MVA | 40+63 | 18.59 | 0 | 0 | 18.59 | 0 | 42 | 23.41 |  |  |  | Nom. capacity LV, MVA | 40+63 | 5.7438 | 24.3338 | 0 | 0 | 24.3338 | 0 | 42 | 17.6662
37 | SS 110/35/10 kV Dubrovskaya | 16+16 | 8.741 | 0 | 0 | 8.741 | 0 | 16.8 | 8.059 | 8.059 | available | 37 | SS 110/35/10 kV Dubrovskaya | 16+16 | 0.1105 | 8.8515 | 0 | 0 | 8.8515 | 0 | 16.8 | 7.9485 | 7.9485 | available
| Nom. capacity MV, MVA | 16+16 | 5.239 | 0 | 0 | 5.239 | 0 | 16.8 | 11.561 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.239 | 0 | 0 | 5.239 | 0 | 16.8 | 11.561
| Nom. capacity LV, MVA | 16+16 | 3.502 | 0 | 0 | 3.502 | 0 | 16.8 | 13.298 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1105 | 3.6125 | 0 | 0 | 3.6125 | 0 | 16.8 | 13.1875
38 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 37.17 | 7.92 | 12 hours | 29.25 | 0 | 26.25 | -3 | -3 | unavailable | 38 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 0.636 | 37.806 | 8.9 | 12 hours | 28.906 | 0 | 26.25 | -2.656 | -3.636 | unavailable
| Nom. capacity MV, MVA | 25+25 | 7.92 | 7.92 | 12 hours | 0 | 0 | 26.25 | 18.33 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 7.92 | 8.9 | 12 hours | -0.98 | 0 | 26.25 | 18.33
| Nom. capacity LV, MVA | 25+25 | 29.25 | 0 | 0 | 29.25 | 0 | 26.25 | -3 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.636 | 29.886 | 0 | 0 | 29.886 | 0 | 26.25 | -3.636
39 | SS 110/35/10 kV Zhukovskaya | 16+25 | 12.76 | 5.2 | 6 hours | 7.56 | 0 | 16.8 | 9.24 | 9.24 | available | 39 | SS 110/35/10 kV Zhukovskaya | 16+25 | 0.2581 | 13.0181 | 5.2 | 6 hours | 7.8181 | 0 | 16.8 | 8.9819 | 8.9819 | available
| Nom. capacity MV, MVA | 16+25 | 5.9 | 5.2 | 6 hours | 0.7 | 0 | 16.8 | 10.9 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 5.9 | 5.2 | 6 hours | 0.7 | 0 | 16.8 | 10.9
| Nom. capacity LV, MVA | 16+25 | 6.86 | 0 | 0 | 6.86 | 0 | 16.8 | 9.94 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.2581 | 7.1181 | 0 | 0 | 7.1181 | 0 | 16.8 | 9.6819
40 | SS 110/6 kV Zarechnaya | 10+10 | 8.27 | 0 | 0 | 8.27 | 0 | 10.5 | 2.23 | 2.23 | available | 40 | SS 110/6 kV Zarechnaya | 10+10 | 1.721 | 9.991 | 0 | 0 | 9.991 | 0 | 10.5 | 0.509 | 0.509 | available
41 | SS 110/35/6 kV Ivotskaya | 25+25 | 15.72 | 2.68 | 6 hours | 13.04 | 0 | 26.25 | 13.21 | 13.21 | available | 41 | SS 110/35/6 kV Ivotskaya | 25+25 | 0 | 15.72 | 2.4 | 6 hours | 13.32 | 0 | 26.25 | 12.93 | 12.93 | available
| Nom. capacity MV, MVA | 25+25 | 6.07 | 2.68 | 6 hours | 3.39 | 0 | 26.25 | 20.18 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.07 | 2.4 | 6 hours | 3.67 | 0 | 26.25 | 20.18
| Nom. capacity LV, MVA | 25+25 | 9.65 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 9.65 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kV Kamvolnaya | 25+25 | 17.92 | 0 | 0 | 17.92 | 0 | 26.25 | 8.33 | 8.33 | available | 42 | SS 110/6 kV Kamvolnaya | 25+25 | 5.0198 | 22.9398 | 0 | 0 | 22.9398 | 0 | 26.25 | 3.3102 | 3.3102 | available
43 | SS 110/6 kV Karachevskaya | 16+25 | 11.684 | 0 | 0 | 11.684 | 0 | 16.8 | 5.116 | 5.116 | available | 43 | SS 110/6 kV Karachevskaya | 16+25 | 0.4708 | 12.1548 | 0 | 0 | 12.1548 | 0 | 16.8 | 4.6452 | 4.6452 | available
44 | SS 110/6 kV Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | unavailable | 44 | SS 110/6 kV Karachizhskaya | 10+10 | 2.7528 | 21.0328 | 0 | 0 | 21.0328 | 0 | 10.5 | -10.5328 | -10.5328 | unavailable
45 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 7.056 | 1.4 | 6 hours | 5.656 | 0 | 10.5 | 4.844 | 4.844 | available | 45 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 0.8137 | 7.8697 | 1.4 | 6 hours | 6.4697 | 0 | 10.5 | 4.0303 | 4.0303 | available
| Nom. capacity MV, MVA | 10+16 | 2.234 | 1.4 | 6 hours | 0.834 | 0 | 10.5 | 8.266 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 2.234 | 1.4 | 6 hours | 0.834 | 0 | 10.5 | 8.266
| Nom. capacity LV, MVA | 10+16 | 4.822 | 0 | 0 | 4.822 | 0 | 10.5 | 5.678 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.8137 | 5.6357 | 0 | 0 | 5.6357 | 0 | 10.5 | 4.8643
46 | SS 110/35/10 kV Komarichi | 16+16 | 10.253 | 3.7 | 6 hours | 6.553 | 0 | 16.8 | 10.247 | 10.247 | available | 46 | SS 110/35/10 kV Komarichi | 16+16 | 0.2245 | 10.4775 | 3.7 | 6 hours | 6.7775 | 0 | 16.8 | 10.0225 | 10.0225 | available
| Nom. capacity MV, MVA | 16+16 | 4.997 | 3.7 | 6 hours | 1.297 | 0 | 16.8 | 11.803 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.997 | 3.7 | 6 hours | 1.297 | 0 | 16.8 | 11.803
| Nom. capacity LV, MVA | 16+16 | 5.256 | 0 | 0 | 5.256 | 0 | 16.8 | 11.544 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.2245 | 5.4805 | 0 | 0 | 5.4805 | 0 | 16.8 | 11.3195
47 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.717 | 0 | 0 | 0.717 | 0 | 2.625 | 1.908 | 1.908 | available | 47 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.2765 | 0.9935 | 0 | 0 | 0.9935 | 0 | 2.625 | 1.6315 | 1.6315 | available
48 | SS 110/6 kV Mamonovskaya | 16+16 | 15.29 | 0 | 0 | 15.29 | 0 | 16.8 | 1.51 | 1.51 | available | 48 | SS 110/6 kV Mamonovskaya | 16+16 | 0.9592 | 16.2492 | 0 | 0 | 16.2492 | 0 | 16.8 | 0.5508 | 0.5508 | available
49 | SS 110/35/10 kV Maritskaya | 10+16 | 5.796 | 4.5 | 6 hours | 1.296 | 0 | 10.5 | 9.204 | 5.362 | available | 49 | SS 110/35/10 kV Maritskaya | 10+16 | 0.7403 | 6.5363 | 4.5 | 6 hours | 2.0363 | 0 | 10.5 | 8.4637 | 5.362 | available
| Nom. capacity MV, MVA | 10+16 | 5.138 | 4.5 | 6 hours | 0 | 0 | 10.5 | 5.362 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 5.138 | 4.5 | 6 hours | 0 | 0 | 10.5 | 5.362
| Nom. capacity LV, MVA | 10+16 | 0.658 | 0 | 0 | 0.658 | 0 | 10.5 | 9.842 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.7403 | 1.3983 | 0 | 0 | 1.3983 | 0 | 10.5 | 9.1017
50 | SS 110/6 kV Michurinskaya | 10+10 | 3.457 | 0 | 0 | 3.457 | 0 | 6.615 | 3.158 | 3.158 | available | 50 | SS 110/6 kV Michurinskaya | 10+10 | 1.2903 | 4.7473 | 0 | 0 | 4.7473 | 0 | 6.615 | 1.8677 | 1.8677 | available
51 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 2.438 | 0 | 0 | 2.438 | 0 | 6.615 | 4.177 | 4.177 | available | 51 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 0.3663 | 2.8043 | 0 | 0 | 2.8043 | 0 | 6.615 | 3.8107 | 3.8107 | available
52 | SS 110/10 kV Polpinskaya | 16+16 | 5.734 | 0 | 0 | 5.734 | 0 | 16.8 | 11.066 | 11.066 | available | 52 | SS 110/10 kV Polpinskaya | 16+16 | 0.308 | 6.042 | 0 | 0 | 6.042 | 0 | 16.8 | 10.758 | 10.758 | available
53 | SS 110/6 kV Sovetskaya | 16+16+25+40 | 36.96 | 0 | 0 | 36.96 | 0 | 59.85 | 22.89 | 22.89 | available | 53 | SS 110/6 kV Sovetskaya | 16+16+25+40 | 22.3976 | 59.3576 | 0 | 0 | 59.3576 | 0 | 59.85 | 0.4924 | 0.4924 | available
54 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 46.85 | 0 | 0 | 46.85 | 0 | 75.075 | 28.225 | 28.225 | available | 54 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 0.4468 | 47.2968 | 0 | 0 | 47.2968 | 0 | 75.075 | 27.7782 | 27.7782 | available
55 | SS 110/10 kV Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | available | 55 | SS 110/10 kV Teplichnaya | 10+10 | 0.7125 | 5.6125 | 0 | 0 | 5.6125 | 0 | 10.5 | 4.8875 | 4.8875 | available
56 | SS 110/6 kV Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | available | 56 | SS 110/6 kV Uritskaya | 20+20 | 0.1742 | 14.5542 | 0 | 0 | 14.5542 | 0 | 21 | 6.4458 | 6.4458 | available
57 | SS 110/35/10 kV Tsentralnaya | 16+16 | 10.488 | 4.8 | 6 hours | 5.688 | 0 | 16.8 | 11.112 | 10.032 | available | 57 | SS 110/35/10 kV Tsentralnaya | 16+16 | 0.1817 | 10.6697 | 4.8 | 6 hours | 5.8697 | 0 | 16.8 | 10.9303 | 9.8503 | available
| Nom. capacity MV, MVA | 16+16 | 3.72 | 4.8 | 6 hours | -1.08 | 0 | 16.8 | 13.08 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.72 | 4.8 | 6 hours | -1.08 | 0 | 16.8 | 13.08
| Nom. capacity LV, MVA | 16+16 | 6.768 | 0 | 0 | 6.768 | 0 | 16.8 | 10.032 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1817 | 6.9497 | 0 | 0 | 6.9497 | 0 | 16.8 | 9.8503
58 | SS 110/6 kV Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | unavailable | 58 | SS 110/6 kV Yuzhnaya | 16+25 | 0.238 | 19.668 | 0 | 0 | 19.668 | 0 | 16.8 | -2.868 | -2.868 | unavailable
59 | SS 110/10 kV Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | available | 59 | SS 110/10 kV Bobovichi | 6,3+2,5 | 0.0418 | 1.5388 | 0 | 0 | 1.5388 | 0 | 2.625 | 1.0862 | 1.0862 | available
60 | SS 110/6 kV Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | available | 60 | SS 110/6 kV Belaya Berezka | 16+25 | 0 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | available
61 | SS 110/10 kV Valuets | 4+6,3 | 1.239 | 0 | 0 | 1.239 | 0 | 4.2 | 2.961 | 2.961 | available | 61 | SS 110/10 kV Valuets | 4+6,3 | 0.5353 | 1.7743 | 0 | 0 | 1.7743 | 0 | 4.2 | 2.4257 | 2.4257 | available
62 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 1.873 | 0.54 | 3 hours | 1.333 | 0 | 6.615 | 5.282 | 4.984 | available | 62 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 0.0161 | 1.8891 | 0.54 | 3 hours | 1.3491 | 0 | 6.615 | 5.2659 | 4.9679 | available
| Nom. capacity MV, MVA | 10+6,3 | 0.242 | 0.54 | 3 hours | 0 | 0 | 6.615 | 6.373 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.242 | 0.54 | 3 hours | 0 | 0 | 6.615 | 6.373
| Nom. capacity LV, MVA | 10+6,3 | 1.631 | 0 | 0 | 1.631 | 0 | 6.615 | 4.984 |  |  |  | Nom. capacity LV, MVA | 10+6,3 | 0.0161 | 1.6471 | 0 | 0 | 1.6471 | 0 | 6.615 | 4.9679
63 | SS 110/6 kV Vysokoe | 40+40 | 31.467 | 0 | 0 | 31.467 | 0 | 42 | 10.533 | 10.533 | available | 63 | SS 110/6 kV Vysokoe | 40+40 | 0.0708 | 31.5378 | 0 | 0 | 31.5378 | 0 | 42 | 10.4622 | 10.4622 | available
64 | SS 110/10 kV Zalineynaya | 10+6,3 | 2.493 | 0 | 0 | 2.493 | 0 | 6.615 | 4.122 | 4.122 | available | 64 | SS 110/10 kV Zalineynaya | 10+6,3 | 0.3571 | 2.8501 | 0 | 0 | 2.8501 | 0 | 6.615 | 3.7649 | 3.7649 | available
65 | SS 110/6 kV Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | unavailable | 65 | SS 110/6 kV Zapadnaya | 10+10 | 0.6479 | 11.1479 | 0 | 0 | 11.1479 | 0 | 10.5 | -0.6479 | -0.6479 | unavailable
66 | SS 110/35/10 kV Klimovo | 16+16 | 10.535 | 1.64 | 6 hours | 8.895 | 0 | 16.8 | 7.905 | 7.905 | available | 66 | SS 110/35/10 kV Klimovo | 16+16 | 0.2328 | 10.7678 | 1.64 | 6 hours | 9.1278 | 0 | 16.8 | 7.6722 | 7.6722 | available
| Nom. capacity MV, MVA | 16+16 | 3.301 | 1.64 | 6 hours | 1.661 | 0 | 16.8 | 13.499 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.301 | 1.64 | 6 hours | 1.661 | 0 | 16.8 | 13.499
| Nom. capacity LV, MVA | 16+16 | 7.234 | 0 | 0 | 7.234 | 0 | 16.8 | 9.566 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.2328 | 7.4668 | 0 | 0 | 7.4668 | 0 | 16.8 | 9.3332
67 | SS 110/35/6 kV Kozhany | 10+10 | 3.521 | 3.12 | 6 hours | 0.401 | 0 | 10.5 | 10.099 | 7.795 | available | 67 | SS 110/35/6 kV Kozhany | 10+10 | 0.019 | 3.54 | 3.12 | 6 hours | 0.42 | 0 | 10.5 | 10.08 | 7.795 | available
| Nom. capacity MV, MVA | 10+10 | 2.705 | 3.12 | 6 hours | -0.415 | 0 | 10.5 | 7.795 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 2.705 | 3.12 | 6 hours | -0.415 | 0 | 10.5 | 7.795
| Nom. capacity LV, MVA | 10+10 | 0.816 | 0 | 0 | 0.816 | 0 | 10.5 | 9.684 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.019 | 0.835 | 0 | 0 | 0.835 | 0 | 10.5 | 9.665
68 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 0.668 | 0 | 0 | 0.668 | 0 | 2.625 | 1.957 | 1.957 | available | 68 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 0.1831 | 0.8511 | 0 | 0 | 0.8511 | 0 | 2.625 | 1.7739 | 1.7739 | available
69 | SS 110/35/10 kV Pogar | 16+16+16 | 9.411 | 1.8 | 6 hours | 7.611 | 0 | 33.6 | 25.989 | 25.989 | available | 69 | SS 110/35/10 kV Pogar | 16+16+16 | 1.7507 | 11.1617 | 1.8 | 6 hours | 9.3617 | 0 | 33.6 | 24.2383 | 24.2383 | available
| Nom. capacity MV, MVA | 16+16 | 1.952 | 1.8 | 6 hours | 0.152 | 0 | 33.6 | 31.648 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.952 | 1.8 | 6 hours | 0.152 | 0 | 33.6 | 31.648
| Nom. capacity LV, MVA | 16+16 | 7.459 | 0 | 0 | 7.459 | 0 | 33.6 | 26.141 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.7507 | 9.2097 | 0 | 0 | 9.2097 | 0 | 33.6 | 24.3903
70 | SS 110/35/10 kV Pochepskaya | 25+25 | 11.182 | 2.21 | 3 hours | 8.972 | 0 | 26.25 | 17.278 | 16.497 | available | 70 | SS 110/35/10 kV Pochepskaya | 25+25 | 3.7249 | 14.9069 | 2.21 | 3 hours | 12.6969 | 0 | 26.25 | 13.5531 | 12.7721 | available
| Nom. capacity MV, MVA | 25+25 | 1.429 | 2.21 | 3 hours | -0.781 | 0 | 26.25 | 24.821 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 1.429 | 2.21 | 3 hours | -0.781 | 0 | 26.25 | 24.821
| Nom. capacity LV, MVA | 25+25 | 9.753 | 0 | 0 | 9.753 | 0 | 26.25 | 16.497 |  |  |  | Nom. capacity LV, MVA | 25+25 | 3.7249 | 13.4779 | 0 | 0 | 13.4779 | 0 | 26.25 | 12.7721
71 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.279 | 0 | 0 | 0.279 | 0 | 2.625 | 2.346 | 2.346 | available | 71 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.221 | 0.5 | 0 | 0 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | available
72 | SS 110/35/10 kV Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 16.8 | 11.576 | 9.465 | available | 72 | SS 110/35/10 kV Starodub | 16+16 | 0.0658 | 12.6298 | 7.34 | 6 hours | 5.2898 | 0 | 16.8 | 11.5102 | 9.465 | available
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 16.8 | 9.465 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 16.8 | 9.465
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 16.8 | 11.571 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.0658 | 5.2948 | 0 | 0 | 5.2948 | 0 | 16.8 | 11.5052
73 | SS 110/10 kV Staroselye | 6,3+6,3 | 1.116 | 0 | 0 | 1.116 | 0 | 6.615 | 5.499 | 5.499 | available | 73 | SS 110/10 kV Staroselye | 6,3+6,3 | 0.1533 | 1.2693 | 0 | 0 | 1.2693 | 0 | 6.615 | 5.3457 | 5.3457 | available
74 | SS 110/35/6 kV Surazh | 16+16 | 19.433 | 3.04 | 6 hours | 16.393 | 0 | 16.8 | 0.407 | 0.185 | available | 74 | SS 110/35/6 kV Surazh | 16+16 | 0 | 19.433 | 3.04 | 6 hours | 16.393 | 0 | 16.8 | 0.407 | 0.185 | available
| Nom. capacity MV, MVA | 16+16 | 2.818 | 3.04 | 6 hours | -0.222 | 0 | 16.8 | 13.982 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 2.818 | 3.04 | 6 hours | -0.222 | 0 | 16.8 | 13.982
| Nom. capacity LV, MVA | 16+16 | 16.615 | 0 | 0 | 16.615 | 0 | 16.8 | 0.185 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 16.615 | 0 | 0 | 16.615 | 0 | 16.8 | 0.185
75 | SS 110/10 kV Trubchevsk | 16+10 | 7.977 | 0 | 0 | 7.977 | 0 | 10.5 | 2.523 | 2.523 | available | 75 | SS 110/10 kV Trubchevsk | 16+10 | 0.7203 | 8.6973 | 0 | 0 | 8.6973 | 0 | 10.5 | 1.8027 | 1.8027 | available
76 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.819 | 0 | 0 | 0.819 | 0 | 6.615 | 5.796 | 5.796 | available | 76 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.0301 | 0.8491 | 0 | 0 | 0.8491 | 0 | 6.615 | 5.7659 | 5.7659 | available
77 | SS 110/35/6 kV Yubileynaya | 16+16 | 13.228 | 6.45 | 3 hours | 6.778 | 0 | 16.8 | 10.022 | 9.905 | available | 77 | SS 110/35/6 kV Yubileynaya | 16+16 | 1.9362 | 15.1642 | 6.45 | 3 hours | 8.7142 | 0 | 16.8 | 8.0858 | 7.9688 | available
| Nom. capacity MV, MVA | 16+16 | 6.333 | 6.45 | 3 hours | 0 | 0 | 16.8 | 10.467 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.333 | 6.45 | 3 hours | 0 | 0 | 16.8 | 10.467
| Nom. capacity LV, MVA | 16+16 | 6.895 | 0 | 0 | 6.895 | 0 | 16.8 | 9.905 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.9362 | 8.8312 | 0 | 0 | 8.8312 | 0 | 16.8 | 7.9688
78 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 3.334 | 0 | 0 | 3.334 | 0 | 6.615 | 3.281 | 3.281 | available | 78 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 0.043 | 3.377 | 0 | 0 | 3.377 | 0 | 6.615 | 3.238 | 3.238 | available
79 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 3.119 | 0 | 0 | 3.119 | 0 | 6.615 | 3.496 | 3.496 | available | 79 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 0.0187 | 3.1377 | 0 | 0 | 3.1377 | 0 | 6.615 | 3.4773 | 3.4773 | available
80 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.708 | 0 | 0 | 0.708 | 0 | 1.68 | 0.972 | 0.972 | available | 80 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.1153 | 0.8233 | 0 | 0 | 0.8233 | 0 | 1.68 | 0.8567 | 0.8567 | available
81 | SS 35/6 kV Bytosh | 3,2+6,3 | 2.533 | 0 | 0 | 2.533 | 0 | 3.36 | 0.827 | 0.827 | available | 81 | SS 35/6 kV Bytosh | 3,2+6,3 | 0.0022 | 2.5352 | 0 | 0 | 2.5352 | 0 | 3.36 | 0.8248 | 0.8248 | available
82 | SS 35/6 kV Velyaminovskaya | 4+4 | 1.217 | 0 | 0 | 1.217 | 0 | 4.2 | 2.983 | 2.983 | available | 82 | SS 35/6 kV Velyaminovskaya | 4+4 | 0.241 | 1.458 | 0 | 0 | 1.458 | 0 | 4.2 | 2.742 | 2.742 | available
83 | SS 35/6 kV Vetma | 2,5+2,5 | 0.425 | 0 | 0 | 0.425 | 0 | 2.625 | 2.2 | 2.2 | available | 83 | SS 35/6 kV Vetma | 2,5+2,5 | 0.0423 | 0.4673 | 0 | 0 | 0.4673 | 0 | 2.625 | 2.1577 | 2.1577 | available
84 | SS 35/6 kV Volodarskaya | 10+6,3 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | unavailable | 84 | SS 35/6 kV Volodarskaya | 10+6,3 | 0 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | unavailable
85 | SS 35/10 kV Glodnevskaya | 4+2,5 | 1.099 | 0 | 0 | 1.099 | 0 | 2.625 | 1.526 | 1.526 | available | 85 | SS 35/10 kV Glodnevskaya | 4+2,5 | 0.0594 | 1.1584 | 0 | 0 | 1.1584 | 0 | 2.625 | 1.4666 | 1.4666 | available
86 | SS 35/6 kV Gorodskaya | 10+10 | 12.37 | 0 | 0 | 12.37 | 0 | 10.5 | -1.87 | -1.87 | unavailable | 86 | SS 35/6 kV Gorodskaya | 10+10 | 0 | 12.37 | 0 | 0 | 12.37 | 0 | 10.5 | -1.87 | -1.87 | unavailable
87 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.833 | 0 | 0 | 0.833 | 0 | 4.2 | 3.367 | 3.367 | available | 87 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.0697 | 0.9027 | 0 | 0 | 0.9027 | 0 | 4.2 | 3.2973 | 3.2973 | available
88 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0.253 | 0 | 0 | 0.253 | 0 | 1.68 | 1.427 | 1.427 | available | 88 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0 | 0.253 | 0 | 0 | 0.253 | 0 | 1.68 | 1.427 | 1.427 | available
89 | SS 35/10 kV Zhiryatinskaya | 4+4 | 1.101 | 0 | 0 | 1.101 | 0 | 4.2 | 3.099 | 3.099 | available | 89 | SS 35/10 kV Zhiryatinskaya | 4+4 | 0.3674 | 1.4684 | 0 | 0 | 1.4684 | 0 | 4.2 | 2.7316 | 2.7316 | available
90 | SS 35/10 kV Igritskaya | 4+6,3 | 1.379 | 0 | 0 | 1.379 | 0 | 4.2 | 2.821 | 2.821 | available | 90 | SS 35/10 kV Igritskaya | 4+6,3 | 0.101 | 1.48 | 0 | 0 | 1.48 | 0 | 4.2 | 2.72 | 2.72 | available
91 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.168 | 0 | 0 | 0.168 | 0 | 1.05 | 0.882 | 0.882 | available | 91 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.038 | 0.206 | 0 | 0 | 0.206 | 0 | 1.05 | 0.844 | 0.844 | available
92 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.258 | 0 | 0 | 0.258 | 0 | 2.625 | 2.367 | 2.367 | available | 92 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.0262 | 0.2842 | 0 | 0 | 0.2842 | 0 | 2.625 | 2.3408 | 2.3408 | available
93 | SS 35/10 kV Krupets | 2,5+2,5 | 0.805 | 0 | 0 | 0.805 | 0 | 2.625 | 1.82 | 1.82 | available | 93 | SS 35/10 kV Krupets | 2,5+2,5 | 0.7713 | 1.5763 | 0 | 0 | 1.5763 | 0 | 2.625 | 1.0487 | 1.0487 | available
94 | SS 35/10 kV Luna | 1,6+1,6 | 0.638 | 0 | 0 | 0.638 | 0 | 1.68 | 1.042 | 1.042 | available | 94 | SS 35/10 kV Luna | 1,6+1,6 | 0 | 0.638 | 0 | 0 | 0.638 | 0 | 1.68 | 1.042 | 1.042 | available
95 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 5.144 | 0 | 0 | 5.144 | 0 | 6.615 | 1.471 | 1.471 | available | 95 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 0.0285 | 5.1725 | 0 | 0 | 5.1725 | 0 | 6.615 | 1.4425 | 1.4425 | available
96 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.86 | 0 | 0 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | available | 96 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.1441 | 1.0041 | 0 | 0 | 1.0041 | 0 | 1.68 | 0.6759 | 0.6759 | available
97 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.155 | 0 | 0 | 0.155 | 0 | 1.68 | 1.525 | 1.525 | available | 97 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.0122 | 0.1672 | 0 | 0 | 0.1672 | 0 | 1.68 | 1.5128 | 1.5128 | available
98 | SS 35/10 kV Norinskaya | 4+4 | 0.512 | 0 | 0 | 0.512 | 0 | 4.2 | 3.688 | 3.688 | available | 98 | SS 35/10 kV Norinskaya | 4+4 | 0.0744 | 0.5864 | 0 | 0 | 0.5864 | 0 | 4.2 | 3.6136 | 3.6136 | available
99 | SS 35/6 kV Paltso | 4+2,5 | 0.468 | 0 | 0 | 0.468 | 0 | 2.625 | 2.157 | 2.157 | available | 99 | SS 35/6 kV Paltso | 4+2,5 | 0.0331 | 0.5011 | 0 | 0 | 0.5011 | 0 | 2.625 | 2.1239 | 2.1239 | available
100 | SS 35/6 kV Pobeda | 4+4 | 2.399 | 0 | 0 | 2.399 | 0 | 4.2 | 1.801 | 1.801 | available | 100 | SS 35/6 kV Pobeda | 4+4 | 0.0336 | 2.4326 | 0 | 0 | 2.4326 | 0 | 4.2 | 1.7674 | 1.7674 | available
101 | SS 35/10 kV Pogreby | 4+4 | 0.915 | 0 | 0 | 0.915 | 0 | 4.2 | 3.285 | 3.285 | available | 101 | SS 35/10 kV Pogreby | 4+4 | 0.057 | 0.972 | 0 | 0 | 0.972 | 0 | 4.2 | 3.228 | 3.228 | available
102 | SS 35/10 kV Privolskaya | 2,5+1,6 | 1.329 | 0 | 0 | 1.329 | 0 | 1.68 | 0.351 | 0.351 | available | 102 | SS 35/10 kV Privolskaya | 2,5+1,6 | 0.3468 | 1.6758 | 0 | 0 | 1.6758 | 0 | 1.68 | 0.0042 | 0.0042 | available
103 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0.711 | 0 | 0 | 0.711 | 0 | 2.625 | 1.914 | 1.914 | available | 103 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0 | 0.711 | 0 | 0 | 0.711 | 0 | 2.625 | 1.914 | 1.914 | available
104 | SS 35/10 kV Rognedinskaya | 4+6,3 | 1.511 | 0 | 0 | 1.511 | 0 | 4.2 | 2.689 | 2.689 | available | 104 | SS 35/10 kV Rognedinskaya | 4+6,3 | 0.0474 | 1.5584 | 0 | 0 | 1.5584 | 0 | 4.2 | 2.6416 | 2.6416 | available
105 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.835 | 0 | 0 | 0.835 | 0 | 4.2 | 3.365 | 3.365 | available | 105 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.029 | 0.864 | 0 | 0 | 0.864 | 0 | 4.2 | 3.336 | 3.336 | available
106 | SS 35/10 kV Sevskaya | 6,3+6,3 | 3.607 | 0 | 0 | 3.607 | 0 | 6.615 | 3.008 | 3.008 | available | 106 | SS 35/10 kV Sevskaya | 6,3+6,3 | 0.8179 | 4.4249 | 0 | 0 | 4.4249 | 0 | 6.615 | 2.1901 | 2.1901 | available
107 | SS 35/6 kc Seshcha | 1,6+4 | 2.1 | 0 | 0 | 2.1 | 0 | 1.68 | -0.42 | -0.42 | unavailable | 107 | SS 35/6 kc Seshcha | 1,6+4 | 0.5551 | 2.6551 | 0 | 0 | 2.6551 | 0 | 1.68 | -0.9751 | -0.9751 | unavailable
108 | SS 35/6 kV Star | 10+10 | 2.806 | 0 | 0 | 2.806 | 0 | 10.5 | 7.694 | 7.694 | available | 108 | SS 35/6 kV Star | 10+10 | 0 | 2.806 | 0 | 0 | 2.806 | 0 | 10.5 | 7.694 | 7.694 | available
109 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.578 | 0 | 0 | 0.578 | 0 | 2.625 | 2.047 | 2.047 | available | 109 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.5185 | 1.0965 | 0 | 0 | 1.0965 | 0 | 2.625 | 1.5285 | 1.5285 | available
110 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.493 | 0 | 0 | 0.493 | 0 | 1.68 | 1.187 | 1.187 | available | 110 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.0467 | 0.5397 | 0 | 0 | 0.5397 | 0 | 1.68 | 1.1403 | 1.1403 | available
111 | SS 35/6 kV Fokinskaya | 16+16+16 | 19.71 | 0 | 0 | 19.71 | 0 | 33.6 | 13.89 | 13.89 | available | 111 | SS 35/6 kV Fokinskaya | 16+16+16 | 4.9711 | 24.6811 | 0 | 0 | 24.6811 | 0 | 33.6 | 8.9189 | 8.9189 | available
112 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | available | 112 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 3.8008 | 12.1008 | 0 | 0 | 12.1008 | 0 | 12.495 | 0.3942 | 0.3942 | available
113 | SS 35/10 kV Khvoshchevskaya | 2,5+2,5 | 1.288 | 0 | 0 | 1.288 | 0 | 2.625 | 1.337 | 1.337 | available | 113 | SS 35/10 kV Khvoshchevskaya | 2,5+2,5 | 0.1743 | 1.4623 | 0 | 0 | 1.4623 | 0 | 2.625 | 1.1627 | 1.1627 | available
114 | SS 35/10 kV Abarinskaya | 4+4 | 0.643 | 0 | 0 | 0.643 | 0 | 4.2 | 3.557 | 3.557 | available | 114 | SS 35/10 kV Abarinskaya | 4+4 | 0.101 | 0.744 | 0 | 0 | 0.744 | 0 | 4.2 | 3.456 | 3.456 | available
115 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 1.023 | 0 | 0 | 1.023 | 0 | 2.625 | 1.602 | 1.602 | available | 115 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 0.0872 | 1.1102 | 0 | 0 | 1.1102 | 0 | 2.625 | 1.5148 | 1.5148 | available
116 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.933 | 0 | 0 | 0.933 | 0 | 1.68 | 0.747 | 0.747 | available | 116 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.046 | 0.979 | 0 | 0 | 0.979 | 0 | 1.68 | 0.701 | 0 | available
117 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.537 | 0 | 0 | 0.537 | 0 | 1.68 | 1.143 | 1.143 | available | 117 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.0343 | 0.5713 | 0 | 0 | 0.5713 | 0 | 1.68 | 1.1087 | 1.1087 | available
118 | SS 35/6 kV Water intake | 2,5+2,5 | 0.242 | 0 | 0 | 0.242 | 0 | 2.625 | 2.383 | 2.383 | available | 118 | SS 35/6 kV Water intake | 2,5+2,5 | 0 | 0.242 | 0 | 0 | 0.242 | 0 | 2.625 | 2.383 | 2.383 | available
119 | SS 35/10 kV Voronok | 2,5+3,2 | 1.517 | 0 | 0 | 1.517 | 0 | 2.625 | 1.108 | 1.108 | available | 119 | SS 35/10 kV Voronok | 2,5+3,2 | 0.0437 | 1.5607 | 0 | 0 | 1.5607 | 0 | 2.625 | 1.0643 | 1.0643 | available
120 | SS 35/10 kV Gordeevka | 4+4 | 2.201 | 0 | 0 | 2.201 | 0 | 4.2 | 1.999 | 1.999 | available | 120 | SS 35/10 kV Gordeevka | 4+4 | 0.1411 | 2.3421 | 0 | 0 | 2.3421 | 0 | 4.2 | 1.8579 | 1.8579 | available
121 | SS 35/10 kV Gridenki | 2,5+3,2 | 1.167 | 0 | 0 | 1.167 | 0 | 2.625 | 1.458 | 1.458 | available | 121 | SS 35/10 kV Gridenki | 2,5+3,2 | 0.1208 | 1.2878 | 0 | 0 | 1.2878 | 0 | 2.625 | 1.3372 | 1.3372 | available
122 | SS 35/10 kV Zavodskaya | 4+2,5 | 1.428 | 0 | 0 | 1.428 | 0 | 2.625 | 1.197 | 1.197 | available | 122 | SS 35/10 kV Zavodskaya | 4+2,5 | 0.034 | 1.462 | 0 | 0 | 1.462 | 0 | 2.625 | 1.163 | 1.163 | available
123 | SS 35/10 kV Istopki | 1,6+1,6 | 1.251 | 0 | 0 | 1.251 | 0 | 1.68 | 0.429 | 0.429 | available | 123 | SS 35/10 kV Istopki | 1,6+1,6 | 0.0318 | 1.2828 | 0 | 0 | 1.2828 | 0 | 1.68 | 0.3972 | 0.3972 | available
124 | SS 35/10 kV Katashin | 1,6+1,6 | 1.017 | 0 | 0 | 1.017 | 0 | 1.68 | 0.663 | 0.663 | available | 124 | SS 35/10 kV Katashin | 1,6+1,6 | 0.0261 | 1.0431 | 0 | 0 | 1.0431 | 0 | 1.68 | 0.6369 | 0.6369 | available
125 | SS 35/10 kV Kivay | 2,5+2,5 | 1.33 | 0 | 0 | 1.33 | 0 | 2.625 | 1.295 | 1.295 | available | 125 | SS 35/10 kV Kivay | 2,5+2,5 | 0.0748 | 1.4048 | 0 | 0 | 1.4048 | 0 | 2.625 | 1.2202 | 1.2202 | available
126 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.806 | 0 | 0 | 0.806 | 0 | 1.68 | 0.874 | 0.874 | available | 126 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.0093 | 0.8153 | 0 | 0 | 0.8153 | 0 | 1.68 | 0.8647 | 0.8647 | available
127 | SS 35/10 kV Logovatoe | 2,5+1,6 | 0.939 | 0 | 0 | 0.939 | 0 | 1.68 | 0.741 | 0.741 | available | 127 | SS 35/10 kV Logovatoe | 2,5+1,6 | 0.0107 | 0.9497 | 0 | 0 | 0.9497 | 0 | 1.68 | 0.7303 | 0.7303 | available
128 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.268 | 0 | 0 | 0.268 | 0 | 2.625 | 2.357 | 2.357 | available | 128 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.0282 | 0.2962 | 0 | 0 | 0.2962 | 0 | 2.625 | 2.3288 | 2.3288 | available
129 | SS 35/10 kV Mglinskaya | 4+4 | 3.559 | 0 | 0 | 3.559 | 0 | 4.2 | 0.641 | 0.641 | available | 129 | SS 35/10 kV Mglinskaya | 4+4 | 0.0319 | 3.5909 | 0 | 0 | 3.5909 | 0 | 4.2 | 0.6091 | 0.6091 | available
130 | SS 35/10 kV Mishkovka | 2,5+1,6 | 0.531 | 0 | 0 | 0.531 | 0 | 1.68 | 1.149 | 1.149 | available | 130 | SS 35/10 kV Mishkovka | 2,5+1,6 | 0.0247 | 0.5557 | 0 | 0 | 0.5557 | 0 | 1.68 | 1.1243 | 1.1243 | available
131 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.563 | 0 | 0 | 0.563 | 0 | 2.625 | 2.062 | 2.062 | available | 131 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.008 | 0.571 | 0 | 0 | 0.571 | 0 | 2.625 | 2.054 | 2.054 | available
132 | SS 35/10 kV Putevaya | 6,3+6,3 | 5.093 | 0 | 0 | 5.093 | 0 | 6.615 | 1.522 | 1.522 | available | 132 | SS 35/10 kV Putevaya | 6,3+6,3 | 0.072 | 5.165 | 0 | 0 | 5.165 | 0 | 6.615 | 1.45 | 1.45 | available
133 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 0.797 | 0 | 0 | 0.797 | 0 | 2.625 | 1.828 | 1.828 | available | 133 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 0.1105 | 0.9075 | 0 | 0 | 0.9075 | 0 | 2.625 | 1.7175 | 1.7175 | available
134 | SS 35/10 kV Slava | 2,5+1,6 | 1.271 | 0 | 0 | 1.271 | 0 | 1.68 | 0.409 | 0.409 | available | 134 | SS 35/10 kV Slava | 2,5+1,6 | 0.1133 | 1.3843 | 0 | 0 | 1.3843 | 0 | 1.68 | 0.2957 | 0.2957 | available
135 | SS 35/10 kV Smolevichi | 6,3+6,3 | 2.692 | 0 | 0 | 2.692 | 0 | 6.615 | 3.923 | 3.923 | available | 135 | SS 35/10 kV Smolevichi | 6,3+6,3 | 0.2843 | 2.9763 | 0 | 0 | 2.9763 | 0 | 6.615 | 3.6387 | 3.6387 | available
136 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.387 | 0 | 0 | 0.387 | 0 | 1.68 | 1.293 | 1.293 | available | 136 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.0158 | 0.4028 | 0 | 0 | 0.4028 | 0 | 1.68 | 1.2772 | 1.2772 | available
137 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 137 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.0297 | 0.4297 | 0 | 0 | 0.4297 | 0 | 2.625 | 2.1953 | 2.1953 | available
138 | SS 35/6 kV Tembr | 4+4+3,2 | 6.43 | 0 | 0 | 6.43 | 0 | 7.56 | 1.13 | 1.13 | available | 138 | SS 35/6 kV Tembr | 4+4+3,2 | 0.1309 | 6.5609 | 0 | 0 | 6.5609 | 0 | 7.56 | 0.9991 | 0.9991 | available
139 | SS 35/10 kV Churovichi | 2,5+4 | 0.726 | 0 | 0 | 0.726 | 0 | 2.625 | 1.899 | 1.899 | available | 139 | SS 35/10 kV Churovichi | 2,5+4 | 0.0822 | 0.8082 | 0 | 0 | 0.8082 | 0 | 2.625 | 1.8168 | 1.8168 | available
140 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 0.999 | 0 | 0 | 0.999 | 0 | 2.625 | 1.626 | 1.626 | available | 140 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 0.0745 | 1.0735 | 0 | 0 | 1.0735 | 0 | 2.625 | 1.5515 | 1.5515 | available
| Total: | 2302.5 | 756.754 | [8 empty] | 2: Total:; 3: 2302.5; 4: 94.9591; 5: 851.7131
| deficit | [8 empty] | -38.503 |  | 2: deficit; Min 12: -60.5565
| proficit | [8 empty] | 416.533 |  | 2: proficit; Min 12: 390.6952