## Kursk
Transmission capacity of supply centres of IDGC of Center - Kurskenergo following the winter peak load measurements in
2011
| Calculation formula of transmission capacity of supply centres of IDGC of Center - Kurskenergo | [11 empty] | Calculation formula of transmission capacity of supply centres of IDGC of Center - Kurskenergo for January 2012
[9 empty] | table 1 | [12 empty] | table 2
Item # | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note | cosφ
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 2.32 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.98 | 0.53 | available | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.034365 | 2.3544 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.9456 | 0.51235 | available | 0.95
| Nom. capacity MV, MVA | 6.3 | 1.77 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 0.53 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.017647 | 1.7876 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 0.51235
| Nom. capacity MV, MVA | 6.3 | 0.55 | 4 | 1 day and night | 4 | 0 | 4 | 3.45 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.015 | 0.565 | 4 | 1 day and night | 4 | 0 | 4 | 3.435
2 | SS 110/10 Beketovo | 1*6,3 | 0.44 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.71 | 1.71 | available | 2 | SS 110/10 Beketovo | 1*6,3 | 2.9548 | 3.3948 | 2.15 | 120 | 2.15 | 0 | 2.15 | -1.2448 | -1.2448 | unavailable | 0.84
3 | SS 110/35/10 Besedino | 1*6,3 | 2.85 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.95 | 1.04 | available | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.44734 | 3.2973 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.5027 | 0.728 | available | 0.85
| Nom. capacity MV, MVA | 6.3 | 0.59 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.91 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.068235 | 0.65824 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.8418
| Nom. capacity LV, MVA | 6.3 | 2.26 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.04 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.312 | 2.572 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.728
4 | SS 110/10 Voskhod | 1*10,0 | 0.8 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.7 | 1.7 | available | 4 | SS 110/10 Voskhod | 1*10,0 | 0.16905 | 0.96905 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.531 | 1.531 | available | 0.84
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.8 | 6 | 1 day and night | 6 | 0 | 6 | 5.2 | 1.5 | available | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.019277 | 0.81928 | 6 | 1 day and night | 6 | 0 | 6 | 5.1807 | 1.484 | available | 0.83
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.8 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.5 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.016 | 0.816 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.484
6 | SS 110/10 Zabelye | 1*2,5 | 0.31 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.84 | 1.84 | available | 6 | SS 110/10 Zabelye | 1*2,5 | 0.01039 | 0.32039 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8296 | 1.8296 | available | 0.77
7 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.27 | 0.27 | available | 7 | SS 110/10 Ivnitsa | 1*6,3 | 0 | 0.4 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.27 | 0.27 | available | 0.85
8 | SS 110/35/10 Lachinovo | 1*10,0 | 0.98 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 4.15 | 0.93 | available | 8 | SS 110/35/10 Lachinovo | 1*10,0 | 0.03128 | 1.0113 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 4.1187 | 0.916 | available | 0.85
| Nom. capacity MV, MVA | 10 | 0.38 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 3.22 |  |  |  | Nom. capacity MV, MVA | 10 | 0.012588 | 0.39259 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 3.2074
| Nom. capacity LV, MVA | 10 | 0.6 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.93 |  |  |  | Nom. capacity LV, MVA | 10 | 0.014 | 0.614 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.916
9 | SS 110/10 Malaya Loknya | 1*10,0 | 1.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.2 | 0.2 | available | 9 | SS 110/10 Malaya Loknya | 1*10,0 | 0.011905 | 1.2119 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.1881 | 0.1881 | available | 0.84
10 | SS 110/35/10 Maritsa | 1*2,5 | 1.6 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.32 | 0.32 | available | 10 | SS 110/35/10 Maritsa | 1*6,3 | 0.0020408 | 1.602 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.31796 | 0.31796 | available | 0.98
11 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.3 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.1 | 1.1 | available | 11 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.011765 | 0.31176 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.0882 | 1.0882 | available | 0.85
12 | SS 110/6 Teplichnaya | 2х25 | 3.1 | 6.64 | 1 day and night | -3.54 | 0 | 26.25 | 29.79 | 29.79 | available | 12 | SS 110/6 Teplichnaya | 2х25 | 9.7711 | 12.8711 | 6.64 | 0 | 6.2311 | 0 | 26.25 | 20.0189 | 20.0189 | available | 0.9
13 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.65 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 4.85 | 0.7 | available | 13 | SS 110/35/10 Troitskaya | 1 х 10,0 | 0.86381 | 3.5138 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 3.9862 | 0.674 | available | 0.85
| Nom. capacity MV, MVA | 10 | 2.25 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 4.15 |  |  |  | Nom. capacity MV, MVA | 10 | 0.70824 | 2.9582 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 3.4418
| Nom. capacity LV, MVA | 10 | 0.4 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.7 |  |  |  | Nom. capacity LV, MVA | 10 | 0.026 | 0.426 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.674
14 | SS 35/10 Avtodor | 1 х 2,5 | 0.34 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.46 | 0.46 | available | 14 | SS 35/10 Avtodor | 1 х 2,5 | 0.017647 | 0.35765 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.44235 | 0.44235 | available | 0.85
15 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.45 | 0.45 | available | 15 | SS 35/10 Agronom | 1 х 1,8 | 0.21505 | 0.71505 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.23495 | 0.23495 | available | 0.93
16 | SS 35/10 Akimovka | 1 х 2,5 | 0.3 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.38 | 0.38 | available | 16 | SS 35/10 Akimovka | 1 х 2,5 | 0.0068966 | 0.3069 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.3731 | 0.3731 | available | 0.87
17 | SS 35/10 Alekseevka | 1 х 2,5 | 0.2 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.23 | 1.23 | available | 17 | SS 35/10 Alekseevka | 1 х 2,5 | 0.017442 | 0.21744 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.2126 | 1.2126 | available | 0.86
18 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.61 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.73 | 0.73 | available | 18 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.015957 | 0.62596 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.71404 | 0.71404 | available | 0.94
19 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.74 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.22 | 0.22 | available | 19 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0 | 0.74 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.22 | 0.22 | available | 0.88
20 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.2 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.63 | 2.63 | available | 20 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.55529 | 0.75529 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.0747 | 2.0747 | available | 0.85
21 | SS 35/10 Banishchi | 1 х 1,6 | 0.43 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.21 | 0.21 | available | 21 | SS 35/10 Banishchi | 1 х 1,6 | 0.069149 | 0.49915 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.14085 | 0.14085 | available | 0.94
22 | SS 35/10 Baranovo | 1 х 4,0 | 0.15 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.28 | 1.28 | available | 22 | SS 35/10 Baranovo | 1 х 4,0 | 0.66203 | 0.81203 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.61797 | 0.61797 | available | 0.79
23 | SS 35/10 Belgorodka | 1 х 2,5 | 0.27 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.88 | 1.88 | available | 23 | SS 35/10 Belgorodka | 1 х 2,5 | 0.065217 | 0.33522 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8148 | 1.8148 | available | 0.69
24 | SS 35/10 Belitsa | 1 х 4,0 | 0.55 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.21 | 1.21 | available | 24 | SS 35/10 Belitsa | 1 х 4,0 | 0.094681 | 0.64468 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.1153 | 1.1153 | available | 0.94
25 | SS 35/10 Biryukovka | 1х1,6 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available | 25 | SS 35/10 Biryukovka | 1х1,6 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available | 0.85
26 | SS 35/10 Bobrovka | 1 х 1,6 | 0.22 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.45 | 0.45 | available | 26 | SS 35/10 Bobrovka | 1 х 1,6 | 0.016471 | 0.23647 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.43353 | 0.43353 | available | 0.85
27 | SS 35/10 Bobrovo | 1 х 2,5 | 0.49 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.27 | 0.27 | available | 27 | SS 35/10 Bobrovo | 1 х 2,5 | 0.02809 | 0.51809 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.24191 | 0.24191 | available | 0.89
28 | SS 35/10 Budki | 1 х 1,0 | 0.24 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.5 | 0.5 | available | 28 | SS 35/10 Budki | 1 х 1,0 |  | 0.24 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.5 | 0.5 | available | 0.89
29 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.52 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.08 | 1.08 | available | 29 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.018824 | 0.53882 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.0612 | 1.0612 | available | 0.85
30 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.37 | 1 | 1 day and night | 1 | 0 | 1 | 0.63 | 0.63 | available | 30 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.014737 | 0.38474 | 1 | 1 day and night | 1 | 0 | 1 | 0.61526 | 0.61526 | available | 0.95
31 | SS 35/10 Burtsevka | 1 х 1,6 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | available | 31 | SS 35/10 Burtsevka | 1 х 1,6 | 0 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | available | 0.8
32 | SS 35/10 Bykovo | 1х4,0 | 0.51 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.92 | 0.92 | available | 32 | SS 35/10 Bykovo | 1х4 | 4.4793 | 4.9893 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | -3.5593 | -3.5593 | unavailable | 0.82
33 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.13 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.02 | 2.02 | available | 33 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.13 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.02 | 2.02 | available | 0.85
34 | SS 35/10 Vanino | 1 х 2,5 | 0.38 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.42 | 0.42 | available | 34 | SS 35/10 Vanino | 1 х 2,5 | 0.021176 | 0.40118 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.39882 | 0.39882 | available | 0.85
35 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.5 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.55 | 0.55 | available | 35 | SS 35/10 Vasilyevka | 1 х 2,5 | 1.109 | 1.609 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | -0.559 | -0.559 | unavailable | 0.95
36 | SS 35/10 Water storage | 1 х 4,0 | 1.35 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | 1.37 | 1.37 | available | 36 | SS 35/10 Water storage | 1 х 4,0 | 8.46 | 9.81 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | -7.09 | -7.09 | unavailable | 0.85
37 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available | 37 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available | 0.93
38 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.16 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.74 | 0.74 | available | 38 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.0023529 | 0.16235 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.73765 | 0.73765 | available | 0.85
39 | SS 35/10 Voronok | 1 х 4,0 | 0.68 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.42 | 1.42 | available | 39 | SS 35/10 Voronok | 1 х 4,0 | 0.4978 | 1.1778 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 0.9222 | 0.9222 | available | 0.91
40 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.27 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.88 | 1.88 | available | 40 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.017647 | 0.28765 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8624 | 1.8624 | available | 0.85
41 | SS 35/10 Gakhovo | 1 х 2,5 | 0.22 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.58 | 1.58 | available | 41 | SS 35/10 Gakhovo | 1 х 2,5 | 0.0082353 | 0.22824 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.5718 | 1.5718 | available | 0.85
42 | SS 35/10 Generalshino | 1 х 2,5 | 0.13 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.37 | 1.37 | available | 42 | SS 35/10 Generalshino | 1 х 2,5 | 0.16235 | 0.29235 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.2076 | 1.2076 | available | 0.85
43 | SS 35/10 Glazovo | 1 х 2,5 | 0.9 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.6 | 0.6 | available | 43 | SS 35/10 Glazovo | 1 х 2,5 | 0 | 0.9 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.6 | 0.6 | available | 0.95
44 | SS 35/10 Glebovo | 1 х 2,5 | 0.09 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.31 | 1.31 | available | 44 | SS 35/10 Glebovo | 1 х 2,5 | 0.058824 | 0.14882 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2512 | 1.2512 | available | 0.85
45 | SS 35/10 Gordeevka | 1 х 1,6 | 0.18 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.52 | 0.52 | available | 45 | SS 35/10 Gordeevka | 1 х 1,6 | 0.014286 | 0.19429 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.50571 | 0.50571 | available | 0.98
46 | SS 35/10 Gorodensk | 1 х 1,6 | 0.61 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.15 | 0.15 | available | 46 | SS 35/10 Gorodensk | 1 х 1,6 | 0.016667 | 0.62667 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.13333 | 0.13333 | available | 0.9
47 | SS 35/10 Goryainovo | 1 х 2,5 | 0.5 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.6 | 0.6 | available | 47 | SS 35/10 Goryainovo | 1 х 2,5 | 0.016471 | 0.51647 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.58353 | 0.58353 | available | 0.85
48 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.33 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1 | 1.1 | available | 48 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.012588 | 0.34259 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0874 | 1.0874 | available | 0.85
49 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.22 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.21 | 1.21 | available | 49 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.046667 | 0.26667 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1633 | 1.1633 | available | 0.75
50 | SS 35/10 Grinyovka | 1 х 2,5 | 0.22 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.63 | 2.63 | available | 50 | SS 35/10 Grinyovka | 1 х 2,5 | 0.015294 | 0.23529 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.6147 | 2.6147 | available | 0.85
51 | SS 35/10 Gustomoy | 1 х 1,6 | 0.18 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.76 | 0.76 | available | 51 | SS 35/10 Gustomoy | 1 х 1,6 | 0.020408 | 0.20041 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.73959 | 0.73959 | available | 0.98
52 | SS 35/10 Daryino | 1 х 2,5 | 0.4 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4 | 1.4 | available | 52 | SS 35/10 Daryino | 1 х 2,5 | 0.021176 | 0.42118 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.3788 | 1.3788 | available | 0.85
53 | SS 35/10 Demyakino | 1 х 2,5 | 0.56 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.24 | 0.24 | available | 53 | SS 35/10 Demyakino | 1 х 2,5 | 0.052941 | 0.61294 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.18706 | 0.18706 | available | 0.85
54 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.23 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.84 | 0.84 | available | 54 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.022353 | 0.25235 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.81765 | 0.81765 | available | 0.85
55 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.26 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.59 | 0.59 | available | 55 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.030588 | 0.29059 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.55941 | 0.55941 | available | 0.85
56 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.36 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.79 | 1.79 | available | 56 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.68652 | 1.0465 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.1035 | 1.1035 | available | 0.89
57 | SS 35/10 Zvannoe | 1 х 2,5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 57 | SS 35/10 Zvannoe | 1 х 2,5 | 0.033708 | 0.58371 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.25629 | 0.25629 | available | 0.89
58 | SS 35/10 Znamenka | 1 х 1,8 | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | available | 58 | SS 35/10 Znamenka | 1 х 1,8 | 0.013415 | 1.0234 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.1266 | 1.1266 | available | 0.82
59 | SS 35/10 Iskra | 1 х 2,5 | 0.21 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.37 | 0.37 | available | 59 | SS 35/10 Iskra | 1 х 2,5 | 0.068235 | 0.27824 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.30176 | 0.30176 | available | 0.85
60 | SS 35/10 Kazanka | 1 х 4,0 | 0.49 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.31 | 0.31 | available | 60 | SS 35/10 Kazanka | 1 х 4,0 | 0.010588 | 0.50059 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.29941 | 0.29941 | available | 0.85
61 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.24 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.56 | 1.56 | available | 61 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.070588 | 0.31059 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4894 | 1.4894 | available | 0.85
62 | SS 35/10 Karyzh | 1 х 1,6 | 0.31 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33 | 0.33 | available | 62 | SS 35/10 Karyzh | 1 х 1,6 | 0.22921 | 0.53921 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.10079 | 0.10079 | available | 0.89
63 | SS 35/10 Kitaevka | 1 х 1,6 | 0.39 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.35 | 0.35 | available | 63 | SS 35/10 Kitaevka | 1 х 1,6 | 0 | 0.39 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.35 | 0.35 | available | 0.85
64 | SS 35/10 Kobylki | 1 х 2,5 | 0.61 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.92 | 0.92 | available | 64 | SS 35/10 Kobylki | 1 х 2,5 | 0.1427 | 0.7527 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.7773 | 0.7773 | available | 0.89
65 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 65 | SS 35/10 Kolontaevka | 1 х 2,5 | 0 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 0.98
66 | SS 35/10 Kondratovka | 1 х 1,8 | 0.55 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.87 | 0.87 | available | 66 | SS 35/10 Kondratovka | 1 х 1,8 | 0.025532 | 0.57553 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.84447 | 0.84447 | available | 0.94
67 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.45 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.31 | 0.31 | available | 67 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.0078652 | 0.45787 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.30213 | 0.30213 | available | 0.89
68 | SS 35/10 Lezhenki | 1 х 2,5 | 0.14 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.29 | 1.29 | available | 68 | SS 35/10 Lezhenki | 1 х 2,5 | 0 | 0.14 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.29 | 1.29 | available | 0.76
69 | SS 35/10 Leninskaya | 1 х 1,8 | 0.36 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.47 | 0.47 | available | 69 | SS 35/10 Leninskaya | 1 х 1,8 | 0.042353 | 0.40235 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.42765 | 0.42765 | available | 0.85
70 | SS 35/10 Lobazovka | 1 х 2,5 | 0.68 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.42 | 0.42 | available | 70 | SS 35/10 Lobazovka | 1 х 2,5 | 0.017647 | 0.69765 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.40235 | 0.40235 | available | 0.85
71 | SS 35/10 Lugovka | 1 х 1,6 | 0.5 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.79 | 0.79 | available | 71 | SS 35/10 Lugovka | 1 х 1,6 | 0.040449 | 0.54045 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.74955 | 0.74955 | available | 0.89
72 | SS 35/10 Lyubava | 1 х 6,3 | 0.37 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.78 | 0.78 | available | 72 | SS 35/10 Lyubava | 1 х 6,3 | 0.040426 | 0.41043 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.73957 | 0.73957 | available | 0.94
73 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.96 | 0.96 | available | 73 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.0058824 | 0.0058824 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.95412 | 0.95412 | available | 0.85
74 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 74 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.13293 | 0.73293 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.36707 | 0.36707 | available | 0.82
75 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.8 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.48 | 0.48 | available | 75 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0 | 0.8 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.48 | 0.48 | available | 0.89
76 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.3 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.89 | 0.89 | available | 76 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.018987 | 0.31899 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.87101 | 0.87101 | available | 0.79
77 | SS 35/10 Markovo | 1 х 2,5 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | available | 77 | SS 35/10 Markovo | 1 х 2,5 | 0 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | available | 0.89
78 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.43 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 0.9 | 0.9 | available | 78 | SS 35/10 Marmyzhi | 1 х 2,5 | 0 | 0.43 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 0.9 | 0.9 | available | 0.94
79 | SS 35/10 Melovoe | 1 х 4,0 | 0.7 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.45 | 1.45 | available | 79 | SS 35/10 Melovoe | 1 х 4,0 | 0.024444 | 0.72444 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.4256 | 1.4256 | available | 0.9
80 | SS 35/10 Mokva | 1 х 4,0 | 0.65 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.5 | 1.5 | available | 80 | SS 35/10 Mokva | 1 х 4,0 | 0.2 | 0.85 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.3 | 1.3 | available | 0.85
81 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 81 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.035789 | 0.63579 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.46421 | 0.46421 | available | 0.95
82 | SS 35/10 Molotychi | 1 х 2,5 | 0.05 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.85 | 0.85 | available | 82 | SS 35/10 Molotychi | 1 х 2,5 | 0 | 0.05 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.85 | 0.85 | available | 0.85
83 | SS 35/10 Mochaki | 1 х 2,5 | 0.01 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.06 | 1.06 | available | 83 | SS 35/10 Mochaki | 1 х 2,5 | 0.0023529 | 0.012353 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.0576 | 1.0576 | available | 0.85
84 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.1 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.2 | 4.2 | available | 84 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0 | 0.1 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.2 | 4.2 | available | 0.87
85 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.42 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.73 | 1.73 | available | 85 | SS 35/10 N. Gurovo | 1 х 4,0 | 0 | 0.42 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.73 | 1.73 | available | 0.76
86 | SS 35/10 Nadeyka | 1 х 2,5 | 0.07 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.33 | 1.33 | available | 86 | SS 35/10 Nadeyka | 1 х 2,5 | 0 | 0.07 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.33 | 1.33 | available | 0.85
87 | SS 35/10 Niva | 1 х 2,5 | 0.4 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.16 | 1.16 | available | 87 | SS 35/10 Niva | 1 х 2,5 | 0.17647 | 0.57647 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 0.98353 | 0.98353 | available | 0.85
88 | SS 35/10 Olgovka | 1 х 2,5 | 0.43 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.54 | 0.54 | available | 88 | SS 35/10 Olgovka | 1 х 2,5 | 0 | 0.43 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.54 | 0.54 | available | 0.98
89 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.4 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.24 | 0.24 | available | 89 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.021176 | 0.42118 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.21882 | 0.21882 | available | 0.85
90 | SS 35/10 Orositelnaya | 1 х 4,0 | 1.96 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 1.01 | 1.01 | available | 90 | SS 35/10 Orositelnaya | 1 х 4,0 | 3.2306 | 5.1906 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | -2.2206 | -2.2206 | unavailable | 0.85
91 | SS 35/10 Peny-2 | 1 х 2,5 | 0.6 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.72 | 1.72 | available | 91 | SS 35/10 Peny-2 | 1 х 2,5 | 0.057143 | 0.65714 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.6629 | 1.6629 | available | 0.77
92 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.13 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.27 | 1.27 | available | 92 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.13 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.27 | 1.27 | available | 0.85
93 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.26 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.14 | 1.14 | available | 93 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0 | 0.26 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.14 | 1.14 | available | 0.85
94 | SS 35/10 Petrovo | 1 х 6,3 | 0.46 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.69 | 1.69 | available | 94 | SS 35/10 Petrovo | 1 х 6,3 | 0.21765 | 0.67765 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.4724 | 1.4724 | available | 0.92
95 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.02 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.72 | 0.72 | available | 95 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.011765 | 0.031765 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.70824 | 0.70824 | available | 0.85
96 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.24 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.91 | 1.91 | available | 96 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0 | 0.24 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.91 | 1.91 | available | 0.83
97 | SS 35/10 Prilepy | 1 х 1,6 | 0.38 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.77 | 1.77 | available | 97 | SS 35/10 Prilepy | 1 х 1,6 | 0.0094118 | 0.38941 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.7606 | 1.7606 | available | 0.85
98 | SS 35/10 Pristen | 1 х 4,0 | 2.2 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.1 | 1.1 | available | 98 | SS 35/10 Pristen | 1 х 4 | 8.6824 | 10.8824 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | -7.5824 | -7.5824 | unavailable | 0.85
99 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.74 | 0.74 | available | 99 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.10471 | 0.10471 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.63529 | 0.63529 | available | 0.85
100 | SS 35/10 Reut | 1 х 2,5 | 0.04 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.06 | 1.06 | available | 100 | SS 35/10 Reut | 1 х 2,5 | 0.035294 | 0.075294 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.0247 | 1.0247 | available | 0.85
101 | SS 35/10 Rovenka | 1 х 1,6 | 0.16 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.44 | 1.44 | available | 101 | SS 35/10 Rovenka | 1 х 1,6 | 0.022727 | 0.18273 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.4173 | 1.4173 | available | 0.88
102 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.09 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.61 | 0.61 | available | 102 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0 | 0.09 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.61 | 0.61 | available | 0.85
103 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.35 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.95 | 1.95 | available | 103 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.43294 | 0.78294 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.5171 | 1.5171 | available | 0.85
104 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.4 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.91 | 0.91 | available | 104 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.46292 | 0.86292 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.44708 | 0.44708 | available | 0.89
105 | SS 35/10 Rusanovo | 1 х 1,8 | 0.29 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.14 | 1.14 | available | 105 | SS 35/10 Rusanovo | 1 х 1,8 | 0 | 0.29 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.14 | 1.14 | available | 0.85
106 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.32 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.62 | 0.62 | available | 106 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.070588 | 0.39059 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.54941 | 0.54941 | available | 0.85
107 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.61 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.54 | 0.54 | available | 107 | SS 35/10 Ryazanovo | 1 х 1,6 | 0 | 0.61 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.54 | 0.54 | available | 0.85
108 | SS 35/10 Sazanovka | 1 х 2,5 | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | available | 108 | SS 35/10 Sazanovka | 1 х 2,5 | 0.0035294 | 0.30353 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.94647 | 0.94647 | available | 0.85
109 | SS 35/10 Sergievka | 1 х 2,5 | 0.53 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.17 | 2.17 | available | 109 | SS 35/10 Sergievka | 1 х 2,5 | 0.025882 | 0.55588 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.1441 | 2.1441 | available | 0.85
110 | SS 35/10 Sokolye | 1 х 2,5 | 0.3 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.13 | 1.13 | available | 110 | SS 35/10 Sokolye | 1 х 2,5 | 0.017647 | 0.31765 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1124 | 1.1124 | available | 0.85
111 | SS 35/10 Solntsevo | 1 х 2,5 | 0.87 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.89 | 0.89 | available | 111 | SS 35/10 Solntsevo | 1 х 2,5 | 0.042353 | 0.91235 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.84765 | 0.84765 | available | 0.85
112 | SS 35/10 Spasskoe | 1 х 1,6 | 0.33 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.77 | 0.77 | available | 112 | SS 35/10 Spasskoe | 1 х 1,6 | 0 | 0.33 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.77 | 0.77 | available | 0.85
113 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | available | 113 | SS 35/10 Sr. Olshanka | 1 х 6,3 | 1.8941 | 2.0941 | 2.2 | 1 day and night | 2.2 | 0 | 2.2 | 0.10588 | 0.10588 | available | 0.85
114 | SS 35/10 Streletskaya | 1 х 2,5 | 0.46 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.84 | 0.84 | available | 114 | SS 35/10 Streletskaya | 1 х 2,5 | 0.066279 | 0.52628 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.77372 | 0.77372 | available | 0.86
115 | SS 35/10 Subbotino | 1 х 2,5 | 0.6 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.74 | 0.74 | available | 115 | SS 35/10 Subbotino | 1 х 2,5 | 0.002381 | 0.60238 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.73762 | 0.73762 | available | 0.84
116 | SS 35/10 Sukhaya | 1 х 1,6 | 0.31 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.4 | 0.4 | available | 116 | SS 35/10 Sukhaya | 1 х 1,6 | 0 | 0.31 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.4 | 0.4 | available | 0.91
117 | SS 35/10 Telmana | 1 х 2,5 | 0.49 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.66 | 0.66 | available | 117 | SS 35/10 Telmana | 1 х 2,5 | 0.01875 | 0.50875 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.64125 | 0.64125 | available | 0.96
118 | SS 35/10 Terebuzh | 1 х 2,5 | 0.35 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.08 | 1.08 | available | 118 | SS 35/10 Terebuzh | 1 х 2,5 | 0.036735 | 0.38673 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0433 | 1.0433 | available | 0.98
119 | SS 35/10 Fateevka | 1 х 2,5 | 0.07 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.63 | 0.63 | available | 119 | SS 35/10 Fateevka | 1 х 2,5 | 0.0094118 | 0.079412 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.62059 | 0.62059 | available | 0.85
120 | SS 35/10 Fentisovo | 1 х 1,6 | 0.29 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.43 | 1.43 | available | 120 | SS 35/10 Fentisovo | 1 х 1,6 | 0.0047059 | 0.29471 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.4253 | 1.4253 | available | 0.85
121 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.09 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.01 | 1.01 | available | 121 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0 | 0.09 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.01 | 1.01 | available | 0.85
122 | SS 35/10 Chemerki | 1 х 1,6 | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available | 122 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available | 0.85
123 | SS 35/10 Chizhovka | 1 х 1,6 | 0.3 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.13 | 1.13 | available | 123 | SS 35/10 Chizhovka | 1 х 1,6 | 0.052941 | 0.35294 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0771 | 1.0771 | available | 0.85
124 | SS 35/10 Shatilovka | 1 х 2,5 | 0.11 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.32 | 1.32 | available | 124 | SS 35/10 Shatilovka | 1 х 2,5 | 0 | 0.11 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.32 | 1.32 | available | 0.81
125 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.74 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.73 | 0.73 | available | 125 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.04 | 0.78 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.69 | 0.69 | available | 0.85
126 | SS 35/10 Shuklino | 1 х 2,5 | 0.02 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.83 | 0.83 | available | 126 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.02 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.83 | 0.83 | available | 0.85
127 | SS 35/10 Elevator | 1х6,3 | 0.19 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.41 | 0.41 | available | 127 | SS 35/10 Elevator | 1х6,3 | 0 | 0.19 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.41 | 0.41 | available | 0.85
128 | SS 35/10 Yankovo | 1 х 1,6 | 0.3 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.34 | 0.34 | available | 128 | SS 35/10 Yankovo | 1 х 1,6 | 0.0094737 | 0.30947 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33053 | 0.33053 | available | 0.95
129 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.67 | 1.67 | available | 129 | SS 35/10 Yasenki | 1 х 2,5 | 4.2928 | 4.7728 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -2.6228 | -2.6228 | unavailable | 0.83
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 11.06 | 0 | 0 | 11.06 | 0 | 26.25 | 15.19 | 15.19 | available | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 11.06 | 0 | 0 | 11.06 | 0 | 26.25 | 15.19 | 15.19 | available | 0.89
2 | SS 110/10 ARZ | 6,3+10,0 | 2.6 | 0.9 | 45 | 1.7 | 0 | 6.615 | 4.915 | 4.915 | available | 2 | SS 110/10 ARZ | 6,3+10,0 | 0.019048 | 2.619 | 0.9 | 45 | 1.719 | 0 | 6.615 | 4.896 | 4.896 | available | 0.84
3 | SS 110/35/10 Atomgrad | 2*25 | 11.35 | 20.2 | 120 | -8.85 | 0 | 26.25 | 35.1 | 27.95 | available | 3 | SS 110/35/10 Atomgrad | 2*25 | 1.0343 | 12.3843 | 20.2 | 120 | -7.8157 | 0 | 26.25 | 34.0657 | 27.552 | available | 0.85
| Nom. capacity MV, MVA | 25 | 3.45 | 10.6 | 120 | -7.15 | 0 | 26.25 | 33.4 |  |  |  | Nom. capacity MV, MVA | 25 | 0.48118 | 3.9312 | 10.6 | 120 | -6.6688 | 0 | 26.25 | 32.9188
| Nom. capacity lV, MVA | 25 | 7.9 | 9.6 | 120 | -1.7 | 0 | 26.25 | 27.95 |  |  |  | Nom. capacity lV, MVA | 25 | 0.398 | 8.298 | 9.6 | 120 | -1.302 | 0 | 26.25 | 27.552
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.9 | 0.6 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.315 | available | 4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.082353 | 0.98235 | 0.6 | 120 | 0.38235 | 0 | 6.615 | 6.2326 | 6.2326 | available | 0.85
5 | SS 110/35/10 Basovo | 5,6+10,0 | 1.28 | 6.19 | 15 | -4.91 | 0 | 5.88 | 10.79 | 5.29 | available | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.79828 | 2.0783 | 6.19 | 15 | -4.1117 | 0 | 5.88 | 9.9917 | 5.29 | available | 0.86
| Nom. capacity MV, MVA | 5,6+10,0 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38 |  |  |  | Nom. capacity MV, MVA | 5,6+10,0 | 0.68652 | 1.1865 | 6 |  | -4.8135 | 0 | 5.88 | 10.6935
| Nom. capacity LV, MVA | 5,6+10,0 | 0.78 | 0.19 | 120 | 0.59 | 0 | 5.88 | 5.29 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0 | 0.78 | 0.19 | 120 | 0.59 | 0 | 5.88 | 5.29
6 | SS 110/35/10 Belaya | 2*16,0 | 7.3 | 12 | 120 | -4.7 | 0 | 16.8 | 21.5 | 13.6 | available | 6 | SS 110/35/10 Belaya | 2*16,0 | 2.0937 | 9.3937 | 12 | 120 | -2.6063 | 0 | 16.8 | 19.4063 | 13.3869 | available | 0.77
| Nom. capacity MV, MVA | 16 | 3.2 | 0 |  | 3.2 | 0 | 16.8 | 13.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.21315 | 3.4131 | 0 |  | 3.4131 | 0 | 16.8 | 13.3869
| Nom. capacity LV, MVA | 16 | 4.1 | 12 | 120 | -7.9 | 0 | 16.8 | 24.7 |  |  |  | Nom. capacity LV, MVA | 16 | 1.399 | 5.499 | 12 | 120 | -6.501 | 0 | 16.8 | 23.301
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.6 | 1.3 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.015 | available | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 4.5136 | 6.1136 | 1.3 | 120 | 4.8136 | 0 | 6.615 | 1.8014 | 1.8014 | available | 0.89
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity MV, MVA | 6.3 | 1.8941 | 2.4941 | 0 |  | 2.4941 | 0 | 6.615 | 4.1209
| Nom. capacity LV, MVA | 6.3 | 1 | 1.3 | 120 | -0.3 | 0 | 6.615 | 6.915 |  |  |  | Nom. capacity LV, MVA | 6.3 | 2.123 | 3.123 | 1.3 | 120 | 1.823 | 0 | 6.615 | 4.792
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 1.41 | 1.17 | 45 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.09375 | 1.5037 | 1.17 | 45 | 0.33375 | 0 | 2.625 | 2.2912 | 2.2912 | available | 0.96
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 35.14 | 16.8 | 0 | 18.34 | 0 | 84.525 | 66.185 | 65.335 | available | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.3185 | 36.4585 | 16.8 | 0 | 19.6585 | 0 | 84.525 | 64.8665 | 64.8665 | available | 0.9
| Nom. capacity MV, MVA | 40,0+2*40,5 | 15.95 | 16.8 | 0 | -0.85 | 0 | 84.525 | 85.375 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.92763 | 16.8776 | 16.8 | 0 | 0.077632 | 0 | 84.525 | 84.4474
| Nom. capacity MV, MVA | 40,0+2*40,5 | 19.19 | 0 | 0 | 19.19 | 0 | 84.525 | 65.335 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.259 | 19.449 | 0 | 0 | 19.449 | 0 | 84.525 | 65.076
10 | SS 110/10 Vysokaya | 2*16,0 | 27.2 | 3.2 | 15 | 24 | 0 | 16.8 | -7.2 | -7.2 | unavailable | 10 | SS 110/10 Vysokaya | 2*16,0 |  | 27.2 | 3.2 | 15 | 24 | 0 | 16.8 | -7.2 | -7.2 | unavailable | 0.94
11 | SS 110/35/10 Glushkovo | 2*10,0 | 6.54 | 8.04 | 120 | -1.5 | 0 | 10.5 | 12 | 8.94 | available | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 4.0543 | 10.5943 | 8.04 | 120 | 2.5543 | 0 | 10.5 | 7.9457 | 7.088 | available | 0.85
| Nom. capacity MV, MVA | 10 | 3.54 | 6.6 | 120 | -3.06 | 0 | 10.5 | 13.56 |  |  |  | Nom. capacity MV, MVA | 10 | 1.5941 | 5.1341 | 6.6 | 120 | -1.4659 | 0 | 10.5 | 11.9659
| Nom. capacity LV, MVA | 10 | 3 | 1.44 | 80 | 1.56 | 0 | 10.5 | 8.94 |  |  |  | Nom. capacity LV, MVA | 10 | 1.852 | 4.852 | 1.44 | 80 | 3.412 | 0 | 10.5 | 7.088
12 | SS 110/10 Gorodskaya | 2*25,0 | 13.76 | 0 | 0 | 13.76 | 0 | 26.25 | 12.49 | 12.49 | available | 12 | SS 110/10 Gorodskaya | 2*25,0 | 6.5558 | 20.3158 | 0 | 0 | 20.3158 | 0 | 26.25 | 5.9342 | 5.9342 | available | 0.95
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 9.9 | 6.52 | 120 | 3.38 | 0 | 10.5 | 7.12 | 5.06 | available | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 14.7964 | 24.6964 | 6.52 | 120 | 18.1764 | 0 | 10.5 | -7.6764 | -7.6764 | unavailable | 0.83
| Nom. capacity MV, MVA | 10+16,0 | 4 | 6.06 |  | -2.06 | 0 | 10.5 | 12.56 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 12.1622 | 16.1622 | 6.06 |  | 10.1022 | 0 | 10.5 | 0.39777
| Nom. capacity LV, MVA | 10+16,0 | 5.9 | 0.46 | 120 | 5.44 | 0 | 10.5 | 5.06 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.763 | 6.663 | 0.46 | 120 | 6.203 | 0 | 10.5 | 4.297
14 | SS 110/35/10 Dmitriev | 2*10,0 | 4.68 | 10.4 | 120 | -5.72 | 0 | 10.5 | 16.22 | 10.51 | available | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 2.0794 | 6.7594 | 10.4 | 120 | -3.6406 | 0 | 10.5 | 14.1406 | 8.789 | available | 0.85
| Nom. capacity MV, MVA | 10 | 1.69 | 7.4 |  | -5.71 | 0 | 10.5 | 16.21 |  |  |  | Nom. capacity MV, MVA | 10 | 0.046512 | 1.7365 | 7.4 |  | -5.6635 | 0 | 10.5 | 16.1635
| Nom. capacity LV, MVA | 10 | 2.99 | 3 | 80 | -0.01 | 0 | 10.5 | 10.51 |  |  |  | Nom. capacity LV, MVA | 10 | 1.721 | 4.711 | 3 | 80 | 1.711 | 0 | 10.5 | 8.789
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.9 | 0.5 | 120 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | available | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.056701 | 0.9567 | 0.5 | 120 | 0.4567 | 0 | 10.5 | 10.0433 | 10.0433 | available | 0.97
16 | SS 110/35/10 Zhukovka | 2*10,0 | 1.3 | 5.16 | 120 | -3.86 | 0 | 10.5 | 14.36 | 10.96 | available | 16 | SS 110/35/10 Zhukovka | 2*10,0 | 3.9329 | 5.2329 | 5.16 | 120 | 0.072858 | 0 | 10.5 | 10.4271 | 10.0165 | available | 0.99
| Nom. capacity MV, MVA | 10 | 1.1 | 4.5 | 1 day and night | -3.4 | 0 | 10.5 | 13.9 |  |  |  | Nom. capacity MV, MVA | 10 | 3.8835 | 4.9835 | 4.5 | 1 day and night | 0.48353 | 0 | 10.5 | 10.0165
| Nom. capacity LV, MVA | 10 | 0.2 | 0.66 | 120 | -0.46 | 0 | 10.5 | 10.96 |  |  |  | Nom. capacity LV, MVA | 10 | 0.01 | 0.21 | 0.66 | 120 | -0.45 | 0 | 10.5 | 10.95
17 | SS 110/35/10 Zolotukhino | 2*25,0 | 7.77 | 22.1 | 80 | -14.33 | 0 | 26.25 | 40.58 | 25.3 | available | 17 | SS 110/35/10 Zolotukhino | 2*25,0 | 3.5946 | 11.3646 | 22.1 | 80 | -10.7354 | 0 | 26.25 | 36.9854 | 21.965 | available | 0.97
| Nom. capacity MV, MVA | 25 | 3.52 | 18.8 |  | -15.28 | 0 | 26.25 | 41.53 |  |  |  | Nom. capacity MV, MVA | 25 | 0.15176 | 3.6718 | 18.8 |  | -15.1282 | 0 | 26.25 | 41.3782
| Nom. capacity LV, MVA | 25 | 4.25 | 3.3 | 120 | 0.95 | 0 | 26.25 | 25.3 |  |  |  | Nom. capacity LV, MVA | 25 | 3.335 | 7.585 | 3.3 | 120 | 4.285 | 0 | 26.25 | 21.965
18 | SS 110/35/10 Kamyshi | 2*6,3 | 9.4 | 5.45 | 20 | 3.95 | 0 | 6.615 | 2.665 | 1.595 | available | 18 | SS 110/35/10 Kamyshi | 2*6,3 | 11.0906 | 20.4906 | 5.45 | 20 | 15.0406 | 0 | 6.615 | -8.4256 | -8.4256 | unavailable | 0.84
| Nom. capacity MV, MVA | 6.3 | 8.47 | 3.45 |  | 5.02 | 0 | 6.615 | 1.595 |  |  |  | Nom. capacity MV, MVA | 6.3 | 8.9031 | 17.3731 | 3.45 |  | 13.9231 | 0 | 6.615 | -7.3081
| Nom. capacity LV, MVA | 6.3 | 0.93 | 2 | 20 | -1.07 | 0 | 6.615 | 7.685 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.413 | 1.343 | 2 | 20 | -0.657 | 0 | 6.615 | 7.272
19 | SS 110/35/10 Kastornoe | 15,0+16,0 | 12.32 | 6.97 | 120 | 5.35 | 0 | 15.75 | 10.4 | 10.4 | available | 19 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.32386 | 12.6439 | 6.97 | 120 | 5.6739 | 0 | 15.75 | 10.0761 | 10.0761 | available | 0.93
| Nom. capacity MV, MVA | 15,0+16,0 | 9.41 | 6.6 |  | 2.81 | 0 | 15.75 | 12.94 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.26719 | 9.6772 | 6.6 |  | 3.0772 | 0 | 15.75 | 12.6728
| Nom. capacity LV, MVA | 15,0+16,0 | 2.91 | 0.37 | 120 | 2.54 | 0 | 15.75 | 13.21 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.034 | 2.944 | 0.37 | 120 | 2.574 | 0 | 15.75 | 13.176
20 | SS 110/35/10 Kilikino | 2*16,0 | 1.19 | 4.5 | 120 | -3.31 | 0 | 16.8 | 20.11 | 18.26 | available | 20 | SS 110/35/10 Kilikino | 2*16,0 | 0.2809 | 1.4709 | 4.5 | 120 | -3.0291 | 0 | 16.8 | 19.8291 | 18.0682 | available | 0.85
| Nom. capacity MV, MVA | 16 | 1.14 | 2.6 |  | -1.46 | 0 | 16.8 | 18.26 |  |  |  | Nom. capacity MV, MVA | 16 | 0.19176 | 1.3318 | 2.6 |  | -1.2682 | 0 | 16.8 | 18.0682
| Nom. capacity LV, MVA | 16 | 0.05 | 1.9 | 120 | -1.85 | 0 | 16.8 | 18.65 |  |  |  | Nom. capacity LV, MVA | 16 | 0.047 | 0.097 | 1.9 | 120 | -1.803 | 0 | 16.8 | 18.603
21 | SS 110/35/6 Kirovskaya | 2*40,0 | 46.3 | 16.36 | 120 | 29.94 | 0 | 42 | 12.06 | 12.06 | available | 21 | SS 110/35/6 Kirovskaya | 2*40,0 | 4.5225 | 50.8225 | 16.36 | 120 | 34.4625 | 0 | 42 | 7.5375 | 7.5375 | available | 0.89
| Nom. capacity MV, MVA | 40 | 20.08 | 13.06 | 120 | 7.02 | 0 | 42 | 34.98 |  |  |  | Nom. capacity MV, MVA | 40 |  | 20.08 | 13.06 | 120 | 7.02 | 0 | 42 | 34.98
| Nom. capacity LV, MVA | 40 | 26.22 | 3.3 | 120 | 22.92 | 0 | 42 | 19.08 |  |  |  | Nom. capacity LV, MVA | 40 | 4.025 | 30.245 | 3.3 | 120 | 26.945 | 0 | 42 | 15.055
22 | SS 110/35/10 Klyukva | 2*16,0 | 2.82 | 1.2 | 120 | 1.62 | 0 | 16.8 | 15.18 | 15.18 | available | 22 | SS 110/35/10 Klyukva | 2*16,0 | 1.7688 | 4.5888 | 1.2 | 120 | 3.3887 | 0 | 16.8 | 13.4113 | 13.4113 | available | 0.96
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  | 2: Nom. capacity MV, MVA; 3: 16; 5: 0; MVA 6: 0; Min 8: 0; Min 9: 0; Min 10: 16.8; Min 11: 16.8
| Nom. capacity LV, MVA | 16 | 2.82 | 1.2 | 120 | 1.62 | 0 | 16.8 | 15.18 |  |  |  | Nom. capacity LV, MVA | 16 | 1.698 | 4.518 | 1.2 | 120 | 3.318 | 0 | 16.8 | 13.482
23 | SS 110/10 Kompressornaya | 2*40,0 | 1.55 | 0 | 0 | 1.55 | 0 | 42 | 40.45 | 40.45 | available | 23 | SS 110/10 Kompressornaya | 2*40,0 |  | 1.55 | 0 | 0 | 1.55 | 0 | 42 | 40.45 | 40.45 | available | 0.87
24 | SS 110/35/10 Konyshevka | 10,0+16,0 | 9.2 | 8 | 120 | 1.2 | 0 | 10.5 | 9.3 | 9.05 | available | 24 | SS 110/35/10 Konyshevka | 10,0+16,0 | 4.8467 | 14.0467 | 8 | 120 | 6.0467 | 0 | 10.5 | 4.4533 | 4.4533 | available | 0.89
| Nom. capacity MV, MVA | 10,0+16,0 | 7.35 | 5.9 |  | 1.45 | 0 | 10.5 | 9.05 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 3.5785 | 10.9285 | 5.9 |  | 5.0285 | 0 | 10.5 | 5.4715
| Nom. capacity LV, MVA | 10,0+16,0 | 1.85 | 2.1 |  | -0.25 | 0 | 10.5 | 10.75 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.735 | 2.585 | 2.1 |  | 0.485 | 0 | 10.5 | 10.015
25 | SS 110/10 Kotelnaya | 10,0+25,0 | 1.55 | 4.1 | 0 | -2.55 | 0 | 10.5 | 13.05 | 13.05 | available | 25 | SS 110/10 Kotelnaya | 10,0+25,0 | 0.015385 | 1.5654 | 4.1 | 0 | -2.5346 | 0 | 10.5 | 13.0346 | 13.0346 | available | 0.91
26 | SS 110/35/10 Kshen | 2*10,0 | 8.17 | 7.81 | 10 | 0.36 | 0 | 10.5 | 10.14 | 7.04 | available | 26 | SS 110/35/10 Kshen | 2*10,0 | 7.5608 | 15.7308 | 7.81 | 10 | 7.9208 | 0 | 10.5 | 2.5792 | 0.85 | available | 0.89
| Nom. capacity MV, MVA | 10 | 2.96 | 6.06 |  | -3.1 | 0 | 10.5 | 13.6 |  |  |  | Nom. capacity MV, MVA | 10 | 0.53911 | 3.4991 | 6.06 |  | -2.5609 | 0 | 10.5 | 13.0609
| Nom. capacity LV, MVA | 10 | 5.21 | 1.75 | 120 | 3.46 | 0 | 10.5 | 7.04 |  |  |  | Nom. capacity LV, MVA | 10 | 6.19 | 11.4 | 1.75 | 120 | 9.65 | 0 | 10.5 | 0.85
27 | SS 110/6 Lesnaya | 2*40,0 | 2.31 | 0 | 0 | 2.31 | 0 | 42 | 39.69 | 39.69 | available | 27 | SS 110/6 Lesnaya | 2*40,0 | 3.956 | 6.266 | 0 | 0 | 6.266 | 0 | 42 | 35.734 | 35.734 | available | 0.91
28 | SS 110/35/10 Lgov | 2*25,0 | 12.6 | 4 | 120 | 8.6 | 0 | 26.25 | 17.65 | 17.65 | available | 28 | SS 110/35/10 Lgov | 2*25,0 | 2.6667 | 15.2667 | 4 | 120 | 11.2667 | 0 | 26.25 | 14.9833 | 14.9833 | available | 0.96
| Nom. capacity MV, MVA | 25 | 2.4 |  |  | 2.4 | 0 | 26.25 | 23.85 |  |  |  | Nom. capacity MV, MVA | 25 | 0.663 | 3.063 | 0 |  | 3.063 | 0 | 26.25 | 23.187
| Nom. capacity LV, MVA | 25 | 10.2 | 4 | 120 | 6.2 | 0 | 26.25 | 20.05 |  |  |  | Nom. capacity LV, MVA | 25 | 1.897 | 12.097 | 4 | 120 | 8.097 | 0 | 26.25 | 18.153
29 | SS 110/35/10 Lukashevka | 2*16,0 | 7.41 | 10.6 | 120 | -3.19 | 0 | 16.8 | 19.99 | 17.9 | available | 29 | SS 110/35/10 Lukashevka | 2*16,0 | 0.089965 | 7.5 | 10.6 | 120 | -3.1 | 0 | 16.8 | 19.9 | 17.8235 | available | 0.85
| Nom. capacity MV, MVA | 16 | 4.2 | 5.3 |  | -1.1 | 0 | 16.8 | 17.9 |  |  |  | Nom. capacity MV, MVA | 16 | 0.076471 | 4.2765 | 5.3 |  | -1.0235 | 0 | 16.8 | 17.8235
| Nom. capacity LV, MVA | 16 | 3.21 | 5.3 | 120 | -2.09 | 0 | 16.8 | 18.89 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.21 | 5.3 | 120 | -2.09 | 0 | 16.8 | 18.89
30 | SS 110/35/10 Lyubostan | 6,3+10,0 | 5.9 | 13.1 | 120 | -7.2 | 0 | 6.615 | 13.815 | 6.715 | available | 30 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.28266 | 6.1827 | 13.1 | 120 | -6.9173 | 0 | 6.615 | 13.5323 | 6.67 | available | 0.9
| Nom. capacity MV, MVA | 6,3+10,0 | 4.7 | 11.8 |  | -7.1 | 0 | 6.615 | 13.715 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.2094 | 4.9094 | 11.8 |  | -6.8906 | 0 | 6.615 | 13.5056
| Nom. capacity LV, MVA | 6,3+10,0 | 1.2 | 1.3 |  | -0.1 | 0 | 6.615 | 6.715 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.045 | 1.245 | 1.3 |  | -0.055 | 0 | 6.615 | 6.67
31 | SS 110/35/6 Manturovo | 2*16,0 | 5.78 | 9.35 | 10 | -3.57 | 0 | 16.8 | 20.37 | 16.91 | available | 31 | SS 110/35/6 Manturovo | 2*16,0 | 1.8567 | 7.6367 | 9.35 | 10 | -1.7133 | 0 | 16.8 | 18.5133 | 16.885 | available | 0.83
| Nom. capacity MV, MVA | 16 | 5.63 | 9.09 |  | -3.46 | 0 | 16.8 | 20.26 |  |  |  | Nom. capacity MV, MVA | 16 | 1.5161 | 7.1461 | 9.09 |  | -1.9439 | 0 | 16.8 | 18.7439
| Nom. capacity LV, MVA | 16 | 0.15 | 0.26 | 120 | -0.11 | 0 | 16.8 | 16.91 |  |  |  | Nom. capacity LV, MVA | 16 | 0.025 | 0.175 | 0.26 | 120 | -0.085 | 0 | 16.8 | 16.885
32 | SS 110/35/10 8th Marta | 6,3+10,0 | 5.75 | 9.6 | 120 | -3.85 | 0 | 6.615 | 10.465 | 8.015 | available | 32 | SS 110/35/10 8th Marta | 6,3+10,0 | 7.8696 | 13.6196 | 9.6 | 120 | 4.0196 | 0 | 6.615 | 2.5954 | 1.024 | available | 0.89
| Nom. capacity MV, MVA | 6,3+10,0 | 5.2 | 6.6 | 120 | -1.4 | 0 | 6.615 | 8.015 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 6.991 | 12.191 | 6.6 | 120 | 5.591 | 0 | 6.615 | 1.024
| Nom. capacity LV, MVA | 6,3+10,0 | 0.55 | 3 | 45 | -2.45 | 0 | 6.615 | 9.065 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.013 | 0.563 | 3 | 45 | -2.437 | 0 | 6.615 | 9.052
33 | SS 110/10 Martovskaya | 2*6,3 | 0.61 | 0.55 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | available | 33 | SS 110/10 Martovskaya | 2*6,3 | 0.21889 | 0.82889 | 0.55 | 120 | 0.27889 | 0 | 6.615 | 6.3361 | 6.3361 | available | 0.9
34 | SS 110/35/10 Maryino | 10,0+25,0 | 5.7 | 8.11 | 120 | -2.41 | 0 | 10.5 | 12.91 | 11.7 | available | 34 | SS 110/35/10 Maryino | 10,0+25,0 | 0.45301 | 6.153 | 8.11 | 120 | -1.957 | 0 | 10.5 | 12.457 | 11.3227 | available | 0.88
| Nom. capacity MV, MVA | 10,0+25,0 | 3.7 | 4.9 |  | -1.2 | 0 | 10.5 | 11.7 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.37735 | 4.0773 | 4.9 |  | -0.82265 | 0 | 10.5 | 11.3227
| Nom. capacity LV, MVA | 10,0+25,0 | 2 | 3.21 |  | -1.21 | 0 | 10.5 | 11.71 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.0213 | 2.0213 | 3.21 |  | -1.1887 | 0 | 10.5 | 11.6887
35 | SS 110/35/10 Medvenka | 2*10,0 | 7.27 | 19.22 | 120 | -11.95 | 0 | 10.5 | 22.45 | 9.7 | available | 35 | SS 110/35/10 Medvenka | 2*10,0 | 0.17108 | 7.4411 | 19.22 | 120 | -11.7789 | 0 | 10.5 | 22.2789 | 9.578 | available | 0.83
| Nom. capacity MV, MVA | 10 | 4.35 | 17.1 |  | -12.75 | 0 | 10.5 | 23.25 |  |  |  | Nom. capacity MV, MVA | 10 | 0.02 | 4.37 | 17.1 |  | -12.73 | 0 | 10.5 | 23.23
| Nom. capacity LV, MVA | 10 | 2.92 | 2.12 | 120 | 0.8 | 0 | 10.5 | 9.7 |  |  |  | Nom. capacity LV, MVA | 10 | 0.122 | 3.042 | 2.12 | 120 | 0.922 | 0 | 10.5 | 9.578
36 | SS 110/6 Neftyanaya | 2*10,0 | 0.16 |  |  | 0.16 | 0 | 10.5 | 10.34 | 10.34 | available | 36 | SS 110/6 Neftyanaya | 2*10,0 | 0.016092 | 0.17609 | 0 |  | 0.17609 | 0 | 10.5 | 10.3239 | 10.3239 | available | 0.87
37 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 16.25 | 26.86 | 120 | -10.61 | 0 | 16.8 | 27.41 | 12.01 | available | 37 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 2.0286 | 18.2786 | 26.86 | 120 | -8.5814 | 0 | 16.8 | 25.3814 | 10.302 | available | 0.86
| Nom. capacity MV, MVA | 16,0 + 25,0 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.036634 | 2.0366 | 17.4 | 0 | -15.3634 | 0 | 16.8 | 32.1634
| Nom. capacity LV, MVA | 16,0 + 25,0 | 14.25 | 9.46 |  | 4.79 | 0 | 16.8 | 12.01 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 1.708 | 15.958 | 9.46 |  | 6.498 | 0 | 16.8 | 10.302
38 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 13.55 | 15.5 | 120 | -1.95 | 0 | 16.8 | 18.75 | 13.31 | available | 38 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.40397 | 13.954 | 15.5 | 120 | -1.546 | 0 | 16.8 | 18.346 | 13.052 | available | 0.86
| Nom. capacity MV, MVA | 16 | 9.06 | 14.5 |  | -5.44 | 0 | 16.8 | 22.24 |  |  |  | Nom. capacity MV, MVA | 16 | 0.089412 | 9.1494 | 14.5 |  | -5.3506 | 0 | 16.8 | 22.1506
| Nom. capacity LV, MVA | 16 | 4.49 | 1 | 120 | 3.49 | 0 | 16.8 | 13.31 |  |  |  | Nom. capacity LV, MVA | 16 | 0.258 | 4.748 | 1 | 120 | 3.748 | 0 | 16.8 | 13.052
39 | SS 110/35/10 Olkhovka | 2 х 6,3 | 1.66 | 6.31 | 120 | -4.65 | 0 | 6.615 | 11.265 | 7.715 | available | 39 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.13073 | 1.7907 | 6.31 | 120 | -4.5193 | 0 | 6.615 | 11.1343 | 7.698 | available | 0.76
| Nom. capacity MV, MVA | 6.3 | 1.45 | 5 | 120 | -3.55 | 0 | 6.615 | 10.165 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.082353 | 1.5324 | 5 | 120 | -3.4676 | 0 | 6.615 | 10.0826
| Nom. capacity LV, MVA | 6.3 | 0.21 | 1.31 | 120 | -1.1 | 0 | 6.615 | 7.715 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.017 | 0.227 | 1.31 | 120 | -1.083 | 0 | 6.615 | 7.698
40 | SS 110/10 Paniki | 2 х 2,5 | 0.62 | 0.1 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 40 | SS 110/10 Paniki | 2 х 2,5 | 0.046739 | 0.66674 | 0.1 | 120 | 0.56674 | 0 | 2.625 | 2.0583 | 2.0583 | available | 0.92
41 | SS 110/35/10 Peny | 2 х 16,0 | 6.44 | 6.9 | 120 | -0.46 | 0 | 16.8 | 17.26 | 16.88 | available | 41 | SS 110/35/10 Peny | 2 х 16,0 | 0.412 | 6.852 | 6.9 | 120 | -0.048005 | 0 | 16.8 | 16.848 | 16.5798 | available | 0.85
| Nom. capacity MV, MVA | 16 | 3.42 | 3.5 |  | -0.08 | 0 | 16.8 | 16.88 |  |  |  | Nom. capacity MV, MVA | 16 | 0.3002 | 3.7202 | 3.5 |  | 0.2202 | 0 | 16.8 | 16.5798
| Nom. capacity LV, MVA | 16 | 3.02 | 3.4 | 120 | -0.38 | 0 | 16.8 | 17.18 |  |  |  | Nom. capacity LV, MVA | 16 | 0.05 | 3.07 | 3.4 | 120 | -0.33 | 0 | 16.8 | 17.13
42 | SS 110/35/10 Pribor | 2 х 25,0 | 25.99 | 6.5 | 0 | 19.49 | 0 | 26.25 | 6.76 | 6.76 | available | 42 | SS 110/35/10 Pribor | 2 х 25,0 | 3.9474 | 29.9374 | 6.5 | 0 | 23.4374 | 0 | 26.25 | 2.8126 | 2.8126 | available | 0.95
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  | 2: Nom. capacity MV, MVA; 3: 25; 5: 0; MVA 6: 0; Min 8: 0; Min 9: 0; Min 10: 26.25; Min 11: 26.25
| Nom. capacity LV, MVA | 25 | 25.99 | 6.5 | 0 | 19.49 | 0 | 26.25 | 6.76 |  |  |  | Nom. capacity LV, MVA | 25 | 3.75 | 29.74 | 6.5 | 0 | 23.24 | 0 | 26.25 | 3.01
43 | SS 110/10 Progress | 2 х 63,0 | 16.27 | 0 | 0 | 16.27 | 0 | 66.15 | 49.88 | 49.88 | available | 43 | SS 110/10 Progress | 2 х 63,0 |  | 16.27 | 0 | 0 | 16.27 | 0 | 66.15 | 49.88 | 49.88 | available | 0.94
44 | SS 110/10 Poultry plant | 6,3 + 10,0 | 3.26 | 0.32 | 0 | 2.94 | 0 | 6.615 | 3.675 | 3.675 | available | 44 | SS 110/10 Poultry plant | 6,3 + 10,0 | 0.52289 | 3.7829 | 0.32 | 0 | 3.4629 | 0 | 6.615 | 3.1521 | 3.1521 | available | 0.83
45 | SS 110/35/10 R. Budy | 2 х 10,0 | 3.2 | 15.7 | 120 | -12.5 | 0 | 10.5 | 23 | 15.5 | available | 45 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.010345 | 3.2103 | 15.7 | 120 | -12.4897 | 0 | 10.5 | 22.9897 | 15.491 | available | 0.87
| Nom. capacity MV, MVA | 10 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.009 | 1.409 | 6.4 |  | -4.991 | 0 | 10.5 | 15.491
46 | SS 110/35/10 Raskhovets | 2 х 6,3 | 0.34 | 5.89 | 1 day and night | -5.55 | 0 | 6.615 | 12.165 | 8.675 | available | 46 | SS 110/35/10 Raskhovets | 2 х 6,3 | 0.01875 | 0.35875 | 5.89 | 1 day and night | -5.5312 | 0 | 6.615 | 12.1463 | 8.675 | available | 0.8
| Nom. capacity MV, MVA | 6.3 | 0.25 | 3.74 | 1 day and night | -3.49 | 0 | 6.615 | 10.105 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.015 | 0.265 | 3.74 | 1 day and night | -3.475 | 0 | 6.615 | 10.09
| Nom. capacity LV, MVA | 6.3 | 0.09 | 2.15 | 1 day and night | -2.06 | 0 | 6.615 | 8.675 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.09 | 2.15 | 1 day and night | -2.06 | 0 | 6.615 | 8.675
47 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.3 | 21.4 | 45 | -19.1 | 0 | 6.615 | 25.715 | 9.495 | available | 47 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 0.17197 | 2.472 | 21.4 | 45 | -18.928 | 0 | 6.615 | 25.543 | 9.45 | available | 0.98
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.58 | 17.8 |  | -16.22 | 0 | 6.615 | 22.835 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 0.12353 | 1.7035 | 17.8 |  | -16.0965 | 0 | 6.615 | 22.7115
| Nom. capacity LV, MVA | 6,3 + 10,0 | 0.72 | 3.6 | 45 | -2.88 | 0 | 6.615 | 9.495 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.045 | 0.765 | 3.6 | 45 | -2.835 | 0 | 6.615 | 9.45
48 | SS 110/10 Rodniki | 2х25 | 4.2 | 9.2 | 120 | -5 | 0 | 26.25 | 31.25 | 31.25 | available |  | SS 110/10 Rodniki | 2х25 | 16.8 | 21 | 9.2 | 120 | 11.8 | 0 | 26.25 | 14.45 | 14.45 | available | 0.85
49 | SS 110/35/10 Rudnaya | 2 х 31,5 | 15.85 | 3.25 | 10 | 12.6 | 0 | 33.075 | 20.475 | 20.475 | available | 48 | SS 110/35/10 Rudnaya | 2 х 31,5 | 1.2077 | 17.0577 | 3.25 | 10 | 13.8077 | 0 | 33.075 | 19.2673 | 19.2673 | available | 0.83
| Nom. capacity MV, MVA | 31.5 | 9.58 | 1.7 |  | 7.88 | 0 | 33.075 | 25.195 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.90235 | 10.4824 | 1.7 |  | 8.7824 | 0 | 33.075 | 24.2926
| Nom. capacity LV, MVA | 31.5 | 6.27 | 1.55 | 120 | 4.72 | 0 | 33.075 | 28.355 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.1 | 6.37 | 1.55 | 120 | 4.82 | 0 | 33.075 | 28.255
50 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 14.8 | 11 | 120 | 3.8 | 0 | 16.8 | 13 | 13 | available | 49 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 10.7881 | 25.5881 | 11 | 120 | 14.5881 | 0 | 16.8 | 2.2119 | 2.2119 | available | 0.92
| Nom. capacity MV, MVA | 16,0 + 25,0 | 8.4 | 7 |  | 1.4 | 0 | 16.8 | 15.4 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 6.717 | 15.117 | 7 |  | 8.117 | 0 | 16.8 | 8.683
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.4 | 4 | 120 | 2.4 | 0 | 16.8 | 14.4 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 3.208 | 9.608 | 4 | 120 | 5.608 | 0 | 16.8 | 11.192
51 | SS 110/10 Solovyinaya | 2 х 25,0 | 6.09 | 0 | 0 | 6.09 | 0 | 26.25 | 20.16 | 20.16 | available | 50 | SS 110/10 Solovyinaya | 2 х 25,0 | 1.6875 | 7.7775 | 0 | 0 | 7.7775 | 0 | 26.25 | 18.4725 | 18.4725 | available | 0.96
52 | SS 110/10 STK | 2 х 10,0 | 0.6 | 0 | 0 | 0.6 | 0 | 10.5 | 9.9 | 9.9 | available | 51 | SS 110/10 STK | 2 х 10,0 | 0.01 | 0.61 | 0 | 0 | 0.61 | 0 | 10.5 | 9.89 | 9.89 | available | 0.8
53 | SS 110/10 Studenok | 2 х 6,3 | 1.39 | 0.7 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | available | 52 | SS 110/10 Studenok | 2 х 6,3 | 0.13176 | 1.5218 | 0.7 | 120 | 0.82176 | 0 | 6.615 | 5.7932 | 5.7932 | available | 0.85
54 | SS 110/35/10 Sudzha | 2 х 25,0 | 16.6 | 29 | 120 | -12.4 | 0 | 26.25 | 38.65 | 28.25 | available | 53 | SS 110/35/10 Sudzha | 2 х 25,0 | 2.4199 | 19.0199 | 29 | 120 | -9.9801 | 0 | 26.25 | 36.2301 | 27.453 | available | 0.9
| Nom. capacity MV, MVA | 25 | 6.7 | 17.1 |  | -10.4 | 0 | 26.25 | 36.65 |  |  |  | Nom. capacity MV, MVA | 25 | 1.3809 | 8.0809 | 17.1 |  | -9.0191 | 0 | 26.25 | 35.2691
| Nom. capacity LV, MVA | 25 | 9.9 | 11.9 |  | -2 | 0 | 26.25 | 28.25 |  |  |  | Nom. capacity LV, MVA | 25 | 0.797 | 10.697 | 11.9 |  | -1.203 | 0 | 26.25 | 27.453
55 | SS 110/35/10 Schyotmash | 2 х 25,0 | 14.82 | 0 | 0 | 14.82 | 0 | 26.25 | 11.43 | 11.43 | available | 54 | SS 110/35/10 Schyotmash | 2 х 25,0 | 9.5785 | 24.3985 | 0 | 0 | 24.3985 | 0 | 26.25 | 1.8515 | 1.8515 | available | 0.95
| Nom. capacity MV, MVA | 25 | 4.47 |  |  | 4.47 | 0 | 26.25 | 21.78 |  |  |  | Nom. capacity MV, MVA | 25 | 3.8835 | 8.3535 | 0 |  | 8.3535 | 0 | 26.25 | 17.8965
| Nom. capacity LV, MVA | 25 | 10.35 | 0 | 0 | 10.35 | 0 | 26.25 | 15.9 |  |  |  | Nom. capacity LV, MVA | 25 | 5.216 | 15.566 | 0 | 0 | 15.566 | 0 | 26.25 | 10.684
56 | SS 110/35/10 Tyotkino | 2 х 10,0 | 4 | 3.44 | 120 | 0.56 | 0 | 10.5 | 9.94 | 8.34 | available | 55 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.073408 | 4.0734 | 3.44 | 120 | 0.63341 | 0 | 10.5 | 9.8666 | 8.284 | available | 0.87
| Nom. capacity MV, MVA | 10 | 0.4 | 2 |  | -1.6 | 0 | 10.5 | 12.1 |  |  |  | Nom. capacity MV, MVA | 10 | 0.0078652 | 0.40787 | 2 |  | -1.5921 | 0 | 10.5 | 12.0921
| Nom. capacity LV, MVA | 10 | 3.6 | 1.44 |  | 2.16 | 0 | 10.5 | 8.34 |  |  |  | Nom. capacity LV, MVA | 10 | 0.056 | 3.656 | 1.44 |  | 2.216 | 0 | 10.5 | 8.284
57 | SS 110/35/10 Tim | 6,3 + 16,0 | 4.07 | 9.59 | 120 | -5.52 | 0 | 6.615 | 12.135 | 5.675 | available | 56 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.1722 | 4.2422 | 9.59 | 120 | -5.3478 | 0 | 6.615 | 11.9628 | 5.628 | available | 0.84
| Nom. capacity MV, MVA | 6,3 + 16,0 | 2.63 | 9.09 |  | -6.46 | 0 | 6.615 | 13.075 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.097647 | 2.7276 | 9.09 |  | -6.3624 | 0 | 6.615 | 12.9774
| Nom. capacity LV, MVA | 6,3 + 16,0 | 1.44 | 0.5 | 120 | 0.94 | 0 | 6.615 | 5.675 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.047 | 1.487 | 0.5 | 120 | 0.987 | 0 | 6.615 | 5.628
58 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.57 | 0.5 | 120 | 0.07 | 0 | 10.5 | 10.43 | 10.22 | available | 57 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.20159 | 0.77159 | 0.5 | 120 | 0.27159 | 0 | 10.5 | 10.2284 | 10.0576 | available | 0.85
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0.16235 | 0.44235 | 0 |  | 0.44235 | 0 | 10.5 | 10.0576
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.29 | 0.5 | 120 | -0.21 | 0 | 10.5 | 10.71 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.009 | 0.299 | 0.5 | 120 | -0.201 | 0 | 10.5 | 10.701
59 | SS 110/35/10 Fatezh | 2 х 16,0 | 9.28 | 17.4 | 120 | -8.12 | 0 | 16.8 | 24.92 | 15.52 | available | 58 | SS 110/35/10 Fatezh | 2 х 16,0 | 4.1173 | 13.3973 | 17.4 | 120 | -4.0027 | 0 | 16.8 | 20.8027 | 12.311 | available | 0.86
| Nom. capacity MV, MVA | 16 | 3.4 | 12.8 |  | -9.4 | 0 | 16.8 | 26.2 |  |  |  | Nom. capacity MV, MVA | 16 | 0.33192 | 3.7319 | 12.8 |  | -9.0681 | 0 | 16.8 | 25.8681
| Nom. capacity LV, MVA | 16 | 5.88 | 4.6 | 120 | 1.28 | 0 | 16.8 | 15.52 |  |  |  | Nom. capacity LV, MVA | 16 | 3.209 | 9.089 | 4.6 | 120 | 4.489 | 0 | 16.8 | 12.311
60 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 3.43 | 12.34 | 120 | -8.91 | 0 | 26.25 | 35.16 | 24.72 | available | 59 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.29545 | 3.7255 | 12.34 | 120 | -8.6145 | 0 | 26.25 | 34.8645 | 24.657 | available | 0.88
| Nom. capacity MV, MVA | 25 | 1.68 | 12.12 |  | -10.44 | 0 | 26.25 | 36.69 |  |  |  | Nom. capacity MV, MVA | 25 | 0.197 | 1.877 | 12.12 |  | -10.243 | 0 | 26.25 | 36.493
| Nom. capacity LV, MVA | 25 | 1.75 | 0.22 | 10 | 1.53 | 0 | 26.25 | 24.72 |  |  |  | Nom. capacity LV, MVA | 25 | 0.063 | 1.813 | 0.22 | 10 | 1.593 | 0 | 26.25 | 24.657
61 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 2 | 6.3 | 80 | -4.3 | 0 | 7.875 | 12.175 | 8.765 | available | 60 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.99836 | 2.9984 | 6.3 | 80 | -3.3016 | 0 | 7.875 | 11.1766 | 7.977 | available | 0.86
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.49 | 3.9 |  | -3.41 | 0 | 7.875 | 11.285 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.070588 | 0.56059 | 3.9 |  | -3.3394 | 0 | 7.875 | 11.2144
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.51 | 2.4 | 80 | -0.89 | 0 | 7.875 | 8.765 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.788 | 2.298 | 2.4 | 80 | -0.102 | 0 | 7.875 | 7.977
62 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 1.67 | 9.38 | 10 | -7.71 | 0 | 16.8 | 24.51 | 15.71 | available | 61 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.68667 | 2.3567 | 9.38 | 10 | -7.0233 | 0 | 16.8 | 23.8233 | 15.39 | available | 0.87
| Nom. capacity MV, MVA | 16 | 0.29 | 9.09 |  | -8.8 | 0 | 16.8 | 25.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.2774 | 0.5674 | 9.09 |  | -8.5226 | 0 | 16.8 | 25.3226
| Nom. capacity LV, MVA | 16 | 1.38 | 0.29 | 120 | 1.09 | 0 | 16.8 | 15.71 |  |  |  | Nom. capacity LV, MVA | 16 | 0.32 | 1.7 | 0.29 | 120 | 1.41 | 0 | 16.8 | 15.39
63 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 3.2 | 8.25 | 120 | -5.05 | 0 | 6.615 | 11.665 | 5.665 | available | 62 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.1261 | 3.3261 | 8.25 | 120 | -4.9239 | 0 | 6.615 | 11.5389 | 5.65 | available | 0.9
| Nom. capacity MV, MVA | 6.3 | 1 | 7 |  | -6 | 0 | 6.615 | 12.615 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.098487 | 1.0985 | 7 |  | -5.9015 | 0 | 6.615 | 12.5165
| Nom. capacity LV, MVA | 6.3 | 2.2 | 1.25 | 129 | 0.95 | 0 | 6.615 | 5.665 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.015 | 2.215 | 1.25 | 129 | 0.965 | 0 | 6.615 | 5.65
64 | SS 110/35/10 Shumakovo | 2 х 10,0 | 4.6 | 13.73 | 120 | -9.13 | 0 | 10.5 | 19.63 | 11.83 | available | 63 | SS 110/35/10 Shumakovo | 2 х 10,0 | 2.563 | 7.163 | 13.73 | 120 | -6.567 | 0 | 10.5 | 17.067 | 11.776 | available | 0.85
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3 |  |  |  | Nom. capacity MV, MVA | 10 | 2.1246 | 5.5246 | 11.2 |  | -5.6754 | 0 | 10.5 | 16.1754
| Nom. capacity LV, MVA | 10 | 1.2 | 2.53 | 120 | -1.33 | 0 | 10.5 | 11.83 |  |  |  | Nom. capacity LV, MVA | 10 | 0.054 | 1.254 | 2.53 | 120 | -1.276 | 0 | 10.5 | 11.776
65 | SS 110/35/10 Shchigry | 2 х 25,0 | 12.83 | 12.9 | 120 | -0.07 | 0 | 26.25 | 26.32 | 19.35 | available | 64 | SS 110/35/10 Shchigry | 2 х 25,0 | 1.0656 | 13.8956 | 12.9 | 120 | 0.99564 | 0 | 26.25 | 25.2544 | 19.33 | available | 0.9
| Nom. capacity MV, MVA | 25 | 5.15 | 12.12 |  | -6.97 | 0 | 26.25 | 33.22 |  |  |  | Nom. capacity MV, MVA | 25 | 0.93907 | 6.0891 | 12.12 |  | -6.0309 | 0 | 26.25 | 32.2809
| Nom. capacity LV, MVA | 25 | 7.68 | 0.78 | 120 | 6.9 | 0 | 26.25 | 19.35 |  |  |  | Nom. capacity LV, MVA | 25 | 0.02 | 7.7 | 0.78 | 120 | 6.92 | 0 | 26.25 | 19.33
66 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.51 | 6.31 | 10 | -3.8 | 0 | 7.875 | 11.675 | 6.85 | available | 65 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 1.014 | 3.524 | 6.31 | 10 | -2.786 | 0 | 7.875 | 10.661 | 6.758 | available | 0.83
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.23 | 6.06 |  | -4.83 | 0 | 7.88 | 12.71 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.7496 | 1.9796 | 6.06 |  | -4.0804 | 0 | 7.88 | 11.9604
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.28 | 0.25 | 10 | 1.03 | 0 | 7.88 | 6.85 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.092 | 1.372 | 0.25 | 10 | 1.122 | 0 | 7.88 | 6.758
67 | SS 35/10 Amosovka | 2 х 2,5 | 0.32 | 0.2 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available | 66 | SS 35/10 Amosovka | 2 х 2,5 | 0.011765 | 0.33176 | 0.2 | 120 | 0.13176 | 0 | 2.625 | 2.4932 | 2.4932 | available | 0.85
68 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available | 67 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.015957 | 0.51596 | 0.37 | 120 | 0.14596 | 0 | 1.68 | 1.534 | 1.534 | available | 0.94
69 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | available | 68 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | available | 0.85
70 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.15 | 1.43 | 120 | -1.28 | 0 | 1.68 | 2.96 | 2.96 | available | 69 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0 | 0.15 | 1.43 | 120 | -1.28 | 0 | 1.68 | 2.96 | 2.96 | available | 0.81
71 | SS 35/10 Bezlesnaya | 2 х 4,0 | 2.15 | 6.1 | 0 | -3.95 | 0 | 4.2 | 8.15 | 8.15 | available | 70 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.279 | 2.429 | 6.1 | 0 | -3.671 | 0 | 4.2 | 7.871 | 7.871 | available | 1
72 | SS 35/10 Bereza | 1,0 + 2,5 | 0.05 | 0.15 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | available | 71 | SS 35/10 Bereza | 1,0 + 2,5 | 0.0094118 | 0.059412 | 0.15 | 120 | -0.090588 | 0 | 1.05 | 1.1406 | 1.1406 | available | 0.85
73 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.81 | 0.29 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 72 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.026923 | 0.83692 | 0.29 | 120 | 0.54692 | 0 | 2.625 | 2.0781 | 2.0781 | available | 0.78
74 | SS 35/10 Bykanovo | 2 х 2,5 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 73 | SS 35/10 Bykanovo | 2 х 2,5 | 0 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 0.7
75 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.27 | 0.4 | 120 | -0.13 | 0 | 4.2 | 4.33 | 4.33 | available | 74 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.12235 | 0.39235 | 0.4 | 120 | -0.0076471 | 0 | 4.2 | 4.2076 | 4.2076 | available | 0.85
76 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.86 | 0.22 | 120 | 0.64 | 0 | 1.68 | 1.04 | 1.04 | available | 75 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.093023 | 0.95302 | 0.22 | 120 | 0.73302 | 0 | 1.68 | 0.94698 | 0.94698 | available | 0.86
77 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.56 | 0.46 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 76 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.035294 | 0.59529 | 0.46 | 120 | 0.13529 | 0 | 2.625 | 2.4897 | 2.4897 | available | 0.85
78 | SS 35/10 Voropaevo | 2 х 4,0 | 0.4 | 0 | 0 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | available | 77 | SS 35/10 Voropaevo | 2 х 4,0 | 0.025882 | 0.42588 | 0 | 0 | 0.42588 | 0 | 4.2 | 3.7741 | 3.7741 | available | 0.85
79 | SS 35/10 Vostochnaya | 2 х 6,3 | 4 | 0.46 | 120 | 3.54 | 0 | 6.615 | 3.075 | 3.075 | available | 78 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.14239 | 4.1424 | 0.46 | 120 | 3.6824 | 0 | 6.615 | 2.9326 | 2.9326 | available | 0.92
80 | SS 35/10 Vygornoe | 2 х 2,5 | 1.16 | 0.51 | 120 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | available | 79 | SS 35/10 Vygornoe | 2 х 2,5 | 0.044706 | 1.2047 | 0.51 | 120 | 0.69471 | 0 | 2.625 | 1.9303 | 1.9303 | available | 0.85
81 | SS 35/10 Gastomlya | 2 х 1,6 | 0.45 | 0.17 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 80 | SS 35/10 Gastomlya | 2 х 1,6 | 0 | 0.45 | 0.17 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 0.85
82 | SS 35/10 Gorodok | 2 х 4,0 | 1.45 | 0.7 | 45 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | available | 81 | SS 35/10 Gorodok | 2 х 4,0 | 0.0059524 | 1.456 | 0.7 | 45 | 0.75595 | 0 | 4.2 | 3.444 | 3.444 | available | 0.84
83 | SS 35/10 Guevo | 2 х 2,5 | 1.25 | 1.69 | 20 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | available | 82 | SS 35/10 Guevo | 2 х 2,5 | 0.051163 | 1.3012 | 1.69 | 20 | -0.38884 | 0 | 2.625 | 3.0138 | 3.0138 | available | 0.86
84 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.3 | 0.38 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | available | 83 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0 | 0.3 | 0.38 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | available | 0.89
85 | SS 35/6 Dukhovets | 2,5 + 4,0 | 4.12 | 3.5 | 0 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | available | 84 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.034091 | 4.1541 | 3.5 | 0 | 0.65409 | 0 | 2.625 | 1.9709 | 1.9709 | available | 0.88
86 | SS 35/10 Zhernovets | 2 х 2,5 | 0.53 | 0.26 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available | 85 | SS 35/10 Zhernovets | 2 х 2,5 | 0.010638 | 0.54064 | 0.26 | 120 | 0.28064 | 0 | 2.625 | 2.3444 | 2.3444 | available | 0.94
87 | SS 35/6 Zapadnaya | 2 х 10,0 | 9.39 | 2.5 | 0 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | available | 86 | SS 35/6 Zapadnaya | 2 х 10,0 | 0 | 9.39 | 2.5 | 0 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | available | 0.9
88 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.78 | 1.67 | 0 | -0.89 | 0 | 4.2 | 5.09 | 5.09 | available | 87 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.076623 | 0.85662 | 1.67 | 0 | -0.81338 | 0 | 4.2 | 5.0134 | 5.0134 | available | 0.77
89 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 88 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.17294 | 1.0729 | 0.93 | 45 | 0.14294 | 0 | 1.68 | 1.5371 | 1.5371 | available | 0.85
90 | SS 35/10 Ivanino | 2 х 6,3 | 2.27 | 2.69 | 80 | -0.42 | 0 | 6.615 | 7.035 | 7.035 | available | 89 | SS 35/10 Ivanino | 2 х 6,3 | 0.21294 | 2.4829 | 2.69 | 80 | -0.20706 | 0 | 6.615 | 6.8221 | 6.8221 | available | 0.85
91 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.63 | 0.5 | 120 | 0.13 | 0 | 1.89 | 1.76 | 1.76 | available | 90 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0 | 0.63 | 0.5 | 120 | 0.13 | 0 | 1.89 | 1.76 | 1.76 | available | 0.85
92 | SS 35/10 Kirilovka | 2 х 1,6 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | available | 91 | SS 35/10 Kirilovka | 2 х 1,6 | 0 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | available | 0.85
93 | SS 35/6 Kislinskaya | 2 х 10,0 | 9.73 | 6.25 | 20 | 3.48 | 0 | 10.5 | 7.02 | 7.02 | available | 92 | SS 35/6 Kislinskaya | 2 х 10,0 | 0 | 9.73 | 6.25 | 20 | 3.48 | 0 | 10.5 | 7.02 | 7.02 | available | 0.89
94 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 3.51 | 0.21 | 120 | 3.3 | 0 | 6.615 | 3.315 | 3.315 | available | 93 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.78 | 4.29 | 0.21 | 120 | 4.08 | 0 | 6.615 | 2.535 | 2.535 | available | 0.8
95 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 2.2 | 1.14 | 80 | 1.06 | 0 | 3.36 | 2.3 | 2.3 | available | 94 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 1.9153 | 4.1153 | 1.14 | 80 | 2.9753 | 0 | 3.36 | 0.38471 | 0.38471 | available | 0.85
96 | SS 35/10 Korenevo | 4,0 + 6,3 | 4.3 | 1.56 | 80 | 2.74 | 0 | 4.2 | 1.46 | 1.46 | available | 95 | SS 35/10 Korenevo | 4,0 + 6,3 | 5.8531 | 10.1531 | 1.56 | 80 | 8.5931 | 0 | 4.2 | -4.3931 | -4.3931 | unavailable | 0.98
97 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.68 | 0.24 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 96 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.025 | 0.705 | 0.24 | 120 | 0.465 | 0 | 2.625 | 2.16 | 2.16 | available | 0.92
98 | SS 35/10 Krupets | 1,8 + 2,5 | 1.23 | 0.42 | 120 | 0.81 | 0 | 1.89 | 1.08 | 1.08 | available | 97 | SS 35/10 Krupets | 1,8 + 2,5 | 0.21209 | 1.4421 | 0.42 | 120 | 1.0221 | 0 | 1.89 | 0.86791 | 0.86791 | available | 0.91
99 | SS 35/10 Kulbaki | 2 х 2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 98 | SS 35/10 Kulbaki | 2 х 2,5 | 1.0955 | 1.8955 | 0.6 | 120 | 1.2955 | 0 | 2.625 | 1.3295 | 1.3295 | available | 0.89
100 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.625 | 2.665 | 2.665 | available | 99 | SS 35/10 Kultprosvet | 2 х 2,5 | 0 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.625 | 2.665 | 2.665 | available | 0.85
101 | SS 35/10 Kurchatov | 2 х 10,0 | 4.88 | 4.5 | 80 | 0.38 | 0 | 10.5 | 10.12 | 10.12 | available | 100 | SS 35/10 Kurchatov | 2 х 10,0 | 0 | 4.88 | 4.5 | 80 | 0.38 | 0 | 10.5 | 10.12 | 10.12 | available | 0.85
102 | SS 35/10 Kutok | 2 х 2,5 | 0.07 | 0.05 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 101 | SS 35/10 Kutok | 2 х 2,5 | 0 | 0.07 | 0.05 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 0.85
103 | SS 35/10 Linets | 2 х 2,5 | 0.42 | 0.25 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 102 | SS 35/10 Linets | 2 х 2,5 | 0.017647 | 0.43765 | 0.25 | 120 | 0.18765 | 0 | 2.625 | 2.4374 | 2.4374 | available | 0.85
104 | SS 35/10 Luch | 2 х 6,3 | 1.44 | 0.23 | 120 | 1.21 | 0 | 6.615 | 5.405 | 5.405 | available | 103 | SS 35/10 Luch | 2 х 6,3 | 1.3361 | 2.7761 | 0.23 | 120 | 2.5461 | 0 | 6.615 | 4.0689 | 4.0689 | available | 0.83
105 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | available | 104 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.070588 | 0.82059 | 1.59 | 80 | -0.76941 | 0 | 4.2 | 4.9694 | 4.9694 | available | 0.85
106 | SS 35/10 Matveevka | 2 х 2,5 | 0.92 | 0.08 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 105 | SS 35/10 Matveevka | 2 х 2,5 | 0 | 0.92 | 0.08 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 0.96
107 | SS 35/10 Mayak | 2 х 2,5 | 0.35 | 0.3 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 106 | SS 35/10 Mayak | 2 х 2,5 | 0.067059 | 0.41706 | 0.3 | 120 | 0.11706 | 0 | 2.625 | 2.5079 | 2.5079 | available | 0.85
108 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.94 | 1.7 | 80 | -0.76 | 0 | 4.2 | 4.96 | 4.96 | available | 107 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.45412 | 1.3941 | 1.7 | 80 | -0.30588 | 0 | 4.2 | 4.5059 | 4.5059 | available | 0.85
109 | SS 35/10 Murynovka | 2 х 4,0 | 0.34 | 0.3 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | available | 108 | SS 35/10 Murynovka | 2 х 4,0 | 0.32784 | 0.66784 | 0.3 | 120 | 0.36784 | 0 | 4.2 | 3.8322 | 3.8322 | available | 0.97
110 | SS 35/10 N. Borki | 2 х 2,5 | 0.51 | 0.63 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 109 | SS 35/10 N. Borki | 2 х 2,5 | 0.10556 | 0.61556 | 0.63 | 120 | -0.014444 | 0 | 2.625 | 2.6394 | 2.6394 | available | 0.9
111 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.26 | 0.03 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 110 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.0082353 | 0.26824 | 0.03 | 80 | 0.23824 | 0 | 1.68 | 1.4418 | 1.4418 | available | 0.85
112 | SS 35/10 Novaya | 2 х 2,5 | 0.73 | 0.4 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 111 | SS 35/10 Novaya | 2 х 2,5 | 0.45294 | 1.1829 | 0.4 | 120 | 0.78294 | 0 | 2.625 | 1.8421 | 1.8421 | available | 0.85
113 | SS 35/10 Orekhovo | 2 х 2,5 | 0.58 | 0.19 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | available | 112 | SS 35/10 Orekhovo | 2 х 2,5 | 0.086111 | 0.66611 | 0.19 | 120 | 0.47611 | 0 | 2.625 | 2.1489 | 2.1489 | available | 0.72
114 | SS 35/10 Orlovka | 2 х 2,5 | 0.17 | 0.95 | 120 | -0.78 | 0 | 2.625 | 3.405 | 3.405 | available | 113 | SS 35/10 Orlovka | 2 х 2,5 | 3.2241 | 3.3941 | 0.95 | 120 | 2.4441 | 0 | 2.625 | 0.18095 | 0.18095 | available | 0.79
115 | SS 35/10 Osotskoe | 2 х 2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 114 | SS 35/10 Osotskoe | 2 х 2,5 | 0.15294 | 0.34294 | 0.2 | 120 | 0.14294 | 0 | 2.625 | 2.4821 | 2.4821 | available | 0.85
116 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.26 | 0.74 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available | 115 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.045783 | 1.3058 | 0.74 | 120 | 0.56578 | 0 | 4.2 | 3.6342 | 3.6342 | available | 0.83
117 | SS 35/10 Panino | 2 х 2,5 | 0.39 | 0.11 | 80 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 116 | SS 35/10 Panino | 2 х 2,5 | 0.016471 | 0.40647 | 0.11 | 80 | 0.29647 | 0 | 2.625 | 2.3285 | 2.3285 | available | 0.85
118 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.39 | 0.52 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | available | 117 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.02 | 0.41 | 0.52 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | available | 0.85
119 | SS 35/10 Petrinka | 2,5 + 4,0 | 2.21 | 0.3 | 120 | 1.91 | 0 | 2.625 | 0.715 | 0.715 | available | 118 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.56471 | 2.7747 | 0.3 | 120 | 2.4747 | 0 | 2.625 | 0.15029 | 0.15029 | available | 0.85
120 | SS 35/10 Platava | 2 х 2,5 | 1.66 | 0.26 | 120 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | available | 119 | SS 35/10 Platava | 2 х 2,5 | 0.027083 | 1.6871 | 0.26 | 120 | 1.4271 | 0 | 2.625 | 1.1979 | 1.1979 | available | 0.96
121 | SS 35/10 Pogozhee | 2 х 1,6 | 0.3 | 0.46 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | available | 120 | SS 35/10 Pogozhee | 2 х 1,6 | 0 | 0.3 | 0.46 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | available | 0.84
122 | SS 35/10 Porechnoe | 2 х 4,0 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | available | 121 | SS 35/10 Porechnoe | 2 х 4,0 | 0.075294 | 0.57529 | 1.16 | 120 | -0.58471 | 0 | 4.2 | 4.7847 | 4.7847 | available | 0.85
123 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available | 122 | SS 35/10 Pochepnoe | 2 х 6,3 | 0 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available | 0.85
124 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.56 | 0.3 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available | 123 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.10588 | 0.66588 | 0.3 | 80 | 0.36588 | 0 | 2.625 | 2.2591 | 2.2591 | available | 0.85
125 | SS 35/10 Pselets | 2 х 1,6 | 0.2 | 0.42 | 120 | -0.22 | 0 | 1.68 | 1.9 | 1.9 | available | 124 | SS 35/10 Pselets | 2 х 1,6 | 1.8286 | 2.0286 | 0.42 | 120 | 1.6086 | 0 | 1.68 | 0.071429 | 0.071429 | available | 0.7
126 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.39 | 0.43 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 125 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.072941 | 0.46294 | 0.43 | 120 | 0.032941 | 0 | 1.68 | 1.6471 | 1.6471 | available | 0.85
127 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.86 | 0.32 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 126 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.069149 | 0.92915 | 0.32 | 120 | 0.60915 | 0 | 2.625 | 2.0159 | 2.0159 | available | 0.94
128 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.48 | 0.44 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 127 | SS 35/10 R.Kolodets | 2 х 2,5 | 0 | 0.48 | 0.44 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 0.84
129 | SS 35/10 Razvetye | 2 х 4,0 | 1.1 | 1.03 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | available | 128 | SS 35/10 Razvetye | 2 х 4,0 | 0.44824 | 1.5482 | 1.03 | 120 | 0.51824 | 0 | 4.2 | 3.6818 | 3.6818 | available | 0.85
130 | SS 35/10 V. Reutets | 2 х 4,0 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | available | 129 | SS 35/10 V. Reutets | 2 х 4,0 | 0 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | available | 0.85
131 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | available | 130 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | available | 0.84
132 | SS 35/10 Rubilnik | 2 х 2,5 | 1.97 | 1.18 | 80 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 131 | SS 35/10 Rubilnik | 2 х 2,5 | 0 | 1.97 | 1.18 | 80 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 0.94
133 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.5 | 0.08 | 20 | 0.42 | 0 | 1.68 | 1.26 | 1.26 | available | 132 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.5383 | 1.0383 | 0.08 | 20 | 0.9583 | 0 | 1.68 | 0.7217 | 0.7217 | available | 0.94
134 | SS 35/10 Sapogovo | 2 х 2,5 | 1.44 | 0.6 | 20 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 133 | SS 35/10 Sapogovo | 2 х 2,5 | 1.3837 | 2.8237 | 0.6 | 20 | 2.2237 | 0 | 2.625 | 0.40133 | 0.40133 | available | 0.98
135 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 3.4 | 2.25 | 80 | 1.15 | 0 | 6.615 | 5.465 | 5.465 | available | 134 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.090526 | 3.4905 | 2.25 | 80 | 1.2405 | 0 | 6.615 | 5.3745 | 5.3745 | available | 0.95
136 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.34 | 1.4 | 45 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | available | 135 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.17653 | 2.5165 | 1.4 | 45 | 1.1165 | 0 | 4.2 | 3.0835 | 3.0835 | available | 0.98
137 | SS 35/10 Semyonovka | 2 х 2,5 | 0.23 | 0 | - | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 136 | SS 35/10 Semyonovka | 2 х 2,5 | 0.011765 | 0.24176 | 0 | - | 0.24176 | 0 | 2.625 | 2.3832 | 2.3832 | available | 0.85
138 | SS 35/10 Seed plant | 2 х 2,5 | 0.51 | 0.6 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | available | 137 | SS 35/10 Seed plant | 2 х 2,5 | 0.050588 | 0.56059 | 0.6 | 120 | -0.039412 | 0 | 2.625 | 2.6644 | 2.6644 | available | 0.85
139 | SS 35/10 Snagost | 2 х 4,0 | 1.17 | 0.05 | 10 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | available | 138 | SS 35/10 Snagost | 2 х 4,0 | 0.028125 | 1.1981 | 0.05 | 10 | 1.1481 | 0 | 4.2 | 3.0519 | 3.0519 | available | 0.96
140 | SS 35/10 SOM | 1,6 + 4,0 | 1.01 | 0.08 | 10 | 0.93 | 0 | 1.68 | 0.75 | 0.75 | available | 139 | SS 35/10 SOM | 1,6 + 4,0 | 0.09759 | 1.1076 | 0.08 | 10 | 1.0276 | 0 | 1.68 | 0.65241 | 0.65241 | available | 0.83
141 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.92 | 0.69 | 120 | 0.23 | 0 | 3.36 | 3.13 | 3.13 | available | 140 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.092941 | 1.0129 | 0.69 | 120 | 0.32294 | 0 | 3.36 | 3.0371 | 3.0371 | available | 0.85
142 | SS 35/10 Stakanovo | 2 х 2,5 | 1.02 | 0.58 | 80 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 141 | SS 35/10 Stakanovo | 2 х 2,5 | 0.059756 | 1.0798 | 0.58 | 80 | 0.49976 | 0 | 2.625 | 2.1252 | 2.1252 | available | 0.82
143 | SS 35/10 Starkovo | 2 х 1,6 | 0.42 | 0.2 | 80 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 142 | SS 35/10 Starkovo | 2 х 1,6 | 0.017647 | 0.43765 | 0.2 | 80 | 0.23765 | 0 | 1.68 | 1.4424 | 1.4424 | available | 0.85
144 | CC 35/10 Starshee | 2 х 1,6 | 0.2 | 0.2 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 143 | CC 35/10 Starshee | 2 х 1,6 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 0.85
145 | SS 35/10 Teplitsy | 2 х 4,0 | 1.1 | 1.08 | 45 | 0.02 | 0 | 4.2 | 4.18 | 4.18 | available | 144 | SS 35/10 Teplitsy | 2 х 4,0 | 0.076471 | 1.1765 | 1.08 | 45 | 0.096471 | 0 | 4.2 | 4.1035 | 4.1035 | available | 0.85
146 | SS 35/10 Turovka | 2 х 2,5 | 0.44 | 0.6 | 120 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | available | 145 | SS 35/10 Turovka | 2 х 2,5 | 0.12941 | 0.56941 | 0.6 | 120 | -0.030588 | 0 | 2.625 | 2.6556 | 2.6556 | available | 0.85
147 | SS 35/10 Uspenka | 2 х 2,5 | 1.23 | 1 | 80 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 146 | SS 35/10 Uspenka | 2 х 2,5 | 0.31176 | 1.5418 | 1 | 80 | 0.54176 | 0 | 2.625 | 2.0832 | 2.0832 | available | 0.85
148 | SS 35/6 Tsentralnaya | 2 х 40,0 | 21.2 | 5 |  | 16.2 | 0 | 42 | 25.8 | 25.8 | available | 147 | SS 35/6 Tsentralnaya | 2 х 40,0 | 0 | 21.2 | 5 |  | 16.2 | 0 | 42 | 25.8 | 25.8 | available | 0.91
149 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.25 | 0.5 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | available | 148 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.011765 | 0.26176 | 0.5 | 120 | -0.23824 | 0 | 2.625 | 2.8632 | 2.8632 | available | 0.85
150 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.34 | 0.21 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available | 149 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.0061728 | 0.34617 | 0.21 | 80 | 0.13617 | 0 | 2.625 | 2.4888 | 2.4888 | available | 0.81
151 | SS 35/10 Shipy | 2 х 2,5 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 150 | SS 35/10 Shipy | 2 х 2,5 | 0 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 0.83
152 | SS 35/10 Elevator | 4,0 + 6,3 | 1.22 | 0.6 | 120 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | available | 151 | SS 35/10 Elevator | 4,0 + 6,3 | 0.046512 | 1.2665 | 0.6 | 120 | 0.66651 | 0 | 4.2 | 3.5335 | 3.5335 | available | 0.86
153 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.74 | 4.7 | 80 | 4.04 | 0 | 10.5 | 6.46 | 6.46 | available | 152 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 4.191 | 12.931 | 4.7 | 80 | 8.231 | 0 | 10.5 | 2.269 | 2.269 | available | 0.89
154 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 3.11 | 3.9 | 120 | -0.79 | 0 | 2.625 | 3.415 | 3.415 | available | 153 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 0.33882 | 3.4488 | 3.9 | 120 | -0.45118 | 0 | 2.625 | 3.0762 | 3.0762 | available | 0.85
| TOTAL: | 3311.2 | 701.21 | 795.42 | [5 empty] | 1369.655 |  | 2: TOTAL:; 3: 3311.2; 4: 236.246; 5: 937.456; MVA 6: 796.22; Min 12: 1253.1177
| deficit | [8 empty] | -7.2 |  | 2: deficit; Min 12: -52.5738
| proficit | [8 empty] | 1362.455 |  | 2: proficit; Min 12: 1200.5437
|  | *Note: the power shortage at the substation Vysokaya due to transfer loads from the substation Central | [9 empty] | 3: *Note: The facilities are included in the Investment Program for 2012-2017.
|  | and will be removed after commissioning of SWG-10kV at substation Central. | [9 empty] | 3: Power shortage will be removed after the reconstruction and replacement of transformers with higher power.
|  |  | Deputy director for technical policy - | [8 empty] | 4: Deputy director for technical policy -
|  |  | Chief engineer | [6 empty] | A.N. Rudnevsky |  | 4: Chief engineer; Min 11: A.N. Rudnevsky

## Total current deficit
The list of closed supply centers of IDGC of Centre - Kurskenergo division in winter 2011 (current deficit of capacity)
Item # | Name of supply center, voltage class |  | Current deficit, MVA
Kurskenergo
1. | SS 110/10 Vysokaya* | 2*16 | -7.2
Total current deficit (winter 2011) |  |  | -7.2
*Note: Power shortage at SS Vysokaya is due to transfer of load
from SS Central and will be removed after the trnsfer of load by customers

## Total expected deficit
The list of closed supply centers of IDGC of Centre - Kurskenergo division with expected load taking into account new connections and other development of the electical networks (expected deficit of capacity) for January 2011
Item # | Name of supply center, voltage class | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Expected deficit, MVA
Kurskenergo
1 | SS 110/10 Beketovo | 1х6,3 | -1.245
2 | SS 35/10 Bykovo | 1х4 | -3.559
3 | SS 35/10 Vasilevka | 1х2,5 | -0.559
4 | SS 35/10 Water storage | 1х4 | -7.09
5 | SS 35/10 Irrigating | 1х4 | -2.221
6 | SS 35/10 Pristen | 1х4 | -7.582
7 | SS 35/10 Yasenki | 1х2,5 | -2.623
8 | SS 110/10 Vysokaya | 2х16 | -7.2
9 | SS 110/35/10 Gorshechnoye | 10+16 | -7.676
10 | SS 110/35/10 Kamyshi | 2х6,3 | -8.426
11 | SS 35/10 Korenevo | 4,0 + 6,3 | -4.3931
Total expected deficit (winter 2012) |  |  | -52.5741
*Note: The facilities are included in the Investment Program for 2012-2017.
Power shortage will be removed after the reconstruction and replacement of transformers with higher power.