## Kursk
Transmission capacity of supply centres of IDGC of Center - Kurskenergo following the winter peak load measurements in 2011 | [11 empty] | Transmission capacity of supply centres of IDGC of Center - Kurskenergo following the winter peak load measurements in 2011
[9 empty] | table 1 | [12 empty] | table 2
Item # | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note | cosφ
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
1 | SS 110/35/10 Artyukhovka | 6.3 | 2.32 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.98 | 0.53 | available | 1 | SS 110/35/10 Artyukhovka | 6.3 | 0.033437 | 2.3534 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.9466 | 0.51235 | available | 0.95
| Nom. capacity MV, MVA | 6.3 | 1.77 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 0.53 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.017647 | 1.7876 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 0.51235
| Nom. capacity MV, MVA | 6.3 | 0.55 | 4 | 1 day and night | 4 | 0 | 4 | 3.45 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.015789 | 0.56579 | 4 | 1 day and night | 4 | 0 | 4 | 3.4342
2 | SS 110/10 Beketovo | 6.3 | 0.44 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.71 | 1.71 | available | 2 | SS 110/10 Beketovo | 6.3 | 2.9548 | 3.3948 | 2.15 | 120 | 2.15 | 0 | 2.15 | -1.2448 | -1.2448 | unavailable | 0.84
3 | SS 110/35/10 Besedino | 6.3 | 2.85 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.95 | 1.04 | available | 3 | SS 110/35/10 Besedino | 6.3 | 0.50588 | 3.3559 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.4441 | 0.60235 | available | 0.85
| Nom. capacity MV, MVA | 6.3 | 0.59 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.91 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.068235 | 0.65824 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.8418
| Nom. capacity LV, MVA | 6.3 | 2.26 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.04 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.43765 | 2.6976 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.60235
4 | SS 110/10 Voskhod | 10 | 0.8 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.7 | 1.7 | available | 4 | SS 110/10 Voskhod | 10 | 0.16905 | 0.96905 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.531 | 1.531 | available | 0.84
5 | SS 110/35/10 Zhuryatino | 6.3 | 0.8 | 6 | 1 day and night | 6 | 0 | 6 | 5.2 | 1.5 | available | 5 | SS 110/35/10 Zhuryatino | 6.3 | 0.019277 | 0.81928 | 6 | 1 day and night | 6 | 0 | 6 | 5.1807 | 1.4807 | available | 0.83
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.8 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.5 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.019277 | 0.81928 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.4807
6 | SS 110/10 Zabelye | 2.5 | 0.31 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.84 | 1.84 | available | 6 | SS 110/10 Zabelye | 2.5 | 0.01039 | 0.32039 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8296 | 1.8296 | available | 0.77
7 | SS 110/10 Ivnitsa | 6.3 | 0.4 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.27 | 0.27 | available | 7 | SS 110/10 Ivnitsa | 6.3 | 0 | 0.4 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.27 | 0.27 | available | 0.85
8 | SS 110/35/10 Lachinovo | 10 | 0.98 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 4.15 | 0.93 | available | 8 | SS 110/35/10 Lachinovo | 10 | 0.029059 | 1.0091 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 4.1209 | 0.91353 | available | 0.85
| Nom. capacity MV, MVA | 10 | 0.38 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 3.22 |  |  |  | Nom. capacity MV, MVA | 10 | 0.012588 | 0.39259 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 3.2074
| Nom. capacity LV, MVA | 10 | 0.6 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.93 |  |  |  | Nom. capacity LV, MVA | 10 | 0.016471 | 0.61647 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.91353
9 | SS 110/10 Malaya Loknya | 10 | 1.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.2 | 0.2 | available | 9 | SS 110/10 Malaya Loknya | 10 | 0.021429 | 1.2214 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.17857 | 0.17857 | available | 0.84
10 | SS 110/35/10 Maritsa | 2.5 | 1.6 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.32 | 0.32 | available | 10 | SS 110/35/10 Maritsa | 6.3 | 0.012245 | 1.6122 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.30776 | 0.30776 | available | 0.98
11 | SS 110/10 Semyonovskaya | 2.5 | 0.3 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.1 | 1.1 | available | 11 | SS 110/10 Semyonovskaya | 2.5 | 0.011765 | 0.31176 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.0882 | 1.0882 | available | 0.85
12 | SS 110/35/10 Troitskaya | 10 | 2.65 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 4.85 | 0.7 | available | 12 | SS 110/35/10 Troitskaya | 10 | 0.82706 | 3.4771 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 4.0229 | 0.66941 | available | 0.85
| Nom. capacity MV, MVA | 10 | 2.25 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 4.15 |  |  |  | Nom. capacity MV, MVA | 10 | 0.79647 | 3.0465 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 3.3535
| Nom. capacity LV, MVA | 10 | 0.4 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.7 |  |  |  | Nom. capacity LV, MVA | 10 | 0.030588 | 0.43059 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.66941
13 | SS 35/10 Avtodor | 2.5 | 0.34 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.46 | 0.46 | available | 13 | SS 35/10 Avtodor | 2.5 | 0.017647 | 0.35765 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.44235 | 0.44235 | available | 0.85
14 | SS 35/10 Agronom | 1.8 | 0.5 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.45 | 0.45 | available | 14 | SS 35/10 Agronom | 1.8 | 0.22796 | 0.72796 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.22204 | 0.22204 | available | 0.93
15 | SS 35/10 Akimovka | 2.5 | 0.3 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.38 | 0.38 | available | 15 | SS 35/10 Akimovka | 2.5 | 0.018391 | 0.31839 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.36161 | 0.36161 | available | 0.87
16 | SS 35/10 Alekseevka | 2.5 | 0.2 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.23 | 1.23 | available | 16 | SS 35/10 Alekseevka | 2.5 | 0.034884 | 0.23488 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1951 | 1.1951 | available | 0.86
17 | SS 35/10 Afanasyevka (WPS) | 4 | 0.61 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.73 | 0.73 | available | 17 | SS 35/10 Afanasyevka (WPS) | 4 | 0.031915 | 0.64191 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.69809 | 0.69809 | available | 0.94
18 | SS 35/10 B. Gneushevo | 2.5 | 0.74 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.22 | 0.22 | available | 18 | SS 35/10 B. Gneushevo | 2.5 | 0 | 0.74 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.22 | 0.22 | available | 0.88
19 | SS 35/10 B.Soldatskoe1 | 3.2 | 0.2 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.63 | 2.63 | available | 19 | SS 35/10 B.Soldatskoe1 | 3.2 | 0.57294 | 0.77294 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.0571 | 2.0571 | available | 0.85
20 | SS 35/10 Banishchi | 1.6 | 0.43 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.21 | 0.21 | available | 20 | SS 35/10 Banishchi | 1.6 | 0.069149 | 0.49915 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.14085 | 0.14085 | available | 0.94
21 | SS 35/10 Baranovo | 4 | 0.15 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.28 | 1.28 | available | 21 | SS 35/10 Baranovo | 4 | 0.69241 | 0.84241 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58759 | 0.58759 | available | 0.79
22 | SS 35/10 Belgorodka | 2.5 | 0.27 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.88 | 1.88 | available | 22 | SS 35/10 Belgorodka | 2.5 | 0.065217 | 0.33522 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8148 | 1.8148 | available | 0.69
23 | SS 35/10 Belitsa | 4 | 0.55 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.21 | 1.21 | available | 23 | SS 35/10 Belitsa | 4 | 0.094681 | 0.64468 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.1153 | 1.1153 | available | 0.94
24 | SS 35/10 Biryukovka | 1.6 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available | 24 | SS 35/10 Biryukovka | 1.6 | 0.017647 | 0.41765 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.34235 | 0.34235 | available | 0.85
25 | SS 35/10 Bobrovka | 1.6 | 0.22 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.45 | 0.45 | available | 25 | SS 35/10 Bobrovka | 1.6 | 0.016471 | 0.23647 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.43353 | 0.43353 | available | 0.85
26 | SS 35/10 Bobrovo | 2.5 | 0.49 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.27 | 0.27 | available | 26 | SS 35/10 Bobrovo | 2.5 | 0.02809 | 0.51809 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.24191 | 0.24191 | available | 0.89
27 | SS 35/10 Budki | 1 | 0.24 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.5 | 0.5 | available | 27 | SS 35/10 Budki | 1 |  | 0.24 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.5 | 0.5 | available | 0.89
28 | SS 35/10 Bukreevka (CPS) | 1.8 | 0.52 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.08 | 1.08 | available | 28 | SS 35/10 Bukreevka (CPS) | 1.8 | 0.042353 | 0.56235 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.0376 | 1.0376 | available | 0.85
29 | SS 35/10 Bukreevka (WPS) | 1.6 | 0.37 | 1 | 1 day and night | 1 | 0 | 1 | 0.63 | 0.63 | available | 29 | SS 35/10 Bukreevka (WPS) | 1.6 | 0.014737 | 0.38474 | 1 | 1 day and night | 1 | 0 | 1 | 0.61526 | 0.61526 | available | 0.95
30 | SS 35/10 Burtsevka | 1.6 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | available | 30 | SS 35/10 Burtsevka | 1.6 | 0 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | available | 0.8
31 | SS 35/10 Bykovo | 4 | 0.51 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.92 | 0.92 | available | 31 | SS 35/10 Bykovo | 4 | 4.4835 | 4.9935 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | -3.5635 | -3.5635 | unavailable | 0.82
32 | SS 35/10 V. Shchigor | 2.5 | 0.13 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.02 | 2.02 | available | 32 | SS 35/10 V. Shchigor | 2.5 | 0.035294 | 0.16529 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.9847 | 1.9847 | available | 0.85
33 | SS 35/10 Vanino | 2.5 | 0.38 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.42 | 0.42 | available | 33 | SS 35/10 Vanino | 2.5 | 0.032941 | 0.41294 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.38706 | 0.38706 | available | 0.85
34 | SS 35/10 Vasilyevka | 2.5 | 0.5 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.55 | 0.55 | available | 34 | SS 35/10 Vasilyevka | 2.5 | 1.109 | 1.609 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | -0.559 | -0.559 | unavailable | 0.95
35 | SS 35/10 Water storage | 4 | 1.35 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | 1.37 | 1.37 | available | 35 | SS 35/10 Water storage | 4 | 5.6859 | 7.0359 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | -4.3159 | -4.3159 | unavailable | 0.85
36 | SS 35/10 Volokonsk | 2.5 | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available | 36 | SS 35/10 Volokonsk | 2.5 |  | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available | 0.93
37 | SS 35/10 Vorobyovka | 2.5 | 0.16 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.74 | 0.74 | available | 37 | SS 35/10 Vorobyovka | 2.5 | 0.014118 | 0.17412 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.72588 | 0.72588 | available | 0.85
38 | SS 35/10 Voronok | 4 | 0.68 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.42 | 1.42 | available | 38 | SS 35/10 Voronok | 4 | 0.5033 | 1.1833 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 0.9167 | 0.9167 | available | 0.91
39 | SS 35/10 Vyazovoe | 2.5 | 0.27 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.88 | 1.88 | available | 39 | SS 35/10 Vyazovoe | 2.5 | 0.017647 | 0.28765 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8624 | 1.8624 | available | 0.85
40 | SS 35/10 Gakhovo | 2.5 | 0.22 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.58 | 1.58 | available | 40 | SS 35/10 Gakhovo | 2.5 | 0.0082353 | 0.22824 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.5718 | 1.5718 | available | 0.85
41 | SS 35/10 Generalshino | 2.5 | 0.13 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.37 | 1.37 | available | 41 | SS 35/10 Generalshino | 2.5 | 0.16235 | 0.29235 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.2076 | 1.2076 | available | 0.85
42 | SS 35/10 Glazovo | 2.5 | 0.9 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.6 | 0.6 | available | 42 | SS 35/10 Glazovo | 2.5 | 0 | 0.9 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.6 | 0.6 | available | 0.95
43 | SS 35/10 Glebovo | 2.5 | 0.09 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.31 | 1.31 | available | 43 | SS 35/10 Glebovo | 2.5 | 0.058824 | 0.14882 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2512 | 1.2512 | available | 0.85
44 | SS 35/10 Gordeevka | 1.6 | 0.18 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.52 | 0.52 | available | 44 | SS 35/10 Gordeevka | 1.6 | 0.014286 | 0.19429 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.50571 | 0.50571 | available | 0.98
45 | SS 35/10 Gorodensk | 1.6 | 0.61 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.15 | 0.15 | available | 45 | SS 35/10 Gorodensk | 1.6 | 0.016667 | 0.62667 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.13333 | 0.13333 | available | 0.9
46 | SS 35/10 Goryainovo | 2.5 | 0.5 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.6 | 0.6 | available | 46 | SS 35/10 Goryainovo | 2.5 | 0.034118 | 0.53412 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.56588 | 0.56588 | available | 0.85
47 | SS 35/10 12th State stud farm | 2.5 | 0.33 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1 | 1.1 | available | 47 | SS 35/10 12th State stud farm | 2.5 | 0.012588 | 0.34259 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0874 | 1.0874 | available | 0.85
48 | SS 35/10 Grayvoronka | 2.5 | 0.22 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.21 | 1.21 | available | 48 | SS 35/10 Grayvoronka | 2.5 | 0.046667 | 0.26667 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1633 | 1.1633 | available | 0.75
49 | SS 35/10 Grinyovka | 2.5 | 0.22 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.63 | 2.63 | available | 49 | SS 35/10 Grinyovka | 2.5 | 0.027059 | 0.24706 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.6029 | 2.6029 | available | 0.85
50 | SS 35/10 Gustomoy | 1.6 | 0.18 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.76 | 0.76 | available | 50 | SS 35/10 Gustomoy | 1.6 | 0.045918 | 0.22592 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.71408 | 0.71408 | available | 0.98
51 | SS 35/10 Daryino | 2.5 | 0.4 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4 | 1.4 | available | 51 | SS 35/10 Daryino | 2.5 | 0.021176 | 0.42118 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.3788 | 1.3788 | available | 0.85
52 | SS 35/10 Demyakino | 2.5 | 0.56 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.24 | 0.24 | available | 52 | SS 35/10 Demyakino | 2.5 | 0.056471 | 0.61647 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.18353 | 0.18353 | available | 0.85
53 | SS 35/10 Efrosimovka | 1.8 | 0.23 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.84 | 0.84 | available | 53 | SS 35/10 Efrosimovka | 1.8 | 0.034118 | 0.26412 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.80588 | 0.80588 | available | 0.85
54 | SS 35/10 Zhdanovo | 2.5 | 0.26 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.59 | 0.59 | available | 54 | SS 35/10 Zhdanovo | 2.5 | 0.030588 | 0.29059 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.55941 | 0.55941 | available | 0.85
55 | SS 35/10 Zashchitnoe | 1.6 | 0.36 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.79 | 1.79 | available | 55 | SS 35/10 Zashchitnoe | 1.6 | 0.68652 | 1.0465 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.1035 | 1.1035 | available | 0.89
56 | SS 35/10 Zvannoe | 2.5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 56 | SS 35/10 Zvannoe | 2.5 | 0.042697 | 0.5927 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.2473 | 0.2473 | available | 0.89
57 | SS 35/10 Znamenka | 1.8 | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | available | 57 | SS 35/10 Znamenka | 1.8 | 0.013415 | 1.0234 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.1266 | 1.1266 | available | 0.82
58 | SS 35/10 Iskra | 2.5 | 0.21 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.37 | 0.37 | available | 58 | SS 35/10 Iskra | 2.5 | 0.068235 | 0.27824 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.30176 | 0.30176 | available | 0.85
59 | SS 35/10 Kazanka | 4 | 0.49 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.31 | 0.31 | available | 59 | SS 35/10 Kazanka | 4 | 0.028235 | 0.51824 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.28176 | 0.28176 | available | 0.85
60 | SS 35/10 Kalinovka (new) | 2.5 | 0.24 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.56 | 1.56 | available | 60 | SS 35/10 Kalinovka (new) | 2.5 | 0.070588 | 0.31059 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4894 | 1.4894 | available | 0.85
61 | SS 35/10 Karyzh | 1.6 | 0.31 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33 | 0.33 | available | 61 | SS 35/10 Karyzh | 1.6 | 0.24045 | 0.55045 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.089551 | 0.089551 | available | 0.89
62 | SS 35/10 Kitaevka | 1.6 | 0.39 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.35 | 0.35 | available | 62 | SS 35/10 Kitaevka | 1.6 | 0 | 0.39 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.35 | 0.35 | available | 0.85
63 | SS 35/10 Kobylki | 2.5 | 0.61 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.92 | 0.92 | available | 63 | SS 35/10 Kobylki | 2.5 | 0.15843 | 0.76843 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.76157 | 0.76157 | available | 0.89
64 | SS 35/10 Kolontaevka | 2.5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 64 | SS 35/10 Kolontaevka | 2.5 | 0 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 0.98
65 | SS 35/10 Kondratovka | 1.8 | 0.55 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.87 | 0.87 | available | 65 | SS 35/10 Kondratovka | 1.8 | 0.025532 | 0.57553 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.84447 | 0.84447 | available | 0.94
66 | SS 35/10 Korovyakovka | 1.6 | 0.45 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.31 | 0.31 | available | 66 | SS 35/10 Korovyakovka | 1.6 | 0.0078652 | 0.45787 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.30213 | 0.30213 | available | 0.89
67 | SS 35/10 Lezhenki | 2.5 | 0.14 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.29 | 1.29 | available | 67 | SS 35/10 Lezhenki | 2.5 | 0 | 0.14 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.29 | 1.29 | available | 0.76
68 | SS 35/10 Leninskaya | 1.8 | 0.36 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.47 | 0.47 | available | 68 | SS 35/10 Leninskaya | 1.8 | 0.054118 | 0.41412 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.41588 | 0.41588 | available | 0.85
69 | SS 35/10 Lobazovka | 2.5 | 0.68 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.42 | 0.42 | available | 69 | SS 35/10 Lobazovka | 2.5 | 0.017647 | 0.69765 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.40235 | 0.40235 | available | 0.85
70 | SS 35/10 Lugovka | 1.6 | 0.5 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.79 | 0.79 | available | 70 | SS 35/10 Lugovka | 1.6 | 0.072247 | 0.57225 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.71775 | 0.71775 | available | 0.89
71 | SS 35/10 Lyubava | 6.3 | 0.37 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.78 | 0.78 | available | 71 | SS 35/10 Lyubava | 6.3 | 0.054255 | 0.42426 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.72574 | 0.72574 | available | 0.94
72 | SS 35/10 Lyubimovka-1 | 3.2 | 0 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.96 | 0.96 | available | 72 | SS 35/10 Lyubimovka-1 | 3.2 | 0.0058824 | 0.0058824 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.95412 | 0.95412 | available | 0.85
73 | SS 35/10 M. Kamenets | 1.6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 73 | SS 35/10 M. Kamenets | 1.6 | 0.14512 | 0.74512 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.35488 | 0.35488 | available | 0.82
74 | SS 35/10 М. Gneushevo | 4 | 0.8 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.48 | 0.48 | available | 74 | SS 35/10 М. Gneushevo | 4 | 0.011236 | 0.81124 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.46876 | 0.46876 | available | 0.89
75 | SS 35/10 М. Kryuki | 2.5 | 0.3 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.89 | 0.89 | available | 75 | SS 35/10 М. Kryuki | 2.5 | 0.018987 | 0.31899 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.87101 | 0.87101 | available | 0.79
76 | SS 35/10 Markovo | 2.5 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | available | 76 | SS 35/10 Markovo | 2.5 | 0 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | available | 0.89
77 | SS 35/10 Marmyzhi | 2.5 | 0.43 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 0.9 | 0.9 | available | 77 | SS 35/10 Marmyzhi | 2.5 | 0 | 0.43 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 0.9 | 0.9 | available | 0.94
78 | SS 35/10 Melovoe | 4 | 0.7 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.45 | 1.45 | available | 78 | SS 35/10 Melovoe | 4 | 0.037778 | 0.73778 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.4122 | 1.4122 | available | 0.9
79 | SS 35/10 Mokva | 4 | 0.65 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.5 | 1.5 | available | 79 | SS 35/10 Mokva | 4 | 0.27647 | 0.92647 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.2235 | 1.2235 | available | 0.85
80 | SS 35/10 Mokrusheno | 1.6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 80 | SS 35/10 Mokrusheno | 1.6 | 0.035789 | 0.63579 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.46421 | 0.46421 | available | 0.95
81 | SS 35/10 Molotychi | 2.5 | 0.05 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.85 | 0.85 | available | 81 | SS 35/10 Molotychi | 2.5 | 0 | 0.05 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.85 | 0.85 | available | 0.85
82 | SS 35/10 Mochaki | 2.5 | 0.01 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.06 | 1.06 | available | 82 | SS 35/10 Mochaki | 2.5 | 0.0023529 | 0.012353 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.0576 | 1.0576 | available | 0.85
83 | SS 35/10 N. Vladimirovka | 2.5 | 0.1 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.2 | 4.2 | available | 83 | SS 35/10 N. Vladimirovka | 2.5 | 0 | 0.1 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.2 | 4.2 | available | 0.87
84 | SS 35/10 N. Gurovo | 4 | 0.42 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.73 | 1.73 | available | 84 | SS 35/10 N. Gurovo | 4 | 0 | 0.42 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.73 | 1.73 | available | 0.76
85 | SS 35/10 Nadeyka | 2.5 | 0.07 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.33 | 1.33 | available | 85 | SS 35/10 Nadeyka | 2.5 | 0 | 0.07 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.33 | 1.33 | available | 0.85
86 | SS 35/10 Niva | 2.5 | 0.4 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.16 | 1.16 | available | 86 | SS 35/10 Niva | 2.5 | 0.21176 | 0.61176 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 0.94824 | 0.94824 | available | 0.85
87 | SS 35/10 Olgovka | 2.5 | 0.43 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.54 | 0.54 | available | 87 | SS 35/10 Olgovka | 2.5 | 0 | 0.43 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.54 | 0.54 | available | 0.98
88 | SS 35/10 Olkhovatka | 4 | 0.4 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.24 | 0.24 | available | 88 | SS 35/10 Olkhovatka | 4 | 0.021176 | 0.42118 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.21882 | 0.21882 | available | 0.85
89 | SS 35/10 Orositelnaya | 4 | 1.96 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 1.01 | 1.01 | available | 89 | SS 35/10 Orositelnaya | 4 | 3.6953 | 5.6553 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | -2.6853 | -2.6853 | unavailable | 0.85
90 | SS 35/10 Peny-2 | 2.5 | 0.6 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.72 | 1.72 | available | 90 | SS 35/10 Peny-2 | 2.5 | 0.057143 | 0.65714 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.6629 | 1.6629 | available | 0.77
91 | SS 35/10 Perestuplino (old) | 2.5 | 0.13 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.27 | 1.27 | available | 91 | SS 35/10 Perestuplino (old) | 2.5 |  | 0.13 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.27 | 1.27 | available | 0.85
92 | SS 35/10 Perestuplino (new) | 2.5 | 0.26 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.14 | 1.14 | available | 92 | SS 35/10 Perestuplino (new) | 2.5 | 0.0058824 | 0.26588 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.1341 | 1.1341 | available | 0.85
93 | SS 35/10 Petrovo | 6.3 | 0.46 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.69 | 1.69 | available | 93 | SS 35/10 Petrovo | 6.3 | 0.28912 | 0.74912 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.4009 | 1.4009 | available | 0.92
94 | SS 35/10 Petrovskaya | 2.5 | 0.02 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.72 | 0.72 | available | 94 | SS 35/10 Petrovskaya | 2.5 | 0.011765 | 0.031765 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.70824 | 0.70824 | available | 0.85
95 | SS 35/10 Pokrovskoe | 2.5 | 0.24 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.91 | 1.91 | available | 95 | SS 35/10 Pokrovskoe | 2.5 | 0 | 0.24 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.91 | 1.91 | available | 0.83
96 | SS 35/10 Prilepy | 1.6 | 0.38 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.77 | 1.77 | available | 96 | SS 35/10 Prilepy | 1.6 | 0.030588 | 0.41059 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.7394 | 1.7394 | available | 0.85
97 | SS 35/10 Pristen | 4 | 2.2 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.1 | 1.1 | available | 97 | SS 35/10 Pristen | 4 | 8.7 | 10.9 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | -7.6 | -7.6 | unavailable | 0.85
98 | SS 35/10 R. Budy 35/10 | 4 | 0 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.74 | 0.74 | available | 98 | SS 35/10 R. Budy 35/10 | 4 | 0.11882 | 0.11882 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.62118 | 0.62118 | available | 0.85
99 | SS 35/10 Reut | 2.5 | 0.04 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.06 | 1.06 | available | 99 | SS 35/10 Reut | 2.5 | 0.035294 | 0.075294 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.0247 | 1.0247 | available | 0.85
100 | SS 35/10 Rovenka | 1.6 | 0.16 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.44 | 1.44 | available | 100 | SS 35/10 Rovenka | 1.6 | 0.022727 | 0.18273 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.4173 | 1.4173 | available | 0.88
101 | SS 35/10 Rodina (NPC) | 2.5 | 0.09 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.61 | 0.61 | available | 101 | SS 35/10 Rodina (NPC) | 2.5 | 0 | 0.09 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.61 | 0.61 | available | 0.85
102 | SS 35/10 Rodina (EPS) | 4 | 0.35 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.95 | 1.95 | available | 102 | SS 35/10 Rodina (EPS) | 4 | 0.43882 | 0.78882 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.5112 | 1.5112 | available | 0.85
103 | SS 35/10 Rubanshchina | 2.5 | 0.4 | 1.41 | 1 day and night | 1.41 | 0 | 1.41 | 1.01 | 1.01 | available | 103 | SS 35/10 Rubanshchina | 2.5 | 0.91236 | 1.3124 | 1.41 | 1 day and night | 1.41 | 0 | 1.41 | 0.09764 | 0.09764 | available | 0.89
104 | SS 35/10 Rusanovo | 1.8 | 0.29 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.14 | 1.14 | available | 104 | SS 35/10 Rusanovo | 1.8 | 0.017647 | 0.30765 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1224 | 1.1224 | available | 0.85
105 | SS 35/10 Ryshkovo | 2.5 | 0.32 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.62 | 0.62 | available | 105 | SS 35/10 Ryshkovo | 2.5 | 0.070588 | 0.39059 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.54941 | 0.54941 | available | 0.85
106 | SS 35/10 Ryazanovo | 1.6 | 0.61 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.54 | 0.54 | available | 106 | SS 35/10 Ryazanovo | 1.6 | 0 | 0.61 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.54 | 0.54 | available | 0.85
107 | SS 35/10 Sazanovka | 2.5 | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | available | 107 | SS 35/10 Sazanovka | 2.5 | 0.0035294 | 0.30353 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.94647 | 0.94647 | available | 0.85
108 | SS 35/10 Sergievka | 2.5 | 0.53 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.17 | 2.17 | available | 108 | SS 35/10 Sergievka | 2.5 | 0.030588 | 0.56059 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.1394 | 2.1394 | available | 0.85
109 | SS 35/10 Sokolye | 2.5 | 0.3 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.13 | 1.13 | available | 109 | SS 35/10 Sokolye | 2.5 | 0.017647 | 0.31765 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.1124 | 1.1124 | available | 0.85
110 | SS 35/10 Solntsevo | 2.5 | 0.87 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.89 | 0.89 | available | 110 | SS 35/10 Solntsevo | 2.5 | 0.06 | 0.93 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.83 | 0.83 | available | 0.85
111 | SS 35/10 Spasskoe | 1.6 | 0.33 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.77 | 0.77 | available | 111 | SS 35/10 Spasskoe | 1.6 | 0.016471 | 0.34647 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.75353 | 0.75353 | available | 0.85
112 | SS 35/10 Sr. Olshanka | 2.5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | available | 112 | SS 35/10 Sr. Olshanka | 4 | 1.8982 | 2.0982 | 2.2 | 1 day and night | 2.2 | 0 | 2.2 | 0.10176 | 0.10176 | available | 0.85
113 | SS 35/10 Streletskaya | 2.5 | 0.46 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.84 | 0.84 | available | 113 | SS 35/10 Streletskaya | 2.5 | 0.1186 | 0.5786 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.7214 | 0.7214 | available | 0.86
114 | SS 35/10 Subbotino | 2.5 | 0.6 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.74 | 0.74 | available | 114 | SS 35/10 Subbotino | 2.5 | 0.002381 | 0.60238 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.73762 | 0.73762 | available | 0.84
115 | SS 35/10 Sukhaya | 1.6 | 0.31 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.4 | 0.4 | available | 115 | SS 35/10 Sukhaya | 1.6 | 0 | 0.31 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.4 | 0.4 | available | 0.91
116 | SS 35/10 Telmana | 2.5 | 0.49 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.66 | 0.66 | available | 116 | SS 35/10 Telmana | 2.5 | 0.45625 | 0.94625 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.20375 | 0.20375 | available | 0.96
117 | SS 35/10 Terebuzh | 2.5 | 0.35 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.08 | 1.08 | available | 117 | SS 35/10 Terebuzh | 2.5 | 0.036735 | 0.38673 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0433 | 1.0433 | available | 0.98
118 | SS 35/10 Fateevka | 2.5 | 0.07 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.63 | 0.63 | available | 118 | SS 35/10 Fateevka | 2.5 | 0.0094118 | 0.079412 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.62059 | 0.62059 | available | 0.85
119 | SS 35/10 Fentisovo | 1.6 | 0.29 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.43 | 1.43 | available | 119 | SS 35/10 Fentisovo | 1.6 | 0.0047059 | 0.29471 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.4253 | 1.4253 | available | 0.85
120 | SS 35/10 Chapaevskaya | 2.5 | 0.09 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.01 | 1.01 | available | 120 | SS 35/10 Chapaevskaya | 2.5 | 0 | 0.09 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 1.01 | 1.01 | available | 0.85
121 | SS 35/10 Chemerki | 1.6 | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available | 121 | SS 35/10 Chemerki | 1.6 |  | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available | 0.85
122 | SS 35/10 Chizhovka | 1.6 | 0.3 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.13 | 1.13 | available | 122 | SS 35/10 Chizhovka | 1.6 | 0.052941 | 0.35294 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.0771 | 1.0771 | available | 0.85
123 | SS 35/10 Shatilovka | 2.5 | 0.11 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.32 | 1.32 | available | 123 | SS 35/10 Shatilovka | 2.5 | 0 | 0.11 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.32 | 1.32 | available | 0.81
124 | SS 35/10 Sheptukhovka | 2.5 | 0.74 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.73 | 0.73 | available | 124 | SS 35/10 Sheptukhovka | 2.5 | 0.04 | 0.78 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.69 | 0.69 | available | 0.85
125 | SS 35/10 Shuklino | 2.5 | 0.02 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.83 | 0.83 | available | 125 | SS 35/10 Shuklino | 2.5 |  | 0.02 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.83 | 0.83 | available | 0.85
126 | SS 35/10 Elevator | 6.3 | 0.19 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.41 | 0.41 | available | 126 | SS 35/10 Elevator | 6.3 | 0 | 0.19 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.41 | 0.41 | available | 0.85
127 | SS 35/10 Yankovo | 1.6 | 0.3 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.34 | 0.34 | available | 127 | SS 35/10 Yankovo | 1.6 | 0.0094737 | 0.30947 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33053 | 0.33053 | available | 0.95
128 | SS 35/10 Yasenki | 2.5 | 0.48 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.67 | 1.67 | available | 128 | SS 35/10 Yasenki | 2.5 | 4.361 | 4.841 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -2.691 | -2.691 | unavailable | 0.83
129 | SS 110/6 Akkumulyatornaya | 25+25 | 11.06 | 0 | 0 | 11.06 | 0 | 26.25 | 15.19 | 15.19 | available | 129 | SS 110/6 Akkumulyatornaya | 25+25 |  | 11.06 | 0 | 0 | 11.06 | 0 | 26.25 | 15.19 | 15.19 | available | 0.89
130 | SS 110/10 ARZ | 6,3+10 | 2.6 | 0.9 | 45 | 1.7 | 0 | 6.615 | 4.915 | 4.915 | available | 130 | SS 110/10 ARZ | 6,3+10 | 0.019048 | 2.619 | 0.9 | 45 | 1.719 | 0 | 6.615 | 4.896 | 4.896 | available | 0.84
131 | SS 110/35/10 Atomgrad | 25+25 | 11.35 | 20.2 | 120 | -8.85 | 0 | 26.25 | 35.1 | 27.95 | available | 131 | SS 110/35/10 Atomgrad | 25+25 | 1.0235 | 12.3735 | 20.2 | 120 | -7.8265 | 0 | 26.25 | 34.0765 | 27.4724 | available | 0.85
| Nom. capacity MV, MVA | 25 | 3.45 | 10.6 | 120 | -7.15 | 0 | 26.25 | 33.4 |  |  |  | Nom. capacity MV, MVA | 25 | 0.54588 | 3.9959 | 10.6 | 120 | -6.6041 | 0 | 26.25 | 32.8541
| Nom. capacity lV, MVA | 25 | 7.9 | 9.6 | 120 | -1.7 | 0 | 26.25 | 27.95 |  |  |  | Nom. capacity lV, MVA | 25 | 0.47765 | 8.3776 | 9.6 | 120 | -1.2224 | 0 | 26.25 | 27.4724
132 | SS 110/10 B. Zhirovo | 6,3+6,3 | 0.9 | 0.6 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.315 | available | 132 | SS 110/10 B. Zhirovo | 6,3+6,3 | 0.082353 | 0.98235 | 0.6 | 120 | 0.38235 | 0 | 6.615 | 6.2326 | 6.2326 | available | 0.85
133 | SS 110/35/10 Basovo | 5,6+10 | 1.28 | 6.19 | 15 | -4.91 | 0 | 5.88 | 10.79 | 5.29 | available | 133 | SS 110/35/10 Basovo | 5,6+10 | 0.68652 | 1.9665 | 6.19 | 15 | -4.2235 | 0 | 5.88 | 10.1035 | 5.29 | available | 0.86
| Nom. capacity MV, MVA | 5,6+10 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38 |  |  |  | Nom. capacity MV, MVA | 5,6+10 | 0.68652 | 1.1865 | 6 |  | -4.8135 | 0 | 5.88 | 10.6935
| Nom. capacity LV, MVA | 5,6+10 | 0.78 | 0.19 | 120 | 0.59 | 0 | 5.88 | 5.29 |  |  |  | Nom. capacity LV, MVA | 5,6+10 | 0 | 0.78 | 0.19 | 120 | 0.59 | 0 | 5.88 | 5.29
134 | SS 110/35/10 Belaya | 16+16 | 7.3 | 12 | 120 | -4.7 | 0 | 16.8 | 21.5 | 13.6 | available | 134 | SS 110/35/10 Belaya | 16+16 | 2.0735 | 9.3735 | 12 | 120 | -2.6265 | 0 | 16.8 | 19.4265 | 13.3869 | available | 0.77
| Nom. capacity MV, MVA | 16 | 3.2 | 0 |  | 3.2 | 0 | 16.8 | 13.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.21315 | 3.4131 | 0 |  | 3.4131 | 0 | 16.8 | 13.3869
| Nom. capacity LV, MVA | 16 | 4.1 | 12 | 120 | -7.9 | 0 | 16.8 | 24.7 |  |  |  | Nom. capacity LV, MVA | 16 | 1.8604 | 5.9604 | 12 | 120 | -6.0396 | 0 | 16.8 | 22.8396
135 | SS 110/35/10 Bobryshovo | 6,3+6,3 | 1.6 | 1.3 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.015 | available | 135 | SS 110/35/10 Bobryshovo | 6,3+6,3 | 4.2836 | 5.8836 | 1.3 | 120 | 4.5836 | 0 | 6.615 | 2.0314 | 2.0314 | available | 0.89
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity MV, MVA | 6.3 | 1.8982 | 2.4982 | 0 |  | 2.4982 | 0 | 6.615 | 4.1168
| Nom. capacity LV, MVA | 6.3 | 1 | 1.3 | 120 | -0.3 | 0 | 6.615 | 6.915 |  |  |  | Nom. capacity LV, MVA | 6.3 | 2.3854 | 3.3854 | 1.3 | 120 | 2.0854 | 0 | 6.615 | 4.5296
136 | SS 110/10 Vinnikovo | 2,5+6,3 | 1.41 | 1.17 | 45 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 136 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.125 | 1.535 | 1.17 | 45 | 0.365 | 0 | 2.625 | 2.26 | 2.26 | available | 0.96
137 | SS 110/35/6 Volokno | 40+40,5+40,5 | 35.14 | 16.8 | 0 | 18.34 | 0 | 84.525 | 66.185 | 65.335 | available | 137 | SS 110/35/6 Volokno | 40+40,5+40,5 | 1.3781 | 36.5181 | 16.8 | 0 | 19.7181 | 0 | 84.525 | 64.8069 | 64.8069 | available | 0.9
| Nom. capacity MV, MVA | 40+40,5+40,5 | 15.95 | 16.8 | 0 | -0.85 | 0 | 84.525 | 85.375 |  |  |  | Nom. capacity MV, MVA | 40+40,5+40,5 | 1.0903 | 17.0403 | 16.8 | 0 | 0.24033 | 0 | 84.525 | 84.2847
| Nom. capacity MV, MVA | 40+40,5+40,5 | 19.19 | 0 | 0 | 19.19 | 0 | 84.525 | 65.335 |  |  |  | Nom. capacity MV, MVA | 40+40,5+40,5 | 0.28778 | 19.4778 | 0 | 0 | 19.4778 | 0 | 84.525 | 65.0472
138 | SS 110/10 Vysokaya | 16+16 | 27.2 | 3.2 | 15 | 24 | 0 | 16.8 | -7.2 | -7.2 | unavailable | 138 | SS 110/10 Vysokaya | 16+16 |  | 27.2 | 3.2 | 15 | 24 | 0 | 16.8 | -7.2 | -7.2 | unavailable | 0.94
139 | SS 110/35/10 Glushkovo | 10+10 | 6.54 | 8.04 | 120 | -1.5 | 0 | 10.5 | 12 | 8.94 | available | 139 | SS 110/35/10 Glushkovo | 10+10 | 3.8089 | 10.3489 | 8.04 | 120 | 2.3089 | 0 | 10.5 | 8.1911 | 6.7612 | available | 0.85
| Nom. capacity MV, MVA | 10 | 3.54 | 6.6 | 120 | -3.06 | 0 | 10.5 | 13.56 |  |  |  | Nom. capacity MV, MVA | 10 | 1.6301 | 5.1701 | 6.6 | 120 | -1.4299 | 0 | 10.5 | 11.9299
| Nom. capacity LV, MVA | 10 | 3 | 1.44 | 80 | 1.56 | 0 | 10.5 | 8.94 |  |  |  | Nom. capacity LV, MVA | 10 | 2.1788 | 5.1788 | 1.44 | 80 | 3.7388 | 0 | 10.5 | 6.7612
140 | SS 110/10 Gorodskaya | 25+25 | 13.76 | 0 | 0 | 13.76 | 0 | 26.25 | 12.49 | 12.49 | available | 140 | SS 110/10 Gorodskaya | 50+50 | 6.5558 | 20.3158 | 0 | 0 | 20.3158 | 0 | 26.25 | 5.9342 | 5.9342 | available | 0.95
141 | SS 110/35/10 Gorshechnoe | 10+16 | 9.9 | 4.82 | 120 | 5.08 | 0 | 10.5 | 5.42 | 5.06 | available | 141 | SS 110/35/10 Gorshechnoe | 10+16 | 13.1962 | 23.0962 | 4.82 | 120 | 18.2762 | 0 | 10.5 | -7.7762 | -7.7762 | unavailable | 0.83
| Nom. capacity MV, MVA | 10+16 | 4 | 4.36 |  | -0.36 | 0 | 10.5 | 10.86 |  |  |  | Nom. capacity MV, MVA | 10+16 | 12.248 | 16.248 | 4.36 |  | 11.888 | 0 | 10.5 | -1.388
| Nom. capacity LV, MVA | 10+16 | 5.9 | 0.46 | 120 | 5.44 | 0 | 10.5 | 5.06 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.94819 | 6.8482 | 0.46 | 120 | 6.3882 | 0 | 10.5 | 4.1118
142 | SS 110/35/10 Dmitriev | 10+10 | 4.68 | 10.4 | 120 | -5.72 | 0 | 10.5 | 16.22 | 10.51 | available | 142 | SS 110/35/10 Dmitriev | 10+10 | 2.3345 | 7.0145 | 10.4 | 120 | -3.3855 | 0 | 10.5 | 13.8855 | 8.4453 | available | 0.85
| Nom. capacity MV, MVA | 10 | 1.69 | 7.4 |  | -5.71 | 0 | 10.5 | 16.21 |  |  |  | Nom. capacity MV, MVA | 10 | 0.26977 | 1.9598 | 7.4 |  | -5.4402 | 0 | 10.5 | 15.9402
| Nom. capacity LV, MVA | 10 | 2.99 | 3 | 80 | -0.01 | 0 | 10.5 | 10.51 |  |  |  | Nom. capacity LV, MVA | 10 | 2.0647 | 5.0547 | 3 | 80 | 2.0547 | 0 | 10.5 | 8.4453
143 | SS 110/6 Dolgie Budy | 10+10 | 0.9 | 0.5 | 120 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | available | 143 | SS 110/6 Dolgie Budy | 10+10 | 0.062887 | 0.96289 | 0.5 | 120 | 0.46289 | 0 | 10.5 | 10.0371 | 10.0371 | available | 0.97
144 | SS 110/35/10 Zhukovka | 10+10 | 1.3 | 5.16 | 120 | -3.86 | 0 | 10.5 | 14.36 | 10.96 | available | 144 | SS 110/35/10 Zhukovka | 10+10 | 4.5027 | 5.8027 | 5.16 | 120 | 0.64266 | 0 | 10.5 | 9.8573 | 9.4276 | available | 0.99
| Nom. capacity MV, MVA | 10 | 1.1 | 4.5 | 1 day and night | -3.4 | 0 | 10.5 | 13.9 |  |  |  | Nom. capacity MV, MVA | 10 | 4.4724 | 5.5724 | 4.5 | 1 day and night | 1.0724 | 0 | 10.5 | 9.4276
| Nom. capacity LV, MVA | 10 | 0.2 | 0.66 | 120 | -0.46 | 0 | 10.5 | 10.96 |  |  |  | Nom. capacity LV, MVA | 10 | 0.030303 | 0.2303 | 0.66 | 120 | -0.4297 | 0 | 10.5 | 10.9297
145 | SS 110/35/10 Zolotukhino | 25+25 | 7.77 | 22.1 | 80 | -14.33 | 0 | 26.25 | 40.58 | 25.3 | available | 145 | SS 110/35/10 Zolotukhino | 25+25 | 3.6193 | 11.3893 | 22.1 | 80 | -10.7107 | 0 | 26.25 | 36.9607 | 21.8619 | available | 0.97
| Nom. capacity MV, MVA | 25 | 3.52 | 18.8 |  | -15.28 | 0 | 26.25 | 41.53 |  |  |  | Nom. capacity MV, MVA | 25 | 0.18118 | 3.7012 | 18.8 |  | -15.0988 | 0 | 26.25 | 41.3488
| Nom. capacity LV, MVA | 25 | 4.25 | 3.3 | 120 | 0.95 | 0 | 26.25 | 25.3 |  |  |  | Nom. capacity LV, MVA | 25 | 3.4381 | 7.6881 | 3.3 | 120 | 4.3881 | 0 | 26.25 | 21.8619
146 | SS 110/35/10 Kamyshi | 6,3+6,3 | 9.4 | 5.45 | 20 | 3.95 | 0 | 6.615 | 2.665 | 1.595 | available | 146 | SS 110/35/10 Kamyshi | 6,3+6,3 | 6.8937 | 16.2937 | 5.45 | 20 | 10.8437 | 0 | 6.615 | -4.2287 | -4.7558 | unavailable | 0.84
| Nom. capacity MV, MVA | 6.3 | 8.47 | 3.45 |  | 5.02 | 0 | 6.615 | 1.595 |  |  |  | Nom. capacity MV, MVA | 6.3 | 6.3508 | 14.8208 | 3.45 |  | 11.3708 | 0 | 6.615 | -4.7558
| Nom. capacity LV, MVA | 6.3 | 0.93 | 2 | 20 | -1.07 | 0 | 6.615 | 7.685 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.54286 | 1.4729 | 2 | 20 | -0.52714 | 0 | 6.615 | 7.1421
147 | SS 110/35/10 Kastornoe | 15+16 | 12.32 | 6.97 | 120 | 5.35 | 0 | 15.75 | 10.4 | 10.4 | available | 147 | SS 110/35/10 Kastornoe | 15+16 | 0.32002 | 12.64 | 6.97 | 120 | 5.67 | 0 | 15.75 | 10.08 | 10.08 | available | 0.93
| Nom. capacity MV, MVA | 15+16 | 9.41 | 6.6 |  | 2.81 | 0 | 15.75 | 12.94 |  |  |  | Nom. capacity MV, MVA | 15+16 | 0.28023 | 9.6902 | 6.6 |  | 3.0902 | 0 | 15.75 | 12.6598
| Nom. capacity LV, MVA | 15+16 | 2.91 | 0.37 | 120 | 2.54 | 0 | 15.75 | 13.21 |  |  |  | Nom. capacity LV, MVA | 15+16 | 0.039785 | 2.9498 | 0.37 | 120 | 2.5798 | 0 | 15.75 | 13.1702
148 | SS 110/35/10 Kilikino | 16+16 | 1.19 | 4.5 | 120 | -3.31 | 0 | 16.8 | 20.11 | 18.26 | available | 148 | SS 110/35/10 Kilikino | 16+16 | 0.26471 | 1.4547 | 4.5 | 120 | -3.0453 | 0 | 16.8 | 19.8453 | 18.0565 | available | 0.85
| Nom. capacity MV, MVA | 16 | 1.14 | 2.6 |  | -1.46 | 0 | 16.8 | 18.26 |  |  |  | Nom. capacity MV, MVA | 16 | 0.20353 | 1.3435 | 2.6 |  | -1.2565 | 0 | 16.8 | 18.0565
| Nom. capacity LV, MVA | 16 | 0.05 | 1.9 | 120 | -1.85 | 0 | 16.8 | 18.65 |  |  |  | Nom. capacity LV, MVA | 16 | 0.061176 | 0.11118 | 1.9 | 120 | -1.7888 | 0 | 16.8 | 18.5888
149 | SS 110/35/6 Kirovskaya | 40+40 | 46.3 | 16.36 | 120 | 29.94 | 0 | 42 | 12.06 | 12.06 | available | 149 | SS 110/35/6 Kirovskaya | 40+40 | 4.5225 | 50.8225 | 16.36 | 120 | 34.4625 | 0 | 42 | 7.5375 | 7.5375 | available | 0.89
| Nom. capacity MV, MVA | 40 | 20.08 | 13.06 | 120 | 7.02 | 0 | 42 | 34.98 |  |  |  | Nom. capacity MV, MVA | 40 |  | 20.08 | 13.06 | 120 | 7.02 | 0 | 42 | 34.98
| Nom. capacity LV, MVA | 40 | 26.22 | 3.3 | 120 | 22.92 | 0 | 42 | 19.08 |  |  |  | Nom. capacity LV, MVA | 40 | 4.5225 | 30.7425 | 3.3 | 120 | 27.4425 | 0 | 42 | 14.5575
150 | SS 110/35/10 Klyukva | 16+16 | 2.82 | 1.2 | 120 | 1.62 | 0 | 16.8 | 15.18 | 15.18 | available | 150 | SS 110/35/10 Klyukva | 16+16 | 1.8156 | 4.6356 | 1.2 | 120 | 3.4356 | 0 | 16.8 | 13.3644 | 13.3644 | available | 0.96
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  | 2: Nom. capacity MV, MVA; 3: 16; 5: 0; MVA 6: 0; Min 8: 0; Min 9: 0; Min 10: 16.8; Min 11: 16.8
| Nom. capacity LV, MVA | 16 | 2.82 | 1.2 | 120 | 1.62 | 0 | 16.8 | 15.18 |  |  |  | Nom. capacity LV, MVA | 16 | 1.8156 | 4.6356 | 1.2 | 120 | 3.4356 | 0 | 16.8 | 13.3644
151 | SS 110/10 Kompressornaya | 40+40 | 1.55 | 0 | 0 | 1.55 | 0 | 42 | 40.45 | 40.45 | available | 151 | SS 110/10 Kompressornaya | 40+40 |  | 1.55 | 0 | 0 | 1.55 | 0 | 42 | 40.45 | 40.45 | available | 0.87
152 | SS 110/35/10 Konyshevka | 10+16 | 9.2 | 8 | 120 | 1.2 | 0 | 10.5 | 9.3 | 9.05 | available | 152 | SS 110/35/10 Konyshevka | 10+16 | 4.4513 | 13.6513 | 8 | 120 | 5.6513 | 0 | 10.5 | 4.8487 | 4.8487 | available | 0.89
| Nom. capacity MV, MVA | 10+16 | 7.35 | 5.9 |  | 1.45 | 0 | 10.5 | 9.05 |  |  |  | Nom. capacity MV, MVA | 10+16 | 3.6086 | 10.9586 | 5.9 |  | 5.0586 | 0 | 10.5 | 5.4414
| Nom. capacity LV, MVA | 10+16 | 1.85 | 2.1 |  | -0.25 | 0 | 10.5 | 10.75 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.8427 | 2.6927 | 2.1 |  | 0.5927 | 0 | 10.5 | 9.9073
153 | SS 110/10 Kotelnaya | 10+25 | 1.55 | 4.1 | 0 | -2.55 | 0 | 10.5 | 13.05 | 13.05 | available | 153 | SS 110/10 Kotelnaya | 10+25 | 0.016484 | 1.5665 | 4.1 | 0 | -2.5335 | 0 | 10.5 | 13.0335 | 13.0335 | available | 0.91
154 | SS 110/35/10 Kshen | 10+10 | 8.17 | 7.81 | 10 | 0.36 | 0 | 10.5 | 10.14 | 7.04 | available | 154 | SS 110/35/10 Kshen | 10+10 | 7.8042 | 15.9742 | 7.81 | 10 | 8.1642 | 0 | 10.5 | 2.3358 | 0.0040449 | available | 0.89
| Nom. capacity MV, MVA | 10 | 2.96 | 6.06 |  | -3.1 | 0 | 10.5 | 13.6 |  |  |  | Nom. capacity MV, MVA | 10 | 0.76825 | 3.7282 | 6.06 |  | -2.3318 | 0 | 10.5 | 12.8318
| Nom. capacity LV, MVA | 10 | 5.21 | 1.75 | 120 | 3.46 | 0 | 10.5 | 7.04 |  |  |  | Nom. capacity LV, MVA | 10 | 7.036 | 12.246 | 1.75 | 120 | 10.496 | 0 | 10.5 | 0.0040449
155 | SS 110/6 Lesnaya | 40+40 | 2.31 | 0 | 0 | 2.31 | 0 | 42 | 39.69 | 39.69 | available | 155 | SS 110/6 Lesnaya | 40+40 | 3.956 | 6.266 | 0 | 0 | 6.266 | 0 | 42 | 35.734 | 35.734 | available | 0.91
156 | SS 110/35/10 Lgov | 25+25 | 12.6 | 4 | 120 | 8.6 | 0 | 26.25 | 17.65 | 17.65 | available | 156 | SS 110/35/10 Lgov | 25+25 | 2.6713 | 15.2713 | 4 | 120 | 11.2713 | 0 | 26.25 | 14.9787 | 14.9787 | available | 0.96
| Nom. capacity MV, MVA | 25 | 2.4 |  |  | 2.4 | 0 | 26.25 | 23.85 |  |  |  | Nom. capacity MV, MVA | 25 | 0.663 | 3.063 | 0 |  | 3.063 | 0 | 26.25 | 23.187
| Nom. capacity LV, MVA | 25 | 10.2 | 4 | 120 | 6.2 | 0 | 26.25 | 20.05 |  |  |  | Nom. capacity LV, MVA | 25 | 2.0083 | 12.2083 | 4 | 120 | 8.2083 | 0 | 26.25 | 18.0417
157 | SS 110/35/10 Lukashevka | 16+16 | 7.41 | 10.6 | 120 | -3.19 | 0 | 16.8 | 19.99 | 17.9 | available | 157 | SS 110/35/10 Lukashevka | 16+16 | 0.11412 | 7.5241 | 10.6 | 120 | -3.0759 | 0 | 16.8 | 19.8759 | 17.7859 | available | 0.85
| Nom. capacity MV, MVA | 16 | 4.2 | 5.3 |  | -1.1 | 0 | 16.8 | 17.9 |  |  |  | Nom. capacity MV, MVA | 16 | 0.11412 | 4.3141 | 5.3 |  | -0.98588 | 0 | 16.8 | 17.7859
| Nom. capacity LV, MVA | 16 | 3.21 | 5.3 | 120 | -2.09 | 0 | 16.8 | 18.89 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.21 | 5.3 | 120 | -2.09 | 0 | 16.8 | 18.89
158 | SS 110/35/10 Lyubostan | 6,3+10 | 5.9 | 13.1 | 120 | -7.2 | 0 | 6.615 | 13.815 | 6.715 | available | 158 | SS 110/35/10 Lyubostan | 6,3+10 | 3.9167 | 9.8167 | 13.1 | 120 | -3.2833 | 0 | 6.615 | 9.8983 | 3.0317 | available | 0.9
| Nom. capacity MV, MVA | 6,3+10 | 4.7 | 11.8 |  | -7.1 | 0 | 6.615 | 13.715 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.23336 | 4.9334 | 11.8 |  | -6.8666 | 0 | 6.615 | 13.4816
| Nom. capacity LV, MVA | 6,3+10 | 1.2 | 1.3 |  | -0.1 | 0 | 6.615 | 6.715 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 3.6833 | 4.8833 | 1.3 |  | 3.5833 | 0 | 6.615 | 3.0317
159 | SS 110/35/6 Manturovo | 16+16 | 5.78 | 9.35 | 10 | -3.57 | 0 | 16.8 | 20.37 | 16.91 | available | 159 | SS 110/35/6 Manturovo | 16+16 | 1.999 | 7.779 | 9.35 | 10 | -1.571 | 0 | 16.8 | 18.371 | 16.8799 | available | 0.83
| Nom. capacity MV, MVA | 16 | 5.63 | 9.09 |  | -3.46 | 0 | 16.8 | 20.26 |  |  |  | Nom. capacity MV, MVA | 16 | 1.9689 | 7.5989 | 9.09 |  | -1.4911 | 0 | 16.8 | 18.2911
| Nom. capacity LV, MVA | 16 | 0.15 | 0.26 | 120 | -0.11 | 0 | 16.8 | 16.91 |  |  |  | Nom. capacity LV, MVA | 16 | 0.03012 | 0.18012 | 0.26 | 120 | -0.07988 | 0 | 16.8 | 16.8799
160 | SS 110/35/10 8th Marta | 6,3+10 | 5.75 | 9.6 | 120 | -3.85 | 0 | 6.615 | 10.465 | 8.015 | available | 160 | SS 110/35/10 8th Marta | 6,3+10 | 7.0056 | 12.7556 | 9.6 | 120 | 3.1556 | 0 | 6.615 | 3.4594 | 1.024 | available | 0.89
| Nom. capacity MV, MVA | 6,3+10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 6.615 | 8.015 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 6.991 | 12.191 | 6.6 | 120 | 5.591 | 0 | 6.615 | 1.024
| Nom. capacity LV, MVA | 6,3+10 | 0.55 | 3 | 45 | -2.45 | 0 | 6.615 | 9.065 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0.014607 | 0.56461 | 3 | 45 | -2.4354 | 0 | 6.615 | 9.0504
161 | SS 110/10 Martovskaya | 6,3+6,3 | 0.61 | 0.55 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | available | 161 | SS 110/10 Martovskaya | 6,3+6,3 | 0.23556 | 0.84556 | 0.55 | 120 | 0.29556 | 0 | 6.615 | 6.3194 | 6.3194 | available | 0.9
162 | SS 110/35/10 Maryino | 10+25 | 5.7 | 8.11 | 120 | -2.41 | 0 | 10.5 | 12.91 | 11.7 | available | 162 | SS 110/35/10 Maryino | 10+25 | 1.0616 | 6.7616 | 8.11 | 120 | -1.3484 | 0 | 10.5 | 11.8484 | 10.6626 | available | 0.88
| Nom. capacity MV, MVA | 10+25 | 3.7 | 4.9 |  | -1.2 | 0 | 10.5 | 11.7 |  |  |  | Nom. capacity MV, MVA | 10+25 | 1.0374 | 4.7374 | 4.9 |  | -0.16257 | 0 | 10.5 | 10.6626
| Nom. capacity LV, MVA | 10+25 | 2 | 3.21 |  | -1.21 | 0 | 10.5 | 11.71 |  |  |  | Nom. capacity LV, MVA | 10+25 | 0.024205 | 2.0242 | 3.21 |  | -1.1858 | 0 | 10.5 | 11.6858
163 | SS 110/35/10 Medvenka | 10+10 | 7.27 | 19.22 | 120 | -11.95 | 0 | 10.5 | 22.45 | 9.7 | available | 163 | SS 110/35/10 Medvenka | 10+10 | 0.21209 | 7.4821 | 19.22 | 120 | -11.7379 | 0 | 10.5 | 22.2379 | 9.5361 | available | 0.83
| Nom. capacity MV, MVA | 10 | 4.35 | 17.1 |  | -12.75 | 0 | 10.5 | 23.25 |  |  |  | Nom. capacity MV, MVA | 10 | 0.048235 | 4.3982 | 17.1 |  | -12.7018 | 0 | 10.5 | 23.2018
| Nom. capacity LV, MVA | 10 | 2.92 | 2.12 | 120 | 0.8 | 0 | 10.5 | 9.7 |  |  |  | Nom. capacity LV, MVA | 10 | 0.16386 | 3.0839 | 2.12 | 120 | 0.96386 | 0 | 10.5 | 9.5361
164 | SS 110/6 Neftyanaya | 10+10 | 0.16 |  |  | 0.16 | 0 | 10.5 | 10.34 | 10.34 | available | 164 | SS 110/6 Neftyanaya | 10+10 | 0.016092 | 0.17609 | 0 |  | 0.17609 | 0 | 10.5 | 10.3239 | 10.3239 | available | 0.87
165 | SS 110/35/10 Oboyan | 16+25 | 16.25 | 26.86 | 120 | -10.61 | 0 | 16.8 | 27.41 | 12.01 | available | 165 | SS 110/35/10 Oboyan | 16+25 | 2.2009 | 18.4509 | 26.86 | 120 | -8.4091 | 0 | 16.8 | 25.2091 | 9.8693 | available | 0.86
| Nom. capacity MV, MVA | 16+25 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16+25 | 0.060164 | 2.0602 | 17.4 | 0 | -15.3398 | 0 | 16.8 | 32.1398
| Nom. capacity LV, MVA | 16+25 | 14.25 | 9.46 |  | 4.79 | 0 | 16.8 | 12.01 |  |  |  | Nom. capacity LV, MVA | 16+25 | 2.1407 | 16.3907 | 9.46 |  | 6.9307 | 0 | 16.8 | 9.8693
166 | SS 110/35/10 Oktyabrskaya | 16+16 | 13.55 | 15.5 | 120 | -1.95 | 0 | 16.8 | 18.75 | 13.31 | available | 166 | SS 110/35/10 Oktyabrskaya | 16+16 | 0.54687 | 14.0969 | 15.5 | 120 | -1.4031 | 0 | 16.8 | 18.2031 | 12.8937 | available | 0.86
| Nom. capacity MV, MVA | 16 | 9.06 | 14.5 |  | -5.44 | 0 | 16.8 | 22.24 |  |  |  | Nom. capacity MV, MVA | 16 | 0.13059 | 9.1906 | 14.5 |  | -5.3094 | 0 | 16.8 | 22.1094
| Nom. capacity LV, MVA | 16 | 4.49 | 1 | 120 | 3.49 | 0 | 16.8 | 13.31 |  |  |  | Nom. capacity LV, MVA | 16 | 0.41628 | 4.9063 | 1 | 120 | 3.9063 | 0 | 16.8 | 12.8937
167 | SS 110/35/10 Olkhovka | 6,3+6,3 | 1.66 | 6.31 | 120 | -4.65 | 0 | 6.615 | 11.265 | 7.715 | available | 167 | SS 110/35/10 Olkhovka | 6,3+6,3 | 0.12825 | 1.7883 | 6.31 | 120 | -4.5217 | 0 | 6.615 | 11.1367 | 7.6926 | available | 0.76
| Nom. capacity MV, MVA | 6.3 | 1.45 | 5 | 120 | -3.55 | 0 | 6.615 | 10.165 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.10588 | 1.5559 | 5 | 120 | -3.4441 | 0 | 6.615 | 10.0591
| Nom. capacity LV, MVA | 6.3 | 0.21 | 1.31 | 120 | -1.1 | 0 | 6.615 | 7.715 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.022368 | 0.23237 | 1.31 | 120 | -1.0776 | 0 | 6.615 | 7.6926
168 | SS 110/10 Paniki | 2,5+2,5 | 0.62 | 0.1 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 168 | SS 110/10 Paniki | 2,5+2,5 | 0.046739 | 0.66674 | 0.1 | 120 | 0.56674 | 0 | 2.625 | 2.0583 | 2.0583 | available | 0.92
169 | SS 110/35/10 Peny | 16+16 | 6.44 | 6.9 | 120 | -0.46 | 0 | 16.8 | 17.26 | 16.88 | available | 169 | SS 110/35/10 Peny | 16+16 | 0.37078 | 6.8108 | 6.9 | 120 | -0.089216 | 0 | 16.8 | 16.8892 | 16.568 | available | 0.85
| Nom. capacity MV, MVA | 16 | 3.42 | 3.5 |  | -0.08 | 0 | 16.8 | 16.88 |  |  |  | Nom. capacity MV, MVA | 16 | 0.31196 | 3.732 | 3.5 |  | 0.23196 | 0 | 16.8 | 16.568
| Nom. capacity LV, MVA | 16 | 3.02 | 3.4 | 120 | -0.38 | 0 | 16.8 | 17.18 |  |  |  | Nom. capacity LV, MVA | 16 | 0.058824 | 3.0788 | 3.4 | 120 | -0.32118 | 0 | 16.8 | 17.1212
170 | SS 110/35/10 Pribor | 25+25 | 25.99 | 6.5 | 0 | 19.49 | 0 | 26.25 | 6.76 | 6.76 | available | 170 | SS 110/35/10 Pribor | 25+25 | 3.9474 | 29.9374 | 6.5 | 0 | 23.4374 | 0 | 26.25 | 2.8126 | 2.8126 | available | 0.95
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  | 2: Nom. capacity MV, MVA; 3: 25; 5: 0; MVA 6: 0; Min 8: 0; Min 9: 0; Min 10: 26.25; Min 11: 26.25
| Nom. capacity LV, MVA | 25 | 25.99 | 6.5 | 0 | 19.49 | 0 | 26.25 | 6.76 |  |  |  | Nom. capacity LV, MVA | 25 | 3.9474 | 29.9374 | 6.5 | 0 | 23.4374 | 0 | 26.25 | 2.8126
171 | SS 110/10 Progress | 63+63 | 16.27 | 0 | 0 | 16.27 | 0 | 66.15 | 49.88 | 49.88 | available | 171 | SS 110/10 Progress | 63+63 |  | 16.27 | 0 | 0 | 16.27 | 0 | 66.15 | 49.88 | 49.88 | available | 0.94
172 | SS 110/10 Poultry plant | 6,3+10 | 3.26 | 0.32 | 0 | 2.94 | 0 | 6.615 | 3.675 | 3.675 | available | 172 | SS 110/10 Poultry plant | 6,3+10 | 0.81566 | 4.0757 | 0.32 | 0 | 3.7557 | 0 | 6.615 | 2.8593 | 2.8593 | available | 0.83
173 | SS 110/35/10 R. Budy | 10+10 | 3.2 | 15.7 | 120 | -12.5 | 0 | 10.5 | 23 | 15.5 | available | 173 | SS 110/35/10 R. Budy | 10+10 | 0.010345 | 3.2103 | 15.7 | 120 | -12.4897 | 0 | 10.5 | 22.9897 | 15.4897 | available | 0.87
| Nom. capacity MV, MVA | 10 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.010345 | 1.4103 | 6.4 |  | -4.9897 | 0 | 10.5 | 15.4897
174 | SS 110/35/10 Raskhovets | 6.3 | 0.34 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.55 | 2.06 | available | 174 | SS 110/35/10 Raskhovets | 6.3 | 0.027059 | 0.36706 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.5229 | 2.06 | available | 0.8
| Nom. capacity MV, MVA | 6.3 | 0.25 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.49 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.027059 | 0.27706 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.4629
| Nom. capacity LV, MVA | 6.3 | 0.09 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.06 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.09 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.06
175 | SS 110/35/10 Razinkovo | 6,3 +10 | 2.3 | 21.4 | 45 | -19.1 | 0 | 6.615 | 25.715 | 9.495 | available | 175 | SS 110/35/10 Razinkovo | 6,3+10 | 0.22155 | 2.5215 | 21.4 | 45 | -18.8785 | 0 | 6.615 | 25.4935 | 9.4205 | available | 0.98
| Nom. capacity MV, MVA | 6,3+10 | 1.58 | 17.8 |  | -16.22 | 0 | 6.615 | 22.835 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.14706 | 1.7271 | 17.8 |  | -16.0729 | 0 | 6.615 | 22.6879
| Nom. capacity LV, MVA | 6,3+10 | 0.72 | 3.6 | 45 | -2.88 | 0 | 6.615 | 9.495 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0.07449 | 0.79449 | 3.6 | 45 | -2.8055 | 0 | 6.615 | 9.4205
176 | SS 110/10 Rodniki | 25+25 | 1.5 | 9.2 | 120 | -7.7 | 0 | 26.25 | 33.95 | 33.95 | available | 176 | SS 110/10 Rodniki | 25+25 | 16.8508 | 18.3508 | 9.2 | 120 | 9.1508 | 0 | 26.25 | 17.0992 | 17.0992 | available | 0.85
177 | SS 110/35/10 Rudnaya | 31,5+31,5 | 15.85 | 3.25 | 10 | 12.6 | 0 | 33.075 | 20.475 | 20.475 | available | 177 | SS 110/35/10 Rudnaya | 31,5+31,5 | 1.269 | 17.119 | 3.25 | 10 | 13.869 | 0 | 33.075 | 19.206 | 19.206 | available | 0.83
| Nom. capacity MV, MVA | 31.5 | 9.58 | 1.7 |  | 7.88 | 0 | 33.075 | 25.195 |  |  |  | Nom. capacity MV, MVA | 31.5 | 1.1365 | 10.7165 | 1.7 |  | 9.0165 | 0 | 33.075 | 24.0585
| Nom. capacity LV, MVA | 31.5 | 6.27 | 1.55 | 120 | 4.72 | 0 | 33.075 | 28.355 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.13253 | 6.4025 | 1.55 | 120 | 4.8525 | 0 | 33.075 | 28.2225
178 | SS 110/35/10 Rylsk | 16+25 | 14.8 | 11 | 120 | 3.8 | 0 | 16.8 | 13 | 13 | available | 178 | SS 110/35/10 Rylsk | 16+25 | 10.3603 | 25.1603 | 11 | 120 | 14.1603 | 0 | 16.8 | 2.6397 | 2.6397 | available | 0.92
| Nom. capacity MV, MVA | 16+25 | 8.4 | 7 |  | 1.4 | 0 | 16.8 | 15.4 |  |  |  | Nom. capacity MV, MVA | 16+25 | 6.7972 | 15.1972 | 7 |  | 8.1972 | 0 | 16.8 | 8.6028
| Nom. capacity LV, MVA | 16+25 | 6.4 | 4 | 120 | 2.4 | 0 | 16.8 | 14.4 |  |  |  | Nom. capacity LV, MVA | 16+25 | 3.563 | 9.963 | 4 | 120 | 5.963 | 0 | 16.8 | 10.837
179 | SS 110/10 Solovyinaya | 25+25 | 6.09 | 0 | 0 | 6.09 | 0 | 26.25 | 20.16 | 20.16 | available | 179 | SS 110/10 Solovyinaya | 25+25 | 1.75 | 7.84 | 0 | 0 | 7.84 | 0 | 26.25 | 18.41 | 18.41 | available | 0.96
180 | SS 110/10 STK | 10+10 | 0.6 | 0 | 0 | 0.6 | 0 | 10.5 | 9.9 | 9.9 | available | 180 | SS 110/10 STK | 10+10 | 0.01 | 0.61 | 0 | 0 | 0.61 | 0 | 10.5 | 9.89 | 9.89 | available | 0.8
181 | SS 110/10 Studenok | 6,3+6,3 | 1.39 | 0.7 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | available | 181 | SS 110/10 Studenok | 6,3+6,3 | 0.17176 | 1.5618 | 0.7 | 120 | 0.86176 | 0 | 6.615 | 5.7532 | 5.7532 | available | 0.85
182 | SS 110/35/10 Sudzha | 25+25 | 16.6 | 29 | 120 | -12.4 | 0 | 26.25 | 38.65 | 28.25 | available | 182 | SS 110/35/10 Sudzha | 25+25 | 2.8474 | 19.4474 | 29 | 120 | -9.5526 | 0 | 26.25 | 35.8026 | 27.2811 | available | 0.9
| Nom. capacity MV, MVA | 25 | 6.7 | 17.1 |  | -10.4 | 0 | 26.25 | 36.65 |  |  |  | Nom. capacity MV, MVA | 25 | 1.8785 | 8.5785 | 17.1 |  | -8.5215 | 0 | 26.25 | 34.7715
| Nom. capacity LV, MVA | 25 | 9.9 | 11.9 |  | -2 | 0 | 26.25 | 28.25 |  |  |  | Nom. capacity LV, MVA | 25 | 0.96889 | 10.8689 | 11.9 |  | -1.0311 | 0 | 26.25 | 27.2811
183 | SS 110/35/10 Schyotmash | 25+25 | 14.82 | 0 | 0 | 14.82 | 0 | 26.25 | 11.43 | 11.43 | available | 183 | SS 110/35/10 Schyotmash | 25+25 | 10.0892 | 24.9092 | 0 | 0 | 24.9092 | 0 | 26.25 | 1.3408 | 1.3408 | available | 0.95
| Nom. capacity MV, MVA | 25 | 4.47 |  |  | 4.47 | 0 | 26.25 | 21.78 |  |  |  | Nom. capacity MV, MVA | 25 | 4.4724 | 8.9424 | 0 |  | 8.9424 | 0 | 26.25 | 17.3076
| Nom. capacity LV, MVA | 25 | 10.35 | 0 | 0 | 10.35 | 0 | 26.25 | 15.9 |  |  |  | Nom. capacity LV, MVA | 25 | 5.6168 | 15.9668 | 0 | 0 | 15.9668 | 0 | 26.25 | 10.2832
184 | SS 110/6 Hot House | 25+25 | 3.1 | 6.64 | 1 day and night | -3.54 | 0 | 26.25 | 29.79 | 29.79 | available | 184 | SS 110/6 Hot House | 25+25 | 9.8656 | 12.9656 | 6.64 | 0 | 6.3256 | 0 | 26.25 | 19.9244 | 19.9244 | available | 0.9
185 | SS 110/35/10 Tyotkino | 10+10 | 4 | 3.44 | 120 | 0.56 | 0 | 10.5 | 9.94 | 8.34 | available | 185 | SS 110/35/10 Tyotkino | 10+10 | 0.072233 | 4.0722 | 3.44 | 120 | 0.63223 | 0 | 10.5 | 9.8678 | 8.2756 | available | 0.87
| Nom. capacity MV, MVA | 10 | 0.4 | 2 |  | -1.6 | 0 | 10.5 | 12.1 |  |  |  | Nom. capacity MV, MVA | 10 | 0.0078652 | 0.40787 | 2 |  | -1.5921 | 0 | 10.5 | 12.0921
| Nom. capacity LV, MVA | 10 | 3.6 | 1.44 |  | 2.16 | 0 | 10.5 | 8.34 |  |  |  | Nom. capacity LV, MVA | 10 | 0.064368 | 3.6644 | 1.44 |  | 2.2244 | 0 | 10.5 | 8.2756
186 | SS 110/35/10 Tim | 6,3+16 | 4.07 | 9.59 | 120 | -5.52 | 0 | 6.615 | 12.135 | 5.675 | available | 186 | SS 110/35/10 Tim | 6,3+16 | 0.17853 | 4.2485 | 9.59 | 120 | -5.3415 | 0 | 6.615 | 11.9565 | 5.6 | available | 0.84
| Nom. capacity MV, MVA | 6,3+16 | 2.63 | 9.09 |  | -6.46 | 0 | 6.615 | 13.075 |  |  |  | Nom. capacity MV, MVA | 6,3+16 | 0.10353 | 2.7335 | 9.09 |  | -6.3565 | 0 | 6.615 | 12.9715
| Nom. capacity LV, MVA | 6,3+16 | 1.44 | 0.5 | 120 | 0.94 | 0 | 6.615 | 5.675 |  |  |  | Nom. capacity LV, MVA | 6,3+16 | 0.075 | 1.515 | 0.5 | 120 | 1.015 | 0 | 6.615 | 5.6
187 | SS 110/35/10 Uyutnoe | 10+16 | 0.57 | 0.5 | 120 | 0.07 | 0 | 10.5 | 10.43 | 10.22 | available | 187 | SS 110/35/10 Uyutnoe | 10+16 | 0.17294 | 0.74294 | 0.5 | 120 | 0.24294 | 0 | 10.5 | 10.2571 | 10.0576 | available | 0.85
| Nom. capacity MV, MVA | 10+16 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.16235 | 0.44235 | 0 |  | 0.44235 | 0 | 10.5 | 10.0576
| Nom. capacity LV, MVA | 10+16 | 0.29 | 0.5 | 120 | -0.21 | 0 | 10.5 | 10.71 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.010588 | 0.30059 | 0.5 | 120 | -0.19941 | 0 | 10.5 | 10.6994
188 | SS 110/35/10 Fatezh | 16+16 | 9.28 | 17.4 | 120 | -8.12 | 0 | 16.8 | 24.92 | 15.52 | available | 188 | SS 110/35/10 Fatezh | 16+16 | 4.2129 | 13.4929 | 17.4 | 120 | -3.9071 | 0 | 16.8 | 20.7071 | 11.6874 | available | 0.86
| Nom. capacity MV, MVA | 16 | 3.4 | 12.8 |  | -9.4 | 0 | 16.8 | 26.2 |  |  |  | Nom. capacity MV, MVA | 16 | 0.38037 | 3.7804 | 12.8 |  | -9.0196 | 0 | 16.8 | 25.8196
| Nom. capacity LV, MVA | 16 | 5.88 | 4.6 | 120 | 1.28 | 0 | 16.8 | 15.52 |  |  |  | Nom. capacity LV, MVA | 16 | 3.8326 | 9.7126 | 4.6 | 120 | 5.1126 | 0 | 16.8 | 11.6874
189 | SS 110/35/10 Fosforitnaya | 25+25 | 3.43 | 12.34 | 120 | -8.91 | 0 | 26.25 | 35.16 | 24.72 | available | 189 | SS 110/35/10 Fosforitnaya | 25+25 | 0.26859 | 3.6986 | 12.34 | 120 | -8.6414 | 0 | 26.25 | 34.8914 | 24.6484 | available | 0.88
| Nom. capacity MV, MVA | 25 | 1.68 | 12.12 |  | -10.44 | 0 | 26.25 | 36.69 |  |  |  | Nom. capacity MV, MVA | 25 | 0.197 | 1.877 | 12.12 |  | -10.243 | 0 | 26.25 | 36.493
| Nom. capacity LV, MVA | 25 | 1.75 | 0.22 | 10 | 1.53 | 0 | 26.25 | 24.72 |  |  |  | Nom. capacity LV, MVA | 25 | 0.071591 | 1.8216 | 0.22 | 10 | 1.6016 | 0 | 26.25 | 24.6484
190 | SS 110/35/10 Khomutovka | 7,5+10 | 2 | 6.3 | 80 | -4.3 | 0 | 7.875 | 12.175 | 8.765 | available | 190 | SS 110/35/10 Khomutovka | 7,5+10 | 0.98687 | 2.9869 | 6.3 | 80 | -3.3131 | 0 | 7.875 | 11.1881 | 7.8487 | available | 0.86
| Nom. capacity MV, MVA | 7,5+10 | 0.49 | 3.9 |  | -3.41 | 0 | 7.875 | 11.285 |  |  |  | Nom. capacity MV, MVA | 7,5+10 | 0.070588 | 0.56059 | 3.9 |  | -3.3394 | 0 | 7.875 | 11.2144
| Nom. capacity LV, MVA | 7,5+10 | 1.51 | 2.4 | 80 | -0.89 | 0 | 7.875 | 8.765 |  |  |  | Nom. capacity LV, MVA | 7,5+10 | 0.91628 | 2.4263 | 2.4 | 80 | 0.026279 | 0 | 7.875 | 7.8487
191 | SS 110/35/10 Cheremisinovo | 16+16 | 1.67 | 9.38 | 10 | -7.71 | 0 | 16.8 | 24.51 | 15.71 | available | 191 | SS 110/35/10 Cheremisinovo | 16+16 | 0.80159 | 2.4716 | 9.38 | 10 | -6.9084 | 0 | 16.8 | 23.7084 | 15.3102 | available | 0.87
| Nom. capacity MV, MVA | 16 | 0.29 | 9.09 |  | -8.8 | 0 | 16.8 | 25.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.40181 | 0.69181 | 9.09 |  | -8.3982 | 0 | 16.8 | 25.1982
| Nom. capacity LV, MVA | 16 | 1.38 | 0.29 | 120 | 1.09 | 0 | 16.8 | 15.71 |  |  |  | Nom. capacity LV, MVA | 16 | 0.39977 | 1.7798 | 0.29 | 120 | 1.4898 | 0 | 16.8 | 15.3102
192 | SS 110/35/10 Cheremoshki | 6,3+6,3 | 3.2 | 8.25 | 120 | -5.05 | 0 | 6.615 | 11.665 | 5.665 | available | 192 | SS 110/35/10 Cheremoshki | 6,3+6,3 | 0.55265 | 3.7527 | 8.25 | 120 | -4.4973 | 0 | 6.615 | 11.1123 | 5.6483 | available | 0.9
| Nom. capacity MV, MVA | 6.3 | 1 | 7 |  | -6 | 0 | 6.615 | 12.615 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.53599 | 1.536 | 7 |  | -5.464 | 0 | 6.615 | 12.079
| Nom. capacity LV, MVA | 6.3 | 2.2 | 1.25 | 129 | 0.95 | 0 | 6.615 | 5.665 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.016667 | 2.2167 | 1.25 | 129 | 0.96667 | 0 | 6.615 | 5.6483
193 | SS 110/35/10 Shumakovo | 10+10 | 4.6 | 13.73 | 120 | -9.13 | 0 | 10.5 | 19.63 | 11.83 | available | 193 | SS 110/35/10 Shumakovo | 10+10 | 2.2363 | 6.8363 | 13.73 | 120 | -6.8937 | 0 | 10.5 | 17.3937 | 11.7547 | available | 0.85
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3 |  |  |  | Nom. capacity MV, MVA | 10 | 2.161 | 5.561 | 11.2 |  | -5.639 | 0 | 10.5 | 16.139
| Nom. capacity LV, MVA | 10 | 1.2 | 2.53 | 120 | -1.33 | 0 | 10.5 | 11.83 |  |  |  | Nom. capacity LV, MVA | 10 | 0.075294 | 1.2753 | 2.53 | 120 | -1.2547 | 0 | 10.5 | 11.7547
194 | SS 110/35/10 Shchigry | 25+25 | 12.83 | 12.9 | 120 | -0.07 | 0 | 26.25 | 26.32 | 19.35 | available | 194 | SS 110/35/10 Shchigry | 25+25 | 0.99749 | 13.8275 | 12.9 | 120 | 0.92749 | 0 | 26.25 | 25.3225 | 19.3278 | available | 0.9
| Nom. capacity MV, MVA | 25 | 5.15 | 12.12 |  | -6.97 | 0 | 26.25 | 33.22 |  |  |  | Nom. capacity MV, MVA | 25 | 0.97527 | 6.1253 | 12.12 |  | -5.9947 | 0 | 26.25 | 32.2447
| Nom. capacity LV, MVA | 25 | 7.68 | 0.78 | 120 | 6.9 | 0 | 26.25 | 19.35 |  |  |  | Nom. capacity LV, MVA | 25 | 0.022222 | 7.7022 | 0.78 | 120 | 6.9222 | 0 | 26.25 | 19.3278
195 | SS 110/35/10 Yastrebovka | 7,5+10 | 2.51 | 6.31 | 10 | -3.8 | 0 | 7.875 | 11.675 | 6.85 | available | 195 | SS 110/35/10 Yastrebovka | 7,5+10 | 0.92066 | 3.4307 | 6.31 | 10 | -2.8793 | 0 | 7.875 | 10.7543 | 6.7211 | available | 0.83
| Nom. capacity MV, MVA | 7,5+10 | 1.23 | 6.06 |  | -4.83 | 0 | 7.88 | 12.71 |  |  |  | Nom. capacity MV, MVA | 7,5+10 | 0.79174 | 2.0217 | 6.06 |  | -4.0383 | 0 | 7.88 | 11.9183
| Nom. capacity LV, MVA | 7,5+10 | 1.28 | 0.25 | 10 | 1.03 | 0 | 7.88 | 6.85 |  |  |  | Nom. capacity LV, MVA | 7,5+10 | 0.12892 | 1.4089 | 0.25 | 10 | 1.1589 | 0 | 7.88 | 6.7211
196 | SS 35/10 Amosovka | 2,5+2,5 | 0.32 | 0.2 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available | 196 | SS 35/10 Amosovka | 2,5+2,5 | 0.011765 | 0.33176 | 0.2 | 120 | 0.13176 | 0 | 2.625 | 2.4932 | 2.4932 | available | 0.85
197 | SS 35/10 Afanasyevka (SPS) | 1,6+2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | available | 197 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.015957 | 0.51596 | 0.37 | 120 | 0.14596 | 0 | 1.68 | 1.534 | 1.534 | available | 0.94
198 | SS 35/10 B.Soldatskoe 2 | 4+4 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | available | 198 | SS 35/10 B.Soldatskoe 2 | 4+4 | 0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | available | 0.85
199 | SS 35/10 B.Zmeinets | 1,6+1,6 | 0.15 | 1.43 | 120 | -1.28 | 0 | 1.68 | 2.96 | 2.96 | available | 199 | SS 35/10 B.Zmeinets | 1,6+1,6 | 0 | 0.15 | 1.43 | 120 | -1.28 | 0 | 1.68 | 2.96 | 2.96 | available | 0.81
200 | SS 35/10 Bezlesnaya | 4+4 | 2.15 | 6.1 | 0 | -3.95 | 0 | 4.2 | 8.15 | 8.15 | available | 200 | SS 35/10 Bezlesnaya | 4+4 | 0.379 | 2.529 | 6.1 | 0 | -3.571 | 0 | 4.2 | 7.771 | 7.771 | available | 1
201 | SS 35/10 Bereza | 1+2,5 | 0.05 | 0.15 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | available | 201 | SS 35/10 Bereza | 1+2,5 | 0.0094118 | 0.059412 | 0.15 | 120 | -0.090588 | 0 | 1.05 | 1.1406 | 1.1406 | available | 0.85
202 | SS 35/10 Blagodat | 2,5+4 | 0.81 | 0.29 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 202 | SS 35/10 Blagodat | 2,5+4 | 0.026923 | 0.83692 | 0.29 | 120 | 0.54692 | 0 | 2.625 | 2.0781 | 2.0781 | available | 0.78
203 | SS 35/10 Bykanovo | 2,5+2,5 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 203 | SS 35/10 Bykanovo | 2,5+2,5 | 0.012857 | 0.41286 | 0.41 | 120 | 0.0028571 | 0 | 2.625 | 2.6221 | 2.6221 | available | 0.7
204 | SS 35/10 V. Lyubazh | 4+10 | 0.27 | 0.4 | 120 | -0.13 | 0 | 4.2 | 4.33 | 4.33 | available | 204 | SS 35/10 V. Lyubazh | 4+10 | 0.13882 | 0.40882 | 0.4 | 120 | 0.0088235 | 0 | 4.2 | 4.1912 | 4.1912 | available | 0.85
205 | SS 35/10 Vesyoloe | 1,6+1,6 | 0.86 | 0.22 | 120 | 0.64 | 0 | 1.68 | 1.04 | 1.04 | available | 205 | SS 35/10 Vesyoloe | 1,6+1,6 | 0.093023 | 0.95302 | 0.22 | 120 | 0.73302 | 0 | 1.68 | 0.94698 | 0.94698 | available | 0.86
206 | SS 35/10 Volobuevka | 2,5+4 | 0.56 | 0.46 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 206 | SS 35/10 Volobuevka | 2,5+4 | 0.035294 | 0.59529 | 0.46 | 120 | 0.13529 | 0 | 2.625 | 2.4897 | 2.4897 | available | 0.85
207 | SS 35/10 Voropaevo | 4+4 | 0.4 | 0 | 0 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | available | 207 | SS 35/10 Voropaevo | 4+4 | 0.025882 | 0.42588 | 0 | 0 | 0.42588 | 0 | 4.2 | 3.7741 | 3.7741 | available | 0.85
208 | SS 35/10 Vostochnaya | 6,3+6,3 | 4 | 0.46 | 120 | 3.54 | 0 | 6.615 | 3.075 | 3.075 | available | 208 | SS 35/10 Vostochnaya | 6,3+6,3 | 0.15543 | 4.1554 | 0.46 | 120 | 3.6954 | 0 | 6.615 | 2.9196 | 2.9196 | available | 0.92
209 | SS 35/10 Vygornoe | 2,5+2,5 | 1.16 | 0.51 | 120 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | available | 209 | SS 35/10 Vygornoe | 2,5+2,5 | 0.050588 | 1.2106 | 0.51 | 120 | 0.70059 | 0 | 2.625 | 1.9244 | 1.9244 | available | 0.85
210 | SS 35/10 Gastomlya | 1,6+1,6 | 0.45 | 0.17 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 210 | SS 35/10 Gastomlya | 1,6+1,6 | 0 | 0.45 | 0.17 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 0.85
211 | SS 35/10 Gorodok | 4+4 | 1.45 | 0.7 | 45 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | available | 211 | SS 35/10 Gorodok | 4+4 | 0.0059524 | 1.456 | 0.7 | 45 | 0.75595 | 0 | 4.2 | 3.444 | 3.444 | available | 0.84
212 | SS 35/10 Guevo | 2,5+2,5 | 1.25 | 1.69 | 20 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | available | 212 | SS 35/10 Guevo | 2,5+2,5 | 0.051163 | 1.3012 | 1.69 | 20 | -0.38884 | 0 | 2.625 | 3.0138 | 3.0138 | available | 0.86
213 | SS 35/10 Dolzhenkovo | 1,6+1,6 | 0.3 | 0.38 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | available | 213 | SS 35/10 Dolzhenkovo | 1,6+1,6 | 0 | 0.3 | 0.38 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | available | 0.89
214 | SS 35/6 Dukhovets | 2,5+4 | 4.12 | 3.5 | 0 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | available | 214 | SS 35/6 Dukhovets | 2,5+4 | 0.034091 | 4.1541 | 3.5 | 0 | 0.65409 | 0 | 2.625 | 1.9709 | 1.9709 | available | 0.88
215 | SS 35/10 Zhernovets | 2,5+2,5 | 0.53 | 0.26 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available | 215 | SS 35/10 Zhernovets | 2,5+2,5 | 0.010638 | 0.54064 | 0.26 | 120 | 0.28064 | 0 | 2.625 | 2.3444 | 2.3444 | available | 0.94
216 | SS 35/6 Zapadnaya | 10+10 | 9.39 | 2.5 | 0 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | available | 216 | SS 35/6 Zapadnaya | 10+10 | 0.016667 | 9.4067 | 2.5 | 0 | 6.9067 | 0 | 10.5 | 3.5933 | 3.5933 | available | 0.9
217 | SS 35/10 Zolotukhinskaya KRS | 4+4 | 0.78 | 1.67 | 0 | -0.89 | 0 | 4.2 | 5.09 | 5.09 | available | 217 | SS 35/10 Zolotukhinskaya KRS | 4+4 | 0.1039 | 0.8839 | 1.67 | 0 | -0.7861 | 0 | 4.2 | 4.9861 | 4.9861 | available | 0.77
218 | SS 35/10 Zuevka | 1,6 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 218 | SS 35/10 Zuevka | 1,6+2,5 | 0.18471 | 1.0847 | 0.93 | 45 | 0.15471 | 0 | 1.68 | 1.5253 | 1.5253 | available | 0.85
219 | SS 35/10 Ivanino | 6,3+6,3 | 2.27 | 2.69 | 80 | -0.42 | 0 | 6.615 | 7.035 | 7.035 | available | 219 | SS 35/10 Ivanino | 6,3+6,3 | 0.21294 | 2.4829 | 2.69 | 80 | -0.20706 | 0 | 6.615 | 6.8221 | 6.8221 | available | 0.85
220 | SS 35/10 Kalinovka | 1,8+2,5 | 0.63 | 0.5 | 120 | 0.13 | 0 | 1.89 | 1.76 | 1.76 | available | 220 | SS 35/10 Kalinovka | 1,8+2,5 | 0.017647 | 0.64765 | 0.5 | 120 | 0.14765 | 0 | 1.89 | 1.7424 | 1.7424 | available | 0.85
221 | SS 35/10 Kirilovka | 1,6+1,6 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | available | 221 | SS 35/10 Kirilovka | 1,6+1,6 | 0.017647 | 0.23765 | 0.52 | 120 | -0.28235 | 0 | 1.68 | 1.9624 | 1.9624 | available | 0.85
222 | SS 35/6 Kislinskaya | 10+10 | 9.73 | 6.25 | 20 | 3.48 | 0 | 10.5 | 7.02 | 7.02 | available | 222 | SS 35/6 Kislinskaya | 10+10 | 0.0044944 | 9.7345 | 6.25 | 20 | 3.4845 | 0 | 10.5 | 7.0155 | 7.0155 | available | 0.89
223 | SS 35/10 Mixed fodder plant | 6,3+6,3 | 3.51 | 0.21 | 120 | 3.3 | 0 | 6.615 | 3.315 | 3.315 | available | 223 | SS 35/10 Mixed fodder plant | 6,3+6,3 | 0.79875 | 4.3087 | 0.21 | 120 | 4.0987 | 0 | 6.615 | 2.5162 | 2.5162 | available | 0.8
224 | SS 35/10 Kommunalnaya | 3,2+4 | 2.2 | 1.14 | 80 | 1.06 | 0 | 3.36 | 2.3 | 2.3 | available | 224 | SS 35/10 Kommunalnaya | 3,2+4 | 1.9294 | 4.1294 | 1.14 | 80 | 2.9894 | 0 | 3.36 | 0.37059 | 0.37059 | available | 0.85
225 | SS 35/10 Korenevo | 4+6,3 | 4.3 | 1.56 | 80 | 2.74 | 0 | 4.2 | 1.46 | 1.46 | available | 225 | SS 35/10 Korenevo | 4+6,3 | 5.8531 | 10.1531 | 1.56 | 80 | 8.5931 | 0 | 4.2 | -4.3931 | -4.3931 | unavailable | 0.98
226 | SS 35/10 Kremyanoe | 2,5+4 | 0.68 | 0.24 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 226 | SS 35/10 Kremyanoe | 2,5+4 | 0.025 | 0.705 | 0.24 | 120 | 0.465 | 0 | 2.625 | 2.16 | 2.16 | available | 0.92
227 | SS 35/10 Krupets | 1,8+2,5 | 1.23 | 0.42 | 120 | 0.81 | 0 | 1.89 | 1.08 | 1.08 | available | 227 | SS 35/10 Krupets | 1,8+2,5 | 0.21209 | 1.4421 | 0.42 | 120 | 1.0221 | 0 | 1.89 | 0.86791 | 0.86791 | available | 0.91
228 | SS 35/10 Kulbaki | 2,5+2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 228 | SS 35/10 Kulbaki | 2,5+2,5 | 1.0955 | 1.8955 | 0.6 | 120 | 1.2955 | 0 | 2.625 | 1.3295 | 1.3295 | available | 0.89
229 | SS 35/10 Kultprosvet | 2,5+2,5 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.625 | 2.665 | 2.665 | available | 229 | SS 35/10 Kultprosvet | 2,5+2,5 | 0 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.625 | 2.665 | 2.665 | available | 0.85
230 | SS 35/10 Kurchatov | 10+10 | 4.88 | 4.5 | 80 | 0.38 | 0 | 10.5 | 10.12 | 10.12 | available | 230 | SS 35/10 Kurchatov | 10+10 | 0 | 4.88 | 4.5 | 80 | 0.38 | 0 | 10.5 | 10.12 | 10.12 | available | 0.85
231 | SS 35/10 Kutok | 2,5+2,5 | 0.07 | 0.05 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 231 | SS 35/10 Kutok | 2,5+2,5 | 0 | 0.07 | 0.05 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 0.85
232 | SS 35/10 Linets | 2,5+2,5 | 0.42 | 0.25 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 232 | SS 35/10 Linets | 2,5+2,5 | 0.017647 | 0.43765 | 0.25 | 120 | 0.18765 | 0 | 2.625 | 2.4374 | 2.4374 | available | 0.85
233 | SS 35/10 Luch | 6,3+6,3 | 1.44 | 0.23 | 120 | 1.21 | 0 | 6.615 | 5.405 | 5.405 | available | 233 | SS 35/10 Luch | 6,3+6,3 | 1.4398 | 2.8798 | 0.23 | 120 | 2.6498 | 0 | 6.615 | 3.9652 | 3.9652 | available | 0.83
234 | SS 35/10 Lyubimovka-2 | 4+4 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | available | 234 | SS 35/10 Lyubimovka-2 | 4+4 | 0.082353 | 0.83235 | 1.59 | 80 | -0.75765 | 0 | 4.2 | 4.9576 | 4.9576 | available | 0.85
235 | SS 35/10 Matveevka | 2,5+2,5 | 0.92 | 0.08 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 235 | SS 35/10 Matveevka | 2,5+2,5 | 0 | 0.92 | 0.08 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 0.96
236 | SS 35/10 Mayak | 2,5+2,5 | 0.35 | 0.3 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 236 | SS 35/10 Mayak | 2,5+2,5 | 0.075294 | 0.42529 | 0.3 | 120 | 0.12529 | 0 | 2.625 | 2.4997 | 2.4997 | available | 0.85
237 | SS 35/10 Mikhailovka | 4+6,3 | 0.94 | 1.7 | 80 | -0.76 | 0 | 4.2 | 4.96 | 4.96 | available | 237 | SS 35/10 Mikhailovka | 4+6,3 | 0.52588 | 1.4659 | 1.7 | 80 | -0.23412 | 0 | 4.2 | 4.4341 | 4.4341 | available | 0.85
238 | SS 35/10 Murynovka | 4+4 | 0.34 | 0.3 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | available | 238 | SS 35/10 Murynovka | 4+4 | 0.40082 | 0.74082 | 0.3 | 120 | 0.44082 | 0 | 4.2 | 3.7592 | 3.7592 | available | 0.97
239 | SS 35/10 N. Borki | 2,5+2,5 | 0.51 | 0.63 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 239 | SS 35/10 N. Borki | 2,5+2,5 | 0.10556 | 0.61556 | 0.63 | 120 | -0.014444 | 0 | 2.625 | 2.6394 | 2.6394 | available | 0.9
240 | SS 35/10 Nikolskaya | 1,6+1,8 | 0.26 | 0.03 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 240 | SS 35/10 Nikolskaya | 1,6+1,8 | 0.0082353 | 0.26824 | 0.03 | 80 | 0.23824 | 0 | 1.68 | 1.4418 | 1.4418 | available | 0.85
241 | SS 35/10 Novaya | 2,5+2,5 | 0.73 | 0.4 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 241 | SS 35/10 Novaya | 2,5+2,5 | 0.50059 | 1.2306 | 0.4 | 120 | 0.83059 | 0 | 2.625 | 1.7944 | 1.7944 | available | 0.85
242 | SS 35/10 Orekhovo | 2,5+2,5 | 0.58 | 0.19 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | available | 242 | SS 35/10 Orekhovo | 2,5+2,5 | 0.086111 | 0.66611 | 0.19 | 120 | 0.47611 | 0 | 2.625 | 2.1489 | 2.1489 | available | 0.72
243 | SS 35/10 Orlovka | 2,5+2,5 | 0.17 | 0.95 | 120 | -0.78 | 0 | 2.625 | 3.405 | 3.405 | available | 243 | SS 35/10 Orlovka | 2,5+2,5 | 3.2241 | 3.3941 | 0.95 | 120 | 2.4441 | 0 | 2.625 | 0.18095 | 0.18095 | available | 0.79
244 | SS 35/10 Osotskoe | 2,5+2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 244 | SS 35/10 Osotskoe | 2,5+2,5 | 0.15294 | 0.34294 | 0.2 | 120 | 0.14294 | 0 | 2.625 | 2.4821 | 2.4821 | available | 0.85
245 | SS 35/10 Okhochevka | 4+6,3 | 1.26 | 0.74 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available | 245 | SS 35/10 Okhochevka | 4+6,3 | 0.045783 | 1.3058 | 0.74 | 120 | 0.56578 | 0 | 4.2 | 3.6342 | 3.6342 | available | 0.83
246 | SS 35/10 Panino | 2,5+2,5 | 0.39 | 0.11 | 80 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | available | 246 | SS 35/10 Panino | 2,5+2,5 | 0.027059 | 0.41706 | 0.11 | 80 | 0.30706 | 0 | 2.625 | 2.3179 | 2.3179 | available | 0.85
247 | SS 35/10 Pervoavgustovka | 2,5+3,2 | 0.39 | 0.52 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | available | 247 | SS 35/10 Pervoavgustovka | 2,5+3,2 | 0.031765 | 0.42176 | 0.52 | 120 | -0.098235 | 0 | 2.625 | 2.7232 | 2.7232 | available | 0.85
248 | SS 35/10 Petrinka | 2,5+4 | 2.21 | 0.3 | 120 | 1.91 | 0 | 2.625 | 0.715 | 0.715 | available | 248 | SS 35/10 Petrinka | 2,5+4 | 0.57059 | 2.7806 | 0.3 | 120 | 2.4806 | 0 | 2.625 | 0.14441 | 0.14441 | available | 0.85
249 | SS 35/10 Platava | 2,5+2,5 | 1.66 | 0.26 | 120 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | available | 249 | SS 35/10 Platava | 2,5+2,5 | 0.13125 | 1.7913 | 0.26 | 120 | 1.5312 | 0 | 2.625 | 1.0938 | 1.0938 | available | 0.96
250 | SS 35/10 Pogozhee | 1,6+1,6 | 0.3 | 0.46 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | available | 250 | SS 35/10 Pogozhee | 1,6+1,6 | 0 | 0.3 | 0.46 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | available | 0.84
251 | SS 35/10 Porechnoe | 4+4 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | available | 251 | SS 35/10 Porechnoe | 4+4 | 0.075294 | 0.57529 | 1.16 | 120 | -0.58471 | 0 | 4.2 | 4.7847 | 4.7847 | available | 0.85
252 | SS 35/10 Pochepnoe | 6,3+6,3 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available | 252 | SS 35/10 Pochepnoe | 6,3+6,3 | 0 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available | 0.85
253 | SS 35/10 Prigorodnoe | 2,5+2,5 | 0.56 | 0.3 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | available | 253 | SS 35/10 Prigorodnoe | 2,5+2,5 | 0.12941 | 0.68941 | 0.3 | 80 | 0.38941 | 0 | 2.625 | 2.2356 | 2.2356 | available | 0.85
245 | SS 35/10 Pselets | 1,6+1,6 | 0.2 | 0.42 | 120 | -0.22 | 0 | 1.68 | 1.9 | 1.9 | available | 254 | SS 35/10 Pselets | 1,6+1,6 | 1.8286 | 2.0286 | 0.42 | 120 | 1.6086 | 0 | 1.68 | 0.071429 | 0.071429 | available | 0.7
255 | SS 35/10 Puzachi | 1,6+4 | 0.39 | 0.43 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 255 | SS 35/10 Puzachi | 1,6+4 | 0.38412 | 0.77412 | 0.43 | 120 | 0.34412 | 0 | 1.68 | 1.3359 | 1.3359 | available | 0.85
256 | SS 35/10 Pushkarnoe | 2,5+2,5 | 0.86 | 0.32 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 256 | SS 35/10 Pushkarnoe | 2,5+2,5 | 0.089362 | 0.94936 | 0.32 | 120 | 0.62936 | 0 | 2.625 | 1.9956 | 1.9956 | available | 0.94
257 | SS 35/10 R.Kolodets | 2,5+2,5 | 0.48 | 0.44 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 257 | SS 35/10 R.Kolodets | 2,5+2,5 | 0 | 0.48 | 0.44 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 0.84
258 | SS 35/10 Razvetye | 4+4 | 1.1 | 1.03 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | available | 258 | SS 35/10 Razvetye | 4+4 | 0.61059 | 1.7106 | 1.03 | 120 | 0.68059 | 0 | 4.2 | 3.5194 | 3.5194 | available | 0.85
259 | SS 35/10 V. Reutets | 4+4 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | available | 259 | SS 35/10 V. Reutets | 4+4 | 0.011765 | 0.19176 | 0.11 | 120 | 0.081765 | 0 | 4.2 | 4.1182 | 4.1182 | available | 0.85
260 | SS 35/10 Rozhdestvenka | 1,6+1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | available | 260 | SS 35/10 Rozhdestvenka | 1,6+1,6 | 0 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | available | 0.84
261 | SS 35/10 Rubilnik | 2,5+2,5 | 1.97 | 1.18 | 80 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 261 | SS 35/10 Rubilnik | 2,5+2,5 | 0 | 1.97 | 1.18 | 80 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 0.94
262 | SS 35/10 Ryzhkovo | 1,6+1,6 | 0.5 | 0.08 | 20 | 0.42 | 0 | 1.68 | 1.26 | 1.26 | available | 262 | SS 35/10 Ryzhkovo | 1,6+1,6 | 0.5383 | 1.0383 | 0.08 | 20 | 0.9583 | 0 | 1.68 | 0.7217 | 0.7217 | available | 0.94
263 | SS 35/10 Sapogovo | 2,5+2,5 | 1.44 | 0.6 | 20 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | available | 263 | SS 35/10 Sapogovo | 2,5+2,5 | 1.5065 | 2.9465 | 0.6 | 20 | 2.3465 | 0 | 2.625 | 0.27847 | 0.27847 | available | 0.98
264 | SS 35/10 Svoboda-selskaya | 6,3+6,3 | 3.4 | 2.25 | 80 | 1.15 | 0 | 6.615 | 5.465 | 5.465 | available | 264 | SS 35/10 Svoboda-selskaya | 6,3+6,3 | 0.21579 | 3.6158 | 2.25 | 80 | 1.3658 | 0 | 6.615 | 5.2492 | 5.2492 | available | 0.95
265 | SS 35/10 Selektsionnaya | 4+4 | 2.34 | 1.4 | 45 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | available | 265 | SS 35/10 Selektsionnaya | 4+4 | 0.25561 | 2.5956 | 1.4 | 45 | 1.1956 | 0 | 4.2 | 3.0044 | 3.0044 | available | 0.98
266 | SS 35/10 Semyonovka | 2,5+2,5 | 0.23 | 0 | - | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 266 | SS 35/10 Semyonovka | 2,5+2,5 | 0.011765 | 0.24176 | 0 | - | 0.24176 | 0 | 2.625 | 2.3832 | 2.3832 | available | 0.85
267 | SS 35/10 Seed plant | 2,5+2,5 | 0.51 | 0.6 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | available | 267 | SS 35/10 Seed plant | 2,5+2,5 | 0.057647 | 0.56765 | 0.6 | 120 | -0.032353 | 0 | 2.625 | 2.6574 | 2.6574 | available | 0.85
268 | SS 35/10 Snagost | 4+4 | 1.17 | 0.05 | 10 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | available | 268 | SS 35/10 Snagost | 4+4 | 0.028125 | 1.1981 | 0.05 | 10 | 1.1481 | 0 | 4.2 | 3.0519 | 3.0519 | available | 0.96
269 | SS 35/10 SOM | 1,6+4 | 1.01 | 0.08 | 10 | 0.93 | 0 | 1.68 | 0.75 | 0.75 | available | 269 | SS 35/10 SOM | 1,6+4 | 0.11446 | 1.1245 | 0.08 | 10 | 1.0445 | 0 | 1.68 | 0.63554 | 0.63554 | available | 0.83
270 | SS 35/10 Sosnovy Bor | 3,2+4 | 0.92 | 0.69 | 120 | 0.23 | 0 | 3.36 | 3.13 | 3.13 | available | 270 | SS 35/10 Sosnovy Bor | 3,2+4 | 0.10235 | 1.0224 | 0.69 | 120 | 0.33235 | 0 | 3.36 | 3.0276 | 3.0276 | available | 0.85
271 | SS 35/10 Stakanovo | 2,5+2,5 | 1.02 | 0.58 | 80 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 271 | SS 35/10 Stakanovo | 2,5+2,5 | 0.059756 | 1.0798 | 0.58 | 80 | 0.49976 | 0 | 2.625 | 2.1252 | 2.1252 | available | 0.82
272 | SS 35/10 Starkovo | 1,6+1,6 | 0.42 | 0.2 | 80 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 272 | SS 35/10 Starkovo | 1,6+1,6 | 0.035294 | 0.45529 | 0.2 | 80 | 0.25529 | 0 | 1.68 | 1.4247 | 1.4247 | available | 0.85
273 | CC 35/10 Starshee | 1,6+1,6 | 0.2 | 0.2 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 273 | CC 35/10 Starshee | 1,6+1,6 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 0.85
274 | SS 35/10 Teplitsy | 4+4 | 1.1 | 1.08 | 45 | 0.02 | 0 | 4.2 | 4.18 | 4.18 | available | 274 | SS 35/10 Teplitsy | 4+4 | 0.11412 | 1.2141 | 1.08 | 45 | 0.13412 | 0 | 4.2 | 4.0659 | 4.0659 | available | 0.85
275 | SS 35/10 Turovka | 2,5+2,5 | 0.44 | 0.6 | 120 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | available | 275 | SS 35/10 Turovka | 2,5+2,5 | 0.13529 | 0.57529 | 0.6 | 120 | -0.024706 | 0 | 2.625 | 2.6497 | 2.6497 | available | 0.85
276 | SS 35/10 Uspenka | 2,5+2,5 | 1.23 | 1 | 80 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 276 | SS 35/10 Uspenka | 2,5+2,5 | 0.32941 | 1.5594 | 1 | 80 | 0.55941 | 0 | 2.625 | 2.0656 | 2.0656 | available | 0.85
277 | SS 35/6 Tsentralnaya | 40+40 | 21.2 | 5 |  | 16.2 | 0 | 42 | 25.8 | 25.8 | available | 277 | SS 35/6 Tsentralnaya | 40+40 | 0 | 21.2 | 5 |  | 16.2 | 0 | 42 | 25.8 | 25.8 | available | 0.91
278 | SS 35/10 Chermoshnoe | 2,5+2,5 | 0.25 | 0.5 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | available | 278 | SS 35/10 Chermoshnoe | 2,5+2,5 | 0.011765 | 0.26176 | 0.5 | 120 | -0.23824 | 0 | 2.625 | 2.8632 | 2.8632 | available | 0.85
279 | SS 35/10 Shatalovka | 2,5+4 | 0.34 | 0.21 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available | 279 | SS 35/10 Shatalovka | 2,5+4 | 0.0061728 | 0.34617 | 0.21 | 80 | 0.13617 | 0 | 2.625 | 2.4888 | 2.4888 | available | 0.81
280 | SS 35/10 Shipy | 2,5+2,5 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 280 | SS 35/10 Shipy | 2,5+2,5 | 0 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 0.83
281 | SS 35/10 Elevator | 4+6,3 | 1.22 | 0.6 | 120 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | available | 281 | SS 35/10 Elevator | 4+6,3 | 0.26977 | 1.4898 | 0.6 | 120 | 0.88977 | 0 | 4.2 | 3.3102 | 3.3102 | available | 0.86
282 | SS 35/10 Yugo-Zapadnaya | 10+10 | 8.74 | 4.7 | 80 | 4.04 | 0 | 10.5 | 6.46 | 6.46 | available | 282 | SS 35/10 Yugo-Zapadnaya | 10+10 | 4.191 | 12.931 | 4.7 | 80 | 8.231 | 0 | 10.5 | 2.269 | 2.269 | available | 0.89
283 | SS 35/10 Plant of reinforced-concrete products | 2,5+2,5 | 3.11 | 3.9 | 120 | -0.79 | 0 | 2.625 | 3.415 | 3.415 | available | 283 | SS 35/10 Plant of reinforced-concrete products | 2,5+2,5 | 0.45529 | 3.5653 | 3.9 | 120 | -0.33471 | 0 | 2.625 | 2.9597 | 2.9597 | available | 0.85
| TOTAL: | 3304.9 | 696.51 | 787.52 | [5 empty] | 1365.84 |  | 2: TOTAL:; 3: 3304.9; 4: 236.3144; 5: 932.8244; MVA 6: 787.42; Min 12: 1231.0109
| deficit | [8 empty] | -7.2 |  | 2: deficit; Min 12: -46.7845
| proficit | [8 empty] | 1358.64 |  | 2: proficit; Min 12: 1184.2259
| *Note: the power shortage at the substation Vysokaya due to transfer loads from the substation Central | [10 empty] | 2: *Note: The facilities are included in the Investment Program for 2012-2017.
| and will be removed after commissioning of SWG-10kV at substation Central. | [10 empty] | 2: Power shortage will be removed after the reconstruction and replacement of transformers with higher power.
|  | Deputy director for technical policy - | [9 empty] | 3: Deputy director for technical policy -
|  | Chief engineer | [6 empty] | A.N. Rudnevsky |  |  | 3: Chief engineer; Min 10: A.N. Rudnevsky

## Total current deficit
The list of closed supply centers of IDGC of Centre - Kurskenergo division in winter 2011 (current deficit of capacity)
Item # | Name of supply center, voltage class |  | Current deficit, MVA
Kurskenergo
1. | SS 110/10 Vysokaya* | 16+16 | -7.2
Total current deficit (winter 2011) |  | 32 | -7.2
*Note: Power shortage at SS Vysokaya is due to transfer of load
from SS Central and will be removed after the transfer of load by customers

## Total expected deficit
The list of closed supply centers of IDGC of Centre - Kurskenergo division with expected load taking into account new connections and other development of the electical networks (expected deficit of capacity) for April 2012
Item # | Name of supply center, voltage class | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Expected deficit, MVA
Kurskenergo
1 | SS 110/10 Beketovo | 6.3 | -1.245
2 | SS 35/10 Bykovo | 4 | -3.564
3 | SS 35/10 Vasilevka | 2.5 | -0.559
4 | SS 35/10 Water storage | 4 | -4.316
5 | SS 35/10 Irrigating | 4 | -2.685
6 | SS 35/10 Pristen | 4 | -7.6
7 | SS 35/10 Yasenki | 2.5 | -2.691
8 | SS 110/10 Vysokaya | 16+16 | -7.2
9 | SS 110/35/10 Gorshechnoye | 10+16 | -7.776
10 | SS 110/35/10 Kamyshi | 6,3+6,3 | -4.756
11 | SS 35/10 Korenevo | 4+6,3 | -4.3931
Total expected deficit (winter 2012) |  | 108.2 | -46.7851
*Note: The facilities are included in the Investment Program for 2012-2017.
Power shortage will be removed after the reconstruction and replacement of transformers
with higher power.