## Lipetsk
Transmission capacity calculation of supply centers of IDGC of Centre - Lipetskenergo division following the results of measurements of peak loads in winter 2011
table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | Note | cosφ | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period | Total capacity redistributed according to operating rules, MVA for the time period | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA | [5 empty] | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | MVA | Min | [12 empty] | MVA | Min
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
1 | SS 110/10 kV Lev Tolstoy | 10 | 10 | 2 | 1.8 | 30 | 0.2 | 0 | 1.8 | -0.2 | -0.2 | unavailable | 0.98 | 1 | SS 110/10 kV Lev Tolstoy | 10 | 0.821 | 2.821 | 1.8 | 30 | 1.021 | 0 | 1.8 | -1.021 | -1.021 | unavailable
2 | SS 110/10 kV Dvurechki | 6.3 | 6.3 | 1.6 | 0.1 | 70 | 1.5 | 0 | 0.1 | -1.5 | -1.5 | unavailable | 0.95 | 2 | SS 110/10 kV Dvurechki | 6.3 | 1.041 | 2.641 | 0.1 | 70 | 2.541 | 0 | 0.1 | -2.541 | -2.541 | unavailable
3 | SS 35/10 kV Vesyoloe | 2.5 | 2.5 | 0.10795 | 0.07 | 100 | 0.037952 | 0 | 0.07 | -0.037952 | -0.037952 | unavailable | 0.87 | 3 | SS 35/10 kV Vesyoloe | 2.5 | 0.026 | 0.13395 | 0.07 | 100 | 0.063952 | 0 | 0.07 | -0.063952 | -0.063952 | unavailable
4 | SS 35/10 kV Kr.Palna | 3.2 | 3.2 | 0.88161 | 0.11 | 180 | 0.77161 | 0 | 0.11 | -0.77161 | -0.77161 | unavailable | 0.92 | 4 | SS 35/10 kV Kr.Palna | 3.2 | 0.519 | 1.4006 | 0.11 | 180 | 1.2906 | 0 | 0.11 | -1.2906 | -1.2906 | unavailable
5 | SS 35/10 kV Kamenka | 2.5 | 2.5 | 0.81742 | 0 | 0 | 0.81742 | 0 | 0 | -0.81742 | -0.81742 | unavailable | 0.94 | 5 | SS 35/10 kV Kamenka | 2.5 | 0.334 | 1.1514 | 0 | 0 | 1.1514 | 0 | 0 | -1.1514 | -1.1514 | unavailable
6 | SS 35/10 kV Krasotynovka | 2.5 | 2.5 | 0.47229 | 0.29 | 60 | 0.18229 | 0 | 0.29 | -0.18229 | -0.18229 | unavailable | 0.92 | 6 | SS 35/10 kV Krasotynovka | 2.5 |  | 0.47229 | 0.29 | 60 | 0.18229 | 0 | 0.29 | -0.18229 | -0.18229 | unavailable
7 | SS 35/10 kV Ozyorki | 2.5 | 2.5 | 0.11003 | 0 | 0 | 0.11003 | 0 | 0 | -0.11003 | -0.11003 | unavailable | 0.79 | 7 | SS 35/10 kV Ozyorki | 2.5 |  | 0.11003 | 0 | 0 | 0.11003 | 0 | 0 | -0.11003 | -0.11003 | unavailable
8 | SS 35/10 kV Pankratovka | 2.5 | 2.5 | 0.50862 | 0.05 | 90 | 0.45862 | 0 | 0.05 | -0.45862 | -0.45862 | unavailable | 0.86 | 8 | SS 35/10 kV Pankratovka | 2.5 | 0.015 | 0.52362 | 0.05 | 90 | 0.47362 | 0 | 0.05 | -0.47362 | -0.47362 | unavailable
9 | SS 35/10 kV Preobrazhenye | 2.5 | 2.5 | 0.41485 | 0 | 0 | 0.41485 | 0 | 0 | -0.41485 | -0.41485 | unavailable | 0.87 | 9 | SS 35/10 kV Preobrazhenye | 2.5 | 0.008 | 0.42285 | 0 | 0 | 0.42285 | 0 | 0 | -0.42285 | -0.42285 | unavailable
10 | SS 35/10 kV Yakovlevo | 2.5 | 2.5 | 0.81082 | 0 | 0 | 0.81082 | 0 | 0 | -0.81082 | -0.81082 | unavailable | 0.9 | 10 | SS 35/10 kV Yakovlevo | 2.5 | 0.468 | 1.2788 | 0 | 0 | 1.2788 | 0 | 0 | -1.2788 | -1.2788 | unavailable
11 | SS 35/10 kV Pervomayskaya | 2.5 | 2.5 | 0.83636 | 0.3 | 60 | 0.53636 | 0 | 0.3 | -0.53636 | -0.53636 | unavailable | 0.88 | 11 | SS 35/10 kV Pervomayskaya | 2.5 | 0.028 | 0.86436 | 0.3 | 60 | 0.56436 | 0 | 0.3 | -0.56436 | -0.56436 | unavailable
12 | SS 35/10 kV Kamennaya Lubna | 2.5 | 2.5 | 0.94545 | 0.9 | 90 | 0.045455 | 0 | 0.9 | -0.045455 | -0.045455 | unavailable | 0.96 | 12 | SS 35/10 kV Kamennaya Lubna | 2.5 | 0.071 | 1.0165 | 0.9 | 90 | 0.11645 | 0 | 0.9 | -0.11645 | -0.11645 | unavailable
13 | SS 35/10 kV Znamenka | 2.5 | 2.5 | 0.54545 | 0 | 0 | 0.54545 | 0 | 0 | -0.54545 | -0.54545 | unavailable | 0.93 | 13 | SS 35/10 kV Znamenka | 2.5 |  | 0.54545 | 0 | 0 | 0.54545 | 0 | 0 | -0.54545 | -0.54545 | unavailable
14 | SS 35/10 kV Pikovo | 2.5 | 2.5 | 0.50909 | 0.5 | 120 | 0.0090909 | 0 | 0.5 | -0.0090909 | -0.0090909 | unavailable | 0.88 | 14 | SS 35/10 kV Pikovo | 2.5 | 0.027 | 0.53609 | 0.5 | 120 | 0.036091 | 0 | 0.5 | -0.036091 | -0.036091 | unavailable
15 | SS 35/10 kV Nikolskoe | 4 | 4 | 0.27273 | 0.8 | 120 | -0.52727 | 0 | 0.8 | 0.52727 | 0.52727 | available | 0.97 | 15 | SS 35/10 kV Nikolskoe | 4 | 0.016 | 0.28873 | 0.8 | 120 | -0.51127 | 0 | 0.8 | 0.51127 | 0.51127 | available
16 | SS 35/10 kV Peskovatka | 1.6 | 1.6 | 0.52 | 0.13 | 70 | 0.39 | 0 | 0.13 | -0.39 | -0.39 | unavailable | 0.95 | 16 | SS 35/10 kV Peskovatka | 1.6 | 0.007 | 0.527 | 0.13 | 70 | 0.397 | 0 | 0.13 | -0.397 | -0.397 | unavailable
17 | SS 35/6 kV Druzhba | 5.6 | 5.6 | КРУНН-6kV не наши | [9 empty] | 1: 17; 2: SS 35/6 kV Druzhba; 3: 5.6; 5: 0
18 | SS 35/10 kV SOM | 1.6 | 1.6 | 0.173 | 0 | 0 | 0.173 | 0 | 0 | -0.173 | -0.173 | unavailable | 0.85 | 18 | SS 35/10 kV SOM | 1.6 |  | 0.173 | 0 | 0 | 0.173 | 0 | 0 | -0.173 | -0.173 | unavailable
19 | SS 35/6 kV Novonikolaevka | 4 | 4 | 0.87953 | 0 | 0 | 0.87953 | 0 | 0 | -0.87953 | -0.87953 | unavailable | 0.944 | 19 | SS 35/6 kV Novonikolaevka | 4 | 0.015 | 0.89453 | 0 | 0 | 0.89453 | 0 | 0 | -0.89453 | -0.89453 | unavailable
20 | SS 35/10 kV Sindyakino | 2.5 | 2.5 | 0.22006 | 0 | 0 | 0.22006 | 0 | 0 | -0.22006 | -0.22006 | unavailable | 0.89 | 20 | SS 35/10 kV Sindyakino | 2.5 | 0.122 | 0.34206 | 0 | 0 | 0.34206 | 0 | 0 | -0.34206 | -0.34206 | unavailable
21 | SS 35/10 kV Kurino | 2.5 | 2.5 | 0.45845 | 0.09 | 40 | 0.36845 | 0 | 0.09 | -0.36845 | -0.36845 | unavailable | 0.901 | 21 | SS 35/10 kV Kurino | 2.5 | 0.85 | 1.3084 | 0.09 | 40 | 1.2185 | 0 | 0.09 | -1.2185 | -1.2185 | unavailable
22 | SS 35/10 kV Novodubovoe | 2.5 | 2.5 | 1.0536 | 0 | 0 | 1.0536 | 0 | 0 | -1.0536 | -1.0536 | unavailable | 0.87 | 22 | SS 35/10 kV Novodubovoe | 2.5 | 0.042 | 1.0956 | 0 | 0 | 1.0956 | 0 | 0 | -1.0956 | -1.0956 | unavailable
23 | SS 35/10 kV Beryozovka | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 23 | SS 35/10 kV Beryozovka | 2.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | unavailable
24 | SS 35/6 kV Karyer | 4 | 4 | 0.00865 | [8 empty] | 0.99 | 1: 24; 2: SS 35/6 kV Karyer; 3: 4; 5: 0.00865
25 | SS 110/35/10 kV Chaplygin | 6.3 | 6.3 | 3.9455 | 2.5 | 120 | 1.4455 | 0 | 2.5 | -1.4455 | -1.4455 | unavailable | 0.84 | 25 | SS 110/35/10 kV Chaplygin | 6.3 | 0.675 | 4.6205 | 2.5 | 120 | 2.1205 | 0 | 2.5 | -2.1205 | -2.1205 | unavailable
Two- and more transformer substations (for two voltage levels) | [13 empty] | 1: Two- and more transformer substations (for two voltage levels)
26 | SS 110/6 kV Agregatnaya | 16+16 | 32 | 13.3015 | 0 | 0 | 13.3015 | 0 | 16.8 | 3.4985 | 3.4985 | available | 0.93 | 26 | SS 110/6 kV Agregatnaya | 16+16 | 2.291 | 15.5925 | 0 | 0 | 15.5925 | 0 | 16.8 | 1.2075 | 1.2075 | available
27 | SS 110/6 kV Zapadnaya | 40+40 | 80 | 17.6664 | 0 | 0 | 17.6664 | 0 | 42 | 24.3336 | 24.3336 | available | 0.89 | 27 | SS 110/6 kV Zapadnaya | 40+40 | 6.442 | 24.1084 | 0 | 0 | 24.1084 | 0 | 42 | 17.8916 | 17.8916 | available
28 | SS 110/10 kV Kashary | 2,5+6,3 | 8.8 | 1.7859 | 0.433 | 60 | 1.3529 | 0 | 2.625 | 1.2721 | 1.2721 | available | 0.66 | 28 | SS 110/10 kV Kashary | 2,5+6,3 | 0.313 | 2.0989 | 0.433 | 60 | 1.6659 | 0 | 2.625 | 0.95914 | 0.95914 | available
29 | SS 110/10kV Terbun potter | 25+25 | 50 | 0 | 0 | 0 | 0 | 0 | 26.25 | 26.25 | 26.25 | available |  | 29 | SS 110/10kV Terbun potter | 25+25 | 13.15 | 13.15 | 0 | 0 | 13.15 | 0 | 26.25 | 13.1 | 13.1
30 | SS 110/6 kV Tabak | 16+16 | 32 | 7.8323 | 3.2 | 20 | 4.6323 | 0 | 16.8 | 12.1677 | 12.1677 | available | 0.96 | 30 | SS 110/6 kV Tabak | 16+16 | 0.188 | 8.0203 | 3.2 | 20 | 4.8203 | 0 | 16.8 | 11.9797 | 11.9797 | available
31 | SS 110/10 kV Lukoshkino | 10+2,5 | 12.5 | 0.65103 | 0 | 0 | 0.65103 | 0 | 2.625 | 1.974 | 1.974 | available | 0.95 | 31 | SS 110/10 kV Lukoshkino | 10+2,5 | 0.035 | 0.68603 | 0 | 0 | 0.68603 | 0 | 2.625 | 1.939 | 1.939 | available
32 | SS 110/10kV Niva | 10+10 | 20 | 5.09 | 3 | 120 | 2.09 | 0 | 10.5 | 8.41 | 8.41 | available | 0.91 | 32 | SS 110/10kV Niva | 10+10 | 0.457 | 5.547 | 3 | 120 | 2.547 | 0 | 10.5 | 7.953 | 7.953 | available
33 | SS 110/10 kV Olkhovets | 2,5+2,5 | 5 | 1.2 | 1 | 90 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 0.89 | 33 | SS 110/10 kV Olkhovets | 2,5+2,5 | 0.207 | 1.407 | 1 | 90 | 0.407 | 0 | 2.625 | 2.218 | 2.218 | available
34 | SS 110/10 kV Kuyman | 2,5+2,5 | 5 | 0.72727 | 1 | 90 | -0.27273 | 0 | 2.625 | 2.8977 | 2.8977 | * | 0.93 | 34 | SS 110/10 kV Kuyman | 2,5+2,5 | 1.052 | 1.7793 | 1 | 90 | 0.77927 | 0 | 2.625 | 1.8457 | 1.8457 | available
35 | SS 110/10 kV Lutoshkino | 2,5+2,5 | 5 | 0.29091 | 0.4 | 60 | -0.10909 | 0 | 2.625 | 2.7341 | 2.7341 | available | 0.91 | 35 | SS 110/10 kV Lutoshkino | 2,5+2,5 | 0.023 | 0.31391 | 0.4 | 60 | -0.086091 | 0 | 2.625 | 2.7111 | 2.7111 | available
36 | SS 110/10 kV Krugloe | 2,5+2,5 | 5 | 0.54545 | 0.5 | 60 | 0.045455 | 0 | 2.625 | 2.5795 | 2.5795 | available | 0.93 | 36 | SS 110/10 kV Krugloe | 2,5+2,5 |  | 0.54545 | 0.5 | 60 | 0.045455 | 0 | 2.625 | 2.5795 | 2.5795 | available
37 | SS 110/10/6 kV Yugo-Zapadnaya | 40+40 | 80 | 40.03 | 4.5 | 30 | 35.53 | 0 | 42 | 6.47 | 6.47 | * | 0.93 | 37 | SS 110/10/6 kV Yugo-Zapadnaya | 40+40 | 25.533 | 65.563 | 4.5 | 30 | 61.063 | 0 | 42 | -19.063 | -19.063 | unavailable
38 | SS 110/6 kV Privokzalnaya | 20+20+25 | 65 | 40.51 | 1.38 | 30 | 39.13 | 0 | 42 | 2.87 | 2.87 | available | 0.95 | 38 | SS 110/6 kV Privokzalnaya | 20+20+25 | 0.357 | 40.867 | 1.38 | 30 | 39.487 | 0 | 42 | 2.513 | 2.513 | available
39 | SS 110/10/6 kV Yuzhnaya | 40+40 | 80 | 40.39 | 6 | 30 | 34.39 | 0 | 42 | 7.61 | 7.61 | * | 0.98 | 39 | SS 110/10/6 kV Yuzhnaya | 40+40 | 4.871 | 45.261 | 6 | 30 | 39.261 | 0 | 42 | 2.739 | 2.739 | *
40 | SS 110/6 kV Sitovka | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | * | 0.95 | 40 | SS 110/6 kV Sitovka | 10+10 |  | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
41 | SS 110/6 kV LTP | 6,3+10 | 16.3 | 2.54 | 0 | 0 | 2.54 | 0 | 6.615 | 4.075 | 4.075 | * | 0.95 | 41 | SS 110/6 kV LTP | 6,3+10 | 0.014 | 2.554 | 0 | 0 | 2.554 | 0 | 6.615 | 4.061 | 4.061 | *
42 | SS 110/6 kV KPD | 10+16 | 26 | 2.1 | 0 | 0 | 2.1 | 0 | 10.5 | 8.4 | 8.4 | * | 0.97 | 42 | SS 110/6 kV KPD | 10+16 | 2.426 | 4.526 | 0 | 0 | 4.526 | 0 | 10.5 | 5.974 | 5.974 | *
43 | SS 110/10 kV Oktyabskaya | 40+40 | 80 | 19.779 | 0.12 | 20 | 19.659 | 0 | 42 | 22.341 | 22.341 | * | 0.98 | 43 | SS 110/10 kV Oktyabskaya | 40+40 | 0.648 | 20.427 | 0.12 | 20 | 20.307 | 0 | 42 | 21.693 | 21.693 | *
44 | SS 110/10 kV Manezhnaya | 40+40 | 80 | 0.48 | 0 | 0 | 0.48 | 0 | 42 | 41.52 | 41.52 | * |  | 44 | SS 110/10 kV Manezhnaya | 40+40 | 39.501 | 39.981 | 0 | 0 | 39.981 | 0 | 42 | 2.019 | 2.019 | available
45 | SS 110/10 kV Universitetskaya | 40+40 | 80 | 0.21 | 0 | 0 | 0.21 | 0 | 42 | 41.79 | 41.79 | available | 0.99 | 45 | SS 110/10 kV Universitetskaya | 40+40 | 42.8 | 43.01 | 0 | 0 | 43.01 | 0 | 42 | -1.01 | -1.01 | unavailable
46 | SS 110/6 kV Teplichnaya | 15+15 | 30 | 6.96 | 0 | 0 | 6.96 | 0 | 15.75 | 8.79 | 8.79 | * | 1 | 46 | SS 110/6 kV Teplichnaya | 15+15 | 4.24 | 11.2 | 0 | 0 | 11.2 | 0 | 15.75 | 4.55 | 4.55 | *
47 | SS 110/6 kV Trubnaya-2 | 25+25 | 50 | 3.6 | 0 | 0 | 3.6 | 0 | 26.25 | 22.65 | 22.65 | * | 0.96 | 47 | SS 110/6 kV Trubnaya-2 | 25+25 | 20.64 | 24.24 | 0 | 0 | 24.24 | 0 | 26.25 | 2.01 | 2.01 | *
48 | SS 110/6 kV GPP-2 LTZ | 63+63 | 126 | 12.37 | 0 | 0 | 12.37 | 0 | 66.15 | 53.78 | 53.78 | * | 0.93 | 48 | SS 110/6 kV GPP-2 LTZ | 63+63 | 7.275 | 19.645 | 0 | 0 | 19.645 | 0 | 66.15 | 46.505 | 46.505 | *
49 | SS 35/10 kV Avangard | 4+4 | 8 | 1.41 | 1.2 | 1.2 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | available | 0.87792 | 49 | SS 35/10 kV Avangard | 4+4 | 0.028 | 1.438 | 1.2 | 1.2 | 0.238 | 0 | 4.2 | 3.962 | 3.962 | available
50 | SS 35/10 kV Afanasysevo | 2,5+2,5 | 5 | 1.4 | 0 | 0 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | available | 0.91 | 50 | SS 35/10 kV Afanasysevo | 2,5+2,5 | 0.145 | 1.545 | 0 | 0 | 1.545 | 0 | 2.625 | 1.08 | 1.08 | available
51 | SS 35/10 kV Babarykino | 2,5+2,5 | 5 | 0.66 | 0.15 | 260 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | available | 0.94 | 51 | SS 35/10 kV Babarykino | 2,5+2,5 | 0.111 | 0.771 | 0.15 | 260 | 0.621 | 0 | 2.625 | 2.004 | 2.004 | available
52 | SS 35/10 kV Avrora | 2,5+2,5 | 5 | 1.1958 | 0.618 | 60 | 0.57778 | 0 | 2.625 | 2.0472 | 2.0472 | available | 0.92 | 52 | SS 35/10 kV Avrora | 2,5+2,5 | 2.895 | 4.0908 | 0.618 | 60 | 3.4728 | 0 | 2.625 | -0.84778 | -0.84778 | unavailable
53 | SS 35/10 kV B.Boyovka | 2,5+2,5 | 5 | 0.34946 | 0.15 | 100 | 0.19946 | 0 | 2.625 | 2.4255 | 2.4255 | available | 0.9 | 53 | SS 35/10 kV B.Boyovka | 2,5+2,5 |  | 0.34946 | 0.15 | 100 | 0.19946 | 0 | 2.625 | 2.4255 | 2.4255 | available
54 | SS 35/10 kV Borki | 2,5+2,5 | 5 | 0.91759 | 0 | 0 | 0.91759 | 0 | 2.625 | 1.7074 | 1.7074 | available | 0.9 | 54 | SS 35/10 kV Borki | 2,5+2,5 | 0.016 | 0.93359 | 0 | 0 | 0.93359 | 0 | 2.625 | 1.6914 | 1.6914 | available
55 | SS 35/6kV Vostochnaya | 10+16 | 26 | 6.295 | 4.8 | 20 | 1.495 | 0 | 10.5 | 9.005 | 9.005 | available | 0.94 | 55 | SS 35/6kV Vostochnaya | 10+16 | 0.73 | 7.025 | 4.8 | 20 | 2.225 | 0 | 10.5 | 8.275 | 8.275 | available
56 | SS 35/10 kV Vasilyevka | 2,5+2,5 | 5 | 0.73179 | 0.02 | 60 | 0.71179 | 0 | 2.625 | 1.9132 | 1.9132 | available | 0.89 | 56 | SS 35/10 kV Vasilyevka | 2,5+2,5 | 0.02 | 0.75179 | 0.02 | 60 | 0.73179 | 0 | 2.625 | 1.8932 | 1.8932 | available
57 | SS 35/10 kV Voronets | 4+4 | 8 | 1.53 | 1.2 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | available | 0.86 | 57 | SS 35/10 kV Voronets | 4+4 | 0.257 | 1.787 | 1.2 | 120 | 0.587 | 0 | 4.2 | 3.613 | 3.613 | available
58 | SS 35/6 kV Golikovo | 1,8+1,6 | 3.4 | 1.4278 | 0 | 0 | 1.4278 | 0 | 1.68 | 0.25223 | 0.25223 | available | 0.81 | 58 | SS 35/6 kV Golikovo | 1,8+1,6 | 0.062 | 1.4898 | 0 | 0 | 1.4898 | 0 | 1.68 | 0.19023 | 0.19023 | available
59 | SS 35/10 kV Gatishche | 2,5+2,5 | 5 | 0.36745 | 0 | 0 | 0.36745 | 0 | 2.625 | 2.2575 | 2.2575 | available | 0.81 | 59 | SS 35/10 kV Gatishche | 2,5+2,5 | 0.01 | 0.37745 | 0 | 0 | 0.37745 | 0 | 2.625 | 2.2475 | 2.2475 | available
60 | SS 35/10 kV Gnilusha | 6,3+6,3 | 12.6 | 2.1016 | 0.05 | 40 | 2.0516 | 0 | 6.615 | 4.5634 | 4.5634 | available | 0.86 | 60 | SS 35/10 kV Gnilusha | 6,3+6,3 | 1.33 | 3.4316 | 0.05 | 40 | 3.3816 | 0 | 6.615 | 3.2334 | 3.2334 | available
61 | SS 35/10kV Gryzlovo | 2,5+2,5 | 5 | 0.61467 | 0.4 | 260 | 0.21467 | 0 | 2.625 | 2.4103 | 2.4103 | available | 0.91 | 61 | SS 35/10kV Gryzlovo | 2,5+2,5 |  | 0.61467 | 0.4 | 260 | 0.21467 | 0 | 2.625 | 2.4103 | 2.4103 | available
62 | SS 35/10 kV Zhernovnoe | 2,5+2,5 | 5 | 0.36157 | 0 | 0 | 0.36157 | 0 | 2.625 | 2.2634 | 2.2634 | available | 0.9 | 62 | SS 35/10 kV Zhernovnoe | 2,5+2,5 | 0.356 | 0.71757 | 0 | 0 | 0.71757 | 0 | 2.625 | 1.9074 | 1.9074 | available
63 | SS 35/10 kV Zadonsk-selsk. | 3,2+1,6 | 4.8 | 1.9227 | 0 | 0 | 1.9227 | 0 | 1.68 | -0.24272 | -0.24272 | unavailable | 0.82 | 63 | SS 35/10 kV Zadonsk-selsk. | 3,2+1,6 | 0.341 | 2.2637 | 0 | 0 | 2.2637 | 0 | 1.68 | -0.58372 | -0.58372 | unavailable
64 | SS 35/10 kV Zakharovka | 2,5+2,5 | 5 | 0.43821 | 0.02 | 60 | 0.41821 | 0 | 2.625 | 2.2068 | 2.2068 | available | 0.8 | 64 | SS 35/10 kV Zakharovka | 2,5+2,5 | 0.02 | 0.45821 | 0.02 | 60 | 0.43821 | 0 | 2.625 | 2.1868 | 2.1868 | available
65 | SS 35/10 kV Kazaki | 4+4 | 8 | 1.67 | 0 | 0 | 1.67 | 0 | 4.2 | 2.53 | 2.53 | available | 0.9 | 65 | SS 35/10 kV Kazaki | 4+4 | 0.249 | 1.919 | 0 | 0 | 1.919 | 0 | 4.2 | 2.281 | 2.281 | available
66 | SS 35/10 kV Kolesovo | 6,3+6,3 | 12.6 | 2.5535 | 0.4 | 60 | 2.1535 | 0 | 6.615 | 4.4615 | 4.4615 | available | 0.91 | 66 | SS 35/10 kV Kolesovo | 6,3+6,3 | 0.238 | 2.7915 | 0.4 | 60 | 2.3915 | 0 | 6.615 | 4.2235 | 4.2235 | available
67 | SS 35/10 kV Knyazevo | 2,5+2,5 | 5 | 0.3851 | 0 | 0 | 0.3851 | 0 | 2.625 | 2.2399 | 2.2399 | available | 0.75 | 67 | SS 35/10 kV Knyazevo | 2,5+2,5 | 0.057 | 0.4421 | 0 | 0 | 0.4421 | 0 | 2.625 | 2.1829 | 2.1829 | available
68 | SS 35/10 kV Kirillovo | 2,5+2,5 | 5 | 0.346 | 0.05 | 60 | 0.296 | 0 | 2.625 | 2.329 | 2.329 | available | 0.91 | 68 | SS 35/10 kV Kirillovo | 2,5+2,5 | 0.014 | 0.36 | 0.05 | 60 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available
69 | SS 35/10 kV Ksizovo | 2,5+2,5 | 5 | 0.23147 | 0 | 0 | 0.23147 | 0 | 2.625 | 2.3935 | 2.3935 | available | 0.94 | 69 | SS 35/10 kV Ksizovo | 2,5+2,5 | 0.05 | 0.28147 | 0 | 0 | 0.28147 | 0 | 2.625 | 2.3435 | 2.3435 | available
70 | SS 35/10 kV Lamskoe | 2,5+2,5 | 5 | 1.6165 | 0.22 | 180 | 1.3965 | 0 | 2.625 | 1.2285 | 1.2285 | available | 0.9 | 70 | SS 35/10 kV Lamskoe | 2,5+2,5 | 0.04 | 1.6565 | 0.22 | 180 | 1.4365 | 0 | 2.625 | 1.1885 | 1.1885 | available
71 | SS 35/10 kV Kazachye | 2,5+2,5 | 5 | 0.4588 | 0 | 0 | 0.4588 | 0 | 2.625 | 2.1662 | 2.1662 | available | 0.88 | 71 | SS 35/10 kV Kazachye | 2,5+2,5 | 0.184 | 0.6428 | 0 | 0 | 0.6428 | 0 | 2.625 | 1.9822 | 1.9822 | available
72 | SS 35/10 kV Lebyazhye | 2,5+1,6 | 4.1 | 0.29064 | 0 | 0 | 0.29064 | 0 | 1.68 | 1.3894 | 1.3894 | available | 0.95 | 72 | SS 35/10 kV Lebyazhye | 2,5+1,6 | 0.015 | 0.30564 | 0 | 0 | 0.30564 | 0 | 1.68 | 1.3744 | 1.3744 | available
73 | SS 35/10 kV Lomovets | 1,6+2,5 | 4.1 | 0.38146 | 0 | 0 | 0.38146 | 0 | 1.68 | 1.2985 | 1.2985 | available | 0.8 | 73 | SS 35/10 kV Lomovets | 1,6+2,5 | 0.01 | 0.39147 | 0 | 0 | 0.39147 | 0 | 1.68 | 1.2885 | 1.2885 | available
74 | SS 35/10 kV Olshanets | 2,5+4 | 6.5 | 1.2958 | 0 | 0 | 1.2958 | 0 | 2.625 | 1.3292 | 1.3292 | available | 0.87 | 74 | SS 35/10 kV Olshanets | 2,5+4 | 4.489 | 5.7848 | 0 | 0 | 5.7848 | 0 | 2.625 | -3.1598 | -3.1598 | unavailable
75 | SS 35/10 kV Ploskoe | 4+4 | 8 | 3.2925 | 0.74 | 140 | 2.5525 | 0 | 4.2 | 1.6475 | 1.6475 | available | 0.93 | 75 | SS 35/10 kV Ploskoe | 4+4 | 3.469 | 6.7615 | 0.74 | 140 | 6.0215 | 0 | 4.2 | -1.8215 | -1.8215 | unavailable
76 | SS 35/10 kV Stegalovka | 2,5+3,2 | 5.7 | 0.46883 | 0.1 | 80 | 0.36883 | 0 | 2.625 | 2.2562 | 2.2562 | available | 0.9 | 76 | SS 35/10 kV Stegalovka | 2,5+3,2 | 0.018 | 0.48683 | 0.1 | 80 | 0.38683 | 0 | 2.625 | 2.2382 | 2.2382 | available
77 | SS 35/10 kV Solidarnost | 4+4 | 8 | 1.8 | 1.2 | 70 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | available | 0.93 | 77 | SS 35/10 kV Solidarnost | 4+4 | 1.938 | 3.738 | 1.2 | 70 | 2.538 | 0 | 4.2 | 1.662 | 1.662 | available
78 | SS 35/10 kV Timiryazevo | 4+4 | 8 | 1.2183 | 0.35 | 60 | 0.86827 | 0 | 4.2 | 3.3317 | 3.3317 | available | 0.93 | 78 | SS 35/10 kV Timiryazevo | 4+4 | 0.166 | 1.3843 | 0.35 | 60 | 1.0343 | 0 | 4.2 | 3.1657 | 3.1657 | available
79 | SS 35/10 kV Talitsa | 2,5+2,5 | 5 | 1.5086 | 0.55 | 110 | 0.95856 | 0 | 2.625 | 1.6664 | 1.6664 | available | 0.94 | 79 | SS 35/10 kV Talitsa | 2,5+2,5 | 0.167 | 1.6756 | 0.55 | 110 | 1.1256 | 0 | 2.625 | 1.4994 | 1.4994 | available
80 | SS 35/10 kV the II Terbuny | 2,5+2,5 | 5 | 1.2653 | 0 | 0 | 1.2653 | 0 | 2.625 | 1.3597 | 1.3597 | available | 0.92 | 80 | SS 35/10 kV the II Terbuny | 2,5+2,5 | 0.1 | 1.3653 | 0 | 0 | 1.3653 | 0 | 2.625 | 1.2597 | 1.2597 | available
81 | SS 35/10 kV Tikhii Don | 4+4 | 8 | 0.5882 | 0.103 | 60 | 0.4852 | 0 | 4.2 | 3.7148 | 3.7148 | available | 0.94 | 81 | SS 35/10 kV Tikhii Don | 4+4 | 0.11 | 0.6982 | 0.103 | 60 | 0.5952 | 0 | 4.2 | 3.6048 | 3.6048 | available
82 | SS 35/10 kV Khitrovo | 6,3+6,3 | 12.6 | 1.3183 | 0 | 0 | 1.3183 | 0 | 6.615 | 5.2967 | 5.2967 | available | 0.95 | 82 | SS 35/10 kV Khitrovo | 6,3+6,3 | 0.04 | 1.3583 | 0 | 0 | 1.3583 | 0 | 6.62 | 5.2617 | 5.2617 | available
83 | SS 35/10 kV Chernava | 2,5+2,5 | 5 | 1.479 | 0 | 0 | 1.479 | 0 | 2.625 | 1.146 | 1.146 | available | 0.87 | 83 | SS 35/10 kV Chernava | 2,5+2,5 | 0.069 | 1.548 | 0 | 0 | 1.548 | 0 | 2.625 | 1.077 | 1.077 | available
84 | SS 35/10 kV Chernoles | 2,5+2,5 | 5 | 0.25189 | 0 | 0 | 0.25189 | 0 | 2.625 | 2.3731 | 2.3731 | available | 0.96 | 84 | SS 35/10 kV Chernoles | 2,5+2,5 | 0.015 | 0.26689 | 0 | 0 | 0.26689 | 0 | 2.625 | 2.3581 | 2.3581 | available
85 | SS 35/6 kV SS No. 5 | 6,3+3,2 | 9.5 | 1.3484 | 0 | 0 | 1.3484 | 0 | 3.36 | 2.0116 | 2.0116 | available | 0.72 | 85 | SS 35/6 kV SS No. 5 | 6,3+3,2 |  | 1.3484 | 0 | 0 | 1.3484 | 0 | 3.36 | 2.0116 | 2.0116 | available
86 | SS 35/10 kV Krasnoe | 4+4 | 8 | 3.2909 | 1.3 | 150 | 1.9909 | 0 | 4.2 | 2.2091 | 2.2091 | available | 0.92 | 86 | SS 35/10 kV Krasnoe | 4+4 | 0.301 | 3.5919 | 1.3 | 150 | 2.2919 | 0 | 4.2 | 1.9081 | 1.9081 | available
87 | SS 35/10 kV Tyoploe | 2,5+2,5 | 5 | 1.0909 | 1 | 60 | 0.090909 | 0 | 2.625 | 2.5341 | 2.5341 | available | 0.88 | 87 | SS 35/10 kV Tyoploe | 2,5+2,5 | 0.017 | 1.1079 | 1 | 60 | 0.10791 | 0 | 2.625 | 2.5171 | 2.5171 | available
88 | SS 35/10 kV Dankov-selskaya | 6,3+4 | 10.3 | 3.9091 | 2 | 120 | 1.9091 | 0 | 4.2 | 2.2909 | 2.2909 | available | 0.92 | 88 | SS 35/10 kV Dankov-selskaya | 6,3+4 | 0.592 | 4.5011 | 2 | 120 | 2.5011 | 0 | 4.2 | 1.6989 | 1.6989 | available
89 | SS 35/10 kV Kolybelskaya | 2,5+2,5 | 5 | 1.0182 | 0 | 0 | 1.0182 | 0 | 2.625 | 1.6068 | 1.6068 | available | 0.96 | 89 | SS 35/10 kV Kolybelskaya | 2,5+2,5 | 0.092 | 1.1102 | 0 | 0 | 1.1102 | 0 | 2.625 | 1.5148 | 1.5148 | available
90 | SS 35/10 kV Topki | 2,5+2,5 | 5 | 0.55455 | 0.5 | 60 | 0.054545 | 0 | 2.625 | 2.5705 | 2.5705 | available | 0.88 | 90 | SS 35/10 kV Topki | 2,5+2,5 | 0.02 | 0.57455 | 0.5 | 60 | 0.074545 | 0 | 2.625 | 2.5505 | 2.5505 | available
91 | SS 35/10 kV Agronom | 4+6,3 | 10.3 | 1.5455 | 1 | 60 | 0.54545 | 0 | 4.2 | 3.6545 | 3.6545 | available | 0.94 | 91 | SS 35/10 kV Agronom | 4+6,3 | 0.069 | 1.6145 | 1 | 60 | 0.61445 | 0 | 4.2 | 3.5855 | 3.5855 | available
92 | SS 35/10 kV Troekurovo-sovkhoznaya | 2,5+2,5 | 5 | 1.8727 | 1 | 60 | 0.87273 | 0 | 2.625 | 1.7523 | 1.7523 | available | 0.96 | 92 | SS 35/10 kV Troekurovo-sovkhoznaya | 2,5+2,5 | 1.262 | 3.1347 | 1 | 60 | 2.1347 | 0 | 2.625 | 0.49027 | 0.49027 | available
93 | SS 35/10 kV Gagarino | 1,8+1,8 | 3.6 | 0.38182 | 0.5 | 120 | -0.11818 | 0 | 1.89 | 2.0082 | 2.0082 | available | 0.95 | 93 | SS 35/10 kV Gagarino | 1,8+1,8 |  | 0.38182 | 0.5 | 120 | -0.11818 | 0 | 1.89 | 2.0082 | 2.0082 | available
94 | SS 35/10 kV Ranenburg | 1,6+1,6 | 3.2 | 1.8182 | 0.3 | 120 | 1.5182 | 0 | 1.68 | 0.16182 | 0.16182 | available | 0.93 | 94 | SS 35/10 kV Ranenburg | 1,6+1,6 | 0.399 | 2.2172 | 0.3 | 120 | 1.9172 | 0 | 1.68 | -0.23718 | -0.23718 | unavailable
95 | SS 35/10 kV Sergievka | 2,5+2,5 | 5 | 0.41818 | 0.3 | 60 | 0.11818 | 0 | 2.625 | 2.5068 | 2.5068 | available | 0.87 | 95 | SS 35/10 kV Sergievka | 2,5+2,5 | 0.068 | 0.48618 | 0.3 | 60 | 0.18618 | 0 | 2.625 | 2.4388 | 2.4388 | available
96 | SS 35/10 kV Drezgalovo | 1,6+1,6 | 3.2 | 0.58182 | 0.5 | 60 | 0.081818 | 0 | 1.68 | 1.5982 | 1.5982 | available | 0.93 | 96 | SS 35/10 kV Drezgalovo | 1,6+1,6 | 0.024 | 0.60582 | 0.5 | 60 | 0.10582 | 0 | 1.68 | 1.5742 | 1.5742 | available
97 | SS 35/10 kV Dolgoe | 2,5+2,5 | 5 | 0.2 | 0 | 0 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 0.87 | 97 | SS 35/10 kV Dolgoe | 2,5+2,5 | 0.026 | 0.226 | 0 | 0 | 0.226 | 0 | 2.625 | 2.399 | 2.399 | available
98 | SS 35/10 kV Voskresenovka | 1,6+1,6 | 3.2 | 0.50909 | 0 | 0 | 0.50909 | 0 | 1.68 | 1.1709 | 1.1709 | available | 0.88 | 98 | SS 35/10 kV Voskresenovka | 1,6+1,6 | 0.099 | 0.60809 | 0 | 0 | 0.60809 | 0 | 1.68 | 1.0719 | 1.0719 | available
99 | SS 35/10 kV Saprykino | 1,6+2,5 | 4.1 | 0.50909 | 0 | 0 | 0.50909 | 0 | 1.68 | 1.1709 | 1.1709 | available | 0.81 | 99 | SS 35/10 kV Saprykino | 1,6+2,5 | 0.12 | 0.62909 | 0 | 0 | 0.62909 | 0 | 1.68 | 1.0509 | 1.0509 | available
100 | SS 35/10 kV Nopolyanye | 2,5+2,5 | 5 | 0.43636 | 0 | 0 | 0.43636 | 0 | 2.625 | 2.1886 | 2.1886 | available | 0.82 | 100 | SS 35/10 kV Nopolyanye | 2,5+2,5 | 0.046 | 0.48236 | 0 | 0 | 0.48236 | 0 | 2.625 | 2.1426 | 2.1426 | available
101 | SS 35/10 kV Vednoe | 2,5+2,5 | 5 | 0.69091 | 0.5 | 180 | 0.19091 | 0 | 2.625 | 2.4341 | 2.4341 | available | 0.9 | 101 | SS 35/10 kV Vednoe | 2,5+2,5 | 0.014 | 0.70491 | 0.5 | 180 | 0.20491 | 0 | 2.625 | 2.4201 | 2.4201 | available
102 | SS 35/10 kV Bigildino | 2,5+2,5 | 5 | 0.96364 | 0.5 | 60 | 0.46364 | 0 | 2.625 | 2.1614 | 2.1614 | available | 0.9 | 102 | SS 35/10 kV Bigildino | 2,5+2,5 | 0.052 | 1.0156 | 0.5 | 60 | 0.51564 | 0 | 2.625 | 2.1094 | 2.1094 | available
103 | SS 35/10 kV Kultura | 2,5+2,5 | 5 | 0.83636 | 1 | 60 | -0.16364 | 0 | 2.625 | 2.7886 | 2.7886 | available | 0.87 | 103 | SS 35/10 kV Kultura | 2,5+2,5 | 0.078 | 0.91436 | 1 | 60 | -0.085636 | 0 | 2.625 | 2.7106 | 2.7106 | available
104 | SS 35/10 kV Boryatino | 2,5+2,5 | 5 | 0.30909 | 0.1 | 60 | 0.20909 | 0 | 2.625 | 2.4159 | 2.4159 | available | 0.91 | 104 | SS 35/10 kV Boryatino | 2,5+2,5 | 0.006 | 0.31509 | 0.1 | 60 | 0.21509 | 0 | 2.625 | 2.4099 | 2.4099 | available
105 | SS 35/10 kV B.Popovo | 2,5+2,5 | 5 | 1.1818 | 1 | 90 | 0.18182 | 0 | 2.625 | 2.4432 | 2.4432 | available | 0.94 | 105 | SS 35/10 kV B.Popovo | 2,5+2,5 | 0.2 | 1.3818 | 1 | 90 | 0.38182 | 0 | 2.625 | 2.2432 | 2.2432 | available
106 | SS 35/10 kV B. Izbishchi | 2,5+2,5 | 5 | 1.6182 | 1 | 60 | 0.61818 | 0 | 2.625 | 2.0068 | 2.0068 | available | 0.89 | 106 | SS 35/10 kV B. Izbishchi | 2,5+2,5 | 0.025 | 1.6432 | 1 | 60 | 0.64318 | 0 | 2.625 | 1.9818 | 1.9818 | available
107 | SS 35/10 kV Polibino | 2,5+2,5 | 5 | 0.23636 | 0 | 0 | 0.23636 | 0 | 2.625 | 2.3886 | 2.3886 | available | 0.93 | 107 | SS 35/10 kV Polibino | 2,5+2,5 | 0.093 | 0.32936 | 0 | 0 | 0.32936 | 0 | 2.625 | 2.2956 | 2.2956 | available
108 | SS 35/10 kV Dubrava | 2,5+2,5 | 5 | 0.33 | 0 | 0 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 0.77 | 108 | SS 35/10 kV Dubrava | 2,5+2,5 | 0.01 | 0.34 | 0 | 0 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available
109 | SS 35/10 kV Khrushchevo | 2,5+2,5 | 5 | 0.50909 | 0 | 0 | 0.50909 | 0 | 2.625 | 2.1159 | 2.1159 | available | 0.78 | 109 | SS 35/10 kV Khrushchevo | 2,5+2,5 | 0.019 | 0.52809 | 0 | 0 | 0.52809 | 0 | 2.625 | 2.0969 | 2.0969 | available
110 | SS 35/10 kV B. Verkh | 2,5+2,5 | 5 | 0.74545 | 0 | 0 | 0.74545 | 0 | 2.625 | 1.8795 | 1.8795 | available | 0.9 | 110 | SS 35/10 kV B. Verkh | 2,5+2,5 | 0.03 | 0.77545 | 0 | 0 | 0.77545 | 0 | 2.625 | 1.8495 | 1.8495 | available
111 | SS 35/10 kV Golovinshchino | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available | 0.9 | 111 | SS 35/10 kV Golovinshchino | 2,5+2,5 | 0.29 | 0.89 | 0 | 0 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available
112 | SS 35/10 kV Yablonevoe | 2,5+2,5 | 5 | 0.56364 | 0 | 0 | 0.56364 | 0 | 2.625 | 2.0614 | 2.0614 | available | 0.88 | 112 | SS 35/10 kV Yablonevoe | 2,5+2,5 | 2.807 | 3.3706 | 0 | 0 | 3.3706 | 0 | 2.625 | -0.74564 | -0.74564 | unavailable
113 | SS 35/10 kV Politovo | 2,5+2,5 | 5 | 0.74545 | 0 | 0 | 0.74545 | 0 | 2.625 | 1.8795 | 1.8795 | available | 0.87 | 113 | SS 35/10 kV Politovo | 2,5+2,5 | 0.015 | 0.76045 | 0 | 0 | 0.76045 | 0 | 2.625 | 1.8645 | 1.8645 | available
114 | SS 35/10 kV Complex | 4+4 | 8 | 0.90909 | 1 | 120 | -0.090909 | 0 | 4.2 | 4.2909 | 4.2909 | available | 0.9 | 114 | SS 35/10 kV Complex | 4+4 |  | 0.90909 | 1 | 120 | -0.090909 | 0 | 4.2 | 4.2909 | 4.2909 | available
115 | SS 35/10 kV No.1 | 4+4 | 8 | 3.427 | 0 | 0 | 3.427 | 0 | 4.2 | 0.773 | 0.773 | available | 0.98 | 115 | SS 35/10 kV No.1 | 4+4 | 1.411 | 4.838 | 0 | 0 | 4.838 | 0 | 4.2 | -0.638 | -0.638 | unavailable
116 | SS 35/6 kV No. 2 | 1+1+1 | 3 | 1.7127 | 0 | 0 | 1.7127 | 0 | 1.05 | -0.6627 | -0.6627 | unavailable | 0.915 | 116 | SS 35/6 kV No. 2 | 1+1+1 | 0.09 | 1.8027 | 0 | 0 | 1.8027 | 0 | 1.05 | -0.7527 | -0.7527 | unavailable
117 | SS 35/10 kV No. 3 | 2,5+2,5 | 5 | 1.831 | 0.52 | 75 | 1.311 | 0 | 2.625 | 1.314 | 1.314 | * | 0.96 | 117 | SS 35/10 kV No. 3 | 2,5+2,5 | 1.504 | 3.335 | 0.52 | 75 | 2.815 | 0 | 2.625 | -0.19 | -0.19 | *
118 | SS 35/6 kV No. 4 | 4+4 | 8 | 2.423 | 0.82 | 70 | 1.603 | 0 | 4.2 | 2.597 | 2.597 | * | 0.91 | 118 | SS 35/6 kV No. 4 | 4+4 | 0.283 | 2.706 | 0.82 | 70 | 1.886 | 0 | 4.2 | 2.314 | 2.314 | *
119 | SS 35/6 kV Gryazi-gorod | 6,3+5,6 | 11.9 | 4.5 | 0 | 0 | 4.5 | 0 | 5.88 | 1.38 | 1.38 | available | 0.95 | 119 | SS 35/6 kV Gryazi-gorod | 6,3+5,6 | 0.371 | 4.871 | 0 | 0 | 4.871 | 0 | 5.88 | 1.009 | 1.009 | available
120 | SS 35/10 kV Butyrki | 5,6+4 | 9.6 | 6.5 | 0 | 0 | 6.5 | 0 | 4.2 | -2.3 | -2.3 | unavailable | 0.95 | 120 | SS 35/10 kV Butyrki | 5,6+4 | 3.698 | 10.198 | 0 | 0 | 10.198 | 0 | 4.2 | -5.998 | -5.998 | unavailable
121 | SS 35/10 kV Yarlukovo | 3,2+4 | 7.2 | 3.7873 | 0.93 | 160 | 2.8573 | 0 | 3.36 | 0.50268 | 0.50268 | available | 0.922 | 121 | SS 35/10 kV Yarlukovo | 3,2+4 | 1.043 | 4.8303 | 0.93 | 160 | 3.9003 | 0 | 3.36 | -0.54032 | -0.54032 | unavailable
122 | SS 35/10 kV Knyazhya Baygora | 1,6+1,6 | 3.2 | 0.26192 | 0.094 | 130 | 0.16792 | 0 | 1.68 | 1.5121 | 1.5121 | available | 0.888 | 122 | SS 35/10 kV Knyazhya Baygora | 1,6+1,6 | 0.1 | 0.36192 | 0.094 | 130 | 0.26792 | 0 | 1.68 | 1.4121 | 1.4121 | available
123 | SS 35/10 kV Pravda | 4+2,5 | 6.5 | 0.97036 | 0.5 | 100 | 0.47036 | 0 | 2.625 | 2.1546 | 2.1546 | available | 0.909 | 123 | SS 35/10 kV Pravda | 4+2,5 | 0.05 | 1.0204 | 0.5 | 100 | 0.52036 | 0 | 2.625 | 2.1046 | 2.1046 | available
124 | SS 35/10 kV Krasnaya Dubrava | 2,5+2,5 | 5 | 0.643 | 0.09 | 140 | 0.553 | 0 | 2.625 | 2.072 | 2.072 | available | 0.98 | 124 | SS 35/10 kV Krasnaya Dubrava | 2,5+2,5 | 0.047 | 0.69 | 0.09 | 140 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available
125 | SS 35/10 kV Matyra | 4+3,2 | 7.2 | 3.272 | 0 | 0 | 3.272 | 0 | 3.36 | 0.088 | 0.088 | available | 0.95 | 125 | SS 35/10 kV Matyra | 4+3,2 | 0.015 | 3.287 | 0 | 0 | 3.287 | 0 | 3.36 | 0.073 | 0.073 | available
126 | SS 35/10 kV Vperyod | 4+4 | 8 | 0.68231 | 0.2 | 80 | 0.48231 | 0 | 4.2 | 3.7177 | 3.7177 | available | 0.956 | 126 | SS 35/10 kV Vperyod | 4+4 | 0.13 | 0.81231 | 0.2 | 80 | 0.61231 | 0 | 4.2 | 3.5877 | 3.5877 | available
127 | SS 35/10 kV Maley | 4+2,5 | 6.5 | 0.73594 | 0.23 | 70 | 0.50594 | 0 | 2.625 | 2.1191 | 2.1191 | available | 0.89 | 127 | SS 35/10 kV Maley | 4+2,5 | 0.617 | 1.3529 | 0.23 | 70 | 1.1229 | 0 | 2.625 | 1.5021 | 1.5021 | available
128 | SS 35/10 kV SKhТ | 2,5+1,6 | 4.1 | 1.5612 | 0 | 0 | 1.5612 | 0 | 1.68 | 0.11885 | 0.11885 | available | 0.923 | 128 | SS 35/10 kV SKhТ | 2,5+1,6 | 0.481 | 2.0422 | 0 | 0 | 2.0422 | 0 | 1.68 | -0.36215 | -0.36215 | unavailable
129 | SS 35/10 kV Soshki | 4+4 | 8 | 0.77573 | 0.3 | 80 | 0.47573 | 0 | 4.2 | 3.7243 | 3.7243 | available | 0.947 | 129 | SS 35/10 kV Soshki | 4+4 | 0.088 | 0.86373 | 0.3 | 80 | 0.56373 | 0 | 4.2 | 3.6363 | 3.6363 | available
130 | SS 35/6 kV Tavolzhanka | 4+4 | 8 | 3.888 | 0 | 0 | 3.888 | 0 | 4.2 | 0.312 | 0.312 | available | 0.95 | 130 | SS 35/6 kV Tavolzhanka | 4+4 | 1.32 | 5.208 | 0 | 0 | 5.208 | 0 | 4.2 | -1.008 | -1.008 | unavailable
131 | SS 35/10 kV Trubetchino | 2,5+2,5 | 5 | 1.1807 | 0 | 0 | 1.1807 | 0 | 2.625 | 1.4443 | 1.4443 | * | 0.879 | 131 | SS 35/10 kV Trubetchino | 2,5+2,5 | 0.08 | 1.2607 | 0 | 0 | 1.2607 | 0 | 2.625 | 1.3643 | 1.3643 | available
132 | SS 35/10 kV Ratchino | 2,5+2,5 | 5 | 1.1939 | 0 | 0 | 1.1939 | 0 | 2.625 | 1.4311 | 1.4311 | * | 0.896 | 132 | SS 35/10 kV Ratchino | 2,5+2,5 | 0.075 | 1.2689 | 0 | 0 | 1.2689 | 0 | 2.625 | 1.3561 | 1.3561 | *
133 | SS 35/10 kV Kalikino | 3,2+3,2 | 6.4 | 1.55 | 0 | 0 | 1.55 | 0 | 3.36 | 1.81 | 1.81 | * | 0.88 | 133 | SS 35/10 kV Kalikino | 3,2+3,2 | 0.093 | 1.643 | 0 | 0 | 1.643 | 0 | 3.36 | 1.717 | 1.717 | *
134 | SS 35/10 kV Borisovka | 4+2,5 | 6.5 | 2.329 | 0 | 0 | 2.329 | 0 | 2.625 | 0.296 | 0.296 | available | 0.93 | 134 | SS 35/10 kV Borisovka | 4+2,5 | 2.073 | 4.402 | 0 | 0 | 4.402 | 0 | 2.625 | -1.777 | -1.777 | unavailable
135 | SS 35/10 kV Vvedenka | 4+4 | 8 | 3.393 | 0.05 | 50 | 3.343 | 0 | 4.2 | 0.857 | 0.857 | * | 0.95 | 135 | SS 35/10 kV Vvedenka | 4+4 | 5.911 | 9.304 | 0.05 | 50 | 9.254 | 0 | 4.2 | -5.054 | -5.054 | unavailable
136 | SS 35/10 kV Gryaznoe | 4+4 | 8 | 1.0034 | 0 | 0 | 1.0034 | 0 | 4.2 | 3.1966 | 3.1966 | * | 0.948 | 136 | SS 35/10 kV Gryaznoe | 4+4 | 1.184 | 2.1874 | 0 | 0 | 2.1874 | 0 | 4.2 | 2.0126 | 2.0126 | *
137 | SS 35/10 kV Borino | 4+4 | 8 | 3.96 | 0.81 | 75 | 3.15 | 0 | 4.2 | 1.05 | 1.05 | * | 0.88 | 137 | SS 35/10 kV Borino | 4+4 | 2.03 | 5.99 | 0.81 | 75 | 5.18 | 0 | 4.2 | -0.98 | -0.98 | *
138 | SS 35/10 kV Chastaya Dubrava | 2,5+2,5 | 5 | 1.1894 | 1.25 | 115 | -0.060625 | 0 | 2.625 | 2.6856 | 2.6856 | * | 0.905 | 138 | SS 35/10 kV Chastaya Dubrava | 2,5+2,5 | 2.863 | 4.0524 | 1.25 | 115 | 2.8024 | 0 | 2.625 | -0.17738 | -0.17738 | unavailable
139 | SS 35/10 kV Troitskaya | 2,5+4 | 6.5 | 2.343 | 0.04 | 30 | 2.303 | 0 | 2.625 | 0.322 | 0.322 | * | 0.61 | 139 | SS 35/10 kV Troitskaya | 2,5+4 | 0.732 | 3.075 | 0.04 | 30 | 3.035 | 0 | 2.625 | -0.41 | -0.41 | *
140 | SS 35/6 kV Veshalovka | 2,5+2,5 | 5 | 0.70671 | 0 | 0 | 0.70671 | 0 | 2.625 | 1.9183 | 1.9183 | * | 0.942 | 140 | SS 35/6 kV Veshalovka | 2,5+2,5 | 0.198 | 0.9047 | 0 | 0 | 0.9047 | 0 | 2.625 | 1.7203 | 1.7203 | *
141 | SS 35/10 kV Pruzhinki | 2,5+2,5 | 5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | * | 0.937 | 141 | SS 35/10 kV Pruzhinki | 2,5+2,5 | 0.197 | 0.897 | 0 | 0 | 0.897 | 0 | 2.625 | 1.728 | 1.728 | *
142 | SS 35/10 kV Stebaevo | 2,5+2,5 | 5 | 0.79 | 0.26 | 80 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | * | 0.926 | 142 | SS 35/10 kV Stebaevo | 2,5+2,5 | 0.318 | 1.108 | 0.26 | 80 | 0.848 | 0 | 2.625 | 1.777 | 1.777 | *
143 | SS 35/10 kV Khleboprodukty | 6,3+6,3 | 12.6 | 4.199 | 0.36 | 30 | 3.839 | 0 | 6.615 | 2.776 | 2.776 | * | 0.91 | 143 | SS 35/10 kV Khleboprodukty | 6,3+6,3 | 0.738 | 4.937 | 0.36 | 30 | 4.577 | 0 | 6.615 | 2.038 | 2.038 | *
144 | SS 35/10 kV Sentsovo | 10+10 | 20 | 5.5014 | 0.23 | 40 | 5.2714 | 0 | 10.5 | 5.2286 | 5.2286 | * | 0.95 | 144 | SS 35/10 kV Sentsovo | 10+10 | 0.723 | 6.2244 | 0.23 | 40 | 5.9944 | 0 | 10.5 | 4.5056 | 4.5056 | *
145 | SS 35/10 kV Meet processing plant | 6,3+6,3 | 12.6 | 4.251 | 1.31 | 60 | 2.941 | 0 | 6.62 | 3.679 | 3.679 | * | 0.88 | 145 | SS 35/10 kV Meet processing plant | 6,3+6,3 | 0.778 | 5.029 | 1.31 | 60 | 3.719 | 0 | 6.62 | 2.901 | 2.901 | *
146 | SS 35/6 kV Poultry plant | 4+4 | 8 | 2.0587 | 0 | 0 | 2.0587 | 0 | 4.2 | 2.1413 | 2.1413 | * | 0.924 | 146 | SS 35/6 kV Poultry plant | 4+4 | 2.491 | 4.5497 | 0 | 0 | 4.5497 | 0 | 4.2 | -0.3497 | -0.3497 | *
147 | SS 35/6 kV Water intake | 10+10 | 20 | 1.407 | 0 | 0 | 1.407 | 0 | 10.5 | 9.093 | 9.093 | * | 0.87 | 147 | SS 35/6 kV Water intake | 10+10 | 0.832 | 2.239 | 0 | 0 | 2.239 | 0 | 10.5 | 8.261 | 8.261 | *
148 | SS 35/10 kV Petrovskaya | 2,5+4 | 6.5 | 0.48371 | 0 | 0 | 0.48371 | 0 | 2.625 | 2.1413 | 2.1413 | available | 0.914 | 148 | SS 35/10 kV Petrovskaya | 2,5+4 | 0.021 | 0.50471 | 0 | 0 | 0.50471 | 0 | 2.625 | 2.1203 | 2.1203 | available
149 | SS 35/10 kV Lebedyanka | 2,5+2,5 | 5 | 0.59235 | 0 | 0 | 0.59235 | 0 | 2.625 | 2.0326 | 2.0326 | available | 0.935 | 149 | SS 35/10 kV Lebedyanka | 2,5+2,5 | 0.54 | 1.1324 | 0 | 0 | 1.1324 | 0 | 2.625 | 1.4926 | 1.4926 | available
150 | SS 35/10 kV Novocherkutino | 4+4 | 8 | 1.1103 | 0 | 0 | 1.1103 | 0 | 4.2 | 3.0897 | 3.0897 | available | 0.939 | 150 | SS 35/10 kV Novocherkutino | 4+4 | 0.41 | 1.5203 | 0 | 0 | 1.5203 | 0 | 4.2 | 2.6797 | 2.6797 | available
151 | SS 35/10 kV Ivanovka | 2,5+2,5 | 5 | 0.84649 | 0 | 0 | 0.84649 | 0 | 2.625 | 1.7785 | 1.7785 | available | 0.802 | 151 | SS 35/10 kV Ivanovka | 2,5+2,5 | 0.055 | 0.90149 | 0 | 0 | 0.90149 | 0 | 2.625 | 1.7235 | 1.7235 | available
152 | SS 35/10 kV Poddubrovka | 2,5+2,5 | 5 | 1.161 | 0.2 | 60 | 0.961 | 0 | 2.625 | 1.664 | 1.664 | available | 0.895 | 152 | SS 35/10 kV Poddubrovka | 2,5+2,5 | 0.177 | 1.338 | 0.2 | 60 | 1.138 | 0 | 2.625 | 1.487 | 1.487 | available
153 | SS 35/10 kV Plavitsa | 1,6+1,6 | 3.2 | 0.3697 | 0 | 0 | 0.3697 | 0 | 1.68 | 1.3103 | 1.3103 | available | 0.936 | 153 | SS 35/10 kV Plavitsa | 1,6+1,6 | 0.35 | 0.7197 | 0 | 0 | 0.7197 | 0 | 1.68 | 0.9603 | 0.9603 | available
154 | SS 35/10 kV Parshinovka | 1,6+2,5 | 4.1 | 0.21798 | 0 | 0 | 0.21798 | 0 | 1.68 | 1.462 | 1.462 | available | 0.913 | 154 | SS 35/10 kV Parshinovka | 1,6+2,5 | 0.007 | 0.22498 | 0 | 0 | 0.22498 | 0 | 1.68 | 1.455 | 1.455 | available
155 | SS 35/10 kV Talitsky Chamlyk | 3,2+4 | 7.2 | 1.1522 | 0 | 0 | 1.1522 | 0 | 3.36 | 2.2078 | 2.2078 | available | 0.898 | 155 | SS 35/10 kV Talitsky Chamlyk | 3,2+4 | 0.024 | 1.1762 | 0 | 0 | 1.1762 | 0 | 3.36 | 2.1838 | 2.1838 | available
156 | SS 35/10 kV Demshinka | 2,5+2,5 | 5 | 0.36676 | 0 | 0 | 0.36676 | 0 | 2.625 | 2.2582 | 2.2582 | available | 0.947 | 156 | SS 35/10 kV Demshinka | 2,5+2,5 | 0.3 | 0.66676 | 0 | 0 | 0.66676 | 0 | 2.625 | 1.9582 | 1.9582 | available
157 | SS 35/10 kV Bereznyagovka | 1,6+1,6 | 3.2 | 0.58958 | 0.163 | 70 | 0.42658 | 0 | 1.68 | 1.2534 | 1.2534 | available | 0.88 | 157 | SS 35/10 kV Bereznyagovka | 1,6+1,6 | 0.03 | 0.61958 | 0.163 | 70 | 0.45658 | 0 | 1.68 | 1.2234 | 1.2234 | available
158 | SS 35/10 kV Dmitrievka | 2,5+2,5 | 5 | 0.58439 | 0.09 | 70 | 0.49439 | 0 | 2.625 | 2.1306 | 2.1306 | available | 0.963 | 158 | SS 35/10 kV Dmitrievka | 2,5+2,5 |  | 0.58439 | 0.09 | 70 | 0.49439 | 0 | 2.625 | 2.1306 | 2.1306 | available
159 | SS 35/10 kV Pashkovo | 2,5+2,5 | 5 | 1.9544 | 0.364 | 60 | 1.5904 | 0 | 2.625 | 1.0346 | 1.0346 | available | 0.958 | 159 | SS 35/10 kV Pashkovo | 2,5+2,5 | 0.032 | 1.9864 | 0.364 | 60 | 1.6224 | 0 | 2.625 | 1.0026 | 1.0026 | available
160 | SS 35/10 kV Moskovka | 1,6+1,6 | 3.2 | 0.56398 | 0.073 | 30 | 0.49098 | 0 | 1.68 | 1.189 | 1.189 | available | 0.916 | 160 | SS 35/10 kV Moskovka | 1,6+1,6 | 0.042 | 0.60598 | 0.073 | 30 | 0.53298 | 0 | 1.68 | 1.147 | 1.147 | available
161 | SS 35/10 kV Bochinovka | 4+4 | 8 | 2.1919 | 0.473 | 150 | 1.7189 | 0 | 4.2 | 2.4811 | 2.4811 | available | 0.886 | 161 | SS 35/10 kV Bochinovka | 4+4 | 1.686 | 3.8779 | 0.473 | 150 | 3.4049 | 0 | 4.2 | 0.79509 | 0.79509 | available
162 | SS 35/10 kV Fyodorovka | 2,5+2,5 | 5 | 0.52713 | 0.2 | 150 | 0.32713 | 0 | 2.625 | 2.2979 | 2.2979 | available | 0.91 | 162 | SS 35/10 kV Fyodorovka | 2,5+2,5 | 0.13 | 0.65713 | 0.2 | 150 | 0.45713 | 0 | 2.625 | 2.1679 | 2.1679 | available
163 | SS 35/10 kV Kulikovo | 2,5+2,5 | 5 | 0.6721 | 0 | 0 | 0.6721 | 0 | 2.625 | 1.9529 | 1.9529 | available | 0.949 | 163 | SS 35/10 kV Kulikovo | 2,5+2,5 | 0.059 | 0.73111 | 0 | 0 | 0.73111 | 0 | 2.625 | 1.8939 | 1.8939 | available
164 | SS 35/10 kV Kon-Kolodez | 2,5+2,5 | 5 | 1.3079 | 0 | 0 | 1.3079 | 0 | 2.625 | 1.3171 | 1.3171 | * | 0.883 | 164 | SS 35/10 kV Kon-Kolodez | 2,5+2,5 | 0.69 | 1.9979 | 0 | 0 | 1.9979 | 0 | 2.625 | 0.62712 | 0.62712 | *
165 | SS 35/10 kV Dmitryashevka | 2,5+2,5 | 5 | 0.38873 | 0 | 0 | 0.38873 | 0 | 2.625 | 2.2363 | 2.2363 | * | 0.784 | 165 | SS 35/10 kV Dmitryashevka | 2,5+2,5 | 0.165 | 0.55373 | 0 | 0 | 0.55373 | 0 | 2.625 | 2.0713 | 2.0713 | *
166 | SS 35/10 kV Rechnaya | 4+4 | 8 | 1.7997 | 0 | 0 | 1.7997 | 0 | 4.2 | 2.4003 | 2.4003 | * | 0.863 | 166 | SS 35/10 kV Rechnaya | 4+4 | 1.285 | 3.0847 | 0 | 0 | 3.0847 | 0 | 4.2 | 1.1153 | 1.1153 | *
167 | SS 35/10 kV Negachevka | 2,5+2,5 | 5 | 0.3851 | 0 | 0 | 0.3851 | 0 | 2.625 | 2.2399 | 2.2399 | * | 0.852 | 167 | SS 35/10 kV Negachevka | 2,5+2,5 | 0.017 | 0.4021 | 0 | 0 | 0.4021 | 0 | 2.625 | 2.2229 | 2.2229 | *
168 | SS 35/10 kV Karamyshevo | 10+10 | 20 | 0.95531 | 0 | 0 | 0.95531 | 0 | 10.5 | 9.5447 | 9.5447 | available | 0.969 | 168 | SS 35/10 kV Karamyshevo | 10+10 | 0.267 | 1.2223 | 0 | 0 | 1.2223 | 0 | 10.5 | 9.2777 | 9.2777 | available
169 | SS 35/10 kV Tyushevka | 1,6+1,6 | 3.2 | 0.95358 | 0.04 | 110 | 0.91358 | 0 | 1.68 | 0.76642 | 0.76642 | * | 1 | 169 | SS 35/10 kV Tyushevka | 1,6+1,6 | 0.015 | 0.96858 | 0.04 | 110 | 0.92858 | 0 | 1.68 | 0.75142 | 0.75142 | *
170 | SS 35/10 kV Sselki | 10+10 | 20 | 0.322 | 0 | 0 | 0.322 | 0 | 10.5 | 10.178 | 10.178 | available | 0.99 | 170 | SS 35/10 kV Sselki | 10+10 | 6.286 | 6.608 | 0 | 0 | 6.608 | 0 | 10.5 | 3.892 | 3.892 | available
Two- and more transformer substations (for three voltage levels) | [13 empty] | 1: Two- and more transformer substations (for three voltage levels)
171 | SS 110/35/10 kV Terbuny-110 | 10+10 | 20 | 6.27 | 0.9 |  | 5.37 | 0 | 10.5 | 5.13 | 5.13 | available |  | 171 | SS 110/35/10 kV Terbuny-110 | 10+10 | 1.848 | 8.118 | 0.9 |  | 7.218 | 0 | 10.5 | 3.282 | 3.282 | available
| Nom. Capacity MV, МVA | 10+10 |  | 0.93 | 0.9 | 30 | 0.03 | 0 | 10.5 | 10.47 |  |  | 0.97 |  | Nom. Capacity MV, МVA | 10+10 | 0.514 | 1.444 | 0.9 | 30 | 0.544 | 0 | 10.5 | 9.956
| Nom. capacity LV, МVA | 10+10 |  | 5.34 | 0 | 0 | 5.34 | 0 | 10.5 | 5.16 |  |  | 0.93 |  | Nom. capacity LV, МVA | 10+10 | 1.334 | 6.674 | 0 | 0 | 6.674 | 0 | 10.5 | 3.826
172 | SS 110/35/10 kV Dolgorukovo | 6,3+10 | 16.3 | 6.37 | 4.57 |  | 1.8 | 0 | 6.615 | 4.815 | 4.815 | available |  | 172 | SS 110/35/10 kV Dolgorukovo | 6,3+10 | 0.766 | 7.136 | 4.57 |  | 2.566 | 0 | 6.615 | 4.049 | 4.049 | available
| Nom. capacity MV, МVA | 6,3+10 |  | 4.18 | 2.9 | 45 | 1.28 | 0 | 6.615 | 5.335 |  |  | 0.94 |  | Nom. capacity MV, МVA | 6,3+10 | 0.576 | 4.756 | 2.9 | 45 | 1.856 | 0 | 6.615 | 4.759
| Nom. capacity LV, МVA | 6,3+10 |  | 2.19 | 1.67 | 140 | 0.52 | 0 | 6.615 | 6.095 |  |  | 0.95 |  | Nom. capacity LV, МVA | 6,3+10 | 0.19 | 2.38 | 1.67 | 140 | 0.71 | 0 | 6.615 | 5.905
173 | SS 110/35/10 kV Volovo | 10+10 | 20 | 4.47 | 1.97 |  | 2.5 | 0 | 10.5 | 8 | 8 | available |  | 173 | SS 110/35/10 kV Volovo | 10+10 | 1.21 | 5.68 | 1.97 |  | 3.71 | 0 | 10.5 | 6.79 | 6.79 | available
| Nom. capacity MV, МVA | 10+10 |  | 2.02 | 1.8 | 60 | 0.22 | 0 | 10.5 | 10.28 |  |  | 0.88 |  | Nom. capacity MV, МVA | 10+10 |  | 2.02 | 1.8 | 60 | 0.22 | 0 | 10.5 | 10.28
| Nom. capacity LV, МVА | 10+10 |  | 2.45 | 0.17 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  | 0.91 |  | Nom. capacity LV, МVА | 10+10 | 1.21 | 3.66 | 0.17 | 120 | 3.49 | 0 | 10.5 | 7.01
174 | SS 110/35/10 kV Izmalkovo | 10+10 | 20 | 5.25 | 0.82 |  | 4.43 | 0 | 10.5 | 6.07 | 6.07 | available |  | 174 | SS 110/35/10 kV Izmalkovo | 10+10 | 2.952 | 8.202 | 0.82 |  | 7.382 | 0 | 10.5 | 3.118 | 3.118 | available
| Nom. capacity MV, МVА | 10+10 |  | 1.65 | 0.8 | 30 | 0.85 | 0 | 10.5 | 9.65 |  |  | 0.91 |  | Nom. capacity MV, МVА | 10+10 | 0.052 | 1.702 | 0.8 | 30 | 0.902 | 0 | 10.5 | 9.598
| Nom. capacity LV, МVА | 10+10 |  | 3.6 | 0.02 | 90 | 3.58 | 0 | 10.5 | 6.92 |  |  | 0.92 |  | Nom. capacity LV, МVА | 10+10 | 2.9 | 6.5 | 0.02 | 90 | 6.48 | 0 | 10.5 | 4.02
175 | SS 110/35/10 kV Gorokhovskaya | 16+16 | 32 | 12.72 | 1.886 |  | 10.834 | 0 | 16.8 | 5.966 | 5.966 | available |  | 175 | SS 110/35/10 kV Gorokhovskaya | 16+16 | 11.857 | 24.577 | 1.886 |  | 22.691 | 0 | 16.8 | -5.891 | -5.891 | unavailable
| Nom. capacity MV, МVА | 16+16 |  | 9.03 | 1.4 | 30 | 7.63 | 0 | 16.8 | 9.17 |  |  | 0.89 |  | Nom. capacity MV, МVА | 16+16 | 9.527 | 18.557 | 1.4 | 30 | 17.157 | 0 | 16.8 | -0.357
| Nom. capacity LV, МVА | 16+16 |  | 3.69 | 0.486 | 60 | 3.204 | 0 | 16.8 | 13.596 |  |  | 0.95 |  | Nom. capacity LV, МVА | 16+16 | 2.33 | 6.02 | 0.486 | 60 | 5.534 | 0 | 16.8 | 11.266
176 | SS 110/35/10 kV Donskaya | 10+10 | 20 | 6.73 | 3.018 |  | 3.712 | 0 | 10.5 | 6.788 | 6.788 | available |  | 176 | SS 110/35/10 kV Donskaya | 10+10 | 1.587 | 8.317 | 3.018 |  | 5.299 | 0 | 10.5 | 5.201 | 5.201 | available
| Nom. capacity MV, МVА | 10+10 |  | 3.83 | 3 | 30 | 0.83 | 0 | 10.5 | 9.67 |  |  | 0.89 |  | Nom. capacity MV, МVА | 10+10 | 0.181 | 4.011 | 3 | 30 | 1.011 | 0 | 10.5 | 9.489
| Nom. capacity LV, МVА | 10+10 |  | 2.9 | 0.018 | 60 | 2.882 | 0 | 10.5 | 7.618 |  |  | 0.9 |  | Nom. capacity LV, МVА | 10+10 | 1.406 | 4.306 | 0.018 | 60 | 4.288 | 0 | 10.5 | 6.212
177 | SS 110/35/10 kV Lebedyan | 16+16 | 32 | 14.1364 | 11 |  | 3.1364 | 0 | 16.8 | 13.6636 | 13.6636 | available |  | 177 | SS 110/35/10 kV Lebedyan | 16+16 | 4.749 | 18.8854 | 11 |  | 7.8854 | 0 | 16.8 | 8.9146 | 8.9146 | available
| Nom. capacity MV, МVА | 16+16 |  | 6.5 | 6 | 60 | 0.5 | 0 | 16.8 | 16.3 |  |  | 0.87 |  | Nom. capacity MV, МVА | 16+16 | 1.561 | 8.061 | 6 | 60 | 2.061 | 0 | 16.8 | 14.739
| Nom. capacity LV, МVА | 16+16 |  | 7.6364 | 5 | 120 | 2.6364 | 0 | 16.8 | 14.1636 |  |  | 0.96 |  | Nom. capacity LV, МVА | 16+16 | 3.188 | 10.8244 | 5 | 120 | 5.8244 | 0 | 16.8 | 10.9756
178 | SS 110/35/10 kV Chaplygin-novaya | 16+16 | 32 | 6.7432 | 5 |  | 1.7432 | 0 | 16.8 | 15.0568 | 14.6818 | available |  | 178 | SS 110/35/10 kV Chaplygin-novaya | 16+16 | 0.294 | 7.0372 | 5 |  | 2.0372 | 0 | 16.8 | 14.7628 | 14.4808 | available
| Nom. capacity MV, МVА | 16+16 |  | 2.125 | 2.5 | 30 | -0.375 | 0 | 16.8 | 17.175 |  |  | 0.89 |  | Nom. capacity MV, МVА | 16+16 | 0.093 | 2.218 | 2.5 | 30 | -0.282 | 0 | 16.8 | 17.082
| Nom. capacity LV, МVА | 16+16 |  | 4.6182 | 2.5 | 100 | 2.1182 | 0 | 16.8 | 14.6818 |  |  | 0.96 |  | Nom. capacity LV, МVА | 16+16 | 0.201 | 4.8192 | 2.5 | 100 | 2.3192 | 0 | 16.8 | 14.4808
179 | SS 110/35/10 kV Kompressornaya | 16+16 | 32 | 4.2727 | 3.7 |  | 0.57273 | 0 | 16.8 | 16.2273 | 16.2 | available |  | 179 | SS 110/35/10 kV Kompressornaya | 16+16 | 4.266 | 8.5387 | 3.7 |  | 4.8387 | 0 | 16.8 | 11.9613 | 11.9613 | available
| Nom. Capacity MV, МVА | 16+16 |  | 2.8 | 2.2 | 30 | 0.6 | 0 | 16.8 | 16.2 |  |  | 0.94 |  | Nom. Capacity MV, МVА | 16+16 | 0.514 | 3.314 | 2.2 | 30 | 1.114 | 0 | 16.8 | 15.686
| Nom. capacity LV, МVА | 16+16 |  | 1.4727 | 1.5 | 60 | -0.027273 | 0 | 16.8 | 16.8273 |  |  | 0.93 |  | Nom. capacity LV, МVА | 16+16 | 3.752 | 5.2247 | 1.5 | 60 | 3.7247 | 0 | 16.8 | 13.0753
180 | SS 110/35/10 kV Rossiya | 16+16 | 32 | 4.1455 | 3.8 |  | 0.34545 | 0 | 16.8 | 16.4545 | 16.4 | available |  | 180 | SS 110/35/10 kV Rossiya | 16+16 | 4.251 | 8.3965 | 3.8 |  | 4.5965 | 0 | 16.8 | 12.2035 | 12.2035 | available
| Nom. capacity MV, МVА | 16+16 |  | 3.4 | 3 | 60 | 0.4 | 0 | 16.8 | 16.4 |  |  | 0.93 |  | Nom. capacity MV, МVА | 16+16 | 3.33 | 6.73 | 3 | 60 | 3.73 | 0 | 16.8 | 13.07
| Nom. capacity LV, МVА | 16+16 |  | 0.74545 | 0.8 | 100 | -0.054545 | 0 | 16.8 | 16.8545 |  |  | 0.94 |  | Nom. capacity LV, МVА | 16+16 | 0.921 | 1.6665 | 0.8 | 100 | 0.86645 | 0 | 16.8 | 15.9335
181 | SS 110/35/10 kV Beryozovka | 16+10 | 26 | 1.7 | 3.37 |  | -1.67 | 0 | 10.5 | 12.17 | 10.52 | available |  | 181 | SS 110/35/10 kV Beryozovka | 16+10 | 0.249 | 1.949 | 3.37 |  | -1.421 | 0 | 10.5 | 11.921 | 10.463 | available
| Nom. capacity MV, МVА | 16+10 |  | 1.35 | 3 | 60 | -1.65 | 0 | 10.5 | 12.15 |  |  | 0.94 |  | Nom. capacity MV, МVА | 16+10 | 0.192 | 1.542 | 3 | 60 | -1.458 | 0 | 10.5 | 11.958
| Nom. capacity LV, МVА | 16+10 |  | 0.35 | 0.37 | 90 | -0.02 | 0 | 10.5 | 10.52 |  |  | 0.92 |  | Nom. capacity LV, МVА | 16+10 | 0.057 | 0.407 | 0.37 | 90 | 0.037 | 0 | 10.5 | 10.463
182 | SS 110/35/10 kV Astapovo | 16+16 | 32 | 4.4955 | 4.8 |  | -0.30455 | 0 | 16.8 | 17.1045 | 16.85 | available |  | 182 | SS 110/35/10 kV Astapovo | 16+16 | 3.57 | 8.0655 | 4.8 |  | 3.2655 | 0 | 16.8 | 13.5345 | 13.5345 | available
| Nom. capacity MV, МVА | 16+16 |  | 1.95 | 2 | 60 | -0.05 | 0 | 16.8 | 16.85 |  |  | 0.95 |  | Nom. capacity MV, МVА | 16+16 | 0.316 | 2.266 | 2 | 60 | 0.266 | 0 | 16.8 | 16.534
| Nom. capacity LV, МVА | 16+16 |  | 2.5455 | 2.8 | 120 | -0.25455 | 0 | 16.8 | 17.0545 |  |  | 0.91 |  | Nom. capacity LV, МVА | 16+16 | 3.254 | 5.7995 | 2.8 | 120 | 2.9995 | 0 | 16.8 | 13.8005
183 | SS 110/35/10 kV Khimicheskaya | 16+16 | 32 | 7.6136 | 3.7 |  | 3.9136 | 0 | 16.8 | 12.8864 | 12.8864 | available |  | 183 | SS 110/35/10 kV Khimicheskaya | 16+16 | 7.941 | 15.5546 | 3.7 |  | 11.8546 | 0 | 16.8 | 4.9454 | 4.9454 | available
| Nom. capacity MV, МVА | 16+16 |  | 5.25 | 2.5 | 90 | 2.75 | 0 | 16.8 | 14.05 |  |  | 0.92 |  | Nom. capacity MV, МVА | 16+16 | 0.727 | 5.977 | 2.5 | 90 | 3.477 | 0 | 16.8 | 13.323
| Nom. capacity LV, МVА | 16+16 |  | 2.3636 | 1.2 | 60 | 1.1636 | 0 | 16.8 | 15.6364 |  |  | 0.99 |  | Nom. capacity LV, МVА | 16+16 | 7.214 | 9.5776 | 1.2 | 60 | 8.3776 | 0 | 16.8 | 8.4224
184 | SS 110/35/6 kV Bugor | 63+15+25 | 103 | 30.215 | 0.5 |  | 29.715 | 1 | 42 | 11.285 | 11.285 | available |  | 184 | SS 110/35/6 kV Bugor | 63+15+25 | 18.152 | 48.367 | 0.5 |  | 47.867 | 1 | 42 | -6.867 | -6.867 | unavailable
| Nom. capacity MV, МVА | 63+15+25 |  | 8.785 | 0 | 0 | 8.785 | 0 | 42 | 33.215 |  |  | 0.946 |  | Nom. capacity MV, МVА | 63+15+25 | 10.4 | 19.185 | 0 | 0 | 19.185 | 0 | 42 | 22.815
| Nom. capacity LV, МVА | 63+15+25 |  | 21.43 | 0.5 | 40 | 20.93 | 1 | 42 | 20.07 |  |  | 0.96 |  | Nom. capacity LV, МVА | 63+15+25 | 7.752 | 29.182 | 0.5 | 40 | 28.682 | 1 | 42 | 12.318
185 | SS 110/35/6 kVВ Tsementnaya | 63+32+63 | 158 | 45.46 | 1.81 |  | 43.65 | 0 | 99.75 | 56.1 | 52.39 | available |  | 185 | SS 110/35/6 kVВ Tsementnaya | 63+32+63 | 26.9565 | 72.4165 | 1.81 |  | 70.6065 | 0 | 99.75 | 29.1435 | 28.8835 | available
| Nom. capacity MV, МVА | 63+63 |  | 15.57 | 1.81 | 60 | 13.76 | 0 | 66.15 | 52.39 |  |  | 1 |  | Nom. capacity MV, МVА | 63+63 | 23.5065 | 39.0765 | 1.81 | 60 | 37.2665 | 0 | 66.15 | 28.8835
| Nom. capacity LV, МVА | 63+32+63 |  | 29.89 | 0 | 0 | 29.89 | 0 | 99.75 | 69.86 |  |  | 0.89 |  | Nom. capacity LV, МVА | 63+32+63 | 3.45 | 33.34 | 0 | 0 | 33.34 | 0 | 99.75 | 66.41
186 | SS 110/35/10/60 kV Gidrooborudovanie | 25+25 | 50 | 9.56 | 0.25 |  | 9.31 | 0 | 26.25 | 16.94 | 7.625 | available |  | 186 | SS 110/35/10/60 kV Gidrooborudovanie | 25+25 | 0.589 | 10.149 | 0.25 |  | 9.899 | 0 | 26.25 | 16.351 | 7.115 | available
| Nom. capacity MV, МVА | 12,5+12,5 |  | 5.5 | 0 | 0 | 5.5 | 0 | 13.125 | 7.625 |  |  | 0.94 |  | Nom. capacity MV, МVА | 12,5+12,5 | 0.515 | 6.015 | 0 | 0 | 6.015 | 0 | 13.13 | 7.115
| Nom. capacity LV, МVА | 12,5+12,5 |  | 4.06 | 0.25 | 80 | 3.81 | 0 | 13.125 | 9.315 |  |  | 0.96 |  | Nom. capacity LV, МVА | 12,5+12,5 | 0.074 | 4.134 | 0.25 | 80 | 3.884 | 0 | 13.13 | 9.246
| SS 110/35 kV T-3 Gidrooborudovanie | 31.5 | 31.5 | 4.38 | 2.6 | 10 | 1.78 | 0 | 2 | -2.38 | -2.38 | unavailable | 0.54 |  | SS 110/35 kV T-3 Gidrooborudovanie | 31.5 | 0.3945 | 4.7745 | 2.6 | 10 | 2.1745 | 0 | 2 | -2.7745 | -2.7745 | unavailable
187 | SS 110/35/10 kV Usman | 16+16 | 32 | 13.127 | 4.25 |  | 8.877 | 0 | 16.8 | 7.923 | 7.923 | available |  | 187 | SS 110/35/10 kV Usman | 16+16 | 3.951 | 17.078 | 4.25 |  | 12.828 | 0 | 16.8 | 3.972 | 3.972 | available
| Nom. capacity MV, МVА | 16+16 |  | 4.146 | 4 | 45 | 0.146 | 0 | 16.8 | 16.654 |  |  | 0.91 |  | Nom. capacity MV, МVА | 16+16 | 1.718 | 5.864 | 4 | 45 | 1.864 | 0 | 16.8 | 14.936
| Nom. Capacity LV, МVА | 16+16 |  | 8.981 | 0.25 | 70 | 8.731 | 0 | 16.8 | 8.069 |  |  | 0.95 |  | Nom. Capacity LV, МVА | 16+16 | 2.233 | 11.214 | 0.25 | 70 | 10.964 | 0 | 16.8 | 5.836
188 | SS 110/35/10 kV Aksai | 10+10 | 20 | 6.7 | 1.145 |  | 5.555 | 0 | 10.5 | 4.945 | 4.945 | available |  | 188 | SS 110/35/10 kV Aksai | 10+10 | 0.544 | 7.2437 | 1.145 |  | 6.0987 | 0 | 10.5 | 4.4013 | 4.4013 | available
| Nom. Capacity MV, МVА | 10+10 |  | 4.4497 | 1 | 60 | 3.4497 | 0 | 10.5 | 7.0503 |  |  | 0.99 |  | Nom. Capacity MV, МVА | 10+10 | 0.464 | 4.9137 | 1 | 60 | 3.9137 | 0 | 10.5 | 6.5863
| Nom. capacity LV, МVА | 10+10 |  | 2.25 | 0.145 | 70 | 2.105 | 0 | 10.5 | 8.395 |  |  | 0.92 |  | Nom. capacity LV, МVА | 10+10 | 0.08 | 2.33 | 0.145 | 70 | 2.185 | 0 | 10.5 | 8.315
189 | SS 110/35/10 kV Nikolskaya | 6,3+6,3 | 12.6 | 3.96 | 3.182 |  | 0.778 | 0 | 6.615 | 5.837 | 5.837 | available |  | 189 | SS 110/35/10 kV Nikolskaya | 6,3+6,3 | 0.4965 | 4.4565 | 3.182 |  | 1.2745 | 0 | 6.615 | 5.3405 | 5.3405 | available
| Nom. capacity MV, МVА | 6,3+6,3 |  | 3.1 | 3 | 120 | 0.1 | 0 | 6.615 | 6.515 |  |  | 0.95 |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.3935 | 3.4935 | 3 | 120 | 0.4935 | 0 | 6.615 | 6.1215
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.86 | 0.182 | 60 | 0.678 | 0 | 6.615 | 5.937 |  |  | 0.94 |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.103 | 0.963 | 0.182 | 60 | 0.781 | 0 | 6.615 | 5.834
190 | SS 110/35/10 kV Khvorostyanka | 10+16 | 26 | 11.582 | 5.16 |  | 6.422 | 0 | 10.5 | 4.078 | 4.078 | available |  | 190 | SS 110/35/10 kV Khvorostyanka | 10+16 | 2.394 | 13.976 | 5.16 |  | 8.816 | 0 | 10.5 | 1.684 | 1.684 | available
| Nom. capacity MV, МVА | 10+16 |  | 9.549 | 4.8 | 20 | 4.749 | 0 | 10.5 | 5.751 |  |  | 0.93 |  | Nom. capacity MV, МVА | 10+16 | 1.481 | 11.03 | 4.8 | 20 | 6.23 | 0 | 10.5 | 4.27
| Nom. capacity LV, МVА | 10+16 |  | 2.033 | 0.36 | 140 | 1.673 | 0 | 10.5 | 8.827 |  |  | 0.92 |  | Nom. capacity LV, МVА | 10+16 | 0.913 | 2.946 | 0.36 | 140 | 2.586 | 0 | 10.5 | 7.914
191 | SS 110/35/10 kV Dobrinka | 16+10 | 26 | 7.036 | 5.63 |  | 1.406 | 0 | 10.5 | 9.094 | 9.045 | available |  | 191 | SS 110/35/10 kV Dobrinka | 16+10 | 0.7645 | 7.8005 | 5.63 |  | 2.1705 | 0 | 10.5 | 8.3295 | 8.3295 | available
| Nom. capacity СН, МВА | 16+10 |  | 2.751 | 2.8 | 80 | -0.049 | 0 | 10.5 | 10.549 |  |  | 0.92 |  | Nom. capacity СН, МВА | 16+10 | 0.5815 | 3.3325 | 2.8 | 80 | 0.5325 | 0 | 10.5 | 9.9675
| Nom. capacity LV, МVА | 16+10 |  | 4.285 | 2.83 | 340 | 1.455 | 0 | 10.5 | 9.045 |  |  | 0.95 |  | Nom. capacity LV, МVА | 16+10 | 0.183 | 4.468 | 2.83 | 340 | 1.638 | 0 | 10.5 | 8.862
192 | SS 110/35/10 kV Verkhnyaya Matryonka | 6,3+6,3 | 12.6 | 2.148 | 1.04 |  | 1.108 | 0 | 6.615 | 5.507 | 5.507 | available |  | 192 | SS 110/35/10 kV Verkhnyaya Matryonka | 6,3+6,3 | 0.54 | 2.688 | 1.04 |  | 1.648 | 0 | 6.615 | 4.967 | 4.967 | available
| Nom. capacity MV, МVА | 6,3+6,3 |  | 1.343 | 0.7 | 30 | 0.643 | 0 | 6.615 | 5.972 |  |  | 0.99 |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.3 | 1.643 | 0.7 | 30 | 0.943 | 0 | 6.615 | 5.672
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.805 | 0.34 | 150 | 0.465 | 0 | 6.615 | 6.15 |  |  | 0.94 |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.045 | 0.34 | 150 | 0.705 | 0 | 6.615 | 5.91
193 | SS 110/35/10 kV Kazinka | 16+16 | 32 | 20.6 | 3.2 |  | 17.4 | 0 | 16.8 | -0.6 | -0.6 | unavailable |  | 193 | SS 110/35/10 kV Kazinka | 16+16 | 5.3435 | 25.9435 | 3.2 |  | 22.7435 | 0 | 16.8 | -5.9435 | -5.9435 | unavailable
| Nom. capacity MV, МVА | 16+16 |  | 13.15 | 3.2 | 15 | 9.95 | 0 | 16.8 | 6.85 |  |  | 0.942 |  | Nom. capacity MV, МVА | 16+16 | 3.6855 | 16.8355 | 3.2 | 15 | 13.6355 | 0 | 16.8 | 3.1645
| Nom. capacity LV, МVА | 16+16 |  | 7.45 | 0 | 0 | 7.45 | 0 | 16.8 | 9.35 |  |  | 0.917 |  | Nom. capacity LV, МVА | 16+16 | 1.658 | 9.108 | 0 | 0 | 9.108 | 0 | 16.8 | 7.692
194 | SS 110/35/10 kV Dobroe | 16+16 | 32 | 9.9 | 3.71 |  | 6.19 | 0 | 16.8 | 10.61 | 10.61 | * |  | 194 | SS 110/35/10 kV Dobroe | 16+16 | 4.058 | 13.958 | 3.71 |  | 10.248 | 0 | 16.8 | 6.552 | 6.552 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.59 | 2.5 | 30 | 3.09 | 0 | 16.8 | 13.71 |  |  | 0.93 |  | Nom. capacity MV, МVА | 16+16 | 2.241 | 7.831 | 2.5 | 30 | 5.331 | 0 | 16.8 | 11.469
| Nom. capacity LV, МVА | 16+16 |  | 4.31 | 1.21 | 100 | 3.1 | 0 | 16.8 | 13.7 |  |  | 0.93 |  | Nom. capacity LV, МVА | 16+16 | 1.817 | 6.127 | 1.21 | 100 | 4.917 | 0 | 16.8 | 11.883
195 | SS 110/35/6 kV Novaya Derevnya | 10+6,3 | 16.3 | 7 | 1.96 |  | 5.04 | 0 | 6.615 | 1.575 | 1.575 | * |  | 195 | SS 110/35/6 kV Novaya Derevnya | 10+6,3 | 2.1715 | 9.1715 | 1.96 |  | 7.2115 | 0 | 6.615 | -0.5965 | -0.5965 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 4.6 | 1.2 | 20 | 3.4 | 0 | 6.615 | 3.215 |  |  | 0.97 |  | Nom. capacity MV, МVА | 10+6,3 | 1.9385 | 6.5385 | 1.2 | 20 | 5.3385 | 0 | 6.615 | 1.2765
| Nom. capacity LV, МVА | 10+6,3 |  | 2.4 | 0.76 | 70 | 1.64 | 0 | 6.615 | 4.975 |  |  | 0.92 |  | Nom. capacity LV, МVА | 10+6,3 | 0.233 | 2.633 | 0.76 | 70 | 1.873 | 0 | 6.615 | 4.742
196 | SS 110/35/6 kV Verbilovo | 10+6,3 | 16.3 | 2.552 | 1.9 |  | 0.652 | 0 | 6.62 | 5.968 | 5.876 | * |  | 196 | SS 110/35/6 kV Verbilovo | 10+6,3 | 1.582 | 4.134 | 1.9 |  | 2.234 | 0 | 6.62 | 4.386 | 4.386 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 1.808 | 1.9 | 20 | -0.092 | 0 | 6.62 | 6.712 |  |  | 0.97 |  | Nom. capacity MV, МVА | 10+6,3 | 1.502 | 3.31 | 1.9 | 20 | 1.41 | 0 | 6.62 | 5.21
| Nom. capacity LV, МVА | 10+6,3 |  | 0.744 | 0 | 0 | 0.744 | 0 | 6.62 | 5.876 |  |  | 0.95 |  | Nom. capacity LV, МVА | 10+6,3 | 0.08 | 0.824 | 0 | 0 | 0.824 | 0 | 6.62 | 5.796
197 | SS 110/35/10 kV Khlevnoe | 16+16 | 32 | 10.43 | 0.85 |  | 9.58 | 0 | 16.8 | 7.22 | 7.22 | * |  | 197 | SS 110/35/10 kV Khlevnoe | 16+16 | 6.237 | 16.667 | 0.85 |  | 15.817 | 0 | 16.8 | 0.983 | 0.983 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.63 | 0.8 | 20 | 4.83 | 0 | 16.8 | 11.97 |  |  | 0.93 |  | Nom. capacity MV, МVА | 16+16 | 3.171 | 8.801 | 0.8 | 20 | 8.001 | 0 | 16.8 | 8.799
| Nom. capacity LV, МVА | 16+16 |  | 4.8 | 0.05 | 50 | 4.75 | 0 | 16.8 | 12.05 |  |  | 0.94 |  | Nom. capacity LV, МVА | 16+16 | 3.066 | 7.866 | 0.05 | 50 | 7.816 | 0 | 16.8 | 8.984
198 | SS 110/35/10 kV Naberezhnoe | 6,3+10 | 16.3 | 1.9595 | 0.8 |  | 1.1595 | 0 | 6.62 | 5.4605 | 5.4605 | available |  | 198 | SS 110/35/10 kV Naberezhnoe | 6,3+10 | 0.207 | 2.1665 | 0.8 |  | 1.3665 | 0 | 6.62 | 5.2535 | 5.2535 | available
| Nom. capacity MV, МVА | 6,3+10 |  | 0.9 | 0.8 | 10 | 0.1 | 0 | 6.62 | 6.52 |  |  | 0.98 |  | Nom. capacity MV, МVА | 6,3+10 | 0.177 | 1.077 | 0.8 | 10 | 0.277 | 0 | 6.62 | 6.343
| Nom. capacity LV, МVА | 6,3+10 |  | 1.0595 | 0 | 0 | 1.0595 | 0 | 6.62 | 5.5605 |  |  | 0.83 |  | Nom. capacity LV, МVА | 6,3+10 | 0.03 | 1.0895 | 0 | 0 | 1.0895 | 0 | 6.62 | 5.5305
199 | SS 110/35/10 kV Troekurovo | 10+6,3 | 16.3 | 1.3182 | 1.5 |  | -0.18182 | 0 | 6.62 | 6.8018 | 6.7018 | available |  | 199 | SS 110/35/10 kV Troekurovo | 10+6,3 | 0.041 | 1.3592 | 1.5 |  | -0.14082 | 0 | 6.62 | 6.7608 | 6.6678 | available
| Nom. capacity MV, МVА | 10+6,3 |  | 0.9 | 1 | 60 | -0.1 | 0 | 6.62 | 6.72 |  |  | 0.97 |  | Nom. capacity MV, МVА | 10+6,3 | 0.007 | 0.907 | 1 | 60 | -0.093 | 0 | 6.62 | 6.713
| Nom. capacity LV, МVА | 10+6,3 |  | 0.41818 | 0.5 | 120 | -0.081818 | 0 | 6.62 | 6.7018 |  |  | 0.97 |  | Nom. capacity LV, МVА | 10+6,3 | 0.034 | 0.45218 | 0.5 | 120 | -0.047818 | 0 | 6.62 | 6.6678
| Total: | 2862.5 | 2862.5 | 681.1869 | [6 empty] | 862.3064 |  |  | 2: Total:; 3: 2864.1; 5: 1048.3817; Min 12: 499.415
| deficit | [9 empty] | -16.9824 |  |  | 2: deficit; Min 12: -83.6444
| proficit | [9 empty] | 879.4618 | taken into account * |  | 2: proficit; Min 12: 583.2324; Min 13: taken into account *
* Restriction on connected capacity in the grid operation mode 110, 220 kV (according to Lipetsk Transmission Control Centre)

## Total current deficit
The list of closed supply centers of IDGC of Centre following the results of measurements of winter peak loads in 2011 (current capacity deficit).
Item # | Name of supply center, voltage class | Installed power capacity of transformers Sinst. including their number, pcs/ MVA |  | Current deficit
Lipetskenergo
1 | SS 110/10kV Leo Tolstoy | 10 | 10 | -0.2
2 | SS 110/10 kV Dvurechki | 6.3 | 6.3 | -1.5
3 | SS 35/10 kV Cheerful | 2.5 | 2.5 | -0.04
4 | SS 35/10 kV Kr.Palna | 3.2 | 3.2 | -0.77
5 | SS 35/10 kV Kamenka | 2.5 | 2.5 | -0.82
6 | SS 35/10 kV Krasotynovka | 2.5 | 2.5 | -0.18
7 | SS 35/10 kV Ozerki | 2.5 | 2.5 | -0.11
8 | SS 35/10 kV Pankratovka | 2.5 | 2.5 | -0.46
9 | SS 35/10 kV Transformation | 2.5 | 2.5 | -0.41
10 | SS 35/10 kV Yakovlevo | 2.5 | 2.5 | -0.81
11 | SS 35/10 kV Pervomayskaya | 2.5 | 2.5 | -0.54
12 | SS 35/10 kV Stone Lubna | 2.5 | 2.5 | -0.05
13 | SS 35/10 kV Znamenka | 2.5 | 2.5 | -0.55
14 | SS 35/10 kV Peak | 2.5 | 2.5 | -0.01
15 | SS 35/10 kV Peskovatka | 1.6 | 1.6 | -0.39
16 | SS 35/6 kV Novonikolaevka | 4 | 4 | -0.88
17 | SS 35/10 kV Sindyakino | 2.5 | 2.5 | -0.22
18 | SS 35/10 kV Chicken | 2.5 | 2.5 | -0.37
19 | SS 35/10 kV Novodubovoe | 2.5 | 2.5 | -1.05
20 | SS 110/35/10 kV Chaplygin | 6.3 | 6.3 | -1.45
21 | SS 35/10 kV Zadonsk-rural. | 3,2+1,6 | 4.8 | -0.24
22 | SS 35/6 kV № 2 | 1+1+1 | 3 | -0.66
23 | SS 35/10 kV Butyrki | 5,6+4 | 9.6 | -2.3
24 | SS 110/35 kV T-3 Hydraulic Equipment | 31.5 | 31.5 | -2.38
25 | SS 110/35/10 kV Kazinka | 16+16 | 32 | -0.6
| Nom. capacity MV, МVА | 16+16
| Nom. capacity LV, МVА | 16+16
Total current deficit (winter) |  | 147.3 |  | -16.99

## Total expected deficit
The list of closed supply centers of IDGC of Centre following the results of measurements of winter peak loads in 2011 (expected capacity deficit).
Item # | Name of supply center, voltage class | Installed power capacity of transformers Sinst. including their number, pcs/ MVA |  | Expected deficit
Lipetskenergo
1 | SS 110/10kV Leo Tolstoy | 10 | 10 | -1.02
2 | SS 110/10 kV Dvurechki | 6.3 | 6.3 | -2.54
3 | SS 35/10 kV Cheerful | 2.5 | 2.5 | -0.06
4 | SS 35/10 kV Kr.Palna | 3.2 | 3.2 | -1.29
5 | SS 35/10 kV Kamenka | 2.5 | 2.5 | -1.15
6 | SS 35/10 kV Krasotynovka | 2.5 | 2.5 | -0.18
7 | SS 35/10 kV Ozerki | 2.5 | 2.5 | -0.11
8 | SS 35/10 kV Pankratovka | 2.5 | 2.5 | -0.47
9 | SS 35/10 kV Transformation | 2.5 | 2.5 | -0.42
10 | SS 35/10 kV Yakovlevo | 2.5 | 2.5 | -1.28
11 | SS 35/10 kV Pervomayskaya | 2.5 | 2.5 | -0.56
12 | SS 35/10 kV Stone Lubna | 2.5 | 2.5 | -0.12
13 | SS 35/10 kV Znamenka | 2.5 | 2.5 | -0.55
14 | SS 35/10 kV Peak | 2.5 | 2.5 | -0.04
15 | SS 35/10 kV Peskovatka | 1.6 | 1.6 | -0.4
16 | SS 35/6 kV Novonikolaevka | 4 | 4 | -0.89
17 | SS 35/10 kV Sindyakino | 2.5 | 2.5 | -0.34
18 | SS 35/10 kV Chicken | 2.5 | 2.5 | -1.22
19 | SS 35/10 kV Novodubovoe | 2.5 | 2.5 | -1.1
20 | SS 110/35/10 kV Chaplygin | 6.3 | 6.3 | -2.12
21 | SS 110/10/6 kV Southwest | 40+40 | 80 | -19.06
22 | SS 110/10 kV University | 40+40 | 80 | -1.01
23 | SS 35/10 kV Aurora | 2,5+2,5 | 5 | -0.85
24 | SS 35/10 kV Zadonsk-rural. | 3,2+1,6 | 4.8 | -0.58
25 | SS 35/10 kV Olshanets | 2,5+4 | 6.5 | -3.16
26 | SS 35/10 kV Flat | 4+4 | 8 | -1.82
27 | SS 35/10 kV Ranenburg | 1,6+1,6 | 3.2 | -0.24
28 | SS 35/10 kV Apple | 2,5+2,5 | 5 | -0.75
29 | SS 35/10 kV № 1 | 4+4 | 8 | -0.64
30 | SS 35/6 kV № 2 | 1+1+1 | 3 | -0.75
31 | SS 35/10 kV № 3 | 2,5+2,5 | 5 | -0.19
32 | SS 35/10 kV Butyrki | 5,6+4 | 9.6 | -6
33 | SS 35/10 kV Yarlukovo | 3,2+4 | 7.2 | -0.54
34 | SS 35/10 kV SHT | 2,5+1,6 | 4.1 | -0.36
35 | SS 35/6 kV Tavolzhanka | 4+4 | 8 | -1.01
36 | SS 35/10 kV Borisovka | 4+2,5 | 6.5 | -1.78
37 | SS 35/10 kV Vvedenka | 4+4 | 8 | -5.05
38 | SS 35/10 kV Borin | 4+4 | 8 | -0.98
39 | SS 35/10 kV Frequent Dubrava | 2,5+2,5 | 5 | -0.18
40 | SS 35/10 kV Trinity | 2,5+4 | 6.5 | -0.41
41 | SS 35/6 kV Poultry | 4+4 | 8 | -0.35
42 | SS 110/35/10 kV Gorokhovskaya | 16+16 | 32 | -5.89
| Nom. capacity MV, MVA | 16+16
| Nom. capacity LV, MVA | 16+16
43 | SS 110/35/6 kV Hillock | 63+15+25 | 103 | -6.87
| Nom. capacity MV, MVA | 63+15+25
| Nom. capacity LV, MVA | 63+15+25
44 | SS 110/35 kV T-3 Hydraulic Equipment | 31.5 | 31.5 | -2.77
45 | SS 110/35/10 kV Kazinka | 16+16 | 32 | -5.94
| Nom. capacity MV, MVA | 16+16
| Nom. capacity LV, MVA | 16+16
46 | SS 110/35/6 kV New Village | 10+6,3 | 16.3 | -0.6
| Nom. capacity MV, МVА | 10+6,3
| Nom. capacity LV, МVА | 10+6,3
Total expected deficit (winter) |  | 560.6 |  | -83.64