## Smolenskenergo
Appendix 2
Calculation of transmission capacity of supply centers of IDGC of Centre - Smolenskenergo division following the results of measurements of peak loads in winter 2011
[9 empty] | table 1 | [14 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [9 empty] | Note | cosφ | No. | Name of supply center, voltage class | Expected deficit/proficit | [10 empty] | Note | cosφ
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA | Текущий дефицит/ профицит, МВт |  |  |  |  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Дополнительная мощность по выданным ТУ на ТП, МВт | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period provided that technical requirements at connections or other measures performed for reconstruction of the grid investment programs and etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [14 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 11 | 12 |  | 1 | 2 | 3 | 4 |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.3 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.4 | 0.4 | 0.396 | available | 0.99 | 1 | Gerchiki 35/10 | 2.5 | 0.34343 | 0.34 | 0.64343 | 0.7 | 1 day and night | -0.056566 | 0 | 0.7 | 0.056566 | 0.056566 | available | 0.99
2 | Verkhovye 35/10 | 4 | 0.55 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.81 | 0.81 | 0.8019 | available | 0.99 | 2 | Verkhovye 35/10 | 4 | 0 | 0 | 0.55 | 1.36 | 1 day and night | -0.81 | 0 | 1.36 | 0.81 | 0.81 | available | 0.99
3 | Neykovo 35/10 | 2.5 | 0.22 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.51 | 1.51 | 1.2533 | available | 0.83 | 3 | Neykovo 35/10 | 2.5 | 0 | 0 | 0.22 | 1.73 | 1 day and night | -1.51 | 0 | 1.73 | 1.51 | 1.51 | available | 0.83
4 | Merlino 110/35/10 | 6.3 | 0.35 | 0.35 | 1 day and night | 0.35 | 0 | 0.35 | 0 | 0 | 0 | available | 0.89 | 4 | Merlino 110/35/10 | 6.3 | 0.41067 | 0.3655 | 0.76067 | 0.76067 | 1 day and night | 0 | 0 | 0.76067 | 0 | 0 | available | 0.89
| Nom. capacity MV, МVА | 6.3 | 0.05 | 0.05 | 1 day and night | 0.05 | 0 | 0.05 | 0 |  | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0.37247 |  | 0.42247 | 0.42247 |  | 0 | 0 | 0.42247 | 0
| Nom. capacity LV, МVА | 6.3 | 0.3 | 0.3 | 1 day and night | 0.3 | 0 | 0.3 | 0 |  | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.038202 | 0.034 | 0.3382 | 0.3382 | 1 day and night | 0 | 0 | 0.3382 | 0
5 | Belyaevo 35/10 | 1.6 | 0.22 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 1.46 | 1.46 | 1.168 | available | 0.8 | 5 | Belyaevo 35/10 | 1.6 | 0 | 0 | 0.22 | 1.68 | 1 day and night | -1.46 | 0 | 1.68 | 1.46 | 1.46 | available | 0.8
6 | Zaozerye 35/10 | 1.6 | 0.15 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.7 | 0.7 | 0.693 | available | 0.99 | 6 | Zaozerye 35/10 | 1.6 | 0 | 0 | 0.15 | 0.85 | 1 day and night | -0.7 | 0 | 0.85 | 0.7 | 0.7 | available | 0.99
7 | Selezni 35/10 | 2.5 | 0.41 | 2.21 | 1 day and night | 2.21 | 0 | 2.21 | 1.8 | 1.8 | 1.746 | available | 0.97 | 7 | Selezni 35/10 | 2.5 | 0 | 0 | 0.41 | 2.21 | 1 day and night | -1.8 | 0 | 2.21 | 1.8 | 1.8 | available | 0.97
8 | Logovo 110/10 | 6.3 | 0.43 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.93 | 0.93 | 0.9207 | available | 0.99 | 8 | Logovo 110/10 | 6.3 | 0 | 0 | 0.43 | 1.36 | 1 day and night | -0.93 | 0 | 1.36 | 0.93 | 0.93 | available | 0.99
9 | Dubrovka 35/10 | 2.5 | 0.43 | 1.36 | 1 day and night | 1.36 | 0 | 1.36 | 0.93 | 0.93 | 0.9021 | available | 0.97 | 9 | Dubrovka 35/10 | 2.5 | 0.087629 | 0.085 | 0.51763 | 1.36 | 1 day and night | -0.84237 | 0 | 1.36 | 0.84237 | 0.84237 | available | 0.97
10 | Svistovichi 35/10 | 2.5 | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | 0.6633 | available | 0.99 | 10 | Svistovichi 35/10 | 2.5 | 0 | 0 | 0.18 | 0.85 | 1 day and night | -0.67 | 0 | 0.85 | 0.67 | 0.67 | available | 0.99
11 | Elsha 35/10 | 1.6 | 0.15 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.7 | 0.7 | 0.693 | available | 0.99 | 11 | Elsha 35/10 | 1.6 | 0 | 0 | 0.15 | 0.85 | 1 day and night | -0.7 | 0 | 0.85 | 0.7 | 0.7 | available | 0.99
12 | Sapsho 35/10 | 4 | 0.76 | 2.12 | 1 day and night | 2.12 | 0 | 2.12 | 1.36 | 1.36 | 1.292 | available | 0.95 | 12 | Sapsho 35/10 | 4 | 0.16105 | 0.153 | 0.92105 | 2.12 | 1 day and night | -1.1989 | 0 | 2.12 | 1.1989 | 1.1989 | available | 0.95
13 | Divo 110/10 | 2.5 | 0.43 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.42 | 0.42 | 0.399 | available | 0.95 | 13 | Divo 110/10 | 2.5 | 0.20579 | 0.1955 | 0.63579 | 0.85 | 1 day and night | -0.21421 | 0 | 0.85 | 0.21421 | 0.21421 | available | 0.95
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 1 day and night | 1.02 | 0 | 1.02 | 0.57 | 0.57 | 0.5073 | available | 0.89 | 14 | Vachkovo 35/10 | 2.5 | 0 | 0 | 0.45 | 1.02 | 1 day and night | -0.57 | 0 | 1.02 | 0.57 | 0.57 | available | 0.89
15 | Zamoshye 35/10 | 2.5 | 0.14 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.54 | 0.54 | 0.4806 | available | 0.89 | 15 | Zamoshye 35/10 | 2.5 | 0 | 0 | 0.14 | 0.68 | 1 day and night | -0.54 | 0 | 0.68 | 0.54 | 0.54 | available | 0.89
16 | Loino 35/10 | 2.5 | 0.19 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.66 | 0.66 | 0.6534 | available | 0.99 | 16 | Loino 35/10 | 2.5 | 0 | 0 | 0.19 | 0.85 | 1 day and night | -0.66 | 0 | 0.85 | 0.66 | 0.66 | available | 0.99
17 | Rokot 35/10 | 2.5 | 0.22 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 1.08 | 1.08 | 0.8964 | available | 0.83 | 17 | Rokot 35/10 | 2.5 | 0 | 0 | 0.22 | 1.3 | 1 day and night | -1.08 | 0 | 1.3 | 1.08 | 1.08 | available | 0.83
18 | Nikontsy 35/10 | 2.5 | 0.14 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.71 | 0.71 | 0.5041 | available | 0.71 | 18 | Nikontsy 35/10 | 2.5 | 0 | 0 | 0.14 | 0.85 | 1 day and night | -0.71 | 0 | 0.85 | 0.71 | 0.71 | available | 0.71
19 | Batishchevo 35/10 | 2.5 | 0.36 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.37 | 1.37 | 1.2741 | available | 0.93 | 19 | Batishchevo 35/10 | 2.5 | 0.064516 | 0.06 | 0.42452 | 1.73 | 1 day and night | -1.3055 | 0 | 1.73 | 1.3055 | 1.3055 | available | 0.93
20 | Vasino 35/10 | 2.5 | 1.08 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 1.47 | 1.47 | 1.1025 | available | 0.75 | 20 | Vasino 35/10 | 2.5 | 0 | 0 | 1.08 | 2.55 | 1 day and night | -1.47 | 0 | 2.55 | 1.47 | 1.47 | available | 0.75
21 | Bulgakovo 35/10 | 2.5 | 0.36 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.37 | 1.37 | 1.1371 | available | 0.83 | 21 | Bulgakovo 35/10 | 2.5 | 0.072289 | 0.06 | 0.43229 | 1.73 | 1 day and night | -1.2977 | 0 | 1.73 | 1.2977 | 1.2977 | available | 0.83
22 | Spas-Ugly 35/10 | 1.6 | 0.18 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.5 | 0.5 | 0.43 | available | 0.86 | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0 | 0.18 | 0.68 | 1 day and night | -0.5 | 0 | 0.68 | 0.5 | 0.5 | available | 0.86
23 | Tretyakovo 35/10 | 4 | 0.36 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.19 | 2.19 | 1.8177 | available | 0.83 | 23 | Tretyakovo 35/10 | 4 | 0.096386 | 0.08 | 0.45639 | 2.55 | 1 day and night | -2.0936 | 0 | 2.55 | 2.0936 | 2.0936 | available | 0.83
24 | Velisto 35/10 | 2.5 | 0.14 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 1.16 | 1.16 | 0.9628 | available | 0.83 | 24 | Velisto 35/10 | 2.5 | 0 | 0 | 0.14 | 1.3 | 1 day and night | -1.16 | 0 | 1.3 | 1.16 | 1.16 | available | 0.83
25 | Baturino 35/10 | 1.6 | 0.14 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.71 | 0.71 | 0.7029 | available | 0.99 | 25 | Baturino 35/10 | 1.6 | 0 | 0 | 0.14 | 0.85 | 1 day and night | -0.71 | 0 | 0.85 | 0.71 | 0.71 | available | 0.99
26 | Pechatniki 35/10 | 2.5 | 0.72 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 1.905 | 1.905 | 1.6954 | available | 0.89 | 26 | Pechatniki 35/10 | 2.5 | 0 | 0 | 0.72 | 2.625 | 1 day and night | -1.905 | 0 | 2.625 | 1.905 | 1.905 | available | 0.89
27 | Garistovo 35/10 | 1.6 | 0.11 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.74 | 0.74 | 0.6586 | available | 0.89 | 27 | Garistovo 35/10 | 1.6 | 0.011236 | 0.01 | 0.12124 | 0.85 | 1 day and night | -0.72876 | 0 | 0.85 | 0.72876 | 0.72876 | available | 0.89
28 | Bezzaboty 35/10 | 2.5 | 0.14 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.59 | 1.59 | 1.4151 | available | 0.89 | 28 | Bezzaboty 35/10 | 2.5 | 0.5618 | 0.5 | 0.7018 | 1.73 | 1 day and night | -1.0282 | 0 | 1.73 | 1.0282 | 1.0282 | available | 0.89
29 | Vysokoe 35/10 | 2.5 | 0.14 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.41 | 2.41 | 2.1449 | available | 0.89 | 29 | Vysokoe 35/10 | 2.5 | 0 | 0 | 0.14 | 2.55 | 1 day and night | -2.41 | 0 | 2.55 | 2.41 | 2.41 | available | 0.89
30 | Zaytsevo 35/10 | 1.6 | 0.38 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.47 | 0.47 | 0.4559 | available | 0.97 | 30 | Zaytsevo 35/10 | 1.6 | 0.014433 | 0.014 | 0.39443 | 0.85 | 1 day and night | -0.45557 | 0 | 0.85 | 0.45557 | 0.45557 | available | 0.97
31 | Saveevo 35/10 | 2.5 | 0.44 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.41 | 0.41 | 0.3936 | available | 0.96 | 31 | Saveevo 35/10 | 2.5 | 0.09375 | 0.09 | 0.53375 | 0.85 | 1 day and night | -0.31625 | 0 | 0.85 | 0.31625 | 0.31625 | available | 0.96
32 | Gorenovo 35/10 | 1.6 | 0.24 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 1.44 | 1.44 | 1.1808 | available | 0.82 | 32 | Gorenovo 35/10 | 1.6 | 0.060976 | 0.05 | 0.30098 | 1.68 | 1 day and night | -1.379 | 0 | 1.68 | 1.379 | 1.379 | available | 0.82
33 | Shpunty 35/10 | 2.5 | 0.51 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.34 | 0.34 | 0.2652 | available | 0.78 | 33 | Shpunty 35/10 | 2.5 | 1.0256 | 0.8 | 1.5356 | 0.85 | 1 day and night | 0.68564 | 0 | 0.85 | -0.68564 | -0.68564 | unavailable | 0.78
34 | Kadino 35/10 | 2.5 | 0.18 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.55 | 1.55 | 1.3795 | available | 0.89 | 34 | Kadino 35/10 | 2.5 | 0 | 0 | 0.18 | 1.73 | 1 day and night | -1.55 | 0 | 1.73 | 1.55 | 1.55 | available | 0.89
35 | Стегримово 35/10 | 2.5 | 0.53 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 2.095 | 2.095 | 2.0322 | available | 0.97 | 35 | Стегримово 35/10 | 2.5 | 0.020619 | 0.02 | 0.55062 | 2.625 | 1 day and night | -2.0744 | 0 | 2.625 | 2.0744 | 2.0744 | available | 0.97
36 | Zhukovo 35/10 | 2.5 | 0.26 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.47 | 1.47 | 1.3083 | available | 0.89 | 36 | Zhukovo 35/10 | 2.5 | 0 | 0 | 0.26 | 1.73 | 1 day and night | -1.47 | 0 | 1.73 | 1.47 | 1.47 | available | 0.89
37 | Mikshino 35/10 | 2.5 | 0.11 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.62 | 1.62 | 1.0854 | available | 0.67 | 37 | Mikshino 35/10 | 2.5 | 0.022388 | 0.015 | 0.13239 | 1.73 | 1 day and night | -1.5976 | 0 | 1.73 | 1.5976 | 1.5976 | available | 0.67
38 | Petrovichi 35/10 | 2.5 | 0.16 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.39 | 2.39 | 1.9837 | available | 0.83 | 38 | Petrovichi 35/10 | 2.5 | 0.0012048 | 0.001 | 0.1612 | 2.55 | 1 day and night | -2.3888 | 0 | 2.55 | 2.3888 | 2.3888 | available | 0.83
39 | Mikulichi 35/10 | 2.5 | 0.35 | 2.625 | 1 day and night | 2.625 | 0 | 2.625 | 2.275 | 2.275 | 1.9565 | available | 0.86 | 39 | Mikulichi 35/10 | 2.5 | 0.011628 | 0.01 | 0.36163 | 2.625 | 1 day and night | -2.2634 | 0 | 2.625 | 2.2634 | 2.2634 | available | 0.86
40 | Nedeykovichi 35/10 | 2.5 | 0.24 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.61 | 0.61 | 0.4758 | available | 0.78 | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0 | 0.24 | 0.85 | 1 day and night | -0.61 | 0 | 0.85 | 0.61 | 0.61 | available | 0.78
41 | Posyolki 110/35/10 | 6.3 | 0.48 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.46 | 0.46 | 0.3266 | available | 0.71 | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0 | 0.48 | 0.94 | 1 day and night | -0.46 | 0 | 0.94 | 0.46 | 0.46 | available | 0.71
42 | Kuzmichi 35/10 | 2.5 | 0.23 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.5 | 1.5 | 1.065 | available | 0.71 | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0 | 0.23 | 1.73 | 1 day and night | -1.5 | 0 | 1.73 | 1.5 | 1.5 | available | 0.71
43 | Maksheevo 110/10 | 6.3 | 0.53 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.02 | 2.02 | 1.7574 | available | 0.87 | 43 | Maksheevo 110/10 | 6.3 | 0.057471 | 0.05 | 0.58747 | 2.55 | 1 day and night | -1.9625 | 0 | 2.55 | 1.9625 | 1.9625 | available | 0.87
44 | Putkovo 35/10 | 1.8 | 0.22 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.63 | 0.63 | 0.4473 | available | 0.71 | 44 | Putkovo 35/10 | 1.8 | 0.071831 | 0.051 | 0.29183 | 0.85 | 1 day and night | -0.55817 | 0 | 0.85 | 0.55817 | 0.55817 | available | 0.71
45 | Uspenskoe 35/10 | 2.5 | 0.45 | 2.55 | 1 day and night | 2.55 | 0 | 2.55 | 2.1 | 2.1 | 2.079 | available | 0.99 | 45 | Uspenskoe 35/10 | 2.5 | 0.12879 | 0.1275 | 0.57879 | 2.55 | 1 day and night | -1.9712 | 0 | 2.55 | 1.9712 | 1.9712 | available | 0.99
46 | Kalpita 35/10 | 1.6 | 0.06 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.79 | 0.79 | 0.5609 | available | 0.71 | 46 | Kalpita 35/10 | 1.6 | 0 | 0 | 0.06 | 0.85 | 1 day and night | -0.79 | 0 | 0.85 | 0.79 | 0.79 | available | 0.71
47 | Kasnya 110/10 | 2.5 | 0.29 | 2.62 | 1 day and night | 2.62 | 0 | 2.62 | 2.33 | 2.33 | 2.1669 | available | 0.93 | 47 | Kasnya 110/10 | 2.5 | 0 | 0 | 0.29 | 2.62 | 1 day and night | -2.33 | 0 | 2.62 | 2.33 | 2.33 | available | 0.93
48 | Akatovo 35/10 | 1.6 | 1.06 | 1.68 | 1 day and night | 1.68 | 0 | 1.68 | 0.62 | 0.62 | 0.5766 | available | 0.93 | 48 | Akatovo 35/10 | 1.6 | 1.2247 | 1.139 | 2.2847 | 1.68 | 1 day and night | 0.60473 | 0 | 1.68 | -0.60473 | -0.60473 | unavailable | 0.93
49 | Gorki 35/10 | 1.6 | 0.19 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.49 | 0.49 | 0.4214 | available | 0.86 | 49 | Gorki 35/10 | 1.6 | 0 | 0 | 0.19 | 0.68 | 1 day and night | -0.49 | 0 | 0.68 | 0.49 | 0.49 | available | 0.86
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.06 | 0.06 | 0.051 | available | 0.85 | 50 | Druzhba 35/10 | 2.5 | 0 | 0 | 0.79 | 0.85 | 1 day and night | -0.06 | 0 | 0.85 | 0.06 | 0.06 | available | 0.85
51 | NS-21 110/10 | 16 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 | 0 | 0 | available | 1 | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 | 0 | available | 1
52 | NS-22 110/35/10 | 25 | 2.97 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0 | 0 | 0 | available | 0.91 | 52 | NS-22 110/35/10 | 25 | 1.6907 | 1.5385 | 4.6607 | 4.6607 | 1 day and night | 0 | 0 | 4.6607 | 0 | 0 | available | 0.91
| Nom. capacity MV, МVА | 25 | 2.97 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0 | [5 empty] | Nom. capacity MV, МVА | 25 | 1.6907 |  | 4.6607 | 4.6607 | 1 day and night | 0 | 0 | 4.6607 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0 | [5 empty] | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 0 | 1 day and night | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.44 | 2.62 | 1 day and night | 2.62 | 0 | 2.62 | 2.18 | 2.18 | 2.1582 | available | 0.99 | 53 | Shuyskoe 35/10 | 2.5 | 0.042929 | 0.0425 | 0.48293 | 2.62 | 1 day and night | -2.1371 | 0 | 2.62 | 2.1371 | 2.1371 | available | 0.99
54 | Torbeevo 110/10 | 6.3 | 0.3 | 2.89 | 1 day and night | 2.89 | 0 | 2.89 | 2.59 | 2.59 | 2.3051 | available | 0.89 | 54 | Torbeevo 110/10 | 6.3 | 0.14326 | 0.1275 | 0.44326 | 2.89 | 1 day and night | -2.4467 | 0 | 2.89 | 2.4467 | 2.4467 | available | 0.89
55 | Leuzdovo 35/10 | 1 | 0.14 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.54 | 0.54 | 0.5346 | available | 0.99 | 55 | Leuzdovo 35/10 | 1 | 0.25758 | 0.255 | 0.39758 | 0.68 | 1 day and night | -0.28242 | 0 | 0.68 | 0.28242 | 0.28242 | available | 0.99
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.56 | 1.56 | 1.482 | available | 0.95 | 56 | Maltsevo 35/10 | 2.5 | 0.0089474 | 0.0085 | 0.17895 | 1.73 | 1 day and night | -1.5511 | 0 | 1.73 | 1.5511 | 1.5511 | available | 0.95
57 | Avrora 35/10 | 2.5 | 0.26 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.42 | 0.42 | 0.3948 | available | 0.94 | 57 | Avrora 35/10 | 2.5 | 3.0564 | 2.873 | 3.3164 | 0.68 | 1 day and night | 2.6364 | 0 | 0.68 | -2.6364 | -2.6364 | unavailable | 0.94
58 | Bekhteevo 35/10 | 2.5 | 0.13 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.55 | 0.55 | 0.4785 | available | 0.87 | 58 | Bekhteevo 35/10 | 2.5 | 0.068391 | 0.0595 | 0.19839 | 0.68 | 1 day and night | -0.48161 | 0 | 0.68 | 0.48161 | 0.48161 | available | 0.87
59 | Sereda 35/10 | 2.5 | 0.31 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.37 | 0.37 | 0.3293 | available | 0.89 | 59 | Sereda 35/10 | 2.5 | 0 | 0 | 0.31 | 0.68 | 1 day and night | -0.37 | 0 | 0.68 | 0.37 | 0.37 | available | 0.89
60 | Mikhali 35/10 | 2.5 | 0.08 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.77 | 0.77 | 0.6314 | available | 0.82 | 60 | Mikhali 35/10 | 2.5 | 0 | 0 | 0.08 | 0.85 | 1 day and night | -0.77 | 0 | 0.85 | 0.77 | 0.77 | available | 0.82
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 1 day and night | 0 | 0 | 0 | -0.06 | -0.06 | -0.048 | unavailable | 0.8 | 61 | Mytishino 35/10 | 1.6 | 0 | 0 | 0.06 | 0 | 1 day and night | 0.06 | 0 | 0 | -0.06 | -0.06 | unavailable | 0.8
62 | Zakharyevskoe 35/10 | 1.6 | 0.04 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.81 | 0.81 | 0.729 | available | 0.9 | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0 | 0.04 | 0.85 | 1 day and night | -0.81 | 0 | 0.85 | 0.81 | 0.81 | available | 0.9
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.8 | 0.8 | 0.736 | available | 0.92 | 63 | Kholm 35/10 | 1.6 | 0 | 0 | 0.05 | 0.85 | 1 day and night | -0.8 | 0 | 0.85 | 0.8 | 0.8 | available | 0.92
64 | Baskakovka 35/10 | 4 | 0.24 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.49 | 1.49 | 1.3708 | available | 0.92 | 64 | Baskakovka 35/10 | 4 | 0 | 0 | 0.24 | 1.73 | 1 day and night | -1.49 | 0 | 1.73 | 1.49 | 1.49 | available | 0.92
65 | Ekimtsevo 110/10 | 2.5 | 0.25 | 1.73 | 1 day and night | 1.73 | 0 | 1.73 | 1.48 | 1.48 | 1.3468 | available | 0.91 | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0 | 0.25 | 1.73 | 1 day and night | -1.48 | 0 | 1.73 | 1.48 | 1.48 | available | 0.91
Two-transformer substations | [13 empty] | Two-transformer substations
66 | Смоленск 1 (ФСК) 110/35/6 | 40+40 | 35.1 | 4.35 | 120 | 30.75 | 0 | 42 | 11.25 | 11.25 | 11.25 | available |  | 66 | Смоленск 1 (ФСК) 110/35/6 | 40+40 | 24.29 |  | 59.39 | 10.83 | 120 | 48.56 | 0 | 42 | -6.56 | -6.56 | unavailable
| Ном. Мощность СН, МВА | 40+40 | 2.43 | 2.43 |  | 0 | 0 | 42 | 42 | [5 empty] | Ном. Мощность СН, МВА | 40+40 | 6.48 |  | 8.91 | 8.91 |  | 0 | 0 | 42 | 42
| Ном. мощность НН, МВА | 40+40 | 32.67 | 1.92 | 120 | 30.75 | 0 | 42 | 11.25 | [5 empty] | Ном. мощность НН, МВА | 40+40 | 17.81 |  | 50.48 | 1.92 | 120 | 48.56 | 0 | 42 | -6.56
67 | Water intake 35/6 | 4+4 | 2.91 | 1.2 | 120 | 1.71 | 0 | 4.2 | 2.49 | 2.49 | 2.2161 | available | 0.89 | 67 | Water intake 35/6 | 4+4 | 1.9865 | 1.768 | 4.8965 | 1.2 | 120 | 3.6965 | 0 | 4.2 | 0.50348 | 0.50348 | available | 0.89
68 | Tychinino 35/10 | 4+4 | 1.06 | 0.91 | 120 | 0.15 | 0 | 4.2 | 4.05 | 4.05 | 3.6045 | available | 0.89 | 68 | Tychinino 35/10 | 4+4 | 0.39157 | 0.3485 | 1.4516 | 0.91 | 120 | 0.54157 | 0 | 4.2 | 3.6584 | 3.6584 | available | 0.89
69 | Ryabtsevo 35/10 | 4+4 | 3.29 | 0 | 120 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | 0.7462 | available | 0.82 | 69 | Ryabtsevo 35/10 | 4+4 | 2.7988 | 2.295 | 6.0888 | 0 | 120 | 6.0888 | 0 | 4.2 | -1.8888 | -1.8888 | unavailable | 0.82
70 | Smolensk 2 110/6 | 40+40 | 18.45 | 6.41 | 120 | 12.04 | 0 | 42 | 29.96 | 29.96 | 25.7656 | available | 0.86 | 70 | Smolensk 2 110/6 | 40+40 | 6.5134 | 5.6015 | 24.9634 | 6.41 | 120 | 18.5534 | 0 | 42 | 23.4466 | 23.4466 | available | 0.86
71 | Vostochnaya 110/6 | 25+16 | 8.28 | 0 | 120 | 8.28 | 0 | 16.8 | 8.52 | 8.52 | 7.9236 | available | 0.93 | 71 | Vostochnaya 110/6 | 25+16 | 11.5161 | 10.71 | 19.7961 | 0 | 120 | 19.7961 | 0 | 16.8 | -2.9961 | -2.9961 | unavailable | 0.93
72 | Diffuzion 110/6 | 25+25 | 17.24 | 1.06 | 120 | 16.18 | 0 | 26.25 | 10.07 | 10.07 | 9.2644 | available | 0.92 | 72 | Diffuzion 110/6 | 25+25 | 19.7717 | 18.19 | 37.0117 | 1.06 | 120 | 35.9517 | 0 | 26.25 | -9.7017 | -9.7017 | unavailable | 0.92
73 | Zavodskaya 110/35/10 | 16+16 | 10.63 | 9.34 | 120 | 1.29 | 0 | 16.8 | 15.51 | 13.11 | 12.3234 | available | 0.94 | 73 | Zavodskaya 110/35/10 | 16+16 | 12.0176 | 11.2965 | 22.6476 | 11.9578 | 120 | 10.6897 | 0 | 16.8 | 6.1103 | 6.1103 | available | 0.94
| Nom. capacity MV, МVА | 16+16 | 7.38 | 3.69 |  | 3.69 | 0 | 16.8 | 13.11 | [5 empty] | Nom. capacity MV, МVА | 16+16 | 5.2356 |  | 12.6156 | 6.3078 |  | 6.3078 | 0 | 16.8 | 10.4922
| Nom. capacity LV, МVА | 16+16 | 3.25 | 5.65 | 120 | -2.4 | 0 | 16.8 | 19.2 | [5 empty] | Nom. capacity LV, МVА | 16+16 | 6.7819 | 6.375 | 10.0319 | 5.65 | 120 | 4.3819 | 0 | 16.8 | 12.4181
74 | Yasennaya 35/6 | 10+10 | 8.82 | 0 | 120 | 8.82 | 0 | 10.5 | 1.68 | 1.68 | 1.6128 | available | 0.96 | 74 | Yasennaya 35/6 | 10+10 | 1.4609 | 1.4025 | 10.2809 | 0 | 120 | 10.2809 | 0 | 10.5 | 0.21906 | 0.21906 | available | 0.96
75 | Gnezodovo 35/6 | 7,5+7,5 | 5.89 | 0.42 | 120 | 5.47 | 0 | 7.875 | 2.405 | 2.405 | 2.1645 | available | 0.9 | 75 | Gnezodovo 35/6 | 7,5+7,5 | 3.9006 | 3.5105 | 9.7906 | 0.42 | 120 | 9.3706 | 0 | 7.875 | -1.4956 | -1.4956 | unavailable | 0.9
76 | Zapadnaya 110/6 | 25+16 | 13.4 | 0.63 | 120 | 12.77 | 0 | 16.8 | 4.03 | 4.03 | 3.8688 | available | 0.96 | 76 | Zapadnaya 110/6 | 25+16 | 10.0052 | 9.605 | 23.4052 | 0.63 | 120 | 22.7752 | 0 | 16.8 | -5.9752 | -5.9752 | unavailable | 0.96
77 | Katyn 2 110/35/10 | 10+16 | 4.43 | 2.66 | 120 | 1.77 | 0 | 10.5 | 8.73 | 8.73 | 7.6824 | available | 0.88 | 77 | Katyn 2 110/35/10 | 10+16 | 11.079 | 9.7495 | 15.509 | 8.6776 | 120 | 6.8314 | 0 | 10.5 | 3.6686 | 3.6686 | available | 0.88
| Nom. capacity MV, МVА | 10+16 | 2.66 | 2.66 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+16 | 6.0176 |  | 8.6776 | 8.6776 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.77 | 0 | 120 | 1.77 | 0 | 10.5 | 8.73 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 5.0614 | 4.454 | 6.8314 | 0 | 120 | 6.8314 | 0 | 10.5 | 3.6686
78 | Katyn 1 35/10 | 4+4 | 1.69 | 0.05 | 120 | 1.64 | 0 | 4.2 | 2.56 | 2.56 | 2.1248 | available | 0.83 | 78 | Katyn 1 35/10 | 4+4 | 2.3247 | 1.9295 | 4.0147 | 0.05 | 120 | 3.9647 | 0 | 4.2 | 0.2353 | 0.2353 | available | 0.83
79 | Lubnya 35/10 | 4+4 | 1.2 | 0.13 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 | 2.9422 | available | 0.94 | 79 | Lubnya 35/10 | 4+4 | 2.7399 | 2.5755 | 3.9399 | 0.13 | 120 | 3.8099 | 0 | 4.2 | 0.39011 | 0.39011 | available | 0.94
80 | Kozino 110/35/10 | 10+10 | 10.79 | 6.9 | 120 | 3.89 | 0 | 10.5 | 6.61 | 6.61 | 5.8168 | available | 0.88 | 80 | Kozino 110/35/10 | 10+10 | 15.4062 | 13.5575 | 26.1962 | 2.3329 | 120 | 23.8634 | 0 | 10.5 | -13.3634 | -13.3634 | unavailable | 0.88
| Nom. capacity MV, МVА | 10+10 | 6.89 | 6.89 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 11.3398 |  | 18.2298 | 2.3229 |  | 15.9069 | 0 | 10.5 | -5.4069
| Nom. capacity LV, МVА | 10+10 | 3.9 | 0.01 | 120 | 3.89 | 0 | 10.5 | 6.61 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 4.0665 | 3.5785 | 7.9665 | 0.01 | 120 | 7.9565 | 0 | 10.5 | 2.5435
81 | Odintsovo 35/10 | 6,3+6,3 | 5.97 | 2.15 | 120 | 3.82 | 0 | 6.615 | 2.795 | 2.795 | 2.3478 | available | 0.84 | 81 | Odintsovo 35/10 | 6,3+6,3 | 9.9369 | 8.347 | 15.9069 | 2.15 | 120 | 13.7569 | 0 | 6.615 | -7.1419 | -7.1419 | unavailable | 0.84
82 | Trudilovo 35/10 | 2,5+2,5 | 1.13 | 0.08 | 120 | 1.05 | 0 | 2.625 | 1.575 | 1.575 | 1.3545 | available | 0.86 | 82 | Trudilovo 35/10 | 2,5+2,5 | 1.2058 | 1.037 | 2.3358 | 0.08 | 120 | 2.2558 | 0 | 2.625 | 0.36919 | 0.36919 | available | 0.86
83 | KS-3 SSNo.2 110/10 | 40+40 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | 41.02 | available | 1 | 83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | available | 1
84 | Pronino 110/35/6 | 10+10 | 6.31 | 4.62 | 120 | 1.69 | 0 | 10.5 | 8.81 | 8.81 | 7.2242 | available | 0.82 | 84 | Pronino 110/35/6 | 10+10 | 6.8104 | 5.5845 | 13.1204 | 10.031 | 120 | 3.0894 | 0 | 10.5 | 7.4106 | 7.4106 | available | 0.82
| Nom. capacity MV, МVА | 10+10 | 3.43 | 3.43 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 5.411 |  | 8.841 | 8.841 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.88 | 1.19 | 120 | 1.69 | 0 | 10.5 | 8.81 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 1.3994 | 1.1475 | 4.2794 | 1.19 | 120 | 3.0894 | 0 | 10.5 | 7.4106
85 | Olsha 35/10 | 2,5+2,5 | 1.06 | 0 | 120 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | 1.3772 | available | 0.88 | 85 | Olsha 35/10 | 2,5+2,5 | 1.4972 | 1.3175 | 2.5572 | 0 | 120 | 2.5572 | 0 | 2.625 | 0.067841 | 0.067841 | available | 0.88
86 | Krasny bor 35/6 | 4+4 | 3.08 | 0 | 120 | 3.08 | 0 | 4.2 | 1.12 | 1.12 | 1.008 | available | 0.9 | 86 | Krasny bor 35/6 | 4+4 | 3.3811 | 3.043 | 6.4611 | 0 | 120 | 6.4611 | 0 | 4.2 | -2.2611 | -2.2611 | unavailable | 0.9
87 | Severnaya 110/35/6 | 25+25 | 20.07 | 10.59 | 120 | 9.48 | 0 | 26.25 | 16.77 | 16.77 | 14.9253 | available | 0.89 | 87 | Severnaya 110/35/6 | 25+25 | 14.6124 | 13.005 | 34.6824 | 10.6411 | 120 | 24.0412 | 0 | 26.25 | 2.2088 | 2.2088 | available | 0.89
| Nom. capacity MV, МVА | 25+25 | 8 | 8 |  | 0 | 0 | 26.25 | 26.25 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 8.0511 | 7.1655 | 8.0511 | 8.0511 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 12.07 | 2.59 | 120 | 9.48 | 0 | 26.25 | 16.77 | [5 empty] | Nom. capacity LV, МVА | 25+25 | 6.5612 | 5.8395 | 18.6312 | 2.59 | 120 | 16.0412 | 0 | 26.25 | 10.2088
88 | Peсhersk 35/6 | 4+4 | 3.32 | 0.34 | 120 | 2.98 | 0 | 4.2 | 1.22 | 1.22 | 1.0858 | available | 0.89 | 88 | Peсhersk 35/6 | 4+4 | 5.2528 | 4.675 | 8.5728 | 0.34 | 120 | 8.2328 | 0 | 4.2 | -4.0328 | -4.0328 | unavailable | 0.89
89 | Kolodnya 35/6 | 6,3+4 | 3.01 | 0 | 120 | 3.01 | 0 | 4.2 | 1.19 | 1.19 | 1.1186 | available | 0.94 | 89 | Kolodnya 35/6 | 6,3+4 | 2.6585 | 2.499 | 5.6685 | 0 | 120 | 5.6685 | 0 | 4.2 | -1.4685 | -1.4685 | unavailable | 0.94
90 | Tsentralnaya 110/10/6 | 25+25 | 19.2 | 7.75 | 120 | 11.45 | 0 | 26.25 | 14.8 | 14.8 | 13.764 | available | 0.93 | 90 | Tsentralnaya 110/10/6 | 25+25 | 13.0608 | 12.1465 | 32.2608 | 8.43 | 120 | 23.8308 | 0 | 26.25 | 2.4192 | 2.4192 | available | 0.93
| Nom. capacity MV, МVА | 25+25 | 1.99 | 1.99 |  | 0 | 0 | 26.25 | 26.25 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 8.6645 | 8.058 | 10.6545 | 3 |  | 7.6545 | 0 | 26.25 | 18.5955
| Nom. capacity LV, МVА | 25+25 | 17.21 | 5.76 | 120 | 11.45 | 0 | 26.25 | 14.8 | [5 empty] | Nom. capacity LV, МVА | 25+25 | 4.3962 | 4.0885 | 21.6062 | 5.43 | 120 | 16.1762 | 0 | 26.25 | 10.0738
91 | Chernushki 110/10/6 | 25+25 | 20.97 | 0 | 120 | 20.97 | 0 | 26.25 | 5.28 | 5.28 | 4.9632 | available | 0.94 | 91 | Chernushki 110/10/6 | 25+25 | 15.1011 | 14.195 | 36.0711 | 2.12 | 120 | 33.9511 | 0 | 26.25 | -7.7011 | -7.7011 | unavailable | 0.94
| Nom. capacity MV, МVА | 25+25 | 8.1 | 0 |  | 8.1 | 0 | 26.25 | 18.15 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 5.3532 | 5.032 | 13.4532 | 0 |  | 13.4532 | 0 | 26.25 | 12.7968
| Nom. Capacity LV, МVА | 25+25 | 12.87 | 0 | 120 | 12.87 | 0 | 26.25 | 13.38 | [5 empty] | Nom. Capacity LV, МVА | 25+25 | 9.7479 | 9.163 | 22.6179 | 2.12 | 120 | 20.4979 | 0 | 26.25 | 5.7521
92 | Yuzhnaya 110/35/6 | 40+40 | 36.1 | 10.6 | 120 | 25.5 | 0 | 42 | 16.5 | 16.5 | 15.015 | available | 0.91 | 92 | Yuzhnaya 110/35/6 | 40+40 | 26.9945 | 24.565 | 63.0945 | 13.0426 | 120 | 50.0519 | 0 | 42 | -8.0519 | -8.0519 | unavailable | 0.91
| Nom. capacity MV, МVА | 40+40 | 9.76 | 4.88 |  | 4.88 | 0 | 42 | 37.12 | [5 empty] | Nom. capacity MV, МVА | 40+40 | 4.8852 | 4.4455 | 14.6452 | 7.3226 |  | 7.3226 | 0 | 42 | 34.6774
| Nom. capacity LV, МVА | 40+40 | 26.34 | 5.72 | 120 | 20.62 | 0 | 42 | 21.38 | [5 empty] | Nom. capacity LV, МVА | 40+40 | 22.1093 | 20.1195 | 48.4493 | 5.72 | 120 | 42.7293 | 0 | 42 | -0.72934
93 | Karyernaya 110/35/6 | 16+16 | 5.7 | 5.13 | 120 | 0.57 | 0 | 16.8 | 16.23 | 16.23 | 13.4709 | available | 0.83 | 93 | Karyernaya 110/35/6 | 16+16 | 3.4614 | 2.873 | 9.1614 | 8.5607 | 120 | 0.60072 | 0 | 16.8 | 16.1993 | 16.1993 | available | 0.83
| Nom. capacity MV, МВА | 16+16 | 5.13 | 5.13 |  | 0 | 0 | 16.8 | 16.8 | [5 empty] | Nom. capacity MV, МВА | 16+16 | 3.4307 | 2.8475 | 8.5607 | 8.5607 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0.57 | 0 | 120 | 0.57 | 0 | 16.8 | 16.23 | [5 empty] | Nom. capacity LV, МVА | 16+16 | 0.030723 | 0.0255 | 0.60072 | 0 | 120 | 0.60072 | 0 | 16.8 | 16.1993
94 | Koshchino 35/10 | 4+4 | 0.55 | 0.11 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | 3.572 | available | 0.95 | 94 | Koshchino 35/10 | 4+4 | 0.19684 | 0.187 | 0.74684 | 0.11 | 120 | 0.63684 | 0 | 4.2 | 3.5632 | 3.5632 | available | 0.95
95 | Kommunar 35/10 | 2,5+2,5 | 0.44 | 0.03 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | 2.1928 | available | 0.99 | 95 | Kommunar 35/10 | 2,5+2,5 | 0.12121 | 0.12 | 0.56121 | 0.03 | 120 | 0.53121 | 0 | 2.625 | 2.0938 | 2.0938 | available | 0.99
96 | Kasplya 110/35/10 | 10+10 | 3.6 | 3.33 | 120 | 0.27 | 0 | 10.5 | 10.23 | 10.23 | 8.7978 | available | 0.86 | 96 | Kasplya 110/35/10 | 10+10 | 6.4541 | 5.5505 | 10.0541 | 9.4974 | 120 | 0.55663 | 0 | 10.5 | 9.9434 | 9.9434 | available | 0.86
| Nom. capacity MV, МVА | 10+10 | 2.47 | 2.47 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 6.1674 | 5.304 | 8.6374 | 8.6374 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.13 | 0.86 | 120 | 0.27 | 0 | 10.5 | 10.23 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.28663 | 0.2465 | 1.4166 | 0.86 | 120 | 0.55663 | 0 | 10.5 | 9.9434
97 | Apolye 35/10 | 2,5+2,5 | 0.71 | 0.17 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | 1.9599 | available | 0.94 | 97 | Apolye 35/10 | 2,5+2,5 | 0.063298 | 0.0595 | 0.7733 | 0.17 | 120 | 0.6033 | 0 | 2.625 | 2.0217 | 2.0217 | available | 0.94
98 | Zhukovskaya 35/10 | 4+4 | 2.01 | 0.19 | 120 | 1.82 | 0 | 4.2 | 2.38 | 2.38 | 2.0944 | available | 0.88 | 98 | Zhukovskaya 35/10 | 4+4 | 4.0665 | 3.5785 | 6.0765 | 0.19 | 120 | 5.8865 | 0 | 4.2 | -1.6865 | -1.6865 | unavailable | 0.88
99 | Mazaltsevo 110/35/10 | 10+10 | 6.01 | 5.6 | 120 | 0.41 | 0 | 10.5 | 10.09 | 10.09 | 8.5765 | available | 0.85 | 99 | Mazaltsevo 110/35/10 | 10+10 | 11.03 | 9.3755 | 17.04 | 16.53 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.99 | available | 0.85
| Nom. capacity MV, МVА | 10+10 | 5.34 | 5.34 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 10.93 | 9.2905 | 16.27 | 16.27 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.67 | 0.26 | 120 | 0.41 | 0 | 10.5 | 10.09 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.1 | 0.085 | 0.77 | 0.26 | 120 | 0.51 | 0 | 10.5 | 9.99
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | 1.276 | available | 0.88 | 100 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 0.88
101 | Krasny 110/35/10 | 10+10 | 3.53 | 1.32 | 120 | 2.21 | 0 | 10.5 | 8.29 | 8.29 | 6.8807 | available | 0.83 | 101 | Krasny 110/35/10 | 10+10 | 2.1404 | 1.7765 | 5.6704 | 2.5592 | 120 | 3.1112 | 0 | 10.5 | 7.3888 | 7.3888 | available | 0.83
| Nom. capacity MV, МVА | 10+10 | 0.86 | 0.86 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 1.2392 | 1.0285 | 2.0992 | 2.0992 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.67 | 0.46 | 120 | 2.21 | 0 | 10.5 | 8.29 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.9012 | 0.748 | 3.5712 | 0.46 | 120 | 3.1112 | 0 | 10.5 | 7.3888
102 | Voloelovo 35/10 | 2,5+2,5 | 0.33 | 0.01 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | 2.0284 | available | 0.88 | 102 | Voloelovo 35/10 | 2,5+2,5 | 0.018182 | 0.016 | 0.34818 | 0.01 | 120 | 0.33818 | 0 | 2.625 | 2.2868 | 2.2868 | available | 0.88
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | 2.4885 | available | 0.9 | 103 | Kryukovo 35/10 | 2,5+2,5 | 0.37778 | 0.34 | 0.49778 | 0.26 | 120 | 0.23778 | 0 | 2.625 | 2.3872 | 2.3872 | available | 0.9
104 | Miganovo 35/10 | 2,5+2,5 | 1.51 | 0.49 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | 1.4124 | available | 0.88 | 104 | Miganovo 35/10 | 2,5+2,5 | 1.1494 | 1.0115 | 2.6594 | 0.49 | 120 | 2.1694 | 0 | 2.625 | 0.45557 | 0.45557 | available | 0.88
105 | Velizh 110/35/10 | 10+10 | 5.61 | 1.5 | 120 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | 6.0066 | available | 0.94 | 105 | Velizh 110/35/10 | 10+10 | 3.0383 | 2.856 | 8.6483 | 1.6718 | 120 | 6.9765 | 0 | 10.5 | 3.5235 | 3.5235 | available | 0.94
| Nom. capacity MV, МVА | 10+10 | 0.83 | 0.83 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.17181 | 0.1615 | 1.0018 | 1.0018 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.78 | 0.67 | 120 | 4.11 | 0 | 10.5 | 6.39 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 2.8665 | 2.6945 | 7.6465 | 0.67 | 120 | 6.9765 | 0 | 10.5 | 3.5235
106 | Chepli 35/10 | 2,5+2,5 | 0.37 | 0.09 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | 2.3215 | available | 0.99 | 106 | Chepli 35/10 | 2,5+2,5 | 0.0085859 | 0.0085 | 0.37859 | 0.09 | 120 | 0.28859 | 0 | 2.625 | 2.3364 | 2.3364 | available | 0.99
107 | Demidov 110/35/10 | 10+16 | 5.78 | 1.47 | 120 | 4.31 | 0 | 10.5 | 6.19 | 6.19 | 5.7567 | available | 0.93 | 107 | Demidov 110/35/10 | 10+16 | 1.9559 | 1.819 | 7.7359 | 1.8722 | 120 | 5.8638 | 0 | 10.5 | 4.6362 | 4.6362 | available | 0.93
| Nom. capacity MV, МVА | 10+16 | 1.29 | 1.29 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+16 | 0.40215 | 0.374 | 1.6922 | 1.6922 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.49 | 0.18 | 120 | 4.31 | 0 | 10.5 | 6.19 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 1.5538 | 1.445 | 6.0438 | 0.18 | 120 | 5.8638 | 0 | 10.5 | 4.6362
108 | Staroe selo 35/10 | 2,5+2,5 | 0.4 | 0.17 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | 2.1795 | available | 0.91 | 108 | Staroe selo 35/10 | 2,5+2,5 | 0.12143 | 0.1105 | 0.52143 | 0.17 | 120 | 0.35143 | 0 | 2.625 | 2.2736 | 2.2736 | available | 0.91
109 | Zakrutye 35/10 | 2,5+2,5 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | 1.2005 | available | 0.53 | 109 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 0.53
110 | Zaborye 35/10 | 1,6+2,5 | 0.39 | 0.21 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | 2.1761 | available | 0.89 | 110 | Zaborye 35/10 | 1,6+2,5 | 0.019101 | 0.017 | 0.4091 | 0.21 | 120 | 0.1991 | 0 | 2.625 | 2.4259 | 2.4259 | available | 0.89
111 | Mikhailovskoe 110/35/10 | 10+10 | 2.35 | 1.24 | 120 | 1.11 | 0 | 10.5 | 9.39 | 9.39 | 7.7937 | available | 0.83 | 111 | Mikhailovskoe 110/35/10 | 10+10 | 0.98313 | 0.816 | 3.3331 | 1.8545 | 120 | 1.4787 | 0 | 10.5 | 9.0213 | 9.0213 | available | 0.83
| Nom. capacity MV, МVА | 10+10 | 0.82 | 0.82 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.61446 | 0.51 | 1.4345 | 1.4345 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.53 | 0.42 | 120 | 1.11 | 0 | 10.5 | 9.39 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.36867 | 0.306 | 1.8987 | 0.42 | 120 | 1.4787 | 0 | 10.5 | 9.0213
112 | Kardymovo 110/35/10 | 10+16 | 5.88 | 3.09 | 120 | 2.79 | 0 | 10.5 | 7.71 | 7.71 | 6.939 | available | 0.9 | 112 | Kardymovo 110/35/10 | 10+16 | 11.5506 | 10.3955 | 17.4306 | 6.8678 | 120 | 10.5628 | 0 | 10.5 | -0.062778 | -0.062778 | unavailable | 0.9
| Nom. capacity MV, МVА | 10+16 | 2.47 | 2.47 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+16 | 3.7778 | 3.4 | 6.2478 | 6.2478 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 3.41 | 0.62 | 120 | 2.79 | 0 | 10.5 | 7.71 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 7.7728 | 6.9955 | 11.1828 | 0.62 | 120 | 10.5628 | 0 | 10.5 | -0.062778
113 | Sinkovo 35/6 | 4+2,5 | 1.54 | 0.16 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | 1.2326 | available | 0.99 | 113 | Sinkovo 35/6 | 4+2,5 | 0.051515 | 0.051 | 1.5915 | 0.16 | 120 | 1.4315 | 0 | 2.625 | 1.1935 | 1.1935 | available | 0.99
114 | Kamenka 35/10 | 2,5+2,5 | 1.56 | 0.42 | 120 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | 1.3811 | available | 0.93 | 114 | Kamenka 35/10 | 2,5+2,5 | 1.2522 | 1.1645 | 2.8122 | 0.42 | 120 | 2.3922 | 0 | 2.625 | 0.23285 | 0.23285 | available | 0.93
115 | Solovyevo 35/10 | 4+4 | 0.45 | 0.04 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | 3.7521 | available | 0.99 | 115 | Solovyevo 35/10 | 4+4 | 0.18182 | 0.18 | 0.63182 | 0.04 | 120 | 0.59182 | 0 | 4.2 | 3.6082 | 3.6082 | available | 0.99
116 | Rudnya (FGC) 110/35/10 | 10+16 | 8.56 | 2.37 | 120 | 6.19 | 0 | 10.5 | 4.31 | 4.31 | 4.31 | available | 1 | 116 | Rudnya (FGC) 110/35/10 | 10+16 | 0 |  | 8.56 | 2.37 | 120 | 6.19 | 0 | 10.5 | 4.31 | 4.31 | available | 1
| Nom. capacity MV, МVА | 10+16 | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+16 | 0 |  | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.12 | 0.93 | 120 | 6.19 | 0 | 10.5 | 4.31 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 0 |  | 7.12 | 0.93 | 120 | 6.19 | 0 | 10.5 | 4.31
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.19 | 0.75 | 120 | -0.56 | 0 | 2.625 | 3.185 | 3.185 | 3.1532 | available | 0.99 | 117 | Zhichitsy 35/10 | 2,5+2,5 | 0.042929 | 0.0425 | 0.23293 | 0.75 | 120 | -0.51707 | 0 | 2.625 | 3.1421 | 3.1421 | available | 0.99
118 | Mikulino 35/10 | 6,3+6,3 | 0.98 | 1.1 | 120 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | 5.59 | available | 0.83 | 118 | Mikulino 35/10 | 6,3+6,3 | 0.18434 | 0.153 | 1.1643 | 1.1 | 120 | 0.064337 | 0 | 6.615 | 6.5507 | 6.5507 | available | 0.83
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.62 | 0.74 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | 2.2235 | available | 0.81 | 119 | Lyubavichi 35/10 | 2,5+2,5 | 0.30432 | 0.2465 | 0.92432 | 0.74 | 120 | 0.18432 | 0 | 2.625 | 2.4407 | 2.4407 | available | 0.81
120 | Kazimirovo 35/10 | 4+4 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | 3.4443 | available | 0.89 | 120 | Kazimirovo 35/10 | 4+4 | 0 | 0 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | available | 0.89
121 | Golynki 110/35/6 | 25+25 | 3.35 | 1.81 | 120 | 1.54 | 0 | 26.25 | 24.71 | 24.71 | 20.2622 | available | 0.82 | 121 | Golynki 110/35/6 | 25+25 | 4.872 | 3.995 | 8.222 | 6.5265 | 120 | 1.6955 | 0 | 26.25 | 24.5545 | 24.5545 | available | 0.82
| Nom. Capacity MV, МVА | 25+25 | 1.65 | 1.65 |  | 0 | 0 | 26.25 | 26.25 | [5 empty] | Nom. Capacity MV, МVА | 25+25 | 4.7165 | 3.8675 | 6.3665 | 6.3665 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.7 | 0.16 | 120 | 1.54 | 0 | 26.25 | 24.71 | [5 empty] | Nom. capacity LV, МVА | 25+25 | 0.15549 | 0.1275 | 1.8555 | 0.16 | 120 | 1.6955 | 0 | 26.25 | 24.5545
122 | Belei 35/10 | 2,5+2,5 | 1.78 | 0.75 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | 1.4993 | available | 0.94 | 122 | Belei 35/10 | 2,5+2,5 | 3.9335 | 3.6975 | 5.7135 | 0.75 | 120 | 4.9635 | 0 | 2.625 | -2.3385 | -2.3385 | unavailable | 0.94
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.27 | 2.35 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | 4.8977 | available | 0.86 | 123 | Ponizovye 110/35/10 | 6,3+6,3 | 0.29651 | 0.255 | 3.5665 | 2.6465 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | available | 0.86
| Nom. capacity MV, МVА | 6,3+6,3 | 2.29 | 2.29 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0.29651 | 0.255 | 2.5865 | 2.5865 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | 2.1446 | available | 0.87 | 124 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 0.87
125 | Safonovo 110/6 | 15+20 | 11.46 | 0.06 | 120 | 11.4 | 0 | 15.75 | 4.35 | 4.35 | 4.0455 | available | 0.93 | 125 | Safonovo 110/6 | 15+20 | 3.0968 | 2.88 | 14.5568 | 0.06 | 120 | 14.4968 | 0 | 15.75 | 1.2532 | 1.2532 | available | 0.93
126 | Gornaya 110/35/6 | 25+25 | 16.12 | 15.14 | 120 | 0.98 | 0 | 26.25 | 25.27 | 25.27 | 20.7214 | available | 0.82 | 126 | Gornaya 110/35/6 | 25+25 | 4.7317 | 3.88 | 20.8517 | 19.5668 | 120 | 1.2849 | 0 | 26.25 | 24.9651 | 24.9651 | available | 0.82
| Nom. capacity MV, МVА | 25+25 | 10.47 | 10.47 |  | 0 | 0 | 26.25 | 26.25 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 4.4268 |  | 14.8968 | 14.8968 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 5.65 | 4.67 | 120 | 0.98 | 0 | 26.25 | 25.27 | [5 empty] | Nom. capacity LV, МVА | 25+25 | 0.30488 | 0.25 | 5.9549 | 4.67 | 120 | 1.2849 | 0 | 26.25 | 24.9651
127 | Water intake 35/6 | 6,3+4 | 3.1 | 0.69 | 120 | 2.41 | 0 | 4.2 | 1.79 | 1.79 | 1.6289 | available | 0.91 | 127 | Water intake 35/6 | 6,3+4 | 0.97802 | 0.89 | 4.078 | 0.69 | 120 | 3.388 | 0 | 4.2 | 0.81198 | 0.81198 | available | 0.91
128 | Vadino 35/10 | 4+4 | 1.78 | 0 | 120 | 1.78 | 0 | 4.2 | 2.42 | 2.42 | 2.178 | available | 0.9 | 128 | Vadino 35/10 | 4+4 | 2.0778 | 1.87 | 3.8578 | 0 | 120 | 3.8578 | 0 | 4.2 | 0.34222 | 0.34222 | available | 0.9
129 | ZSSK 35/6 | 4+4 | 1.81 | 0.75 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | 2.5434 | available | 0.81 | 129 | ZSSK 35/6 | 4+4 | 1.0309 | 0.835 | 2.8409 | 0.75 | 120 | 2.0909 | 0 | 4.2 | 2.1091 | 2.1091 | available | 0.81
130 | Yanovo 35/10 | 4+6,3 | 0.5 | 0.05 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | 3.5625 | available | 0.95 | 130 | Yanovo 35/10 | 4+6,3 | 0 | 0 | 0.5 | 0.05 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | available | 0.95
131 | Kapyrevshchina 35/10 | 4+4 | 1.35 | 0.22 | 120 | 1.13 | 0 | 4.2 | 3.07 | 3.07 | 2.7016 | available | 0.88 | 131 | Kapyrevshchina 35/10 | 4+4 | 0.034091 | 0.03 | 1.3841 | 0.22 | 120 | 1.1641 | 0 | 4.2 | 3.0359 | 3.0359 | available | 0.88
132 | Miropolye 35/10 | 2,5+2,5 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | 1.7008 | available | 0.87 | 132 | Miropolye 35/10 | 2,5+2,5 | 0.011494 | 0.01 | 0.68149 | 0 | 120 | 0.68149 | 0 | 2.625 | 1.9435 | 1.9435 | available | 0.87
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 4.8 | 2.63 | 120 | 2.17 | 0 | 5.88 | 3.71 | 3.71 | 2.7825 | available | 0.75 | 133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.8533 | 1.39 | 6.6533 | 3.63 | 120 | 3.0233 | 0 | 5.88 | 2.8567 | 2.8567 | available | 0.75
| Nom. capacity MV, МVА | 5,6+6,3 | 2.2 | 2.2 |  | 0 | 0 | 5.88 | 5.88 | [5 empty] | Nom. capacity MV, МVА | 5,6+6,3 | 1 |  | 3.2 | 3.2 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.6 | 0.43 | 120 | 2.17 | 0 | 5.88 | 3.71 | [5 empty] | Nom. capacity LV, МVА | 5,6+6,3 | 0.85333 | 0.64 | 3.4533 | 0.43 | 120 | 3.0233 | 0 | 5.88 | 2.8567
134 | Alferovo 35/10 | 2,5+2,5 | 0.75 | 0.2 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | 1.5562 | available | 0.75 | 134 | Alferovo 35/10 | 2,5+2,5 | 0.16 | 0.12 | 0.91 | 0.2 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | available | 0.75
135 | Kasulino 35/10 | 2,5+2,5 | 0.33 | 0 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | 1.7901 | available | 0.78 | 135 | Kasulino 35/10 | 2,5+2,5 | 0 | 0 | 0.33 | 0 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 0.78
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.6 | 0.15 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | 1.1931 | available | 0.97 | 136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.59794 | 0.58 | 1.1979 | 0.15 | 120 | 1.0479 | 0 | 1.68 | 0.63206 | 0.63206 | available | 0.97
137 | Glinka 110/35/10 | 10+6,3 | 2.13 | 0.56 | 120 | 1.57 | 0 | 6.615 | 5.045 | 5.045 | 4.5405 | available | 0.9 | 137 | Glinka 110/35/10 | 10+6,3 | 0.43333 | 0.39 | 2.5633 | 0.91556 | 120 | 1.6478 | 0 | 6.615 | 4.9672 | 4.9672 | available | 0.9
| Nom. capacity MV, МVА | 10+6,3 | 0.45 | 0.45 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 10+6,3 | 0.35556 |  | 0.80556 | 0.80556 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.68 | 0.11 | 120 | 1.57 | 0 | 6.615 | 5.045 | [5 empty] | Nom. capacity LV, МVА | 10+6,3 | 0.077778 | 0.07 | 1.7578 | 0.11 | 120 | 1.6478 | 0 | 6.615 | 4.9672
138 | Dobromino 35/10 | 2,5+2,5 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | 2.28 | available | 0.96 | 138 | Dobromino 35/10 | 2,5+2,5 | 0.125 | 0.12 | 0.375 | 0 | 120 | 0.375 | 0 | 2.625 | 2.25 | 2.25 | available | 0.96
139 | Bely kholm 35/10 | 1,6+1,6 | 0.18 | 0 | 120 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | 1.485 | available | 0.99 | 139 | Bely kholm 35/10 | 1,6+1,6 | 0.080808 | 0.08 | 0.26081 | 0 | 120 | 0.26081 | 0 | 1.68 | 1.4192 | 1.4192 | available | 0.99
140 | Dukhovshchina 110/35/10 | 10+10 | 3.65 | 1.99 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | 7.7792 | available | 0.88 | 140 | Dukhovshchina 110/35/10 | 10+10 | 1.9205 | 1.69 | 5.5705 | 2.8991 | 120 | 2.6714 | 0 | 10.5 | 7.8286 | 7.8286 | available | 0.88
| Nom. capacity MV, МVА | 10+10 | 1.73 | 1.73 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.90909 |  | 2.6391 | 2.6391 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.92 | 0.26 | 120 | 1.66 | 0 | 10.5 | 8.84 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 1.0114 | 0.89 | 2.9314 | 0.26 | 120 | 2.6714 | 0 | 10.5 | 7.8286
141 | Zimets 35/10 | 4+4 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | 3.3292 | available | 0.82 | 141 | Zimets 35/10 | 4+4 | 0 | 0 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | available | 0.82
142 | Beresnevo 35/10 | 1,6+1,6 | 0.53 | 0.01 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | 1.0904 | available | 0.94 | 142 | Beresnevo 35/10 | 1,6+1,6 | 0.0010638 | 0.001 | 0.53106 | 0.01 | 120 | 0.52106 | 0 | 1.68 | 1.1589 | 1.1589 | available | 0.94
143 | Prechistoe 110/35/10 | 6,3+6,3 | 2.02 | 0.14 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | 4.1194 | available | 0.87 | 143 | Prechistoe 110/35/10 | 6,3+6,3 | 0.47126 | 0.41 | 2.4913 | 0.14 | 120 | 2.3513 | 0 | 6.615 | 4.2637 | 4.2637 | available | 0.87
| Nom. capacity MV, МVА | 6,3+6,3 | 1.5 | 0 |  | 1.5 | 0 | 6.615 | 5.115 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0.36782 |  | 1.8678 | 0 |  | 1.8678 | 0 | 6.615 | 4.7472
| Nom. capacity LV, МVА | 6,3+6,3 | 0.52 | 0.14 | 120 | 0.38 | 0 | 6.615 | 6.235 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.10345 | 0.09 | 0.62345 | 0.14 | 120 | 0.48345 | 0 | 6.615 | 6.1316
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.24 | 0.07 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | 1.964 | available | 0.8 | 144 | Vorontsovo 35/10 | 2,5+2,5 | 0.03125 | 0.025 | 0.27125 | 0.07 | 120 | 0.20125 | 0 | 2.625 | 2.4238 | 2.4238 | available | 0.8
145 | Ozyorny 35/10 | 6,3+6,3 | 1.58 | 0.01 | 120 | 1.57 | 0 | 6.615 | 5.045 | 5.045 | 4.6918 | available | 0.93 | 145 | Ozyorny 35/10 | 6,3+6,3 | 0.32258 | 0.3 | 1.9026 | 0.01 | 120 | 1.8926 | 0 | 6.615 | 4.7224 | 4.7224 | available | 0.93
146 | Igorevskaya 110/10 | 10+10 | 7.93 | 0 | 120 | 7.93 | 0 | 10.5 | 2.57 | 2.57 | 2.2359 | available | 0.87 | 146 | Igorevskaya 110/10 | 10+10 | 0.22989 | 0.2 | 8.1599 | 0 | 120 | 8.1599 | 0 | 10.5 | 2.3401 | 2.3401 | available | 0.87
147 | Kanyutino 110/35/10 | 5,6+6,3 | 3.4 | 1.68 | 120 | 1.72 | 0 | 5.88 | 4.16 | 4.16 | 3.6608 | available | 0.88 | 147 | Kanyutino 110/35/10 | 5,6+6,3 | 1.5568 | 1.37 | 4.9568 | 4.7568 | 120 | 0.2 | 0 | 5.88 | 5.68 | 5.68 | available | 0.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.99 | 2.99 |  | 0 | 0 | 5.88 | 5.88 | [5 empty] | Nom. capacity LV, МVА | 5,6+6,3 | 1.5568 |  | 4.5468 | 4.5468 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68 | [5 empty] | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.11 | 0.25 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | 1.412 | available | 0.8 | 148 | Bogolyubovo 35/10 | 2,5+2,5 | 0.0625 | 0.05 | 1.1725 | 0.25 | 120 | 0.9225 | 0 | 2.625 | 1.7025 | 1.7025 | available | 0.8
149 | Kholm-Zhirki 35/10 | 2,5+4 | 2.73 | 0.5 | 120 | 2.23 | 0 | 2.625 | 0.395 | 0.395 | 0.35155 | available | 0.89 | 149 | Kholm-Zhirki 35/10 | 2,5+4 | 1.4831 | 1.32 | 4.2131 | 0.5 | 120 | 3.7131 | 0 | 2.625 | -1.0881 | -1.0881 | unavailable | 0.89
150 | Dorogobuzh 1 110/35/10 | 16+16 | 10.38 | 4.87 | 120 | 5.51 | 0 | 16.8 | 11.29 | 11.29 | 9.3707 | available | 0.83 | 150 | Dorogobuzh 1 110/35/10 | 16+16 | 2 | 1.66 | 12.38 | 5.3399 | 120 | 7.0401 | 0 | 16.8 | 9.7599 | 9.7599 | available | 0.83
| Nom. capacity MV, МVА | 16+16 | 4.35 | 4.35 |  | 0 | 0 | 16.8 | 16.8 | [5 empty] | Nom. capacity MV, МVА | 16+16 | 0.46988 |  | 4.8199 | 4.8199 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 6.03 | 0.52 | 120 | 5.51 | 0 | 16.8 | 11.29 | [5 empty] | Nom. capacity LV, МVА | 16+16 | 1.5301 | 1.27 | 7.5601 | 0.52 | 120 | 7.0401 | 0 | 16.8 | 9.7599
151 | Kaskovo 35/10 | 1,6+4 | 0.84 | 0.09 | 120 | 0.75 | 0 | 1.68 | 0.93 | 0.93 | 0.8184 | available | 0.88 | 151 | Kaskovo 35/10 | 1,6+4 | 0.18182 | 0.16 | 1.0218 | 0.09 | 120 | 0.93182 | 0 | 1.68 | 0.74818 | 0.74818 | available | 0.88
152 | Usvyatye 35/10 | 2,5+4 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | 1.4313 | available | 0.78 | 152 | Usvyatye 35/10 | 2,5+4 | 0.038462 | 0.03 | 0.82846 | 0 | 120 | 0.82846 | 0 | 2.625 | 1.7965 | 1.7965 | available | 0.78
153 | Ushakovo 35/10 | 1,6+2,5 | 0.84 | 0 | 120 | 0.84 | 0 | 1.68 | 0.84 | 0.84 | 0.7896 | available | 0.94 | 153 | Ushakovo 35/10 | 1,6+2,5 | 0.021277 | 0.02 | 0.86128 | 0 | 120 | 0.86128 | 0 | 1.68 | 0.81872 | 0.81872 | available | 0.94
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | 4.2 | available | 1 | 154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | available | 1
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | 6.1322 | available | 0.95 | 155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | available | 0.95
156 | Elnya 110/35/10 | 16+16 | 5.88 | 2.12 | 120 | 3.76 | 0 | 16.8 | 13.04 | 13.04 | 12.1272 | available | 0.93 | 156 | Elnya 110/35/10 | 16+16 | 0.95699 | 0.89 | 6.837 | 2.7867 | 120 | 4.0503 | 0 | 16.8 | 12.7497 | 12.7497 | available | 0.93
| Nom. capacity MV, МVА | 16+16 | 1.58 | 1.58 |  | 0 | 0 | 16.8 | 16.8 | [5 empty] | Nom. capacity MV, МVА | 16+16 | 0.66667 |  | 2.2467 | 2.2467 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.3 | 0.54 | 10 | 3.76 | 0 | 16.8 | 13.04 | [5 empty] | Nom. capacity LV, МVА | 16+16 | 0.29032 | 0.27 | 4.5903 | 0.54 | 120 | 4.0503 | 0 | 16.8 | 12.7497
157 | Pavlovo 35/10 | 2,5+2,5 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | 2.1404 | available | 0.89 | 157 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available | 0.89
158 | Sharapovo 35/10 | 4+4 | 0.48 | 1 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | 3.5872 | available | 0.76 | 158 | Sharapovo 35/10 | 4+4 | 0.0039474 | 0.003 | 0.48395 | 1 | 120 | -0.51605 | 0 | 4.2 | 4.7161 | 4.7161 | available | 0.76
159 | Korobets 35/10 | 2,5+2,5 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | 1.6979 | available | 0.99 | 159 | Korobets 35/10 | 2,5+2,5 | 0 | 0 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | available | 0.99
160 | Baltutino 35/10 | 2,5+2,5 | 0.54 | 0 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | 1.5846 | available | 0.76 | 160 | Baltutino 35/10 | 2,5+2,5 | 0.14474 | 0.11 | 0.68474 | 0 | 120 | 0.68474 | 0 | 2.625 | 1.9403 | 1.9403 | available | 0.76
161 | Lapino 110/35/10 | 5,6+5,6 | 1.13 | 0.72 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | 5.3606 | available | 0.98 | 161 | Lapino 110/35/10 | 5,6+5,6 | 0.016327 | 0.016 | 1.1463 | 0.72612 | 120 | 0.4202 | 0 | 5.88 | 5.4598 | 5.4598 | available | 0.98
| Nom. capacity MV, МVА | 5,6+5,6 | 0.72 | 0.72 |  | 0 | 0 | 5.88 | 5.88 | [5 empty] | Nom. capacity MV, МVА | 5,6+5,6 | 0.0061224 |  | 0.72612 | 0.72612 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47 | [5 empty] | Nom. capacity LV, МVА | 5,6+5,6 | 0.010204 | 0.01 | 0.4202 | 0 | 120 | 0.4202 | 0 | 5.88 | 5.4598
162 | Mutishche 35/10 | 1,6+2,5 | 0.22 | 0.08 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | 1.3706 | available | 0.89 | 162 | Mutishche 35/10 | 1,6+2,5 | 0 | 0 | 0.22 | 0.08 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | available | 0.89
163 | Suetovo 110/35/10 | 6,3+6,3 | 3.12 | 2.33 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | 4.8347 | available | 0.83 | 163 | Suetovo 110/35/10 | 6,3+6,3 | 1.4819 | 1.23 | 4.6019 | 3.7035 | 120 | 0.89843 | 0 | 6.615 | 5.7166 | 5.7166 | available | 0.83
| Nom. capacity MV, МVА | 6,3+6,3 | 1.75 | 1.75 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 1.3735 |  | 3.1235 | 3.1235 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.37 | 0.58 | 120 | 0.79 | 0 | 6.615 | 5.825 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.10843 | 0.09 | 1.4784 | 0.58 | 120 | 0.89843 | 0 | 6.615 | 5.7166
164 | Pushkino 35/10 | 2,5+2,5 | 0.97 | 0.04 | 120 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | 1.6272 | available | 0.96 | 164 | Pushkino 35/10 | 2,5+2,5 | 1.0833 | 1.04 | 2.0533 | 0.04 | 120 | 2.0133 | 0 | 2.625 | 0.61167 | 0.61167 | available | 0.96
165 | Yartsevo 1 110/10 | 40+40 | 17.99 | 5.34 | 120 | 12.65 | 0 | 42 | 29.35 | 29.35 | 27.2955 | available | 0.93 | 165 | Yartsevo 1 110/10 | 40+40 | 2.3441 | 2.18 | 20.3341 | 5.34 | 120 | 14.9941 | 0 | 42 | 27.0059 | 27.0059 | available | 0.93
166 | Yartsevo 2 110/10 | 16+16 | 12.7 | 0.75 | 120 | 11.95 | 0 | 16.8 | 4.85 | 4.85 | 4.3165 | available | 0.89 | 166 | Yartsevo 2 110/10 | 16+16 | 10.2697 | 9.14 | 22.9697 | 0.75 | 120 | 22.2197 | 0 | 16.8 | -5.4197 | -5.4197 | unavailable | 0.89
167 | Saprykino 110/35/10 | 6,3+6,3 | 1.72 | 0.87 | 120 | 0.85 | 0 | 6.615 | 5.765 | 5.765 | 4.7273 | available | 0.82 | 167 | Saprykino 110/35/10 | 6,3+6,3 | 0.26829 | 0.22 | 1.9883 | 0.87 | 120 | 1.1183 | 0 | 6.615 | 5.4967 | 5.4967 | available | 0.82
| Nom. capacity MV, МVА | 6,3+6,3 | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0 |  | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.25 | 0.4 | 120 | 0.85 | 0 | 6.615 | 5.765 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.26829 | 0.22 | 1.5183 | 0.4 | 120 | 1.1183 | 0 | 6.615 | 5.4967
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.87 | 0 | 120 | 2.87 | 0 | 6.615 | 3.745 | 3.745 | 3.3331 | available | 0.89 | 168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.80899 | 0.72 | 3.679 | 0 | 120 | 3.679 | 0 | 6.615 | 2.936 | 2.936 | available | 0.89
169 | Egoryevo 35/10 | 6,3+6,3 | 5.39 | 0 | 120 | 5.39 | 0 | 6.615 | 1.225 | 1.225 | 1.1515 | available | 0.94 | 169 | Egoryevo 35/10 | 6,3+6,3 | 0.40426 | 0.38 | 5.7943 | 0 | 120 | 5.7943 | 0 | 6.615 | 0.82074 | 0.82074 | available | 0.94
170 | Shalomino 35/10 | 1,6+2,5 | 0.65 | 0.13 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | 1.0672 | available | 0.92 | 170 | Shalomino 35/10 | 1,6+2,5 | 0.23913 | 0.22 | 0.88913 | 0.13 | 120 | 0.75913 | 0 | 1.68 | 0.92087 | 0.92087 | available | 0.92
171 | Roslavl 110/35/6 | 25+40 | 24.09 | 1.4 | 120 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | 3.1684 | available | 0.89 | 171 | Roslavl 110/35/6 | 25+40 | 4.1348 | 3.68 | 28.2248 | 4.0697 | 120 | 24.1551 | 0 | 26.25 | 2.0949 | 2.0949 | available | 0.89
| Nom. capacity MV, МVА | 25+40 | 11.48 | 1.4 |  | 10.08 | 0 | 26.25 | 16.17 | [5 empty] | Nom. capacity MV, МVА | 25+40 | 1.809 |  | 13.289 | 4.0697 |  | 9.2192 | 0 | 26.25 | 17.0308
| Nom. сapacity LV, МVА | 25+40 | 12.61 | 0 | 120 | 12.61 | 0 | 26.25 | 13.64 | [5 empty] | Nom. сapacity LV, МVА | 25+40 | 2.3258 | 2.07 | 14.9358 | 0 | 120 | 14.9358 | 0 | 26.25 | 11.3142
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.98 | 0 | 120 | 1.98 | 0 | 6.615 | 4.635 | 4.635 | 4.0324 | available | 0.87 | 172 | Meet processing plant 35/6 | 6,3+6,3 | 0.091954 | 0.08 | 2.072 | 0 | 120 | 2.072 | 0 | 6.615 | 4.543 | 4.543 | available | 0.87
173 | Perenka 35/10 | 4+4 | 0.59 | 0 | 120 | 0.59 | 0 | 4.2 | 3.61 | 3.61 | 3.4295 | available | 0.95 | 173 | Perenka 35/10 | 4+4 | 0.010526 | 0.01 | 0.60053 | 0 | 120 | 0.60053 | 0 | 4.2 | 3.5995 | 3.5995 | available | 0.95
174 | Khoroshevo 35/10 | 2,5+4 | 1.22 | 0 | 120 | 1.22 | 0 | 2.625 | 1.405 | 1.405 | 1.2645 | available | 0.9 | 174 | Khoroshevo 35/10 | 2,5+4 | 0.70556 | 0.635 | 1.9256 | 0 | 120 | 1.9256 | 0 | 2.625 | 0.69944 | 0.69944 | available | 0.9
175 | Lipovka 35/10 | 2,5+2,5 | 0.57 | 0 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | 1.2125 | available | 0.59 | 175 | Lipovka 35/10 | 2,5+2,5 | 0 | 0 | 0.57 | 0 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | available | 0.59
176 | Kirilly 35/10 | 2,5+2,5 | 0.83 | 0 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 1.5437 | available | 0.86 | 176 | Kirilly 35/10 | 2,5+2,5 | 0.74419 | 0.64 | 1.5742 | 0 | 120 | 1.5742 | 0 | 2.625 | 1.0508 | 1.0508 | available | 0.86
177 | Desnogorsk 110/35/10 | 25+25 | 19.62 | 6.34 | 120 | 13.28 | 0 | 26.25 | 12.97 | 12.97 | 11.673 | available | 0.9 | 177 | Desnogorsk 110/35/10 | 25+25 | 1.2444 | 1.12 | 20.8644 | 3.16 | 120 | 17.7044 | 0 | 26.25 | 8.5456 | 8.5456 | available | 0.9
| Nom. capacity MV, МVА | 25+25 | 6.34 | 6.34 |  | 0 | 0 | 26.25 | 26.25 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 1.2411 |  | 7.5811 | 3.16 |  | 4.4211 | 0 | 26.25 | 21.8289
| Nom. capacidty LV, МVА | 25+25 | 13.28 | 0 | 120 | 13.28 | 0 | 26.25 | 12.97 | [5 empty] | Nom. capacidty LV, МVА | 25+25 | 0.0033333 | 0.003 | 13.2833 | 0 | 120 | 13.2833 | 0 | 26.25 | 12.9667
178 | Ekimovichi 35/10 | 4+4 | 2.3 | 0.24 | 120 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | 2.0544 | available | 0.96 | 178 | Ekimovichi 35/10 | 4+4 | 0.39583 | 0.38 | 2.6958 | 0.24 | 120 | 2.4558 | 0 | 4.2 | 1.7442 | 1.7442 | available | 0.96
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.27 | 0.07 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | 2.1582 | available | 0.89 | 179 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0 | 0.27 | 0.07 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 0.89
180 | Kokhany 35/10 | 1,6+1,6 | 0.38 | 0.09 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | 1.3483 | available | 0.97 | 180 | Kokhany 35/10 | 1,6+1,6 | 0.0061856 | 0.006 | 0.38619 | 0.09 | 120 | 0.29619 | 0 | 1.68 | 1.3838 | 1.3838 | available | 0.97
181 | Koski 35/10 | 4+4 | 0.39 | 0 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | 3.5052 | available | 0.92 | 181 | Koski 35/10 | 4+4 | 0.01087 | 0.01 | 0.40087 | 0 | 120 | 0.40087 | 0 | 4.2 | 3.7991 | 3.7991 | available | 0.92
182 | Industrialnaya 110/35/6 | 16+16 | 4.62 | 1.33 | 120 | 3.29 | 0 | 16.8 | 13.51 | 5.565 | 4.9528 | available | 0.89 | 182 | Industrialnaya 110/35/6 | 16+16 | 1.9438 | 1.73 | 6.5638 | 1.4536 | 120 | 5.1102 | 0 | 16.8 | 11.6898 | 5.565 | available | 0.89
| Nom. capacity MV, МVА | 16,3+5,3 | 1.33 | 1.33 |  | 0 | 0 | 5.565 | 5.565 | [5 empty] | Nom. capacity MV, МVА | 16,3+5,3 | 0.1236 |  | 1.4536 | 1.4536 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 3.29 | 0 | 120 | 3.29 | 0 | 11.235 | 7.945 | [5 empty] | Nom. capacity LV, МVА | 16+10,7 | 1.8202 | 1.62 | 5.1102 | 0 | 120 | 5.1102 | 0 | 11.235 | 6.1248
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.83 | 0 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 1.5437 | available | 0.86 | 183 | Astapkovichi 35/10 | 2,5+2,5 | 0.069767 | 0.06 | 0.89977 | 0 | 120 | 0.89977 | 0 | 2.625 | 1.7252 | 1.7252 | available | 0.86
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.14 | 0.86 | 120 | 0.28 | 0 | 6.615 | 6.335 | 6.335 | 5.6382 | available | 0.89 | 184 | Barsuki 110/35/10 | 6,3+6,3 | 0.08427 | 0.075 | 1.2243 | 0.94427 | 120 | 0.28 | 0 | 6.615 | 6.335 | 6.335 | available | 0.89
| Nom. capacity MV, МVА | 6,3+6,3 | 0.86 | 0.86 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0.08427 |  | 0.94427 | 0.94427 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335
185 | Bogdanovo 35/10 | 4+4 | 0.44 | 0 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | 3.384 | available | 0.9 | 185 | Bogdanovo 35/10 | 4+4 | 0.077778 | 0.07 | 0.51778 | 0 | 120 | 0.51778 | 0 | 4.2 | 3.6822 | 3.6822 | available | 0.9
186 | Prigorye 110/35/10 | 10+2,5 | 0.99 | 0.42 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | 1.7468 | available | 0.85 | 186 | Prigorye 110/35/10 | 10+2,5 | 0 | 0 | 0.99 | 0.42 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | available | 0.85
| Nom. capacity MV, МVА | 10+2,5 | 0.42 | 0.42 |  | 0 | 0 | 2.625 | 2.625 | [5 empty] | Nom. capacity MV, МVА | 10+2,5 | 0 |  | 0.42 | 0.42 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.57 | 0 | 120 | 0.57 | 0 | 2.625 | 2.055 | [5 empty] | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0 | 0.57 | 0 | 120 | 0.57 | 0 | 2.625 | 2.055
187 | Bekhovo 35/10 | 2,5+2,5 | 0.34 | 0 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | 1.8965 | available | 0.83 | 187 | Bekhovo 35/10 | 2,5+2,5 | 0 | 0 | 0.34 | 0 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available | 0.83
188 | Pochinok 110/35/10 | 10+16 | 9.02 | 3.12 | 120 | 5.9 | 0 | 10.5 | 4.6 | 4.6 | 4.094 | available | 0.89 | 188 | Pochinok 110/35/10 | 10+16 | 3.7865 | 3.37 | 12.8065 | 3.7942 | 120 | 9.0124 | 0 | 10.5 | 1.4876 | 1.4876 | available | 0.89
| Nom. capacidty MV, МVА | 10+16 | 3.04 | 3.04 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacidty MV, МVА | 10+16 | 0.67416 |  | 3.7142 | 3.7142 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.98 | 0.08 | 120 | 5.9 | 0 | 10.5 | 4.6 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 3.1124 | 2.77 | 9.0924 | 0.08 | 120 | 9.0124 | 0 | 10.5 | 1.4876
189 | Divinskaya 35/10 | 4+4 | 1.19 | 0.17 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | 2.5122 | available | 0.79 | 189 | Divinskaya 35/10 | 4+4 | 0.17722 | 0.14 | 1.3672 | 0.17 | 120 | 1.1972 | 0 | 4.2 | 3.0028 | 3.0028 | available | 0.79
190 | Shatalovo 35/10 | 2,5+2,5 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | 1.1327 | available | 0.94 | 190 | Shatalovo 35/10 | 2,5+2,5 | 0 | 0 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | available | 0.94
191 | Panskaya 35/10 | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | 4.1514 | available | 0.79 | 191 | Panskaya 35/10 | 6,3+6,3 | 0.57722 | 0.456 | 1.9372 | 0 | 120 | 1.9372 | 0 | 6.615 | 4.6778 | 4.6778 | available | 0.79
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.41 | 1.82 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | 4.1707 | available | 0.83 | 192 | Stodolishche 110/35/10 | 6,3+6,3 | 2.8193 | 2.34 | 6.2293 | 2.0248 | 120 | 4.2045 | 0 | 6.615 | 2.4105 | 2.4105 | available | 0.83
| Nom. capacity MV, МVА | 6,3+6,3 | 1.37 | 1.37 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0.20482 |  | 1.5748 | 1.5748 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.04 | 0.45 | 120 | 1.59 | 0 | 6.615 | 5.025 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 2.6145 | 2.17 | 4.6545 | 0.45 | 120 | 4.2045 | 0 | 6.615 | 2.4105
193 | Belik 35/10 | 2,5+2,5 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | 2.0404 | available | 0.73 | 193 | Belik 35/10 | 2,5+2,5 | 0 | 0 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | available | 0.73
194 | Pervomayskaya 35/10 | 4+4 | 1.52 | 0 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | 2.0904 | available | 0.78 | 194 | Pervomayskaya 35/10 | 4+4 | 0.12821 | 0.1 | 1.6482 | 0 | 120 | 1.6482 | 0 | 4.2 | 2.5518 | 2.5518 | available | 0.78
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.85 | 2.07 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.355 | 5.3382 | available | 0.84 | 195 | Vaskovo 110/35/10 | 6,3+6,3 | 2.4167 | 2.03 | 4.2667 | 3.9948 | 120 | 0.2719 | 0 | 6.615 | 6.3431 | 6.3431 | available | 0.84
| Nom. capacity MV, МVА | 6,3+6,3 | 1.38 | 1.38 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 2.4048 |  | 3.7848 | 3.7848 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.47 | 0.21 | 120 | 0.26 | 0 | 6.615 | 6.355 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.011905 | 0.01 | 0.4819 | 0.21 | 120 | 0.2719 | 0 | 6.615 | 6.3431
196 | Strigino 35/10 | 2,5+2,5 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | 1.8596 | available | 0.77 | 196 | Strigino 35/10 | 2,5+2,5 | 1.5909 | 1.225 | 1.8009 | 0 | 120 | 1.8009 | 0 | 2.625 | 0.82409 | 0.82409 | available | 0.77
197 | Komintern 35/10 | 2,5+2,5 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | 1.2905 | available | 0.58 | 197 | Komintern 35/10 | 2,5+2,5 | 0 | 0 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 0.58
198 | Monastyrshchina 110/35/10 | 10+10 | 6.21 | 1.77 | 120 | 4.44 | 0 | 10.5 | 6.06 | 6.06 | 5.2116 | available | 0.86 | 198 | Monastyrshchina 110/35/10 | 10+10 | 0.26744 | 0.23 | 6.4774 | 1.9212 | 120 | 4.5563 | 0 | 10.5 | 5.9437 | 5.9437 | available | 0.86
| Nom. capacity MV, МVА | 10+10 | 1.77 | 1.77 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.15116 |  | 1.9212 | 1.9212 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.44 | 0 | 120 | 4.44 | 0 | 10.5 | 6.06 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.11628 | 0.1 | 4.5563 | 0 | 120 | 4.5563 | 0 | 10.5 | 5.9437
199 | N.Mikhailov 35/10 | 4+4 | 0.57 | 0 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | 3.3396 | available | 0.92 | 199 | N.Mikhailov 35/10 | 4+4 | 0.016304 | 0.015 | 0.5863 | 0 | 120 | 0.5863 | 0 | 4.2 | 3.6137 | 3.6137 | available | 0.92
200 | Tatarsk 35/10 | 3,2+4 | 0.94 | 0 | 120 | 0.94 | 0 | 3.36 | 2.42 | 2.42 | 1.694 | available | 0.7 | 200 | Tatarsk 35/10 | 3,2+4 | 0.092857 | 0.065 | 1.0329 | 0 | 120 | 1.0329 | 0 | 3.36 | 2.3271 | 2.3271 | available | 0.7
201 | Turki 35/10 | 1,6+1,6 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | 0.7701 | available | 0.51 | 201 | Turki 35/10 | 1,6+1,6 | 0 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | available | 0.51
202 | Sozh 35/10 | 4+4 | 0.47 | 0 | 120 | 0.47 | 0 | 4.2 | 3.73 | 3.73 | 2.8348 | available | 0.76 | 202 | Sozh 35/10 | 4+4 | 0.013158 | 0.01 | 0.48316 | 0 | 120 | 0.48316 | 0 | 4.2 | 3.7168 | 3.7168 | available | 0.76
203 | Khislavichi 110/35/10 | 16+16 | 3.95 | 1.62 | 120 | 2.33 | 0 | 16.8 | 14.47 | 14.47 | 12.2995 | available | 0.85 | 203 | Khislavichi 110/35/10 | 16+16 | 0.91765 | 0.78 | 4.8676 | 1.9906 | 120 | 2.8771 | 0 | 16.8 | 13.9229 | 13.9229 | available | 0.85
| Nom. capacity MV, МVА | 16+16 | 1.44 | 1.44 |  | 0 | 0 | 16.8 | 16.8 | [5 empty] | Nom. capacity MV, МVА | 16+16 | 0.37059 |  | 1.8106 | 1.8106 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.51 | 0.18 | 120 | 2.33 | 0 | 16.8 | 14.47 | [5 empty] | Nom. capacity LV, МVА | 16+16 | 0.54706 | 0.465 | 3.0571 | 0.18 | 120 | 2.8771 | 0 | 16.8 | 13.9229
204 | Gorodishche 35/10 | 1,8+2,5 | 0.8 | 0 | 120 | 0.8 | 0 | 1.89 | 1.09 | 1.09 | 0.9919 | available | 0.91 | 204 | Gorodishche 35/10 | 1,8+2,5 | 0.065934 | 0.06 | 0.86593 | 0 | 120 | 0.86593 | 0 | 1.89 | 1.0241 | 1.0241 | available | 0.91
205 | Komarovka 35/10 | 4+4 | 0.34 | 0.02 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | 2.4056 | available | 0.62 | 205 | Komarovka 35/10 | 4+4 | 0.1129 | 0.07 | 0.4529 | 0.02 | 120 | 0.4329 | 0 | 4.2 | 3.7671 | 3.7671 | available | 0.62
206 | Cherepovo 35/10 | 2,5+2,5 | 0.33 | 0 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | 1.9737 | available | 0.86 | 206 | Cherepovo 35/10 | 2,5+2,5 | 0.046512 | 0.04 | 0.37651 | 0 | 120 | 0.37651 | 0 | 2.625 | 2.2485 | 2.2485 | available | 0.86
207 | Studenets 35/10 | 1,6+2,5 | 0.29 | 0.01 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | 1.302 | available | 0.93 | 207 | Studenets 35/10 | 1,6+2,5 | 0.13441 | 0.125 | 0.42441 | 0.01 | 120 | 0.41441 | 0 | 1.68 | 1.2656 | 1.2656 | available | 0.93
208 | Shumyachi 110/35/10 | 10+10 | 4.78 | 2.84 | 120 | 1.94 | 0 | 10.5 | 8.56 | 8.56 | 7.8752 | available | 0.92 | 208 | Shumyachi 110/35/10 | 10+10 | 2.0109 | 1.85 | 6.7909 | 3.8509 | 120 | 2.94 | 0 | 10.5 | 7.56 | 7.56 | available | 0.92
| Nom. capacity MV, МVА | 10+10 | 2.2 | 2.2 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 1.0109 |  | 3.2109 | 3.2109 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.58 | 0.64 | 120 | 1.94 | 0 | 10.5 | 8.56 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 1 | 0.92 | 3.58 | 0.64 | 120 | 2.94 | 0 | 10.5 | 7.56
209 | Ershichi 110/35/10 | 10+10 | 2.26 | 0.42 | 120 | 1.84 | 0 | 10.5 | 8.66 | 8.66 | 7.6208 | available | 0.88 | 209 | Ershichi 110/35/10 | 10+10 | 0.70455 | 0.62 | 2.9645 | 0.42 | 120 | 2.5445 | 0 | 10.5 | 7.9555 | 7.9555 | available | 0.88
| Nom. capacity MV, МVА | 10+10 | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0 |  | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.06 | 0.22 | 120 | 1.84 | 0 | 10.5 | 8.66 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.70455 | 0.62 | 2.7645 | 0.22 | 120 | 2.5445 | 0 | 10.5 | 7.9555
210 | Rukhan 35/10 | 2,5+2,5 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | 1.8289 | available | 0.79 | 210 | Rukhan 35/10 | 2,5+2,5 | 0 | 0 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available | 0.79
211 | Vyazma 1 110/35/10 | 40+40 | 41.71 | 2.665 | 120 | 39.045 | 0 | 42 | 2.955 | 2.955 | 2.689 | available | 0.91 | 211 | Vyazma 1 110/35/10 | 40+40 | 21.0912 | 19.193 | 62.8012 | 5.8082 | 120 | 56.993 | 0 | 42 | -14.993 | -14.993 | unavailable | 0.91
| Nom. capacity MV, МVА | 40+40 | 26.3 | 2.105 | 121 | 24.195 | 0 | 42 | 17.805 | [5 empty] | Nom. capacity MV, МVА | 40+40 | 11.1995 | 10.1915 | 37.4995 | 5.2482 |  | 32.2513 | 0 | 42 | 9.7487
| Nom. capacity LV, МVА | 40+40 | 15.41 | 0.56 | 122 | 14.85 | 0 | 42 | 27.15 | [5 empty] | Nom. capacity LV, МVА | 40+40 | 9.8918 | 9.0015 | 25.3018 | 0.56 | 120 | 24.7418 | 0 | 42 | 17.2582
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.38 | 0 | 120 | 2.38 | 0 | 6.615 | 4.235 | 4.235 | 3.9386 | available | 0.93 | 212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 0.85914 | 0.799 | 3.2391 | 0 | 120 | 3.2391 | 0 | 6.615 | 3.3759 | 3.3759 | available | 0.93
213 | Khmelita 35/10 | 1,6+2,5 | 0.43 | 0.11 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | 1.2376 | available | 0.91 | 213 | Khmelita 35/10 | 1,6+2,5 | 0.32692 | 0.2975 | 0.75692 | 0.11 | 120 | 0.64692 | 0 | 1.68 | 1.0331 | 1.0331 | available | 0.91
214 | Isakovo 35/10 | 2,5+4 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | 2.1808 | available | 0.93 | 214 | Isakovo 35/10 | 2,5+4 | 0.0091398 | 0.0085 | 0.58914 | 0.3 | 120 | 0.28914 | 0 | 2.625 | 2.3359 | 2.3359 | available | 0.93
215 | Rizskoe 35/10 | 2,5+2,5 | 0.73 | 0.01 | 120 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | 1.6954 | available | 0.89 | 215 | Rizskoe 35/10 | 2,5+2,5 | 0.19101 | 0.17 | 0.92101 | 0.01 | 120 | 0.91101 | 0 | 2.625 | 1.714 | 1.714 | available | 0.89
216 | Beryozka 35/10 | 4+4 | 0.97 | 0 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | 2.7132 | available | 0.84 | 216 | Beryozka 35/10 | 4+4 | 0.69821 | 0.5865 | 1.6682 | 0 | 120 | 1.6682 | 0 | 4.2 | 2.5318 | 2.5318 | available | 0.84
217 | Shimanovo 35/10 | 1,8+4 | 0.47 | 0.32 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | 1.2354 | available | 0.71 | 217 | Shimanovo 35/10 | 1,8+4 | 0.11972 | 0.085 | 0.58972 | 0.32 | 120 | 0.26972 | 0 | 1.89 | 1.6203 | 1.6203 | available | 0.71
218 | Kaydakovo 35/10 | 4+4 | 1.29 | 0.2 | 120 | 1.09 | 0 | 4.2 | 3.11 | 3.11 | 2.6124 | available | 0.84 | 218 | Kaydakovo 35/10 | 4+4 | 0.35417 | 0.2975 | 1.6442 | 0.2 | 120 | 1.4442 | 0 | 4.2 | 2.7558 | 2.7558 | available | 0.84
219 | Flour mill 35/10 | 10+10 | 7.89 | 0.13 | 120 | 7.76 | 0 | 10.5 | 2.74 | 2.74 | 2.4386 | available | 0.89 | 219 | Flour mill 35/10 | 10+10 | 8.8152 | 7.8455 | 16.7052 | 0.13 | 120 | 16.5752 | 0 | 10.5 | -6.0752 | -6.0752 | unavailable | 0.89
220 | Kikino 35/10 | 2,5+2,5 | 0.56 | 0.41 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | 2.2523 | available | 0.91 | 220 | Kikino 35/10 | 2,5+2,5 | 0.12143 | 0.1105 | 0.68143 | 0.41 | 120 | 0.27143 | 0 | 2.625 | 2.3536 | 2.3536 | available | 0.91
221 | Vyazma 2 110/10 | 16+16 | 15.6 | 0 | 120 | 15.6 | 0 | 16.8 | 1.2 | 1.2 | 1.128 | available | 0.94 | 221 | Vyazma 2 110/10 | 16+16 | 6.2303 | 5.8565 | 21.8303 | 0 | 120 | 21.8303 | 0 | 16.8 | -5.0303 | -5.0303 | unavailable | 0.94
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.19 | 1.22 | 120 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | 5.4756 | available | 0.97 | 222 | Tumanovo 110/35/10 | 6,3+6,3 | 0.26289 | 0.255 | 2.4529 | 1.3602 | 120 | 1.0927 | 0 | 6.615 | 5.5223 | 5.5223 | available | 0.97
| Nom. capacity MV, МVА | 6,3+6,3 | 0.88 | 0.88 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0.14021 | 0.136 | 1.0202 | 1.0202 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.31 | 0.34 | 120 | 0.97 | 0 | 6.615 | 5.645 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.12268 | 0.119 | 1.4327 | 0.34 | 120 | 1.0927 | 0 | 6.615 | 5.5223
223 | Rossiya 110/35/10 | 10+16 | 2.38 | 1.82 | 120 | 0.56 | 0 | 10.5 | 9.94 | 9.94 | 8.6478 | available | 0.87 | 223 | Rossiya 110/35/10 | 10+16 | 1.6121 | 1.4025 | 3.9921 | 3.4125 | 120 | 0.57954 | 0 | 10.5 | 9.9205 | 9.9205 | available | 0.87
| Nom. capacity MV, МVА | 10+16 | 1.5 | 1.5 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+16 | 1.5925 | 1.3855 | 3.0925 | 3.0925 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 0.88 | 0.32 | 120 | 0.56 | 0 | 10.5 | 9.94 | [5 empty] | Nom. capacity LV, МVА | 10+16 | 0.01954 | 0.017 | 0.89954 | 0.32 | 120 | 0.57954 | 0 | 10.5 | 9.9205
224 | Semlevo 35/10 | 2,5+4 | 0.87 | 0 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | 1.6497 | available | 0.94 | 224 | Semlevo 35/10 | 2,5+4 | 0.64202 | 0.6035 | 1.512 | 0 | 120 | 1.512 | 0 | 2.625 | 1.113 | 1.113 | available | 0.94
225 | Artyomovo 35/10 | 2,5+2,5 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | 2.1949 | available | 0.94 | 225 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available | 0.94
226 | Gagarin 110/35/10 | 25+25 | 23.41 | 4.78 | 120 | 18.63 | 0 | 26.25 | 7.62 | 7.62 | 6.9342 | available | 0.91 | 226 | Gagarin 110/35/10 | 25+25 | 13.628 | 12.4015 | 37.038 | 6.82 | 120 | 30.218 | 0 | 26.25 | -3.968 | -3.968 | unavailable | 0.91
| Nom. capacity MV, МVА | 25+25 | 8.21 | 3.06 |  | 5.15 | 0 | 26.25 | 21.1 | [5 empty] | Nom. capacity MV, МVА | 25+25 | 5.4923 | 4.998 | 13.7023 | 5.1 |  | 8.6023 | 0 | 26.25 | 17.6477
| Nom. capacity LV, МVА | 25+25 | 15.2 | 1.72 | 120 | 13.48 | 0 | 26.25 | 12.77 | [5 empty] | Nom. capacity LV, МVА | 25+25 | 8.1357 | 7.4035 | 23.3357 | 1.72 | 120 | 21.6157 | 0 | 26.25 | 4.6343
227 | Rodomanovo 35/10 | 4+4 | 0.91 | 1.18 | 120 | -0.27 | 0 | 4.2 | 4.47 | 4.47 | 3.1737 | available | 0.71 | 227 | Rodomanovo 35/10 | 4+4 | 2.8852 | 2.0485 | 3.7952 | 1.18 | 120 | 2.6152 | 0 | 4.2 | 1.5848 | 1.5848 | available | 0.71
228 | Klushino 35/10 | 4+4 | 0.78 | 0.57 | 120 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | 3.5511 | available | 0.89 | 228 | Klushino 35/10 | 4+4 | 0.43933 | 0.391 | 1.2193 | 0.57 | 120 | 0.64933 | 0 | 4.2 | 3.5507 | 3.5507 | available | 0.89
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | 1.3578 | available | 0.93 | 229 | Ivino 35/10 | 1,6+1,6 | 0 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 0.93
230 | Karmanovo 35/10 | 4+4 | 3.56 | 0.21 | 120 | 3.35 | 0 | 4.2 | 0.85 | 0.85 | 0.799 | available | 0.94 | 230 | Karmanovo 35/10 | 4+4 | 1.284 | 1.207 | 4.844 | 0.21 | 120 | 4.634 | 0 | 4.2 | -0.43404 | -0.43404 | unavailable | 0.94
231 | Sverchkovo 35/10 | 2,5+2,5 | 2.04 | 0.75 | 120 | 1.29 | 0 | 2.625 | 1.335 | 1.335 | 1.0947 | available | 0.82 | 231 | Sverchkovo 35/10 | 2,5+2,5 | 0.10366 | 0.085 | 2.1437 | 0.75 | 120 | 1.3937 | 0 | 2.625 | 1.2313 | 1.2313 | available | 0.82
232 | Lesnaya 35/10 | 4+4 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | 1.8559 | available | 0.67 | 232 | Lesnaya 35/10 | 4+4 | 0 | 0 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available | 0.67
233 | Tesovo 35/10 | 1,6+2,5 | 0.52 | 0.48 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | 1.5252 | available | 0.93 | 233 | Tesovo 35/10 | 1,6+2,5 | 0.082258 | 0.0765 | 0.60226 | 0.48 | 120 | 0.12226 | 0 | 1.68 | 1.5577 | 1.5577 | available | 0.93
234 | Svetotekhnika 110/10 | 16+16 | 4.5 | 0.97 | 120 | 3.53 | 0 | 16.8 | 13.27 | 13.27 | 12.0757 | available | 0.91 | 234 | Svetotekhnika 110/10 | 16+16 | 2.2604 | 2.057 | 6.7604 | 0.97 | 120 | 5.7904 | 0 | 16.8 | 11.0096 | 11.0096 | available | 0.91
235 | Mishino 110/35/10 | 10+10 | 3.81 | 3.17 | 120 | 0.64 | 0 | 10.5 | 9.86 | 9.86 | 8.381 | available | 0.85 | 235 | Mishino 110/35/10 | 10+10 | 3 | 2.55 | 6.81 | 4.52 | 120 | 2.29 | 0 | 10.5 | 8.21 | 8.21 | available | 0.85
| Nom. capacity MV, МVА | 10+10 | 2.53 | 2.53 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 1.35 | 1.1475 | 3.88 | 3.88 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.28 | 0.64 | 120 | 0.64 | 0 | 10.5 | 9.86 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 1.65 | 1.4025 | 2.93 | 0.64 | 120 | 2.29 | 0 | 10.5 | 8.21
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.71 | 0.59 | 120 | 1.12 | 0 | 6.615 | 5.495 | 5.495 | 4.7257 | available | 0.86 | 236 | Nikolskoe 35/10 | 6,3+6,3 | 1.018 | 0.8755 | 2.728 | 0.59 | 120 | 2.138 | 0 | 6.615 | 4.477 | 4.477 | available | 0.86
237 | Bekrino 35/10 | 2,5+2,5 | 0.51 | 0.09 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | 1.9183 | available | 0.87 | 237 | Bekrino 35/10 | 2,5+2,5 | 0.22471 | 0.1955 | 0.73471 | 0.09 | 120 | 0.64471 | 0 | 2.625 | 1.9803 | 1.9803 | available | 0.87
238 | Trubnaya 110/10 | 25+25 | 6.49 | 1.57 | 120 | 4.92 | 0 | 26.25 | 21.33 | 21.33 | 20.0502 | available | 0.94 | 238 | Trubnaya 110/10 | 25+25 | 4.7835 | 4.4965 | 11.2735 | 1.57 | 120 | 9.7035 | 0 | 26.25 | 16.5465 | 16.5465 | available | 0.94
239 | Temkino 110/35/10 | 10+10 | 3.66 | 1.65 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | 8.1504 | available | 0.96 | 239 | Temkino 110/35/10 | 10+10 | 1.824 | 1.751 | 5.484 | 2.0042 | 120 | 3.4798 | 0 | 10.5 | 7.0202 | 7.0202 | available | 0.96
| Nom. capacity MV, МVА | 10+10 | 1.4 | 1.4 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.35417 | 0.34 | 1.7542 | 1.7542 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.26 | 0.25 | 120 | 2.01 | 0 | 10.5 | 8.49 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 1.4698 | 1.411 | 3.7298 | 0.25 | 120 | 3.4798 | 0 | 10.5 | 7.0202
240 | Narytka 35/10 | 2,5+2,5 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | 2.0377 | available | 0.83 | 240 | Narytka 35/10 | 2,5+2,5 | 0 | 0 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 0.83
241 | Novodugino 110/35/10 | 10+10 | 3.9 | 1.89 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | 8.2353 | available | 0.97 | 241 | Novodugino 110/35/10 | 10+10 | 1.0603 | 1.0285 | 4.9603 | 2.7575 | 120 | 2.2028 | 0 | 10.5 | 8.2972 | 8.2972 | available | 0.97
| Nom. capacity MV, МVА | 10+10 | 1.41 | 1.41 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.86753 | 0.8415 | 2.2775 | 2.2775 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.49 | 0.48 | 120 | 2.01 | 0 | 10.5 | 8.49 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.19278 | 0.187 | 2.6828 | 0.48 | 120 | 2.2028 | 0 | 10.5 | 8.2972
242 | Vysokoe 35/10 | 1,6+4 | 0.64 | 0.42 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | 1.0366 | available | 0.71 | 242 | Vysokoe 35/10 | 1,6+4 | 1.0176 | 0.7225 | 1.6576 | 0.42 | 120 | 1.2376 | 0 | 1.68 | 0.44239 | 0.44239 | available | 0.71
243 | Khotkovo 35/10 | 4+4 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | 3.0408 | available | 0.84 | 243 | Khotkovo 35/10 | 4+4 | 0 | 0 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | available | 0.84
244 | Dneprovsk 110/35/10 | 10+10 | 3.67 | 3.29 | 120 | 0.38 | 0 | 10.5 | 10.12 | 10.12 | 9.0068 | available | 0.89 | 244 | Dneprovsk 110/35/10 | 10+10 | 2.4354 | 2.1675 | 6.1054 | 5.7063 | 120 | 0.3991 | 0 | 10.5 | 10.1009 | 10.1009 | available | 0.89
| Nom. capacity MV, МVА | 10+10 | 3.13 | 3.13 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 2.4163 | 2.1505 | 5.5463 | 5.5463 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.54 | 0.16 | 120 | 0.38 | 0 | 10.5 | 10.12 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 0.019101 | 0.017 | 0.5591 | 0.16 | 120 | 0.3991 | 0 | 10.5 | 10.1009
245 | Lipetsy 35/10 | 2,5+2,5 | 0.26 | 0.75 | 120 | -0.49 | 0 | 2.625 | 3.115 | 3.115 | 2.4297 | available | 0.78 | 245 | Lipetsy 35/10 | 2,5+2,5 | 0.032692 | 0.0255 | 0.29269 | 0.75 | 120 | -0.45731 | 0 | 2.625 | 3.0823 | 3.0823 | available | 0.78
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.66 | 0.7 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | 1.634 | available | 0.95 | 246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.017895 | 0.017 | 0.67789 | 0.7 | 120 | -0.022105 | 0 | 1.68 | 1.7021 | 1.7021 | available | 0.95
247 | Sychevka 110/35/10 | 16+25 | 8.8 | 1.47 | 120 | 7.33 | 0 | 16.8 | 9.47 | 9.47 | 8.7124 | available | 0.92 | 247 | Sychevka 110/35/10 | 16+25 | 6.1255 | 5.6355 | 14.9255 | 1.78 | 120 | 13.1455 | 0 | 16.8 | 3.6545 | 3.6545 | available | 0.92
| Nom. capacity MV, МVА | 16+25 | 3.43 | 0.7 |  | 2.73 | 0 | 16.8 | 14.07 | [5 empty] | Nom. capacity MV, МVА | 16+25 | 3.6402 | 3.349 | 7.0702 | 1.01 |  | 6.0602 | 0 | 16.8 | 10.7398
| Nom. capacfity LV, МVА | 16+25 | 5.37 | 0.77 | 120 | 4.6 | 0 | 16.8 | 12.2 | [5 empty] | Nom. capacfity LV, МVА | 16+25 | 2.4853 | 2.2865 | 7.8553 | 0.77 | 120 | 7.0853 | 0 | 16.8 | 9.7147
248 | Sutormino 35/10 | 1,8+4 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | 1.218 | available | 0.87 | 248 | Sutormino 35/10 | 1,8+4 | 0 | 0 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | available | 0.87
249 | Karavaevo 35/10 | 4+4 | 1.29 | 0.29 | 120 | 1 | 0 | 4.2 | 3.2 | 3.2 | 2.944 | available | 0.92 | 249 | Karavaevo 35/10 | 4+4 | 0.39728 | 0.3655 | 1.6873 | 0.29 | 120 | 1.3973 | 0 | 4.2 | 2.8027 | 2.8027 | available | 0.92
250 | Lukino 35/10 | 4+1,6 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | 0.7216 | available | 0.88 | 250 | Lukino 35/10 | 4+1,6 | 0 | 0 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | available | 0.88
251 | Subbotniki 110/10 | 6,3+6,3 | 0.75 | 0 | 120 | 0.75 | 0 | 6.615 | 5.865 | 5.865 | 5.3958 | available | 0.92 | 251 | Subbotniki 110/10 | 6,3+6,3 | 0.22174 | 0.204 | 0.97174 | 0 | 120 | 0.97174 | 0 | 6.615 | 5.6433 | 5.6433 | available | 0.92
252 | Ugra 110/10 | 6,3+6,3 | 3.64 | 0 | 120 | 3.64 | 0 | 6.615 | 2.975 | 2.975 | 2.856 | available | 0.96 | 252 | Ugra 110/10 | 6,3+6,3 | 0.5401 | 0.5185 | 4.1801 | 0 | 120 | 4.1801 | 0 | 6.615 | 2.4349 | 2.4349 | available | 0.96
253 | Znamenka 110/35/10 | 10+10 | 3.58 | 2.35 | 120 | 1.23 | 0 | 10.5 | 9.27 | 9.27 | 8.343 | available | 0.9 | 253 | Znamenka 110/35/10 | 10+10 | 3.3622 | 3.026 | 6.9422 | 2.7467 | 120 | 4.1956 | 0 | 10.5 | 6.3044 | 6.3044 | available | 0.9
| Nom. capacity MV, МVА | 10+10 | 2.32 | 2.32 |  | 0 | 0 | 10.5 | 10.5 | [5 empty] | Nom. capacity MV, МVА | 10+10 | 0.39667 | 0.357 | 2.7167 | 2.7167 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.26 | 0.03 | 120 | 1.23 | 0 | 10.5 | 9.27 | [5 empty] | Nom. capacity LV, МVА | 10+10 | 2.9656 | 2.669 | 4.2256 | 0.03 | 120 | 4.1956 | 0 | 10.5 | 6.3044
254 | Losmino 35/10 | 2,5+2,5 | 1.5 | 0.4 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | 1.2657 | available | 0.83 | 254 | Losmino 35/10 | 2,5+2,5 | 0.071687 | 0.0595 | 1.5717 | 0.4 | 120 | 1.1717 | 0 | 2.625 | 1.4533 | 1.4533 | available | 0.83
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.41 | 0.37 | 120 | 1.04 | 0 | 6.615 | 5.575 | 5.575 | 5.2405 | available | 0.94 | 255 | Vskhody 110/35/10 | 6,3+6,3 | 0.19894 | 0.187 | 1.6089 | 0.37 | 120 | 1.2389 | 0 | 6.615 | 5.3761 | 5.3761 | available | 0.94
| Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 0.36 |  | 0 | 0 | 6.615 | 6.615 | [5 empty] | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 | 0.36 | 0.36 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.05 | 0.01 | 120 | 1.04 | 0 | 6.615 | 5.575 | [5 empty] | Nom. capacity LV, МVА | 6,3+6,3 | 0.19894 | 0.187 | 1.2489 | 0.01 | 120 | 1.2389 | 0 | 6.615 | 5.3761
| Total: | 3150.6 | 578.51 | [11 empty] | Total: | 3150.6 | 307.9633 |  | 886.4733
| deficit | [8 empty] | -0.06 | -0.048 |  |  |  | deficit | [10 empty] | -111.161
| proficit | [8 empty] | 1025.89 | 908.7885 |  |  |  | proficit | [10 empty] | 782.376

## Total current deficit Jan 2012
The list of closed supply centers of IDGC of Centre - Smolenskenergo division according to winter load in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class, transformer capacity (installed MVA) |  | Current deficit, MVA | Note | cosφ
Smolenskenergo
1 | Mytishino 35/10 | 1.6 | -0.06 | unavailable | 0.8
Total current deficit (January 2012) |  |  | -0.06

## Total expected deficit Jan 2012
The list of closed supply centers of IDGC of Centre - Smolenskenergo with expected load taking into account new connections and other development of the electical networks
No. | Name of supply center, voltage class | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Expected deficit/proficit, MVA | Note | cosφ
Smolenskenergo
1 | Akatovo 35/10 | 1.6 | -0.60473 | unavailable | 0.93
2 | Avrora 35/10 | 2.5 | -2.6364 | unavailable | 0.94
3 | Mytishino 35/10 | 1.6 | -0.06 | unavailable | 0.8
4 | Ryabtsevo 35/10 | 4+4 | -1.8888 | unavailable | 0.82
5 | Vostochnaya 110/6 | 25+16 | -2.9961 | unavailable | 0.93
6 | Diffuzion 110/6 | 25+25 | -9.7017 | unavailable | 0.92
7 | Gnezodovo 35/6 | 7,5+7,5 | -1.4956 | unavailable | 0.9
8 | Zapadnaya 110/6 | 25+16 | -5.9752 | unavailable | 0.96
9 | Kozino 110/35/10 | 10+10 | -13.3634 | unavailable | 0.88
| Nom. capacity MV, MVA | 10+10
| Nom. capacity LV, MVA | 10+10
10 | Odintsovo 35/10 | 6,3+6,3 | -7.1419 | unavailable | 0.84
11 | Krasny bor 35/6 | 4+4 | -2.2611 | unavailable | 0.9
12 | Peсhersk 35/6 | 4+4 | -4.0328 | unavailable | 0.89
13 | Kolodnya 35/6 | 6,3+4 | -1.4685 | unavailable | 0.94
14 | Chernushki 110/10/6 | 25+25 | -7.7011 | unavailable | 0.94
| Nom. capacity MV, MVA | 25+25
| Nom. capacity LV, MVA | 25+25
15 | Yuzhnaya 110/35/6 | 40+40 | -8.0519 | unavailable | 0.91
| Nom. capacity MV, MVA | 40+40
| Nom. capacity LV, MVA | 40+40
16 | Zhukovskaya 35/10 | 4+4 | -1.6865 | unavailable | 0.88
17 | Kardymovo 110/35/10 | 10+16 | -0.062778 | unavailable | 0.9
| Nom. capacity MV, MVA | 10+16
| Nom. capacity LV, MVA | 10+16
18 | Belei 35/10 | 2,5+2,5 | -2.3385 | unavailable | 0.94
19 | Kholm-Zhirki 35/10 | 2,5+4 | -1.0881 | unavailable | 0.89
20 | Yartsevo 2 110/10 | 16+16 | -5.4197 | unavailable | 0.89
21 | Vyazma 1 110/35/10 | 40+40 | -14.993 | unavailable | 0.91
| Nom. capacity MV, MVA | 40+40
| Nom. capacity LV, MVA | 40+40
22 | Flour mill 35/10 | 10+10 | -6.0752 | unavailable | 0.89
23 | Vyazma 2 110/10 | 16+16 | -5.0303 | unavailable | 0.94
24 | Gagarin 110/35/10 | 25+25 | -3.968 | unavailable | 0.91
| Nom. capacity MV, MVA | 25+25
| Nom. capacity LV, MVA | 25+25
25 | Karmanovo 35/10 | 4+4 | -0.43404 | unavailable | 0.94
| Total: |  | -110.4754