## Table 1+Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.81 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.49 | 1.08 | available | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.035 | 1.845 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.455 | 1.059 | available
| Nom. capacity MV, MVA | 6.3 | 1.22 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.08 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.021 | 1.241 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.059
| Nom. capacity MV, MVA | 6.3 | 0.59 | 4 | 1 day and night | 4 | 0 | 4 | 3.41 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.014 | 0.604 | 4 | 1 day and night | 4 | 0 | 4 | 3.396
2 | SS 110/10 Beketovo | 1*6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | available | 2 | SS 110/10 Beketovo | 1*6,3 | 2.476 | 2.806 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -0.656 | -0.656 | unavailable
3 | SS 110/35/10 Besedino | 1*6,3 | 3.34 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.46 | 0.52 | available | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.171 | 3.511 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.289 | 0.407 | available
| Nom. capacity MV, MVA | 6.3 | 0.56 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.94 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.058 | 0.618 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.882
| Nom. capacity LV, MVA | 6.3 | 2.78 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.52 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.113 | 2.893 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.407
4 | SS 110/10 Voskhod | 1*10,0 | 0.6 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.9 | 1.9 | available | 4 | SS 110/10 Voskhod | 1*10,0 | 0.096 | 0.696 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.804 | 1.804 | available
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.91 | 6 | 1 day and night | 6 | 0 | 6 | 5.09 | 1.39 | available | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.055 | 0.965 | 6 | 1 day and night | 6 | 0 | 6 | 5.035 | 1.335 | available
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.91 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.39 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.055 | 0.965 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.335
6 | SS 110/35/10 Zhukovka | 1*10,0 | 1.22 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.94 | 0.47 | available | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.111 | 1.331 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.829 | 0.47 | available
| Nom. capacity MV, MVA | 10 | 1.03 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.47 |  |  |  | Nom. capacity MV, MVA | 10 | 0.111 | 1.141 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.359
| Nom. capacity LV, MVA | 10 | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47 |  |  |  | Nom. capacity LV, MVA | 10 |  | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47
7 | SS 110/10 Zabelye | 1*2,5 | 0.3 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.85 | 1.85 | available | 7 | SS 110/10 Zabelye | 1*2,5 | 0.046 | 0.346 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.804 | 1.804 | available
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | available | 8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | available
9 | SS 110/35/10 Lachinovo | 1*10,0 | 1.4 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.73 | 1.13 | available | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.59 | 1.99 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.14 | 0.54 | available
| Nom. capacity MV, MVA | 10 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6
| Nom. capacity LV, MVA | 10 | 0.4 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 1.13 |  |  |  | Nom. capacity LV, MVA | 10 | 0.59 | 0.99 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.54
10 | SS 110/10 Malaya Loknya | 1*10,0 | 1.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.2 | 0.2 | available | 10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.019 | 1.219 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.181 | 0.181 | available
11 | SS 110/35/10 Maritsa | 1*2,5 | 1.65 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.27 | 0.27 | available | 11 | SS 110/35/10 Maritsa | 1*6,3 | 0.046 | 1.696 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.224 | 0.224 | available
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.55 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.34 | 2.04 | available | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.026 | 0.576 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.314 | 2.04 | available
| Nom. capacity MV, MVA | 6.3 | 0.44 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.3 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.026 | 0.466 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.274
| Nom. capacity LV, MVA | 6.3 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.03 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.37 | 1.37 | available | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.013 | 0.043 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.357 | 1.357 | available
14 | SS 110/6 Teplichnaya | 1х16 | 6.46 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | 0.18 | 0.18 | available | 14 | SS 110/6 Teplichnaya | 1х16 | 6.1645 | 12.6245 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | -5.9845 | -5.9845 | unavailable
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.43 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 5.07 | 0.64 | available | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.0143 | 4.4443 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 3.0557 | 0.557 | available
| Nom. capacity MV, MVA | 10 | 1.97 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 4.43 |  |  |  | Nom. capacity MV, MVA | 10 | 1.9313 | 3.9013 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 2.4987
| Nom. capacity LV, MVA | 10 | 0.46 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.64 |  |  |  | Nom. capacity LV, MVA | 10 | 0.083 | 0.543 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.557
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.53 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.27 | 0.27 | available | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.573 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.227 | 0.227 | available
17 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.45 | 0.45 | available | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.2 | 0.7 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.25 | 0.25 | available
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | available | 18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | available
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.24 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.19 | 1.19 | available | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.025 | 0.265 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.165 | 1.165 | available
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.56 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.78 | 0.78 | available | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.045 | 0.605 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.735 | 0.735 | available
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.79 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.17 | 0.17 | available | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.006 | 0.796 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.164 | 0.164 | available
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.76 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.07 | 2.07 | available | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.4024 | 1.1624 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 1.6676 | 1.6676 | available
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.36 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.28 | 0.28 | available | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.03 | 0.39 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.25 | 0.25 | available
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.46 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.97 | 0.97 | available | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.596 | 1.056 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.374 | 0.374 | available
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.28 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.87 | 1.87 | available | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.098 | 0.378 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.772 | 1.772 | available
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.5 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.26 | 1.26 | available | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.296 | 0.796 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.964 | 0.964 | available
27 | SS 35/10 Biryukovka | 1х1,6 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available | 27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.26 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.41 | 0.41 | available | 28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.014 | 0.274 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.396 | 0.396 | available
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available | 29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | available
30 | SS 35/10 Budki | 1 х 1,0 | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | available | 30 | SS 35/10 Budki | 1 х 1,0 |  | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | available
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.66 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.94 | 0.94 | available | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.055 | 0.715 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.885 | 0.885 | available
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.22 | 1 | 1 day and night | 1 | 0 | 1 | 0.78 | 0.78 | available | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.045 | 0.265 | 1 | 1 day and night | 1 | 0 | 1 | 0.735 | 0.735 | available
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | available | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.04 | 0.32 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.11 | 1.11 | available
34 | SS 35/10 Bykovo | 1х4,0 | 0.89 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.54 | 0.54 | available | 34 | SS 35/10 Bykovo | 1х4 | 3.8303 | 4.7203 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | -3.2903 | -3.2903 | unavailable
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | available | 35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | available
36 | SS 35/10 Vanino | 1 х 2,5 | 0.24 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.56 | 0.56 | available | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.078 | 0.318 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.482 | 0.482 | available
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.6 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.45 | 0.45 | available | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.06 | 0.66 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.39 | 0.39 | available
38 | SS 35/10 Water storage | 1 х 4,0 | 1.76 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | 0.96 | 0.96 | available | 38 | SS 35/10 Water storage | 1 х 4,0 | 4.808 | 6.568 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | -3.848 | -3.848 | unavailable
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available | 39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | available
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.72 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.18 | 0.18 | available | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.734 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.166 | 0.166 | available
41 | SS 35/10 Voronok | 1 х 4,0 | 0.82 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.28 | 1.28 | available | 41 | SS 35/10 Voronok | 1 х 4,0 | 0.02 | 0.84 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.26 | 1.26 | available
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.45 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.7 | 1.7 | available | 42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.032 | 0.482 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.668 | 1.668 | available
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.59 | 1.59 | available | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.025 | 0.235 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.565 | 1.565 | available
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.21 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.29 | 1.29 | available | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.14 | 0.35 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.15 | 1.15 | available
45 | SS 35/10 Glazovo | 1 х 2,5 | 1.26 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.24 | 0.24 | available | 45 | SS 35/10 Glazovo | 1 х 2,5 | 0.02 | 1.28 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.22 | 0.22 | available
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.53 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.87 | 0.87 | available | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.068 | 0.598 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.802 | 0.802 | available
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.3 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.4 | 0.4 | available | 47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.07 | 0.37 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.33 | 0.33 | available
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.57 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.19 | 0.19 | available | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.048 | 0.618 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.142 | 0.142 | available
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.5 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.6 | 0.6 | available | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.055 | 0.555 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.545 | 0.545 | available
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | available | 50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | available
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.96 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.47 | 0.47 | available | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.052 | 1.012 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.418 | 0.418 | available
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.61 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.24 | 2.24 | available | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.026 | 0.636 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.214 | 2.214 | available
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.26 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.68 | 0.68 | available | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.014 | 0.274 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.666 | 0.666 | available
54 | SS 35/10 Daryino | 1 х 2,5 | 0.4 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4 | 1.4 | available | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.05 | 0.45 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.35 | 1.35 | available
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.61 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.19 | 0.19 | available | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.075 | 0.685 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.115 | 0.115 | available
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.33 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.74 | 0.74 | available | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.06525 | 0.39525 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.67475 | 0.67475 | available
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.3 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.55 | 0.55 | available | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.056 | 0.356 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.494 | 0.494 | available
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.36 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.79 | 1.79 | available | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.611 | 0.971 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.179 | 1.179 | available
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.49 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.35 | 0.35 | available | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.075 | 0.565 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.275 | 0.275 | available
60 | SS 35/10 Znamenka | 1 х 1,8 | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | available | 60 | SS 35/10 Znamenka | 1 х 1,8 | 0.008 | 1.018 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.132 | 1.132 | available
61 | SS 35/10 Iskra | 1 х 2,5 | 0.2 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.38 | 0.38 | available | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.058 | 0.258 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.322 | 0.322 | available
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.41 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.39 | 0.39 | available | 62 | SS 35/10 Kazanka | 1 х 4,0 | 0.009 | 0.419 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.381 | 0.381 | available
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.13 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.67 | 1.67 | available | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.06 | 0.19 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.61 | 1.61 | available
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.31 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33 | 0.33 | available | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.015 | 0.325 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.315 | 0.315 | available
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.28 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.46 | 0.46 | available | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.257 | 0.537 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.203 | 0.203 | available
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.64 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.89 | 0.89 | available | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.046 | 0.686 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.844 | 0.844 | available
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | available | 67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.03 | 0.58 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.26 | 0.26 | available
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.55 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.87 | 0.87 | available | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.024 | 0.574 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.846 | 0.846 | available
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.55 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.21 | 0.21 | available | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.024 | 0.574 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.186 | 0.186 | available
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | available | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.264 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.166 | 1.166 | available
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.64 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.19 | 0.19 | available | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.088 | 0.728 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.102 | 0.102 | available
72 | SS 35/10 Lobazovka | 1 х 2,5 | 1.06 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.03 | 0.03 | available | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.021 | 1.081 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.009 | 0.009 | available
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.58 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.71 | 0.71 | available | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.091 | 0.671 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.619 | 0.619 | available
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.32 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.83 | 0.83 | available | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0.026 | 0.346 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.804 | 0.804 | available
75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.96 | 0.96 | available | 75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.046 | 0.046 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.914 | 0.914 | available
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.063 | 0.663 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.437 | 0.437 | available
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.76 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.52 | 0.52 | available | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.015 | 0.775 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.505 | 0.505 | available
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.3 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.89 | 0.89 | available | 78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.01 | 0.31 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.88 | 0.88 | available
79 | SS 35/10 Markovo | 1 х 2,5 | 0.68 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.12 | 0.12 | available | 79 | SS 35/10 Markovo | 1 х 2,5 | 0.01 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | available
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.23 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.1 | 1.1 | available | 80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.015 | 0.245 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.085 | 1.085 | available
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.99 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.16 | 1.16 | available | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.03 | 1.02 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.13 | 1.13 | available
82 | SS 35/10 Mokva | 1 х 4,0 | 0.56 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.59 | 1.59 | available | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.2473 | 0.8073 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.3427 | 1.3427 | available
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | available | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.033 | 0.633 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.467 | 0.467 | available
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | available | 84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | available
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | available | 85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | available
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | available | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | available
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 1.1 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.05 | 1.05 | available | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.014 | 1.114 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.036 | 1.036 | available
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.04 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.36 | 1.36 | available | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.048 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.352 | 1.352 | available
89 | SS 35/10 Niva | 1 х 2,5 | 0.4 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.16 | 1.16 | available | 89 | SS 35/10 Niva | 1 х 2,5 | 0.035 | 0.435 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.125 | 1.125 | available
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.5 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.47 | 0.47 | available | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0.13 | 0.63 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.34 | 0.34 | available
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.49 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.15 | 0.15 | available | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.08 | 0.57 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.07 | 0.07 | available
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 1.46 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 1.51 | 1.51 | available | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 2.296 | 3.756 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | -0.786 | -0.786 | unavailable
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.6 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.72 | 1.72 | available | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.5 | 1.1 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.22 | 1.22 | available
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | available | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | available
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | available | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.015 | 0.215 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.185 | 1.185 | available
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | available | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0.334 | 0.664 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.486 | 1.486 | available
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | available | 97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | available
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.19 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.96 | 1.96 | available | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.035 | 0.225 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.925 | 1.925 | available
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.35 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8 | 1.8 | available | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.359 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.791 | 1.791 | available
100 | SS 35/10 Pristen | 1 х 4,0 | 2.2 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.1 | 1.1 | available | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.097 | 2.297 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.003 | 1.003 | available
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.74 | 0.74 | available | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.033 | 0.033 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.707 | 0.707 | available
102 | SS 35/10 Reut | 1 х 2,5 | 0.44 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.66 | 0.66 | available | 102 | SS 35/10 Reut | 1 х 2,5 | 0.916 | 1.356 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | -0.256 | -0.256 | unavailable
103 | SS 35/10 Rovenka | 1 х 1,6 | 1.16 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.44 | 0.44 | available | 103 | SS 35/10 Rovenka | 1 х 1,6 | 1.385 | 2.545 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | -0.945 | -0.945 | unavailable
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.18 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.52 | 0.52 | available | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.037 | 0.217 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.483 | 0.483 | available
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.38 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.92 | 1.92 | available | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.2418 | 0.6218 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.6782 | 1.6782 | available
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.4 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.91 | 0.91 | available | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.0304 | 0.4304 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.8796 | 0.8796 | available
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.19 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.24 | 1.24 | available | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.214 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.216 | 1.216 | available
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.42 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.52 | 0.52 | available | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.059 | 0.479 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.461 | 0.461 | available
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.53 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.62 | 0.62 | available | 109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.031 | 0.561 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.589 | 0.589 | available
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | available | 110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | available
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.3 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.4 | 2.4 | available | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0.017 | 0.317 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.383 | 2.383 | available
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | available | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.066 | 0.316 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.114 | 1.114 | available
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.81 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.95 | 0.95 | available | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.095 | 0.905 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.855 | 0.855 | available
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.28 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.82 | 0.82 | available | 114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.108 | 0.388 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.712 | 0.712 | available
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | available | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.373 | 0.573 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.827 | 0.827 | available
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.35 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.95 | 0.95 | available | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.065 | 0.415 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.885 | 0.885 | available
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.6 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.74 | 0.74 | available | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.04 | 0.64 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.7 | 0.7 | available
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.54 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.17 | 0.17 | available | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.009 | 0.549 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.161 | 0.161 | available
119 | SS 35/10 Telmana | 1 х 2,5 | 0.41 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.74 | 0.74 | available | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.025 | 0.435 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.715 | 0.715 | available
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | available | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.042 | 0.402 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.028 | 1.028 | available
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.07 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.63 | 0.63 | available | 121 | SS 35/10 Fateevka | 1 х 2,5 | 0.016 | 0.086 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.614 | 0.614 | available
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.18 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.54 | 1.54 | available | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.044 | 0.224 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.496 | 1.496 | available
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.34 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.76 | 0.76 | available | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.017 | 0.357 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.743 | 0.743 | available
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available | 124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | available
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | available | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.033 | 0.393 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.037 | 1.037 | available
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.16 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.27 | 1.27 | available | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.02032 | 0.18032 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.2497 | 1.2497 | available
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.58 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.89 | 0.89 | available | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.023 | 0.603 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.867 | 0.867 | available
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | available | 128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | available
129 | SS 35/10 Elevator | 1х6,3 | 0.21 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.39 | 0.39 | available | 129 | SS 35/10 Elevator | 1х6,3 | 0.02 | 0.23 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.37 | 0.37 | available
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.24 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.4 | 0.4 | available | 130 | SS 35/10 Yankovo | 1 х 1,6 | 0.009 | 0.249 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.391 | 0.391 | available
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.67 | 1.67 | available | 131 | SS 35/10 Yasenki | 1 х 2,5 | 3.533 | 4.013 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -1.863 | -1.863 | unavailable
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | available | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | available
2 | SS 110/10 ARZ | 6,3+10,0 | 1.78 | 0.9 | 45 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | available | 2 | SS 110/10 ARZ | 6,3+10,0 | 0.022 | 1.802 | 0.9 | 45 | 0.902 | 0 | 6.615 | 5.713 | 5.713 | available
3 | SS 110/35/10 Atomgrad | 2*25 | 11.72 | 20.2 | 120 | -8.48 | 0 | 26.25 | 34.73 | 27.68 | available | 3 | SS 110/35/10 Atomgrad | 2*25 | 0.858 | 12.578 | 20.2 | 120 | -7.622 | 0 | 26.25 | 33.872 | 27.339 | available
| Nom. capacity MV, MVA | 25 | 3.55 | 10.6 | 120 | -7.05 | 0 | 26.25 | 33.3 |  |  |  | Nom. capacity MV, MVA | 25 | 0.517 | 4.067 | 10.6 | 120 | -6.533 | 0 | 26.25 | 32.783
| Nom. capacity lV, MVA | 25 | 8.17 | 9.6 | 120 | -1.43 | 0 | 26.25 | 27.68 |  |  |  | Nom. capacity lV, MVA | 25 | 0.341 | 8.511 | 9.6 | 120 | -1.089 | 0 | 26.25 | 27.339
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.83 | 0.6 | 120 | 0.23 | 0 | 6.615 | 6.385 | 6.385 | available | 4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.035 | 0.865 | 0.6 | 120 | 0.265 | 0 | 6.615 | 6.35 | 6.35 | available
5 | SS 110/35/10 Basovo | 5,6+10,0 | 1.32 | 6.19 | 15 | -4.87 | 0 | 5.88 | 10.75 | 5.34 | available | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.623 | 1.943 | 6.19 | 15 | -4.247 | 0 | 5.88 | 10.127 | 5.328 | available
| Nom. capacity MV, MVA | 5,6+10,0 | 0.59 | 6 |  | -5.41 | 0 | 5.88 | 11.29 |  |  |  | Nom. capacity MV, MVA | 5,6+10,0 | 0.611 | 1.201 | 6 |  | -4.799 | 0 | 5.88 | 10.679
| Nom. capacity LV, MVA | 5,6+10,0 | 0.73 | 0.19 | 120 | 0.54 | 0 | 5.88 | 5.34 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.012 | 0.742 | 0.19 | 120 | 0.552 | 0 | 5.88 | 5.328
6 | SS 110/35/10 Belaya | 2*16,0 | 7.1 | 12 | 120 | -4.9 | 0 | 16.8 | 21.7 | 13.6 | available | 6 | SS 110/35/10 Belaya | 2*16,0 | 1.466 | 8.566 | 12 | 120 | -3.434 | 0 | 16.8 | 20.234 | 12.747 | available
| Nom. capacity MV, MVA | 16 | 3.2 | 0 |  | 3.2 | 0 | 16.8 | 13.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.853 | 4.053 | 0 |  | 4.053 | 0 | 16.8 | 12.747
| Nom. capacity LV, MVA | 16 | 3.9 | 12 | 120 | -8.1 | 0 | 16.8 | 24.9 |  |  |  | Nom. capacity LV, MVA | 16 | 0.613 | 4.513 | 12 | 120 | -7.487 | 0 | 16.8 | 24.287
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.6 | 1.3 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.015 | available | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.12 | 2.72 | 1.3 | 120 | 1.42 | 0 | 6.615 | 5.195 | 5.195 | available
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.373 | 0.973 |  |  | 0.973 | 0 | 6.615 | 5.642
| Nom. capacity LV, MVA | 6.3 | 1 | 1.3 | 120 | -0.3 | 0 | 6.615 | 6.915 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.747 | 1.747 | 1.3 | 120 | 0.447 | 0 | 6.615 | 6.168
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.57 | 1.17 | 45 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | available | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.0865 | 2.6565 | 1.17 | 45 | 1.4865 | 0 | 2.625 | 1.1385 | 1.1385 | available
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 41.48 | 16.8 | 0 | 24.68 | 0 | 84.525 | 59.845 | 58.045 | available | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 2.177 | 43.657 | 16.8 | 0 | 26.857 | 0 | 84.525 | 57.668 | 57.668 | available
| Nom. capacity MV, MVA | 40,0+2*40,5 | 15 | 16.8 | 0 | -1.8 | 0 | 84.525 | 86.325 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 1.908 | 16.908 | 16.8 | 0 | 0.108 | 0 | 84.525 | 84.417
| Nom. capacity MV, MVA | 40,0+2*40,5 | 26.48 | 0 | 0 | 26.48 | 0 | 84.525 | 58.045 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.269 | 26.749 | 0 | 0 | 26.749 | 0 | 84.525 | 57.776
10 | SS 110/10 Vysokaya* | 2*16,0 | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | unavailable | 10 | SS 110/10 Vysokaya* | 2*16,0 |  | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | unavailable
11 | SS 110/35/10 Glushkovo | 2*10,0 | 6.23 | 8.04 | 120 | -1.81 | 0 | 10.5 | 12.31 | 8.67 | available | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 1.5975 | 7.8275 | 8.04 | 120 | -0.2125 | 0 | 10.5 | 10.7125 | 8.6645 | available
| Nom. capacity MV, MVA | 10 | 2.96 | 6.6 | 120 | -3.64 | 0 | 10.5 | 14.14 |  |  |  | Nom. capacity MV, MVA | 10 | 1.592 | 4.552 | 6.6 | 120 | -2.048 | 0 | 10.5 | 12.548
| Nom. capacity LV, MVA | 10 | 3.27 | 1.44 | 80 | 1.83 | 0 | 10.5 | 8.67 |  |  |  | Nom. capacity LV, MVA | 10 | 0.0055 | 3.2755 | 1.44 | 80 | 1.8355 | 0 | 10.5 | 8.6645
12 | SS 110/10 Gorodskaya | 2*25,0 | 12.72 | 0 | 0 | 12.72 | 0 | 26.25 | 13.53 | 13.53 | available | 12 | SS 110/10 Gorodskaya | 2*25,0 | 4.9952 | 17.7152 | 0 | 0 | 17.7152 | 0 | 26.25 | 8.5348 | 8.5348 | available
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 8 | 6.52 | 120 | 1.48 | 0 | 10.5 | 9.02 | 7.61 | available | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 11.9941 | 19.9941 | 6.52 | 120 | 13.4741 | 0 | 10.5 | -2.9741 | -2.9741 | unavailable
| Nom. capacity MV, MVA | 10+16,0 | 4.65 | 6.06 |  | -1.41 | 0 | 10.5 | 11.91 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 11.4406 | 16.0906 | 6.06 |  | 10.0306 | 0 | 10.5 | 0.46936
| Nom. capacity LV, MVA | 10+16,0 | 3.35 | 0.46 | 120 | 2.89 | 0 | 10.5 | 7.61 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.5535 | 3.9035 | 0.46 | 120 | 3.4435 | 0 | 10.5 | 7.0565
14 | SS 110/35/10 Dmitriev | 2*10,0 | 5.94 | 10.4 | 120 | -4.46 | 0 | 10.5 | 14.96 | 9.97 | available | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 1.5102 | 7.4502 | 10.4 | 120 | -2.9498 | 0 | 10.5 | 13.4498 | 8.528 | available
| Nom. capacity MV, MVA | 10 | 2.41 | 7.4 |  | -4.99 | 0 | 10.5 | 15.49 |  |  |  | Nom. capacity MV, MVA | 10 | 0.0682 | 2.4782 | 7.4 |  | -4.9218 | 0 | 10.5 | 15.4218
| Nom. capacity LV, MVA | 10 | 3.53 | 3 | 80 | 0.53 | 0 | 10.5 | 9.97 |  |  |  | Nom. capacity LV, MVA | 10 | 1.442 | 4.972 | 3 | 80 | 1.972 | 0 | 10.5 | 8.528
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.9 | 0.5 | 120 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | available | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.917 | 0.5 | 120 | 0.417 | 0 | 10.5 | 10.083 | 10.083 | available
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 7.52 | 22.1 | 80 | -14.58 | 0 | 26.25 | 40.83 | 25.21 | available | 16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.509 | 8.029 | 22.1 | 80 | -14.071 | 0 | 26.25 | 40.321 | 24.891 | available
| Nom. capacity MV, MVA | 25 | 3.18 | 18.8 |  | -15.62 | 0 | 26.25 | 41.87 |  |  |  | Nom. capacity MV, MVA | 25 | 0.19 | 3.37 | 18.8 |  | -15.43 | 0 | 26.25 | 41.68
| Nom. capacity LV, MVA | 25 | 4.34 | 3.3 | 120 | 1.04 | 0 | 26.25 | 25.21 |  |  |  | Nom. capacity LV, MVA | 25 | 0.319 | 4.659 | 3.3 | 120 | 1.359 | 0 | 26.25 | 24.891
17 | SS 110/35/10 Kamyshi | 2*6,3 | 12.08 | 5.45 | 20 | 6.63 | 0 | 6.615 | -0.015 | -0.305 | unavailable | 17 | SS 110/35/10 Kamyshi | 2*6,3 | 5.83 | 17.91 | 5.45 | 20 | 12.46 | 0 | 6.615 | -5.845 | -5.936 | unavailable
| Nom. capacity MV, MVA | 6.3 | 10.37 | 3.45 |  | 6.92 | 0 | 6.615 | -0.305 |  |  |  | Nom. capacity MV, MVA | 6.3 | 5.631 | 16.001 | 3.45 |  | 12.551 | 0 | 6.615 | -5.936
| Nom. capacity LV, MVA | 6.3 | 1.71 | 2 | 20 | -0.29 | 0 | 6.615 | 6.905 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.199 | 1.909 | 2 | 20 | -0.091 | 0 | 6.615 | 6.706
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 12.92 | 6.97 | 120 | 5.95 | 0 | 15.75 | 9.8 | 9.8 | available | 18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.7366 | 13.6566 | 6.97 | 120 | 6.6866 | 0 | 15.75 | 9.0634 | 9.0634 | available
| Nom. capacity MV, MVA | 15,0+16,0 | 9.88 | 6.6 |  | 3.28 | 0 | 15.75 | 12.47 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.6386 | 10.5186 | 6.6 |  | 3.9186 | 0 | 15.75 | 11.8314
| Nom. capacity LV, MVA | 15,0+16,0 | 3.04 | 0.37 | 120 | 2.67 | 0 | 15.75 | 13.08 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.098 | 3.138 | 0.37 | 120 | 2.768 | 0 | 15.75 | 12.982
19 | SS 110/35/10 Kilikino | 2*16,0 | 2.41 | 4.5 | 120 | -2.09 | 0 | 16.8 | 18.89 | 17.15 | available | 19 | SS 110/35/10 Kilikino | 2*16,0 | 0.2478 | 2.6578 | 4.5 | 120 | -1.8422 | 0 | 16.8 | 18.6422 | 16.9062 | available
| Nom. capacity MV, MVA | 16 | 2.25 | 2.6 |  | -0.35 | 0 | 16.8 | 17.15 |  |  |  | Nom. capacity MV, MVA | 16 | 0.2438 | 2.4938 | 2.6 |  | -0.1062 | 0 | 16.8 | 16.9062
| Nom. capacity LV, MVA | 16 | 0.16 | 1.9 | 120 | -1.74 | 0 | 16.8 | 18.54 |  |  |  | Nom. capacity LV, MVA | 16 | 0.004 | 0.164 | 1.9 | 120 | -1.736 | 0 | 16.8 | 18.536
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 52.37 | 16.36 | 120 | 36.01 | 0 | 42 | 5.99 | 5.99 | available | 20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.745 | 55.115 | 16.36 | 120 | 38.755 | 0 | 42 | 3.245 | 3.245 | available
| Nom. capacity MV, MVA | 40 | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73 |  |  |  | Nom. capacity MV, MVA | 40 |  | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73
| Nom. capacity LV, MVA | 40 | 24.03 | 3.3 | 120 | 20.73 | 0 | 42 | 21.27 |  |  |  | Nom. capacity LV, MVA | 40 | 2.745 | 26.775 | 3.3 | 120 | 23.475 | 0 | 42 | 18.525
21 | SS 110/35/10 Klyukva | 2*16,0 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | available | 21 | SS 110/35/10 Klyukva | 2*16,0 | 0.777 | 4.477 | 1.2 | 120 | 3.277 | 0 | 16.8 | 13.523 | 13.523 | available
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  | 2: Nom. capacity MV, MVA; 3: 16; 5: 0; Min 8: 0; Min 9: 0; Min 10: 16.8; Min 11: 16.8
| Nom. capacity LV, MVA | 16 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3 |  |  |  | Nom. capacity LV, MVA | 16 | 0.777 | 4.477 | 1.2 | 120 | 3.277 | 0 | 16.8 | 13.523
22 | SS 110/10 Kompressornaya | 2*40,0 | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | available | 22 | SS 110/10 Kompressornaya | 2*40,0 |  | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | available
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 10.28 | 8 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.18 | available | 23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.7306 | 12.0106 | 8 | 120 | 4.0106 | 0 | 10.5 | 6.4894 | 6.4894 | available
| Nom. capacity MV, MVA | 10,0+16,0 | 8.22 | 5.9 |  | 2.32 | 0 | 10.5 | 8.18 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.701 | 8.921 | 5.9 |  | 3.021 | 0 | 10.5 | 7.479
| Nom. capacity LV, MVA | 10,0+16,0 | 2.06 | 2.1 |  | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 1.0296 | 3.0896 | 2.1 |  | 0.98958 | 0 | 10.5 | 9.5104
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 10.27 | 4.1 | 0 | 6.17 | 0 | 10.5 | 4.33 | 4.33 | available | 24 | SS 110/10 Kotelnaya | 10,0+25,0 | 3.6616 | 13.9316 | 4.1 | 0 | 9.8316 | 0 | 10.5 | 0.6684 | 0.6684 | available
25 | SS 110/35/10 Kshen | 2*10,0 | 9.69 | 6.63 | 10 | 3.06 | 0 | 10.5 | 7.44 | 5.94 | available | 25 | SS 110/35/10 Kshen | 2*10,0 | 2.6686 | 12.3586 | 6.63 | 10 | 5.7286 | 0 | 10.5 | 4.7714 | 4.2607 | available
| Nom. capacity MV, MVA | 10 | 4.56 | 6.06 |  | -1.5 | 0 | 10.5 | 12 |  |  |  | Nom. capacity MV, MVA | 10 | 0.98932 | 5.5493 | 6.06 |  | -0.51068 | 0 | 10.5 | 11.0107
| Nom. capacity LV, MVA | 10 | 5.13 | 0.57 | 120 | 4.56 | 0 | 10.5 | 5.94 |  |  |  | Nom. capacity LV, MVA | 10 | 1.6793 | 6.8093 | 0.57 | 120 | 6.2393 | 0 | 10.5 | 4.2607
26 | SS 110/6 Lesnaya | 2*40,0 | 2.34 | 0 | 0 | 2.34 | 0 | 42 | 39.66 | 39.66 | available | 26 | SS 110/6 Lesnaya | 2*40,0 | 0.9 | 3.24 | 0 | 0 | 3.24 | 0 | 42 | 38.76 | 38.76 | available
27 | SS 110/35/10 Lgov | 2*25,0 | 13.76 | 4 | 120 | 9.76 | 0 | 26.25 | 16.49 | 16.49 | available | 27 | SS 110/35/10 Lgov | 2*25,0 | 0.676 | 14.436 | 4 | 120 | 10.436 | 0 | 26.25 | 15.814 | 15.814 | available
| Nom. capacity MV, MVA | 25 | 2.07 |  |  | 2.07 | 0 | 26.25 | 24.18 |  |  |  | Nom. capacity MV, MVA | 25 | 0.013 | 2.083 |  |  | 2.083 | 0 | 26.25 | 24.167
| Nom. capacity LV, MVA | 25 | 11.69 | 4 | 120 | 7.69 | 0 | 26.25 | 18.56 |  |  |  | Nom. capacity LV, MVA | 25 | 0.663 | 12.353 | 4 | 120 | 8.353 | 0 | 26.25 | 17.897
28 | SS 110/35/10 Lukashevka | 2*16,0 | 8.83 | 10.6 | 120 | -1.77 | 0 | 16.8 | 18.57 | 17.03 | available | 28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.148 | 8.978 | 10.6 | 120 | -1.622 | 0 | 16.8 | 18.422 | 16.882 | available
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03 |  |  |  | Nom. capacity MV, MVA | 16 | 0.148 | 5.218 | 5.3 |  | -0.082 | 0 | 16.8 | 16.882
| Nom. capacity LV, MVA | 16 | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 5.9 | 13.1 | 120 | -7.2 | 0 | 6.615 | 13.815 | 6.715 | available | 29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.269 | 6.169 | 13.1 | 120 | -6.931 | 0 | 6.615 | 13.546 | 6.676 | available
| Nom. capacity MV, MVA | 6,3+10,0 | 4.7 | 11.8 |  | -7.1 | 0 | 6.615 | 13.715 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.23 | 4.93 | 11.8 |  | -6.87 | 0 | 6.615 | 13.485
| Nom. capacity LV, MVA | 6,3+10,0 | 1.2 | 1.3 |  | -0.1 | 0 | 6.615 | 6.715 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.039 | 1.239 | 1.3 |  | -0.061 | 0 | 6.615 | 6.676
30 | SS 110/35/6 Manturovo | 2*16,0 | 7.38 | 9.35 | 10 | -1.97 | 0 | 16.8 | 18.77 | 16.89 | available | 30 | SS 110/35/6 Manturovo | 2*16,0 | 0.69639 | 8.0764 | 9.35 | 10 | -1.2736 | 0 | 16.8 | 18.0736 | 16.855 | available
| Nom. capacity MV, MVA | 16 | 7.21 | 9.09 |  | -1.88 | 0 | 16.8 | 18.68 |  |  |  | Nom. capacity MV, MVA | 16 | 0.66139 | 7.8714 | 9.09 |  | -1.2186 | 0 | 16.8 | 18.0186
| Nom. capacity LV, MVA | 16 | 0.17 | 0.26 | 120 | -0.09 | 0 | 16.8 | 16.89 |  |  |  | Nom. capacity LV, MVA | 16 | 0.035 | 0.205 | 0.26 | 120 | -0.055 | 0 | 16.8 | 16.855
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 5.81 | 9.6 | 120 | -3.79 | 0 | 6.615 | 10.405 | 8.025 | available | 31 | SS 110/35/10 8th Marta | 6,3+10,0 | 3.404 | 9.214 | 9.6 | 120 | -0.386 | 0 | 6.615 | 7.001 | 4.63 | available
| Nom. capacity MV, MVA | 6,3+10,0 | 5.19 | 6.6 | 120 | -1.41 | 0 | 6.615 | 8.025 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 3.395 | 8.585 | 6.6 | 120 | 1.985 | 0 | 6.615 | 4.63
| Nom. capacity LV, MVA | 6,3+10,0 | 0.62 | 3 | 45 | -2.38 | 0 | 6.615 | 8.995 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 0.629 | 3 | 45 | -2.371 | 0 | 6.615 | 8.986
32 | SS 110/10 Martovskaya | 2*6,3 | 0.61 | 0.55 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | available | 32 | SS 110/10 Martovskaya | 2*6,3 | 0.371 | 0.981 | 0.55 | 120 | 0.431 | 0 | 6.615 | 6.184 | 6.184 | available
33 | SS 110/35/10 Maryino | 10,0+25,0 | 6.09 | 8.11 | 120 | -2.02 | 0 | 10.5 | 12.52 | 11.41 | available | 33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.25 | 6.34 | 8.11 | 120 | -1.77 | 0 | 10.5 | 12.27 | 11.368 | available
| Nom. capacity MV, MVA | 10,0+25,0 | 3.79 | 4.9 |  | -1.11 | 0 | 10.5 | 11.61 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.208 | 3.998 | 4.9 |  | -0.902 | 0 | 10.5 | 11.402
| Nom. capacity LV, MVA | 10,0+25,0 | 2.3 | 3.21 |  | -0.91 | 0 | 10.5 | 11.41 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.042 | 2.342 | 3.21 |  | -0.868 | 0 | 10.5 | 11.368
34 | SS 110/35/10 Medvenka | 2*10,0 | 7.29 | 19.22 | 120 | -11.93 | 0 | 10.5 | 22.43 | 8.31 | available | 34 | SS 110/35/10 Medvenka | 2*10,0 | 0.715 | 8.005 | 19.22 | 120 | -11.215 | 0 | 10.5 | 21.715 | 8.05 | available
| Nom. capacity MV, MVA | 10 | 2.98 | 17.1 |  | -14.12 | 0 | 10.5 | 24.62 |  |  |  | Nom. capacity MV, MVA | 10 | 0.455 | 3.435 | 17.1 |  | -13.665 | 0 | 10.5 | 24.165
| Nom. capacity LV, MVA | 10 | 4.31 | 2.12 | 120 | 2.19 | 0 | 10.5 | 8.31 |  |  |  | Nom. capacity LV, MVA | 10 | 0.26 | 4.57 | 2.12 | 120 | 2.45 | 0 | 10.5 | 8.05
35 | SS 110/6 Neftyanaya | 2*10,0 | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | available | 35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | available
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 16.25 | 26.86 | 120 | -10.61 | 0 | 16.8 | 27.41 | 12.01 | available | 36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 1.603 | 17.853 | 26.86 | 120 | -9.007 | 0 | 16.8 | 25.807 | 10.469 | available
| Nom. capacity MV, MVA | 16,0 + 25,0 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.062 | 2.062 | 17.4 | 0 | -15.338 | 0 | 16.8 | 32.138
| Nom. capacity LV, MVA | 16,0 + 25,0 | 14.25 | 9.46 |  | 4.79 | 0 | 16.8 | 12.01 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 1.541 | 15.791 | 9.46 |  | 6.331 | 0 | 16.8 | 10.469
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 11.36 | 15.5 | 120 | -4.14 | 0 | 16.8 | 20.94 | 14.38 | available | 37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.864 | 12.224 | 15.5 | 120 | -3.276 | 0 | 16.8 | 20.076 | 13.704 | available
| Nom. capacity MV, MVA | 16 | 7.93 | 14.5 |  | -6.57 | 0 | 16.8 | 23.37 |  |  |  | Nom. capacity MV, MVA | 16 | 0.188 | 8.118 | 14.5 |  | -6.382 | 0 | 16.8 | 23.182
| Nom. capacity LV, MVA | 16 | 3.42 | 1 | 120 | 2.42 | 0 | 16.8 | 14.38 |  |  |  | Nom. capacity LV, MVA | 16 | 0.676 | 4.096 | 1 | 120 | 3.096 | 0 | 16.8 | 13.704
38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 1.76 | 6.31 | 120 | -4.55 | 0 | 6.615 | 11.165 | 7.415 | available | 38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.1244 | 1.8844 | 6.31 | 120 | -4.4256 | 0 | 6.615 | 11.0406 | 7.377 | available
| Nom. capacity MV, MVA | 6.3 | 1.25 | 5 | 120 | -3.75 | 0 | 6.615 | 10.365 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.0864 | 1.3364 | 5 | 120 | -3.6636 | 0 | 6.615 | 10.2786
| Nom. capacity LV, MVA | 6.3 | 0.51 | 1.31 | 120 | -0.8 | 0 | 6.615 | 7.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.038 | 0.548 | 1.31 | 120 | -0.762 | 0 | 6.615 | 7.377
39 | SS 110/10 Paniki | 2 х 2,5 | 0.88 | 0.1 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available | 39 | SS 110/10 Paniki | 2 х 2,5 | 0.03 | 0.91 | 0.1 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | available
40 | SS 110/35/10 Peny | 2 х 16,0 | 5.83 | 6.9 | 120 | -1.07 | 0 | 16.8 | 17.87 | 17.3 | available | 40 | SS 110/35/10 Peny | 2 х 16,0 | 0.459 | 6.289 | 6.9 | 120 | -0.611 | 0 | 16.8 | 17.411 | 16.917 | available
| Nom. capacity MV, MVA | 16 | 3 | 3.5 |  | -0.5 | 0 | 16.8 | 17.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.383 | 3.383 | 3.5 |  | -0.117 | 0 | 16.8 | 16.917
| Nom. capacity LV, MVA | 16 | 2.83 | 3.4 | 120 | -0.57 | 0 | 16.8 | 17.37 |  |  |  | Nom. capacity LV, MVA | 16 | 0.076 | 2.906 | 3.4 | 120 | -0.494 | 0 | 16.8 | 17.294
41 | SS 110/35/10 Pribor | 2 х 25,0 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | available | 41 | SS 110/35/10 Pribor | 2 х 25,0 | 1.8 | 30.99 | 6.5 | 0 | 24.49 | 0 | 26.25 | 1.76 | 1.76 | available
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  | 2: Nom. capacity MV, MVA; 3: 25; 5: 0; Min 8: 0; Min 9: 0; Min 10: 26.25; Min 11: 26.25
| Nom. capacity LV, MVA | 25 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 |  |  |  | Nom. capacity LV, MVA | 25 | 1.8 | 30.99 | 6.5 | 0 | 24.49 | 0 | 26.25 | 1.76
42 | SS 110/10 Progress | 2 х 63,0 | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | available | 42 | SS 110/10 Progress | 2 х 63,0 |  | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | available
43 | SS 110/10 Poultry plant | 6,3 + 10,0 | 6.58 | 0.19 | 0 | 6.39 | 0 | 6.615 | 0.225 | 0.225 | available | 43 | SS 110/10 Poultry plant | 6,3 + 10,0 | 0.223 | 6.803 | 0.19 | 0 | 6.613 | 0 | 6.615 | 0.002 | 0.002 | available
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 3.2 | 15.7 | 120 | -12.5 | 0 | 10.5 | 23 | 15.5 | available | 44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.009 | 3.209 | 15.7 | 120 | -12.491 | 0 | 10.5 | 22.991 | 15.491 | available
| Nom. capacity MV, MVA | 10 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.009 | 1.409 | 6.4 |  | -4.991 | 0 | 10.5 | 15.491
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.8 | 21.4 | 45 | -18.6 | 0 | 6.615 | 25.215 | 9.195 | available | 45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 1.608 | 4.408 | 21.4 | 45 | -16.992 | 0 | 6.615 | 23.607 | 9.092 | available
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.78 | 17.8 |  | -16.02 | 0 | 6.615 | 22.635 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 1.505 | 3.285 | 17.8 |  | -14.515 | 0 | 6.615 | 21.13
| Nom. capacity LV, MVA | 6,3 + 10,0 | 1.02 | 3.6 | 45 | -2.58 | 0 | 6.615 | 9.195 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.103 | 1.123 | 3.6 | 45 | -2.477 | 0 | 6.615 | 9.092
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 19.35 | 3.25 | 10 | 16.1 | 0 | 33.075 | 16.975 | 16.975 | available | 46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 1.1113 | 20.4613 | 3.25 | 10 | 17.2113 | 0 | 33.075 | 15.8637 | 15.8637 | available
| Nom. capacity MV, MVA | 31.5 | 13 | 1.7 |  | 11.3 | 0 | 33.075 | 21.775 |  |  |  | Nom. capacity MV, MVA | 31.5 | 1.0153 | 14.0153 | 1.7 |  | 12.3153 | 0 | 33.075 | 20.7597
| Nom. capacity LV, MVA | 31.5 | 6.35 | 1.55 | 120 | 4.8 | 0 | 33.075 | 28.275 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.096 | 6.446 | 1.55 | 120 | 4.896 | 0 | 33.075 | 28.179
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 15.28 | 11 | 120 | 4.28 | 0 | 16.8 | 12.52 | 12.52 | available | 47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 2.651 | 17.931 | 11 | 120 | 6.931 | 0 | 16.8 | 9.869 | 9.869 | available
| Nom. capacity MV, MVA | 16,0 + 25,0 | 8.41 | 7 |  | 1.41 | 0 | 16.8 | 15.39 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 2.583 | 10.993 | 7 |  | 3.993 | 0 | 16.8 | 12.807
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.87 | 4 | 120 | 2.87 | 0 | 16.8 | 13.93 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.068 | 6.938 | 4 | 120 | 2.938 | 0 | 16.8 | 13.862
48 | SS 110/10 Solovyinaya | 2 х 25,0 | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | available | 48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | available
49 | SS 110/10 STK | 2 х 10,0 | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 | 9.28 | available | 49 | SS 110/10 STK | 2 х 10,0 | 0.028 | 1.248 | 0 | 0 | 1.248 | 0 | 10.5 | 9.252 | 9.252 | available
50 | SS 110/10 Studenok | 2 х 6,3 | 2.08 | 0.7 | 120 | 1.38 | 0 | 6.615 | 5.235 | 5.235 | available | 50 | SS 110/10 Studenok | 2 х 6,3 | 0.187 | 2.267 | 0.7 | 120 | 1.567 | 0 | 6.615 | 5.048 | 5.048 | available
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 15.6 | 29 | 120 | -13.4 | 0 | 26.25 | 39.65 | 27.95 | available | 51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.8648 | 17.4648 | 29 | 120 | -11.5352 | 0 | 26.25 | 37.7852 | 26.92 | available
| Nom. capacity MV, MVA | 25 | 5.4 | 17.1 |  | -11.7 | 0 | 26.25 | 37.95 |  |  |  | Nom. capacity MV, MVA | 25 | 0.8348 | 6.2348 | 17.1 |  | -10.8652 | 0 | 26.25 | 37.1152
| Nom. capacity LV, MVA | 25 | 10.2 | 11.9 |  | -1.7 | 0 | 26.25 | 27.95 |  |  |  | Nom. capacity LV, MVA | 25 | 1.03 | 11.23 | 11.9 |  | -0.67 | 0 | 26.25 | 26.92
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | available | 52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 8.3663 | 21.9663 | 0 | 0 | 21.9663 | 0 | 26.25 | 4.2837 | 4.2837 | available
| Nom. capacity MV, MVA | 25 | 3.67 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, MVA | 25 | 2.8663 | 6.5363 |  |  | 6.5363 | 0 | 26.25 | 19.7137
| Nom. capacity LV, MVA | 25 | 9.93 | 0 | 0 | 9.93 | 0 | 26.25 | 16.32 |  |  |  | Nom. capacity LV, MVA | 25 | 5.5 | 15.43 | 0 | 0 | 15.43 | 0 | 26.25 | 10.82
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 3.87 | 3.44 | 120 | 0.43 | 0 | 10.5 | 10.07 | 8.57 | available | 53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.072 | 3.942 | 3.44 | 120 | 0.502 | 0 | 10.5 | 9.998 | 8.522 | available
| Nom. capacity MV, MVA | 10 | 0.5 | 2 |  | -1.5 | 0 | 10.5 | 12 |  |  |  | Nom. capacity MV, MVA | 10 | 0.024 | 0.524 | 2 |  | -1.476 | 0 | 10.5 | 11.976
| Nom. capacity LV, MVA | 10 | 3.37 | 1.44 |  | 1.93 | 0 | 10.5 | 8.57 |  |  |  | Nom. capacity LV, MVA | 10 | 0.048 | 3.418 | 1.44 |  | 1.978 | 0 | 10.5 | 8.522
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 4.72 | 9.59 | 120 | -4.87 | 0 | 6.615 | 11.485 | 6.525 | available | 54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.6504 | 5.3704 | 9.59 | 120 | -4.2196 | 0 | 6.615 | 10.8346 | 6.412 | available
| Nom. capacity MV, MVA | 6,3 + 16,0 | 4.13 | 9.09 |  | -4.96 | 0 | 6.615 | 11.575 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.5374 | 4.6674 | 9.09 |  | -4.4226 | 0 | 6.615 | 11.0376
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.59 | 0.5 | 120 | 0.09 | 0 | 6.615 | 6.525 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.113 | 0.703 | 0.5 | 120 | 0.203 | 0 | 6.615 | 6.412
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.63 | 0.5 | 120 | 0.13 | 0 | 10.5 | 10.37 | 10.04 | available | 55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.213 | 0.843 | 0.5 | 120 | 0.343 | 0 | 10.5 | 10.157 | 9.884 | available
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.46 |  |  | 0.46 | 0 | 10.5 | 10.04 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0.156 | 0.616 |  |  | 0.616 | 0 | 10.5 | 9.884
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.17 | 0.5 | 120 | -0.33 | 0 | 10.5 | 10.83 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.057 | 0.227 | 0.5 | 120 | -0.273 | 0 | 10.5 | 10.773
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 6.29 | 17.4 | 120 | -11.11 | 0 | 16.8 | 27.91 | 16.96 | available | 56 | SS 110/35/10 Fatezh | 2 х 16,0 | 4.6365 | 10.9265 | 17.4 | 120 | -6.4735 | 0 | 16.8 | 23.2735 | 14.8475 | available
| Nom. capacity MV, MVA | 16 | 1.85 | 12.8 |  | -10.95 | 0 | 16.8 | 27.75 |  |  |  | Nom. capacity MV, MVA | 16 | 2.524 | 4.374 | 12.8 |  | -8.426 | 0 | 16.8 | 25.226
| Nom. capacity LV, MVA | 16 | 4.44 | 4.6 | 120 | -0.16 | 0 | 16.8 | 16.96 |  |  |  | Nom. capacity LV, MVA | 16 | 2.1125 | 6.5525 | 4.6 | 120 | 1.9525 | 0 | 16.8 | 14.8475
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 4.33 | 12.34 | 120 | -8.01 | 0 | 26.25 | 34.26 | 25.08 | available | 57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.285 | 4.615 | 12.34 | 120 | -7.725 | 0 | 26.25 | 33.975 | 24.992 | available
| Nom. capacity MV, MVA | 25 | 2.94 | 12.12 |  | -9.18 | 0 | 26.25 | 35.43 |  |  |  | Nom. capacity MV, MVA | 25 | 0.197 | 3.137 | 12.12 |  | -8.983 | 0 | 26.25 | 35.233
| Nom. capacity LV, MVA | 25 | 1.39 | 0.22 | 10 | 1.17 | 0 | 26.25 | 25.08 |  |  |  | Nom. capacity LV, MVA | 25 | 0.088 | 1.478 | 0.22 | 10 | 1.258 | 0 | 26.25 | 24.992
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 3.15 | 6.3 | 80 | -3.15 | 0 | 7.875 | 11.025 | 7.985 | available | 58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.931 | 4.081 | 6.3 | 80 | -2.219 | 0 | 7.875 | 10.094 | 7.141 | available
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.86 | 3.9 |  | -3.04 | 0 | 7.875 | 10.915 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.087 | 0.947 | 3.9 |  | -2.953 | 0 | 7.875 | 10.828
| Nom. capacity LV, MVA | 7,5 + 10,0 | 2.29 | 2.4 | 80 | -0.11 | 0 | 7.875 | 7.985 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.844 | 3.134 | 2.4 | 80 | 0.734 | 0 | 7.875 | 7.141
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 3.24 | 9.38 | 10 | -6.14 | 0 | 16.8 | 22.94 | 16.01 | available | 59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.8875 | 4.1275 | 9.38 | 10 | -5.2525 | 0 | 16.8 | 22.0525 | 15.6055 | available
| Nom. capacity MV, MVA | 16 | 2.16 | 9.09 |  | -6.93 | 0 | 16.8 | 23.73 |  |  |  | Nom. capacity MV, MVA | 16 | 0.483 | 2.643 | 9.09 |  | -6.447 | 0 | 16.8 | 23.247
| Nom. capacity LV, MVA | 16 | 1.08 | 0.29 | 120 | 0.79 | 0 | 16.8 | 16.01 |  |  |  | Nom. capacity LV, MVA | 16 | 0.4045 | 1.4845 | 0.29 | 120 | 1.1945 | 0 | 16.8 | 15.6055
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 2.7 | 8.25 | 120 | -5.55 | 0 | 6.615 | 12.165 | 7.025 | available | 60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.164 | 2.864 | 8.25 | 120 | -5.386 | 0 | 6.615 | 12.001 | 6.997 | available
| Nom. capacity MV, MVA | 6.3 | 1.86 | 7 |  | -5.14 | 0 | 6.615 | 11.755 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.136 | 1.996 | 7 |  | -5.004 | 0 | 6.615 | 11.619
| Nom. capacity LV, MVA | 6.3 | 0.84 | 1.25 | 129 | -0.41 | 0 | 6.615 | 7.025 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.028 | 0.868 | 1.25 | 129 | -0.382 | 0 | 6.615 | 6.997
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 4.6 | 13.73 | 120 | -9.13 | 0 | 10.5 | 19.63 | 11.83 | available | 61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.649 | 5.249 | 13.73 | 120 | -8.481 | 0 | 10.5 | 18.981 | 11.694 | available
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3 |  |  |  | Nom. capacity MV, MVA | 10 | 0.513 | 3.913 | 11.2 |  | -7.287 | 0 | 10.5 | 17.787
| Nom. capacity LV, MVA | 10 | 1.2 | 2.53 | 120 | -1.33 | 0 | 10.5 | 11.83 |  |  |  | Nom. capacity LV, MVA | 10 | 0.136 | 1.336 | 2.53 | 120 | -1.194 | 0 | 10.5 | 11.694
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 10.49 | 12.9 | 120 | -2.41 | 0 | 26.25 | 28.66 | 21.53 | available | 62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.84 | 11.33 | 12.9 | 120 | -1.57 | 0 | 26.25 | 27.82 | 21.251 | available
| Nom. capacity MV, MVA | 25 | 4.99 | 12.12 |  | -7.13 | 0 | 26.25 | 33.38 |  |  |  | Nom. capacity MV, MVA | 25 | 0.561 | 5.551 | 12.12 |  | -6.569 | 0 | 26.25 | 32.819
| Nom. capacity LV, MVA | 25 | 5.5 | 0.78 | 120 | 4.72 | 0 | 26.25 | 21.53 |  |  |  | Nom. capacity LV, MVA | 25 | 0.279 | 5.779 | 0.78 | 120 | 4.999 | 0 | 26.25 | 21.251
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.875 | 11.625 | 6.83 | available | 63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 1.2223 | 3.7822 | 6.31 | 10 | -2.5278 | 0 | 7.875 | 10.4027 | 6.407 | available
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.26 | 6.06 |  | -4.8 | 0 | 7.88 | 12.68 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.79925 | 2.0593 | 6.06 |  | -4.0008 | 0 | 7.88 | 11.8808
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.3 | 0.25 | 10 | 1.05 | 0 | 7.88 | 6.83 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.423 | 1.723 | 0.25 | 10 | 1.473 | 0 | 7.88 | 6.407
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 64 | SS 35/10 Amosovka | 2 х 2,5 | 0.018 | 0.378 | 0.2 | 120 | 0.178 | 0 | 2.625 | 2.447 | 2.447 | available
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.45 | 0.37 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | available | 65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.023 | 0.473 | 0.37 | 120 | 0.103 | 0 | 1.68 | 1.577 | 1.577 | available
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | available | 66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 0.055 | 1.275 | 1.1 | 80 | 0.175 | 0 | 4.2 | 4.025 | 4.025 | available
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.2 | 1.43 | 120 | -1.23 | 0 | 1.68 | 2.91 | 2.91 | available | 67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.062 | 0.262 | 1.43 | 120 | -1.168 | 0 | 1.68 | 2.848 | 2.848 | available
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.47 | 6.1 | 0 | -5.63 | 0 | 4.2 | 9.83 | 9.83 | available | 68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.64 | 1.11 | 6.1 | 0 | -4.99 | 0 | 4.2 | 9.19 | 9.19 | available
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.08 | 0.15 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | available | 69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.0268 | 0.1068 | 0.15 | 120 | -0.0432 | 0 | 1.05 | 1.0932 | 1.0932 | available
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 1.05 | 0.29 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available | 70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.107 | 1.157 | 0.29 | 120 | 0.867 | 0 | 2.625 | 1.758 | 1.758 | available
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.109 | 0.509 | 0.41 | 120 | 0.099 | 0 | 2.625 | 2.526 | 2.526 | available
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 1.37 | 0.4 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | available | 72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.581 | 1.951 | 0.4 | 120 | 1.551 | 0 | 4.2 | 2.649 | 2.649 | available
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.55 | 0.22 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | available | 73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.465 | 1.015 | 0.22 | 120 | 0.795 | 0 | 1.68 | 0.885 | 0.885 | available
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.4 | 0.46 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | available | 74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.0674 | 0.4674 | 0.46 | 120 | 0.0074 | 0 | 2.625 | 2.6176 | 2.6176 | available
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.4 | 0 | 0 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | available | 75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.033 | 0.433 | 0 | 0 | 0.433 | 0 | 4.2 | 3.767 | 3.767 | available
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 2.37 | 0.46 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | available | 76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.3766 | 2.7466 | 0.46 | 120 | 2.2866 | 0 | 6.615 | 4.3284 | 4.3284 | available
77 | SS 35/10 Vygornoe | 2 х 2,5 | 1.38 | 0.51 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | available | 77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.222 | 1.602 | 0.51 | 120 | 1.092 | 0 | 2.625 | 1.533 | 1.533 | available
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.44 | 0.17 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | available | 78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.017 | 0.457 | 0.17 | 120 | 0.287 | 0 | 1.68 | 1.393 | 1.393 | available
79 | SS 35/10 Gorodok | 2 х 4,0 | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | available | 79 | SS 35/10 Gorodok | 2 х 4,0 |  | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | available
80 | SS 35/10 Guevo | 2 х 2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.625 | 3.115 | 3.115 | available | 80 | SS 35/10 Guevo | 2 х 2,5 | 0.036 | 1.236 | 1.69 | 20 | -0.454 | 0 | 2.625 | 3.079 | 3.079 | available
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.2 | 0.38 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | available | 81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.242 | 0.38 | 120 | -0.138 | 0 | 1.68 | 1.818 | 1.818 | available
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 3.44 | 3.5 | 0 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | available | 82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 3.555 | 3.5 | 0 | 0.055 | 0 | 2.625 | 2.57 | 2.57 | available
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.86 | 0.26 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available | 83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.865 | 0.26 | 120 | 0.605 | 0 | 2.625 | 2.02 | 2.02 | available
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 10.39 | 2.5 | 0 | 7.89 | 0 | 10.5 | 2.61 | 2.61 | available | 84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 10.4 | 2.5 | 0 | 7.9 | 0 | 10.5 | 2.6 | 2.6 | available
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.98 | 1.67 | 0 | -0.69 | 0 | 4.2 | 4.89 | 4.89 | available | 85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.673 | 1.653 | 1.67 | 0 | -0.017 | 0 | 4.2 | 4.217 | 4.217 | available
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.231 | 1.131 | 0.93 | 45 | 0.201 | 0 | 1.68 | 1.479 | 1.479 | available
87 | SS 35/10 Ivanino | 2 х 6,3 | 2.29 | 2.69 | 80 | -0.4 | 0 | 6.615 | 7.015 | 7.015 | available | 87 | SS 35/10 Ivanino | 2 х 6,3 | 0.238 | 2.528 | 2.69 | 80 | -0.162 | 0 | 6.615 | 6.777 | 6.777 | available
88 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 1.89 | 1.99 | 1.99 | available | 88 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.0034 | 0.4034 | 0.5 | 120 | -0.0966 | 0 | 1.89 | 1.9866 | 1.9866 | available
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.33 | 0.52 | 120 | -0.19 | 0 | 1.68 | 1.87 | 1.87 | available | 89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.345 | 0.52 | 120 | -0.175 | 0 | 1.68 | 1.855 | 1.855 | available
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 9.78 | 6.25 | 20 | 3.53 | 0 | 10.5 | 6.97 | 6.97 | available | 90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 10.189 | 6.25 | 20 | 3.939 | 0 | 10.5 | 6.561 | 6.561 | available
91 | SS 35/10 Mixed fodder plant | 4,0+6,3 | 0.49 | 0 | 0 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | available | 91 | SS 35/10 Mixed fodder plant | 4,0+6,3 | 0.013 | 0.503 | 0 | 0 | 0.503 | 0 | 4.2 | 3.697 | 3.697 | available
92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 3.1 | 0.21 | 120 | 2.89 | 0 | 6.615 | 3.725 | 3.725 | available | 92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.129 | 3.229 | 0.21 | 120 | 3.019 | 0 | 6.615 | 3.596 | 3.596 | available
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 2.19 | 1.14 | 80 | 1.05 | 0 | 3.36 | 2.31 | 2.31 | available | 93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 0.514 | 2.704 | 1.14 | 80 | 1.564 | 0 | 3.36 | 1.796 | 1.796 | available
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 4.35 | 1.56 | 80 | 2.79 | 0 | 4.2 | 1.41 | 1.41 | available | 94 | SS 35/10 Korenevo | 4,0 + 6,3 | 2.05 | 6.4 | 1.56 | 80 | 4.84 | 0 | 4.2 | -0.64 | -0.64 | available
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.62 | 0.24 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available | 95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.013 | 0.633 | 0.24 | 120 | 0.393 | 0 | 2.625 | 2.232 | 2.232 | available
96 | SS 35/10 Krupets | 1,8 + 2,5 | 1.5 | 0.42 | 120 | 1.08 | 0 | 1.89 | 0.81 | 0.81 | available | 96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.18 | 1.68 | 0.42 | 120 | 1.26 | 0 | 1.89 | 0.63 | 0.63 | available
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.7 | 0.6 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.981 | 1.681 | 0.6 | 120 | 1.081 | 0 | 2.625 | 1.544 | 1.544 | available
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.14 | 0.17 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | available | 98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.008 | 0.148 | 0.17 | 120 | -0.022 | 0 | 2.625 | 2.647 | 2.647 | available
99 | SS 35/10 Kurchatov | 2 х 10,0 | 4.52 | 4.5 | 80 | 0.02 | 0 | 10.5 | 10.48 | 10.48 | available | 99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 4.525 | 4.5 | 80 | 0.025 | 0 | 10.5 | 10.475 | 10.475 | available
100 | SS 35/10 Kutok | 2 х 2,5 | 0.08 | 0.05 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | available | 100 | SS 35/10 Kutok | 2 х 2,5 | 0.009 | 0.089 | 0.05 | 120 | 0.039 | 0 | 2.625 | 2.586 | 2.586 | available
101 | SS 35/10 Linets | 2 х 2,5 | 0.23 | 0.25 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available | 101 | SS 35/10 Linets | 2 х 2,5 | 1.129 | 1.359 | 0.25 | 120 | 1.109 | 0 | 2.625 | 1.516 | 1.516 | available
102 | SS 35/10 Luch | 2 х 6,3 | 3.03 | 0.23 | 120 | 2.8 | 0 | 6.615 | 3.815 | 3.815 | available | 102 | SS 35/10 Luch | 2 х 6,3 | 0.45589 | 3.4859 | 0.23 | 120 | 3.2559 | 0 | 6.615 | 3.3591 | 3.3591 | available
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | available | 103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.066 | 0.816 | 1.59 | 80 | -0.774 | 0 | 4.2 | 4.974 | 4.974 | available
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.65 | 0.08 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | available | 104 | SS 35/10 Matveevka | 2 х 2,5 | 0.032 | 0.682 | 0.08 | 120 | 0.602 | 0 | 2.625 | 2.023 | 2.023 | available
105 | SS 35/10 Mayak | 2 х 2,5 | 0.5 | 0.3 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 105 | SS 35/10 Mayak | 2 х 2,5 | 0.031 | 0.531 | 0.3 | 120 | 0.231 | 0 | 2.625 | 2.394 | 2.394 | available
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 1.27 | 1.7 | 80 | -0.43 | 0 | 4.2 | 4.63 | 4.63 | available | 106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.3423 | 1.6123 | 1.7 | 80 | -0.0877 | 0 | 4.2 | 4.2877 | 4.2877 | available
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.87 | 0.3 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available | 107 | SS 35/10 Murynovka | 2 х 4,0 | 0.346 | 1.216 | 0.3 | 120 | 0.916 | 0 | 4.2 | 3.284 | 3.284 | available
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.51 | 0.63 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 108 | SS 35/10 N. Borki | 2 х 2,5 | 0.08032 | 0.59032 | 0.63 | 120 | -0.03968 | 0 | 2.625 | 2.6647 | 2.6647 | available
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.4 | 0.03 | 80 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | available | 109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.007 | 0.407 | 0.03 | 80 | 0.377 | 0 | 1.68 | 1.303 | 1.303 | available
110 | SS 35/10 Novaya | 2 х 2,5 | 1.2 | 0.4 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 110 | SS 35/10 Novaya | 2 х 2,5 | 0.323 | 1.523 | 0.4 | 120 | 1.123 | 0 | 2.625 | 1.502 | 1.502 | available
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.56 | 0.19 | 120 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available | 111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.059 | 0.619 | 0.19 | 120 | 0.429 | 0 | 2.625 | 2.196 | 2.196 | available
112 | SS 35/10 Orlovka | 2 х 2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.625 | 2.975 | 2.975 | available | 112 | SS 35/10 Orlovka | 2 х 2,5 | 2.574 | 2.744 | 0.52 | 120 | 2.224 | 0 | 2.625 | 0.401 | 0.401 | available
113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.18 | 0.2 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | available | 113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.14 | 0.32 | 0.2 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.26 | 0.74 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available | 114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.247 | 1.507 | 0.74 | 120 | 0.767 | 0 | 4.2 | 3.433 | 3.433 | available
115 | SS 35/10 Panino | 2 х 2,5 | 0.28 | 0.11 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 115 | SS 35/10 Panino | 2 х 2,5 | 0.047 | 0.327 | 0.11 | 80 | 0.217 | 0 | 2.625 | 2.408 | 2.408 | available
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.62 | 0.52 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.077 | 0.697 | 0.52 | 120 | 0.177 | 0 | 2.625 | 2.448 | 2.448 | available
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.61 | 0.3 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | available | 117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.751 | 2.361 | 0.3 | 120 | 2.061 | 0 | 2.625 | 0.564 | 0.564 | available
118 | SS 35/10 Platava | 2 х 2,5 | 1.38 | 0.26 | 120 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | available | 118 | SS 35/10 Platava | 2 х 2,5 | 0.014 | 1.394 | 0.26 | 120 | 1.134 | 0 | 2.625 | 1.491 | 1.491 | available
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.19 | 0.46 | 120 | -0.27 | 0 | 1.68 | 1.95 | 1.95 | available | 119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.237 | 0.46 | 120 | -0.223 | 0 | 1.68 | 1.903 | 1.903 | available
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | available | 120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.061 | 0.561 | 1.16 | 120 | -0.599 | 0 | 4.2 | 4.799 | 4.799 | available
121 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available | 121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | available
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 1.39 | 0.3 | 80 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | available | 122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.339 | 1.729 | 0.3 | 80 | 1.429 | 0 | 2.625 | 1.196 | 1.196 | available
123 | SS 35/10 Pselets | 2 х 1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.39 | 0.43 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | available | 124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.081 | 0.471 | 0.43 | 120 | 0.041 | 0 | 1.68 | 1.639 | 1.639 | available
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.77 | 0.32 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available | 125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.203 | 0.973 | 0.32 | 120 | 0.653 | 0 | 2.625 | 1.972 | 1.972 | available
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.38 | 0.44 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | available | 126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.597 | 0.977 | 0.44 | 120 | 0.537 | 0 | 2.625 | 2.088 | 2.088 | available
127 | SS 35/10 Razvetye | 2 х 4,0 | 1.91 | 1.03 | 120 | 0.88 | 0 | 4.2 | 3.32 | 3.32 | available | 127 | SS 35/10 Razvetye | 2 х 4,0 | 0.673 | 2.583 | 1.03 | 120 | 1.553 | 0 | 4.2 | 2.647 | 2.647 | available
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.74 | 0.11 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | available | 128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.03 | 0.77 | 0.11 | 120 | 0.66 | 0 | 4.2 | 3.54 | 3.54 | available
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.28 | 0.29 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available | 129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.121 | 0.401 | 0.29 | 120 | 0.111 | 0 | 1.68 | 1.569 | 1.569 | available
130 | SS 35/10 Rubilnik | 2 х 2,5 | 1.25 | 1.18 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.058 | 1.308 | 1.18 | 80 | 0.128 | 0 | 2.625 | 2.497 | 2.497 | available
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.28 | 0.08 | 20 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | available | 131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.015 | 0.295 | 0.08 | 20 | 0.215 | 0 | 1.68 | 1.465 | 1.465 | available
132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.39 | 0.6 | 20 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.5109 | 2.9009 | 0.6 | 20 | 2.3009 | 0 | 2.625 | 0.3241 | 0.3241 | available
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 4.41 | 2.25 | 80 | 2.16 | 0 | 6.615 | 4.455 | 4.455 | available | 133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.422 | 4.832 | 2.25 | 80 | 2.582 | 0 | 6.615 | 4.033 | 4.033 | available
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.09 | 1.4 | 45 | 0.69 | 0 | 4.2 | 3.51 | 3.51 | available | 134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.086 | 2.176 | 1.4 | 45 | 0.776 | 0 | 4.2 | 3.424 | 3.424 | available
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.4 | 0 | - | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.096 | 0.496 | 0 | - | 0.496 | 0 | 2.625 | 2.129 | 2.129 | available
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.51 | 0.6 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | available | 136 | SS 35/10 Seed plant | 2 х 2,5 | 0.124 | 0.634 | 0.6 | 120 | 0.034 | 0 | 2.625 | 2.591 | 2.591 | available
137 | SS 35/10 Snagost | 2 х 4,0 | 1.31 | 0.05 | 10 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | available | 137 | SS 35/10 Snagost | 2 х 4,0 | 0.106 | 1.416 | 0.05 | 10 | 1.366 | 0 | 4.2 | 2.834 | 2.834 | available
138 | SS 35/10 SOM | 1,6 + 4,0 | 1.03 | 0.08 | 10 | 0.95 | 0 | 1.68 | 0.73 | 0.73 | available | 138 | SS 35/10 SOM | 1,6 + 4,0 | 0.1155 | 1.1455 | 0.08 | 10 | 1.0655 | 0 | 1.68 | 0.6145 | 0.6145 | available
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.77 | 0.69 | 120 | 0.08 | 0 | 3.36 | 3.28 | 3.28 | available | 139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.183 | 0.953 | 0.69 | 120 | 0.263 | 0 | 3.36 | 3.097 | 3.097 | available
140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.65 | 0.58 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.09 | 0.74 | 0.58 | 80 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.2 | 0.2 | 80 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 141 | SS 35/10 Starkovo | 2 х 1,6 | 0.015 | 0.215 | 0.2 | 80 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | available
142 | CC 35/10 Starshee | 2 х 1,6 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | available | 142 | CC 35/10 Starshee | 2 х 1,6 | 0.019 | 0.259 | 0.2 | 120 | 0.059 | 0 | 1.68 | 1.621 | 1.621 | available
143 | SS 35/10 Teplitsy | 2 х 4,0 | 2.02 | 1.08 | 45 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | available | 143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.143 | 2.163 | 1.08 | 45 | 1.083 | 0 | 4.2 | 3.117 | 3.117 | available
144 | SS 35/10 Turovka | 2 х 2,5 | 0.44 | 0.6 | 120 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | available | 144 | SS 35/10 Turovka | 2 х 2,5 | 0.065 | 0.505 | 0.6 | 120 | -0.095 | 0 | 2.625 | 2.72 | 2.72 | available
145 | SS 35/10 Uspenka | 2 х 2,5 | 1.11 | 1 | 80 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 145 | SS 35/10 Uspenka | 2 х 2,5 | 0.186 | 1.296 | 1 | 80 | 0.296 | 0 | 2.625 | 2.329 | 2.329 | available
146 | SS 35/6 Tsentralnaya | 2 х 40,0 | 22.44 | 5 |  | 17.44 | 0 | 42 | 24.56 | 24.56 | available | 146 | SS 35/6 Tsentralnaya | 2 х 40,0 | 0.008 | 22.448 | 5 |  | 17.448 | 0 | 42 | 24.552 | 24.552 | available
147 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | available | 147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | available
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.38 | 0.21 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.085 | 0.465 | 0.21 | 80 | 0.255 | 0 | 2.625 | 2.37 | 2.37 | available
149 | SS 35/10 Shipy | 2 х 2,5 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.112 | 0.3 | 120 | -0.188 | 0 | 2.625 | 2.813 | 2.813 | available
150 | SS 35/10 Elevator | 4,0 + 6,3 | 1.53 | 0.6 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | available | 150 | SS 35/10 Elevator | 4,0 + 6,3 | 0.0592 | 1.5892 | 0.6 | 120 | 0.9892 | 0 | 4.2 | 3.2108 | 3.2108 | available
151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.43 | 4.7 | 80 | 3.73 | 0 | 10.5 | 6.77 | 6.77 | available | 151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 2.35 | 10.78 | 4.7 | 80 | 6.08 | 0 | 10.5 | 4.42 | 4.42 | available
152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 2.46 | 3.9 | 120 | -1.44 | 0 | 2.625 | 4.065 | 4.065 | available | 152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 0.186 | 2.646 | 3.9 | 120 | -1.254 | 0 | 2.625 | 3.879 | 3.879 | available
| TOTAL: | 3185.9 | 761.961 | 778.18 | [5 empty] | 1237.834 |  | 2: TOTAL:; 3: 3185.9; 4: 143.7635; 5: 905.7245; MVA 6: 784.07; Min 12: 1167.2415
| deficit | [8 empty] | -7.475 |  | 2: deficit; Min 12: -33.709
| proficit | [8 empty] | 1230.354 |  | 2: proficit; Min 12: 1133.5325