## Yaroslavl
[14 empty] | Table 1 | [13 empty] | Table 2
No. | Name of supply center, voltage class | Текущий дефицит | [13 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | tg (по счетчикам) | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | available | 1 | SS 35/10 Matveevo | 1.6 | 0.02 | 0.28 | 0.779 | 1 day and night | 0.28 | 0 | 0.779 | 0.499 | 0.499 | available
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | available | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | available
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 0.275 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | unavailable | 3 | SS 35/10 Shirinye | 2.5 | 0.267 | 2.417 | 1.68 | 1 day and night | 2.417 | 0 | 1.68 | -0.737 | -0.737 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | available | 4 | SS 110/10 Pokrov | 2.5 | 0.016 | 0.286 | 1.282 | 1 day and night | 0.286 | 0 | 1.282 | 0.996 | 0.996 | available
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | available | 5 | SS 35/10 Obnora | 1.6 | 0.063 | 0.263 | 1.212 | 1 day and night | 0.263 | 0 | 1.212 | 0.949 | 0.949 | available
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 | [5 empty] | 10.09 | 0 | 10.5 | 0.41 | 0.41 | available | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 21.5191 |  |  | 21.5191 | 0 | 10.5 | -11.0191 | -11.0191 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  | Min 7: 8.12; Min 8: 0; Min 9: 10.5; Min 10: 2.38 |  | Nom. capacity MV, МVА | 10+10 |  | 17.2797 |  |  | 17.2797 | 0 | 10.5 | -6.7796
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  | Min 7: 1.97; Min 8: 0; Min 9: 10.5; Min 10: 8.53 |  | Nom. capacity LV, МVА | 10+10 | 2.2695 | 4.2395 |  |  | 4.2395 | 0 | 10.5 | 6.2605
7 | SS 35/10 Ananyino | 2,5+1,6 | 2.5 | 1.6 | 1.31 | 0.82 | 0.49 |  |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | available | 7 | SS 35/10 Ananyino | 1,6+1,6 | 1.059 | 2.369 |  |  | 2.369 | 0 | 1.68 | -0.689 | -0.689 | unavailable
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 |  | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | available | 8 | SS 110/10/10 Bragino | 40+40 | 3.724 | 38.634 | 2.338 | 120 | 36.296 | 0 | 42 | 5.704 | 5.704 | available
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 |  | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | available | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 1.039 | 3.069 | 0.554 | 120 | 2.515 | 0 | 4.2 | 1.685 | 1.685 | available
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | available | 10 | SS 35/10 Vatolino | 4,0+4,0 | 3.957 | 7.377 |  |  | 7.377 | 0 | 4.2 | -3.177 | -3.177 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | available | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.091258 | 4.2113 |  |  | 4.2113 | 0 | 6.62 | 2.4087 | 2.4087 | available
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | available | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.129 | 2.099 |  |  | 2.099 | 0 | 4.2 | 2.101 | 2.101 | available
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | available | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.072 | 0.782 |  |  | 0.782 | 0 | 1.68 | 0.898 | 0.898 | available
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | available | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 3.1764 | 4.3464 |  |  | 4.3464 | 0 | 4.2 | -0.1464 | -0.1464 | unavailable
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | available | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | available
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 |  | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | available | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.32 | 2.53 | 0.139 | 120 | 2.391 | 0 | 2.63 | 0.239 | 0.239 | available
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 |  | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | available | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.089 | 0.749 | 0.329 | 120 | 0.42 | 0 | 2.63 | 2.21 | 2.21 | available
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 |  | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | available | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.898 | 3.508 | 0.312 | 120 | 3.196 | 0 | 4.2 | 1.004 | 1.004 | available
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 |  | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | available | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 5.5379 | 8.4079 | 0.866 | 120 | 7.5419 | 0 | 4.2 | -3.3419 | -3.3419 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | available | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | available
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | available | 21 | SS 110/6 Depo | 16+16 | 2.7977 | 9.8677 |  |  | 9.8677 | 0 | 16.8 | 6.9323 | 6.9323 | available
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 |  | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | available | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.838 | 3.428 | 1.039 | 120 | 2.389 | 0 | 1.68 | -0.709 | -0.709 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 |  | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | available | 23 | SS 110/10 Druzhba | 16+16 | 0.7253 | 6.2353 | 1.932 | 120 | 4.3033 | 0 | 16.8 | 12.4967 | 12.4967 | available
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 |  | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | available | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.8835 | 5.7535 | 1.386 | 120 | 4.3675 | 0 | 6.62 | 2.2525 | 2.2525 | available
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | available | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.5 | 1.73 |  |  | 1.73 | 0 | 2.63 | 0.9 | 0.9 | available
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | available | 26 | SS 35/6 Zavolzhskaya | 10+10 | 0.8721 | 10.5921 |  |  | 10.5921 | 0 | 10.5 | -0.092098 | -0.092098 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | available | 27 | SS 110/6/6 Institutskaya | 40+40 | 2.5793 | 34.4093 |  |  | 34.4093 | 0 | 42 | 7.5907 | 7.5907 | available
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 |  | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | available | 28 | SS 35/10 Koza | 1,6+1,6 | 0.053 | 0.353 | 0.052 | 120 | 0.301 | 0 | 1.68 | 1.379 | 1.379 | available
29 | SS 110/35/6 Konstantinovo | 20+16 | 20 | 16 | 10.56 |  |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | available | 29 | SS 110/35/6 Konstantinovo | 20+16 |  | 13.127 | 0.021 | 120 | 13.106 | 0 | 16.8 | 3.694 | 3.694 | available
| Nom. capacity MV, МVА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  | Min 7: 7.47; Min 8: 0; Min 9: 16.8; Min 10: 9.33 |  | Nom. capacity MV, МVА | 20+16 |  | 9.585 |  |  | 9.585 | 0 | 16.8 | 7.215
| Nom. capacity LV, МVА | 20+16 |  |  | 3.09 | 2.1 | 0.99 |  | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Nom. capacity LV, МVА | 20+16 | 0.452 | 3.542 | 0.021 | 120 | 3.521 | 0 | 16.8 | 13.279
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 |  | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | available | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.431 | 2.911 | 0.242 | 120 | 2.669 | 0 | 2.63 | -0.039 | -0.039 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 |  | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | available | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.327 | 8.407 | 1.212 | 120 | 7.195 | 0 | 10.5 | 3.305 | 3.305 | available
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 |  | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | available | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.2307 | 12.0807 | 2.338 | 120 | 9.7427 | 0 | 6.62 | -3.1227 | -3.1227 | unavailable
33 | SS 35/10 Nekrasovo | 16+16 | 16 | 16 | 11.17 | 5.47 | 5.7 |  |  |  | 11.17 | 0 | 16.8 | 5.63 | 5.63 | available | 33 | SS 35/10 Nekrasovo | 10+10 | 3.5114 | 14.6814 |  |  | 14.6814 | 0 | 10.5 | -4.1814 | -4.1814 | unavailable
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 |  | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | available | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.091 | 0.821 | 0.398 | 120 | 0.423 | 0 | 2.63 | 2.207 | 2.207 | available
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 | [5 empty] | 15.58 | 0 | 26.25 | 10.67 | 10.67 | available | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.9713 |  |  | 22.9713 | 0 | 26.25 | 3.2787 | 3.2787 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  | Min 7: 8.31; Min 8: 0; Min 9: 26.25; Min 10: 17.94 |  | Nom. capacity MV, МVА | 25+25 |  | 8.4013 |  |  | 8.4013 | 0 | 26.25 | 17.8487
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  | Min 7: 7.27; Min 8: 0; Min 9: 26.25; Min 10: 18.98 |  | Nom. capacity LV, МVА | 25+25 | 7.3 | 14.57 |  |  | 14.57 | 0 | 26.25 | 11.68
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | available | 36 | SS 110/6/6 Orion | 40+40 | 0.67533 | 15.3853 |  |  | 15.3853 | 0 | 42 | 26.6147 | 26.6147 | available
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 | [5 empty] | 23.56 | 0 | 21 | -2.56 | -2.56 | unavailable | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 24.0557 |  |  | 24.0557 | 0 | 21 | -3.0557 | -3.0557 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  | Min 7: 5.71; Min 8: 0; Min 9: 21; Min 10: 15.29 |  | Nom. capacity MV, МVА | 20+25 |  | 6.159 |  |  | 6.159 | 0 | 21 | 14.841
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 | 0.285 | Min 7: 17.85; Min 8: 0; Min 9: 21; Min 10: 3.15 |  | Nom. capaity LV, МVА | 20+25 | 0.046702 | 17.8967 |  |  | 17.8967 | 0 | 21 | 3.1033
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | available | 38 | SS 110/10 Pereval | 16+16 | 7.8703 | 16.3803 |  |  | 16.3803 | 0 | 16.8 | 0.41968 | 0.41968 | available
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | available | 39 | SS 110/6/6 Perekop | 25+25 | 0.3832 | 10.7132 |  |  | 10.7132 | 0 | 26.25 | 15.5368 | 15.5368 | available
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | available | 40 | SS 110/6/6 Poligraf | 40+40 | 2.276 | 36.246 |  |  | 36.246 | 0 | 42 | 5.754 | 5.754 | available
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | available | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.3815 | 0.52 | 120 | 3.8615 | 0 | 10.5 | 6.6385 | 6.6385 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  | Min 7: 1; Min 8: 0; Min 9: 10.5; Min 10: 9.5 |  | Nom. capacity MV, МVА | 10+10 |  | 1.1295 |  |  | 1.1295 | 0 | 10.5 | 9.3705
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 |  | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.432 | 3.252 | 0.52 | 120 | 2.732 | 0 | 10.5 | 7.768
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 |  | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | available | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.7463 | 3.7963 | 0.26 | 120 | 3.5363 | 0 | 2.63 | -0.9063 | -0.9063 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 |  | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | available | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.015 | 0.245 | 0.052 | 120 | 0.193 | 0 | 2.63 | 2.437 | 2.437 | available
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | available | 44 | SS 110/6/6 Severnaya | 63+63 | 4.7209 | 42.7109 |  |  | 42.7109 | 0 | 66.15 | 23.4391 | 23.4391 | available
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 |  | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | available | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.705 | 2.045 | 0.987 | 120 | 1.058 | 0 | 2.63 | 1.572 | 1.572 | available
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | available | 46 | SS 110/6 Tormoznaya | 16+16 | 0.26737 | 14.7754 |  |  | 14.7754 | 0 | 16.8 | 2.0246 | 2.0246 | available
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 |  | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | available | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.012 | 0.352 | 0.277 | 120 | 0.075 | 0 | 2.63 | 2.555 | 2.555 | available
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 |  | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | available | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.435 | 1.125 | 0.191 | 120 | 0.934 | 0 | 2.63 | 1.696 | 1.696 | available
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 | 0.243 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | unavailable | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.334 | 7.594 |  |  | 7.594 | 0 | 6.62 | -0.974 | -0.974 | unavailable
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | available | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.3234 | 1.0434 |  |  | 1.0434 | 0 | 2.63 | 1.5866 | 1.5866 | available
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 |  | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | available | 52 | SS 35/10 Urozhay | 4,0+4,0 | 1.019 | 2.599 | 0.346 | 120 | 2.253 | 0 | 4.2 | 1.947 | 1.947 | available
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | 2.92 |  |  |  | Min 11: 2.83; Min 12: available | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8375 |  |  |  | 0 |  |  | 2.7825 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 2.13 |  | 2.13 | [10 empty] | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 |  | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0475 | 0.8375 | 0.26 | 120 | 0.5775 | 0 | 3.36 | 2.7825
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | available | 54 | SS 110/10 Chayka | 25+25 | 1.118 | 20.498 |  |  | 20.498 | 0 | 26.25 | 5.752 | 5.752 | available
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 |  | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | available | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.6 | 3.17 | 0.156 | 120 | 3.014 | 0 | 2.63 | -0.384 | -0.384 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.6935 | 2.1235 |  |  | 2.1235 | 0 | 4.2 | 2.0765 | 2.0765 | available
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | available | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 4.5101 | 36.4901 |  |  | 36.4901 | 0 | 42 | 5.5099 | 5.5099 | available
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | available | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.784 | 7.664 |  |  | 7.664 | 0 | 26.25 | 18.586 | 18.586 | available
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | available | 59 | ПС 110/6/6 Kotorosl | 25+25 | 0.71255 | 6.7525 |  |  | 6.7525 |  | 26.25 | 19.4975 | 19.4975 | available
60 | SS 35/6 Kelnot | 4 | 4 |  | 0.29 | 0.29 |  |  | 4.2 | 1 day and night | 0.29 | 0 | 4.2 | 3.91 | 3.91 | available | 60 | SS 35/6 Kelnot | 4 | 0 | 0.29 | 4.2 | 1 day and night | 0.29 |  | 4.2 | 3.91 | 3.91 | available
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | available | 61 | SS 110/10 Altynovo | 6,3+6,3 | 1.6093 | 4.9093 |  |  | 4.9093 | 0 | 6.62 | 1.7107 | 1.7107 | available
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 | [5 empty] | 7.8 | 0 | 10.5 | 2.7 | 2.7 | available | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 10.7453 |  |  | 10.7453 | 0 | 10.5 | -0.24525 | -0.24525 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  | Min 7: 3.35; Min 8: 0; Min 9: 10.5; Min 10: 7.15 |  | Nom. capacity MV, МVА | 16+10 |  | 4.5491 |  |  | 4.5491 | 0 | 10.5 | 5.9509
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  | Min 7: 4.45; Min 8: 0; Min 9: 10.5; Min 10: 6.05 |  | Nom. capacity LV, МVА | 16+10 | 1.7462 | 6.1962 |  |  | 6.1962 | 0 | 10.5 | 4.3038
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | available | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.644 | 0.537 | 120 | 3.107 | 0 | 10.5 | 7.393 | 7.393 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  | Min 7: 2.1; Min 8: 0; Min 9: 10.5; Min 10: 8.4 |  | Nom. capacity MV, МVА | 10+10 |  | 2.273 |  |  | 2.273 | 0 | 10.5 | 8.227
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 |  | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.071 | 1.371 | 0.537 | 120 | 0.834 | 0 | 10.5 | 9.666
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 |  | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | available | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | available
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 | 0.413 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | unavailable | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | unavailable
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 | [5 empty] | 1.7 | 0 | 6.62 | 4.92 | 4.92 | available | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.789 |  |  | 1.789 | 0 | 6.62 | 4.831 | 4.831 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 0.36 |  | 0.36 |  | Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.391 |  |  | 0.391 | 0 | 6.62 | 6.229
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  | Min 7: 1.34; Min 8: 0; Min 9: 6.62; Min 10: 5.28 |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.058 | 1.398 |  |  | 1.398 | 0 | 6.62 | 5.222
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | unavailable | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 25.8472 | 0.97 | 120 | 24.8772 | 0 | 6.62 | -18.2572 | -18.2572 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  | Min 7: 7.66; Min 8: 0; Min 9: 6.62; Min 10: -1.04 |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.7817 |  |  | 11.7817 | 0 | 6.62 | -5.1617
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.265 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 11.3755 | 14.0655 | 0.97 | 120 | 13.0955 | 0 | 6.62 | -6.4755
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 | [5 empty] | 24.89 | 0 | 26.25 | 1.36 | 1.36 | available | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 36.3255 |  |  | 36.3255 | 0 | 26.25 | -10.0755 | -10.0755 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  | Min 7: 10.56; Min 8: 0; Min 9: 26.25; Min 10: 15.69 |  | Nom. capacity MV, МVА | 25+25 |  | 21.7245 |  |  | 21.7245 | 0 | 26.25 | 4.5255
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  | Min 7: 14.33; Min 8: 0; Min 9: 26.25; Min 10: 11.92 |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | available | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.6385 | 2.3985 |  |  | 2.3985 | 0 | 2.63 | 0.2315 | 0.2315 | available
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 | [5 empty] | 21.21 | 0 | 21 | -0.21 | -0.21 | unavailable | 71 | SS 110/35/10 Rostov | 20+25 |  | 24.5055 |  |  | 24.5055 | 0 | 21 | -3.5055 | -3.5055 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  | Min 7: 1.66; Min 8: 0; Min 9: 21; Min 10: 19.34 |  | Nom. capacity MV, МVА | 20+25 |  | 2.2225 |  |  | 2.2225 | 0 | 21 | 18.7775
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 | 0.327 | Min 7: 19.55; Min 8: 0; Min 9: 21; Min 10: 1.45 |  | Nom. Capacity LV, МVА | 20+25 | 2.733 | 22.283 |  |  | 22.283 | 0 | 21 | -1.283
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 | [5 empty] | 7.62 | 0 | 6.62 | -1 | -1 | unavailable | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 13.3458 |  |  | 13.3458 | 0 | 6.62 | -6.7257 | -6.7257 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  | Min 7: 4.13; Min 8: 0; Min 9: 6.62; Min 10: 2.49 |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 7.0518 |  |  | 7.0518 | 0 | 6.62 | -0.43175
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 | 0.4 | Min 7: 3.49; Min 8: 0; Min 9: 6.62; Min 10: 3.13 |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.804 | 6.294 |  |  | 6.294 | 0 | 6.62 | 0.326
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 | [5 empty] | 23.08 | 0 | 26.25 | 3.17 | 3.17 | available | 73 | SS 110/35/10 Uglich | 25+25 |  | 31.415 |  |  | 31.415 | 0 | 26.25 | -5.165 | -5.165 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  | Min 7: 18.49; Min 8: 0; Min 9: 26.25; Min 10: 7.76 |  | Nom. capacidty MV, МVА | 25+25 |  | 22.734 |  |  | 22.734 | 0 | 26.25 | 3.516
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  | Min 7: 4.59; Min 8: 0; Min 9: 26.25; Min 10: 21.66 |  | Nom. capacity LV, МVА | 25+25 | 4.091 | 8.681 |  |  | 8.681 | 0 | 26.25 | 17.569
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 |  | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | available | 74 | SS 110/10 Ustye | 10+10 | 0.338 | 4.688 | 0.797 | 120 | 3.891 | 0 | 10.5 | 6.609 | 6.609 | available
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 |  | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | available | 75 | SS 110/10 Shurskol | 10+10 | 0.096 | 1.436 | 0.97 | 120 | 0.466 | 0 | 10.5 | 10.034 | 10.034 | available
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 |  | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | available | 76 | SS 110/10 Yur.Sloboda | 10+10 | 1.1352 | 8.3052 | 0.866 | 120 | 7.4392 | 0 | 10.5 | 3.0608 | 3.0608 | available
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.114 | 1.044 |  |  | 1.044 | 0 | 2.63 | 1.586 | 1.586 | available
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | available | 78 | SS 35/6 Batki | 1,6+1,6 | 0.615 | 1.755 |  |  | 1.755 | 0 | 1.68 | -0.075 | -0.075 | unavailable
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | available | 79 | SS 35/10 Beregovaya | 1,6 | 0.01 | 0.19 | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | available
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 |  | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | available | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.102 | 1.862 | 0.225 |  | 1.637 | 0 | 2.63 | 0.993 | 0.993 | available
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 |  | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | available | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.026 | 0.526 | 0.087 | 120 | 0.439 | 0 | 1.68 | 1.241 | 1.241 | available
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 |  | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.356 | 1.106 | 0.52 | 120 | 0.586 | 0 | 1.68 | 1.094 | 1.094 | available
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | available | 83 | SS 35/10 Glebovo | 2,5+2,5 | 4.348 | 6.428 |  |  | 6.428 | 0 | 2.63 | -3.798 | -3.798 | unavailable
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.324 | 1.254 |  |  | 1.254 | 0 | 2.63 | 1.376 | 1.376 | available
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.096 | 1.206 |  |  | 1.206 | 0 | 1.68 | 0.474 | 0.474 | available
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | available | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.105 | 1.645 |  |  | 1.645 | 0 | 1.68 | 0.035 | 0.035 | available
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | available | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.1295 | 1.6195 |  |  | 1.6195 | 0 | 2.63 | 1.0105 | 1.0105 | available
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | available | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 2.522 | 4.762 |  |  | 4.762 | 0 | 6.62 | 1.858 | 1.858 | available
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | available | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | available
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 |  | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | available | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.56 | 3.29 | 0.953 | 120 | 2.337 | 0 | 4.2 | 1.863 | 1.863 | available
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | available | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.438 | 1.788 |  |  | 1.788 | 0 | 2.63 | 0.842 | 0.842 | available
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | available | 92 | SS 35/6 Kupan | 2,5+2,5 | 1.2677 | 3.8477 |  |  | 3.8477 | 0 | 2.63 | -1.2177 | -1.2177 | unavailable
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 |  | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | available | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.375 | 1.365 | 0.502 | 120 | 0.863 | 0 | 2.63 | 1.767 | 1.767 | available
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | available | 94 | SS 35/10 Nagorye | 4,0+4,0 | 1.925 | 5.415 |  |  | 5.415 | 0 | 4.2 | -1.215 | -1.215 | unavailable
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 |  | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | available | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.274 | 2.404 | 0.087 | 120 | 2.317 | 0 | 4.2 | 1.883 | 1.883 | available
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | available | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.5165 | 1.6265 |  |  | 1.6265 | 0 | 2.63 | 1.0035 | 1.0035 | available
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 |  | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | available | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.05 | 0.96 | 0.035 | 120 | 0.925 | 0 | 2.63 | 1.705 | 1.705 | available
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | available | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.109 | 1.389 |  |  | 1.389 | 0 | 2.63 | 1.241 | 1.241 | available
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 | 0.253 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | unavailable | 99 | SS 35/10 Saraevo | 1+1,6 | 0.85 | 2.17 |  |  | 2.17 | 0 | 1.05 | -1.12 | -1.12 | unavailable
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 |  | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | available | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 1.697 | 3.147 | 0.953 | 120 | 2.194 | 0 | 2.63 | 0.436 | 0.436 | available
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 |  | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | available | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.277 | 0.897 | 0.052 | 120 | 0.845 | 0 | 4.2 | 3.355 | 3.355 | available
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | available | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.1881 | 2.2881 |  |  | 2.2881 | 0 | 1.68 | -0.6081 | -0.6081 | unavailable
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.071 | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | unavailable | 103 | SS 35/10 Solomidino | 2.5 | 1.157 | 2.357 | 0.866 | 1 day and night | 2.357 | 0 | 0.866 | -1.491 | -1.491 | unavailable
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 |  | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | available | 104 | SS 35/10 Stavotino | 4,0+4,0 | 1.095 | 2.565 | 0.346 | 120 | 2.219 | 0 | 4.2 | 1.981 | 1.981 | available
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 |  | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | available | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.049 | 0.449 | 0.052 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | available
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | available | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 0.987 | 1.837 |  |  | 1.837 | 0 | 2.63 | 0.793 | 0.793 | available
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | available | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.26 | 0.64 |  |  | 0.64 | 0 | 2.63 | 1.99 | 1.99 | available
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 |  | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | available | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.087 | 1.197 | 0.242 | 120 | 0.955 | 0 | 2.63 | 1.675 | 1.675 | available
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | available | 109 | SS 35/10 Neksans | 10+10 | 3.5 | 5.43 |  |  | 5.43 | 0 | 10.5 | 5.07 | 5.07 | available
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | unavailable | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.4935 | 11.1935 |  |  | 11.1935 | 0 | 10.5 | -0.6935 | -0.6935 | unavailable
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  |  | 18.25 | 0 | 26.25 | 8 | 8 | available | 111 | SS 110/10 Tishino | 25+25 | 0.188 | 18.438 |  |  | 18.438 | 0 | 26.25 | 7.812 | 7.812 | available
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 |  | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | available | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.027 | 2.387 | 0.069 | 120 | 2.318 | 0 | 6.62 | 4.302 | 4.302 | available
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | available | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.15866 | 20.1887 |  |  | 20.1887 | 0 | 26.25 | 6.0613 | 6.0613 | available
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 |  | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | available | 115 | SS 110/10 Optika | 10+10 | 0.406 | 5.796 | 0.26 | 120 | 5.536 | 0 | 10.5 | 4.964 | 4.964 | available
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | available | 116 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 7.82 |  |  | 7.82 | 0 | 16.8 | 8.98 | 8.98 | available
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | available | 117 | SS 110/6/6 Zapadnaya | 63+63 | 2.599 | 30.499 |  |  | 30.499 | 0 | 66.15 | 35.651 | 35.651 | available
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 | [5 empty] | 10.75 | 0 | 42 | 31.25 | 31.25 | available | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.962 |  |  | 10.962 | 0 | 42 | 31.038 | 31.038 | available
| Nom. capacity MV, МVА | 40+40 |  |  | 0 | 0 | 0 | [10 empty] | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  | Min 7: 10.75; Min 8: 0; Min 9: 42; Min 10: 31.25 |  | Nom. capacity LV, МVА | 40+40 | 0.212 | 10.962 |  |  | 10.962 | 0 | 42 | 31.038
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 | [5 empty] | 14.06 | 0 | 16.8 | 2.74 | 2.74 | available | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.28 |  |  | 15.28 | 0 | 16.8 | 1.52 | 1.52 | available
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  | Min 7: 9.1; Min 8: 0; Min 9: 16.8; Min 10: 7.7 |  | Nom. capacity MV, МVА | 16+16 |  | 10.289 |  |  | 10.289 | 0 | 16.8 | 6.511
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  | Min 7: 4.96; Min 8: 0; Min 9: 16.8; Min 10: 11.84 |  | Nom. capacity LV, МVА | 16+16 | 0.031 | 4.991 |  |  | 4.991 | 0 | 16.8 | 11.809
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 | [5 empty] | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  | Min 7: 1.18; Min 8: 0; Min 9: 7.88; Min 10: 6.7 |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  | Min 7: 0.78; Min 8: 0; Min 9: 7.88; Min 10: 7.1 |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | available | 121 | SS 110/6 Dock yard | 10+10 | 0.148 | 5.468 |  |  | 5.468 | 0 | 10.5 | 5.032 | 5.032 | available
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | available | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.713 | 4.133 |  |  | 4.133 | 0 | 6.62 | 2.487 | 2.487 | available
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | available | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 2.449 |  |  | 2.449 | 0 | 4.2 | 1.751 | 1.751 | available
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  |  | 0.68 | 0 | 1.68 | 1 | 1 | available | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.312 | 0.992 |  |  | 0.992 | 0 | 1.68 | 0.688 | 0.688 | available
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | available | 125 | SS 110/6 Veretye | 25+25 | 0.73016 | 22.0902 |  |  | 22.0902 | 0 | 26.25 | 4.1598 | 4.1598 | available
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 |  | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | available | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 1.5848 | 4.3848 | 0.554 | 120 | 3.8308 | 0 | 4.2 | 0.3692 | 0.3692 | available
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 |  | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | available | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.027 | 1.227 | 0.017 | 120 | 1.21 | 0 | 2.63 | 1.42 | 1.42 | available
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | available | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.101 | 0.921 |  |  | 0.921 | 0 | 1.68 | 0.759 | 0.759 | available
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 |  | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | available | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.003 | 0.593 | 0.294 | 120 | 0.299 | 0 | 1.68 | 1.381 | 1.381 | available
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 |  | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | available | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | available
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | available | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.591 | 1.901 |  |  | 1.901 | 0 | 2.63 | 0.729 | 0.729 | available
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | available | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.8544 | 5.1644 |  |  | 5.1644 | 0 | 6.62 | 1.4556 | 1.4556 | available
133 | SS 35/10 Breytovo | 6,3+6,3 | 6.3 | 6.3 | 4.6 | 2.55 | 2.05 |  |  |  | 4.6 | 0 | 6.62 | 2.02 | 2.02 | available | 133 | SS 35/10 Breytovo | 6,3+4,0 | 1.552 | 6.152 |  |  | 6.152 | 0 | 4.2 | -1.952 | -1.952 | unavailable
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 |  | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | available | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.028 | 1.088 | 0.208 | 120 | 0.88 | 0 | 1.68 | 0.8 | 0.8 | available
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 |  | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | available | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.01 | 0.92 | 0.173 | 120 | 0.747 | 0 | 2.63 | 1.883 | 1.883 | available
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | available | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.062 | 1.022 |  |  | 1.022 | 0 | 2.63 | 1.608 | 1.608 | available
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | available | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.17 | 0.71 |  |  | 0.71 | 0 | 2.63 | 1.92 | 1.92 | available
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 |  | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | available | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.181 | 1.581 | 0.364 | 120 | 1.217 | 0 | 1.68 | 0.463 | 0.463 | available
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 |  | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | available | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.01 | 0.23 | 0.017 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | available
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 |  | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | available | 140 | SS 35/10 Borok | 2,5+4,0 | 0.398 | 1.958 | 0.277 | 120 | 1.681 | 0 | 2.63 | 0.949 | 0.949 | available
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | available | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.744 | 4.504 |  |  | 4.504 | 0 | 6.62 | 2.116 | 2.116 | available
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | available | 142 | SS 110/10 Volga | 5,6+6,3 | 0 | 2.13 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | available
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 |  | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | available | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.494 | 2.584 | 0.104 | 120 | 2.48 | 0 | 2.63 | 0.15 | 0.15 | available
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 | [5 empty] | 20.08 | 0 | 26.25 | 6.17 | 6.17 | available | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 21.9348 |  |  | 21.9348 | 0 | 26.25 | 4.3152 | 4.3152 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  | Min 7: 3.67; Min 8: 0; Min 9: 26.25; Min 10: 22.58 |  | Nom. capacity MV, МVА | 25+25 |  | 5.1264 |  |  | 5.1264 | 0 | 26.25 | 21.1236
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  | Min 7: 16.41; Min 8: 0; Min 9: 26.25; Min 10: 9.84 |  | Nom. capacity LV, МVА | 25+25 | 0.39842 | 16.8084 |  |  | 16.8084 | 0 | 26.25 | 9.4416
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | available | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.125 | 1.212 | 120 | 6.913 | 0 | 10.5 | 3.587 | 3.587 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  | Min 7: 0.78; Min 8: 0; Min 9: 10.5; Min 10: 9.72 |  | Nom. capacity MV, МVА | 10+10 |  | 0.79 |  |  | 0.79 | 0 | 10.5 | 9.71
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 |  | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.085 | 7.335 | 1.212 | 120 | 6.123 | 0 | 10.5 | 4.377
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | available | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.351 | 3.201 |  |  | 3.201 | 0 | 6.62 | 3.419 | 3.419 | available
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | available | 147 | SS 110/35/10 Lom | 10+10 |  | 9.596 | 1.368 | 120 | 8.228 | 0 | 10.5 | 2.272 | 2.272 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  | Min 7: 6.07; Min 8: 0; Min 9: 10.5; Min 10: 4.43 |  | Nom. capacity MV, МVА | 10+10 |  | 7.6664 |  |  | 7.6664 | 0 | 10.5 | 2.8336
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 |  | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.4496 | 1.9296 | 1.368 | 120 | 0.5616 | 0 | 10.5 | 9.9384
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | available | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.151 | 0.951 |  |  | 0.951 | 0 | 1.68 | 0.729 | 0.729 | available
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | available | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 10.136 | 0.242 | 120 | 9.894 | 0 | 10.5 | 0.606 | 0.606 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  | Min 7: 7.16; Min 8: 0; Min 9: 10.5; Min 10: 3.34 |  | Nom. capacity MV, МVА | 10+10 |  | 9.314 |  |  | 9.314 | 0 | 10.5 | 1.186
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 |  | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.202 | 0.822 | 0.242 | 120 | 0.58 | 0 | 10.5 | 9.92
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | 3.21 |  |  |  | Min 11: 1.432; Min 12: available | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.582 |  |  |  | 0 |  |  | 1.432 | available
| Nom. capacidty MV, МVА | 6.3 |  |  | 2.91 | 2.91 | [11 empty] | Nom. capacidty MV, МVА | 6.3 |  | 3.282 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.3 | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | available | 151 | SS 35/10 Beloe | 2.5 | 0.065 | 0.775 | 1.472 | 1 day and night | 0.775 | 0 | 1.472 | 0.697 | 0.697 | available
152 | SS 110/35/10 Glebovo | 10 | 10 |  | 6.05 |  |  |  | Min 11: -2.505; Min 12: unavailable | 152 | SS 110/35/10 Glebovo | 10 |  | 8.7074 |  |  |  | 0 |  |  | -4.189 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | 2.87 | 2.87 | [11 empty] | Nom. capacity MV, МVА | 10 |  | 3.8434 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.2 | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.684 | 4.864 | 0.675 | 1 day and night | 4.864 | 0 | 0.675 | -4.189
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | available | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | available
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 |  | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | available | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | available
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | available | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | available
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | available | 157 | SS 35/10 Ermakovo | 1.6 | 0.182 | 1.202 | 1.212 | 1 day and night | 1.202 | 0 | 1.212 | 0.01 | 0.01 | available
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | available | 158 | SS 35/10 Milyushino | 1.6 | 0.683 | 1.523 | 0.918 | 1 day and night | 1.523 | 0 | 0.918 | -0.605 | -0.605 | unavailable
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.391 | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | unavailable | 159 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 day and night | 0.779 | 0 | 0.554 | -0.225 | -0.225 | unavailable
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | available | 160 | SS 35/10 Sit | 1.6 | 0.241 | 0.911 | 0.68 | 1 day and night | 0.911 | 0 | 0.68 | -0.231 | -0.231 | unavailable
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.276 | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | unavailable | 161 | SS 35/10 Gorelovo | 1.6 | 0.563 | 1.763 | 0.901 | 1 day and night | 1.763 | 0 | 0.901 | -0.862 | -0.862 | unavailable
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | available | 164 | SS 35/10 Levoberezhnaya | 4 | 0.8216 | 2.1316 | 1.334 | 1 day and night | 2.1316 |  | 1.334 | -0.7976 | -0.7976 | unavailable
| Total: | 2873.9 | 1463.2 | 1410.7 | 885.648 | [12 empty] | Total: | 2857.9 | а | 1033.0549
| deficit | [7 empty] | Min 11: -15.784 |  | deficit | [9 empty] | -101.7628
| proficit | [7 empty] | Min 11: 650.045 |  | proficit | [9 empty] | 539.685
Note on F143: Some load has been transferred to 220/110/6 kV
Note on G193: Т2
Note on G213: Т3
Note on G215: Т3
Note on H193: Т3