## Tambovenergo
Calculation of transmission capacity of supply centers of IDGC of Centre - Tambovenergo division following the results of measurements of peak loads as of June 1, 2012.
[9 empty] | table 1 | [11 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period provided that technical requirements at connections or other measures performed for reconstruction of the grid investment programs and etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA |  |  |  | Installed transformer capacity, Sinst. | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS of 110 kV | [11 empty] | 1: SS of 110 kV
1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 22.33 |  |  | 22.33 | 0 | 26.25 | 3.92 | 3.92 | available | 1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 |  | 22.33 |  |  | 22.33 | 0 | 26.25 | 3.92 | 3.92 | available |  |  | 65 | 65
2 | SS 110/6 Tambovskaya No.3 | 2*25 | 14.41 |  |  | 14.41 | 0 | 26.25 | 11.84 | 11.84 | available | 2 | SS 110/6 Tambovskaya No.3 | 2*25 |  | 14.41 |  |  | 14.41 | 0 | 26.25 | 11.84 | 11.84 | available |  |  | 50 | 50
3 | SS 110/6 Tambovskaya No.5 | 2*25 | 13.76 |  |  | 13.76 | 0 | 26.25 | 12.49 | 12.49 | available | 3 | SS 110/6 Tambovskaya No.5 | 2*25 |  | 13.76 |  |  | 13.76 | 0 | 26.25 | 12.49 | 12.49 | available |  |  | 50 | 50
4 | SS 110/6 Tambovskaya No.7 | 2*25 | 18.2 |  |  | 18.2 | 0 | 26.25 | 8.05 | 8.05 | available | 4 | SS 110/6 Tambovskaya No.7 | 2*25 | 1.49 | 19.69 |  |  | 19.69 | 0 | 26.25 | 6.56 | 6.56 | available |  |  | 50 | 50
5 | SS 110/35/6 Pigment | 2*63 | 32.07 | 27.68 | 80 | 4.39 | 0 | 66.15 | 61.76 | 61.76 | available | 5 | SS 110/35/6 Pigment | 2*63 |  | 32.07 | 27.68 | 80 | 4.39 | 0 | 66.15 | 61.76 | 61.76 | available |  |  | 126 | 126
6 | SS 110/6 Tambovskaya No.8 | 40+16 | 16.06 |  |  | 16.06 | 0 | 16.8 | 0.74 | 0.74 | available | 6 | SS 110/6 Tambovskaya No.8 | 2*40 | 12.3 | 28.36 |  |  | 28.36 | 0 | 42 | 13.64 | 13.64 | available | Scheduled reconstruction works (replacement of a transformer capacity of 16 MVA to 40 MVA) |  | 56 | 80
7 | SS 110/35/6 Malinovskaya | 2*40 | 6.22 | 4.75 | 120 | 1.47 | 0 | 42 | 40.53 | 40.53 | available | 7 | SS 110/35/6 Malinovskaya | 2*40 |  | 6.22 | 4.75 | 120 | 1.47 | 0 | 42 | 40.53 | 40.53 | available |  |  | 80 | 80
8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 9.21 | 1.25 | 120 | 7.96 | 0 | 10.5 | 2.54 | 2.54 | available | 8 | SS 110/35/10 Tambovskaya No.6 | 10+16 | 1.2 | 10.41 | 1.25 | 120 | 9.16 | 0 | 10.5 | 1.34 | 1.34 | available |  |  | 26 | 26
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5 | 0.62 | 120 | 4.38 | 0 | 6.615 | 2.235 | 2.235 | available | 9 | SS 110/10 N.Lyadinskaya | 10+6,3 |  | 5 | 0.62 | 120 | 4.38 | 0 | 6.615 | 2.235 | 2.235 | available |  |  | 16.3 | 16.3
10 | SS 110/35/10 Komsomolskaya | 2*10 | 9.9 | 2 | 80 | 7.9 | 0 | 10.5 | 2.6 | 2.6 | available | 10 | SS 110/35/10 Komsomolskaya | 2*10 | 1.08 | 10.98 | 2 | 80 | 8.98 | 0 | 10.5 | 1.52 | 1.52 | available |  |  | 20 | 20
11 | SS 110/10 М.Talinskaya | 10 | 0.87 | 0.52 | 1 day and night | 0.35 | 0 | 10.5 | 10.15 | 10.15 | available | 11 | SS 110/10 М.Talinskaya | 10 |  | 0.87 | 0.52 | 1 day and night | 0.35 | 0 | 10.5 | 10.15 | 10.15 | available |  |  | 10 | 10
12 | SS 110/35/10 Promyshlennaya | 2*40 | 23.05 | 5 | 120 | 18.05 | 0 | 42 | 23.95 | 23.95 | available | 12 | SS 110/35/10 Promyshlennaya | 2*40 | 1.37 | 24.42 | 5 | 120 | 19.42 | 0 | 42 | 22.58 | 22.58 | available |  |  | 80 | 80
13 | SS 110/35/10 Arzhenskaya | 2*10 | 3.41 | 1.5 | 80 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | available | 13 | SS 110/35/10 Arzhenskaya | 2*10 |  | 3.41 | 1.5 | 80 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | available |  |  | 20 | 20
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 14 | SS 110/10 Teleshovskaya | 2*2,5 |  | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available |  |  | 5 | 5
15 | SS 110/6 Oktyabrskaya | 2*25 | 7.14 |  |  | 7.14 | 0 | 26.25 | 19.11 | 19.11 | available | 15 | SS 110/6 Oktyabrskaya | 2*25 | 0.32 | 7.46 |  |  | 7.46 | 0 | 26.25 | 18.79 | 18.79 | available |  |  | 50 | 50
16 | SS 110/10 Spasskaya | 2*6,3 | 2.24 |  |  | 2.24 | 0 | 6.615 | 4.375 | 4.375 | available | 16 | SS 110/10 Spasskaya | 2*6,3 |  | 2.24 |  |  | 2.24 | 0 | 6.615 | 4.375 | 4.375 | available |  |  | 12.6 | 12.6
17 | SS 110/35/10 Kuzminskaya | 2*10 | 6.48 | 2 | 45 | 4.48 | 0 | 10.5 | 6.02 | 6.02 | available | 17 | SS 110/35/10 Kuzminskaya | 2*10 |  | 6.48 | 2 | 45 | 4.48 | 0 | 10.5 | 6.02 | 6.02 | available |  |  | 20 | 20
18 | SS 110/35/10 Sampurskaya | 10+16 | 6.65 | 4 | 80 | 2.65 | 0 | 10.5 | 7.85 | 7.85 | available | 18 | SS 110/35/10 Sampurskaya | 10+16 | 7.69 | 14.34 | 4 | 80 | 10.34 | 0 | 10.5 | 0.16 | 0.16 | available |  |  | 26 | 26
19 | SS 110/6 Leather plant | 2*10 | 1.15 |  |  | 1.15 | 0 | 10.5 | 9.35 | 9.35 | available | 19 | SS 110/6 Leather plant | 2*10 |  | 1.15 |  |  | 1.15 | 0 | 10.5 | 9.35 | 9.35 | available |  |  | 20 | 20
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 14.24 | 1.5 | 120 | 12.74 | 0 | 21 | 8.26 | 8.26 | available | 20 | SS 110/35/6 Rasskazovskaya | 25+20 | 0.09 | 14.33 | 1.5 | 120 | 12.83 | 0 | 21 | 8.17 | 8.17 | available |  |  | 45 | 45
21 | SS 110/35/10 Volchkovskaya | 2*10 | 2.76 | 0.95 | 120 | 1.81 | 0 | 10.5 | 8.69 | 8.69 | available | 21 | SS 110/35/10 Volchkovskaya | 2*10 |  | 2.76 | 0.95 | 120 | 1.81 | 0 | 10.5 | 8.69 | 8.69 | available |  |  | 20 | 20
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 2.99 | 1 | 120 | 1.99 | 0 | 6.615 | 4.625 | 4.625 | available | 22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 0.43 | 3.42 | 1 | 120 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | available |  |  | 22.3 | 22.3
23 | SS 110/35/10 Khmelevskaya | 2*10 | 5.49 | 0.5 | 120 | 4.99 | 0 | 10.5 | 5.51 | 5.51 | available | 23 | SS 110/35/10 Khmelevskaya | 2*10 | 0.16 | 5.65 | 0.5 | 120 | 5.15 | 0 | 10.5 | 5.35 | 5.35 | available |  |  | 20 | 20
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.83 | 1 | 80 | 4.83 | 0 | 6.615 | 1.785 | 1.785 | available | 24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 1.58 | 7.41 | 1 | 80 | 6.41 | 0 | 6.615 | 0.205 | 0.205 | available |  |  | 12.6 | 12.6
25 | SS 110/35/10 Nikiforovskaya | 10+16 | 5.86 | 1.5 | 120 | 4.36 | 0 | 10.5 | 6.14 | 6.14 | available | 25 | SS 110/35/10 Nikiforovskaya | 10+16 | 0.71 | 6.57 | 1.5 | 120 | 5.07 | 0 | 10.5 | 5.43 | 5.43 | available |  |  | 26 | 26
26 | SS 110/10 N.Seslavinskaya | 2.5 | 0.37 | 0.37 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 26 | SS 110/10 N.Seslavinskaya | 2.5 |  | 0.37 | 0.37 | 1 day and night | 0 | 0 | 2.625 | 2.625 | 2.625 | available |  |  | 2.5 | 2.5
27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.21 | 0.33 | 1 day and night | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available | 27 | SS 110/10 N. Arkhangelskaya | 2.5 |  | 0.21 | 0.33 | 1 day and night | -0.12 | 0 | 2.625 | 2.745 | 2.745 | available |  |  | 2.5 | 2.5
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 28 | SS 110/10 Ilovayskaya | 2*2,5 |  | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available |  |  | 5 | 5
29 | SS 110/35/10 Yuzhnaya | 16 | 7.41 | 3 | 1 day and night | 4.41 | 0 | 16.8 | 12.39 | 12.39 | available | 29 | SS 110/35/10 Yuzhnaya | 16 |  | 7.41 | 3 | 1 day and night | 4.41 | 0 | 16.8 | 12.39 | 12.39 | available |  |  | 16 | 16
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 19.94 | 3 | 120 | 16.94 | 0 | 33.075 | 16.135 | 16.135 | available | 30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 0.22 | 20.16 | 3 | 120 | 17.16 | 0 | 33.075 | 15.915 | 15.915 | available |  |  | 63 | 63
31 | SS 110/35/10 Sosnovskaya | 2*16 | 7.31 | 2 | 80 | 5.31 | 0 | 16.8 | 11.49 | 11.49 | available | 31 | SS 110/35/10 Sosnovskaya | 2*16 | 1.83 | 9.14 | 2 | 80 | 7.14 | 0 | 16.8 | 9.66 | 9.66 | available |  |  | 32 | 32
32 | SS 110/35/10 Pichaevskaya | 2*10 | 5.37 | 2 | 80 | 3.37 | 0 | 10.5 | 7.13 | 7.13 | available | 32 | SS 110/35/10 Pichaevskaya | 2*10 | 0.19 | 5.56 | 2 | 80 | 3.56 | 0 | 10.5 | 6.94 | 6.94 | available |  |  | 20 | 20
33 | SS 110/35/10 Algasovskaya | 2*40 | 12.15 | 2.92 | 120 | 9.23 | 0 | 42 | 32.77 | 32.77 | available | 33 | SS 110/35/10 Algasovskaya | 2*40 |  | 12.15 | 2.92 | 120 | 9.23 | 0 | 42 | 32.77 | 32.77 | available |  |  | 80 | 80
34 | SS 110/35/6 Morshanskaya | 40+25 | 16.99 | 3 | 120 | 13.99 | 0 | 26.25 | 12.26 | 12.26 | available | 34 | SS 110/35/6 Morshanskaya | 40+25 |  | 16.99 | 3 | 120 | 13.99 | 0 | 26.25 | 12.26 | 12.26 | available |  |  | 65 | 65
35 | SS 110/35/6 Kamvolnaya | 16+25 | 10.94 | 5 | 80 | 5.94 | 0 | 16.8 | 10.86 | 10.86 | available | 35 | SS 110/35/6 Kamvolnaya | 16+25 | 4.3 | 15.24 | 5 | 80 | 10.24 | 0 | 16.8 | 6.56 | 6.56 | available |  |  | 41 | 41
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 3.91 | 0.63 | 120 | 3.28 | 0 | 10.5 | 7.22 | 7.22 | available | 36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 0.12 | 4.03 | 0.63 | 120 | 3.4 | 0 | 10.5 | 7.1 | 7.1 | available |  |  | 20 | 20
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 3.17 | 1 | 120 | 2.17 | 0 | 10.5 | 8.33 | 8.33 | available | 37 | SS 110/35/10 Nashchekinskaya | 2*10 |  | 3.17 | 1 | 120 | 2.17 | 0 | 10.5 | 8.33 | 8.33 | available |  |  | 20 | 20
38 | SS 110/10 Shachinskaya | 2.5 | 0.06 | 0.05 | 1 day and night | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available | 38 | SS 110/10 Shachinskaya | 2.5 | 0.89 | 0.95 | 0.05 | 1 day and night | 0.9 | 0 | 2.625 | 1.725 | 1.725 | available |  |  | 2.5 | 2.5
39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 9.71 | 3 | 45 | 6.71 | 0 | 16.8 | 10.09 | 10.09 | available | 39 | SS 110/35/10/6 Uvarovskaya | 16+16 |  | 9.71 | 3 | 45 | 6.71 | 0 | 16.8 | 10.09 | 10.09 | available |  |  | 32 | 32
40 | SS 110/35/10 Muchkapskaya | 2*10 | 3.13 | 0.5 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | available | 40 | SS 110/35/10 Muchkapskaya | 2*10 | 2.26 | 5.39 | 0.5 | 120 | 4.89 | 0 | 10.5 | 5.61 | 5.61 | available |  |  | 20 | 20
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.68 | 0.3 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available | 41 | SS 110/10 M.Alabushskaya | 2*2,5 |  | 0.68 | 0.3 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available |  |  | 5 | 5
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.74 | 0.6 | 120 | 1.14 | 0 | 10.5 | 9.36 | 9.36 | available | 42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.51 | 3.25 | 0.6 | 120 | 2.65 | 0 | 10.5 | 7.85 | 7.85 | available |  |  | 26 | 26
43 | SS 110/10 Shpikulovskaya | 6,3+2,5 | 0.66 | 0.61 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 43 | SS 110/10 Shpikulovskaya | 6,3+2,5 |  | 0.66 | 0.61 | 120 | 0.05 | 0 | 2.63 | 2.58 | 2.58 | available |  |  | 8.8 | 8.8
44 | SS 110/35/10 Zherdevskaya | 2*16 | 7.17 | 3.5 | 80 | 3.67 | 0 | 16.8 | 13.13 | 13.13 | available | 44 | SS 110/35/10 Zherdevskaya | 2*16 | 10.14 | 17.31 | 3.5 | 80 | 13.81 | 0 | 16.8 | 2.99 | 2.99 | available |  |  | 32 | 32
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.37 | 0.4 | 120 | 3.97 | 0 | 10.5 | 6.53 | 6.53 | available | 45 | SS 110/35/10 Rzhaksinskaya | 2*10 |  | 4.37 | 0.4 | 120 | 3.97 | 0 | 10.5 | 6.53 | 6.53 | available |  |  | 20 | 20
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | available | 46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.06 | 0.45 | 0.2 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | available |  |  | 5 | 5
47 | SS 110/35/10 Tokarevskaya | 2*25 | 7.02 | 3 | 120 | 4.02 | 0 | 26.25 | 22.23 | 22.23 | available | 47 | SS 110/35/10 Tokarevskaya | 2*25 | 11.06 | 18.08 | 3 | 120 | 15.08 | 0 | 26.25 | 11.17 | 11.17 | available |  |  | 50 | 50
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0.82 | 0.91 | 120 | -0.09 | 0 | 6.615 | 6.705 | 6.705 | available | 48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0.05 | 0.87 | 0.91 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | available |  |  | 16.3 | 16.3
49 | SS 110/35/10 Mordovskaya | 2*10 | 3.69 | 1 | 120 | 2.69 | 0 | 10.5 | 7.81 | 7.81 | available | 49 | SS 110/35/10 Mordovskaya | 2*10 | 0.43 | 4.12 | 1 | 120 | 3.12 | 0 | 10.5 | 7.38 | 7.38 | available |  |  | 20 | 20
50 | SS 110/35/10 Pavlovskaya | 10 | 1.08 | 1 | 1 day and night | 0.08 | 0 | 10.5 | 10.42 | 10.42 | available | 50 | SS 110/35/10 Pavlovskaya | 10 |  | 1.08 | 1 | 1 day and night | 0.08 | 0 | 10.5 | 10.42 | 10.42 | available |  |  | 10 | 10
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 12.2 | 3 | 120 | 9.2 | 0 | 26.25 | 17.05 | 17.05 | available | 51 | SS 110/35/10 Kirsanovskaya | 2*25 |  | 12.2 | 3 | 120 | 9.2 | 0 | 26.25 | 17.05 | 17.05 | available |  |  | 50 | 50
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 8.58 | 1 | 120 | 7.58 | 0 | 16.8 | 9.22 | 9.22 | available | 52 | SS 110/35/10 Inzhavinskaya | 2*16 | 0.32 | 8.9 | 1 | 120 | 7.9 | 0 | 16.8 | 8.9 | 8.9 | available |  |  | 32 | 32
53 | SS 110/35/10 Umyotskaya | 2*10 | 1.65 | 2 | 80 | -0.35 | 0 | 10.5 | 10.85 | 10.85 | available | 53 | SS 110/35/10 Umyotskaya | 2*10 |  | 1.65 | 2 | 80 | -0.35 | 0 | 10.5 | 10.85 | 10.85 | available |  |  | 20 | 20
54 | SS 110/35/10 Kovylskaya | 2*10 | 0.88 | 1 | 120 | -0.12 | 0 | 10.5 | 10.62 | 10.62 | available | 54 | SS 110/35/10 Kovylskaya | 2*10 |  | 0.88 | 1 | 120 | -0.12 | 0 | 10.5 | 10.62 | 10.62 | available |  |  | 20 | 20
55 | SS 110/10 Inokovskaya | 2.5 | 0.25 | 0.18 | 1 day and night | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 55 | SS 110/10 Inokovskaya | 2.5 |  | 0.25 | 0.18 | 1 day and night | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available |  |  | 2.5 | 2.5
56 | SS 110/10 PTF | 2*16 | 5.29 |  |  | 5.29 | 0 | 16.8 | 11.51 | 11.51 | available | 56 | SS 110/10 PTF | 2*16 |  | 5.29 |  |  | 5.29 | 0 | 16.8 | 11.51 | 11.51 | available |  |  | 32 | 32
SS of 35 kV | [11 empty] | 1: SS of 35 kV |  | TOTAL for 110kV | 1699.9 | 1723.9
57 | SS 35/6 Elevatornaya | 2*2,5 | 1.64 |  |  | 1.64 | 0 | 2.625 | 0.985 | 0.985 | available | 57 | SS 35/6 Elevatornaya | 2*2,5 |  | 1.64 |  |  | 1.64 | 0 | 2.625 | 0.985 | 0.985 | available |  |  | 5 | 5
58 | SS 35/10 Picherskaya | 2*2,5 | 0.42 |  |  | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available | 58 | SS 35/10 Picherskaya | 2*2,5 |  | 0.42 |  |  | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available |  |  | 5 | 5
59 | SS 35/10 Osinovskaya | 2*2,5 | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 59 | SS 35/10 Osinovskaya | 2*2,5 |  | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available |  |  | 5 | 5
60 | SS 35/10 Koptevskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available | 60 | SS 35/10 Koptevskaya | 2*2,5 |  | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available |  |  | 5 | 5
61 | SS 35/10 Sayukinskaya | 2,5+4 | 0.47 | 0.2 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available | 61 | SS 35/10 Sayukinskaya | 2,5+4 |  | 0.47 | 0.2 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available |  |  | 6.5 | 6.5
62 | SS 35/10 Zelyonaya-1 | 2*4 | 1.45 |  |  | 1.45 | 0 | 4.2 | 2.75 | 2.75 | available | 62 | SS 35/10 Zelyonaya-1 | 2*4 |  | 1.45 |  |  | 1.45 | 0 | 4.2 | 2.75 | 2.75 | available |  |  | 8 | 8
63 | SS 35/10 Pyatiletka | 2*4 | 0.32 |  |  | 0.32 | 0 | 4.2 | 3.88 | 3.88 | available | 63 | SS 35/10 Pyatiletka | 2*4 |  | 0.32 |  |  | 0.32 | 0 | 4.2 | 3.88 | 3.88 | available |  |  | 8 | 8
64 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.89 |  |  | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available | 64 | SS 35/10 Yaroslavskaya | 2*2,5 | 1.72 | 2.61 |  |  | 2.61 | 0 | 2.625 | 0.015 | 0.015 | available |  |  | 5 | 5
65 | SS 35/10 Platonovskaya | 2*6,3 | 2.05 | 0.24 | 120 | 1.81 | 0 | 6.615 | 4.805 | 4.805 | available | 65 | SS 35/10 Platonovskaya | 2*6,3 |  | 2.05 | 0.24 | 120 | 1.81 | 0 | 6.615 | 4.805 | 4.805 | available |  |  | 12.6 | 12.6
66 | SS 35/10 Znamenskaya | 2*4 | 2.75 | 1.54 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | available | 66 | SS 35/10 Znamenskaya | 2*4 | 2.19 | 4.94 | 1 | 120 | 3.94 | 0 | 4.2 | 0.26 | 0.26 | available |  |  | 8 | 8
67 | SS 35/10 Sukhotinskaya | 2.5 | 0.65 |  |  | 0.65 | 0 | 0 | -0.65 | -0.65 | unavailable | 67 | SS 35/10 Sukhotinskaya | 2*2,5 |  | 0.65 |  |  | 0.65 | 0 | 2.63 | 1.98 | 1.98 | available | Scheduled reconstruction works (installation of 2-nd transformer 2,5 MVA) |  | 2.5 | 5
68 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.95 |  |  | 0.95 | 0 | 1.68 | 0.73 | 0.73 | available | 68 | SS 35/10 P.Marfinskaya | 2,5+1,6 |  | 0.95 |  |  | 0.95 | 0 | 1.68 | 0.73 | 0.73 | available |  |  | 4.1 | 4.1
69 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.56 | 0.29 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | available | 69 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 1.4 | 1.96 | 0.29 | 120 | 1.67 | 0 | 1.68 | 0.01 | 0.01 | available |  |  | 4.1 | 4.1
70 | SS 35/10 Stepnaya | 2*4 | 2.23 | 0.7 | 80 | 1.53 | 0 | 4.2 | 2.67 | 2.67 | available | 70 | SS 35/10 Stepnaya | 2*4 |  | 2.23 | 0.7 | 80 | 1.53 | 0 | 4.2 | 2.67 | 2.67 | available |  |  | 8 | 8
71 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 1.13 | 0.5 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | available | 71 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 3.55 | 4.68 | 0.5 | 120 | 4.18 | 0 | 4.2 | 0.02 | 0.02 | available |  |  | 8 | 8
72 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.41 | 0.2 | 120 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available | 72 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.11 | 0.52 | 0.2 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | available |  |  | 4.1 | 4.1
73 | SS 35/10 Gorelskaya | 4+6,3 | 1.96 | 0.7 | 80 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | available | 73 | SS 35/10 Gorelskaya | 4+6,3 | 0.45 | 2.41 | 0.7 | 80 | 1.71 | 0 | 4.2 | 2.49 | 2.49 | available |  |  | 10.3 | 10.3
74 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.8 |  |  | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 74 | SS 35/10 B.Dvoynyovskaya | 2*2,5 |  | 0.8 |  |  | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available |  |  | 5 | 5
75 | SS 35/10 Avangardskaya | 2*2,5 | 0.44 |  |  | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 75 | SS 35/10 Avangardskaya | 2*2,5 |  | 0.44 |  |  | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available |  |  | 5 | 5
76 | SS 35/10 Suravskaya | 1,6+2,5 | 0.54 | 0.2 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | available | 76 | SS 35/10 Suravskaya | 1,6+2,5 |  | 0.54 | 0.2 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | available |  |  | 4.1 | 4.1
77 | SS 35/10 Seleznzyovskaya | 3*4 | 3.3 |  |  | 3.3 | 0 | 8.4 | 5.1 | 5.1 | available | 77 | SS 35/10 Seleznzyovskaya | 3*4 |  | 3.3 |  |  | 3.3 | 0 | 8.4 | 5.1 | 5.1 | available |  |  | 12 | 12
78 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.82 | 0.32 | 80 | 1.5 | 0 | 1.68 | 0.18 | 0.18 | available | 78 | SS 35/10 Chernyanskaya | 1,6+2,5 | 0.16 | 1.98 | 0.32 | 80 | 1.66 | 0 | 1.68 | 0.02 | 0.02 | available |  |  | 4.1 | 4.1
79 | SS 35/10 Viktorskaya | 2.5 | 0.39 |  |  | 0.39 | 0 | 0 | -0.39 | -0.39 | unavailable | 79 | SS 35/10 Viktorskaya | 2.5 |  | 0.39 |  |  | 0.39 | 0 | 0 | -0.39 | -0.39 | unavailable |  |  | 2.5 | 2.5
80 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.61 |  |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | available | 80 | SS 35/10 Novoseltsevskaya | 2*1,6 |  | 0.61 |  |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | available |  |  | 3.2 | 3.2
81 | SS 35/10 Avdeevskaya | 2*2,5 | 0.75 |  |  | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available | 81 | SS 35/10 Avdeevskaya | 2*2,5 |  | 0.75 |  |  | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available |  |  | 5 | 5
82 | SS 35/10 Tatanovskaya | 2*2,5 | 2.28 |  |  | 2.28 | 0 | 2.625 | 0.345 | 0.345 | available | 82 | SS 35/10 Tatanovskaya | 2*2,5 | 0.07 | 2.35 |  | 120 | 2.35 | 0 | 2.625 | 0.275 | 0.275 | available |  |  | 5 | 5
83 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 3.31 | 0.3 | 60 | 3.01 | 0 | 5.25 | 2.24 | 2.24 | available | 83 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 0.42 | 3.73 | 0.3 | 60 | 3.43 | 0 | 5.25 | 1.82 | 1.82 | available |  |  | 9 | 9
84 | SS 35/10 P.Prigorodnaya | 2*6,3 | 5.76 |  |  | 5.76 | 0 | 6.615 | 0.855 | 0.855 | available | 84 | SS 35/10 P.Prigorodnaya | 2*6,3 | 0.32 | 6.08 |  |  | 6.08 | 0 | 6.615 | 0.535 | 0.535 | available |  |  | 12.6 | 12.6
85 | SS 35/10 Bokinskaya | 2*6,3 | 3.83 | 0.3 | 30 | 3.53 | 0 | 6.615 | 3.085 | 3.085 | available | 85 | SS 35/10 Bokinskaya | 2*6,3 | 0.09 | 3.92 | 0.3 | 30 | 3.62 | 0 | 6.615 | 2.995 | 2.995 | available |  |  | 12.6 | 12.6
86 | SS 35/10 Stolovskaya | 4 | 0.57 | 0.2 | 1 day and night | 0.37 | 0 | 4.2 | 3.83 | 3.83 | available | 86 | SS 35/10 Stolovskaya | 4 |  | 0.57 | 0.2 | 1 day and night | 0.37 | 0 | 4.2 | 3.83 | 3.83 | available |  |  | 4 | 4
87 | SS 35/10 Tulinovskaya | 2*2,5 | 1.38 |  |  | 1.38 | 0 | 2.625 | 1.245 | 1.245 | available | 87 | SS 35/10 Tulinovskaya | 2*2,5 |  | 1.38 |  |  | 1.38 | 0 | 2.625 | 1.245 | 1.245 | available |  |  | 5 | 5
88 | SS 35/6 Macaroni factory | 1.6 | 0.02 |  |  | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available | 88 | SS 35/6 Macaroni factory | 1.6 |  | 0.02 |  |  | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available |  |  | 1.6 | 1.6
89 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.43 |  |  | 1.43 | 0 | 1.68 | 0.25 | 0.25 | available | 89 | SS 35/10 Serebryakovskaya | 2*1,6 |  | 1.43 |  |  | 1.43 | 0 | 1.68 | 0.25 | 0.25 | available |  |  | 3.2 | 3.2
90 | SS 35/10 B.Doroga | 2*1,6 | 0.38 | 0.2 | 60 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | available | 90 | SS 35/10 B.Doroga | 2*1,6 |  | 0.38 | 0.2 | 60 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | available |  |  | 3.2 | 3.2
91 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.63 |  |  | 0.63 | 0 | 2.625 | 1.995 | 1.995 | available | 91 | SS 35/10 B.Izberdeevskaya | 2*2,5 |  | 0.63 |  |  | 0.63 | 0 | 2.625 | 1.995 | 1.995 | available |  |  | 5 | 5
92 | SS 35/10 Vishnevskaya | 2*2,5 | 0.32 | 0.26 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available | 92 | SS 35/10 Vishnevskaya | 2*2,5 |  | 0.32 | 0.26 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available |  |  | 5 | 5
93 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.38 | 0.32 | 50 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available | 93 | SS 35/10 Vyrubovskaya | 2*2,5 |  | 0.38 | 0.32 | 50 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available |  |  | 5 | 5
94 | SS 35/10 Glazkovskaya | 2*4 | 0.97 | 0.4 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available | 94 | SS 35/10 Glazkovskaya | 2*4 |  | 0.97 | 0.4 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available |  |  | 8 | 8
95 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 95 | SS 35/10 Dmitirievskaya | 2*2,5 |  | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available |  |  | 5 | 5
96 | SS 35/6 Donskaya | 6,3+10 | 3.5 | 2 | 1 day and night | 1.5 | 0 | 6.615 | 5.115 | 5.115 | available | 96 | SS 35/6 Donskaya | 6,3+10 |  | 3.5 | 2 | 1 day and night | 1.5 | 0 | 6.615 | 5.115 | 5.115 | available |  |  | 16.3 | 16.3
97 | SS 35/10 Druzhba | 2.5 | 0.29 | 0.16 | 1 day and night | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available | 97 | SS 35/10 Druzhba | 2.5 |  | 0.29 | 0.16 | 1 day and night | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available |  |  | 2.5 | 2.5
98 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.27 | 0.23 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 98 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.17 | 0.44 | 0.23 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available |  |  | 5 | 5
99 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 99 | SS 35/10 Zhidilovskaya | 2,5+1,6 |  | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available |  |  | 4.1 | 4.1
100 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.34 | 0.4 | 80 | 0.94 | 0 | 2.625 | 1.685 | 1.685 | available | 100 | SS 35/10 Izosimovskaya | 6,3+2,5 | 0.06 | 1.4 | 0.4 | 80 | 1 | 0 | 2.625 | 1.625 | 1.625 | available |  |  | 8.8 | 8.8
101 | SS 35/10 KIM | 2,5+4 | 1.28 | 0.3 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | available | 101 | SS 35/10 KIM | 2,5+4 | 0.06 | 1.34 | 0.3 | 120 | 1.04 | 0 | 2.625 | 1.585 | 1.585 | available |  |  | 6.5 | 6.5
102 | SS 35/10 Klenskaya | 2*2,5 | 0.26 | 0.22 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 102 | SS 35/10 Klenskaya | 2*2,5 |  | 0.26 | 0.22 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available |  |  | 5 | 5
103 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.61 | 0.3 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available | 103 | SS 35/10 Kozmodemyanovskaya | 2*2,5 |  | 0.61 | 0.3 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available |  |  | 5 | 5
104 | SS 35/10 Komintern | 2*2,5 | 0.32 | 0.22 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | available | 104 | SS 35/10 Komintern | 2*2,5 | 0.1 | 0.42 | 0.22 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available |  |  | 5 | 5
105 | SS 35/10 Kochetovskaya | 6.3 | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 6.615 | 6.415 | 6.415 | available | 105 | SS 35/10 Kochetovskaya | 6.3 |  | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 6.615 | 6.415 | 6.415 | available |  |  | 6.3 | 6.3
106 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.21 | 0.14 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 106 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 |  | 0.21 | 0.14 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available |  |  | 5 | 5
107 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 1.05 | 0.3 | 1 day and night | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available | 107 | SS 35/10 Nov.Tarbeevskaya | 2.5 |  | 1.05 | 0.3 | 1 day and night | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available |  |  | 2.5 | 2.5
108 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.31 | 0.28 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | available | 108 | SS 35/10 Nov.Yuryevskaya | 2*1,6 |  | 0.31 | 0.28 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | available |  |  | 3.2 | 3.2
109 | SS 35/10 Petrovskaya | 2*4 | 3.5 | 0.5 | 120 | 3 | 0 | 4.2 | 1.2 | 1.2 | available | 109 | SS 35/10 Petrovskaya | 2*4 | 0.3 | 3.8 | 0.5 | 120 | 3.3 | 0 | 4.2 | 0.9 | 0.9 | available |  |  | 8 | 8
110 | SS 35/10 Prigorodnaya | 2*2,5 | 0.94 | 0.4 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 110 | SS 35/10 Prigorodnaya | 2*2,5 | 2 | 2.94 | 0.4 | 120 | 2.54 | 0 | 2.625 | 0.085 | 0.085 | available |  |  | 5 | 5
111 | SS 35/6 Progress | 2*10 | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | available | 111 | SS 35/6 Progress | 2*10 |  | 9.55 |  |  | 9.55 | 0 | 10.5 | 0.95 | 0.95 | available |  |  | 20 | 20
112 | SS 35/10 Raninskaya | 1.6 | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | available | 112 | SS 35/10 Raninskaya | 1.6 |  | 0.22 | 0.32 | 1 day and night | -0.1 | 0 | 1.68 | 1.78 | 1.78 | available |  |  | 1.6 | 1.6
113 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.22 |  |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 113 | SS 35/10 Rakhmaninskaya | 2*1,6 |  | 0.22 |  |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available |  |  | 3.2 | 3.2
114 | SS 35/10 Saburovskaya | 2*5,6 | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | available | 114 | SS 35/10 Saburovskaya | 2*5,6 |  | 2.26 |  |  | 2.26 | 0 | 5.88 | 3.62 | 3.62 | available |  |  | 11.2 | 11.2
115 | SS 35/10 Sestryonskaya | 2*1,6 | 0.11 |  |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available | 115 | SS 35/10 Sestryonskaya | 2*1,6 |  | 0.11 |  |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available |  |  | 3.2 | 3.2
116 | SS 35/10 Sitovskaya | 1.6 | 0.5 | 0.5 | 1 day and night | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 116 | SS 35/10 Sitovskaya | 1.6 |  | 0.5 | 0.5 | 1 day and night | 0 | 0 | 1.68 | 1.68 | 1.68 | available |  |  | 1.6 | 1.6
117 | SS 35/10 Skobelevskaya | 1.6 | 0.22 | 0.24 | 1 day and night | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available | 117 | SS 35/10 Skobelevskaya | 1.6 |  | 0.22 | 0.24 | 1 day and night | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available |  |  | 1.6 | 1.6
118 | SS 35/10 Ustyinskaya | 2.5 | 1 | 0.4 | 1 day and night | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available | 118 | SS 35/10 Ustyinskaya | 2.5 |  | 1 | 0.4 | 1 day and night | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available |  |  | 2.5 | 2.5
119 | SS 35/10 Yurlovskaya | 2*2,5 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | available | 119 | SS 35/10 Yurlovskaya | 2*2,5 | 0.06 | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available |  |  | 5 | 5
120 | SS 35/10 Yablonovetskaya | 1,6+2,5 | 0.68 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | available | 120 | SS 35/10 Yablonovetskaya | 1,6+2,5 |  | 0.68 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | available |  |  | 4.1 | 4.1
121 | SS 35/10 Agroprom | 2*4 | 3.73 |  |  | 3.73 | 0 | 4.2 | 0.47 | 0.47 | available | 121 | SS 35/10 Agroprom | 2*4 |  | 3.73 |  |  | 3.73 | 0 | 4.2 | 0.47 | 0.47 | available |  |  | 8 | 8
122 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available | 122 | SS 35/10 Alekseevskaya | 1,6+2,5 |  | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available |  |  | 4.1 | 4.1
123 | SS 35/10 Vanovskaya | 2*2,5 | 0.16 | 0.07 | 80 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 123 | SS 35/10 Vanovskaya | 2*2,5 |  | 0.16 | 0.07 | 80 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available |  |  | 5 | 5
124 | SS 35/10 Vyazhlinskaya | 1.8 | 0.52 | 0.3 | 1 day and night | 0.22 | 0 | 1.89 | 1.67 | 1.67 | available | 124 | SS 35/10 Vyazhlinskaya | 1.8 |  | 0.52 | 0.3 | 1 day and night | 0.22 | 0 | 1.89 | 1.67 | 1.67 | available |  |  | 1.8 | 1.8
125 | SS 35/10 Zarechnaya | 2*2,5 | 1.35 |  |  | 1.35 | 0 | 2.625 | 1.275 | 1.275 | available | 125 | SS 35/10 Zarechnaya | 2*2,5 |  | 1.35 |  |  | 1.35 | 0 | 2.625 | 1.275 | 1.275 | available |  |  | 5 | 5
126 | SS 35/10 Kryukovskaya | 2*2,5 | 0.67 | 0.3 | 120 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available | 126 | SS 35/10 Kryukovskaya | 2*2,5 |  | 0.67 | 0.3 | 120 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available |  |  | 5 | 5
127 | SS 35/6 Korshunovskaya | 2*2,5 | 1.01 |  |  | 1.01 | 0 | 2.625 | 1.615 | 1.615 | available | 127 | SS 35/6 Korshunovskaya | 2*2,5 |  | 1.01 |  |  | 1.01 | 0 | 2.625 | 1.615 | 1.615 | available |  |  | 5 | 5
128 | SS 35/6 Lugovaya | 4 | 0.97 | 0.4 | 1 day and night | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available | 128 | SS 35/6 Lugovaya | 4 |  | 0.97 | 0.4 | 1 day and night | 0.57 | 0 | 4.2 | 3.63 | 3.63 | available |  |  | 4 | 4
129 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.21 | 0.15 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available | 129 | SS 35/10 Lyubvinskaya | 2*2,5 |  | 0.21 | 0.15 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | available |  |  | 5 | 5
130 | SS 35/10 Morshanskaya | 2*4 | 3.29 |  |  | 3.29 | 0 | 4.2 | 0.91 | 0.91 | available | 130 | SS 35/10 Morshanskaya | 2*4 | 0.14 | 3.43 |  |  | 3.43 | 0 | 4.2 | 0.77 | 0.77 | available |  |  | 8 | 8
131 | SS 35/10 Piterskaya | 2.5 | 0.79 | 0.4 | 1 day and night | 0.39 | 0 | 2.625 | 2.235 | 2.235 | available | 131 | SS 35/10 Piterskaya | 2.5 | 0.06 | 0.85 | 0.4 | 1 day and night | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available |  |  | 2.5 | 2.5
132 | SS 35/10 Rakshinskaya | 2*4 | 1.78 | 0.6 | 80 | 1.18 | 0 | 4.2 | 3.02 | 3.02 | available | 132 | SS 35/10 Rakshinskaya | 2*4 |  | 1.78 | 0.6 | 80 | 1.18 | 0 | 4.2 | 3.02 | 3.02 | available |  |  | 8 | 8
133 | SS 35/10 Rybinskaya | 2*2,5 | 0.58 | 0.5 | 80 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | available | 133 | SS 35/10 Rybinskaya | 2*2,5 |  | 0.58 | 0.5 | 80 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | available |  |  | 5 | 5
134 | SS 35/10 Serpovskaya | 2*2,5 | 0.81 | 0.3 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | available | 134 | SS 35/10 Serpovskaya | 2*2,5 |  | 0.81 | 0.3 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | available |  |  | 5 | 5
135 | SS 35/10 St.Tomnikovskaya | 1 | 0.17 | 0.09 | 1 day and night | 0.08 | 0 | 1.05 | 0.97 | 0.97 | available | 135 | SS 35/10 St.Tomnikovskaya | 1 |  | 0.17 | 0.09 | 1 day and night | 0.08 | 0 | 1.05 | 0.97 | 0.97 | available |  |  | 1 | 1
136 | SS 35/10 Chernitovskaya | 2.5 | 0.41 | 0.2 | 1 day and night | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available | 136 | SS 35/10 Chernitovskaya | 2.5 |  | 0.41 | 0.2 | 1 day and night | 0.21 | 0 | 2.625 | 2.415 | 2.415 | available |  |  | 2.5 | 2.5
137 | SS 35/10 Bondarskaya | 2*2,5 | 1.47 | 0.3 | 80 | 1.17 | 0 | 2.625 | 1.455 | 1.455 | available | 137 | SS 35/10 Bondarskaya | 2*2,5 | 0.43 | 1.9 | 0.3 | 80 | 1.6 | 0 | 2.625 | 1.025 | 1.025 | available |  |  | 5 | 5
138 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.47 | 0.25 | 80 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 138 | SS 35/10 Vernadovskaya | 2,5+1,6 |  | 0.47 | 0.25 | 80 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available |  |  | 4.1 | 4.1
139 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.22 | 0.15 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | available | 139 | SS 35/10 Gagarinskaya | 2,5+1,6 |  | 0.22 | 0.15 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | available |  |  | 4.1 | 4.1
140 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.6 | 0.3 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 140 | SS 35/10 Egorovskaya | 2,5+3,2 |  | 0.6 | 0.3 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available |  |  | 5.7 | 5.7
141 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.3 |  |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | available | 141 | SS 35/10 Kershinskaya | 1,6+2,5 |  | 0.3 |  |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | available |  |  | 4.1 | 4.1
142 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.25 | 0.05 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | available | 142 | SS 35/10 Kurovshchinskaya | 2*1,6 |  | 0.25 | 0.05 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | available |  |  | 3.2 | 3.2
143 | SS 35/10 Lipovskaya | 2.5 | 0.22 | 0.27 | 1 day and night | -0.05 | 0 | 2.625 | 2.675 | 2.675 | available | 143 | SS 35/10 Lipovskaya | 2.5 |  | 0.22 | 0.27 | 1 day and night | -0.05 | 0 | 2.625 | 2.675 | 2.675 | available |  |  | 2.5 | 2.5
144 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.13 | 0.11 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available | 144 | SS 35/10 Lomovisskaya | 3,2+2,5 |  | 0.13 | 0.11 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | available |  |  | 5.7 | 5.7
145 | SS 35/10 Mitropolskaya | 2.5 | 0.7 | 0.28 | 1 day and night | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available | 145 | SS 35/10 Mitropolskaya | 2.5 |  | 0.7 | 0.28 | 1 day and night | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available |  |  | 2.5 | 2.5
146 | SS 35/10 P.Uglovskaya | 1.6 | 0.41 | 0.15 | 1 day and night | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 146 | SS 35/10 P.Uglovskaya | 1.6 |  | 0.41 | 0.15 | 1 day and night | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available |  |  | 1.6 | 1.6
147 | SS 35/10 Rudovskaya | 2*2,5 | 0.52 |  |  | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 147 | SS 35/10 Rudovskaya | 2*2,5 | 0.89 | 1.41 |  |  | 1.41 | 0 | 2.625 | 1.215 | 1.215 | available |  |  | 5 | 5
148 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.24 | 0.23 | 1 day and night | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available | 148 | SS 35/10 V.Yaroslavskaya | 2.5 | 1.83 | 2.07 | 0.23 | 1 day and night | 1.84 | 0 | 2.625 | 0.785 | 0.785 | available |  |  | 2.5 | 2.5
149 | SS 35/10 Degtyanskaya | 2.5 | 1.1 | 0.4 | 1 day and night | 0.7 | 0 | 2.625 | 1.925 | 1.925 | available | 149 | SS 35/10 Degtyanskaya | 2.5 |  | 1.1 | 0.4 | 1 day and night | 0.7 | 0 | 2.625 | 1.925 | 1.925 | available |  |  | 2.5 | 2.5
150 | SS 35/10 Zelenaya-2 | 1.6 | 0.18 | 0.18 | 1 day and night | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 150 | SS 35/10 Zelenaya-2 | 1.6 |  | 0.18 | 0.18 | 1 day and night | 0 | 0 | 1.68 | 1.68 | 1.68 | available |  |  | 1.6 | 1.6
151 | SS 35/10 Kulevatovskaya | 2*4 | 1.84 | 0.5 | 80 | 1.34 | 0 | 4.2 | 2.86 | 2.86 | available | 151 | SS 35/10 Kulevatovskaya | 2*4 |  | 1.84 | 0.5 | 80 | 1.34 | 0 | 4.2 | 2.86 | 2.86 | available |  |  | 8 | 8
152 | SS 35/10 Lamskaya | 4+2,5 | 0.64 | 0.2 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 152 | SS 35/10 Lamskaya | 4+2,5 | 1.83 | 2.47 | 0.2 | 120 | 2.27 | 0 | 2.625 | 0.355 | 0.355 | available |  |  | 6.5 | 6.5
153 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.24 |  |  | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 153 | SS 35/10 Gryaznovskaya | 2*2,5 |  | 0.24 |  |  | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available |  |  | 5 | 5
154 | SS 35/10 Otyasskaya | 2*2,5 | 0.42 | 0.2 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available | 154 | SS 35/10 Otyasskaya | 2*2,5 |  | 0.42 | 0.2 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | available |  |  | 5 | 5
155 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.17 | 0.19 | 1 day and night | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available | 155 | SS 35/10 P.Vasilyevskaya | 1.6 |  | 0.17 | 0.19 | 1 day and night | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available |  |  | 1.6 | 1.6
156 | SS 35/10 Podlesnaya | 2*2,5 | 0.6 | 0.22 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available | 156 | SS 35/10 Podlesnaya | 2*2,5 |  | 0.6 | 0.22 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available |  |  | 5 | 5
157 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0.5 | 0.2 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 157 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 |  | 0.5 | 0.2 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available |  |  | 5 | 5
158 | SS 35/10 Zherdevskaya | 4 | 3.33 | 0.5 | 1 day and night | 2.83 | 0 | 4.2 | 1.37 | 1.37 | available | 158 | SS 35/10 Zherdevskaya | 4 |  | 3.33 | 0.5 | 1 day and night | 2.83 | 0 | 4.2 | 1.37 | 1.37 | available |  |  | 4 | 4
159 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.3 |  |  | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 159 | SS 35/10 Sukmanovskaya | 2*2,5 |  | 0.3 |  |  | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available |  |  | 5 | 5
160 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.44 | 0.29 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 160 | SS 35/10 Tugolukovskaya | 2,5+4 |  | 0.44 | 0.29 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available |  |  | 6.5 | 6.5
161 | SS 35/10 Artemovskaya | 2*4 | 0.8 | 0.35 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | available | 161 | SS 35/10 Artemovskaya | 2*4 | 2.4 | 3.2 | 0.35 | 120 | 2.85 | 0 | 4.2 | 1.35 | 1.35 | available | Scheduled reconstruction works (replacement of a transformer capacity of 2,5 MVA to 4 MVA) |  | 8 | 8
162 | SS 35/10 RSKhO | 2,5+4 | 1.3 | 1.16 | 80 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 162 | SS 35/10 RSKhO | 2,5+4 | 1.92 | 3.22 | 1.16 | 80 | 2.06 | 0 | 2.625 | 0.565 | 0.565 | available |  |  | 6.5 | 6.5
163 | SS 35/10 Maksimovskaya | 2*1,6 | 0.18 | 0.18 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available | 163 | SS 35/10 Maksimovskaya | 2*1,6 |  | 0.18 | 0.18 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | available |  |  | 3.2 | 3.2
164 | SS 35/10 Burnakskaya | 5,6+6,3 | 2.48 |  |  | 2.48 | 0 | 5.88 | 3.4 | 3.4 | available | 164 | SS 35/10 Burnakskaya | 5,6+6,3 | 0.24 | 2.72 |  |  | 2.72 | 0 | 5.88 | 3.16 | 3.16 | available |  |  | 11.9 | 11.9
165 | SS 35/10 Poletaevskaya | 2*4 | 0.26 | 0.19 | 120 | 0.07 | 2.18 | 4.2 | 1.95 | 1.95 | available | 165 | SS 35/10 Poletaevskaya | 2*4 |  | 0.26 | 0.19 | 120 | 0.07 | 2.18 | 4.2 | 1.95 | 1.95 | available |  |  | 8 | 8
166 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.79 |  |  | 0.79 | 0 | 4.2 | 3.41 | 3.41 | available | 166 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 |  | 0.79 |  |  | 0.79 | 0 | 4.2 | 3.41 | 3.41 | available |  |  | 6.5 | 6.5
167 | SS 35/10 Pioner | 1,6+2,5 | 0.98 | 0.3 | 60 | 0.68 | 0 | 1.68 | 1 | 1 | available | 167 | SS 35/10 Pioner | 1,6+2,5 |  | 0.98 | 0.3 | 60 | 0.68 | 0 | 1.68 | 1 | 1 | available |  |  | 4.1 | 4.1
168 | SS 35/10 Lvovskaya | 2*2,5 | 0.44 | 0.2 | 120 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 168 | SS 35/10 Lvovskaya | 2*2,5 |  | 0.44 | 0.2 | 120 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available |  |  | 5 | 5
169 | SS 35/10 Nadezhdinskaya | 1.6 | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available | 169 | SS 35/10 Nadezhdinskaya | 1.6 |  | 0.37 | 0.28 | 1 day and night | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available |  |  | 1.6 | 1.6
170 | SS 35/10 Kuleshovskaya | 2.5 | 0.37 | 0.26 | 1 day and night | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 170 | SS 35/10 Kuleshovskaya | 2.5 |  | 0.37 | 0.26 | 1 day and night | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available |  |  | 2.5 | 2.5
171 | SS 35/10 Chernyaevskaya | 2*4 | 1.1 |  |  | 1.1 | 0 | 4.2 | 3.1 | 3.1 | available | 171 | SS 35/10 Chernyaevskaya | 2*4 |  | 1.1 |  |  | 1.1 | 0 | 4.2 | 3.1 | 3.1 | available |  |  | 8 | 8
172 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 172 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 |  | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available |  |  | 5 | 5
173 | SS 35/10 Shulginskaya | 2*2,5 | 0.54 | 0.02 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available | 173 | SS 35/10 Shulginskaya | 2*2,5 |  | 0.54 | 0.02 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | available |  |  | 5 | 5
174 | SS 35/10 Lavrovskaya | 2*2,5 | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 174 | SS 35/10 Lavrovskaya | 2*2,5 |  | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available |  |  | 5 | 5
175 | SS 35/10 N.Sergievskaya | 3.2 | 0.5 | 0.3 | 1 day and night | 0.2 | 0 | 3.36 | 3.16 | 3.16 | available | 175 | SS 35/10 N.Sergievskaya | 3.2 |  | 0.5 | 0.3 | 1 day and night | 0.2 | 0 | 3.36 | 3.16 | 3.16 | available |  |  | 3.2 | 3.2
176 | SS 35/10 Kamenskaya | 2*2,5 | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 176 | SS 35/10 Kamenskaya | 2*2,5 |  | 0.4 |  |  | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available |  |  | 5 | 5
177 | SS 35/10 Protasovskaya | 4+2,5 | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 177 | SS 35/10 Protasovskaya | 4+2,5 |  | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available |  |  | 6.5 | 6.5
178 | SS 35/10 Chakinskaya | 4 | 0.53 | 0.53 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | available | 178 | SS 35/10 Chakinskaya | 4 |  | 0.53 | 0.53 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | available |  |  | 4 | 4
179 | SS 35/10 Lukinskaya | 2.5 | 0.14 | 0.22 | 1 day and night | -0.08 | 0 | 2.625 | 2.705 | 2.705 | available | 179 | SS 35/10 Lukinskaya | 2.5 |  | 0.14 | 0.22 | 1 day and night | -0.08 | 0 | 2.625 | 2.705 | 2.705 | available |  |  | 2.5 | 2.5
180 | SS 35/10 Zolotovskaya | 2.5 | 0.24 | 0.2 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available | 180 | SS 35/10 Zolotovskaya | 2.5 |  | 0.24 | 0.2 | 1 day and night | 0.04 | 0 | 2.625 | 2.585 | 2.585 | available |  |  | 2.5 | 2.5
181 | SS 35/10 Mozdokskaya | 2.5 | 0.21 |  |  | 0.21 | 0 | 0 | -0.21 | -0.21 | unavailable | 181 | SS 35/10 Mozdokskaya | 2.5 |  | 0.21 |  |  | 0.21 | 0 | 0 | -0.21 | -0.21 | unavailable |  |  | 2.5 | 2.5
182 | SS 35/10 Oblovskaya | 2*2,5 | 0.38 | 0.25 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available | 182 | SS 35/10 Oblovskaya | 2*2,5 |  | 0.38 | 0.25 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | available |  |  | 5 | 5
183 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.48 | 0.07 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | available | 183 | SS 35/10 V.Vershinskaya | 2,5+4 |  | 0.48 | 0.07 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | available |  |  | 6.5 | 6.5
184 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 184 | SS 35/10 Luchevskaya | 2,5+1,6 |  | 0.26 |  |  | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available |  |  | 4.1 | 4.1
185 | SS 35/10 Olshanskaya | 4+2,5 | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | available | 185 | SS 35/10 Olshanskaya | 4+2,5 |  | 0.93 | 0.32 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | available |  |  | 6.5 | 6.5
186 | SS 35/10 Pavlodarskaya | 2.5 | 0.24 | 0.1 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 186 | SS 35/10 Pavlodarskaya | 2.5 |  | 0.24 | 0.1 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available |  |  | 2.5 | 2.5
187 | SS 35/10 Berezovskaya | 2*2,5 | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 187 | SS 35/10 Berezovskaya | 2*2,5 |  | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available |  |  | 5 | 5
188 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.28 | 0.29 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available | 188 | SS 35/10 K.Zvezdinskaya | 2*1,6 |  | 0.28 | 0.29 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available |  |  | 3.2 | 3.2
189 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available | 189 | SS 35/10 Prudkovskaya | 1,6+2,5 |  | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | available |  |  | 4.1 | 4.1
190 | SS 35/10 Shapkinskaya | 2*4 | 0.62 |  |  | 0.62 | 0 | 4.2 | 3.58 | 3.58 | available | 190 | SS 35/10 Shapkinskaya | 2*4 |  | 0.62 |  |  | 0.62 | 0 | 4.2 | 3.58 | 3.58 | available |  |  | 8 | 8
191 | SS 35/10 Maryinskaya | 2*1,6 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.68 | 1.75 | 1.75 | available | 191 | SS 35/10 Maryinskaya | 2*1,6 |  | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.68 | 1.75 | 1.75 | available |  |  | 3.2 | 3.2
192 | SS 35/10 Irskaya | 1,6+2,5 | 0.16 | 0.35 | 120 | -0.19 | 0 | 1.68 | 1.87 | 1.87 | available | 192 | SS 35/10 Irskaya | 1,6+2,5 |  | 0.16 | 0.35 | 120 | -0.19 | 0 | 1.68 | 1.87 | 1.87 | available |  |  | 4.1 | 4.1
193 | SS 35/10 Zavodskaya | 2*4 | 0.6 | 0.3 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | available | 193 | SS 35/10 Zavodskaya | 2*4 |  | 0.6 | 0.3 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | available |  |  | 8 | 8
194 | SS 35/10 Kalaisskaya | 2.5 | 0.42 | 0.28 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available | 194 | SS 35/10 Kalaisskaya | 2.5 |  | 0.42 | 0.28 | 1 day and night | 0.14 | 0 | 2.625 | 2.485 | 2.485 | available |  |  | 2.5 | 2.5
195 | SS 35/10 Sokolovskaya | 2*2,5 | 1.56 | 0.3 | 80 | 1.26 | 0 | 2.625 | 1.365 | 1.365 | available | 195 | SS 35/10 Sokolovskaya | 2*2,5 |  | 1.56 | 0.3 | 80 | 1.26 | 0 | 2.625 | 1.365 | 1.365 | available |  |  | 5 | 5
196 | SS 35/10 Veterinarnaya | 2.5 | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | available | 196 | SS 35/10 Veterinarnaya | 2.5 |  | 0.1 | 0.13 | 1 day and night | -0.03 | 0 | 2.625 | 2.655 | 2.655 | available |  |  | 2.5 | 2.5
197 | SS 35/10 Glukhovskaya | 2.5 | 0.24 | 0.09 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 197 | SS 35/10 Glukhovskaya | 2.5 |  | 0.24 | 0.09 | 1 day and night | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available |  |  | 2.5 | 2.5
198 | SS 35/10 Orzhevskaya | 2.5 | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 198 | SS 35/10 Orzhevskaya | 2.5 |  | 0.4 | 0.2 | 1 day and night | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available |  |  | 2.5 | 2.5
199 | SS 35/10 Umyotskaya | 2*4 | 1.51 | 0.4 | 120 | 1.11 | 0 | 4.2 | 3.09 | 3.09 | available | 199 | SS 35/10 Umyotskaya | 2*4 |  | 1.51 | 0.4 | 120 | 1.11 | 0 | 4.2 | 3.09 | 3.09 | available |  |  | 8 | 8
200 | SS 35/10 Gavrilovskaya | 2*4 | 1.51 | 0.5 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | available | 200 | SS 35/10 Gavrilovskaya | 2*4 |  | 1.51 | 0.5 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | available |  |  | 8 | 8
201 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.72 | 0.3 | 80 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available | 201 | SS 35/10 Peresypkinskaya | 2*2,5 |  | 0.72 | 0.3 | 80 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | available |  |  | 5 | 5
202 | SS 35/10 Annenskaya | 2*2,5 | 0.84 | 0.3 | 80 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 202 | SS 35/10 Annenskaya | 2*2,5 |  | 0.84 | 0.3 | 80 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available |  |  | 5 | 5
203 | SS 35/10 Filatovskaya | 2*2,5 | 0.41 | 0.33 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | available | 203 | SS 35/10 Filatovskaya | 2*2,5 |  | 0.41 | 0.33 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | available |  |  | 5 | 5
204 | SS 35/10 Nikitinskaya | 2*4 | 1.69 | 0.14 | 120 | 1.55 | 0 | 4.2 | 2.65 | 2.65 | available | 204 | SS 35/10 Nikitinskaya | 2*4 |  | 1.69 | 0.14 | 120 | 1.55 | 0 | 4.2 | 2.65 | 2.65 | available |  |  | 8 | 8
205 | SS 35/10 Balykleyskaya | 2*2,5 | 1.18 | 0.2 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | available | 205 | SS 35/10 Balykleyskaya | 2*2,5 |  | 1.18 | 0.2 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | available |  |  | 5 | 5
206 | SS 35/10 Karavainskaya | 2*1,6 | 0.25 | 0.3 | 80 | -0.05 | 0 | 1.68 | 1.73 | 1.73 | available | 206 | SS 35/10 Karavainskaya | 2*1,6 |  | 0.25 | 0.3 | 80 | -0.05 | 0 | 1.68 | 1.73 | 1.73 | available |  |  | 3.2 | 3.2
207 | SS 35/10 Pavlovskaya | 3.2 | 0.29 | 0.28 | 1 day and night | 0.01 | 0 | 3.36 | 3.35 | 3.35 | available | 207 | SS 35/10 Pavlovskaya | 3.2 |  | 0.29 | 0.28 | 1 day and night | 0.01 | 0 | 3.36 | 3.35 | 3.35 | available |  |  | 3.2 | 3.2
| Total: | 2485.1 | 531.13 | [8 empty] | 2: Total:; 3: 2511.6; 5: 615.9 |  | TOTAL 35kV | 785.2 | 787.7
| deficit | [8 empty] | -1.25 |  | 2: deficit; Min 12: -0.6
| proficit | [8 empty] | 896.555 |  | 2: proficit; Min 12: 838.43 |  | TOTAL 35+110 | 2485.1 | 2511.6

## Total current deficit June 2012
The list of closed supply centers of IDGC of Centre - Tambovenergo division according to winter load measurements as of June 1, 2011 (current deficit of capacity).
No. | Name of supply center, voltage class, transformer capacity (installed MVA) |  | Current deficit, MVA
Tambovenergo
1 | SS 35/10 Sukhotinskaya | 2.5 | -0.65
2 | SS 35/10 Viktorskaya | 2.5 | -0.39
3 | SS 35/10 Mozdokskaya | 2.5 | -0.21
Total current deficit (01.06.12) |  |  | -1.25

## Total expected deficit Jun 2012
The list of closed supply centers of IDGC of Centre - Tambovenergo with expected load taking into account new connections and other development of the electical networks as of as of June 1, 2011 (expected deficitof capacity).
No. | Name of supply center, voltage class |  | Expected deficit/proficit, MVA
Tambovenergo
1 | SS 35/10 Viktorskaya | 2.5 | -0.39
2 | SS 35/10 Mozdokskaya | 2.5 | -0.21
Total expected deficit (1.06.12) |  |  | -0.6