## Summary
Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2011 | [11 empty] | Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2011
[11 empty] | Table 1 | [12 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | No. 44 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | available | 1 | No. 44 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | available
2 | Stupino | 6.3 | 0.78 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.2575 | 0.2575 | available | 2 | Stupino | 6.3 | 1.51 | 2.29 | 1.0375 | 120 | 1.2525 | 0 | 1.0375 | -1.2525 | -1.2525 | unavailable
3 | P.Kommuna | 6.3 | 0.5 | 0.5 | 120 | 0.5 | 0 | 0.5 | 0 | 0 | available | 3 | P.Kommuna | 6.3 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 0.5 | 0 | 0 | available
4 | No. 38 | 2.5 | 0.55 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.25 | 0.25 | available | 4 | No. 38 | 2.5 | 0 | 0.55 | 0.8 | 120 | -0.25 | 0 | 0.8 | 0.25 | 0.25 | available
5 | No. 46 | 4 | 0.11 | 0 | 0 | 0 | 0 | 0 | -0.11 | -0.11 | unavailable | 5 | No. 46 | 4 | 0 | 0.11 | 0 | 0 | 0.11 | 0 | 0 | -0.11 | -0.11 | unavailable
6 | Istobnoe | 4 | 0.33 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.03 | 0.03 | available | 6 | Istobnoe | 4 | 0.29 | 0.62 | 0.36 | 120 | 0.26 | 0 | 0.36 | -0.26 | -0.26 | unavailable
7 | Rodina | 2.5 | 0 | 2.2 | 120 | 2.2 | 0 | 2.2 | 2.2 | 2.2 | available | 7 | Rodina | 2.5 | 0.2 | 0.2 | 2.2 | 120 | -2 | 0 | 2.2 | 2 | 2 | available
8 | Vyaznovatovka | 2.5 | 0.87 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.63 | 0.63 | available | 8 | Vyaznovatovka | 2.5 | 0.02 | 0.89 | 1.5 | 120 | -0.61 | 0 | 1.5 | 0.61 | 0.61 | available
9 | V.Turovo-1 | 3.2 | 1.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.25 | 0.25 | available | 9 | V.Turovo-1 | 3.2 | 0.19 | 1.44 | 1.5 | 120 | -0.06 | 0 | 1.5 | 0.06 | 0.06 | available
10 | Semidesyatnoe | 2.5 | 0.24 | 0 | 0 | 0 | 0 | 0 | -0.24 | -0.24 | unavailable | 10 | Semidesyatnoe | 2.5 | 0.13 | 0.37 | 0 | 0 | 0.37 | 0 | 0 | -0.37 | -0.37 | unavailable
11 | Arkhangelskoe SPS | 2.5 | 1.33 | 0 | 0 | 0 | 0 | 0 | -1.33 | -1.33 | unavailable | 11 | Arkhangelskoe SPS | 2.5 | 0.5 | 1.83 | 0 | 0 | 1.83 | 0 | 0 | -1.83 | -1.83 | unavailable
12 | Khokhol-2 | 4 | 0.98 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | -0.2226 | -0.2226 | unavailable | 12 | Khokhol-2 | 4 | 0.1 | 1.08 | 0.7574 | 120 | 0.3226 | 0 | 0.7574 | -0.3226 | -0.3226 | unavailable
13 | N.Olshanka | 2.5 | 0.27 | 0 | 0 | 0 | 0 | 0 | -0.27 | -0.27 | unavailable | 13 | N.Olshanka | 2.5 | 0.01 | 0.28 | 0 | 0 | 0.28 | 0 | 0 | -0.28 | -0.28 | unavailable
14 | Troitskoe | 4 | 0.66 | 0 | 0 | 0 | 0 | 0 | -0.66 | -0.66 | unavailable | 14 | Troitskoe | 4 | 0.67 | 1.33 | 0 | 0 | 1.33 | 0 | 0 | -1.33 | -1.33 | unavailable
15 | Zemlyansk | 2.5 | 0.55 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.4036 | 0.4036 | available | 15 | Zemlyansk | 2.5 | 0 | 0.55 | 0.9536 | 120 | -0.4036 | 0 | 0.9536 | 0.4036 | 0.4036 | available
16 | Losevo SPS | 2.5 | 1.53 | 2.15 | 120 | 2.15 | 0 | 2.15 | 0.62 | 0.62 | available | 16 | Losevo SPS | 2.5 | 0.13 | 1.66 | 2.15 | 120 | -0.49 | 0 | 2.15 | 0.49 | 0.49 | available
17 | Verny | 2.5 | 1.37 | 1.1 | 120 | 1.1 | 0 | 1.1 | -0.27 | -0.27 | unavailable | 17 | Verny | 2.5 | 0.03 | 1.4 | 1.1 | 120 | 0.3 | 0 | 1.1 | -0.3 | -0.3 | unavailable
18 | Elevator | 4 | 1.16 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.44 | 0.44 | available | 18 | Elevator | 4 | 0.07 | 1.23 | 1.6 | 120 | -0.37 | 0 | 1.6 | 0.37 | 0.37 | available
19 | Yubileynaya | 4 | 2.63 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.5284 | 0.5284 | available | 19 | Yubileynaya | 4 | 0.18 | 2.81 | 3.1584 | 120 | -0.3484 | 0 | 3.1584 | 0.3484 | 0.3484 | available
20 | Parusnoe | 4 | 1.6 | 2.05 | 120 | 2.05 | 0 | 2.05 | 0.45 | 0.45 | available | 20 | Parusnoe | 4 | 0.09 | 1.69 | 2.05 | 120 | -0.36 | 0 | 2.05 | 0.36 | 0.36 | available
21 | Rogachyovka | 2.5 | 0.08 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.22 | 0.22 | available | 21 | Rogachyovka | 2.5 | 0 | 0.08 | 0.3 | 120 | -0.22 | 0 | 0.3 | 0.22 | 0.22 | available
22 | Poultry farm Rassvet | 6.3 | 1.37 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.03 | 0.03 | available | 22 | Poultry farm Rassvet | 6.3 | 0 | 1.37 | 1.4 | 120 | -0.03 | 1 | 1.4 | 0.03 | 0.03 | available
23 | Dankovo | 2.5 | 0.8 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.099 | 0.099 | available | 23 | Dankovo | 2.5 | 0.02 | 0.82 | 0.899 | 120 | -0.079 | 0 | 0.899 | 0.079 | 0.079 | available
24 | Bugaevka | 16 | 7.84 | 14 | 90 | 14 | 0 | 14 | 6.16 | 1.56 | available | 24 | Bugaevka | 16 | 0.28 | 8.12 | 14 | 90 | -5.88 | 0 | 14 | 5.88 | 1.28 | available
| Sn. MV, МVА | 16 | 5.4 | 10 | 90 | 10 | 0 | 10 | 4.6 |  |  |  | Sn. MV, МVА | 16 | 0 | 5.4 | 10 | 90 | -4.6 | 0 | 10 | 4.6
| Sn. LV, МVА | 16 | 2.44 | 4 | 90 | 4 | 0 | 4 | 1.56 |  |  |  | Sn. LV, МVА | 16 | 0.28 | 2.72 | 4 | 90 | -1.28 | 0 | 4 | 1.28
25 | Dobrino | 10 | 2.07 | 8.9 | 90 | 8.9 | 0 | 8.9 | 6.83 | 1.12 | available | 25 | Dobrino | 10 | 0.24 | 2.31 | 6.6 | 90 | -4.29 | 0 | 6.6 | 4.29 | 0.88 | available
| Sn. MV, МVА | 10 | 0 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.8 |  |  |  | Sn. MV, МVА | 10 | 0 | 0 | 5.8 | 90 | -5.8 | 0 | 5.8 | 5.8
| Sn. LV, МVА | 10 | 2 | 3.12 | 90 | 3.12 | 0 | 3.12 | 1.12 |  |  |  | Sn. LV, МVА | 10 | 0.24 | 2.24 | 3.12 | 90 | -0.88 | 0 | 3.12 | 0.88
26 | N. Kalitva | 6.3 | 1.43 | 2.1 | 240 | 2.1 | 0 | 2.1 | 0.67 | 0.67 | available | 26 | N. Kalitva | 6.3 | 0.6 | 2.03 | 2.1 | 240 | -0.07 | 0 | 2.1 | 0.07 | 0.07 | available
27 | Shishovka | 6.3 | 0.69 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.65 | 1.65 | available | 27 | Shishovka | 6.3 | 0.44 | 1.13 | 2.34 | 180 | -1.21 | 0 | 2.34 | 1.21 | 1.21 | available
28 | Azovka | 10 | 1.91 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.21 | 1.21 | available | 28 | Azovka | 10 | 0.59 | 2.5 | 3.12 | 180 | -0.62 | 0 | 3.12 | 0.62 | 0.62 | available
29 | Yurasovka | 2.5 | 0.84 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.72 | 0.72 | available | 29 | Yurasovka | 2.5 | 0.03 | 0.87 | 1.56 | 120 | -0.69 | 0 | 1.56 | 0.69 | 0.69 | available
30 | Nerovnovka | 2.5 | 0.28 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.5 | 0.5 | available | 30 | Nerovnovka | 2.5 | 0.02 | 0.3 | 0.78 | 240 | -0.48 | 0 | 0.78 | 0.48 | 0.48 | available
31 | Saprino | 1.8 | 0.4 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.4 | 1.4 | available | 31 | Saprino | 1.8 | 0.04 | 0.44 | 1.8 | 120 | -1.36 | 0 | 1.8 | 1.36 | 1.36 | available
32 | Sergeevka | 4 | 0.53 | 0 | 0 | 0 | 0 | 0 | -0.53 | -0.53 | unavailable | 32 | Sergeevka | 4 | 0.06 | 0.59 | 0 | 0 | 0.59 | 0 | 0 | -0.59 | -0.59 | unavailable
33 | Stepanovka | 4 | 0.32 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.24 | 1.24 | available | 33 | Stepanovka | 4 | 0.07 | 0.39 | 1.56 | 240 | -1.17 | 0 | 1.56 | 1.17 | 1.17 | available
34 | Kolodezhanskaya | 2.5 | 0.24 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.54 | 0.54 | available | 34 | Kolodezhanskaya | 2.5 | 0.14 | 0.38 | 0.78 | 180 | -0.4 | 0 | 0.78 | 0.4 | 0.4 | available
35 | Andreevka | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | available | 35 | Andreevka | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | available
36 | Kulikovka | 4 | 1.75 | 0 | 0 | 0 | 0 | 0 | -1.75 | -1.75 | unavailable | 36 | Kulikovka | 4 | 0.48 | 2.23 | 0 | 0 | 2.23 | 0 | 0 | -2.23 | -2.23 | unavailable
37 | Lizinovka | 2.5 | 0.87 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.63 | 1.63 | available | 37 | Lizinovka | 2.5 | 0.07 | 0.94 | 2.5 | 240 | -1.56 | 0 | 2.5 | 1.56 | 1.56 | available
38 | Sotnitskaya | 4 | 1.45 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.85 | 0.85 | available | 38 | Sotnitskaya | 4 | 0.17 | 1.62 | 2.3 | 120 | -0.68 | 0 | 2.3 | 0.68 | 0.68 | available
39 | Kr. Polyana | 2.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 | unavailable | 39 | Kr. Polyana | 2.5 | 0.04 | 0.39 | 0 | 0 | 0.39 | 0 | 0 | -0.39 | -0.39 | unavailable
40 | Gumny | 4 | 0.8 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.76 | 0.76 | available | 40 | Gumny | 4 | 0.2 | 1 | 1.56 | 180 | -0.56 | 0 | 1.56 | 0.56 | 0.56 | available
41 | Uryv | 2.5 | 0.67 | 0 | 0 | 0 | 0 | 0 | -0.67 | -0.67 | unavailable | 41 | Uryv | 2.5 | 0.13 | 0.8 | 0 | 0 | 0.8 | 0 | 0 | -0.8 | -0.8 | unavailable
42 | Shubnoe | 2.5 | 1.18 | 1.45 | 180 | 1.45 | 0 | 1.45 | 0.27 | 0.27 | available | 42 | Shubnoe | 2.5 | 0.2 | 1.38 | 1.45 | 180 | -0.07 | 0 | 1.45 | 0.07 | 0.07 | available
43 | Zaluzhnoe | 2.5 | 2.16 | 2 | 240 | 2 | 0 | 2 | -0.16 | -0.16 | unavailable | 43 | Zaluzhnoe | 2.5 | 0.57 | 2.73 | 2 | 240 | 0.73 | 0 | 2 | -0.73 | -0.73 | unavailable
44 | Anna-2 | 25 | 6.18 | 7.8 | 90 | 7.8 | 0 | 7.8 | 1.62 | 0.31 | available | 44 | Anna-2 | 25 | 4.01 | 10.19 | 7.8 | 90 | 2.39 | 0 | 7.8 | -2.39 | -2.7 | unavailable
| Sn. MV, МVА | 25 | 1.93 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.31 |  |  |  | Sn. MV, МVА | 25 | 0 | 1.93 | 2.24 | 90 | -0.31 | 0 | 2.24 | 0.31
| Sn. LV, МVА | 25 | 4.25 | 5.56 | 90 | 5.56 | 0 | 5.56 | 1.31 |  |  |  | Sn. LV, МVА | 25 | 4.01 | 8.26 | 5.56 | 90 | 2.7 | 0 | 5.56 | -2.7
45 | Vostochnaya | 10 | 3.62 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.18 | 1.18 | available | 45 | Vostochnaya | 10 | 1.14 | 4.76 | 4.8 | 30 | -0.04 | 0 | 4.8 | 0.04 | 0.04 | available
46 | BolshevikBPS | 6.3 | 0.9 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.56 | 0.56 | available | 46 | BolshevikBPS | 6.3 | 0.06 | 0.96 | 1.46 | 60 | -0.5 | 0 | 1.46 | 0.5 | 0.5 | available
47 | Rozhdestvo | 6.3 | 0.66 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.09 | 0.09 | available | 47 | Rozhdestvo | 6.3 | 0.36 | 1.02 | 0.75 | 60 | 0.27 | 0 | 0.75 | -0.27 | -0.27 | unavailable
48 | V. Toyda | 6.3 | 1 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.4 | 0.4 | available | 48 | V. Toyda | 6.3 | 0.01 | 1.01 | 1.4 | 90 | -0.39 | 0 | 1.4 | 0.39 | 0.39 | available
49 | Vostochnaya-1 | 40 | 7.63 | 8.13 | 60 | 8.13 | 0 | 8.13 | 0.5 | -0.54 | unavailable | 49 | Vostochnaya-1 | 40 | 1.3 | 8.93 | 8.13 | 60 | 0.8 | 0 | 8.13 | -0.8 | -0.8 | unavailable
| Sn. MV, МVА | 40 | 6.21 | 5.67 | 60 | 5.67 | 0 | 5.67 | -0.54 |  |  |  | Sn. MV, МVА | 40 | 0 | 6.21 | 5.67 | 60 | 0.54 | 0 | 5.67 | -0.54
| Sn. LV, МVА | 40 | 2.19 | 3.1 | 60 | 3.1 | 0 | 3.1 | 0.91 |  |  |  | Sn. LV, МVА | 40 | 1.3 | 3.49 | 3.1 | 60 | 0.39 | 0 | 3.1 | -0.39
50 | Makashevka | 2.5 | 0.36 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.12 | 0.12 | available | 50 | Makashevka | 2.5 | 0.12 | 0.48 | 0.48 | 180 | 0 | 0 | 0.48 | 0 | 0 | available
51 | Mirolyubie | 4 | 0.31 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.19 | 0.19 | available | 51 | Mirolyubie | 4 | 0.03 | 0.34 | 0.5 | 60 | -0.16 | 0 | 0.5 | 0.16 | 0.16 | available
52 | V. Zaton | 2.5 | 0 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | available | 52 | V. Zaton | 2.5 | 0 | 0 | 0.01 | 60 | -0.01 | 0 | 0.01 | 0.01 | 0.01 | available
53 | Oktyabrskoe | 2.5 | 0.59 | 0.8 | 30 | 0.8 | 0 | 0.8 | 0.21 | 0.21 | available | 53 | Oktyabrskoe | 2.5 | 0.19 | 0.78 | 0.8 | 30 | -0.02 | 0 | 0.8 | 0.02 | 0.02 | available
54 | Ilmen | 2.5 | 0.24 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.14 | 0.14 | available | 54 | Ilmen | 2.5 | 0.05 | 0.29 | 0.38 | 60 | -0.09 | 0 | 0.38 | 0.09 | 0.09 | available
55 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 | available | 55 | Vikhlyaevka | 2.5 | 0.01 | 0.11 | 0.12 | 120 | -0.01 | 0 | 0.12 | 0.01 | 0.01 | available
56 | N. Elan | 2.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | -0.5 | -0.5 | unavailable | 56 | N. Elan | 2.5 | 0.05 | 0.55 | 0 | 0 | 0.55 | 0 | 0 | -0.55 | -0.55 | unavailable
57 | B. Alabukhi | 2.5 | 0.83 | 1.1 | 90 | 1.1 | 0 | 1.1 | 0.27 | 0.27 | available | 57 | B. Alabukhi | 2.5 | 0.25 | 1.08 | 1.1 | 90 | -0.02 | 0 | 1.1 | 0.02 | 0.02 | available
58 | Pykhovka | 2.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | -0.25 | -0.25 | unavailable | 58 | Pykhovka | 2.5 | 0 | 0.25 | 0 | 0 | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable
59 | Е. Koleno | 4 | 2.96 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.37 | 0.37 | available | 59 | Е. Koleno | 4 | 0.1 | 3.06 | 3.33 | 120 | -0.27 | 0 | 3.33 | 0.27 | 0.27 | available
60 | Podgornoe BPS | 2.5 | 0.41 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.05 | 0.05 | available | 60 | Podgornoe BPS | 2.5 | 0.01 | 0.42 | 0.46 | 180 | -0.04 | 0 | 0.46 | 0.04 | 0.04 | available
61 | Mikhailovka-1 | 4 | 0.3 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.06 | 0.06 | available | 61 | Mikhailovka-1 | 4 | 0 | 0.3 | 0.36 | 60 | -0.06 | 0 | 0.36 | 0.06 | 0.06 | available
62 | Mikhailovka | 2.5 | 0.31 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.19 | 0.19 | available | 62 | Mikhailovka | 2.5 | 0.01 | 0.32 | 0.5 | 60 | -0.18 | 0 | 0.5 | 0.18 | 0.18 | available
63 | Gnilusha | 4 | 0.74 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.18 | 0.18 | available | 63 | Gnilusha | 4 | 0 | 0.74 | 0.92 | 180 | -0.18 | 0 | 0.92 | 0.18 | 0.18 | available
64 | Mayskaya | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 | unavailable | 64 | Mayskaya | 2.5 | 0 | 0.42 | 0 | 0 | 0.42 | 0 | 0 | -0.42 | -0.42 | unavailable
65 | Khleborodnoe | 2.5 | 0.49 | 0 | 0 | 0 | 0 | 0 | -0.49 | -0.49 | unavailable | 65 | Khleborodnoe | 2.5 | 0.12 | 0.61 | 0 | 0 | 0.61 | 0 | 0 | -0.61 | -0.61 | unavailable
66 | N. Kurlak | 4 | 0.42 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.18 | 0.18 | available | 66 | N. Kurlak | 4 | 0 | 0.42 | 0.6 | 120 | -0.18 | 0 | 0.6 | 0.18 | 0.18 | available
67 | Nikolaevka | 4 | 1.33 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.17 | 0.17 | available | 67 | Nikolaevka | 4 | 0.06 | 1.39 | 1.5 | 120 | -0.11 | 0 | 1.5 | 0.11 | 0.11 | available
68 | Vasilyevka BPS | 2.5 | 0.48 | 0.6 | 180 | 0.6 | 0 | 0.6 | 0.12 | 0.12 | available | 68 | Vasilyevka BPS | 2.5 | 0.09 | 0.57 | 0.6 | 180 | -0.03 | 0 | 0.6 | 0.03 | 0.03 | available
69 | Avangard | 2.5 | 0.9 | 1 | 120 | 1 | 0 | 1 | 0.1 | 0.1 | available | 69 | Avangard | 2.5 | 0.07 | 0.97 | 1 | 120 | -0.03 | 0 | 1 | 0.03 | 0.03 | available
70 | Orlovka | 2.5 | 0.57 | 0.65 | 90 | 0.65 | 0 | 0.65 | 0.08 | 0.08 | available | 70 | Orlovka | 2.5 | 0.05 | 0.62 | 0.65 | 90 | -0.03 | 0 | 0.65 | 0.03 | 0.03 | available
71 | N. Chigla | 2.5 | 0.59 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.31 | 0.31 | available | 71 | N. Chigla | 2.5 | 0.11 | 0.7 | 0.9 | 120 | -0.2 | 0 | 0.9 | 0.2 | 0.2 | available
72 | Troitskoe-1 | 1.6 | 0.12 | 0.2 | 120 | 0.2 | 0 | 0.2 | 0.08 | 0.08 | available | 72 | Troitskoe-1 | 1.6 | 0 | 0.12 | 0.2 | 120 | -0.08 | 0 | 0.2 | 0.08 | 0.08 | available
73 | Tishanka | 2.5 | 1.02 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.49 | 0.49 | available | 73 | Tishanka | 2.5 | 0.05 | 1.07 | 1.51 | 120 | -0.44 | 0 | 1.51 | 0.44 | 0.44 | available
74 | Kalacheevskaya | 6.3 | 0.55 | 1 | 1 day and night | 1 | 0 | 1 | 0.45 | 0.45 | available | 74 | Kalacheevskaya | 6.3 | 1.55 | 2.1 | 1 | 1 day and night | 1.1 | 0 | 1 | -1.1 | -1.1 | unavailable
75 | B.Kazinka | 6.3 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 | -0.51 | unavailable | 75 | B.Kazinka | 6.3 | 3.09 | 3.6 | 0 | 0 | 3.6 | 0 | 0 | -3.6 | -3.6 | unavailable
| Sn. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Sn. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sn. LV, МVА | 6.3 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 |  |  |  | Sn. LV, МVА | 6.3 | 3.09 | 3.6 | 0 | 0 | 3.6 | 0 | 0 | -3.6
76 | Derezovka | 6.3 | 0.36 | 0 | 0 | 0 | 0 | 0 | -0.36 | -0.36 | unavailable | 76 | Derezovka | 6.3 | 0.07 | 0.43 | 0 | 0 | 0.43 | 0 | 0 | -0.43 | -0.43 | unavailable
77 | Osetrovka | 6.3 | 0.88 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.62 | 0.62 | available | 77 | Osetrovka | 6.3 | 2.22 | 3.1 | 1.5 | 1 day and night | 1.6 | 0 | 1.5 | -1.6 | -1.6 | unavailable
78 | sovkhoz Radchensky | 10 | 2.79 | 2 | 1 day and night | 2 | 0 | 2 | -0.79 | -2.64 | unavailable | 78 | sovkhoz Radchensky | 10 | 0.03 | 2.82 | 2 | 1 day and night | 0.82 | 0 | 2 | -0.82 | -2.64 | unavailable
| Sn. MV, МVА | 10 | 2.64 | 0 | 1 day and night | 0 | 0 | 0 | -2.64 |  |  |  | Sn. MV, МVА | 10 | 0 | 2.64 | 0 | 0 | 2.64 | 0 | 0 | -2.64
| Sn. LV, МVА | 10 | 0.15 | 2 | 1 day and night | 2 | 0 | 2 | 1.85 |  |  |  | Sn. LV, МVА | 10 | 0.03 | 0.18 | 2 | 1 day and night | -1.82 | 0 | 2 | 1.82
79 | Klepovka | 4 | 1.16 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.44 | 0.44 | available | 79 | Klepovka | 4 | 0.13 | 1.29 | 1.6 | 120 | -0.31 | 0 | 1.6 | 0.31 | 0.31 | available
80 | Krasnopolye | 4 | 0.31 | 1 | 120 | 1 | 0 | 1 | 0.69 | 0.69 | available | 80 | Krasnopolye | 4 | 0.02 | 0.33 | 1 | 120 | -0.67 | 0 | 1 | 0.67 | 0.67 | available
81 | Nikolskoe | 2.5 | 0.4 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.1 | 1.1 | available | 81 | Nikolskoe | 2.5 | 0 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | available
82 | N. Liman | 2.5 | 0.35 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.15 | 1.15 | available | 82 | N. Liman | 2.5 | 0.1 | 0.45 | 1.5 | 45 | -1.05 | 0 | 1.5 | 1.05 | 1.05 | available
83 | Bereznyagi | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 | available | 83 | Bereznyagi | 2.5 | 0.2 | 0.5 | 1.5 | 45 | -1 | 0 | 1.5 | 1 | 1 | available
84 | Kr.Flot | 2.5 | 0.27 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.23 | 1.23 | available | 84 | Kr.Flot | 2.5 | 0.14 | 0.41 | 1.5 | 45 | -1.09 | 0 | 1.5 | 1.09 | 1.09 | available
85 | R. Zhuravka | 2.5 | 0.72 | 0 | 0 | 0 | 0 | 0 | -0.72 | -0.72 | unavailable | 85 | R. Zhuravka | 2.5 | 0.08 | 0.8 | 0 | 0 | 0.8 | 0 | 0 | -0.8 | -0.8 | unavailable
86 | Gorokhovka | 2.5 | 0.55 | 1.5 | 45 | 1.5 | 0 | 1.5 | 0.95 | 0.95 | available | 86 | Gorokhovka | 2.5 | 0.11 | 0.66 | 1.5 | 45 | -0.84 | 0 | 1.5 | 0.84 | 0.84 | available
87 | Livenka | 2.5 | 0.42 | 0.5 | 1 day and night | 0.5 | 0 | 0.5 | 0.08 | 0.08 | available | 87 | Livenka | 2.5 | 0.05 | 0.47 | 0.5 | 1 day and night | -0.03 | 0 | 0.5 | 0.03 | 0.03 | available
88 | R.Buylovka | 2.5 | 0.5 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1 | 1 | available | 88 | R.Buylovka | 2.5 | 0.06 | 0.56 | 1.5 | 45 | -0.94 | 0 | 1.5 | 0.94 | 0.94 | available
89 | Shurinovka | 2.5 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 | unavailable | 89 | Shurinovka | 2.5 | 0.03 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | unavailable
90 | SS 35/10 kV Tvyordokhlebovka | 4 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 | unavailable | 90 | SS 35/10 kV Tvyordokhlebovka | 4 | 0.1 | 0.39 | 0 | 0 | 0.39 | 0 | 0 | -0.39 | -0.39 | unavailable
91 | SS 35/10 kV Krinitsa | 2.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | -0.12 | -0.12 | unavailable | 91 | SS 35/10 kV Krinitsa | 2.5 | 0.05 | 0.17 | 0 | 0 | 0.17 | 0 | 0 | -0.17 | -0.17 | unavailable
92 | SS 35/10 kV Zarechnaya | 0.1 | 0.01 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.01 | unavailable | 92 | SS 35/10 kV Zarechnaya | 0.1 | 0 | 0.01 | 0 | 0 | 0.01 | 1 | 0 | -0.01 | -0.01 | unavailable
93 | SS 35/10 kV Archangelskaya | 2.5 | 0.56 | 0 | 0 | 0 | 0 | 0 | -0.56 | -0.56 | unavailable | 93 | SS 35/10 kV Archangelskaya | 2.5 | 0 | 0.56 | 0 | 0 | 0.56 | 2 | 0 | -0.56 | -0.56 | unavailable
94 | SS 35/10 kV Krasnogorovka | 2.5 | 0.12 | 0 | 0 | 0 | 0 | 0 | -0.12 | -0.12 | unavailable | 94 | SS 35/10 kV Krasnogorovka | 2.5 | 0.01 | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | unavailable
95 | SS 110/6 kV № 2 | 25+25 | 22.86 | 2.94 | 120 | 19.92 | 0 | 26.25 | 6.33 | 6.33 | available | 95 | SS 110/6 kV № 2 | 25+25 | 4.87 | 27.73 | 2.94 | 120 | 24.79 | 0 | 26.25 | 1.46 | 1.46 | available
96 | SS 35/6 kV № 3 | 6,3 + 10 | 9.41 | 2.5 | 120 | 6.91 | 0 | 6.615 | -0.295 | -0.295 | unavailable | 96 | SS 35/6 kV № 3 | 6,3 + 10 | 0.13 | 9.54 | 2.5 | 120 | 7.04 | 0 | 6.615 | -0.425 | -0.425 | unavailable
97 | SS 35/6 kV № 4 | 10+10+15 | 15.86 | 0 | 0 | 15.86 | 0 | 21 | 5.14 | 5.14 | available | 97 | SS 35/6 kV № 4 | 10+10+15 | 0.09 | 15.95 | 0 | 0 | 15.95 | 0 | 21 | 5.05 | 5.05 | available
98 | SS 110/6 kV № 6 | 25+32 | 15.82 | 1.6 | 120 | 14.22 | 0 | 26.25 | 12.03 | 12.03 | available | 98 | SS 110/6 kV № 6 | 25+32 | 4.21 | 20.03 | 1.6 | 120 | 18.43 | 0 | 26.25 | 7.82 | 7.82 | available
99 | SS 35/10/6 kV № 7 | 2,5+4 | 0.72 | 2.5 | 0 | -1.78 | 0 | 2.625 | 4.405 | 4.405 | available | 99 | SS 35/10/6 kV № 7 | 2,5+4 | 2.22 | 2.94 | 2.5 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available
100 | SS 35/6 kV № 8 | 4+4+4 | 6.11 | 0 | 0 | 6.11 | 0 | 8.4 | 2.29 | 2.29 | available | 100 | SS 35/6 kV № 8 | 4+4+4 | 1.92 | 8.03 | 0 | 0 | 8.03 | 0 | 8.4 | 0.37 | 0.37 | available
101 | SS 110/6 kV № 9 | 40+40 | 21.99 | 3.3 | 120 | 18.69 | 0 | 42 | 23.31 | 23.31 | available | 101 | SS 110/6 kV № 9 | 40+40 | 15.3 | 37.29 | 3.3 | 120 | 33.99 | 0 | 42 | 8.01 | 8.01 | available
102 | SS 110/6 kV Central | 63+63 | 31.86 | 13.3 | 120 | 18.56 | 0 | 66.15 | 47.59 | 47.59 | available | 102 | SS 110/6 kV Central | 63+63 | 15.3 | 47.16 | 13.3 | 120 | 33.86 | 0 | 66.15 | 32.29 | 32.29 | available
103 | SS 35/10 kV № 13 | 6,3+6,3 | 9.47 | 3.7 | 120 | 5.77 | 0 | 6.615 | 0.845 | 0.845 | available | 103 | SS 35/10 kV № 13 | 6,3+6,3 | 5.06 | 14.53 | 3.7 | 120 | 10.83 | 0 | 6.615 | -4.215 | -4.215 | unavailable
104 | SS 110/35/6 kV № 14 | 31,5+31,5 | 12.75 | 1.3 | 120 | 11.45 | 0 | 33.075 | 21.625 | 21.625 | available | 104 | SS 110/35/6 kV № 14 | 31,5+31,5 | 3.36 | 16.11 | 1.3 | 120 | 14.81 | 0 | 33.075 | 18.265 | 18.265 | available
| Sn. MV, МVА | 31,5+31,5 |  | 0 | 0 | 0 | 0 | 33.075 | 33.075 |  |  |  | Sn. MV, МVА | 31,5+31,5 | 0 | 0 | 0 | 0 | 0 | 0 | 33.075 | 33.075
| Sn. LV, МVА | 31,5+31,5 | 12.75 | 1.3 | 120 | 11.45 | 0 | 33.075 | 21.625 |  |  |  | Sn. LV, МVА | 31,5+31,5 | 3.36 | 16.11 | 1.3 | 120 | 14.81 | 0 | 33.075 | 18.265
105 | SS 110/35/6 kV № 15 | 40,5+40,5+63,0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 | 85.05 | available | 105 | SS 110/35/6 kV № 15 | 40,5+40,5+63,0 | 0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 | 67.98 | available
| Sn. MV, МVА | 40,5+40,5+63,0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72 |  |  |  | Sn. MV, МVА | 40,5+40,5+63,0 | 0 | 43.34 | 44.01 | 120 | -0.67 | 0 | 85.05 | 85.72
| Sn. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  |  | Sn. LV, МVА | 40,5+40,5+63,0 | 17.07 | 17.07 | 0 | 0 | 17.07 | 0 | 85.05 | 67.98
106 | SS 110/35/6 kV № 16 | 31,5+31,5+40,0 | 59.48 | 4 | 120 | 55.48 | 0 | 66.15 | 10.67 | 10.67 | available | 106 | SS 110/35/6 kV № 16 | 31,5+31,5+40,0 | 14.88 | 74.36 | 4 | 120 | 70.36 | 0 | 66.15 | -4.21 | -4.21 | unavailable
| Sn. MV, МVА | 31,5+31,5 | 4.5 | 0 | 0 | 4.5 | 0 | 33.075 | 28.575 |  |  |  | Sn. MV, МVА | 31,5+31,5 | 0 | 4.5 | 0 | 0 | 4.5 | 0 | 33.075 | 28.575
| Sn. LV, МVА | 31,5+31,5+40,0 | 54.98 | 4 | 120 | 50.98 | 0 | 66.15 | 15.17 |  |  |  | Sn. LV, МVА | 31,5+31,5+40,0 | 14.88 | 69.86 | 4 | 120 | 65.86 | 0 | 66.15 | 0.29
107 | SS 110/10 kV № 18 | 6,3+6,3 | 2.81 | 0 | 0 | 2.81 | 0 | 6.615 | 3.805 | 3.805 | available | 107 | SS 110/10 kV № 18 | 6,3+6,3 | 1.73 | 4.54 | 0 | 0 | 4.54 | 0 | 6.615 | 2.075 | 2.075 | available
108 | SS 110/10/6 kV № 20 | 25+25 | 22.03 | 9.6 | 120 | 12.43 | 0 | 26.25 | 13.82 | 13.82 | available | 108 | SS 110/10/6 kV № 20 | 25+25 | 10.49 | 32.52 | 9.6 | 120 | 22.92 | 0 | 26.25 | 3.33 | 3.33 | available
| Sn. MV, МVА | 25+25 | 7.55 | 4 | 0 | 3.55 | 0 | 26.25 | 22.7 |  |  |  | Sn. MV, МVА | 25+25 | 0 | 7.55 | 4 | 0 | 3.55 | 0 | 26.25 | 22.7
| Sn. LV, МVА | 25+25 | 14.48 | 5.6 | 120 | 8.88 | 0 | 26.25 | 17.37 |  |  |  | Sn. LV, МVА | 25+25 | 10.49 | 24.97 | 5.6 | 120 | 19.37 | 0 | 26.25 | 6.88
109 | SS 110/35/6 kV № 21 | 25,0+20,0+40,0 | 42.3 | 4.6 | 120 | 37.7 | 0 | 47.25 | 9.55 | 9.55 | available | 109 | SS 110/35/6 kV № 21 | 25,0+20,0+40,0 | 6.49 | 48.79 | 4.6 | 180 | 44.19 | 0 | 49.6125 | 5.4225 | 5.4225 | available
110 | SS 35/6 kV № 23 | 7,5+6,3 | 6.46 | 0.8 | 120 | 5.66 | 0 | 6.615 | 0.955 | 0.955 | available | 110 | SS 35/6 kV № 23 | 7,5+6,3 | 0 | 6.46 | 0.8 | 120 | 5.66 | 0 | 6.615 | 0.955 | 0.955 | available
111 | SS 35/6 kV № 24 | 3,2+4,0 | 1.75 | 0 | 0 | 1.75 | 0 | 3.36 | 1.61 | 1.61 | available | 111 | SS 35/6 kV № 24 | 3,2+4,0 | 0.04 | 1.79 | 0 | 0 | 1.79 | 0 | 3.36 | 1.57 | 1.57 | available
112 | SS 110/6 kV № 25 | 40+40+40 | 45.58 | 3.8 | 120 | 41.78 | 0 | 84 | 42.22 | 42.22 | available | 112 | SS 110/6 kV № 25 | 40+40+40 | 5.28 | 50.86 | 3.8 | 120 | 47.06 | 0 | 84 | 36.94 | 36.94 | available
113 | SS 110/6 kV № 27 | 32,0+32,0+63,0 | 44.43 | 3.3 | 180 | 41.13 | 0 | 67.2 | 26.07 | 26.07 | available | 113 | SS 110/6 kV № 27 | 32,0+32,0+63,0 | 24.07 | 68.5 | 3.3 | 180 | 65.2 | 0 | 67.2 | 2 | 2 | available
114 | SS 110/10 kV № 28 | 10+10 | 14.23 | 0 | 0 | 14.23 | 0 | 10.5 | -3.73 | -3.73 | unavailable | 114 | SS 110/10 kV № 28 | 10+10 | 1.78 | 16.01 | 0 | 0 | 16.01 | 0 | 10.5 | -5.51 | -5.51 | unavailable
115 | SS 110/35/6 kV № 29 | 25+25 | 27.87 | 8.4 | 120 | 19.47 | 0 | 26.25 | 6.78 | 6.78 | available | 115 | SS 110/35/6 kV № 29 | 25+25 | 5.91 | 33.78 | 5.1 | 120 | 28.68 | 0 | 26.25 | -2.43 | -2.43 | unavailable
| Sn. MV, МVА | 25+25 | 10.54 | 4.2 | 120 | 6.34 | 0 | 26.25 | 19.91 |  |  |  | Sn. MV, МVА | 25+25 | 0 | 10.54 | 4.02 | 120 | 6.52 | 0 | 26.25 | 19.73
| Sn. LV, МVА | 25+25 | 17.33 | 4.2 | 120 | 13.13 | 0 | 26.25 | 13.12 |  |  |  | Sn. LV, МVА | 25+25 | 5.91 | 23.24 | 1.09 | 120 | 22.15 | 0 | 26.25 | 4.1
116 | SS 110/35/10 kV № 30 | 40+40+63 | 67.69 | 5.1 | 120 | 62.59 | 0 | 108.15 | 45.56 | 30.34 | available | 116 | SS 110/35/10 kV № 30 | 40+40+63 | 15.84 | 83.53 | 5.1 | 120 | 78.43 | 0 | 108.15 | 29.72 | 29.72 | available
| Sn. MV, МVА | 40+40 | 11.66 | 0 | 0 | 11.66 | 0 | 42 | 30.34 |  |  |  | Sn. MV, МVА | 40+40 | 0 | 11.66 | 0 | 0 | 11.66 | 0 | 42 | 30.34
| Sn. LV, МVА | 40+40+63 | 56.03 | 5.1 | 120 | 50.93 | 0 | 108.15 | 57.22 |  |  |  | Sn. LV, МVА | 40+40+63 | 15.84 | 71.87 | 5.1 | 120 | 66.77 | 0 | 108.15 | 41.38
117 | SS 110/35/10 kV № 32 | 25+25 | 8.16 | 8 | 120 | 0.16 | 0 | 26.25 | 26.09 | 23.39 | available | 117 | SS 110/35/10 kV № 32 | 25+25 | 20.4 | 28.56 | 8 | 120 | 20.56 | 0 | 26.25 | 5.69 | 2.99 | available
| Sn. MV, МVА | 25+25 | 5.3 | 8 | 120 | -2.7 | 0 | 26.25 | 28.95 |  |  |  | Sn. MV, МVА | 25+25 | 0 | 5.3 | 8 | 120 | -2.7 | 0 | 26.25 | 28.95
| Sn. LV, МVА | 25+25 | 2.86 | 0 | 0 | 2.86 | 0 | 26.25 | 23.39 |  |  |  | Sn. LV, МVА | 25+25 | 20.4 | 23.26 | 0 | 0 | 23.26 | 0 | 26.25 | 2.99
118 | SS 35/10 kV № 33 | 4,0+4,0 | 3.8 | 0 | 0 | 3.8 | 0 | 4.2 | 0.4 | 0.4 | available | 118 | SS 35/10 kV № 33 | 4,0+4,0 | 1.98 | 5.78 | 0 | 0 | 5.78 | 0 | 4.2 | -1.58 | -1.58 | unavailable
119 | SS 35/6 kV№ 34 | 2,5+1,8 | 2.09 | 0 | 0 | 2.09 | 0 | 1.89 | -0.2 | -0.2 | unavailable | 119 | SS 35/6 kV№ 34 | 2,5+1,8 | 0.35 | 2.44 | 0 | 0 | 2.44 | 0 | 1.89 | -0.55 | -0.55 | unavailable
120 | SS 35/6 kV№ 35 | 10+10 | 12.27 | 2.4 | 120 | 9.87 | 0 | 10.5 | 0.63 | 0.63 | available | 120 | SS 35/6 kV№ 35 | 10+10 | 1.45 | 13.72 | 2.4 | 120 | 11.32 | 0 | 10.5 | -0.82 | -0.82 | unavailable
121 | SS 110/35/10 kV № 36 | 25+25 | 3.81 | 0 | 0 | 3.81 | 0 | 26.25 | 22.44 | 22.44 | available | 121 | SS 110/35/10 kV № 36 | 25+25 | 6.6 | 10.41 | 0 | 0 | 10.41 | 0 | 26.25 | 15.84 | 15.84 | available
122 | SS 110/6 kV № 39 | 40+25 | 26.38 | 7.08 | 120 | 19.3 | 0 | 26.25 | 6.95 | 6.95 | available | 122 | SS 110/6 kV № 39 | 40+25 | 5.07 | 31.45 | 7.08 | 120 | 24.37 | 0 | 26.25 | 1.88 | 1.88 | available
123 | SS 35/6 kV № 41 | 10+10 | 8.58 | 0 | 0 | 8.58 | 0 | 10.5 | 1.92 | 1.92 | available | 123 | SS 35/6 kV № 41 | 10+10 | 0.22 | 8.8 | 0 | 0 | 8.8 | 0 | 10.5 | 1.7 | 1.7 | available
124 | SS 110/6 kV № 42 | 25+40 | 18.46 | 1.6 | 120 | 16.86 | 0 | 26.25 | 9.39 | 9.39 | available | 124 | SS 110/6 kV № 42 | 25+40 | 7.65 | 26.11 | 1.6 | 120 | 24.51 | 0 | 26.25 | 1.74 | 1.74 | available
125 | SS 110/6 kV № 43 | 63+25 | 15.69 | 1.6 | 60 | 14.09 | 0 | 26.25 | 12.16 | 12.16 | available | 125 | SS 110/6 kV № 43 | 63+25 | 5.46 | 21.15 | 1.6 | 60 | 19.55 | 0 | 26.25 | 6.7 | 6.7 | available
126 | SS 110/6 kV № 45 | 63+63 | 44.43 | 7.1 | 120 | 37.33 | 0 | 66.15 | 28.82 | 28.82 | available | 126 | SS 110/6 kV № 45 | 63+63 | 22.44 | 66.87 | 7.1 | 120 | 59.77 | 0 | 66.15 | 6.38 | 6.38 | available
127 | SS 110/35/6 kV № 47 | 25+25 | 12.35 | 0 | 0 | 12.35 | 0 | 26.25 | 13.9 | 13.9 | available | 127 | SS 110/35/6 kV № 47 | 25+25 | 1.92 | 14.27 | 0 | 0 | 14.27 | 0 | 26.25 | 11.98 | 11.98 | available
| Sn. MV, МVА | 25+25 | 5.17 | 0 | 0 | 5.17 | 0 | 26.25 | 21.08 |  |  |  | Sn. MV, МVА | 25+25 | 0 | 5.17 | 0 | 0 | 5.17 | 0 | 26.25 | 21.08
| Sn. LV, МVА | 25+25 | 7.23 | 0 | 0 | 7.23 | 0 | 26.25 | 19.02 |  |  |  | Sn. LV, МVА | 25+25 | 1.92 | 9.15 | 0 | 0 | 9.15 | 0 | 26.25 | 17.1
128 | SS 110/35/10 kV Panino | 16+16 | 10.99 | 5.2 | 120 | 5.79 | 0 | 16.8 | 11.01 | 11.01 | available | 128 | SS 110/35/10 kV Panino | 16+16 | 2.68 | 13.67 | 5.2 | 120 | 8.47 | 0 | 16.8 | 8.33 | 8.33 | available
| Sn. MV, MVA | 16+16 | 5.07 | 5 | 120 | 0.07 | 0 | 16.8 | 16.73 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 5.07 | 5 | 120 | 0.07 | 0 | 16.8 | 16.73
| Sn. LV, MVA | 16+16 | 5.92 | 0.2 | 120 | 5.72 | 0 | 16.8 | 11.08 |  |  |  | Sn. LV, MVA | 16+16 | 2.68 | 8.6 | 0.2 | 120 | 8.4 | 0 | 16.8 | 8.4
129 | SS 35/10 kV Kriusha | 2,5+2,5 | 0.33 | 0 | 0 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 129 | SS 35/10 kV Kriusha | 2,5+2,5 | 0.13 | 0.46 | 0 | 0 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | available
130 | SS 35/10 kV Sem.Zavod | 4+4 | 1.76 | 0 | 0 | 1.76 | 0 | 4.2 | 2.44 | 2.44 | available | 130 | SS 35/10 kV Sem.Zavod | 4+4 | 0.1 | 1.86 | 0 | 0 | 1.86 | 0 | 4.2 | 2.34 | 2.34 | available
131 | SS 110/35/10 kV Progress | 2,5+10 | 0.53 | 0.5315 | 120 | -0.0015 | 0 | 2.625 | 2.6265 | 2.6265 | available | 131 | SS 110/35/10 kV Progress | 2,5+10 | 0.01 | 0.54 | 0.5315 | 120 | 0.0085 | 0 | 2.625 | 2.6165 | 2.6165 | available
132 | SS 35/10 kV Katuhovka | 2,5+2,5 | 0.36 | 0.385 | 120 | -0.025 | 0 | 2.625 | 2.65 | 2.65 | available | 132 | SS 35/10 kV Katuhovka | 2,5+2,5 | 0.02 | 0.38 | 0.385 | 120 | -0.005 | 0 | 2.625 | 2.63 | 2.63 | available
133 | SS 110/35/10 kV Kr.Liman | 2,5+4,0 | 0.76 | 0 | 0 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | available | 133 | SS 110/35/10 kV Kr.Liman | 2,5+4,0 | 0.02 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available
134 | SS 35/10 kV Ivanovka | 1,8+1,6 | 0.2 | 0.36 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | available | 134 | SS 35/10 kV Ivanovka | 1,8+1,6 | 0.1 | 0.3 | 0.36 | 120 | -0.06 | 0 | 1.68 | 1.74 | 1.74 | available
135 | SS 35/10 kV Don | 2,5+2,5 | 2.82 | 0 | 0 | 2.82 | 0 | 2.625 | -0.195 | -0.195 | unavailable | 135 | SS 35/10 kV Don | 2,5+2,5 | 1.7 | 4.52 | 0 | 0 | 4.52 | 0 | 2.625 | -1.895 | -1.895 | unavailable
136 | SS 35/10 kV Apple | 4+4 | 0.36 | 0 | 0 | 0.36 | 0 | 4.2 | 3.84 | 3.84 | available | 136 | SS 35/10 kV Apple | 4+4 | 0.09 | 0.45 | 0 | 0 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | available
137 | SS 35/10 kV St.Nikolskoe | 2,5+2,5 | 0.76 | 1.227 | 120 | -0.467 | 0 | 2.625 | 3.092 | 3.092 | available | 137 | SS 35/10 kV St.Nikolskoe | 2,5+2,5 | 0.39 | 1.15 | 1.227 | 120 | -0.077 | 0 | 2.625 | 2.702 | 2.702 | available
138 | SS 35/10 kV Rudkino | 4,0+4,0 | 2.2 | 0 | 0 | 2.2 | 0 | 4.2 | 2 | 2 | available | 138 | SS 35/10 kV Rudkino | 4,0+4,0 | 0.53 | 2.73 | 0 | 0 | 2.73 | 0 | 4.2 | 1.47 | 1.47 | available
139 | SS 35/6 kV Crest-1 | 6,3+6,3 | 3.82 | 0 | 0 | 3.82 | 0 | 6.615 | 2.795 | 2.795 | available | 139 | SS 35/6 kV Crest-1 | 6,3+6,3 | 2.36 | 6.18 | 0 | 0 | 6.18 | 0 | 6.615 | 0.435 | 0.435 | available
140 | SS 110/35/6 kV № 11 | 5,6+6,3 | 3.22 | 0.5 | 120 | 2.72 | 0 | 5.88 | 3.16 | 3.16 | available | 140 | SS 110/35/6 kV № 11 | 5,6+6,3 | 0 | 3.22 | 0.5 | 120 | 2.72 | 0 | 5.88 | 3.16 | 3.16 | available
| Sn. MV, MVA | 5,6+6,3 | 0.53 | 0.5 | 120 | 0.03 | 0 | 5.88 | 5.85 |  |  |  | Sn. MV, MVA | 5,6+6,3 | 0 | 0.53 | 0.5 | 120 | 0.03 | 0 | 5.88 | 5.85
| Sn. LV, MVA | 5,6+6,3 | 2.69 | 0 | 0 | 2.69 | 0 | 5.88 | 3.19 |  |  |  | Sn. LV, MVA | 5,6+6,3 | 0 | 2.69 | 0 | 0 | 2.69 | 0 | 5.88 | 3.19
141 | SS 35/10 kV Berezovka | 4+4 | 4.15 | 0 | 0 | 4.15 | 0 | 4.2 | 0.05 | 0.05 | available | 141 | SS 35/10 kV Berezovka | 4+4 | 1.12 | 5.27 | 0 | 0 | 5.27 | 0 | 4.2 | -1.07 | -1.07 | unavailable
142 | SS 35/10 kV N.Zhivotinnoe | 6,3+6,3 | 4.84 | 1 | 120 | 3.84 | 0 | 6.615 | 2.775 | 2.775 | available | 142 | SS 35/10 kV N.Zhivotinnoe | 6,3+6,3 | 5.77 | 10.61 | 1 | 120 | 9.61 | 0 | 6.615 | -2.995 | -2.995 | unavailable
143 | SS 35/10/6 kV Ramon-1 | 4+4+4 | 4.58 | 6.85 | 120 | -2.27 | 0 | 8.4 | 10.67 | 10.67 | available | 143 | SS 35/10/6 kV Ramon-1 | 4+4+4 | 0.79 | 5.37 | 6.85 | 120 | -1.48 | 0 | 8.4 | 9.88 | 9.88 | available
144 | SS 110/35/10 kV Ramon-2 | 16,0+16,0 | 20.17 | 10.48 | 120 | 9.69 | 0 | 16.8 | 7.11 | 7.11 | available | 144 | SS 110/35/10 kV Ramon-2 | 16,0+16,0 | 0.74 | 20.91 | 10.48 | 120 | 10.43 | 0 | 16.8 | 6.37 | 6.37 | available
| Sn. MV, MVA | 16,0+16,0 | 16.21 | 6.85 | 0 | 9.36 | 0 | 16.8 | 7.44 |  |  |  | Sn. MV, MVA | 16,0+16,0 | 0 | 16.21 | 6.85 | 0 | 9.36 | 0 | 16.8 | 7.44
| Sn. LV, MVA | 16,0+16,0 | 3.96 | 3.63 | 120 | 0.33 | 0 | 16.8 | 16.47 |  |  |  | Sn. LV, MVA | 16,0+16,0 | 0.74 | 4.7 | 3.63 | 120 | 1.07 | 0 | 16.8 | 15.73
145 | SS 35/10 kV Vereyka | 2,5+2,5 | 1.11 | 0 | 0 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | available | 145 | SS 35/10 kV Vereyka | 2,5+2,5 | 0.01 | 1.12 | 0 | 0 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | available
146 | SS 110/35/10 kV Complex | 10+10 | 5.19 | 3.4 | 180 | 1.79 | 0 | 10.5 | 8.71 | 8.09 | available | 146 | SS 110/35/10 kV Complex | 10+10 | 0 | 5.19 | 3.4 | 180 | 1.79 | 0 | 10.5 | 8.71 | 8.09 | available
| Sn. MV, MVA | 10+10 | 2.48 | 3.1 | 180 | -0.62 | 0 | 10.5 | 11.12 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 2.48 | 3.1 | 180 | -0.62 | 0 | 10.5 | 11.12
| Sn. LV, MVA | 10+10 | 2.71 | 0.3 | 180 | 2.41 | 0 | 10.5 | 8.09 |  |  |  | Sn. LV, MVA | 10+10 | 0 | 2.71 | 0.3 | 180 | 2.41 | 0 | 10.5 | 8.09
147 | SS 110/35/10 kV N.Veduga | 16+16 | 3.3 | 2.9 | 120 | 0.4 | 0 | 16.8 | 16.4 | 15.68 | available | 147 | SS 110/35/10 kV N.Veduga | 16+16 | 0 | 3.3 | 2.9 | 120 | 0.4 | 0 | 16.8 | 16.4 | 15.68 | available
| Sn. MV, MVA | 16+16 | 2.18 | 2.9 | 120 | -0.72 | 0 | 16.8 | 17.52 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 2.18 | 2.9 | 120 | -0.72 | 0 | 16.8 | 17.52
| Sn. LV, MVA | 16+16 | 1.12 | 0 | 0 | 1.12 | 0 | 16.8 | 15.68 |  |  |  | Sn. LV, MVA | 16+16 | 0 | 1.12 | 0 | 0 | 1.12 | 0 | 16.8 | 15.68
148 | SS 35/10 kV Golosnovka | 2,5+2,5 | 0.45 | 0.512 | 120 | -0.062 | 0 | 2.625 | 2.687 | 2.687 | available | 148 | SS 35/10 kV Golosnovka | 2,5+2,5 | 0.02 | 0.47 | 0.512 | 120 | -0.042 | 0 | 2.625 | 2.667 | 2.667 | available
149 | SS 35/10 kV Bear | 3,2+4,0 | 1.09 | 0 | 0 | 1.09 | 0 | 3.36 | 2.27 | 2.27 | available | 149 | SS 35/10 kV Bear | 3,2+4,0 | 0.11 | 1.2 | 0 | 0 | 1.2 | 0 | 3.36 | 2.16 | 2.16 | available
150 | SS 35/10 kV St.Veduga | 4+4 | 0.93 | 0 | 0 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | available | 150 | SS 35/10 kV St.Veduga | 4+4 | 0.03 | 0.96 | 0 | 0 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | available
151 | SS 35/10 kV M.Pokrovka | 2,5+2,5 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | available | 151 | SS 35/10 kV M.Pokrovka | 2,5+2,5 | 0.01 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available
152 | SS 35/10 kV V.Turovo-2 | 2,5+2,5 | 0.71 | 0.7 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | available | 152 | SS 35/10 kV V.Turovo-2 | 2,5+2,5 | 0.31 | 1.02 | 0.7 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available
153 | SS 35/10 kV S.Lipyagi | 3,2+2,5 | 1.53 | 2.9638 | 120 | -1.4338 | 0 | 2.625 | 4.0588 | 4.0588 | available | 153 | SS 35/10 kV S.Lipyagi | 3,2+2,5 | 1.97 | 3.5 | 2.9638 | 120 | 0.5362 | 0 | 2.625 | 2.0888 | 2.0888 | available
154 | SS 110/35/10 kV N.Devitsk | 25+16 | 7.14 | 8.2225 | 180 | -1.0825 | 0 | 16.8 | 17.8825 | 15.81 | available | 154 | SS 110/35/10 kV N.Devitsk | 25+16 | 1.21 | 8.35 | 8.2225 | 180 | 0.1275 | 0 | 16.8 | 16.6725 | 15.81 | available
| Sn. MV, MVA | 25+16 | 3.79 | 2.8 | 180 | 0.99 | 0 | 16.8 | 15.81 |  |  |  | Sn. MV, MVA | 25+16 | 0 | 3.79 | 2.8 | 180 | 0.99 | 0 | 16.8 | 15.81
| Sn. LV, MVA | 25+16 | 3.35 | 5.393 | 180 | -2.043 | 0 | 16.8 | 18.843 |  |  |  | Sn. LV, MVA | 25+16 | 1.21 | 4.56 | 5.393 | 180 | -0.833 | 0 | 16.8 | 17.633
155 | SS 35/10 kV Repevka | 4+4 | 2.53 | 0.5 | 120 | 2.03 | 0 | 4.2 | 2.17 | 2.17 | available | 155 | SS 35/10 kV Repevka | 4+4 | 0.12 | 2.65 | 0.5 | 120 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | available
156 | SS 110/35/10 kV Krasnolipe | 16+16 | 11.07 | 2.9 | 120 | 8.17 | 0 | 16.8 | 8.63 | 8.63 | available | 156 | SS 110/35/10 kV Krasnolipe | 16+16 | 0.25 | 11.32 | 2.9 | 120 | 8.42 | 0 | 16.8 | 8.38 | 8.38 | available
| Sn. MV, MVA | 16+16 | 9.73 | 2.7 | 120 | 7.03 | 0 | 16.8 | 9.77 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 9.73 | 2.7 | 120 | 7.03 | 0 | 16.8 | 9.77
| Sn. LV, MVA | 16+16 | 1.34 | 0.2 | 120 | 1.14 | 0 | 16.8 | 15.66 |  |  |  | Sn. LV, MVA | 16+16 | 0.25 | 1.59 | 0.2 | 120 | 1.39 | 0 | 16.8 | 15.41
157 | SS 110/10 kV Ulyanovka | 6,3+6,3 | 0.44 | 0.04 | 60 | 0.4 | 0 | 6.615 | 6.215 | 6.215 | available | 157 | SS 110/10 kV Ulyanovka | 6,3+6,3 | 0.11 | 0.55 | 0.04 | 60 | 0.51 | 0 | 6.615 | 6.105 | 6.105 | available
158 | SS 35/10 kV MOB | 4+2,5 | 1.39 | 0.6 | 60 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 158 | SS 35/10 kV MOB | 4+2,5 | 0.21 | 1.6 | 0.6 | 60 | 1 | 0 | 2.625 | 1.625 | 1.625 | available
159 | SS 35/10 kV L.Rossosh | 6,3+6,3 | 6.26 | 0 | 0 | 6.26 | 0 | 6.615 | 0.355 | 0.355 | available | 159 | SS 35/10 kV L.Rossosh | 6,3+6,3 | 1.34 | 7.6 | 0 | 0 | 7.6 | 0 | 6.615 | -0.985 | -0.985 | unavailable
160 | SS 35/10 kV Kashirskoye | 2,5+2,5 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | available | 160 | SS 35/10 kV Kashirskoye | 2,5+2,5 | 0.05 | 0.74 | 0 | 0 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | available
161 | SS 35/10 kV Zaprudskaya | 2,5+2,5 | 1.67 | 0 | 0 | 1.67 | 0 | 2.625 | 0.955 | 0.955 | available | 161 | SS 35/10 kV Zaprudskaya | 2,5+2,5 | 0.31 | 1.98 | 0 | 0 | 1.98 | 0 | 2.625 | 0.645 | 0.645 | available
162 | SS 110/35/10 kV Moscow | 10+10 | 9.96 | 1.8 | 120 | 8.16 | 0 | 10.5 | 2.34 | 1.44 | available | 162 | SS 110/35/10 kV Moscow | 10+10 | 0.19 | 10.15 | 1.8 | 120 | 8.35 | 0 | 10.5 | 2.15 | 1.44 | available
| Sn. MV, MVA | 10+10 | 9.06 | 0 | 0 | 9.06 | 0 | 10.5 | 1.44 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 9.06 | 0 | 0 | 9.06 | 0 | 10.5 | 1.44
| Sn. LV, MVA | 10+10 | 0.9 | 1.8 | 120 | -0.9 | 0 | 10.5 | 11.4 |  |  |  | Sn. LV, MVA | 10+10 | 0.19 | 1.09 | 1.8 | 120 | -0.71 | 0 | 10.5 | 11.21
163 | SS SS 35/10 kV Semenovka SES | 2,5+4,0 | 2.04 | 0 | 0 | 2.04 | 0 | 2.625 | 0.585 | 0.585 | available | 163 | SS SS 35/10 kV Semenovka SES | 2,5+4,0 | 0.01 | 2.05 | 0 | 0 | 2.05 | 0 | 2.625 | 0.575 | 0.575 | available
164 | SS 35/10 kV N.Baygora | 2,5+2,5 | 0.82 | 1.03 | 60 | -0.21 | 0 | 2.625 | 2.835 | 2.835 | available | 164 | SS 35/10 kV N.Baygora | 2,5+2,5 | 0.02 | 0.84 | 1.03 | 60 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | available
165 | SS 35/10 kV Shukavka | 2,5+2,5 | 0.78 | 0.1 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available | 165 | SS 35/10 kV Shukavka | 2,5+2,5 | 0.03 | 0.81 | 0.1 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | available
166 | SS 35/10 kV Uglyanets | 4+2,5 | 2.36 | 0.8 | 120 | 1.56 | 0 | 2.625 | 1.065 | 1.065 | available | 166 | SS 35/10 kV Uglyanets | 4+2,5 | 3.68 | 6.04 | 0.8 | 120 | 5.24 | 0 | 2.625 | -2.615 | -2.615 | unavailable
167 | SS 110/35/10 kV V.Hava | 16+16 | 14.73 | 0.4 | 120 | 14.33 | 0 | 16.8 | 2.47 | 2.47 | available | 167 | SS 110/35/10 kV V.Hava | 16+16 | 2.98 | 17.71 | 0.4 | 120 | 17.31 | 0 | 16.8 | -0.51 | -0.51 | unavailable
| Sn. MV, MVA | 16+16 | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94
| Sn. LV, MVA | 16+16 | 8.86 | 0.4 | 120 | 8.46 | 0 | 16.8 | 8.34 |  |  |  | Sn. LV, MVA | 16+16 | 2.98 | 11.84 | 0.4 | 120 | 11.44 | 0 | 16.8 | 5.36
168 | SS 110/10 kV Novousmanskaya | 25+25 | 0 | 0 | 0 | 0 | 0 | 26.25 | 26.25 | 26.25 | available | 168 | SS 110/10 kV Novousmanskaya | 25+25 | 2.7 | 2.7 | 0 | 0 | 2.7 | 0 | 26.25 | 23.55 | 23.55 | available
169 | SS 35/10 kV-2 N.Usman | 10+10 | 10.56 | 0 | 0 | 10.56 | 0 | 10.5 | -0.06 | -0.06 | unavailable | 169 | SS 35/10 kV-2 N.Usman | 10+10 | 4.29 | 14.85 | 0 | 0 | 14.85 | 0 | 10.5 | -4.35 | -4.35 | unavailable
170 | SS 35/10 kV R.Hava | 4+4 | 3.62 | 0.2 | 120 | 3.42 | 0 | 4.2 | 0.78 | 0.78 | available | 170 | SS 35/10 kV R.Hava | 4+4 | 0.08 | 3.7 | 0.2 | 120 | 3.5 | 0 | 4.2 | 0.7 | 0.7 | available
171 | SS 110/35/10 kV № 31 | 16+25 | 23.02 | 5.6 | 120 | 17.42 | 0 | 16.8 | -0.62 | -0.62 | unavailable | 171 | SS 110/35/10 kV № 31 | 16+25 | 1.17 | 24.19 | 5.6 | 120 | 18.59 | 0 | 16.8 | -1.79 | -1.79 | unavailable
| Sn. MV, MVA | 16+25 | 13.67 | 5.6 | 120 | 8.07 | 0 | 16.8 | 8.73 |  |  |  | Sn. MV, MVA | 16+25 | 0 | 13.67 | 5.6 | 120 | 8.07 | 0 | 16.8 | 8.73
| Sn. LV, MVA | 16+25 | 9.35 | 0 | 0 | 9.35 | 0 | 16.8 | 7.45 |  |  |  | Sn. LV, MVA | 16+25 | 1.17 | 10.52 | 0 | 0 | 10.52 | 0 | 16.8 | 6.28
172 | SS 35/10 kV Maslovka | 4+4 | 4.02 | 0 | 0 | 4.02 | 0 | 4.2 | 0.18 | 0.18 | available | 172 | SS 35/10 kV Maslovka | 4+4 | 1.59 | 5.61 | 0 | 0 | 5.61 | 0 | 4.2 | -1.41 | -1.41 | unavailable
173 | SS 110/35/10 kV Podgornaya district-LES | 16+16 | 4.11 | 1.6 | 180 | 2.51 | 0 | 16.8 | 14.29 | 13.24 | available | 173 | SS 110/35/10 kV Podgornaya district-LES | 16+16 | 2.96 | 7.07 | 1.6 | 180 | 5.47 | 0 | 16.8 | 11.33 | 10.28 | available
| Sn. MV, MVA | 16+16 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85
| Sn. LV, MVA | 16+16 | 4.11 | 0.55 | 180 | 3.56 | 0 | 16.8 | 13.24 |  |  |  | Sn. LV, MVA | 16+16 | 2.96 | 7.07 | 0.55 | 180 | 6.52 | 0 | 16.8 | 10.28
174 | SS 110/35/10 kV Kantemirovka | 10+10 | 9.57 | 1.6 | 60 | 7.97 | 0 | 10.5 | 2.53 | 2.53 | available | 174 | SS 110/35/10 kV Kantemirovka | 10+10 | 0.54 | 10.11 | 1.6 | 60 | 8.51 | 0 | 10.5 | 1.99 | 1.99 | available
| Sn. MV, MVA | 10+10 | 5.88 | 1.4 | 60 | 4.48 | 0 | 10.5 | 6.02 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 5.88 | 1.4 | 60 | 4.48 | 0 | 10.5 | 6.02
| Sn. LV, MVA | 10+10 | 3.69 | 0.2 | 60 | 3.49 | 0 | 10.5 | 7.01 |  |  |  | Sn. LV, MVA | 10+10 | 0.54 | 4.23 | 0.2 | 60 | 4.03 | 0 | 10.5 | 6.47
175 | SS 110/35/10/6 kV Rossosh | 16+16+40 | 24.2 | 2.68 | 120 | 21.52 | 0 | 33.6 | 12.08 | 12.08 | available | 175 | SS 110/35/10/6 kV Rossosh | 16+16+40 | 1.62 | 25.82 | 2.68 | 120 | 23.14 | 0 | 33.6 | 10.46 | 10.46 | available
| Sn. MV, MVA | 16+16+40 | 4 | 1.9 | 120 | 2.1 | 0 | 33.6 | 31.5 |  |  |  | Sn. MV, MVA | 16+16+40 | 0.01 | 4.01 | 1.9 | 120 | 2.11 | 0 | 33.6 | 31.49
| Sn. LV, MVA | 16+16+40 | 20.2 | 0.78 | 120 | 19.42 | 0 | 33.6 | 14.18 |  |  |  | Sn. LV, MVA | 16+16+40 | 1.62 | 21.82 | 0.78 | 120 | 21.04 | 0 | 33.6 | 12.56
176 | SS 110/35/10 kV Kamenka r-naya LES | 16+16 | 3.75 | 0.97 | 120 | 2.78 | 0 | 16.8 | 14.02 | 14.02 | available | 176 | SS 110/35/10 kV Kamenka r-naya LES | 16+16 | 1.28 | 5.03 | 0.97 | 120 | 4.06 | 0 | 16.8 | 12.74 | 12.74 | available
| Sn. MV, MVA | 16+16 | 0.67 | 0 | 120 | 0.67 | 0 | 16.8 | 16.13 |  |  |  | Sn. MV, MVA | 16+16 | 0.03 | 0.7 | 0 | 120 | 0.7 | 0 | 16.8 | 16.1
| Sn. LV, MVA | 16+16 | 3.08 | 0.97 | 120 | 2.11 | 0 | 16.8 | 14.69 |  |  |  | Sn. LV, MVA | 16+16 | 1.26 | 4.34 | 0.97 | 120 | 3.37 | 0 | 16.8 | 13.43
177 | SS 110/35/10 kV Korotoyak | 6,3+10 | 3.77 | 0.47 | 180 | 3.3 | 0 | 6.615 | 3.315 | 3.315 | available | 177 | SS 110/35/10 kV Korotoyak | 6,3+10 | 0.75 | 4.52 | 0.47 | 180 | 4.05 | 0 | 6.615 | 2.565 | 2.565 | available
| Sn. MV, MVA | 6,3+10 | 0 | 0 | 180 | 0 | 0 | 6.615 | 6.615 |  |  |  | Sn. MV, MVA | 6,3+10 | 0 | 0 | 0 | 180 | 0 | 0 | 6.615 | 6.615
| Sn. LV, MVA | 6,3+10 | 3.77 | 0.47 | 180 | 3.3 | 0 | 6.615 | 3.315 |  |  |  | Sn. LV, MVA | 6,3+10 | 0.75 | 4.52 | 0.47 | 180 | 4.05 | 0 | 6.615 | 2.565
178 | Ostrogozhsk | 40,5+40,5 | 19.78 | 2.4 | 60 | 17.38 | 0 | 42.525 | 25.145 | 25.145 | available | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 19.78 | 2.4 | 60 | 17.38 | 0 | 42.525 | 25.145 | 25.145 | available
| Sn. MV, MVA | 40,5+40,5 | 16.81 | 2.4 | 60 | 14.41 | 0 | 42.525 | 28.115 |  |  |  | Sn. MV, MVA | 40,5+40,5 | 0 | 16.81 | 2.4 | 60 | 14.41 | 0 | 42.525 | 28.115
| Sn. LV, MVA | 40,5+40,5 | 2.97 | 0 | 60 | 2.97 | 0 | 42.525 | 39.555 |  |  |  | Sn. LV, MVA | 40,5+40,5 | 0 | 2.97 | 0 | 60 | 2.97 | 0 | 42.525 | 39.555
179 | SS 110/35/10 kV Lousy | 16+6,3 | 4.09 | 0 | 0 | 4.09 | 0 | 6.615 | 2.525 | 2.525 | available | 179 | SS 110/35/10 kV Lousy | 16+6,3 | 1.13 | 5.22 | 0 | 0 | 5.22 | 0 | 6.615 | 1.395 | 1.395 | available
| Sn. MV, MVA | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  |  | Sn. MV, MVA | 16+6,3 | 0.34 | 0.34 | 0 | 0 | 0.34 | 0 | 6.615 | 6.275
| Sn. LV, MVA | 16+6,3 | 4.09 | 0 | 0 | 4.09 | 0 | 6.615 | 2.525 |  |  |  | Sn. LV, MVA | 16+6,3 | 0.8 | 4.89 | 0 | 0 | 4.89 | 0 | 6.615 | 1.725
180 | SS 110/35/6 kV MEZ | 25+25 | 23.52 | 7.9 | 120 | 15.62 | 0 | 26.25 | 10.63 | 10.63 | available | 180 | SS 110/35/6 kV MEZ | 25+25 | 0.3 | 23.82 | 7.9 | 120 | 15.92 | 0 | 26.25 | 10.33 | 10.33 | available
| Sn. MV, MVA | 25+25 | 9.01 | 7.9 | 120 | 1.11 | 0 | 26.25 | 25.14 |  |  |  | Sn. MV, MVA | 25+25 | 0 | 9.01 | 7.9 | 120 | 1.11 | 0 | 26.25 | 25.14
| Sn. LV, MVA | 25+25 | 14.51 | 0 | 0 | 14.51 | 0 | 26.25 | 11.74 |  |  |  | Sn. LV, MVA | 25+25 | 0.3 | 14.81 | 0 | 0 | 14.81 | 0 | 26.25 | 11.44
181 | SS 110/6 kV ANP | 6,3+6,3 | 3.09 | 0.39 | 120 | 2.7 | 0 | 6.615 | 3.915 | 3.915 | available | 181 | SS 110/6 kV ANP | 6,3+6,3 | 4.7 | 4.39 | 0.39 | 120 | 4 | 0 | 6.615 | 2.615 | 2.615 | available
182 | SS 110/10 kV CT. Kalitva | 6,3+6,3 | 1.62 | 0.86 | 240 | 0.76 | 0 | 6.615 | 5.855 | 5.855 | available | 182 | SS 110/10 kV CT. Kalitva | 6,3+6,3 | 0.22 | 1.84 | 0.86 | 240 | 0.98 | 0 | 6.615 | 5.635 | 5.635 | available
183 | SS 110/10 kV Nikanorovka | 2,5+6,3 | 0.67 | 0.5 | 240 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | available | 183 | SS 110/10 kV Nikanorovka | 2,5+6,3 | 0.63 | 1.3 | 0.5 | 240 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available
184 | SS 110/10 kV PTF | 10+10 | 3.37 | 1 | 120 | 2.37 | 0 | 10.5 | 8.13 | 8.13 | available | 184 | SS 110/10 kV PTF | 10+10 | 0.8 | 4.17 | 1 | 120 | 3.17 | 0 | 10.5 | 7.33 | 7.33 | available
185 | SS 110/10 kV Korshevo | 6,3+6,3 | 0.89 | 0.56 | 120 | 0.33 | 0 | 6.615 | 6.285 | 6.285 | available | 185 | SS 110/10 kV Korshevo | 6,3+6,3 | 2.6 | 3.49 | 0.56 | 120 | 2.93 | 0 | 6.615 | 3.685 | 3.685 | available
186 | SS 110/10 kV Davydovka | 6,3+6,3 | 6.25 | 2.11 | 240 | 4.14 | 0 | 6.615 | 2.475 | 2.475 | available | 186 | SS 110/10 kV Davydovka | 6,3+6,3 | 2.51 | 8.76 | 2.11 | 240 | 6.65 | 0 | 6.615 | -0.035 | -0.035 | unavailable
187 | SS 110/10 kV 2nd Five-Year Plan | 6,3+6,3 | 1.28 | 0.66 | 120 | 0.62 | 0 | 6.615 | 5.995 | 5.995 | available | 187 | SS 110/10 kV 2nd Five-Year Plan | 6,3+6,3 | 0.68 | 1.96 | 0.66 | 120 | 1.3 | 0 | 6.615 | 5.315 | 5.315 | available
188 | SS 110/6 kV Liski | 10+16 | 7.22 | 0.72 | 120 | 6.5 | 0 | 10.5 | 4 | 4 | available | 188 | SS 110/6 kV Liski | 10+16 | 1.53 | 8.75 | 0.72 | 120 | 8.03 | 0 | 10.5 | 2.47 | 2.47 | available
189 | SS 35/10 kV Olkhovatka | 4+4 | 3.55 | 2.55 | 180 | 1 | 0 | 4.2 | 3.2 | 3.2 | available | 189 | SS 35/10 kV Olkhovatka | 4+4 | 1.06 | 4.61 | 2.55 | 180 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | available
190 | SS 35/10 kV Shaposhnikovka | 2,5+2,5 | 1.23 | 0.86 | 180 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | available | 190 | SS 35/10 kV Shaposhnikovka | 2,5+2,5 | 0.29 | 1.52 | 0.86 | 180 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | available
191 | SS 35/10 kV Karayashnik | 2,5+2,5 | 0.6 | 0.2875 | 180 | 0.3125 | 0 | 2.625 | 2.3125 | 2.3125 | available | 191 | SS 35/10 kV Karayashnik | 2,5+2,5 | 0.05 | 0.65 | 0.2875 | 180 | 0.3625 | 0 | 2.625 | 2.2625 | 2.2625 | available
192 | SS 35/10 kV Saguna | 2,5+2,5 | 1.02 | 0.91 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 192 | SS 35/10 kV Saguna | 2,5+2,5 | 0.22 | 1.24 | 0.91 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available
193 | SS 35/10 kV Belogorie | 2,5+2,5 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available | 193 | SS 35/10 kV Belogorie | 2,5+2,5 | 0.29 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | available
194 | SS 35/10 kV Taly | 4+4 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | available | 194 | SS 35/10 kV Taly | 4+4 | 0.41 | 1.71 | 0 | 0 | 1.71 | 0 | 4.2 | 2.49 | 2.49 | available
195 | SS 35/10 kV Titarevka | 2,5+2,5 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available | 195 | SS 35/10 kV Titarevka | 2,5+2,5 | 0.33 | 1.08 | 0 | 0 | 1.08 | 0 | 2.625 | 1.545 | 1.545 | available
196 | SS 35/10 kV Mitrofanovka | 4+4 | 2.67 | 0 | 0 | 2.67 | 0 | 4.2 | 1.53 | 1.53 | available | 196 | SS 35/10 kV Mitrofanovka | 4+4 | 0.75 | 3.42 | 0 | 0 | 3.42 | 0 | 4.2 | 0.78 | 0.78 | available
197 | SS 35/10 kV Friendship | 4+4 | 2.11 | 0.44 | 150 | 1.67 | 0 | 4.2 | 2.53 | 2.53 | available | 197 | SS 35/10 kV Friendship | 4+4 | 0.53 | 2.64 | 0.44 | 150 | 2.2 | 0 | 4.2 | 2 | 2 | available
198 | SS 35/10 kV Aleksandrovka LES | 4+4 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | available | 198 | SS 35/10 kV Aleksandrovka LES | 4+4 | 0.22 | 2.85 | 0 | 0 | 2.85 | 0 | 4.2 | 1.35 | 1.35 | available
199 | SS 35/10 kV Thorevka | 4+4 | 0.82 | 0.78 | 180 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | available | 199 | SS 35/10 kV Thorevka | 4+4 | 0.18 | 1 | 0.78 | 180 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | available
200 | SS 35/10 kV Stamps | 2,5+2,5 | 0.42 | 0.27 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 200 | SS 35/10 kV Stamps | 2,5+2,5 | 0.15 | 0.57 | 0.27 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available
201 | SS 35/10 kV Olkhov Log | 2,5+2,5 | 0.69 | 0.58 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available | 201 | SS 35/10 kV Olkhov Log | 2,5+2,5 | 0 | 0.69 | 0.58 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | available
202 | SS 35/10 kV Boldyrevka | 2,5+2,5 | 1 | 0 | 0 | 1 | 0 | 2.625 | 1.625 | 1.625 | available | 202 | SS 35/10 kV Boldyrevka | 2,5+2,5 | 0.32 | 1.32 | 0 | 0 | 1.32 | 0 | 2.625 | 1.305 | 1.305 | available
203 | SS 35/10 kV Victory | 4+4 | 0.61 | 0 | 0 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | available | 203 | SS 35/10 kV Victory | 4+4 | 0.09 | 0.7 | 0 | 0 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | available
204 | SS 35/10 kV Lipovka | 4+4 | 1.64 | 0 | 0 | 1.64 | 0 | 4.2 | 2.56 | 2.56 | available | 204 | SS 35/10 kV Lipovka | 4+4 | 3.57 | 5.21 | 0 | 0 | 5.21 | 0 | 4.2 | -1.01 | -1.01 | unavailable
205 | SS 35/10 kV Yudanovka | 2,5+2,5 | 0.96 | 0.81 | 180 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | available | 205 | SS 35/10 kV Yudanovka | 2,5+2,5 | 0.4 | 1.36 | 0.81 | 180 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | available
206 | SS 35/10 kV Mechetka | 2,5+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | available | 206 | SS 35/10 kV Mechetka | 2,5+1,6 | 0.06 | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | available
207 | SS 35/10 kV Peter | 4+4 | 2.31 | 0.03 | 180 | 2.28 | 0 | 4.2 | 1.92 | 1.92 | available | 207 | SS 35/10 kV Peter | 4+4 | 1.51 | 3.82 | 0.03 | 180 | 3.79 | 0 | 4.2 | 0.41 | 0.41 | available
208 | SS 35/10 kV Wed Ikorets | 4+4 | 3.64 | 0.06 | 120 | 3.58 | 0 | 4.2 | 0.62 | 0.62 | available | 208 | SS 35/10 kV Wed Ikorets | 4+4 | 1.87 | 5.51 | 0.06 | 120 | 5.45 | 0 | 4.2 | -1.25 | -1.25 | unavailable
209 | SS 35/10 kV 2nd Sentry | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available | 209 | SS 35/10 kV 2nd Sentry | 2,5+2,5 | 0.39 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | available
210 | SS 35/6 kV Pts. Facilities | 2,5+2,5 | 2.23 | 0.42 | 120 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | available | 210 | SS 35/6 kV Pts. Facilities | 2,5+2,5 | 2.22 | 4.45 | 0.6 | 120 | 3.85 | 0 | 2.625 | -1.225 | -1.225 | unavailable
211 | SS 110/35/6 kV Borisoglebsk | 25+25 | 28.11 | 24.9 | 240 | 3.21 | 0 | 26.25 | 23.04 | 22.14 | available | 211 | SS 110/35/6 kV Borisoglebsk | 25+25 | 0 | 28.11 | 24.9 | 240 | 3.21 | 0 | 26.25 | 23.04 | 22.14 | available
| Sn. MV, MVA | 25+25 | 20.61 | 16.5 | 240 | 4.11 | 0 | 26.25 | 22.14 |  |  |  | Sn. MV, MVA | 25+25 | 0 | 20.61 | 16.5 | 240 | 4.11 | 0 | 26.25 | 22.14
| Sn. LV, MVA | 25+25 | 7.5 | 8.4 | 240 | -0.9 | 0 | 26.25 | 27.15 |  |  |  | Sn. LV, MVA | 25+25 | 0 | 7.5 | 8.4 | 240 | -0.9 | 0 | 26.25 | 27.15
212 | SS 110/35/10 kV Kamenka BES | 10+10 | 5.85 | 6.01 | 180 | -0.16 | 0 | 10.5 | 10.66 | 10.25 | available | 212 | SS 110/35/10 kV Kamenka BES | 10+10 | 0.63 | 6.48 | 6.01 | 180 | 0.47 | 0 | 10.5 | 10.03 | 9.62 | available
| Sn. MV, MVA | 10+10 | 4.94 | 5.35 | 180 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 4.94 | 5.35 | 180 | -0.41 | 0 | 10.5 | 10.91
| Sn. LV, MVA | 10+10 | 0.91 | 0.66 | 180 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Sn. LV, MVA | 10+10 | 0.63 | 1.54 | 0.66 | 180 | 0.88 | 0 | 10.5 | 9.62
213 | SS 110/35/10 kV Talovaya | 16+16 | 6.1 | 6.39 | 180 | -0.29 | 0 | 16.8 | 17.09 | 15.71 | available | 213 | SS 110/35/10 kV Talovaya | 16+16 | 0.4 | 6.5 | 6.39 | 180 | 0.11 | 0 | 16.8 | 16.69 | 15.31 | available
| Sn. MV, MVA | 16+16 | 5.01 | 6.39 | 180 | -1.38 | 0 | 16.8 | 18.18 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 5.01 | 6.39 | 180 | -1.38 | 0 | 16.8 | 18.18
| Sn. LV, MVA | 16+16 | 1.09 | 0 | 0 | 1.09 | 0 | 16.8 | 15.71 |  |  |  | Sn. LV, MVA | 16+16 | 0.4 | 1.49 | 0 | 0 | 1.49 | 0 | 16.8 | 15.31
214 | SS 110/35/10 kV Anna | 25+25 | 16.6 | 14.11 | 150 | 2.49 | 0 | 26.25 | 23.76 | 23.76 | available | 214 | SS 110/35/10 kV Anna | 25+25 | 1.52 | 18.12 | 14.11 | 150 | 4.01 | 0 | 26.25 | 22.24 | 22.24 | available
| Sn. MV, MVA | 25+25 | 6.75 | 5.37 | 150 | 1.38 | 0 | 26.25 | 24.87 |  |  |  | Sn. MV, MVA | 25+25 | 0 | 6.75 | 5.37 | 150 | 1.38 | 0 | 26.25 | 24.87
| Sn. LV, MVA | 25+25 | 9.85 | 8.74 | 150 | 1.11 | 0 | 26.25 | 25.14 |  |  |  | Sn. LV, MVA | 25+25 | 1.52 | 11.37 | 8.74 | 150 | 2.63 | 0 | 26.25 | 23.62
215 | SS 110/35/10 kV Arkhangelsk BES | 10+10 | 6.76 | 3.02 | 90 | 3.74 | 0 | 10.5 | 6.76 | 6.76 | available | 215 | SS 110/35/10 kV Arkhangelsk BES | 10+10 | 0.01 | 6.77 | 3.02 | 90 | 3.75 | 0 | 10.5 | 6.75 | 6.75 | available
| Sn. MV, MVA | 10+10 | 3.75 | 3.02 | 90 | 0.73 | 0 | 10.5 | 9.77 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 3.75 | 3.02 | 90 | 0.73 | 0 | 10.5 | 9.77
| Sn. LV, MVA | 10+10 | 3.01 | 0 | 0 | 3.01 | 0 | 10.5 | 7.49 |  |  |  | Sn. LV, MVA | 10+10 | 0.01 | 3.02 | 0 | 0 | 3.02 | 0 | 10.5 | 7.48
216 | SS 110/35/10 kV Listopadovka | 10+10 | 2.55 | 1.63 | 90 | 0.92 | 0 | 10.5 | 9.58 | 9.28 | available | 216 | SS 110/35/10 kV Listopadovka | 10+10 | 0.52 | 3.07 | 3.08 | 90 | -0.01 | 0 | 10.5 | 10.51 | 8.76 | available
| Sn. MV, MVA | 10+10 | 1.33 | 1.63 | 90 | -0.3 | 0 | 10.5 | 10.8 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 1.33 | 3.08 | 90 | -1.75 | 0 | 10.5 | 12.25
| Sn. LV, MVA | 10+10 | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 |  |  |  | Sn. LV, MVA | 10+10 | 0.52 | 1.74 | 0 | 0 | 1.74 | 0 | 10.5 | 8.76
217 | SS 110/35/10 kV B. Karachan | 10+10 | 1.9 | 0.81 | 90 | 1.09 | 0 | 10.5 | 9.41 | 8.73 | available | 217 | SS 110/35/10 kV B. Karachan | 10+10 | 0.33 | 2.23 | 1.18 | 90 | 1.05 | 0 | 10.5 | 9.45 | 8.4 | available
| Sn. MV, MVA | 10+10 | 0.13 | 0.81 | 90 | -0.68 | 0 | 10.5 | 11.18 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 0.13 | 1.18 | 90 | -1.05 | 0 | 10.5 | 11.55
| Sn. LV, MVA | 10+10 | 1.77 | 0 | 0 | 1.77 | 0 | 10.5 | 8.73 |  |  |  | Sn. LV, MVA | 10+10 | 0.33 | 2.1 | 0 | 0 | 2.1 | 0 | 10.5 | 8.4
218 | SS 110/35/10 kV Ternovka | 10+10 | 3.89 | 1.03 | 60 | 2.86 | 0 | 10.5 | 7.64 | 7.64 | available | 218 | SS 110/35/10 kV Ternovka | 10+10 | 0.06 | 3.95 | 1.03 | 60 | 2.92 | 0 | 10.5 | 7.58 | 7.58 | available
| Sn. MV, MVA | 10+10 | 1.2 | 1.03 | 60 | 0.17 | 0 | 10.5 | 10.33 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 1.2 | 1.03 | 60 | 0.17 | 0 | 10.5 | 10.33
| Sn. LV, MVA | 10+10 | 2.69 | 0 | 0 | 2.69 | 0 | 10.5 | 7.81 |  |  |  | Sn. LV, MVA | 10+10 | 0.06 | 2.75 | 0 | 0 | 2.75 | 0 | 10.5 | 7.75
219 | SS 110/35/10 kV People | 16+10 | 3.35 | 0.6 | 90 | 2.75 | 0 | 10.5 | 7.75 | 7.68 | available | 219 | SS 110/35/10 kV People | 16+10 | 0.47 | 3.82 | 0.93 | 90 | 2.89 | 0 | 10.5 | 7.61 | 7.21 | available
| Sn. MV, MVA | 16+10 | 0.53 | 0.6 | 90 | -0.07 | 0 | 10.5 | 10.57 |  |  |  | Sn. MV, MVA | 16+10 | 0 | 0.53 | 0.93 | 90 | -0.4 | 0 | 10.5 | 10.9
| Sn. LV, MVA | 16+10 | 2.82 | 0 | 0 | 2.82 | 0 | 10.5 | 7.68 |  |  |  | Sn. LV, MVA | 16+10 | 0.47 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21
220 | SS 110/35/10 kV N. Hopersky | 10+16 | 8.13 | 1.7 | 120 | 6.43 | 0 | 10.5 | 4.07 | 4.07 | available | 220 | SS 110/35/10 kV N. Hopersky | 10+16 | 1.83 | 9.96 | 1.95 | 120 | 8.01 | 0 | 10.5 | 2.49 | 2.49 | available
| Sn. MV, MVA | 10+16 | 2.52 | 1.7 | 120 | 0.82 | 0 | 10.5 | 9.68 |  |  |  | Sn. MV, MVA | 10+16 | 0 | 2.52 | 1.95 | 120 | 0.57 | 0 | 10.5 | 9.93
| Sn. LV, MVA | 10+16 | 5.61 | 0 | 0 | 5.61 | 0 | 10.5 | 4.89 |  |  |  | Sn. LV, MVA | 10+16 | 1.83 | 7.44 | 0 | 0 | 7.44 | 0 | 10.5 | 3.06
221 | SS 110/35/10 kV Ertil | 16+16 | 8.64 | 2.92 | 180 | 5.72 | 0 | 16.8 | 11.08 | 7.35 | available | 221 | SS 110/35/10 kV Ertil | 16+16 | 0.08 | 8.72 | 1.4 | 180 | 7.32 | 0 | 16.8 | 9.48 | 5.83 | available
| Sn. MV, MVA | 10+16 | 6.07 | 2.92 | 180 | 3.15 | 0 | 10.5 | 7.35 |  |  |  | Sn. MV, MVA | 10+16 | 0 | 6.07 | 1.4 | 180 | 4.67 | 0 | 10.5 | 5.83
| Sn. LV, MVA | 10+16 | 2.57 | 0.08 | 0 | 2.49 | 0 | 10.5 | 8.01 |  |  |  | Sn. LV, MVA | 10+16 | 0.08 | 2.65 | 0 | 0 | 2.65 | 0 | 10.5 | 7.85
222 | SS 110/35/10 kV Pike | 6,3+6,3 | 2.06 | 1.09 | 180 | 0.97 | 0 | 6.615 | 5.645 | 5.475 | available | 222 | SS 110/35/10 kV Pike | 6,3+6,3 | 0.78 | 2.84 | 2.33 | 180 | 0.51 | 0 | 6.615 | 6.105 | 4.965 | available
| Sn. MV, MVA | 6,3+6,3 | 0.67 | 0.84 | 180 | -0.17 | 0 | 6.615 | 6.785 |  |  |  | Sn. MV, MVA | 6,3+6,3 | 0 | 0.67 | 1.81 | 180 | -1.14 | 0 | 6.615 | 7.755
| Sn. LV, MVA | 6,3+6,3 | 1.39 | 0.25 | 180 | 1.14 | 0 | 6.615 | 5.475 |  |  |  | Sn. LV, MVA | 6,3+6,3 | 0.78 | 2.17 | 0.52 | 180 | 1.65 | 0 | 6.615 | 4.965
223 | SS 110/10 kV Dokuchaevo | 10+10 | 2.32 | 0.45 | 120 | 1.87 | 0 | 10.5 | 8.63 | 8.63 | available | 223 | SS 110/10 kV Dokuchaevo | 10+10 | 0.08 | 2.4 | 0.45 | 120 | 1.95 | 0 | 10.5 | 8.55 | 8.55 | available
224 | SS 110/10 kV B. Gribanovka | 16+16 | 9.24 | 0.11 | 30 | 9.13 | 0 | 16.8 | 7.67 | 7.67 | available | 224 | SS 110/10 kV B. Gribanovka | 16+16 | 1.91 | 11.15 | 0.24 | 30 | 10.91 | 0 | 16.8 | 5.89 | 5.89 | available
225 | SS 110/6 kV Khimmash | 16+16 | 6.66 | 0 | 0 | 6.66 | 0 | 16.8 | 10.14 | 10.14 | available | 225 | SS 110/6 kV Khimmash | 16+16 | 0 | 6.66 | 0 | 0 | 6.66 | 0 | 16.8 | 10.14 | 10.14 | available
226 | SS 35/10 kV Chigorak | 2,5+4 | 0.9 | 0.74 | 90 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 226 | SS 35/10 kV Chigorak | 2,5+4 | 0.46 | 1.36 | 0.96 | 90 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available
227 | SS 35/10 kV Tretiak | 4+4 | 1.21 | 0 | 0 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | available | 227 | SS 35/10 kV Tretiak | 4+4 | 1.35 | 2.56 | 0 | 0 | 2.56 | 0 | 4.2 | 1.64 | 1.64 | available
228 | SS 35/10 kV Gubar | 2,5+2,5 | 0.31 | 0.08 | 180 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 228 | SS 35/10 kV Gubar | 2,5+2,5 | 0.15 | 0.46 | 0.08 | 180 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | available
229 | SS 35/10 kV Tantsyrey | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 229 | SS 35/10 kV Tantsyrey | 2,5+2,5 | 0.27 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | available
230 | SS 35/10 kV Sands | 4+4 | 3.17 | 0 | 0 | 3.17 | 0 | 4.2 | 1.03 | 1.03 | available | 230 | SS 35/10 kV Sands | 4+4 | 1.99 | 5.16 | 0 | 0 | 5.16 | 0 | 4.2 | -0.96 | -0.96 | unavailable
231 | SS 35/10 kV M. Gribanovka | 1,6+1,6 | 0.38 | 0.07 | 30 | 0.31 | 0 | 1.68 | 1.37 | 1.37 | available | 231 | SS 35/10 kV M. Gribanovka | 1,6+1,6 | 0.33 | 0.71 | 0.07 | 30 | 0.64 | 0 | 1.68 | 1.04 | 1.04 | available
232 | SS 35/10 kV N. Karachan | 2,5+2,5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | available | 232 | SS 35/10 kV N. Karachan | 2,5+2,5 | 0.1 | 0.65 | 0 | 0 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | available
233 | SS 35/10 kV Kozlovka BES | 4+2,5 | 1.04 | 0 | 0 | 1.04 | 0 | 2.625 | 1.585 | 1.585 | available | 233 | SS 35/10 kV Kozlovka BES | 4+2,5 | 0.03 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | available
234 | SS 35/10 kV K. Otdelets | 2,5+2,5 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 234 | SS 35/10 kV K. Otdelets | 2,5+2,5 | 0 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available
235 | SS 35/10 kV Esipovo | 2,5+2,5 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | available | 235 | SS 35/10 kV Esipovo | 2,5+2,5 | 0.02 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | available
236 | SS 35/10 kV Kiselnoe | 2,5+2,5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available | 236 | SS 35/10 kV Kiselnoe | 2,5+2,5 | 0 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | available
237 | SS 35/10 kV Red | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | available | 237 | SS 35/10 kV Red | 4+4 | 1.55 | 2.15 | 0 | 0 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | available
238 | SS 35/10 kV Trinity | 2,5+2,5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | available | 238 | SS 35/10 kV Trinity | 2,5+2,5 | 0.01 | 0.49 | 0 | 0 | 0.49 | 0 | 2.625 | 2.135 | 2.135 | available
239 | SS 35/10 kV Ertil-city | 6,3+6,3 | 3.48 | 1.61 | 240 | 1.87 | 0 | 6.615 | 4.745 | 4.745 | available | 239 | SS 35/10 kV Ertil-city | 6,3+6,3 | 0.2 | 3.68 | 1.61 | 240 | 2.07 | 0 | 6.615 | 4.545 | 4.545 | available
240 | SS 35/10 kV Rostoshi | 4+4 | 1.32 | 0 | 0 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | available | 240 | SS 35/10 kV Rostoshi | 4+4 | 0 | 1.32 | 0 | 0 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | available
241 | SS 35/10 kV Vvedenka | 2,5+2,5 | 0.16 | 0 | 0 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 241 | SS 35/10 kV Vvedenka | 2,5+2,5 | 0 | 0.16 | 0 | 0 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available
242 | SS 35/10 kV Garden | 4+4 | 2.23 | 0 | 0 | 2.23 | 0 | 4.2 | 1.97 | 1.97 | available | 242 | SS 35/10 kV Garden | 4+4 | 0.36 | 2.59 | 0 | 0 | 2.59 | 0 | 4.2 | 1.61 | 1.61 | available
243 | SS 35/10 kV Rubashevka | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 243 | SS 35/10 kV Rubashevka | 2,5+2,5 | 0.03 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | available
244 | SS 35/10 kV N. Nadezhdenka | 2,5+2,5 | 0.46 | 0.37 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 244 | SS 35/10 kV N. Nadezhdenka | 2,5+2,5 | 0 | 0.46 | 0.37 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available
245 | SS 35/10 kV Abramovka | 6,3+4 | 2.77 | 0.17 | 120 | 2.6 | 0 | 4.2 | 1.6 | 1.6 | available | 245 | SS 35/10 kV Abramovka | 6,3+4 | 0.22 | 2.99 | 0.17 | 120 | 2.82 | 0 | 4.2 | 1.38 | 1.38 | available
246 | SS 35/10 kV Aleksandrovka BES | 2,5+2,5 | 0.87 | 0.56 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | available | 246 | SS 35/10 kV Aleksandrovka BES | 2,5+2,5 | 0.05 | 0.92 | 0.56 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | available
247 | SS 35/10 kV Trinity N. | 4+4 | 0.38 | 0.24 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | available | 247 | SS 35/10 kV Trinity N. | 4+4 | 0 | 0.24 | 0.24 | 120 | 0 | 0 | 4.2 | 4.2 | 4.06 | available
248 | SS 110/35/10 kV Kalach-1 | 25+25 | 13.87 | 2.2 | 120 | 11.67 | 0 | 26.25 | 14.58 | 14.58 | available | 248 | SS 110/35/10 kV Kalach-1 | 25+25 | 2.34 | 16.21 | 2.2 | 120 | 14.01 | 0 | 26.25 | 12.24 | 12.24 | available
| Sn. MV, MVA | 25+25 | 6.32 | 1 | 120 | 5.32 | 0 | 26.25 | 20.93 |  |  |  | Sn. MV, MVA | 25+25 | 0 | 6.32 | 1 | 120 | 5.32 | 0 | 26.25 | 20.93
| Sn. LV, MVA | 25+25 | 7.55 | 1.2 | 120 | 6.35 | 0 | 26.25 | 19.9 |  |  |  | Sn. LV, MVA | 25+25 | 2.34 | 9.89 | 1.2 | 120 | 8.69 | 0 | 26.25 | 17.56
249 | SS 110/10 kV Kalach-2 | 16+16 | 7.66 | 2 | 1 day and night | 5.66 | 0 | 16.8 | 11.14 | 11.14 | available | 249 | SS 110/10 kV Kalach-2 | 16+16 | 2.56 | 10.22 | 2 | 1 day and night | 8.22 | 0 | 16.8 | 8.58 | 8.58 | available
250 | SS 110/35/10 kV Buturlinovka-1 | 16+16 | 13.48 | 2 | 120 | 11.48 | 0 | 16.8 | 5.32 | 5.32 | available | 250 | SS 110/35/10 kV Buturlinovka-1 | 16+16 | 0.31 | 13.79 | 2 | 120 | 11.79 | 0 | 16.8 | 5.01 | 5.01 | available
| Sn. MV, MVA | 16+16 | 3.12 | 0 | 0 | 3.12 | 0.37 | 16.8 | 13.31 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 3.12 | 0 | 0 | 3.12 | 0 | 16.8 | 13.68
| Sn. LV, MVA | 16+16 | 10.36 | 2 | 120 | 8.36 | 0 | 16.8 | 8.44 |  |  |  | Sn. LV, MVA | 16+16 | 0.31 | 10.67 | 2 | 120 | 8.67 | 0 | 16.8 | 8.13
251 | SS 110/10 kV Buturlinovka-2 | 6,3+6,3 | 4.42 | 1.5 | 120 | 2.92 | 0 | 6.615 | 3.695 | 3.695 | available | 251 | SS 110/10 kV Buturlinovka-2 | 6,3+6,3 | 0.01 | 4.43 | 1.5 | 120 | 2.93 | 0 | 6.615 | 3.685 | 3.685 | available
252 | SS 110/35/10 kV N.Kislyay | 10+10 | 5.61 | 1.5 | 120 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | available | 252 | SS 110/35/10 kV N.Kislyay | 10+10 | 0.8 | 6.41 | 1.5 | 120 | 4.91 | 0 | 10.5 | 5.59 | 5.59 | available
| Sn. MV, MVA | 10+10 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58
| Sn. LV, MVA | 10+10 | 2.69 | 1.5 | 120 | 1.19 | 0 | 10.5 | 9.31 |  |  |  | Sn. LV, MVA | 10+10 | 0.8 | 3.49 | 1.5 | 120 | 1.99 | 0 | 10.5 | 8.51
253 | SS 110/10 kV Kozlovka IES | 2,5+6,3 | 1.17 | 1.5 | 45 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | available | 253 | SS 110/10 kV Kozlovka IES | 2,5+6,3 | 0.18 | 1.35 | 1.5 | 45 | -0.15 | 0 | 2.625 | 2.775 | 2.775 | available
254 | SS 110/10 kV Filippenkovo | 6,3+6,3 | 1.14 | 1.5 | 120 | -0.36 | 0 | 6.615 | 6.975 | 6.975 | available | 254 | SS 110/10 kV Filippenkovo | 6,3+6,3 | 0.05 | 1.19 | 1.5 | 120 | -0.31 | 0 | 6.615 | 6.925 | 6.925 | available
255 | SS 110/35/10 kV Vorob'evka | 16+16 | 7.48 | 1.5 | 120 | 5.98 | 0 | 16.8 | 10.82 | 10.82 | available | 255 | SS 110/35/10 kV Vorob'evka | 16+16 | 0.43 | 7.91 | 1.5 | 120 | 6.41 | 0 | 16.8 | 10.39 | 10.39 | available
| Sn. MV, MVA | 16+16 | 4.88 | 0.5 | 120 | 4.38 | 0 | 16.8 | 12.42 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 4.88 | 0.5 | 120 | 4.38 | 0 | 16.8 | 12.42
| Sn. LV, MVA | 16+16 | 2.6 | 1 | 120 | 1.6 | 0 | 16.8 | 15.2 |  |  |  | Sn. LV, MVA | 16+16 | 0.43 | 3.03 | 1 | 120 | 2.03 | 0 | 16.8 | 14.77
256 | SS 110/35/10 kV Solontsy | 6,3+6,3 | 0.95 | 1 | 1 day and night | -0.05 | 0 | 6.615 | 6.665 | 5.885 | available | 256 | SS 110/35/10 kV Solontsy | 6,3+6,3 | 0.03 | 0.98 | 1 | 1 day and night | -0.02 | 0 | 6.615 | 6.635 | 5.855 | available
| Sn. MV, MVA | 6,3+6,3 | 0.22 | 1 | 1 day and night | -0.78 | 0 | 6.615 | 7.395 |  |  |  | Sn. MV, MVA | 6,3+6,3 | 0 | 0.22 | 1 | 1 day and night | -0.78 | 0 | 6.615 | 7.395
| Sn. LV, MVA | 6,3+6,3 | 0.73 | 0 | 0 | 0.73 | 0 | 6.615 | 5.885 |  |  |  | Sn. LV, MVA | 6,3+6,3 | 0.03 | 0.76 | 0 | 0 | 0.76 | 0 | 6.615 | 5.855
257 | SS 110/35/10 kV Mannino | 16+16 | 1.22 | 1.5 | 1 day and night | -0.28 | 0 | 16.8 | 17.08 | 16.58 | available | 257 | SS 110/35/10 kV Mannino | 16+16 | 0.04 | 1.26 | 1.5 | 1 day and night | -0.24 | 0 | 16.8 | 17.04 | 16.54 | available
| Sn. MV, MVA | 16+16 | 0 | 0.5 | 1 day and night | -0.5 | 0 | 16.8 | 17.3 |  |  |  | Sn. MV, MVA | 16+16 | 0 | 0 | 0.5 | 1 day and night | -0.5 | 0 | 16.8 | 17.3
| Sn. LV, MVA | 16+16 | 1.22 | 1 | 1 day and night | 0.22 | 0 | 16.8 | 16.58 |  |  |  | Sn. LV, MVA | 16+16 | 0.04 | 1.26 | 1 | 1 day and night | 0.26 | 0 | 16.8 | 16.54
258 | SS 110/35/10 kV Petropavlovka | 10+10 | 4.83 | 2 | 120 | 2.83 | 0 | 10.5 | 7.67 | 7.67 | available | 258 | SS 110/35/10 kV Petropavlovka | 10+10 | 1.49 | 6.32 | 2 | 120 | 4.32 | 0 | 10.5 | 6.18 | 6.18 | available
| Sn. MV, MVA | 10+10 | 1.92 | 1 | 120 | 0.92 | 0 | 10.5 | 9.58 |  |  |  | Sn. MV, MVA | 10+10 | 0 | 2 | 1 | 120 | 1 | 0 | 10.5 | 9.5
| Sn. LV, MVA | 10+10 | 2.91 | 1 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Sn. LV, MVA | 10+10 | 1.49 | 4.4 | 1 | 120 | 3.4 | 0 | 10.5 | 7.1
259 | SS 110/35/10 kV V.Mamon | 16+10 | 5.68 | 2 | 120 | 3.68 | 0 | 10.5 | 6.82 | 6.82 | available | 259 | SS 110/35/10 kV V.Mamon | 16+10 | 1.61 | 7.29 | 2 | 120 | 5.29 | 0 | 10.5 | 5.21 | 5.21 | available
| Sn. MV, MVA | 16+10 | 2.14 | 0 | 0 | 2.14 | 0 | 10.5 | 8.36 |  |  |  | Sn. MV, MVA | 16+10 | 0 | 2.14 | 0 | 0 | 2.14 | 0 | 10.5 | 8.36
| Sn. LV, MVA | 16+10 | 3.54 | 2 | 120 | 1.54 | 0 | 10.5 | 8.96 |  |  |  | Sn. LV, MVA | 16+10 | 1.61 | 5.15 | 2 | 120 | 3.15 | 0 | 10.5 | 7.35
260 | SS 110/10 kV N.Mamon | 2,5+6,3 | 1.28 | 0 | 0 | 1.28 | 0 | 2.625 | 1.345 | 1.345 | available | 260 | SS 110/10 kV N.Mamon | 2,5+6,3 | 0.08 | 1.36 | 0 | 0 | 1.36 | 0 | 2.625 | 1.265 | 1.265 | available
261 | SS 110/35/10 kV Pavlovsk-2 | 25+25 | 20.78 | 1.5 | 120 | 19.28 | 0 | 26.25 | 6.97 | 6.97 | available | 261 | SS 110/35/10 kV Pavlovsk-2 | 25+25 | 0.14 | 20.92 | 1.5 | 120 | 19.42 | 0 | 26.25 | 6.83 | 6.83 | available
| Sn. MV, MVA | 25+25 | 13.01 | 1.5 | 120 | 11.51 | 0 | 26.25 | 14.74 |  |  |  | Sn. MV, MVA | 25+25 | 0 | 13.01 | 1.5 | 120 | 11.51 | 0 | 26.25 | 14.74
| Sn. LV, MVA | 25+25 | 7.77 | 0 | 0 | 7.77 | 0 | 26.25 | 18.48 |  |  |  | Sn. LV, MVA | 25+25 | 0.14 | 7.91 | 0 | 0 | 7.91 | 0 | 26.25 | 18.34
262 | SS 110/35/10 kV Bogucharsky | 16+16 | 9.98 | 2 | 120 | 7.98 | 0 | 16.8 | 8.82 | 8.82 | available | 262 | SS 110/35/10 kV Bogucharsky | 16+16 | 3.88 | 13.86 | 2 | 120 | 11.86 | 0 | 16.8 | 4.94 | 4.94 | unavailable
| Sn. MV, MVA | 16+16 | 4.4 | 1 | 120 | 3.4 | 0 | 16.8 | 13.4 |  |  |  | Sn. MV, MVA | 16+16 | 1.13 | 5.53 | 1 | 120 | 4.53 | 0 | 16.8 | 12.27
| Sn. LV, MVA | 16+16 | 5.58 | 1 | 120 | 4.58 | 0 | 16.8 | 12.22 |  |  |  | Sn. LV, MVA | 16+16 | 2.75 | 8.33 | 1 | 120 | 7.33 | 0 | 16.8 | 9.47
263 | SS 110/10 kV reference | 6,3+6,3 | 2.4 | 1.5 | 120 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | available | 263 | SS 110/10 kV reference | 6,3+6,3 | 1.05 | 3.45 | 1.5 | 120 | 1.95 | 0 | 6.615 | 4.665 | 4.665 | available
264 | SS 35/10 kV Podgornaya IES | 2,5+2,5 | 0.8 | 1 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | available | 264 | SS 35/10 kV Podgornaya IES | 2,5+2,5 | 0.09 | 0.89 | 1 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | available
265 | SS 35/10 kV Bolshevik IES | 4+2,5 | 2.24 | 1.5 | 45 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | available | 265 | SS 35/10 kV Bolshevik IES | 4+2,5 | 0.5 | 2.74 | 1.5 | 45 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | available
266 | SS 35/10 kV Semenovka IES | 2,5+1,8 | 0.71 | 1 | 80 | -0.29 | 0 | 1.89 | 2.18 | 2.18 | available | 266 | SS 35/10 kV Semenovka IES | 2,5+1,8 | 0.1 | 0.81 | 1 | 80 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | available
267 | SS 35/10 kV Popasnaya | 4+4 | 0.34 | 1.5 | 120 | -1.16 | 0 | 4.2 | 5.36 | 5.36 | available | 267 | SS 35/10 kV Popasnaya | 4+4 | 0.04 | 0.38 | 1.5 | 120 | -1.12 | 0 | 4.2 | 5.32 | 5.32 | available
268 | SS 35/10 kV N.Kriusha | 2,5+2,5 | 0.89 | 1.5 | 45 | -0.61 | 0 | 2.625 | 3.235 | 3.235 | available | 268 | SS 35/10 kV N.Kriusha | 2,5+2,5 | 1.74 | 2.63 | 1.5 | 45 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | available
269 | SS 35/10 kV N.Melovatka | 2,5+2,5 | 1.44 | 1.5 | 45 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | available | 269 | SS 35/10 kV N.Melovatka | 2,5+2,5 | 0.26 | 1.7 | 1.5 | 45 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available
270 | SS 35/10 kV Vasilevka IES | 4+4 | 0.89 | 1.5 | 120 | -0.61 | 0 | 4.2 | 4.81 | 4.81 | available | 270 | SS 35/10 kV Vasilevka IES | 4+4 | 0.08 | 0.97 | 1.5 | 120 | -0.53 | 0 | 4.2 | 4.73 | 4.73 | available
271 | SS 35/10 kV V.Oktyabr | 4+4 | 1.76 | 1.5 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | available | 271 | SS 35/10 kV V.Oktyabr | 4+4 | 0.22 | 1.98 | 1.5 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | available
272 | SS 35/10 kV V.Arhangelskoe | 2,5+2,5 | 0.43 | 1.5 | 45 | -1.07 | 0 | 2.625 | 3.695 | 3.695 | available | 272 | SS 35/10 kV V.Arhangelskoe | 2,5+2,5 | 0.07 | 0.5 | 1.5 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 | available
273 | SS 35/10 kV Leschanaya | 2,5+2,5 | 1.82 | 1.5 | 45 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | available | 273 | SS 35/10 kV Leschanaya | 2,5+2,5 | 0.18 | 2 | 1.5 | 45 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | available
274 | SS 35/10 kV Muzhiks | 4+2,5 | 0.52 | 1.5 | 45 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | available | 274 | SS 35/10 kV Muzhiks | 4+2,5 | 0.11 | 0.63 | 1.5 | 45 | -0.87 | 0 | 2.625 | 3.495 | 3.495 | available
275 | SS 35/10 kV Rudnya | 4+4 | 0.48 | 1.5 | 120 | -1.02 | 0 | 4.2 | 5.22 | 5.22 | available | 275 | SS 35/10 kV Rudnya | 4+4 | 0.04 | 0.52 | 1.5 | 120 | -0.98 | 0 | 4.2 | 5.18 | 5.18 | available
276 | SS 35/10 kV S. Chalk | 4+4 | 0.95 | 0 | 0 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | available | 276 | SS 35/10 kV S. Chalk | 4+4 | 0.36 | 1.31 | 0 | 0 | 1.31 | 0 | 4.2 | 2.89 | 2.89 | available
277 | SS 35/10 kV S. Kriusha | 2,5+4 | 1.05 | 0 | 0 | 1.05 | 0 | 2.625 | 1.575 | 1.575 | available | 277 | SS 35/10 kV S. Kriusha | 2,5+4 | 0.3 | 1.35 | 0 | 0 | 1.35 | 0 | 2.625 | 1.275 | 1.275 | available
278 | SS 35/10 kV Lozova | 4+4 | 0.72 | 0 | 0 | 0.72 | 0 | 4.2 | 3.48 | 3.48 | available | 278 | SS 35/10 kV Lozova | 4+4 | 0.3 | 1.02 | 0 | 0 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | available
279 | SS 35/10 kV Pavlovsk-1 | 4+4 | 3.87 | 1 | 120 | 2.87 | 0 | 4.2 | 1.33 | 1.33 | available | 279 | SS 35/10 kV Pavlovsk-1 | 4+4 | 0.38 | 4.25 | 1 | 120 | 3.25 | 0 | 4.2 | 0.95 | 0.95 | available
280 | SS 35/10 kV Losevo IES | 4+4 | 3.2 | 0 | 0 | 3.2 | 0 | 4.2 | 1 | 1 | available | 280 | SS 35/10 kV Losevo IES | 4+4 | 0.09 | 3.29 | 0 | 0 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | available
281 | SS 35/10 kV Gavrilsk | 4+4 | 0.55 | 0 | 0 | 0.55 | 0 | 4.2 | 3.65 | 3.65 | available | 281 | SS 35/10 kV Gavrilsk | 4+4 | 0.03 | 0.58 | 0 | 0 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | available
282 | SS 35/10 kV Pokrovka | 4+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | available | 282 | SS 35/10 kV Pokrovka | 4+2,5 | 0.02 | 0.82 | 0 | 0 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | available
283 | SS 35/10 kV Vorontsovka | 4+4 | 2.99 | 1.5 | 120 | 1.49 | 0 | 4.2 | 2.71 | 2.71 | available | 283 | SS 35/10 kV Vorontsovka | 4+4 | 0.7 | 3.69 | 1.5 | 120 | 2.19 | 0 | 4.2 | 2.01 | 2.01 | available
284 | SS 35/10 kV A.Donskaya | 2,5+2,5 | 1.13 | 1.5 | 45 | -0.37 | 0 | 2.625 | 2.995 | 2.995 | available | 284 | SS 35/10 kV A.Donskaya | 2,5+2,5 | 0.14 | 1.27 | 1.5 | 45 | -0.23 | 0 | 2.625 | 2.855 | 2.855 | available
285 | SS 35/10 kV Petrovka | 2,5+4 | 1.79 | 1.55 | 45 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 285 | SS 35/10 kV Petrovka | 2,5+4 | 2.38 | 4.17 | 1.55 | 45 | 2.62 | 0 | 2.625 | 0.005 | 0.005 | available
286 | SS 35/10 kV Monastyrshchina | 4+4 | 0.66 | 1.5 | 120 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | available | 286 | SS 35/10 kV Monastyrshchina | 4+4 | 0.21 | 0.87 | 1.5 | 120 | -0.63 | 0 | 4.2 | 4.83 | 4.83 | available
287 | SS 35/10 kV Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | available | 287 | SS 35/10 kV Zhuravka | 1,8+2,5 | 0.03 | 0.18 | 0 | 0 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | available
288 | SS 35/10 kV Dyachenkovo | 2,5+2,5 | 1.83 | 1.5 | 45 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 288 | SS 35/10 kV Dyachenkovo | 2,5+2,5 | 1.53 | 3.36 | 1.5 | 45 | 1.86 | 0 | 2.625 | 0.765 | 0.765 | available
289 | SS 35/10 kV Radchenskaya | 1,6+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 1.68 | 0.98 | 0.98 | available | 289 | SS 35/10 kV Radchenskaya | 1,6+2,5 | 0.82 | 1.52 | 0 | 0 | 1.52 | 0 | 1.68 | 0.16 | 0.16 | available
290 | SS 35/10 kV Russia | 4+4 | 1.4 | 1.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | available | 290 | SS 35/10 kV Russia | 4+4 | 0.42 | 1.82 | 1.5 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | available
291 | SS 35/10 kV Pervomayskaya | 4+4 | 0.53 | 1.5 | 120 | -0.97 | 0 | 4.2 | 5.17 | 5.17 | available | 291 | SS 35/10 kV Pervomayskaya | 4+4 | 0.23 | 0.76 | 1.5 | 120 | -0.74 | 0 | 4.2 | 4.94 | 4.94 | available
292 | SS 35/10 kV Podkolodnovka | 2,5+3,2 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 292 | SS 35/10 kV Podkolodnovka | 2,5+3,2 | 0.23 | 1.02 | 0 | 0 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | available
293 | SS 35/10 kV N.Usman-1 | 10+6,3 | 11.43 | 0 | 0 | 11.43 | 0 | 6.62 | -4.81 | -4.81 | перераспределение на новую ПС Новоусманская | 293 | SS 35/10 kV N.Usman-1 | 10+6,3 | 0 | 11.43 | 0 | 0 | 11.43 | 1 | 6.62 | 0 | 0 | available
294 | SS 35/10 kV Levoberezhnaya | 2,5+2,5 | 0 | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 294 | SS 35/10 kV Levoberezhnaya | 2,5+2,5 | 0 | 0 | 0 | 0 | 0 | 2 | 2.625 | 0.625 | 0.625 | available
295 | SS 35/10 kV Southern | 2,5+2,5 | 0.12 | 0 | 0 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available | 295 | SS 35/10 kV Southern | 2,5+2,5 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | available
| TOTAL: | [8 empty] | 1256.5427 |  | 2: TOTAL:; Min 12: 906.8852
| deficit | [8 empty] | 18.6226 |  | 2: deficit; Min 12: 62.5201
| proficit | [8 empty] | 1237.9201 |  | 2: proficit; Min 12: 844.3651
Note on Q1: не нашел
Note on Q2: не нашел
Note on Q411: не нашел
Note on Q412: не нашел
Note on Q413: не нашел
Note on Q414: не нашел
Note on Q415: не нашел
Note on X150: Ivanov_MA:
Note on AG9: не нашел
Note on AG34: не нашел
Note on AG59: не нашел
Note on AG94: не нашел
Note on AG119: не нашел
Note on AG234: не нашел
Note on AG289: не нашел
Note on AG351: не нашел
Note on AG417: не нашел