## Summary
Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2010 | [13 empty] | Calculation of transmission capacity of supply centres of IDGC of Center - Voronezhenergo following the winter peak load measurements in 2010
[11 empty] | Table 1 | [14 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note |  |  | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA | [5 empty] | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [13 empty] | MVA | Min
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
| SPS | [12 empty] | 2: SPS
1 | No. 44 | 10 | 0.02 | 0 | 0 | 0 | 0 | 0 | -0.02 | -0.02 |  |  |  | 1 | No. 44 | 10 | 0 | 0.02 | 0 | 0 | 0.02 | 0 | 0 | -0.02 | -0.02 | 110/6
2 | Stupino | 6.3 | 0.74 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.2975 | 0.2975 |  |  |  | 2 | Stupino | 6.3 | 1.51 | 2.25 | 1.0375 | 120 | 1.2125 | 0 | 1.0375 | -1.2125 | -1.2125 | 110/10
3 | P.Kommuna | 6.3 | 0.35 | 0.5 | 120 | 0.5 | 0 | 0.5 | 0.15 | 0.15 |  |  |  | 3 | P.Kommuna | 6.3 | 0 | 0.35 | 0.5 | 120 | -0.15 | 0 | 0.5 | 0.15 | 0.15 | 110/10
4 | No. 38 | 2.5 | 0.51 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.29 | 0.29 |  |  |  | 4 | No. 38 | 2.5 | 0 | 0.51 | 0.8 | 120 | -0.29 | 0 | 0.8 | 0.29 | 0.29 | 35/10
5 | No. 46 | 4 | 0.01 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.01 |  |  |  | 5 | No. 46 | 4 | 0 | 0.01 | 0 | 0 | 0.01 | 0 | 0 | -0.01 | -0.01 | 35/6
6 | Istobnoe | 4 | 0.32 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.04 | 0.04 |  |  |  | 6 | Istobnoe | 4 | 0.29 | 0.61 | 0.36 | 120 | 0.25 | 0 | 0.36 | -0.25 | -0.25 | 35/10
7 | Rodina | 2.5 | 0.44 | 2.2 | 120 | 2.2 | 0 | 2.2 | 1.76 | 1.76 |  |  |  | 7 | Rodina | 2.5 | 0.17 | 0.61 | 2.2 | 120 | -1.59 | 0 | 2.2 | 1.59 | 1.59 | 35/10
8 | Vyaznovatovka | 2.5 | 0.59 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.91 | 0.91 |  |  |  | 8 | Vyaznovatovka | 2.5 | 0.01 | 0.6 | 1.5 | 120 | -0.9 | 0 | 1.5 | 0.9 | 0.9 | 35/10
9 | V.Turovo-1 | 3.2 | 0.8 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.6 | 0.6 |  |  |  | 9 | V.Turovo-1 | 3.2 | 0.19 | 0.99 | 1.4 | 120 | -0.41 | 0 | 1.4 | 0.41 | 0.41 | 35/10
10 | Semidesyatnoe | 2.5 | 0.127 | 0 | 0 | 0 | 0 | 0 | -0.127 | -0.127 |  |  |  | 10 | Semidesyatnoe | 2.5 | 0.12 | 0.247 | 0 | 0 | 0.247 | 0 | 0 | -0.247 | -0.247 | 35/10
11 | Arkhangelskoe SPS | 2.5 | 0.49 | 0 | 0 | 0 | 0 | 0 | -0.49 | -0.49 |  |  |  | 11 | Arkhangelskoe SPS | 2.5 | 0.09 | 0.58 | 0 | 0 | 0.58 | 0 | 0 | -0.58 | -0.58 | 35/10
12 | Khokhol-2 | 2.5 | 1.29 | 0 | 0 | 0 | 0 | 0 | -1.29 | -1.29 |  |  |  | 12 | Khokhol-2 | 2.5 | 0.42 | 1.71 | 0 | 0 | 1.71 | 0 | 0 | -1.71 | -1.71 | 35/10
13 | N.Olshanka | 4 | 0.61 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | 0.1474 | 0.1474 |  |  |  | 13 | N.Olshanka | 4 | 0.09 | 0.7 | 0.7574 | 120 | -0.0574 | 0 | 0.7574 | 0.0574 | 0.0574 | 35/10
14 | Troitskoe | 2.5 | 0.515 | 0 | 0 | 0 | 0 | 0 | -0.515 | -0.515 |  |  |  | 14 | Troitskoe | 2.5 | 0.01 | 0.525 | 0 | 0 | 0.525 | 0 | 0 | -0.525 | -0.525 | 35/10
15 | Zemlyansk | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | -0.8 | -0.8 |  |  |  | 15 | Zemlyansk | 4 | 0.67 | 1.47 | 0 | 0 | 1.47 | 0 | 0 | -1.47 | -1.47 | 35/10
16 | Losevo SPS | 2.5 | 0.55 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.4036 | 0.4036 |  |  |  | 16 | Losevo SPS | 2.5 | 0 | 0.55 | 0.9536 | 120 | -0.4036 | 0 | 0.9536 | 0.4036 | 0.4036 | 35/10
17 | Verny | 2.5 | 1.55 | 2.15 | 120 | 2.15 | 0 | 2.15 | 0.6 | 0.6 |  |  |  | 17 | Verny | 2.5 | 0.13 | 1.68 | 2.15 | 120 | -0.47 | 0 | 2.15 | 0.47 | 0.47 | 35/10
18 | Elevator | 2.5 | 1.1 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0 | 0 |  |  |  | 18 | Elevator | 2.5 | 0.03 | 1.13 | 1.1 | 120 | 0.03 | 0 | 1.1 | -0.03 | -0.03 | 35/10
19 | Yubileynaya | 4 | 0.73 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.87 | 0.87 |  |  |  | 19 | Yubileynaya | 4 | 0.07 | 0.8 | 1.6 | 120 | -0.8 | 0 | 1.6 | 0.8 | 0.8 | 35/10
20 | Parusnoe | 4 | 2.36 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.7984 | 0.7984 |  |  |  | 20 | Parusnoe | 4 | 0.18 | 2.54 | 3.1584 | 120 | -0.6184 | 0 | 3.1584 | 0.6184 | 0.6184 | 35/10
21 | Rogachyovka | 4 | 1.85 | 2.05 | 120 | 2.05 | 0 | 2.05 | 0.2 | 0.2 |  |  |  | 21 | Rogachyovka | 4 | 0.09 | 1.94 | 2.05 | 120 | -0.11 | 0 | 2.05 | 0.11 | 0.11 | 35/10
22 | Poultry farm Rassvet | 2.5 | 0.19 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.11 | 0.11 |  |  |  | 22 | Poultry farm Rassvet | 2.5 | 0 | 0.19 | 0.3 | 120 | -0.11 | 0 | 0.3 | 0.11 | 0.11 | 35/10
23 | Dankovo | 2.5 | 0.86 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.039 | 0.039 |  |  |  | 23 | Dankovo | 2.5 | 0.02 | 0.88 | 0.899 | 120 | -0.019 | 0 | 0.899 | 0.019 | 0.019 | 35/10
| LPS | [12 empty] | 2: LPS
24 | Bugaevka | 16 | 7.68 | 14 | 90 | 14 | 0 | 14 | 6.32 | 1.3 |  |  |  | 24 | Bugaevka | 16 | 0.28 | 7.96 | 14 | 90 | -6.04 | 0 | 14 | 6.04 | 1.02
| Sн. MV, МVА | 16 | 4.98 | 10 | 90 | 10 | 0 | 10 | 5.02 | [5 empty] | Sн. MV, МVА | 16 | 0 | 4.98 | 10 | 90 | -5.02 | 0 | 10 | 5.02 |  | 110/35/10
| Sн. LV, МVА | 16 | 2.7 | 4 | 90 | 4 | 0 | 4 | 1.3 | [5 empty] | Sн. LV, МVА | 16 | 0.28 | 2.98 | 4 | 90 | -1.02 | 0 | 4 | 1.02
25 | Dobrino | 10 | 1.76 | 6.6 | 90 | 6.6 | 0 | 6.6 | 4.84 | 1.36 |  |  |  | 25 | Dobrino | 10 | 0.23 | 1.99 | 6.6 | 90 | -4.61 | 0 | 6.6 | 4.61 | 1.13
| Sн. MV, МVА | 10 | 0 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.8 | [5 empty] | Sн. MV, МVА | 10 | 0 | 0 | 5.8 | 90 | -5.8 | 0 | 5.8 | 5.8 |  | 110/35/10
| Sн. LV, МVА | 10 | 1.76 | 3.12 | 90 | 3.12 | 0 | 3.12 | 1.36 | [5 empty] | Sн. LV, МVА | 10 | 0.23 | 1.99 | 3.12 | 90 | -1.13 | 0 | 3.12 | 1.13
26 | N. Kalitva | 6.3 | 1.56 | 2 | 240 | 2 | 0 | 2 | 0.44 | 0.44 |  |  |  | 26 | N. Kalitva | 6.3 | 0.59 | 2.15 | 2 | 240 | 0.15 | 0 | 2 | -0.15 | -0.15 | 110/10
27 | Shishovka | 6.3 | 0.63 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.71 | 1.71 |  |  |  | 27 | Shishovka | 6.3 | 0.37 | 1 | 2.34 | 180 | -1.34 | 0 | 2.34 | 1.34 | 1.34 | 110/10
28 | Azovka | 10 | 1.68 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.44 | 1.44 |  |  |  | 28 | Azovka | 10 | 0.47 | 2.15 | 3.12 | 180 | -0.97 | 0 | 3.12 | 0.97 | 0.97 | 110/10
29 | Yurasovka | 2.5 | 0.84 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.72 | 0.72 |  |  |  | 29 | Yurasovka | 2.5 | 0.03 | 0.87 | 1.56 | 120 | -0.69 | 0 | 1.56 | 0.69 | 0.69 | 35/10
30 | Nerovnovka | 2.5 | 0.26 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.52 | 0.52 |  |  |  | 30 | Nerovnovka | 2.5 | 0.02 | 0.28 | 0.78 | 240 | -0.5 | 0 | 0.78 | 0.5 | 0.5 | 35/10
31 | Saprino | 1.8 | 0.35 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.45 | 1.45 |  |  |  | 31 | Saprino | 1.8 | 0.03 | 0.38 | 1.8 | 120 | -1.42 | 0 | 1.8 | 1.42 | 1.42 | 35/10
32 | Sergeevka | 4 | 0.43 | 0 | 0 | 0 | 0 | 0 | -0.43 | -0.43 |  |  |  | 32 | Sergeevka | 4 | 0.06 | 0.49 | 0 | 0 | 0.49 | 0 | 0 | -0.49 | -0.49 | 35/10
33 | Stepanovka | 4 | 0.266 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.294 | 1.294 |  |  |  | 33 | Stepanovka | 4 | 0.04 | 0.306 | 1.56 | 240 | -1.254 | 0 | 1.56 | 1.254 | 1.254 | 35/10
34 | Kolodezhanskaya | 2.5 | 0.29 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.49 | 0.49 |  |  |  | 34 | Kolodezhanskaya | 2.5 | 0.08 | 0.37 | 0.78 | 180 | -0.41 | 0 | 0.78 | 0.41 | 0.41 | 35/10
35 | Andreevka | 2.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.1 |  |  |  | 35 | Andreevka | 2.5 | 0.02 | 0.12 | 0 | 0 | 0.12 | 0 | 0 | -0.12 | -0.12 | 35/10
36 | Kulikovka | 4 | 1.74 | 0 | 0 | 0 | 0 | 0 | -1.74 | -1.74 |  |  |  | 36 | Kulikovka | 4 | 0.44 | 2.18 | 0 | 0 | 2.18 | 0 | 0 | -2.18 | -2.18 | 35/10
37 | Lizinovka | 2.5 | 1.12 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.38 | 1.38 |  |  |  | 37 | Lizinovka | 2.5 | 0.07 | 1.19 | 2.5 | 240 | -1.31 | 0 | 2.5 | 1.31 | 1.31 | 35/10
38 | Sotnitskaya | 4 | 1.4 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.9 | 0.9 |  |  |  | 38 | Sotnitskaya | 4 | 0.16 | 1.56 | 2.3 | 120 | -0.74 | 0 | 2.3 | 0.74 | 0.74 | 35/10
39 | Kr. Polyana | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  |  | 39 | Kr. Polyana | 2.5 | 0.04 | 0.33 | 0 | 0 | 0.33 | 0 | 0 | -0.33 | -0.33 | 35/10
40 | Gumny | 4 | 0.99 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.57 | 0.57 |  |  |  | 40 | Gumny | 4 | 0.19 | 1.18 | 1.56 | 180 | -0.38 | 0 | 1.56 | 0.38 | 0.38 | 35/10
41 | Uryv | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | -0.7 | -0.7 |  |  |  | 41 | Uryv | 2.5 | 0.11 | 0.81 | 0 | 0 | 0.81 | 0 | 0 | -0.81 | -0.81 | 35/10
42 | Shubnoe | 2.5 | 0.9 | 1.17 | 180 | 1.17 | 0 | 1.17 | 0.27 | 0.27 |  |  |  | 42 | Shubnoe | 2.5 | 0.19 | 1.09 | 1.17 | 180 | -0.08 | 0 | 1.17 | 0.08 | 0.08 | 35/10
43 | Zaluzhnoe | 2.5 | 2.01 | 2 | 240 | 2 | 0 | 2 | -0.01 | -0.01 |  |  |  | 43 | Zaluzhnoe | 2.5 | 0.52 | 2.53 | 2 | 240 | 0.53 | 0 | 2 | -0.53 | -0.53 | 35/10
| BPS | [12 empty] | 2: BPS
45 | Anna-2 | 25 | 5.45 | 7.8 | 90 | 7.8 | 0 | 7.8 | 2.35 | 0.74 |  |  |  | 45 | Anna-2 | 25 | 3.55 | 9 | 7.8 | 90 | 1.2 | 0 | 7.8 | -1.2 | -1.94
| Sн. MV, МVА | 25 | 1.5 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.74 | [5 empty] | Sн. MV, МVА | 25 | 0 | 1.5 | 2.24 | 90 | -0.74 | 0 | 2.24 | 0.74 |  | 110/35/10
| Sн. LV, МVА | 25 | 3.95 | 5.56 | 90 | 5.56 | 0 | 5.56 | 1.61 | [5 empty] | Sн. LV, МVА | 25 | 3.55 | 7.5 | 5.56 | 90 | 1.94 | 0 | 5.56 | -1.94
46 | Vostochnaya | 10 | 3.4 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.4 | 1.4 |  |  |  | 46 | Vostochnaya | 10 | 1.14 | 4.54 | 4.8 | 30 | -0.26 | 0 | 4.8 | 0.26 | 0.26 | 35/6
47 | BolshevikBPS | 6.3 | 0.92 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.54 | 0.54 |  |  |  | 47 | BolshevikBPS | 6.3 | 0.06 | 0.98 | 1.46 | 60 | -0.48 | 0 | 1.46 | 0.48 | 0.48 | 110/10
48 | Rozhdestvo | 6.3 | 0.68 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.07 | 0.07 |  |  |  | 48 | Rozhdestvo | 6.3 | 0.26 | 0.94 | 0.75 | 60 | 0.19 | 0 | 0.75 | -0.19 | -0.19 | 110/10
49 | V. Toyda | 6.3 | 0.84 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.56 | 0.56 |  |  |  | 49 | V. Toyda | 6.3 | 0.01 | 0.85 | 1.4 | 90 | -0.55 | 0 | 1.4 | 0.55 | 0.55 | 110/10
50 | Vostochnaya-1 | 40 | 6.43 | 8.13 | 60 | 8.13 | 0 | 8.13 | 1.7 | 0.37 |  |  |  | 50 | Vostochnaya-1 | 40 | 1.3 | 7.73 | 8.13 | 60 | -0.4 | 0 | 8.13 | 0.4 | 0.37
| Sн. MV, МVА | 40 | 5.3 | 5.67 | 60 | 5.67 | 0 | 5.67 | 0.37 | [5 empty] | Sн. MV, МVА | 40 | 0 | 5.3 | 5.67 | 60 | -0.37 | 0 | 5.67 | 0.37 |  | 110/35/6
| Sн. LV, МVА | 40 | 1.13 | 3.1 | 60 | 3.1 | 0 | 3.1 | 1.97 | [5 empty] | Sн. LV, МVА | 40 | 1.3 | 2.43 | 3.1 | 60 | -0.67 | 0 | 3.1 | 0.67
51 | Makashevka | 2.5 | 0.28 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.2 | 0.2 |  |  |  | 51 | Makashevka | 2.5 | 0.12 | 0.4 | 0.48 | 180 | -0.08 | 0 | 0.48 | 0.08 | 0.08 | 35/10
52 | Mirolyubie | 4 | 0.24 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.26 | 0.26 |  |  |  | 52 | Mirolyubie | 4 | 0.03 | 0.27 | 0.5 | 60 | -0.23 | 0 | 0.5 | 0.23 | 0.23 | 35/10
53 | V. Zaton | 2.5 | 0 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0.01 | 0.01 |  |  |  | 53 | V. Zaton | 2.5 | 0 | 0 | 0.01 | 60 | -0.01 | 0 | 0.01 | 0.01 | 0.01 | 35/10
54 | Oktyabrskoe | 2.5 | 0.58 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.09 | 0.09 |  |  |  | 54 | Oktyabrskoe | 2.5 | 0.13 | 0.71 | 0.67 | 30 | 0.04 | 0 | 0.67 | -0.04 | -0.04 | 35/10
55 | Ilmen | 2.5 | 0.217 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.163 | 0.163 |  |  |  | 55 | Ilmen | 2.5 | 0.05 | 0.267 | 0.38 | 60 | -0.113 | 0 | 0.38 | 0.113 | 0.113 | 35/10
56 | Vikhlyaevka | 2.5 | 0.09 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.03 | 0.03 |  |  |  | 56 | Vikhlyaevka | 2.5 | 0 | 0.09 | 0.12 | 120 | -0.03 | 0 | 0.12 | 0.03 | 0.03 | 35/10
57 | N. Elan | 2.5 | 0.53 | 0 | 0 | 0 | 0 | 0 | -0.53 | -0.53 |  |  |  | 57 | N. Elan | 2.5 | 0.02 | 0.55 | 0 | 0 | 0.55 | 0 | 0 | -0.55 | -0.55 | 35/10
58 | B. Alabukhi | 2.5 | 0.7 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.23 | 0.23 |  |  |  | 58 | B. Alabukhi | 2.5 | 0.17 | 0.87 | 0.93 | 90 | -0.06 | 0 | 0.93 | 0.06 | 0.06 | 35/10
59 | Pykhovka | 2.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | -0.25 | -0.25 |  |  |  | 59 | Pykhovka | 2.5 | 0 | 0.25 | 0 | 0 | 0.25 | 0 | 0 | -0.25 | -0.25 | 35/10
60 | Е. Koleno | 4 | 2.42 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.91 | 0.91 |  |  |  | 60 | Е. Koleno | 4 | 0.1 | 2.52 | 3.33 | 120 | -0.81 | 0 | 3.33 | 0.81 | 0.81 | 35/10
61 | Podgornoe BPS | 2.5 | 0.43 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.03 | 0.03 |  |  |  | 61 | Podgornoe BPS | 2.5 | 0.01 | 0.44 | 0.46 | 180 | -0.02 | 0 | 0.46 | 0.02 | 0.02 | 35/10
62 | Mikhailovka-1 | 4 | 0.25 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.11 | 0.11 |  |  |  | 62 | Mikhailovka-1 | 4 | 0 | 0.25 | 0.36 | 60 | -0.11 | 0 | 0.36 | 0.11 | 0.11 | 35/10
63 | Mikhailovka | 2.5 | 0.43 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.07 | 0.07 |  |  |  | 63 | Mikhailovka | 2.5 | 0.01 | 0.44 | 0.5 | 60 | -0.06 | 0 | 0.5 | 0.06 | 0.06 | 35/10
64 | Gnilusha | 4 | 0.75 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.17 | 0.17 |  |  |  | 64 | Gnilusha | 4 | 0 | 0.75 | 0.92 | 180 | -0.17 | 0 | 0.92 | 0.17 | 0.17 | 35/10
65 | Mayskaya | 2.5 | 0.61 | 0 | 0 | 0 | 0 | 0 | -0.61 | -0.61 |  |  |  | 65 | Mayskaya | 2.5 | 0 | 0.61 | 0 | 0 | 0.61 | 0 | 0 | -0.61 | -0.61 | 35/10
66 | Khleborodnoe | 2.5 | 0.45 | 0 | 0 | 0 | 0 | 0 | -0.45 | -0.45 |  |  |  | 66 | Khleborodnoe | 2.5 | 0.09 | 0.54 | 0 | 0 | 0.54 | 0 | 0 | -0.54 | -0.54 | 35/10
67 | N. Kurlak | 4 | 0.49 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.11 | 0.11 |  |  |  | 67 | N. Kurlak | 4 | 0 | 0.49 | 0.6 | 120 | -0.11 | 0 | 0.6 | 0.11 | 0.11 | 35/10
68 | Nikolaevka | 4 | 1.17 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.33 | 0.33 |  |  |  | 68 | Nikolaevka | 4 | 0.04 | 1.21 | 1.5 | 120 | -0.29 | 0 | 1.5 | 0.29 | 0.29 | 35/10
69 | Vasilyevka BPS | 2.5 | 0.52 | 0.39 | 180 | 0.39 | 0 | 0.39 | -0.13 | -0.13 |  |  |  | 69 | Vasilyevka BPS | 2.5 | 0.09 | 0.61 | 0.39 | 180 | 0.22 | 0 | 0.39 | -0.22 | -0.22 | 35/10
70 | Avangard | 2.5 | 0.38 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.53 | 0.53 |  |  |  | 70 | Avangard | 2.5 | 0.07 | 0.45 | 0.91 | 120 | -0.46 | 0 | 0.91 | 0.46 | 0.46 | 35/10
71 | Orlovka | 2.5 | 0.45 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.03 | 0.03 |  |  |  | 71 | Orlovka | 2.5 | 0.05 | 0.5 | 0.48 | 90 | 0.02 | 0 | 0.48 | -0.02 | -0.02 | 35/10
72 | N. Chigla | 2.5 | 0.53 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.37 | 0.37 |  |  |  | 72 | N. Chigla | 2.5 | 0.11 | 0.64 | 0.9 | 120 | -0.26 | 0 | 0.9 | 0.26 | 0.26 | 35/10
73 | Troitskoe-1 | 1.6 | 0.11 | 0.11 | 120 | 0.11 | 0 | 0.11 | 0 | 0 |  |  |  | 73 | Troitskoe-1 | 1.6 | 0 | 0.11 | 0.11 | 120 | 0 | 0 | 0.11 | 0 | 0 | 35/10
74 | Tishanka | 2.5 | 0.91 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.6 | 0.6 |  |  |  | 74 | Tishanka | 2.5 | 0.05 | 0.96 | 1.51 | 120 | -0.55 | 0 | 1.51 | 0.55 | 0.55 | 35/10
| KPS | [12 empty] | 2: KPS
75 | Kalacheevskaya | 6.3 | 0.5 | 1 | 1 day and night | 1 | 0 | 1 | 0.5 | 0.5 |  |  |  | 75 | Kalacheevskaya | 6.3 | 1.55 | 2.05 | 1 | 1 day and night | 1.05 | 0 | 1 | -1.05 | -1.05 | 110/10
76 | B.Kazinka | 6.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | -0.5 | -0.5 |  |  |  | 76 | B.Kazinka | 6.3 | 3.09 | 3.59 | 0 | 0 | 3.59 | 0 | 0 | -3.59 | -3.59
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110/35/10
| Sн. LV, МVА | 6.3 | 0.5 | 0 | 0 | 0 | 0 | 0 | -0.5 | [5 empty] | Sн. LV, МVА | 6.3 | 3.09 | 3.59 | 0 | 0 | 3.59 | 0 | 0 | -3.59
77 | Derezovka | 6.3 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  |  | 77 | Derezovka | 6.3 | 0.07 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | -0.36 | -0.36 | 110/10
78 | Osetrovka | 6.3 | 0.69 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.81 | 0.81 |  |  |  | 78 | Osetrovka | 6.3 | 2.22 | 2.91 | 1.5 | 1 day and night | 1.41 | 0 | 1.5 | -1.41 | -1.41 | 110/10
79 | sovkhoz Radchensky | 10 | 1.125 | 2 | 1 day and night | 2 | 0 | 2 | 0.875 | -0.99 |  |  |  | 79 | sovkhoz Radchensky | 10 | 0.03 | 1.155 | 2 | 1 day and night | -0.845 | 0 | 2 | 0.845 | -0.99
| Sн. MV, МVА | 10 | 0.99 | 0 | 1 day and night | 0 | 0 | 0 | -0.99 | [5 empty] | Sн. MV, МVА | 10 | 0 | 0.99 | 0 | 0 | 0.99 | 0 | 0 | -0.99 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.13 | 2 | 1 day and night | 2 | 0 | 2 | 1.87 | [5 empty] | Sн. LV, МVА | 10 | 0.03 | 0.16 | 2 | 1 day and night | -1.84 | 0 | 2 | 1.84
80 | Klepovka | 4 | 1.21 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.39 | 0.39 |  |  |  | 80 | Klepovka | 4 | 0.13 | 1.34 | 1.6 | 120 | -0.26 | 0 | 1.6 | 0.26 | 0.26 | 35/10
81 | Krasnopolye | 4 | 0.33 | 1 | 120 | 1 | 0 | 1 | 0.67 | 0.67 |  |  |  | 81 | Krasnopolye | 4 | 0.02 | 0.35 | 1 | 120 | -0.65 | 0 | 1 | 0.65 | 0.65 | 35/10
82 | Nikolskoe | 2.5 | 0.38 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.12 | 1.12 |  |  |  | 82 | Nikolskoe | 2.5 | 0 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
83 | N. Liman | 2.5 | 0.33 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.17 | 1.17 |  |  |  | 83 | N. Liman | 2.5 | 0.09 | 0.42 | 1.5 | 45 | -1.08 | 0 | 1.5 | 1.08 | 1.08 | 35/10
84 | Bereznyagi | 2.5 | 0.25 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.25 | 1.25 |  |  |  | 84 | Bereznyagi | 2.5 | 0.13 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
85 | Kr.Flot | 2.5 | 0.27 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.23 | 1.23 |  |  |  | 85 | Kr.Flot | 2.5 | 0.11 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
86 | R. Zhuravka | 2.5 | 0.69 | 0 | 0 | 0 | 0 | 0 | -0.69 | -0.69 |  |  |  | 86 | R. Zhuravka | 2.5 | 0.08 | 0.77 | 0 | 0 | 0.77 | 0 | 0 | -0.77 | -0.77 | 35/10
87 | Gorokhovka | 2.5 | 0.53 | 1.5 | 45 | 1.5 | 0 | 1.5 | 0.97 | 0.97 |  |  |  | 87 | Gorokhovka | 2.5 | 0.11 | 0.64 | 1.5 | 45 | -0.86 | 0 | 1.5 | 0.86 | 0.86 | 35/10
88 | Livenka | 2.5 | 0.42 | 0.5 | 1 day and night | 0.5 | 0 | 0.5 | 0.08 | 0.08 |  |  |  | 88 | Livenka | 2.5 | 0.05 | 0.47 | 0.5 | 1 day and night | -0.03 | 0 | 0.5 | 0.03 | 0.03 | 35/10
89 | R.Buylovka | 2.5 | 0.48 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.02 | 1.02 |  |  |  | 89 | R.Buylovka | 2.5 | 0.06 | 0.54 | 1.5 | 45 | -0.96 | 0 | 1.5 | 0.96 | 0.96 | 35/10
90 | Shurinovka | 2.5 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 |  |  |  | 90 | Shurinovka | 2.5 | 0.03 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | 35/10
91 | Tvyordokhlebovka | 4 | 0.24 | 0 | 0 | 0 | 0 | 0 | -0.24 | -0.24 |  |  |  | 91 | Tvyordokhlebovka | 4 | 0.05 | 0.29 | 0 | 0 | 0.29 | 0 | 0 | -0.29 | -0.29 | 35/10
92 | Krinitsa | 2.5 | 0.135 | 0 | 0 | 0 | 0 | 0 | -0.135 | -0.135 |  |  |  | 92 | Krinitsa | 2.5 | 0.05 | 0.185 | 0 | 0 | 0.185 | 0 | 0 | -0.185 | -0.185 | 35/10
93 | Krasnogorovka | 2.5 | 0.08 | 0 | 0 | 0 | 0 | 0 | -0.08 | -0.08 |  |  |  | 93 | Krasnogorovka | 2.5 | 0.01 | 0.09 | 0 | 0 | 0.09 | 0 | 0 | -0.09 | -0.09 | 35/10
| Two- and more transformer substations | [12 empty] | 2: Two- and more transformer substations
| SPS | [12 empty] | 2: SPS
94 | No. 2 | 25+25 | 21.4 | 2.94 | 120 | 18.46 | 0 | 26.25 | 7.79 | 7.79 |  | 1.05 | 25 | 94 | No. 2 | 25+25 | 4.87 | 26.27 | 2.94 | 120 | 23.33 | 0 | 26.25 | 2.92 | 2.92 | 110/6
95 | No.3 | 6,3 + 10 | 9.66 | 2.5 | 120 | 7.16 | 0 | 6.615 | -0.545 | -0.545 |  | 1.05 | 6.3 | 95 | No.3 | 6,3 + 10 | 0.13 | 9.79 | 2.5 | 120 | 7.29 | 0 | 6.615 | -0.675 | -0.675 | 35/6
96 | No. 4 | 10+10+15 | 13.69 | 0 | 0 | 13.69 | 0 | 21 | 7.31 | 7.31 |  | 1.05 | 20 | 96 | No. 4 | 10+10+15 | 0.09 | 13.78 | 0 | 0 | 13.78 | 0 | 21 | 7.22 | 7.22 | 35/6
97 | No. 6 | 25+32 | 15.6 | 1.6 | 120 | 14 | 0 | 26.25 | 12.25 | 12.25 |  | 1.05 | 25 | 97 | No. 6 | 25+32 | 4.21 | 19.81 | 1.6 | 120 | 18.21 | 0 | 26.25 | 8.04 | 8.04 | 110/6
98 | No. 7 | 2,5+4 | 1.12 | 2.5 | 0 | -1.38 | 0 | 2.625 | 4.005 | 4.005 |  | 1.05 | 2.5 | 98 | No. 7 | 2,5+4 | 2.22 | 3.34 | 2.5 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | 35/10/6
99 | No. 8 | 4+4+4 | 5.26 | 0 | 0 | 5.26 | 0 | 8.4 | 3.14 | 3.14 |  | 1.05 | 8 | 99 | No. 8 | 4+4+4 | 1.91 | 7.17 | 0 | 0 | 7.17 | 0 | 8.4 | 1.23 | 1.23 | 35/6
100 | No. 9 | 16+25 | 21.2 | 3.3 | 120 | 17.9 | 0 | 16.8 | -1.1 | -1.1 |  | 1.05 | 16 | 100 | No. 9 | 16+25 | 1.92 | 23.12 | 3.3 | 120 | 19.82 | 0 | 16.8 | -3.02 | -3.02 | 110/6
101 | No. 10 | 63+63 | 41.4 | 13.3 | 120 | 28.1 | 0 | 66.15 | 38.05 | 38.05 |  | 1.05 | 63 | 101 | No. 10 | 63+63 | 15.3 | 56.7 | 13.3 | 120 | 43.4 | 0 | 66.15 | 22.75 | 22.75 | 35/6
102 | No. 13 | 6,3+6,3 | 9.43 | 3.7 | 120 | 5.73 | 0 | 6.615 | 0.885 | 0.885 |  | 1.05 | 6.3 | 102 | No. 13 | 6,3+6,3 | 5.09 | 14.52 | 3.7 | 120 | 10.82 | 0 | 6.615 | -4.205 | -4.205 | 35/10
103 | No. 14 | 31,5+31,5 | 11.49 | 1.3 | 120 | 10.19 | 0 | 33.075 | 22.885 | 22.885 |  | 1.05 | 31.5 | 103 | No. 14 | 31,5+31,5 | 3.36 | 14.85 | 1.3 | 120 | 13.55 | 0 | 33.075 | 19.525 | 19.525
| Sн. MV, МVА | 31,5+31,5 | 0.92 | 0 | 0 | 0.92 | 0 | 33.075 | 32.155 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 0.92 | 0 | 0 | 0.92 | 0 | 33.075 | 32.155 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5 | 10.57 | 1.3 | 120 | 9.27 | 0 | 33.075 | 23.805 |  |  | 1.05 | 31.5 |  | Sн. LV, МVА | 31,5+31,5 | 3.36 | 13.93 | 1.3 | 120 | 12.63 | 0 | 33.075 | 20.445
104 | No. 15 | 40,5+40,5+63,0 | 33 | 44.01 | 120 | -11.01 | 0 | 85.05 | 96.06 | 85.05 |  | 1.05 | 81 | 104 | No. 15 | 40,5+40,5+63,0 | 0 | 33 | 44.01 | 120 | -11.01 | 0 | 85.05 | 96.06 | 85.05
| Sн. MV, МVА | 40,5+40,5+63,0 | 33 | 44.01 | 120 | -11.01 | 0 | 85.05 | 96.06 |  |  | 1.05 | 81 |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 33 | 44.01 | 120 | -11.01 | 0 | 85.05 | 96.06 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  | 1.05 | 81 |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05
105 | No. 16 | 31,5+31,5+40,0 | 53.03 | 4 | 120 | 49.03 | 0 | 66.15 | 17.12 | 17.12 |  | 1.05 | 63 | 105 | No. 16 | 31,5+31,5+40,0 | 17.07 | 70.1 | 4 | 120 | 66.1 | 0 | 66.15 | 0.05 | 0.05
| Sн. MV, МVА | 31,5+31,5 | 3.63 | 0 | 0 | 3.63 | 0 | 33.075 | 29.445 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 3.63 | 0 | 0 | 3.63 | 0 | 33.075 | 29.445 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5+40,0 | 49.4 | 4 | 120 | 45.4 | 0 | 66.15 | 20.75 |  |  | 1.05 | 63 |  | Sн. LV, МVА | 31,5+31,5+40,0 | 17.07 | 66.47 | 4 | 120 | 62.47 | 0 | 66.15 | 3.68
106 | No. 18 | 6,3+6,3 | 2.09 | 0 | 0 | 2.09 | 0 | 6.615 | 4.525 | 4.525 |  | 1.05 | 6.3 | 106 | No. 18 | 6,3+6,3 | 1.73 | 3.82 | 0 | 0 | 3.82 | 0 | 6.615 | 2.795 | 2.795 | 110/10
107 | No. 20 | 25+25 | 23.72 | 5.6 | 120 | 18.12 | 0 | 26.25 | 8.13 | 8.13 |  | 1.05 | 25 | 107 | No. 20 | 25+25 | 10.49 | 34.21 | 5.6 | 120 | 28.61 | 0 | 26.25 | -2.36 | -2.36
| Sн. MV, МVА | 25+25 | 6.74 | 0 | 0 | 6.74 | 0 | 26.25 | 19.51 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 6.74 | 0 | 0 | 6.74 | 0 | 26.25 | 19.51 |  | 110/10/6
| Sн. LV, МVА | 25+25 | 16.98 | 5.6 | 120 | 11.38 | 0 | 26.25 | 14.87 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 10.49 | 27.47 | 5.6 | 120 | 21.87 | 0 | 26.25 | 4.38
108 | No. 21 | 25,0+20,0+40,0 | 34.98 | 4.6 | 120 | 30.38 | 0 | 47.25 | 16.87 | 16.87 |  | 1.05 | 45 | 108 | No. 21 | 25,0+20,0+40,0 | 6.49 | 41.47 | 4.6 | 180 | 36.87 | 0 | 49.6125 | 12.7425 | 12.7425 | 110/35/6
109 | No. 22 | 10+10 | 4.2 | 1.4 | 120 | 2.8 | 0 | 10.5 | 7.7 | 7.7 |  | 1.05 | 10 | 109 | No. 22 | 10+10 | 2.58 | 6.78 | 1.4 | 120 | 5.38 | 0 | 10.5 | 5.12 | 5.12 | 35/6
110 | No. 23 | 7,5+6,3 | 6.1 | 0.8 | 120 | 5.3 | 0 | 6.615 | 1.315 | 1.315 |  | 1.05 | 6.3 | 110 | No. 23 | 7,5+6,3 | 0 | 6.1 | 0.8 | 120 | 5.3 | 0 | 6.615 | 1.315 | 1.315 | 35/6
111 | No. 24 | 3,2+4,0 | 1.82 | 0 | 0 | 1.82 | 0 | 3.36 | 1.54 | 1.54 |  | 1.05 | 3.2 | 111 | No. 24 | 3,2+4,0 | 0.04 | 1.86 | 0 | 0 | 1.86 | 0 | 3.36 | 1.5 | 1.5 | 35/6
112 | No. 25 | 40+40+40 | 40.5 | 3.8 | 120 | 36.7 | 0 | 84 | 47.3 | 47.3 |  | 1.05 | 80 | 112 | No. 25 | 40+40+40 | 5.28 | 45.78 | 3.8 | 120 | 41.98 | 0 | 84 | 42.02 | 42.02 | 110/6
113 | No. 27 | 32,0+32,0+63,0 | 42.5 | 3.3 | 180 | 39.2 | 0 | 67.2 | 28 | 28 |  | 1.05 | 64 | 113 | No. 27 | 32,0+32,0+63,0 | 24.07 | 66.57 | 3.3 | 180 | 63.27 | 0 | 67.2 | 3.93 | 3.93 | 110/6
114 | No. 28 | 10+10 | 15.2 | 0 | 0 | 15.2 | 0 | 10.5 | -4.7 | -4.7 |  | 1.05 | 10 | 114 | No. 28 | 10+10 | 1.58 | 16.78 | 0 | 0 | 16.78 | 0 | 10.5 | -6.28 | -6.28 | 110/10
115 | No.29 | 25+25 | 26.2 | 8.4 | 120 | 17.8 | 0 | 26.25 | 8.45 | 8.45 |  | 1.05 | 25 | 115 | No.29 | 25+25 | 5.91 | 32.11 | 8.4 | 120 | 23.71 | 0 | 26.25 | 2.54 | 2.54
| Sн. MV, МVА | 25+25 | 9.5 | 4.2 | 120 | 5.3 | 0 | 26.25 | 20.95 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 9.5 | 4.2 | 120 | 5.3 | 0 | 26.25 | 20.95 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 16.7 | 4.2 | 120 | 12.5 | 0 | 26.25 | 13.75 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 5.91 | 22.61 | 4.2 | 120 | 18.41 | 0 | 26.25 | 7.84
116 | No. 30 | 40+40+63 | 63.8 | 5.1 | 120 | 58.7 | 0 | 108.15 | 49.45 | 31.2 |  | 1.05 | 103 | 116 | No. 30 | 40+40+63 | 15.79 | 79.59 | 5.1 | 120 | 74.49 | 0 | 108.15 | 33.66 | 31.2
| Sн. MV, МVА | 40+40 | 10.8 | 0 | 0 | 10.8 | 0 | 42 | 31.2 |  |  | 1.05 | 40 |  | Sн. MV, МVА | 40+40 | 0 | 10.8 | 0 | 0 | 10.8 | 0 | 42 | 31.2 |  | 110/35/10
| Sн. LV, МVА | 40+40+63 | 53 | 5.1 | 120 | 47.9 | 0 | 108.15 | 60.25 |  |  | 1.05 | 103 |  | Sн. LV, МVА | 40+40+63 | 15.79 | 68.79 | 5.1 | 120 | 63.69 | 0 | 108.15 | 44.46
117 | No. 32 | 10+16 | 8.66 | 8 | 120 | 0.66 | 0 | 10.5 | 9.84 | 7 |  | 1.05 | 10 | 117 | No. 32 | 10+16 | 20.4 | 29.06 | 8 | 120 | 21.06 | 0 | 10.5 | -10.56 | -13.4
| Sн. MV, МVА | 10+16 | 5.16 | 8 | 120 | -2.84 | 0 | 10.5 | 13.34 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 5.16 | 8 | 120 | -2.84 | 0 | 10.5 | 13.34 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 3.5 | 0 | 0 | 3.5 | 0 | 10.5 | 7 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 20.4 | 23.9 | 0 | 0 | 23.9 | 0 | 10.5 | -13.4
118 | No. 33 | 4,0+4,0 | 1.8 | 0 | 0 | 1.8 | 0 | 4.2 | 2.4 | 2.4 |  | 1.05 | 4 | 118 | No. 33 | 4,0+4,0 | 1.98 | 3.78 | 0 | 0 | 3.78 | 0 | 4.2 | 0.42 | 0.42 | 35/10
119 | No. 34 | 2,5+1,8 | 1.54 | 0 | 0 | 1.54 | 0 | 1.89 | 0.35 | 0.35 |  | 1.05 | 1.8 | 119 | No. 34 | 2,5+1,8 | 0.35 | 1.89 | 0 | 0 | 1.89 | 0 | 1.89 | 0 | 0 | 35/6
120 | No.35 | 10+10 | 11.5 | 2.4 | 120 | 9.1 | 0 | 10.5 | 1.4 | 1.4 |  | 1.05 | 10 | 120 | No.35 | 10+10 | 1.4 | 12.9 | 2.4 | 120 | 10.5 | 0 | 10.5 | 0 | 0 | 35/6
121 | No. 36 | 6,3+10 | 1.3 | 0 | 0 | 1.3 | 0 | 6.615 | 5.315 | 5.315 |  | 1.05 | 6.3 | 121 | No. 36 | 6,3+10 | 6.6 | 7.9 | 0 | 0 | 7.9 | 0 | 6.615 | -1.285 | -1.285 | 110/35/10
122 | No. 39 | 25+25 | 25.8 | 7.08 | 120 | 18.72 | 0 | 26.25 | 7.53 | 7.53 |  | 1.05 | 25 | 122 | No. 39 | 25+25 | 5.07 | 30.87 | 7.08 | 120 | 23.79 | 0 | 26.25 | 2.46 | 2.46 | 110/6
123 | No. 41 | 10+10 | 10.3 | 0 | 0 | 10.3 | 0 | 10.5 | 0.2 | 0.2 |  | 1.05 | 10 | 123 | No. 41 | 10+10 | 0.18 | 10.48 | 0 | 0 | 10.48 | 0 | 10.5 | 0.02 | 0.02 | 35/6
124 | No. 42 | 25+40 | 19.7 | 1.6 | 120 | 18.1 | 0 | 26.25 | 8.15 | 8.15 |  | 1.05 | 25 | 124 | No. 42 | 25+40 | 7.65 | 27.35 | 1.6 | 120 | 25.75 | 0 | 26.25 | 0.5 | 0.5 | 110/6
125 | No. 43 | 63+25 | 15.7 | 1.6 | 60 | 14.1 | 0 | 26.25 | 12.15 | 12.15 |  | 1.05 | 25 | 125 | No. 43 | 63+25 | 5.46 | 21.16 | 1.6 | 60 | 19.56 | 0 | 26.25 | 6.69 | 6.69 | 110/6
126 | No. 45 | 63+63 | 33.52 | 7.1 | 120 | 26.42 | 0 | 66.15 | 39.73 | 39.73 |  | 1.05 | 63 | 126 | No. 45 | 63+63 | 22.44 | 55.96 | 7.1 | 120 | 48.86 | 0 | 66.15 | 17.29 | 17.29 | 110/6
127 | No. 47 | 25+25 | 11.9 | 0 | 0 | 11.9 | 0 | 26.25 | 14.35 | 14.35 |  | 1.05 | 25 | 127 | No. 47 | 25+25 | 1.92 | 13.82 | 0 | 0 | 13.82 | 0 | 26.25 | 12.43 | 12.43
| Sн. MV, МVА | 25+25 | 5.3 | 0 | 0 | 5.3 | 0 | 26.25 | 20.95 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 5.3 | 0 | 0 | 5.3 | 0 | 26.25 | 20.95 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.6 | 0 | 0 | 6.6 | 0 | 26.25 | 19.65 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 1.92 | 8.52 | 0 | 0 | 8.52 | 0 | 26.25 | 17.73
128 | Panino | 16+16 | 9.84 | 5.2 | 120 | 4.64 | 0 | 16.8 | 12.16 | 11.86 |  | 1.05 | 16 | 128 | Panino | 16+16 | 2.38 | 12.22 | 5.2 | 120 | 7.02 | 0 | 16.8 | 9.78 | 9.48
| Sн. MV, МVА | 16+16 | 4.7 | 5 | 120 | -0.3 | 0 | 16.8 | 17.1 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 4.7 | 5 | 120 | -0.3 | 0 | 16.8 | 17.1 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.14 | 0.2 | 120 | 4.94 | 0 | 16.8 | 11.86 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.38 | 7.52 | 0.2 | 120 | 7.32 | 0 | 16.8 | 9.48
129 | Kriusha | 2,5+2,5 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 |  | 1.05 | 2.5 | 129 | Kriusha | 2,5+2,5 | 0.13 | 1.01 | 0 | 0 | 1.01 | 0 | 2.625 | 1.615 | 1.615 | 35/10
130 | Seed plant | 4+4 | 1.53 | 0 | 0 | 1.53 | 0 | 4.2 | 2.67 | 2.67 |  | 1.05 | 4 | 130 | Seed plant | 4+4 | 0.07 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | 35/10
131 | Progress | 2,5+10 | 0.36 | 0.5315 | 120 | -0.1715 | 0 | 2.625 | 2.7965 | 2.7965 |  | 1.05 | 2.5 | 131 | Progress | 2,5+10 | 0.01 | 0.37 | 0.5315 | 120 | -0.1615 | 0 | 2.625 | 2.7865 | 2.7865 | 110/35/10
132 | Katukhovka | 2,5+2,5 | 0.59 | 0.385 | 120 | 0.205 | 0 | 2.625 | 2.42 | 2.42 |  | 1.05 | 2.5 | 132 | Katukhovka | 2,5+2,5 | 0.02 | 0.61 | 0.385 | 120 | 0.225 | 0 | 2.625 | 2.4 | 2.4 | 35/10
133 | Kr.Liman | 2,5+4,0 | 0.74 | 0 | 0 | 0.74 | 0 | 2.625 | 1.885 | 1.885 |  | 1.05 | 2.5 | 133 | Kr.Liman | 2,5+4,0 | 0.02 | 0.76 | 0 | 0 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | 35/10
134 | Ivanovka | 1,8+1,6 | 0.23 | 0.36 | 120 | -0.13 | 0 | 1.68 | 1.81 | 1.81 |  | 1.05 | 1.6 | 134 | Ivanovka | 1,8+1,6 | 0.09 | 0.32 | 0.36 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | 35/10
135 | Don | 2,5+2,5 | 2.47 | 0 | 0 | 2.47 | 0 | 2.625 | 0.155 | 0.155 |  | 1.05 | 2.5 | 135 | Don | 2,5+2,5 | 1.59 | 4.06 | 0 | 0 | 4.06 | 0 | 2.625 | -1.435 | -1.435 | 35/10
136 | Yablochnoe | 4+4 | 0.35 | 0 | 0 | 0.35 | 0 | 4.2 | 3.85 | 3.85 |  | 1.05 | 4 | 136 | Yablochnoe | 4+4 | 0.09 | 0.44 | 0 | 0 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | 35/10
137 | St.Nikolskoe | 2,5+2,5 | 0.8 | 1.227 | 120 | -0.427 | 0 | 2.625 | 3.052 | 3.052 |  | 1.05 | 2.5 | 137 | St.Nikolskoe | 2,5+2,5 | 0.36 | 1.16 | 1.227 | 120 | -0.067 | 0 | 2.625 | 2.692 | 2.692 | 35/10
138 | Rudkino | 4,0+4,0 | 1.63 | 0 | 0 | 1.63 | 0 | 4.2 | 2.57 | 2.57 |  | 1.05 | 4 | 138 | Rudkino | 4,0+4,0 | 0.37 | 2 | 0 | 0 | 2 | 0 | 4.2 | 2.2 | 2.2 | 35/10
139 | Khokhol-1 | 6,3+6,3 | 4.9 | 0 | 0 | 4.9 | 0 | 6.615 | 1.715 | 1.715 |  | 1.05 | 6.3 | 139 | Khokhol-1 | 6,3+6,3 | 0.86 | 5.76 | 0 | 0 | 5.76 | 0 | 6.615 | 0.855 | 0.855 | 35/6
140 | No. 11 | 5,6+6,3 | 3.27 | 0.5 | 120 | 2.77 | 0 | 5.88 | 3.11 | 3.11 |  | 1.05 | 5.6 | 140 | No. 11 | 5,6+6,3 | 0 | 3.27 | 0.5 | 120 | 2.77 | 0 | 5.88 | 3.11 | 3.11
| Sн. MV, МVА | 5,6+6,3 | 0.51 | 0.5 | 120 | 0.01 | 0 | 5.88 | 5.87 |  |  | 1.05 | 5.6 |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.51 | 0.5 | 120 | 0.01 | 0 | 5.88 | 5.87 |  | 110/35/6
| Sн. LV, МVА | 5,6+6,3 | 2.76 | 0 | 0 | 2.76 | 0 | 5.88 | 3.12 |  |  | 1.05 | 5.6 |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.76 | 0 | 0 | 2.76 | 0 | 5.88 | 3.12
141 | Beryozovka | 4+4 | 3.07 | 0 | 0 | 3.07 | 0 | 4.2 | 1.13 | 1.13 |  | 1.05 | 4 | 141 | Beryozovka | 4+4 | 1.12 | 4.19 | 0 | 0 | 4.19 | 0 | 4.2 | 0.01 | 0.01 | 35/10
142 | N.Zhivotinnoe | 6,3+6,3 | 4.4 | 1 | 120 | 3.4 | 0 | 6.615 | 3.215 | 3.215 |  | 1.05 | 6.3 | 142 | N.Zhivotinnoe | 6,3+6,3 | 5.77 | 10.17 | 1 | 120 | 9.17 | 0 | 6.615 | -2.555 | -2.555 | 35/10
143 | Ramon-1 | 4+4+4 | 5.71 | 6.85 | 120 | -1.14 | 0 | 8.4 | 9.54 | 9.54 |  | 1.05 | 8 | 143 | Ramon-1 | 4+4+4 | 0.79 | 6.5 | 6.85 | 120 | -0.35 | 0 | 8.4 | 8.75 | 8.75 | 35/10/6
144 | Ramon-2 | 16,0+16,0 | 19.1 | 10.48 | 120 | 8.62 | 0 | 16.8 | 8.18 | 8.18 |  | 1.05 | 16 | 144 | Ramon-2 | 16,0+16,0 | 0.74 | 19.84 | 10.48 | 120 | 9.36 | 0 | 16.8 | 7.44 | 7.44
| Sн. MV, МVА | 16,0+16,0 | 14.3 | 6.85 | 0 | 7.45 | 0 | 16.8 | 9.35 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 14.3 | 6.85 | 0 | 7.45 | 0 | 16.8 | 9.35 |  | 110/35/10
| Sн. LV, МVА | 16,0+16,0 | 4.8 | 3.63 | 120 | 1.17 | 0 | 16.8 | 15.63 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.74 | 5.54 | 3.63 | 120 | 1.91 | 0 | 16.8 | 14.89
145 | Vereyka | 2,5+2,5 | 1.04 | 0 | 0 | 1.04 | 0 | 2.625 | 1.585 | 1.585 |  | 1.05 | 2.5 | 145 | Vereyka | 2,5+2,5 | 0.01 | 1.05 | 0 | 0 | 1.05 | 0 | 2.625 | 1.575 | 1.575 | 35/10
146 | Complex | 10+10 | 4.34 | 3.4 | 180 | 0.94 | 0 | 10.5 | 9.56 | 8.9 |  | 1.05 | 10 | 146 | Complex | 10+10 | 0 | 4.34 | 3.4 | 180 | 0.94 | 0 | 10.5 | 9.56 | 8.9
| Sн. MV, МVА | 10+10 | 2.43 | 3.1 | 180 | -0.67 | 0 | 10.5 | 11.17 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.43 | 3.1 | 180 | -0.67 | 0 | 10.5 | 11.17 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.9 | 0.3 | 180 | 1.6 | 0 | 10.5 | 8.9 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0 | 1.9 | 0.3 | 180 | 1.6 | 0 | 10.5 | 8.9
147 | N.Veduga | 16+16 | 3.29 | 2.9 | 120 | 0.39 | 0 | 16.8 | 16.41 | 15.6 |  | 1.05 | 16 | 147 | N.Veduga | 16+16 | 0 | 3.29 | 2.9 | 120 | 0.39 | 0 | 16.8 | 16.41 | 15.6
| Sн. MV, МVА | 16+16 | 2.07 | 2.9 | 120 | -0.83 | 0 | 16.8 | 17.63 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 2.07 | 2.9 | 120 | -0.83 | 0 | 16.8 | 17.63 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.2 | 0 | 0 | 1.2 | 0 | 16.8 | 15.6 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0 | 1.2 | 0 | 0 | 1.2 | 0 | 16.8 | 15.6
148 | Golosnovka | 2,5+2,5 | 0.45 | 0.512 | 120 | -0.062 | 0 | 2.625 | 2.687 | 2.687 |  | 1.05 | 2.5 | 148 | Golosnovka | 2,5+2,5 | 0.02 | 0.47 | 0.512 | 120 | -0.042 | 0 | 2.625 | 2.667 | 2.667 | 35/10
149 | Medvezhye | 3,2+4,0 | 0.83 | 0 | 0 | 0.83 | 0 | 3.36 | 2.53 | 2.53 |  | 1.05 | 3.2 | 149 | Medvezhye | 3,2+4,0 | 0.11 | 0.94 | 0 | 0 | 0.94 | 0 | 3.36 | 2.42 | 2.42 | 35/10
150 | St.Veduga | 4+4 | 0.84 | 0 | 0 | 0.84 | 0 | 4.2 | 3.36 | 3.36 |  | 1.05 | 4 | 150 | St.Veduga | 4+4 | 0.03 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | 35/10
151 | M.Pokrovka | 2,5+2,5 | 0.54 | 0 | 0 | 0.54 | 0 | 2.625 | 2.085 | 2.085 |  | 1.05 | 2.5 | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | 35/10
152 | V.Turovo-2 | 2,5+2,5 | 1.04 | 0.7 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 |  | 1.05 | 2.5 | 152 | V.Turovo-2 | 2,5+2,5 | 0.28 | 1.32 | 0.7 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | 35/10
153 | S.Lipyagi | 3,2+2,5 | 1.49 | 2.9638 | 120 | -1.4738 | 0 | 2.625 | 4.0988 | 4.0988 |  | 1.05 | 2.5 | 153 | S.Lipyagi | 3,2+2,5 | 1.92 | 3.41 | 2.9638 | 120 | 0.4462 | 0 | 2.625 | 2.1788 | 2.1788 | 35/10
154 | N.Devitsk | 25+16 | 5.67 | 8.2225 | 180 | -2.5525 | 0 | 16.8 | 19.3525 | 16.68 |  | 1.05 | 16 | 154 | N.Devitsk | 25+16 | 1.1 | 6.77 | 8.2225 | 180 | -1.4525 | 0 | 16.8 | 18.2525 | 16.68
| Sн. MV, МVА | 25+16 | 2.92 | 2.8 | 180 | 0.12 | 0 | 16.8 | 16.68 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 25+16 | 0 | 2.92 | 2.8 | 180 | 0.12 | 0 | 16.8 | 16.68 |  | 110/35/10
| Sн. LV, МVА | 25+16 | 2.75 | 5.393 | 180 | -2.643 | 0 | 16.8 | 19.443 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 25+16 | 1.1 | 3.85 | 5.393 | 180 | -1.543 | 0 | 16.8 | 18.343
155 | Repyevka | 4+4 | 2.5 | 0.5 | 120 | 2 | 0 | 4.2 | 2.2 | 2.2 |  | 1.05 | 4 | 155 | Repyevka | 4+4 | 0.12 | 2.62 | 0.5 | 120 | 2.12 | 0 | 4.2 | 2.08 | 2.08 | 35/10
156 | Krasnolipye | 16+16 | 9.83 | 2.9 | 120 | 6.93 | 0 | 16.8 | 9.87 | 9.87 |  | 1.05 | 16 | 156 | Krasnolipye | 16+16 | 0.25 | 10.08 | 2.9 | 120 | 7.18 | 0 | 16.8 | 9.62 | 9.62
| Sн. MV, МVА | 16+16 | 8.7 | 2.7 | 120 | 6 | 0 | 16.8 | 10.8 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 8.7 | 2.7 | 120 | 6 | 0 | 16.8 | 10.8 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.13 | 0.2 | 120 | 0.93 | 0 | 16.8 | 15.87 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.25 | 1.38 | 0.2 | 120 | 1.18 | 0 | 16.8 | 15.62
157 | Ulyanovka | 6,3+6,3 | 0.41 | 0.04 | 60 | 0.37 | 0 | 6.615 | 6.245 | 6.245 |  | 1.05 | 6.3 | 157 | Ulyanovka | 6,3+6,3 | 0.11 | 0.52 | 0.04 | 60 | 0.48 | 0 | 6.615 | 6.135 | 6.135 | 110/10
158 | МОB | 4+2,5 | 1.32 | 0.6 | 60 | 0.72 | 0 | 2.625 | 1.905 | 1.905 |  | 1.05 | 2.5 | 158 | МОB | 4+2,5 | 0.21 | 1.53 | 0.6 | 60 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | 35/10
159 | L.Rossosh | 6,3+4 | 4.73 | 0 | 0 | 4.73 | 0 | 4.2 | -0.53 | -0.53 |  | 1.05 | 4 | 159 | L.Rossosh | 6,3+4 | 1.34 | 6.07 | 0 | 0 | 6.07 | 0 | 4.2 | -1.87 | -1.87 | 35/10
160 | Kashirskoe | 2,5+2,5 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 |  | 1.05 | 2.5 | 160 | Kashirskoe | 2,5+2,5 | 0.05 | 0.74 | 0 | 0 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | 35/10
161 | Zaprudskoe | 2,5+2,5 | 1.6 | 0 | 0 | 1.6 | 0 | 2.625 | 1.025 | 1.025 |  | 1.05 | 2.5 | 161 | Zaprudskoe | 2,5+2,5 | 0.31 | 1.91 | 0 | 0 | 1.91 | 0 | 2.625 | 0.715 | 0.715 | 35/10
162 | Moskovskoe | 10+10 | 9.77 | 1.8 | 120 | 7.97 | 0 | 10.5 | 2.53 | 1.61 |  | 1.05 | 10 | 162 | Moskovskoe | 10+10 | 0.19 | 9.96 | 1.8 | 120 | 8.16 | 0 | 10.5 | 2.34 | 1.61
| Sн. MV, МVА | 10+10 | 8.89 | 0 | 0 | 8.89 | 0 | 10.5 | 1.61 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 8.89 | 0 | 0 | 8.89 | 0 | 10.5 | 1.61 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.88 | 1.8 | 120 | -0.92 | 0 | 10.5 | 11.42 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.19 | 1.07 | 1.8 | 120 | -0.73 | 0 | 10.5 | 11.23
163 | SemenovkaSPS | 2,5+4,0 | 2.1 | 0 | 0 | 2.1 | 0 | 2.625 | 0.525 | 0.525 |  | 1.05 | 2.5 | 163 | SemenovkaSPS | 2,5+4,0 | 0.01 | 2.11 | 0 | 0 | 2.11 | 0 | 2.625 | 0.515 | 0.515 | 35/10
164 | N. Baygora | 2,5+2,5 | 1.69 | 1.03 | 60 | 0.66 | 0 | 2.625 | 1.965 | 1.965 |  | 1.05 | 2.5 | 164 | N. Baygora | 2,5+2,5 | 0.02 | 1.71 | 1.03 | 60 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | 35/10
165 | Shukavka | 2,5+2,5 | 0.7 | 0.1 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 |  | 1.05 | 2.5 | 165 | Shukavka | 2,5+2,5 | 0.03 | 0.73 | 0.1 | 120 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | 35/10
166 | Uglyanets | 4+2,5 | 2.3 | 0.8 | 120 | 1.5 | 0 | 2.625 | 1.125 | 1.125 |  | 1.05 | 2.5 | 166 | Uglyanets | 4+2,5 | 3.68 | 5.98 | 0.8 | 120 | 5.18 | 0 | 2.625 | -2.555 | -2.555 | 35/10
167 | V.Khava | 16+16 | 13.6 | 0.4 | 120 | 13.2 | 0 | 16.8 | 3.6 | 3.6 |  | 1.05 | 16 | 167 | V.Khava | 16+16 | 2.98 | 16.58 | 0.4 | 120 | 16.18 | 0 | 16.8 | 0.62 | 0.62
| Sн. MV, МVА | 16+16 | 5.56 | 0 | 0 | 5.56 | 0 | 16.8 | 11.24 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 5.56 | 0 | 0 | 5.56 | 0 | 16.8 | 11.24 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 8.04 | 0.4 | 120 | 7.64 | 0 | 16.8 | 9.16 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.98 | 11.02 | 0.4 | 120 | 10.62 | 0 | 16.8 | 6.18
168 | Usman-1 | 10+6,3 | 10.4 | 0 | 0 | 10.4 | 0 | 6.615 | -3.785 | -3.785 |  | 1.05 | 6.3 | 168 | Usman-1 | 10+6,3 | 2.7 | 13.1 | 0 | 0 | 13.1 | 0 | 6.615 | -6.485 | -6.485 | 35/10
169 | Usman-2 | 10+6,3 | 8.9 | 0 | 0 | 8.9 | 0 | 6.615 | -2.285 | -2.285 |  | 1.05 | 6.3 | 169 | Usman-2 | 10+6,3 | 4.29 | 13.19 | 0 | 0 | 13.19 | 0 | 6.615 | -6.575 | -6.575 | 35/10
170 | R.Khava | 4+4 | 2.75 | 0.2 | 120 | 2.55 | 0 | 4.2 | 1.65 | 1.65 |  | 1.05 | 4 | 170 | R.Khava | 4+4 | 0.08 | 2.83 | 0.2 | 120 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | 35/10
171 | No. 31 | 16+25 | 23.16 | 5.6 | 120 | 17.56 | 0 | 16.8 | -0.76 | -0.76 |  | 1.05 | 16 | 171 | No. 31 | 16+25 | 1.17 | 24.33 | 5.6 | 120 | 18.73 | 0 | 16.8 | -1.93 | -1.93
| Sн. MV, МVА | 16+25 | 15.5 | 5.6 | 120 | 9.9 | 0 | 16.8 | 6.9 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+25 | 0 | 15.5 | 5.6 | 120 | 9.9 | 0 | 16.8 | 6.9 |  | 110/35/10
| Sн. LV, МVА | 16+25 | 7.66 | 0 | 0 | 7.66 | 0 | 16.8 | 9.14 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+25 | 1.17 | 8.83 | 0 | 0 | 8.83 | 0 | 16.8 | 7.97
172 | Maslovka | 2,5+4,0 | 3.6 | 0 | 0 | 3.6 | 0 | 2.625 | -0.975 | -0.975 |  | 1.05 | 2.5 | 172 | Maslovka | 2,5+4,0 | 1.59 | 5.19 | 0 | 0 | 5.19 | 0 | 2.625 | -2.565 | -2.565 | 35/10
| LPS | [12 empty] | 2: LPS
173 | Podgornaya - district Line Maintenance Service | 16+16 | 4.152 | 1.6 | 180 | 2.552 | 0 | 16.8 | 14.248 | 13.198 |  | 1.05 | 16 | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 2.69 | 6.842 | 1.6 | 180 | 5.242 | 0 | 16.8 | 11.558 | 10.508
| Sн. MV, МVА | 16+16 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0 | 1.05 | 180 | -1.05 | 0 | 16.8 | 17.85 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 4.152 | 0.55 | 180 | 3.602 | 0 | 16.8 | 13.198 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.69 | 6.842 | 0.55 | 180 | 6.292 | 0 | 16.8 | 10.508
174 | Kantemirovka | 10+10 | 9.14 | 1.6 | 60 | 7.54 | 0 | 10.5 | 2.96 | 2.96 |  | 1.05 | 10 | 174 | Kantemirovka | 10+10 | 0.52 | 9.66 | 1.6 | 60 | 8.06 | 0 | 10.5 | 2.44 | 2.44
| Sн. СН, МВА | 10+10 | 5.78 | 1.4 | 60 | 4.38 | 0 | 10.5 | 6.12 |  |  | 1.05 | 10 |  | Sн. СН, МВА | 10+10 | 0 | 5.78 | 1.4 | 60 | 4.38 | 0 | 10.5 | 6.12 |  | 110/35/10
| Sн. НН, МВА | 10+10 | 3.36 | 0.2 | 60 | 3.16 | 0 | 10.5 | 7.34 |  |  | 1.05 | 10 |  | Sн. НН, МВА | 10+10 | 0.52 | 3.88 | 0.2 | 60 | 3.68 | 0 | 10.5 | 6.82
175 | Rossosh | 16+16+40 | 21.9 | 2.68 | 120 | 19.22 | 0 | 33.6 | 14.38 | 14.38 |  | 1.05 | 32 | 175 | Rossosh | 16+16+40 | 1.56 | 23.46 | 2.68 | 120 | 20.78 | 0 | 33.6 | 12.82 | 12.82
| Sн. MV, МVА | 16+16+40 | 3.4 | 1.9 | 120 | 1.5 | 0 | 33.6 | 32.1 |  |  | 1.05 | 32 |  | Sн. MV, МVА | 16+16+40 | 0 | 3.4 | 1.9 | 120 | 1.5 | 0 | 33.6 | 32.1 |  | 110/35/10/6
| Sн. LV, МVА | 16+16+40 | 18.5 | 0.78 | 120 | 17.72 | 0 | 33.6 | 15.88 |  |  | 1.05 | 32 |  | Sн. LV, МVА | 16+16+40 | 1.56 | 20.06 | 0.78 | 120 | 19.28 | 0 | 33.6 | 14.32
176 | Kamenka r-naya LPS | 16+16 | 3.96 | 0.97 | 120 | 2.99 | 0 | 16.8 | 13.81 | 13.81 |  | 1.05 | 16 | 176 | Kamenka r-naya LPS | 16+16 | 1.08 | 5.04 | 0.97 | 120 | 4.07 | 0 | 16.8 | 12.73 | 12.73
| Sн. MV, МVА | 16+16 | 0.74 | 0 | 120 | 0.74 | 0 | 16.8 | 16.06 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0.03 | 0.77 | 0 | 120 | 0.77 | 0 | 16.8 | 16.03 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 3.22 | 0.97 | 120 | 2.25 | 0 | 16.8 | 14.55 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 1.05 | 4.27 | 0.97 | 120 | 3.3 | 0 | 16.8 | 13.5
177 | Korotoyak | 6,3+10 | 4.8 | 0.47 | 180 | 4.33 | 0 | 6.615 | 2.285 | 2.285 |  | 1.05 | 6.3 | 177 | Korotoyak | 6,3+10 | 0.72 | 5.52 | 0.47 | 180 | 5.05 | 0 | 6.615 | 1.565 | 1.565
| Sн. MV, МVА | 6,3+10 | 1.28 | 0 | 180 | 1.28 | 0 | 6.615 | 5.335 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+10 | 0 | 1.28 | 0 | 180 | 1.28 | 0 | 6.615 | 5.335 |  | 110/35/10
| Sн. LV, МVА | 6,3+10 | 3.55 | 0.47 | 180 | 3.08 | 0 | 6.615 | 3.535 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+10 | 0.72 | 4.27 | 0.47 | 180 | 3.8 | 0 | 6.615 | 2.815
178 | Ostrogozhsk | 40,5+40,5 | 17.3 | 2.4 | 60 | 14.9 | 0 | 42.525 | 27.625 | 27.625 |  | 1.05 | 40.5 | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 17.3 | 2.4 | 60 | 14.9 | 0 | 42.525 | 27.625 | 27.625
| Sн. MV, МVА | 40,5+40,5 | 15 | 2.4 | 60 | 12.6 | 0 | 42.525 | 29.925 |  |  | 1.05 | 40.5 |  | Sн. MV, МVА | 40,5+40,5 | 0 | 15 | 2.4 | 60 | 12.6 | 0 | 42.525 | 29.925 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225 |  |  | 1.05 | 40.5 |  | Sн. LV, МVА | 40,5+40,5 | 0 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225
179 | Khrenovoe | 16+6,3 | 4.21 | 0 | 0 | 4.21 | 0 | 6.615 | 2.405 | 2.405 |  | 1.05 | 6.3 | 179 | Khrenovoe | 16+6,3 | 1.07 | 5.28 | 0 | 0 | 5.28 | 0 | 6.615 | 1.335 | 1.335
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 16+6,3 | 0.34 | 0.34 | 0 | 0 | 0.34 | 0 | 6.615 | 6.275 |  | 110/35/10
| Sн. LV, МVА | 16+6,3 | 4.21 | 0 | 0 | 4.21 | 0 | 6.615 | 2.405 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 16+6,3 | 0.73 | 4.94 | 0 | 0 | 4.94 | 0 | 6.615 | 1.675
180 | Oil extraction plant | 25+25 | 18.9 | 7.9 | 120 | 11 | 0 | 26.25 | 15.25 | 15.22 |  | 1.05 | 25 | 180 | Oil extraction plant | 25+25 | 0.3 | 19.2 | 7.9 | 120 | 11.3 | 0 | 26.25 | 14.95 | 14.92
| Sн. MV, МVА | 25+25 | 7.93 | 7.9 | 120 | 0.03 | 0 | 26.25 | 26.22 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 7.93 | 7.9 | 120 | 0.03 | 0 | 26.25 | 26.22 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 11.03 | 0 | 0 | 11.03 | 0 | 26.25 | 15.22 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.3 | 11.33 | 0 | 0 | 11.33 | 0 | 26.25 | 14.92
181 | ANP | 6,3+6,3 | 3.23 | 0.39 | 120 | 2.84 | 0 | 6.615 | 3.775 | 3.775 |  | 1.05 | 6.3 | 181 | ANP | 6,3+6,3 | 4.7 | 4.39 | 0.39 | 120 | 4 | 0 | 6.615 | 2.615 | 2.615 | 110/6
182 | St. Kalitva | 6,3+6,3 | 1.05 | 0.86 | 240 | 0.19 | 0 | 6.615 | 6.425 | 6.425 |  | 1.05 | 6.3 | 182 | St. Kalitva | 6,3+6,3 | 0.2 | 1.25 | 0.86 | 240 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | 110/10
183 | Nikanorovka | 2,5+6,3 | 0.58 | 0.5 | 240 | 0.08 | 0 | 2.625 | 2.545 | 2.545 |  | 1.05 | 2.5 | 183 | Nikanorovka | 2,5+6,3 | 0.59 | 1.17 | 0.5 | 240 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | 110/10
184 | Poultry plant | 10+10 | 2.7 | 1 | 120 | 1.7 | 0 | 10.5 | 8.8 | 8.8 |  | 1.05 | 10 | 184 | Poultry plant | 10+10 | 0.78 | 3.48 | 1 | 120 | 2.48 | 0 | 10.5 | 8.02 | 8.02 | 110/10
185 | Korshevo | 6,3+6,3 | 0.65 | 0.56 | 120 | 0.09 | 0 | 6.615 | 6.525 | 6.525 |  | 1.05 | 6.3 | 185 | Korshevo | 6,3+6,3 | 2.55 | 3.2 | 0.56 | 120 | 2.64 | 0 | 6.615 | 3.975 | 3.975 | 110/10
186 | Davydovka | 6,3+6,3 | 6.2 | 2.11 | 240 | 4.09 | 0 | 6.615 | 2.525 | 2.525 |  | 1.05 | 6.3 | 186 | Davydovka | 6,3+6,3 | 2.46 | 8.66 | 2.11 | 240 | 6.55 | 0 | 6.615 | 0.065 | 0.065 | 110/10
187 | the 2nd Pyatiletka | 6,3+6,3 | 0.9 | 0.66 | 120 | 0.24 | 0 | 6.615 | 6.375 | 6.375 |  | 1.05 | 6.3 | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.67 | 1.57 | 0.66 | 120 | 0.91 | 0 | 6.615 | 5.705 | 5.705 | 110/10
188 | Liskinskaya | 10+16 | 3.3 | 0.72 | 120 | 2.58 | 0 | 10.5 | 7.92 | 7.92 |  | 1.05 | 10 | 188 | Liskinskaya | 10+16 | 1.52 | 4.82 | 0.72 | 120 | 4.1 | 0 | 10.5 | 6.4 | 6.4 | 110/6
189 | Olkhovatka | 4+4 | 3.74 | 2.55 | 180 | 1.19 | 0 | 4.2 | 3.01 | 3.01 |  | 1.05 | 4 | 189 | Olkhovatka | 4+4 | 1.06 | 4.8 | 2.55 | 180 | 2.25 | 0 | 4.2 | 1.95 | 1.95 | 35/10
190 | Shaposhnikovka | 2,5+2,5 | 1.21 | 0.86 | 180 | 0.35 | 0 | 2.625 | 2.275 | 2.275 |  | 1.05 | 2.5 | 190 | Shaposhnikovka | 2,5+2,5 | 0.27 | 1.48 | 0.86 | 180 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | 35/10
191 | Karayashnik | 2,5+2,5 | 0.41 | 0.2875 | 180 | 0.1225 | 0 | 2.625 | 2.5025 | 2.5025 |  | 1.05 | 2.5 | 191 | Karayashnik | 2,5+2,5 | 0.05 | 0.46 | 0.2875 | 180 | 0.1725 | 0 | 2.625 | 2.4525 | 2.4525 | 35/10
192 | Saguny | 2,5+2,5 | 1.02 | 0.91 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 |  | 1.05 | 2.5 | 192 | Saguny | 2,5+2,5 | 0.16 | 1.18 | 0.91 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | 35/10
193 | Belogorye | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 |  | 1.05 | 2.5 | 193 | Belogorye | 2,5+2,5 | 0.25 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | 35/10
194 | Taly | 4+4 | 1.23 | 0 | 0 | 1.23 | 0 | 4.2 | 2.97 | 2.97 |  | 1.05 | 4 | 194 | Taly | 4+4 | 0.36 | 1.59 | 0 | 0 | 1.59 | 0 | 4.2 | 2.61 | 2.61 | 35/10
195 | Titarevka | 2,5+2,5 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 |  | 1.05 | 2.5 | 195 | Titarevka | 2,5+2,5 | 0.32 | 1.2 | 0 | 0 | 1.2 | 0 | 2.625 | 1.425 | 1.425 | 35/10
196 | Mitrofanovka | 4+4 | 2.1 | 0 | 0 | 2.1 | 0 | 4.2 | 2.1 | 2.1 |  | 1.05 | 4 | 196 | Mitrofanovka | 4+4 | 0.75 | 2.85 | 0 | 0 | 2.85 | 0 | 4.2 | 1.35 | 1.35 | 35/10
197 | Druzhba | 4+4 | 1.6 | 0.44 | 150 | 1.16 | 0 | 4.2 | 3.04 | 3.04 |  | 1.05 | 4 | 197 | Druzhba | 4+4 | 0.51 | 2.11 | 0.44 | 150 | 1.67 | 0 | 4.2 | 2.53 | 2.53 | 35/10
198 | AlexandrovkaLPS | 4+4 | 2.16 | 0 | 0 | 2.16 | 0 | 4.2 | 2.04 | 2.04 |  | 1.05 | 4 | 198 | AlexandrovkaLPS | 4+4 | 0.22 | 2.38 | 0 | 0 | 2.38 | 0 | 4.2 | 1.82 | 1.82 | 35/10
199 | Tkhorevka | 4+4 | 0.72 | 0.78 | 180 | -0.06 | 0 | 4.2 | 4.26 | 4.26 |  | 1.05 | 4 | 199 | Tkhorevka | 4+4 | 0.17 | 0.89 | 0.78 | 180 | 0.11 | 0 | 4.2 | 4.09 | 4.09 | 35/10
200 | Marki | 2,5+2,5 | 0.33 | 0.27 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 2.5 | 200 | Marki | 2,5+2,5 | 0.14 | 0.47 | 0.27 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | 35/10
201 | Olkhov Log | 2,5+2,5 | 0.71 | 0.58 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 |  | 1.05 | 2.5 | 201 | Olkhov Log | 2,5+2,5 | 0 | 0.71 | 0.58 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | 35/10
202 | Boldyrevka | 2,5+2,5 | 0.95 | 0 | 0 | 0.95 | 0 | 2.625 | 1.675 | 1.675 |  | 1.05 | 2.5 | 202 | Boldyrevka | 2,5+2,5 | 0.26 | 1.21 | 0 | 0 | 1.21 | 0 | 2.625 | 1.415 | 1.415 | 35/10
203 | Pobeda | 4+4 | 0.42 | 0 | 0 | 0.42 | 0 | 4.2 | 3.78 | 3.78 |  | 1.05 | 4 | 203 | Pobeda | 4+4 | 0.08 | 0.5 | 0 | 0 | 0.5 | 0 | 4.2 | 3.7 | 3.7 | 35/10
204 | Lipovka | 4+4 | 1.398 | 0 | 0 | 1.398 | 0 | 4.2 | 2.802 | 2.802 |  | 1.05 | 4 | 204 | Lipovka | 4+4 | 2.8 | 4.198 | 0 | 0 | 4.198 | 0 | 4.2 | 0.002 | 0.002 | 35/10
205 | Yudanovka | 2,5+2,5 | 0.87 | 0.81 | 180 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 2.5 | 205 | Yudanovka | 2,5+2,5 | 2.44 | 3.31 | 0.81 | 180 | 2.5 | 0 | 2.625 | 0.125 | 0.125 | 35/10
206 | Mechetka | 2,5+1,6 | 0.46 | 0 | 0 | 0.46 | 0 | 1.68 | 1.22 | 1.22 |  | 1.05 | 1.6 | 206 | Mechetka | 2,5+1,6 | 0.06 | 0.52 | 0 | 0 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | 35/10
207 | Petrovskaya | 4+4 | 1.1 | 0.03 | 180 | 1.07 | 0 | 4.2 | 3.13 | 3.13 |  | 1.05 | 4 | 207 | Petrovskaya | 4+4 | 1.44 | 2.54 | 0.03 | 180 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | 35/10
208 | Sr. Ikorets | 4+4 | 3.25 | 0.06 | 120 | 3.19 | 0 | 4.2 | 1.01 | 1.01 |  | 1.05 | 4 | 208 | Sr. Ikorets | 4+4 | 1.8 | 5.05 | 0.06 | 120 | 4.99 | 0 | 4.2 | -0.79 | -0.79 | 35/10
209 | the 2nd Storozhevoe | 2,5+2,5 | 0.35 | 0 | 0 | 0.35 | 0 | 2.625 | 2.275 | 2.275 |  | 1.05 | 2.5 | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.39 | 0.74 | 0 | 0 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | 35/10
210 | Purification facilities | 2,5+2,5 | 1.96 | 0.42 | 120 | 1.54 | 0 | 2.625 | 1.085 | 1.085 |  | 1.05 | 2.5 | 210 | Purification facilities | 2,5+2,5 | 2.17 | 4.13 | 0.6 | 120 | 3.53 | 0 | 2.625 | -0.905 | -0.905 | 35/6
| BPS | [12 empty] | 2: BPS
211 | Borisoglebsk | 25+25 | 22.79 | 15.05 | 240 | 7.74 | 0 | 26.25 | 18.51 | 18.51 |  | 1.05 | 25 | 211 | Borisoglebsk | 25+25 | 0 | 22.79 | 24.9 | 240 | -2.11 | 0 | 26.25 | 28.36 | 26.91
| Sн. MV, МVА | 25+25 | 15.84 | 10.9 | 240 | 4.94 | 0 | 26.25 | 21.31 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 15.84 | 16.5 | 240 | -0.66 | 0 | 26.25 | 26.91 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.95 | 4.15 | 240 | 2.8 | 0 | 26.25 | 23.45 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0 | 6.95 | 8.4 | 240 | -1.45 | 0 | 26.25 | 27.7
212 | KamenkaBPS | 10+10 | 4.1 | 2.79 | 180 | 1.31 | 0 | 10.5 | 9.19 | 9.19 |  | 1.05 | 10 | 212 | KamenkaBPS | 10+10 | 0.06 | 4.16 | 6.01 | 180 | -1.85 | 0 | 10.5 | 12.35 | 10.4
| Sн. MV, МVА | 10+10 | 3.4 | 2.54 | 180 | 0.86 | 0 | 10.5 | 9.64 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 3.4 | 5.35 | 180 | -1.95 | 0 | 10.5 | 12.45 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.7 | 0.25 | 180 | 0.45 | 0 | 10.5 | 10.05 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.06 | 0.76 | 0.66 | 180 | 0.1 | 0 | 10.5 | 10.4
213 | Talovaya | 16+16 | 4.7 | 3.6 | 180 | 1.1 | 0 | 16.8 | 15.7 | 15.64 |  | 1.05 | 16 | 213 | Talovaya | 16+16 | 0.4 | 5.1 | 6.39 | 180 | -1.29 | 0 | 16.8 | 18.09 | 15.24
| Sн. MV, МVА | 16+16 | 3.54 | 3.6 | 180 | -0.06 | 0 | 16.8 | 16.86 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.54 | 6.39 | 180 | -2.85 | 0 | 16.8 | 19.65 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.16 | 0 | 0 | 1.16 | 0 | 16.8 | 15.64 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.4 | 1.56 | 0 | 0 | 1.56 | 0 | 16.8 | 15.24
214 | Anna | 25+25 | 12.29 | 7.8 | 150 | 4.49 | 0 | 26.25 | 21.76 | 21.76 |  | 1.05 | 25 | 214 | Anna | 25+25 | 1.03 | 13.32 | 14.11 | 150 | -0.79 | 0 | 26.25 | 27.04 | 25.88
| Sн. MV, МVА | 25+25 | 5.74 | 2.39 | 150 | 3.35 | 0 | 26.25 | 22.9 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 5.74 | 5.37 | 150 | 0.37 | 0 | 26.25 | 25.88 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 6.55 | 5.4 | 150 | 1.15 | 0 | 26.25 | 25.1 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 1.03 | 7.58 | 8.74 | 150 | -1.16 | 0 | 26.25 | 27.41
215 | ArkhangelskoeBPS | 10+10 | 6.12 | 0.88 | 90 | 5.24 | 0 | 10.5 | 5.26 | 5.26 |  | 1.05 | 10 | 215 | ArkhangelskoeBPS | 10+10 | 0.01 | 6.13 | 3.02 | 90 | 3.11 | 0 | 10.5 | 7.39 | 7.39
| Sн. MV, МVА | 10+10 | 3.4 | 0.88 | 90 | 2.52 | 0 | 10.5 | 7.98 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 3.4 | 3.02 | 90 | 0.38 | 0 | 10.5 | 10.12 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.72 | 0 | 0 | 2.72 | 0 | 10.5 | 7.78 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.01 | 2.73 | 0 | 0 | 2.73 | 0 | 10.5 | 7.77
216 | Listopadovka | 10+10 | 3.08 | 1.63 | 90 | 1.45 | 0 | 10.5 | 9.05 | 9.05 |  | 1.05 | 10 | 216 | Listopadovka | 10+10 | 0.37 | 3.45 | 3.08 | 90 | 0.37 | 0 | 10.5 | 10.13 | 8.87
| Sн. MV, МVА | 10+10 | 1.82 | 1.63 | 90 | 0.19 | 0 | 10.5 | 10.31 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.82 | 3.08 | 90 | -1.26 | 0 | 10.5 | 11.76 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.26 | 0 | 0 | 1.26 | 0 | 10.5 | 9.24 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.37 | 1.63 | 0 | 0 | 1.63 | 0 | 10.5 | 8.87
217 | V. Karachan | 10+10 | 2.42 | 0.81 | 90 | 1.61 | 0 | 10.5 | 8.89 | 8.89 |  | 1.05 | 10 | 217 | V. Karachan | 10+10 | 0.3 | 2.72 | 1.18 | 90 | 1.54 | 0 | 10.5 | 8.96 | 8.9
| Sн. MV, МVА | 10+10 | 1.12 | 0.81 | 90 | 0.31 | 0 | 10.5 | 10.19 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.12 | 1.18 | 90 | -0.06 | 0 | 10.5 | 10.56 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.3 | 0 | 0 | 1.3 | 0 | 10.5 | 9.2 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.3 | 1.6 | 0 | 0 | 1.6 | 0 | 10.5 | 8.9
218 | Ternovka | 10+10 | 3.77 | 0.66 | 60 | 3.11 | 0 | 10.5 | 7.39 | 7.39 |  | 1.05 | 10 | 218 | Ternovka | 10+10 | 0.06 | 3.83 | 1.03 | 60 | 2.8 | 0 | 10.5 | 7.7 | 7.7
| Sн. MV, МVА | 10+10 | 1.28 | 0.66 | 60 | 0.62 | 0 | 10.5 | 9.88 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.28 | 1.03 | 60 | 0.25 | 0 | 10.5 | 10.25 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.49 | 0 | 0 | 2.49 | 0 | 10.5 | 8.01 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.06 | 2.55 | 0 | 0 | 2.55 | 0 | 10.5 | 7.95
219 | Narodnoe | 16+10 | 1.88 | 0.6 | 90 | 1.28 | 0 | 10.5 | 9.22 | 8.98 |  | 1.05 | 10 | 219 | Narodnoe | 16+10 | 0.47 | 2.35 | 0.93 | 90 | 1.42 | 0 | 10.5 | 9.08 | 8.51
| Sн. MV, МVА | 16+10 | 0.36 | 0.6 | 90 | -0.24 | 0 | 10.5 | 10.74 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 0.36 | 0.93 | 90 | -0.57 | 0 | 10.5 | 11.07 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 1.52 | 0 | 0 | 1.52 | 0 | 10.5 | 8.98 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 0.47 | 1.99 | 0 | 0 | 1.99 | 0 | 10.5 | 8.51
220 | N. Khopersk | 10+16 | 7.79 | 1.7 | 120 | 6.09 | 0 | 10.5 | 4.41 | 4.41 |  | 1.05 | 10 | 220 | N. Khopersk | 10+16 | 1.83 | 9.62 | 1.95 | 120 | 7.67 | 0 | 10.5 | 2.83 | 2.83
| Sн. MV, МVА | 10+16 | 2.19 | 1.7 | 120 | 0.49 | 0 | 10.5 | 10.01 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 2.19 | 1.95 | 120 | 0.24 | 0 | 10.5 | 10.26 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 5.6 | 0 | 0 | 5.6 | 0 | 10.5 | 4.9 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 1.83 | 7.43 | 0 | 0 | 7.43 | 0 | 10.5 | 3.07
221 | Ertil | 10+16 | 8.36 | 2.92 | 180 | 5.44 | 0 | 10.5 | 5.06 | 5.06 |  | 1.05 | 10 | 221 | Ertil | 10+16 | 0.08 | 8.44 | 1.4 | 180 | 7.04 | 0 | 10.5 | 3.46 | 3.46
| Sн. MV, МVА | 10+16 | 6.06 | 2.92 | 180 | 3.14 | 0 | 10.5 | 7.36 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 6.06 | 1.4 | 180 | 4.66 | 0 | 10.5 | 5.84 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 2.3 | 0.08 | 0 | 2.22 | 0 | 10.5 | 8.28 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 0.08 | 2.38 | 0 | 0 | 2.38 | 0 | 10.5 | 8.12
222 | Shchuchye | 6,3+6,3 | 2.16 | 1.09 | 180 | 1.07 | 0 | 6.615 | 5.545 | 5.375 |  | 1.05 | 6.3 | 222 | Shchuchye | 6,3+6,3 | 0.78 | 2.94 | 2.33 | 180 | 0.61 | 0 | 6.615 | 6.005 | 4.865
| Sн. MV, МVА | 6,3+6,3 | 0.66 | 0.84 | 180 | -0.18 | 0 | 6.615 | 6.795 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 0.66 | 1.81 | 180 | -1.15 | 0 | 6.615 | 7.765 |  | 110/35/10
| Sн.LV, МVА | 6,3+6,3 | 1.49 | 0.25 | 180 | 1.24 | 0 | 6.615 | 5.375 |  |  | 1.05 | 6.3 |  | Sн.LV, МVА | 6,3+6,3 | 0.78 | 2.27 | 0.52 | 180 | 1.75 | 0 | 6.615 | 4.865
223 | Dokuchaevo | 10+10 | 2.94 | 0.12 | 120 | 2.82 | 0 | 10.5 | 7.68 | 7.68 |  | 1.05 | 10 | 223 | Dokuchaevo | 10+10 | 0.08 | 3.02 | 0.45 | 120 | 2.57 | 0 | 10.5 | 7.93 | 7.93 | 110/10
224 | B. Gribanovka | 16+16 | 6.27 | 0.11 | 30 | 6.16 | 0 | 16.8 | 10.64 | 10.64 |  | 1.05 | 16 | 224 | B. Gribanovka | 16+16 | 1.8 | 8.07 | 0.24 | 30 | 7.83 | 0 | 16.8 | 8.97 | 8.97 | 110/10
225 | Khimmash | 16+16 | 6 | 4.47 | 240 | 1.53 | 0 | 16.8 | 15.27 | 15.27 |  | 1.05 | 16 | 225 | Khimmash | 16+16 | 0 | 6 | 7.1 | 240 | -1.1 | 0 | 16.8 | 17.9 | 17.9 | 110/6
226 | Chigorak | 2,5+4 | 0.59 | 0.74 | 90 | -0.15 | 0 | 2.625 | 2.775 | 2.775 |  | 1.05 | 2.5 | 226 | Chigorak | 2,5+4 | 0.44 | 1.03 | 0.96 | 90 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | 35/10
227 | Tretyaki | 4+4 | 0.89 | 0 | 0 | 0.89 | 0 | 4.2 | 3.31 | 3.31 |  | 1.05 | 4 | 227 | Tretyaki | 4+4 | 1.34 | 2.23 | 0 | 0 | 2.23 | 0 | 4.2 | 1.97 | 1.97 | 35/10
228 | Gubari | 2,5+2,5 | 0.32 | 0.06 | 180 | 0.26 | 0 | 2.625 | 2.365 | 2.365 |  | 1.05 | 2.5 | 228 | Gubari | 2,5+2,5 | 0.15 | 0.47 | 0.43 | 180 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | 35/10
229 | Tantsyrey | 2,5+2,5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 |  | 1.05 | 2.5 | 229 | Tantsyrey | 2,5+2,5 | 0.26 | 0.71 | 0 | 0 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | 35/10
230 | Peski | 4+4 | 2.97 | 0 | 0 | 2.97 | 0 | 4.2 | 1.23 | 1.23 |  | 1.05 | 4 | 230 | Peski | 4+4 | 1.16 | 4.13 | 0 | 0 | 4.13 | 0 | 4.2 | 0.07 | 0.07 | 35/10
231 | M. Gribanovka | 1,6+1,6 | 0.41 | 0.31 | 30 | 0.1 | 0 | 1.68 | 1.58 | 1.58 |  | 1.05 | 1.6 | 231 | M. Gribanovka | 1,6+1,6 | 0.31 | 0.72 | 0.87 | 30 | -0.15 | 0 | 1.68 | 1.83 | 1.83 | 35/10
232 | N. Karachan | 2,5+2,5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 |  | 1.05 | 2.5 | 232 | N. Karachan | 2,5+2,5 | 0.07 | 0.54 | 0 | 0 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | 35/10
233 | Kozlovka BPS | 4+2,5 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 |  | 1.05 | 2.5 | 233 | Kozlovka BPS | 4+2,5 | 0.03 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | 35/10
234 | K. Otdelets | 2,5+2,5 | 0.41 | 0 | 30 | 0.41 | 0 | 2.625 | 2.215 | 2.215 |  | 1.05 | 2.5 | 234 | K. Otdelets | 2,5+2,5 | 0 | 0.41 | 0.63 | 30 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | 35/10
235 | Esipovo | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 |  | 1.05 | 2.5 | 235 | Esipovo | 2,5+2,5 | 0.02 | 1.05 | 0 | 0 | 1.05 | 0 | 2.625 | 1.575 | 1.575 | 35/10
236 | Kiselnov | 2,5+2,5 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 |  | 1.05 | 2.5 | 236 | Kiselnov | 2,5+2,5 | 0 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | 35/10
237 | Krasnoe | 4+4 | 1.95 | 0 | 0 | 1.95 | 0 | 4.2 | 2.25 | 2.25 |  | 1.05 | 4 | 237 | Krasnoe | 4+4 | 1.55 | 3.5 | 0 | 0 | 3.5 | 0 | 4.2 | 0.7 | 0.7 | 35/10
238 | Troitskoe | 2,5+2,5 | 0.515 | 0 | 0 | 0.515 | 0 | 2.625 | 2.11 | 2.11 |  | 1.05 | 2.5 | 238 | Troitskoe | 2,5+2,5 | 0.01 | 0.525 | 0 | 0 | 0.525 | 0 | 2.625 | 2.1 | 2.1 | 35/10
239 | Ertil-gorod | 6,3+6,3 | 3.45 | 2.45 | 240 | 1 | 0 | 6.615 | 5.615 | 5.615 |  | 1.05 | 6.3 | 239 | Ertil-gorod | 6,3+6,3 | 0.2 | 3.65 | 5 | 240 | -1.35 | 0 | 6.615 | 7.965 | 7.965 | 35/10
240 | Rostoshi | 4+4 | 0.48 | 0 | 0 | 0.48 | 0 | 4.2 | 3.72 | 3.72 |  | 1.05 | 4 | 240 | Rostoshi | 4+4 | 0 | 0.48 | 0 | 0 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | 35/10
241 | Vvedenka | 2,5+2,5 | 0.16 | 0 | 60 | 0.16 | 0 | 2.625 | 2.465 | 2.465 |  | 1.05 | 2.5 | 241 | Vvedenka | 2,5+2,5 | 0 | 0.16 | 0.48 | 60 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | 35/10
242 | Sadovoe | 4+4 | 2.03 | 0 | 0 | 2.03 | 0 | 4.2 | 2.17 | 2.17 |  | 1.05 | 4 | 242 | Sadovoe | 4+4 | 0.28 | 2.31 | 0 | 0 | 2.31 | 0 | 4.2 | 1.89 | 1.89 | 35/10
243 | Rubashevka | 2,5+2,5 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 |  | 1.05 | 2.5 | 243 | Rubashevka | 2,5+2,5 | 0.03 | 0.91 | 0 | 0 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | 35/10
244 | N. Nadezhdenka | 2,5+2,5 | 0.45 | 0.22 | 180 | 0.23 | 0 | 2.625 | 2.395 | 2.395 |  | 1.05 | 2.5 | 244 | N. Nadezhdenka | 2,5+2,5 | 0 | 0.45 | 0.75 | 180 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | 35/10
245 | Abramovka | 6,3+4 | 2.77 | 0.29 | 120 | 2.48 | 0 | 4.2 | 1.72 | 1.72 |  | 1.05 | 4 | 245 | Abramovka | 6,3+4 | 0.22 | 2.99 | 0.52 | 120 | 2.47 | 0 | 4.2 | 1.73 | 1.73 | 35/10
246 | Alexandrovka BPS | 2,5+2,5 | 0.91 | 0.64 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 |  | 1.05 | 2.5 | 246 | Alexandrovka BPS | 2,5+2,5 | 0.05 | 0.96 | 1.17 | 120 | -0.21 | 0 | 2.625 | 2.835 | 2.835 | 35/10
247 | N. Troitskaya | 4+4 | 0.36 | 0.2 | 120 | 0.16 | 0 | 4.2 | 4.04 | 4.04 |  | 1.05 | 4 | 247 | N. Troitskaya | 4+4 | 0 | 0.36 | 0.34 | 120 | 0.02 | 0 | 4.2 | 4.18 | 4.18 | 35/10
| KPS | [12 empty] | 2: KPS
248 | Kalach-1 | 25+25 | 11.9 | 2.2 | 120 | 9.7 | 0 | 26.25 | 16.55 | 16.55 |  | 1.05 | 25 | 248 | Kalach-1 | 25+25 | 2.36 | 14.26 | 2.2 | 120 | 12.06 | 0 | 26.25 | 14.19 | 14.19
| Sн. MV, МVА | 25+25 | 4.5 | 1 | 120 | 3.5 | 0 | 26.25 | 22.75 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 4.5 | 1 | 120 | 3.5 | 0 | 26.25 | 22.75 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.4 | 1.2 | 120 | 6.2 | 0 | 26.25 | 20.05 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 2.36 | 9.76 | 1.2 | 120 | 8.56 | 0 | 26.25 | 17.69
249 | Kalach-2 | 16+16 | 7.9 | 2 | 1 day and night | 5.9 | 0 | 16.8 | 10.9 | 10.9 |  | 1.05 | 16 | 249 | Kalach-2 | 16+16 | 2.31 | 10.21 | 2 | 1 day and night | 8.21 | 0 | 16.8 | 8.59 | 8.59 | 110/10
250 | Buturlinovka-1 | 16+16 | 10.8 | 2 | 120 | 8.8 | 0 | 16.8 | 8 | 8 |  | 1.05 | 16 | 250 | Buturlinovka-1 | 16+16 | 0.31 | 11.11 | 2 | 120 | 9.11 | 0 | 16.8 | 7.69 | 7.69
| Sн. MV, МVА | 16+16 | 2.28 | 0 | 0 | 2.28 | 0 | 16.8 | 14.52 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 2.28 | 0 | 0 | 2.28 | 0 | 16.8 | 14.52 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 8.5 | 2 | 120 | 6.5 | 0 | 16.8 | 10.3 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.31 | 8.81 | 2 | 120 | 6.81 | 0 | 16.8 | 9.99
251 | Buturlinovka-2 | 6,3+6,3 | 3.9 | 1.5 | 120 | 2.4 | 0 | 6.615 | 4.215 | 4.215 |  | 1.05 | 6.3 | 251 | Buturlinovka-2 | 6,3+6,3 | 0.01 | 3.91 | 1.5 | 120 | 2.41 | 0 | 6.615 | 4.205 | 4.205 | 110/10
252 | N.Kislyai | 10+10 | 6.05 | 1.5 | 120 | 4.55 | 0 | 10.5 | 5.95 | 5.95 |  | 1.05 | 10 | 252 | N.Kislyai | 10+10 | 0.8 | 6.85 | 1.5 | 120 | 5.35 | 0 | 10.5 | 5.15 | 5.15
| Sн. MV, МVА | 10+10 | 3.55 | 0 | 0 | 3.55 | 0 | 10.5 | 6.95 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 3.55 | 0 | 0 | 3.55 | 0 | 10.5 | 6.95 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.5 | 1.5 | 120 | 1 | 0 | 10.5 | 9.5 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.8 | 3.3 | 1.5 | 120 | 1.8 | 0 | 10.5 | 8.7
253 | Kozlovka CPS | 2,5+6,3 | 1.13 | 1.5 | 45 | -0.37 | 0 | 2.625 | 2.995 | 2.995 |  | 1.05 | 2.5 | 253 | Kozlovka CPS | 2,5+6,3 | 0.18 | 1.31 | 1.5 | 45 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | 110/10
254 | Filippenkovo | 6,3+6,3 | 0.82 | 1.5 | 120 | -0.68 | 0 | 6.615 | 7.295 | 7.295 |  | 1.05 | 6.3 | 254 | Filippenkovo | 6,3+6,3 | 0.05 | 0.87 | 1.5 | 120 | -0.63 | 0 | 6.615 | 7.245 | 7.245 | 110/10
255 | Vorobyovka | 16+16 | 5.13 | 1.5 | 120 | 3.63 | 0 | 16.8 | 13.17 | 13.17 |  | 1.05 | 16 | 255 | Vorobyovka | 16+16 | 0.43 | 5.56 | 1.5 | 120 | 4.06 | 0 | 16.8 | 12.74 | 12.74
| Sн. MV, МVА | 16+16 | 3.05 | 0.5 | 120 | 2.55 | 0 | 16.8 | 14.25 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.05 | 0.5 | 120 | 2.55 | 0 | 16.8 | 14.25 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.08 | 1 | 120 | 1.08 | 0 | 16.8 | 15.72 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.43 | 2.51 | 1 | 120 | 1.51 | 0 | 16.8 | 15.29
256 | Solontsy | 6,3+6,3 | 2.2 | 1 | 1 day and night | 1.2 | 0 | 6.615 | 5.415 | 5.415 |  | 1.05 | 6.3 | 256 | Solontsy | 6,3+6,3 | 0.03 | 2.23 | 1 | 1 day and night | 1.23 | 0 | 6.615 | 5.385 | 5.385
| Sн. MV, МVА | 6,3+6,3 | 1.3 | 1 | 1 day and night | 0.3 | 0 | 6.615 | 6.315 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.3 | 1 | 1 day and night | 0.3 | 0 | 6.615 | 6.315 |  | 110/35/10
| Sн. LV, МVА | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+6,3 | 0.03 | 0.93 | 0 | 0 | 0.93 | 0 | 6.615 | 5.685
257 | Manino | 16+16 | 1.76 | 1.5 | 1 day and night | 0.26 | 0 | 16.8 | 16.54 | 16.54 |  | 1.05 | 16 | 257 | Manino | 16+16 | 0.04 | 1.8 | 1.5 | 1 day and night | 0.3 | 0 | 16.8 | 16.5 | 16.5
| Sн. MV, МVА | 16+16 | 0.59 | 0.5 | 1 day and night | 0.09 | 0 | 16.8 | 16.71 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0.59 | 0.5 | 1 day and night | 0.09 | 0 | 16.8 | 16.71 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.17 | 1 | 1 day and night | 0.17 | 0 | 16.8 | 16.63 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.04 | 1.21 | 1 | 1 day and night | 0.21 | 0 | 16.8 | 16.59
258 | Petropavlovka | 10+10 | 4.1 | 2 | 120 | 2.1 | 0 | 10.5 | 8.4 | 8.4 |  | 1.05 | 10 | 258 | Petropavlovka | 10+10 | 1.42 | 5.52 | 2 | 120 | 3.52 | 0 | 10.5 | 6.98 | 6.98
| Sн. MV, МVА | 10+10 | 1.7 | 1 | 120 | 0.7 | 0 | 10.5 | 9.8 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2 | 1 | 120 | 1 | 0 | 10.5 | 9.5 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.4 | 1 | 120 | 1.4 | 0 | 10.5 | 9.1 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 1.42 | 3.82 | 1 | 120 | 2.82 | 0 | 10.5 | 7.68
259 | V.Mamon | 16+10 | 5.1 | 2 | 120 | 3.1 | 0 | 10.5 | 7.4 | 7.4 |  | 1.05 | 10 | 259 | V.Mamon | 16+10 | 1.61 | 6.71 | 2 | 120 | 4.71 | 0 | 10.5 | 5.79 | 5.79
| Sн. MV, МVА | 16+10 | 1.9 | 0 | 0 | 1.9 | 0 | 10.5 | 8.6 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 1.9 | 0 | 0 | 1.9 | 0 | 10.5 | 8.6 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 3.2 | 2 | 120 | 1.2 | 0 | 10.5 | 9.3 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 1.61 | 4.81 | 2 | 120 | 2.81 | 0 | 10.5 | 7.69
260 | N.Mamon | 2,5+6,3 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 |  | 1.05 | 2.5 | 260 | N.Mamon | 2,5+6,3 | 0.08 | 1.18 | 0 | 0 | 1.18 | 0 | 2.625 | 1.445 | 1.445 | 110/10
261 | Pavlovsk-2 | 25+25 | 17.29 | 1.5 | 120 | 15.79 | 0 | 26.25 | 10.46 | 10.46 |  | 1.05 | 25 | 261 | Pavlovsk-2 | 25+25 | 0.14 | 17.43 | 1.5 | 120 | 15.93 | 0 | 26.25 | 10.32 | 10.32
| Sн. MV, МVА | 25+25 | 9.6 | 1.5 | 120 | 8.1 | 0 | 26.25 | 18.15 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 9.6 | 1.5 | 120 | 8.1 | 0 | 26.25 | 18.15 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.69 | 0 | 0 | 7.69 | 0 | 26.25 | 18.56 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.14 | 7.83 | 0 | 0 | 7.83 | 0 | 26.25 | 18.42
262 | Bogucharskaya | 16+16 | 10.6 | 2 | 120 | 8.6 | 0 | 16.8 | 8.2 | 8.2 |  | 1.05 | 16 | 262 | Bogucharskaya | 16+16 | 3.32 | 13.92 | 2 | 120 | 11.92 | 0 | 16.8 | 4.88 | 4.88
| Sн. MV, МVА | 16+16 | 5.5 | 1 | 120 | 4.5 | 0 | 16.8 | 12.3 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 1.01 | 6.51 | 1 | 120 | 5.51 | 0 | 16.8 | 11.29 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.18 | 1 | 120 | 4.18 | 0 | 16.8 | 12.62 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.31 | 7.49 | 1 | 120 | 6.49 | 0 | 16.8 | 10.31
263 | Opornaya | 6,3+6,3 | 1.87 | 1.5 | 120 | 0.37 | 0 | 6.615 | 6.245 | 6.245 |  | 1.05 | 6.3 | 263 | Opornaya | 6,3+6,3 | 1.05 | 2.92 | 1.5 | 120 | 1.42 | 0 | 6.615 | 5.195 | 5.195 | 110/10
264 | Podgornaya KPS | 2,5+2,5 | 0.83 | 1 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 |  | 1.05 | 2.5 | 264 | Podgornaya KPS | 2,5+2,5 | 0.07 | 0.9 | 1 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | 35/10
265 | Bolshevik KPS | 4+2,5 | 2.05 | 1.5 | 45 | 0.55 | 0 | 2.625 | 2.075 | 2.075 |  | 1.05 | 2.5 | 265 | Bolshevik KPS | 4+2,5 | 0.46 | 2.51 | 1.5 | 45 | 1.01 | 0 | 2.625 | 1.615 | 1.615 | 35/10
266 | Semenovka KPS | 2,5+1,8 | 0.72 | 1 | 80 | -0.28 | 0 | 1.89 | 2.17 | 2.17 |  | 1.05 | 1.8 | 266 | Semenovka KPS | 2,5+1,8 | 0.09 | 0.81 | 1 | 80 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | 35/10
267 | Popasnoe | 4+4 | 0.32 | 1.5 | 120 | -1.18 | 0 | 4.2 | 5.38 | 5.38 |  | 1.05 | 4 | 267 | Popasnoe | 4+4 | 0.04 | 0.36 | 1.5 | 120 | -1.14 | 0 | 4.2 | 5.34 | 5.34 | 35/10
268 | N.Kriusha | 2,5+2,5 | 0.9 | 1.5 | 45 | -0.6 | 0 | 2.625 | 3.225 | 3.225 |  | 1.05 | 2.5 | 268 | N.Kriusha | 2,5+2,5 | 1.71 | 2.61 | 1.5 | 45 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | 35/10
269 | N.Melovatka | 2,5+2,5 | 1.65 | 1.5 | 45 | 0.15 | 0 | 2.625 | 2.475 | 2.475 |  | 1.05 | 2.5 | 269 | N.Melovatka | 2,5+2,5 | 0.25 | 1.9 | 1.5 | 45 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | 35/10
270 | Vasilyevka KPS | 4+4 | 0.76 | 1.5 | 120 | -0.74 | 0 | 4.2 | 4.94 | 4.94 |  | 1.05 | 4 | 270 | Vasilyevka KPS | 4+4 | 0.08 | 0.84 | 1.5 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | 35/10
271 | V.Oktyabr | 4+4 | 1.15 | 1.5 | 120 | -0.35 | 0 | 4.2 | 4.55 | 4.55 |  | 1.05 | 4 | 271 | V.Oktyabr | 4+4 | 0.22 | 1.37 | 1.5 | 120 | -0.13 | 0 | 4.2 | 4.33 | 4.33 | 35/10
272 | V.Arkhangelskoe | 2,5+2,5 | 0.37 | 1.5 | 45 | -1.13 | 0 | 2.625 | 3.755 | 3.755 |  | 1.05 | 2.5 | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.07 | 0.44 | 1.5 | 45 | -1.06 | 0 | 2.625 | 3.685 | 3.685 | 35/10
273 | Leshchanaya | 2,5+2,5 | 1.47 | 1.5 | 45 | -0.03 | 0 | 2.625 | 2.655 | 2.655 |  | 1.05 | 2.5 | 273 | Leshchanaya | 2,5+2,5 | 0.18 | 1.65 | 1.5 | 45 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | 35/10
274 | Muzhichye | 4+2,5 | 0.46 | 1.5 | 45 | -1.04 | 0 | 2.625 | 3.665 | 3.665 |  | 1.05 | 2.5 | 274 | Muzhichye | 4+2,5 | 0.11 | 0.57 | 1.5 | 45 | -0.93 | 0 | 2.625 | 3.555 | 3.555 | 35/10
275 | Rudnya | 4+4 | 0.46 | 1.5 | 120 | -1.04 | 0 | 4.2 | 5.24 | 5.24 |  | 1.05 | 4 | 275 | Rudnya | 4+4 | 0.04 | 0.5 | 1.5 | 120 | -1 | 0 | 4.2 | 5.2 | 5.2 | 35/10
276 | St. Melovaya | 4+4 | 0.85 | 0 | 0 | 0.85 | 0 | 4.2 | 3.35 | 3.35 |  | 1.05 | 4 | 276 | St. Melovaya | 4+4 | 0.36 | 1.21 | 0 | 0 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | 35/10
277 | St. Kriusha | 2,5+4 | 0.96 | 0 | 0 | 0.96 | 0 | 2.625 | 1.665 | 1.665 |  | 1.05 | 2.5 | 277 | St. Kriusha | 2,5+4 | 0.26 | 1.22 | 0 | 0 | 1.22 | 0 | 2.625 | 1.405 | 1.405 | 35/10
278 | Lozovaya | 4+4 | 0.69 | 0 | 0 | 0.69 | 0 | 4.2 | 3.51 | 3.51 |  | 1.05 | 4 | 278 | Lozovaya | 4+4 | 0.3 | 0.99 | 0 | 0 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | 35/10
279 | Pavlovsk-1 | 4+4 | 2.5 | 1 | 120 | 1.5 | 0 | 4.2 | 2.7 | 2.7 |  | 1.05 | 4 | 279 | Pavlovsk-1 | 4+4 | 0.38 | 2.88 | 1 | 120 | 1.88 | 0 | 4.2 | 2.32 | 2.32 | 35/10
280 | Losevo KPS | 4+4 | 2.66 | 0 | 0 | 2.66 | 0 | 4.2 | 1.54 | 1.54 |  | 1.05 | 4 | 280 | Losevo KPS | 4+4 | 0.09 | 2.75 | 0 | 0 | 2.75 | 0 | 4.2 | 1.45 | 1.45 | 35/10
281 | Gavrilsk | 4+4 | 0.44 | 0 | 0 | 0.44 | 0 | 4.2 | 3.76 | 3.76 |  | 1.05 | 4 | 281 | Gavrilsk | 4+4 | 0.03 | 0.47 | 0 | 0 | 0.47 | 0 | 4.2 | 3.73 | 3.73 | 35/10
282 | Pokrovka | 4+2,5 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 |  | 1.05 | 2.5 | 282 | Pokrovka | 4+2,5 | 0.02 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 35/10
283 | Vorontsovka | 4+4 | 2.5 | 1.5 | 120 | 1 | 0 | 4.2 | 3.2 | 3.2 |  | 1.05 | 4 | 283 | Vorontsovka | 4+4 | 0.7 | 3.2 | 1.5 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | 35/10
284 | А.Donskaya | 2,5+2,5 | 0.96 | 1.5 | 45 | -0.54 | 0 | 2.625 | 3.165 | 3.165 |  | 1.05 | 2.5 | 284 | А.Donskaya | 2,5+2,5 | 0.14 | 1.1 | 1.5 | 45 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | 35/10
285 | Petrovka | 2,5+4 | 1.38 | 1.5 | 45 | -0.12 | 0 | 2.625 | 2.745 | 2.745 |  | 1.05 | 2.5 | 285 | Petrovka | 2,5+4 | 2.38 | 3.76 | 1.5 | 45 | 2.26 | 0 | 2.625 | 0.365 | 0.365 | 35/10
286 | Monastyrshchina | 4+4 | 0.74 | 1.5 | 120 | -0.76 | 0 | 4.2 | 4.96 | 4.96 |  | 1.05 | 4 | 286 | Monastyrshchina | 4+4 | 0.21 | 0.95 | 1.5 | 120 | -0.55 | 0 | 4.2 | 4.75 | 4.75 | 35/10
287 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 |  | 1.05 | 1.8 | 287 | Zhuravka | 1,8+2,5 | 0.01 | 0.16 | 0 | 0 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | 35/10
288 | Dyachenkovo | 2,5+2,5 | 1.72 | 1.5 | 45 | 0.22 | 0 | 2.625 | 2.405 | 2.405 |  | 1.05 | 2.5 | 288 | Dyachenkovo | 2,5+2,5 | 1.51 | 3.23 | 1.5 | 45 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | 35/10
289 | Radchenskaya | 1,6+2,5 | 0.76 | 0 | 0 | 0.76 | 0 | 1.68 | 0.92 | 0.92 |  | 1.05 | 1.6 | 289 | Radchenskaya | 1,6+2,5 | 0.53 | 1.29 | 0 | 0 | 1.29 | 0 | 1.68 | 0.39 | 0.39 | 35/10
290 | Rossiya | 4+4 | 1.29 | 1.5 | 120 | -0.21 | 0 | 4.2 | 4.41 | 4.41 |  | 1.05 | 4 | 290 | Rossiya | 4+4 | 0.22 | 1.51 | 1.5 | 120 | 0.01 | 0 | 4.2 | 4.19 | 4.19 | 35/10
291 | Pervomayskaya | 4+4 | 0.46 | 1.5 | 120 | -1.04 | 0 | 4.2 | 5.24 | 5.24 |  | 1.05 | 4 | 291 | Pervomayskaya | 4+4 | 0.23 | 0.69 | 1.5 | 120 | -0.81 | 0 | 4.2 | 5.01 | 5.01 | 35/10
292 | Podkolodnovka | 2,5+3,2 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 |  | 1.05 | 2.5 | 292 | Podkolodnovka | 2,5+3,2 | 0.19 | 1.05 | 0 | 0 | 1.05 | 0 | 2.625 | 1.575 | 1.575 | 35/10
293 | Yuzhny | 2,5+2,5 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 |  | 1.05 | 2.5 | 293 | Yuzhny | 2,5+2,5 |  | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 | 35/10
| TOTAL: |  | 1267.3997 | [6 empty] | 1245.248 |  |  |  | 2: TOTAL:; Min 12: 957.2805
| deficit | [8 empty] | 12.937 |  |  |  | 2: deficit; Min 12: 78.5695
| proficit | [8 empty] | 1232.311 |  |  |  | 2: proficit; Min 12: 878.711
Note on S1: не нашел
Note on S2: не нашел
Note on S10: не нашел
Note on S34: не нашел
Note on S59: не нашел
Note on S94: не нашел
Note on S119: не нашел
Note on S235: не нашел
Note on S290: не нашел
Note on S352: не нашел
Note on S418: не нашел
Note on S419: не нашел
Note on S420: не нашел
Note on S421: не нашел
Note on S422: не нашел
Note on Z156: Ivanov_MA:
Note on AD235: не нашел
Note on AD290: не нашел
Note on AD352: не нашел
Note on AD418: не нашел
Note on AE34: не нашел
Note on AE59: не нашел
Note on AE94: не нашел
Note on AE235: не нашел
Note on AE290: не нашел
Note on AE352: не нашел
Note on AE418: не нашел
Note on AE419: не нашел
Note on AE420: не нашел
Note on AE421: не нашел