## Yaroslavl
Calculation of transmission capacity of supply centres of IDGC of Center - Yarenergo following the winter peak load measurements in 2011
[14 empty] | table 1 | [16 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [13 empty] | Note | cosφ | No. | Name of supply center, voltage class |  | Expected deficit/proficit | [10 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA | [6 empty] | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВт | Additional capacity issued for technical specifications for TS, МВА | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period provided that technical requirements at connections or other measures performed for reconstruction of the grid investment programs and etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Expected deficit/proficit, MVA
[9 empty] | MVA | Min | [14 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 |  | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 1 | 2 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.28 |  | 0.28 |  | 0.883 | 1 сутки | 0.28 | 0 | 0.883 | 0.603 | 0.603 | открыт | 0.99 | 1 | SS 35/10 Matveevo | SS 35/10 Matveevo | 1.6 | 0.466 | 0.47071 | 0.75071 | 0.883 | 1 сутки | 0.75071 | 0 | 0.883 | 0.13229 | 0.13229 | открыт
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.24 |  | 1.24 |  | 0 | 1 day and night | 1.24 | 0 | 0 | -1.24 | -1.24 | unavailable | 0.97 | 2 | SS 35/10 Mikhailovskoe | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 0.0030928 | 1.2431 | 0 | 1 day and night | 1.2431 | 0 | 0 | -1.2431 | -1.2431 | unavailable
3 | SS 35/10 Shirinye | 4 | 4 |  | 1.85 |  |  | 1.85 | 2.095 | 1 day and night | 1.85 | 0 | 2.095 | 0.245 | 0.245 | available | 0.95 | 3 | SS 35/10 Shirinye | SS 35/10 Shirinye | 4 | 0.416 | 0.43789 | 2.2879 | 2.095 | 1 day and night | 2.2879 | 0 | 2.095 | -0.19289 | -0.19289 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.3 |  | 0.3 |  | 1.273 | 1 сутки | 0.3 | 0 | 1.273 | 0.973 | 0.973 | открыт | 0.8 | 4 | SS 110/10 Pokrov | SS 110/10 Pokrov | 2.5 | 0.052 | 0.065 | 0.365 | 1.273 | 1 сутки | 0.365 | 0 | 1.273 | 0.908 | 0.908 | открыт
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 |  | 0.2 |  | 1.212 | 1 сутки | 0.2 | 0 | 1.212 | 1.012 | 1.012 | открыт | 0.91 | 5 | SS 35/10 Obnora | SS 35/10 Obnora | 1.6 | 0.0435 | 0.047802 | 0.2478 | 1.212 | 1 сутки | 0.2478 | 0 | 1.212 | 0.9642 | 0.9642 | открыт
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 8.3 | [5 empty] | 8.3 | 0 | 10.5 | 2.2 | 2.2 | available | 0.97 | 6 | SS 110/35/10 Abbakumtsevo | SS 110/35/10 Abbakumtsevo | 10+10 | 0 | 0 | 22.2722 |  |  | 22.2722 | 0 | 10.5 | -11.7722 | -11.7722 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 7.1 |  | Т-1: 1.82; Т-2: 5.28; Min 7: 7.1; Min 8: 0; Min 9: 10.5; Min 10: 3.4 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 17.0381 |  |  | 17.0381 | 0 | 10.5 | -6.5381
| Nom. capacity LV, МVА | 10+10 |  |  | 1.2 |  | Т-1: 0.58; Т-2: 0.62; Min 7: 1.2; Min 8: 0; Min 9: 10.5; Min 10: 9.3 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 3.913 | 4.034 | 5.234 |  |  | 5.234 | 0 | 10.5 | 5.266
7 | SS 35/10 Ananyino | 2,5+2,5 | 2.5 | 2.5 | 1.15 |  | 0.86 | 0.29 |  |  | 1.15 | 0 | 2.63 | 1.48 | 1.48 | available | 0.97 | 7 | SS 35/10 Ananyino | SS 35/10 Ananyino | 2,5+2,5 | 2.133 | 2.199 | 3.349 |  |  | 3.349 | 0 | 2.63 | -0.71897 | -0.71897 | unavailable
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 26.79 |  | 12.53 | 14.26 | 2.252 | 120 | 24.538 | 0 | 42 | 17.462 | 17.462 | открыт | 0.97 | 8 | SS 110/10/10 Bragino | SS 110/10/10 Bragino | 40+40 | 3.4684 | 3.5757 | 30.3657 | 2.252 | 120 | 28.1137 | 0 | 42 | 13.8863 | 13.8863 | открыт
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 1.73 |  | 0.68 | 1.05 | 0.52 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | открыт | 0.97 | 9 | SS 35/10 Burmakino-1 | SS 35/10 Burmakino-1 | 4,0+4,0 | 1.0435 | 1.0758 | 2.8058 | 0.52 | 120 | 2.2858 | 0 | 4.2 | 1.9142 | 1.9142 | открыт
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.14 |  | 1.7 | 1.44 |  |  | 3.14 | 0 | 4.2 | 1.06 | 1.06 | available | 0.96 | 10 | SS 35/10 Vatolino | SS 35/10 Vatolino | 4,0+4,0 | 5.931 | 6.1781 | 9.3181 |  |  | 9.3181 | 0 | 4.2 | -5.1181 | -5.1181 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.55 |  | 1.55 | 3 |  |  | 4.55 | 0 | 6.62 | 2.07 | 2.07 | открыт | 0.92 | 11 | SS 35/6 Vederniki | SS 35/6 Vederniki | 6,3+6,3 | 0.0392 | 0.042609 | 4.5926 |  |  | 4.5926 | 0 | 6.62 | 2.0274 | 2.0274 | открыт
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.78 |  | 1.27 | 0.51 |  |  | 1.78 | 0 | 4.2 | 2.42 | 2.42 | открыт | 0.82 | 12 | SS 35/10 Velikovskaya | SS 35/10 Velikovskaya | 4,0+4,0 | 0.135 | 0.16463 | 1.9446 |  |  | 1.9446 | 0 | 4.2 | 2.2554 | 2.2554 | открыт
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.62 |  | 0.52 | 0.1 |  |  | 0.62 | 0 | 1.68 | 1.06 | 1.06 | открыт | 0.93 | 13 | SS 35/10 Velikoe Selo | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.062 | 0.066667 | 0.68667 |  |  | 0.68667 | 0 | 1.68 | 0.99333 | 0.99333 | открыт
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.23 |  | 0.36 | 0.87 |  |  | 1.23 | 0 | 4.2 | 2.97 | 2.97 | открыт | 0.96 | 14 | SS 35/10 Vozrozhdenie | SS 35/10 Vozrozhdenie | 4,0+4,0 | 0.8704 | 0.90667 | 2.1367 |  |  | 2.1367 | 0 | 4.2 | 2.0633 | 2.0633 | открыт
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.64 |  | 1.51 | 1.13 |  |  | 2.64 | 0 | 2.63 | -0.01 | -0.01 | unavailable | 0.88 | 15 | SS 35/10 Volna | SS 35/10 Volna | 4,0+2,5 | 0 | 0 | 2.64 |  |  | 2.64 | 0 | 2.63 | -0.01 | -0.01 | unavailable
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 1.75 |  | 0.89 | 0.86 | 0.139 | 120 | 1.611 | 0 | 2.63 | 1.019 | 1.019 | открыт | 0.93 | 16 | SS 35/10 Vyatskoe | SS 35/10 Vyatskoe | 2,5+2,5 | 0.432 | 0.46452 | 2.2145 | 0.139 | 120 | 2.0755 | 0 | 2.63 | 0.55448 | 0.55448 | открыт
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.64 |  | 0.32 | 0.32 | 0.277 | 120 | 0.363 | 0 | 2.63 | 2.267 | 2.267 | открыт | 0.93 | 17 | SS 35/10 Gorinskaya | SS 35/10 Gorinskaya | 2,5+2,5 | 0.176 | 0.18925 | 0.82925 | 0.277 | 120 | 0.55225 | 0 | 2.63 | 2.0778 | 2.0778 | открыт
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.18 |  | 1.76 | 0.42 | 0.294 | 120 | 1.886 | 0 | 4.2 | 2.314 | 2.314 | открыт | 0.96 | 18 | SS 35/10 Grigoryevskoe | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.8165 | 0.85052 | 3.0305 | 0.294 | 120 | 2.7365 | 0 | 4.2 | 1.4635 | 1.4635 | открыт
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 3.41 |  | 1.27 | 2.14 | 1.316 | 120 | 2.094 | 0 | 4.2 | 2.106 | 2.106 | available | 0.97 | 19 | SS 35/10 Guzitsino | SS 35/10 Guzitsino | 4,0+4,0 | 5.1229 | 5.2813 | 8.6913 | 1.316 | 120 | 7.3753 | 0 | 4.2 | -3.1753 | -3.1753 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.04 |  | 1.74 | 0.3 |  |  | 2.04 | 0 | 6.62 | 4.58 | 4.58 | открыт | 0.99 | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0.011 | 0.011111 | 2.0511 |  |  | 2.0511 | 0 | 6.62 | 4.5689 | 4.5689 | открыт
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 8.56 |  | 5.24 | 3.32 |  |  | 8.56 | 0 | 16.8 | 8.24 | 8.24 | открыт | 0.97 | 21 | SS 110/6 Depo | SS 110/6 Depo | 16+16 | 1.9459 | 2.0061 | 10.5661 |  |  | 10.5661 | 0 | 16.8 | 6.2339 | 6.2339 | открыт
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.31 |  | 0.61 | 0.7 | 0.675 | 120 | 0.635 | 0 | 1.68 | 1.045 | 1.045 | available | 0.96 | 22 | SS 35/10 Dorozhaevo | SS 35/10 Dorozhaevo | 1,6+1,6 | 2.381 | 2.4802 | 3.7902 | 0.675 | 120 | 3.1152 | 0 | 1.68 | -1.4352 | -1.4352 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.17 |  | 1.63 | 3.54 | 1.706 | 120 | 3.464 | 0 | 16.8 | 13.336 | 13.336 | открыт | 0.91 | 23 | SS 110/10 Druzhba | SS 110/10 Druzhba | 16+16 | 0.99523 | 1.0937 | 6.2637 | 1.706 | 120 | 4.5577 | 0 | 16.8 | 12.2423 | 12.2423 | открыт
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 3.8 |  | 2.58 | 1.22 | 1.083 | 120 | 2.717 | 0 | 6.62 | 3.903 | 3.903 | открыт | 0.91 | 24 | SS 35/10 Dubki | SS 35/10 Dubki | 6,3+6,3 | 1.5075 | 1.6566 | 5.4566 | 1.083 | 120 | 4.3736 | 0 | 6.62 | 2.2464 | 2.2464 | открыт
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 0.96 |  | 0.5 | 0.46 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | открыт | 0.91 | 25 | SS 35/10 Dybino | SS 35/10 Dybino | 2,5+2,5 | 0.526 | 0.57802 | 1.538 |  |  | 1.538 | 0 | 2.63 | 1.092 | 1.092 | открыт
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 11.04 |  | 2.92 | 8.12 |  |  | 11.04 | 0 | 10.5 | -0.54 | -0.54 | unavailable | 0.97 | 26 | SS 35/6 Zavolzhskaya | SS 35/6 Zavolzhskaya | 10+10 | 0.17183 | 0.17714 | 11.2171 |  |  | 11.2171 | 0 | 10.5 | -0.71714 | -0.71714 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 34.35 |  | 18.11 | 16.24 |  |  | 34.35 | 0 | 42 | 7.65 | 7.65 | открыт | 0.95 | 27 | SS 110/6/6 Institutskaya | SS 110/6/6 Institutskaya | 40+40 | 1.2718 | 1.3388 | 35.6888 |  |  | 35.6888 | 0 | 42 | 6.3112 | 6.3112 | открыт
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.33 |  | 0.1 | 0.23 | 0.07 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | открыт | 0.98 | 28 | SS 35/10 Koza | SS 35/10 Koza | 1,6+1,6 | 0.01 | 0.010204 | 0.3402 | 0.07 | 120 | 0.2702 | 0 | 1.68 | 1.4098 | 1.4098 | открыт
29 | SS 110/35/6 Konstantinovo | 15+16 | 15 | 16 | 8.83 |  |  |  | 0.021 | 120 | 8.809 | 0 | 15.75 | 6.941 | 6.941 | открыт | 0.91 | 29 | SS 110/35/6 Konstantinovo | SS 110/35/6 Konstantinovo | 15+16 | 0 | 0 | 12.6023 | 0.021 | 120 | 12.5813 | 0 | 15.75 | 3.1687 | 3.1687 | открыт
| Nom. capacity MV, МVА | 15+16 |  |  | 6.13 |  | Т-1: 4.14; Т-2: 1.99; Min 7: 6.13; Min 8: 0; Min 9: 15.75; Min 10: 9.62 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 15+16 | 0 |  | 8.5639 |  |  | 8.5639 | 0 | 15.75 | 7.1861
| Nom. capacity LV, МVА | 15+16 |  |  | 2.7 |  | 1.94 | 0.76 | 0.021 | 120 | 2.679 | 0 | 15.75 | 13.071 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 15+16 | 1.218 | 1.3385 | 4.0385 | 0.021 | 120 | 4.0175 | 0 | 15.75 | 11.7325
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.35 |  | 0.47 | 1.88 | 0.277 | 120 | 2.073 | 0 | 2.63 | 0.557 | 0.557 | available | 0.96 | 30 | SS 35/10 Kurba | SS 35/10 Kurba | 2,5+2,5 | 0.721 | 0.75104 | 3.101 | 0.277 | 120 | 2.824 | 0 | 2.63 | -0.19404 | -0.19404 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 6.52 |  | 3.43 | 3.09 | 1.212 | 120 | 5.308 | 0 | 10.5 | 5.192 | 5.192 | открыт | 0.91 | 31 | SS 35/10 Lesnye Polyany | SS 35/10 Lesnye Polyany | 10+10 | 3.61 | 3.967 | 10.487 | 1.212 | 120 | 9.275 | 0 | 10.5 | 1.225 | 1.225 | открыт
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.43 |  | 1.52 | 3.91 | 1.905 | 120 | 3.525 | 0 | 6.62 | 3.095 | 3.095 | available | 0.98 | 32 | SS 35/10 Modelovo-2 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.9239 | 7.0652 | 12.4952 | 1.905 | 120 | 10.5902 | 0 | 6.62 | -3.9702 | -3.9702 | unavailable
33 | SS 35/10 Nekrasovo | 16+16 | 16 | 16 | 9.99 |  | 3.8 | 6.19 |  |  | 9.99 | 0 | 16.8 | 6.81 | 6.81 | открыт | 0.96 | 33 | SS 35/10 Nekrasovo | SS 35/10 Nekrasovo | 16+16 | 2.6134 | 2.7223 | 12.7123 |  |  | 12.7123 | 0 | 16.8 | 4.0877 | 4.0877 | открыт
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.77 |  | 0.37 | 0.4 | 0.416 | 120 | 0.354 | 0 | 2.63 | 2.276 | 2.276 | открыт | 0.94 | 34 | SS 35/10 Nikolskoe | SS 35/10 Nikolskoe | 2,5+2,5 | 0.128 | 0.13617 | 0.90617 | 0.416 | 120 | 0.49017 | 0 | 2.63 | 2.1398 | 2.1398 | открыт
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 16.7 | [5 empty] | 16.7 | 0 | 26.25 | 9.55 | 9.55 | открыт | 0.95 | 35 | SS 110/35/6 Oil refinary plant | SS 110/35/6 Oil refinary plant | 25+25 | 0 | 0 | 24.4379 |  |  | 24.4379 | 0 | 26.25 | 1.8121 | 1.8121 | открыт
| Nom. capacity MV, МVА | 25+25 |  |  | 8.79 |  | Т-1: 5.2; Т-2: 3.59; Min 7: 8.79; Min 8: 0; Min 9: 26.25; Min 10: 17.46 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 25+25 | 0 |  | 8.8437 |  |  | 8.8437 | 0 | 26.25 | 17.4063
| Nom. capacity LV, МVА | 25+25 |  |  | 7.91 |  | Т-1: 3.72; Т-2: 4.19; Min 7: 7.91; Min 8: 0; Min 9: 26.25; Min 10: 18.34 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 25+25 | 7.3 | 7.6842 | 15.5942 |  |  | 15.5942 | 0 | 26.25 | 10.6558
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 17.27 |  | 7.44 | 9.83 |  |  | 17.27 | 0 | 42 | 24.73 | 24.73 | открыт | 0.83 | 36 | SS 110/6/6 Orion | SS 110/6/6 Orion | 40+40 | 0.1581 | 0.19048 | 17.4605 |  |  | 17.4605 | 0 | 42 | 24.5395 | 24.5395 | открыт
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 25.52 | [5 empty] | 25.52 | 0 | 21 | -4.52 | -4.52 | unavailable | 0.92 | 37 | SS 110/35/6 Pavlovskaya | SS 110/35/6 Pavlovskaya | 20+25 | 0 |  | 25.9637 |  |  | 25.9637 | 0 | 21 | -4.9637 | -4.9637 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 8.98 |  | Т-1: 0; Т-2: 8.98; Min 7: 8.98; Min 8: 0; Min 9: 21; Min 10: 12.02 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 20+25 | 0 |  | 9.4053 |  |  | 9.4053 | 0 | 21 | 11.5947
| Nom. capaity LV, МVА | 20+25 |  |  | 16.54 |  | Т-1: 8.57; Т-2: 7.97; Min 7: 16.54; Min 8: 0; Min 9: 21; Min 10: 4.46 |  | Nom. capaity LV, МVА | Nom. capaity LV, МVА | 20+25 | 0.017 | 0.018478 | 16.5585 |  |  | 16.5585 | 0 | 21 | 4.4415
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.04 |  | 3.87 | 4.17 |  |  | 8.04 | 0 | 16.8 | 8.76 | 8.76 | открыт | 0.99 | 38 | SS 110/10 Pereval | SS 110/10 Pereval | 16+16 | 6.8497 | 6.9189 | 14.9589 |  |  | 14.9589 | 0 | 16.8 | 1.8411 | 1.8411 | открыт
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 9.59 |  | 4.68 | 4.91 |  |  | 9.59 | 0 | 26.25 | 16.66 | 16.66 | открыт | 0.95 | 39 | SS 110/6/6 Perekop | SS 110/6/6 Perekop | 25+25 | 0.62714 | 0.66014 | 10.2501 |  |  | 10.2501 | 0 | 26.25 | 15.9999 | 15.9999 | открыт
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 30.75 |  | 18.47 | 12.28 |  |  | 30.75 | 0 | 42 | 11.25 | 11.25 | открыт | 0.98 | 40 | SS 110/6/6 Poligraf | SS 110/6/6 Poligraf | 40+40 | 0.62809 | 0.64091 | 31.3909 |  |  | 31.3909 | 0 | 42 | 10.6091 | 10.6091 | открыт
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 4.44 |  |  |  | 0.52 | 120 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | открыт | 0.93 | 41 | SS 110/35/10 Prechistoe | SS 110/35/10 Prechistoe | 10+10 | 0 |  | 5.2566 | 0.52 | 120 | 4.7366 | 0 | 10.5 | 5.7634 | 5.7634 | открыт
| Nom. capacity MV, МVА | 10+10 |  |  | 1.64 |  | Т-1: 0.07; Т-2: 1.57; Min 7: 1.64; Min 8: 0; Min 9: 10.5; Min 10: 8.86 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 1.7808 |  |  | 1.7808 | 0 | 10.5 | 8.7192
| Nom. capacity LV, МVА | 10+10 |  |  | 2.8 |  | 1.34 | 1.46 | 0.52 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 0.62842 | 0.67572 | 3.4757 | 0.52 | 120 | 2.9557 | 0 | 10.5 | 7.5443
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 0.93 |  | 0.36 | 0.57 | 0.346 | 120 | 0.584 | 0 | 2.63 | 2.046 | 2.046 | available | 0.96 | 42 | SS 35/10 Preventorium | SS 35/10 Preventorium | 2,5+2,5 | 2.7373 | 2.8514 | 3.7814 | 0.346 | 120 | 3.4354 | 0 | 2.63 | -0.80535 | -0.80535 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 |  | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | открыт | 0.77 | 43 | SS 35/10 Rozhdestveno | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.043 | 0.055844 | 0.28584 | 0.052 | 120 | 0.23384 | 0 | 2.63 | 2.3962 | 2.3962 | открыт
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 36.14 |  | 16.37 | 19.77 |  |  | 36.14 | 0 | 66.15 | 30.01 | 30.01 | открыт | 0.97 | 44 | SS 110/6/6 Severnaya | SS 110/6/6 Severnaya | 63+63 | 0.44638 | 0.46019 | 36.6002 |  |  | 36.6002 | 0 | 66.15 | 29.5498 | 29.5498 | открыт
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.31 |  | 0.5 | 0.81 | 0.831 | 120 | 0.479 | 0 | 2.63 | 2.151 | 2.151 | открыт | 0.89 | 45 | SS 35/10 Sereda | SS 35/10 Sereda | 2,5+2,5 | 0.42 | 0.47191 | 1.7819 | 0.831 | 120 | 0.95091 | 0 | 2.63 | 1.6791 | 1.6791 | открыт
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 12.84 |  | 9.59 | 3.25 |  |  | 12.84 | 0 | 16.8 | 3.96 | 3.96 | открыт | 0.96 | 46 | SS 110/6 Tormoznaya | SS 110/6 Tormoznaya | 16+16 | 0.08 | 0.083333 | 12.9233 |  |  | 12.9233 | 0 | 16.8 | 3.8767 | 3.8767 | открыт
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.89 |  | 2.47 | 2.42 |  |  | 4.89 | 0 | 16.8 | 11.91 | 11.91 | открыт | 0.98 | 47 | SS 110/6 Petrol station pump | SS 110/6 Petrol station pump | 16+16 | 0.8 | 0.81633 | 5.7063 |  |  | 5.7063 | 0 | 16.8 | 11.0937 | 11.0937 | открыт
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.41 |  | 0.32 | 0.09 | 0.277 | 120 | 0.133 | 0 | 2.63 | 2.497 | 2.497 | открыт | 0.89 | 48 | SS 35/10 Troitsa | SS 35/10 Troitsa | 2,5+2,5 | 0.043 | 0.048315 | 0.45831 | 0.277 | 120 | 0.18131 | 0 | 2.63 | 2.4487 | 2.4487 | открыт
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.9 |  | 0.37 | 0.53 | 0.173 | 120 | 0.727 | 0 | 2.63 | 1.903 | 1.903 | открыт | 0.97 | 49 | SS 35/10 Tunoshna | SS 35/10 Tunoshna | 2,5+2,5 | 0.681 | 0.70206 | 1.6021 | 0.173 | 120 | 1.4291 | 0 | 2.63 | 1.2009 | 1.2009 | открыт
50 | SS 35/10 Tutaev-35 | 10+10 | 10 | 10 | 6.35 |  | 3.11 | 3.24 |  |  | 6.35 | 0 | 10.5 | 4.15 | 4.15 | открыт | 0.96 | 50 | SS 35/10 Tutaev-35 | SS 35/10 Tutaev-35 | 10+10 | 0.516 | 0.5375 | 6.8875 |  |  | 6.8875 | 0 | 10.5 | 3.6125 | 3.6125 | открыт
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.75 |  | 0.62 | 0.13 |  |  | 0.75 | 0 | 2.63 | 1.88 | 1.88 | открыт | 0.96 | 51 | SS 110/10 Tufanovo | SS 110/10 Tufanovo | 2,5+2,5 | 0.21072 | 0.2195 | 0.9695 |  |  | 0.9695 | 0 | 2.63 | 1.6605 | 1.6605 | открыт
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.61 |  | 0.73 | 0.88 | 0.346 | 120 | 1.264 | 0 | 4.2 | 2.936 | 2.936 | открыт | 0.98 | 52 | SS 35/10 Urozhay | SS 35/10 Urozhay | 4,0+4,0 | 1.461 | 1.4908 | 3.1008 | 0.346 | 120 | 2.7548 | 0 | 4.2 | 1.4452 | 1.4452 | открыт
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | 2.69 |  | Min 8: 0; Min 11: 2.813; Min 12: открыт; Min 13: 0.92 | 53 | SS 110/35/10 Khaldeevo | SS 110/35/10 Khaldeevo | 3,2+6,3 | 0 | 0 | 0.74174 |  |  |  | 0 |  |  | 2.7913 | открыт
| Nom. capacity MV, МVА | 0+6,3 |  |  | 1.97 |  | Т-2: 1.97; Min 8: 0 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 0+6,3 | 0 | [5 empty] | 0
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.72 |  | 0.57 | 0.15 | 0.173 | 120 | 0.547 | 0 | 3.36 | 2.813 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 3.2+6.3 | 0.02 | 0.021739 | 0.74174 | 0.173 | 120 | 0.56874 | 0 | 3.36 | 2.7913
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 17.51 |  | 10.5 | 7.01 |  |  | 17.51 | 0 | 26.25 | 8.74 | 8.74 | открыт | 0.98 | 54 | SS 110/10 Chayka | SS 110/10 Chayka | 25+25 | 2.4 | 2.449 | 19.959 |  |  | 19.959 | 0 | 26.25 | 6.291 | 6.291 | открыт
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.55 |  | 0.97 | 0.58 | 0.139 | 120 | 1.411 | 0 | 2.63 | 1.219 | 1.219 | available | 0.93 | 55 | SS 35/6 Chebakovo | SS 35/6 Chebakovo | 2,5+2,5 | 1.868 | 2.0086 | 3.5586 | 0.139 | 120 | 3.4196 | 0 | 2.63 | -0.7896 | -0.7896 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.31 |  | 0.23 | 1.08 |  |  | 1.31 | 0 | 4.2 | 2.89 | 2.89 | открыт | 0.94 | 56 | SS 35/10 Shchedrino | SS 35/10 Shchedrino | 4,0+4,0 | 1.5229 | 1.6201 | 2.9301 |  |  | 2.9301 | 0 | 4.2 | 1.2699 | 1.2699 | открыт
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 29.6 |  | 12.7 | 16.9 |  |  | 29.6 | 0 | 42 | 12.4 | 12.4 | открыт | 0.96 | 57 | SS 110/6 /6 Yuzhnaya | SS 110/6 /6 Yuzhnaya | 40+40 | 2.8087 | 2.9257 | 32.5257 |  |  | 32.5257 | 0 | 42 | 9.4743 | 9.4743 | открыт
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.39 |  | 4.55 | 1.84 |  |  | 6.39 | 0 | 26.25 | 19.86 | 19.86 | открыт | 0.998 | 58 | SS 110/10/6 Yartsevo | SS 110/10/6 Yartsevo | 25+25 | 0.9545 | 0.95641 | 7.3464 |  |  | 7.3464 | 0 | 26.25 | 18.9036 | 18.9036 | открыт
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.89 |  | 2.73 | 4.16 |  |  | 6.89 | 0 | 26.25 | 19.36 | 19.36 | открыт | 0.98 | 59 | ПС 110/6/6 Kotorosl | ПС 110/6/6 Kotorosl | 25+25 | 0.21133 | 0.21564 | 7.1056 |  |  | 7.1056 | 0 | 26.25 | 19.1444 | 19.1444 | открыт
60 | SS 35/6 Kelnot | 4,0 | 4 |  | 0.16 |  | 0.16 |  | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16 | unavailable | 0.89 | 60 | SS 35/6 Kelnot | SS 35/6 Kelnot | 4,0 | 0 | 0 | 0.16 | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16 | unavailable
61 | SS 35/10 Ceramic | 10+10 | 10 | 10 | 6.19 |  | 2.77 | 3.42 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31 | открыт | 0.97 | 61 | SS 35/10 Ceramic | SS 35/10 Ceramic | 10+10 | 0 | 0 | 6.19 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31 | открыт
62 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 2.96 |  | 1.15 | 1.81 |  |  | 2.96 | 0 | 6.62 | 3.66 | 3.66 | открыт | 0.95 | 62 | SS 110/10 Altynovo | SS 110/10 Altynovo | 6,3+6,3 | 2.2858 | 2.4061 | 5.3661 |  |  | 5.3661 | 0 | 6.62 | 1.2539 | 1.2539 | открыт
63 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.83 | [5 empty] | 7.83 | 0 | 10.5 | 2.67 | 2.67 | available | 0.94 | 63 | SS 110/35/10 Borisogleb | SS 110/35/10 Borisogleb | 16+10 | 0 | 0 | 13.6819 |  |  | 13.6819 | 0 | 10.5 | -3.1819 | -3.1819 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.13 |  | Т-1: 1.6; Т-2: 1.53; Min 7: 3.13; Min 8: 0; Min 9: 10.5; Min 10: 7.37 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 16+10 | 0 |  | 6.2765 |  |  | 6.2765 | 0 | 10.5 | 4.2235
| Nom. capacity LV, МVА | 16+10 |  |  | 4.7 |  | Т-1: 2.45; Т-2: 2.25; Min 7: 4.7; Min 8: 0; Min 9: 10.5; Min 10: 5.8 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 16+10 | 2.543 | 2.7053 | 7.4053 |  |  | 7.4053 | 0 | 10.5 | 3.0947
64 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.09 |  |  |  | 0.52 | 120 | 2.57 | 0 | 10.5 | 7.93 | 7.93 | открыт | 0.95 | 64 | SS 110/35/10 Vasilkovo | SS 110/35/10 Vasilkovo | 10+10 | 0 |  | 4.7708 | 0.52 | 120 | 4.2508 | 0 | 10.5 | 6.2492 | 6.2492 | открыт
| Nom. capacity MV, МVА | 10+10 |  |  | 2.14 |  | Т-1: 0; Т-2: 2.14; Min 7: 2.14; Min 8: 0; Min 9: 10.5; Min 10: 8.36 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 2.3945 |  |  | 2.3945 | 0 | 10.5 | 8.1055
| Nom. capacity LV, МVА | 10+10 |  |  | 0.95 |  | 0.28 | 0.67 | 0.52 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 1.355 | 1.4263 | 2.3763 | 0.52 | 120 | 1.8563 | 0 | 10.5 | 8.6437
65 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.32 |  | 0.07 | 0.25 | 0.052 | 120 | 0.268 | 0 | 6.62 | 6.352 | 6.352 | открыт | 0.96 | 65 | SS 110/10 Vakhrushevo | SS 110/10 Vakhrushevo | 6,3+6,3 | 0 | 0 | 0.32 | 0.052 | 120 | 0.268 | 0 | 6.62 | 6.352 | 6.352 | открыт
66 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 13.31 |  | 5.78 | 7.53 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | открыт | 0.81 | 66 | SS 110/6 Gavrilov Yam | SS 110/6 Gavrilov Yam | 16+16 | 0 | 0 | 13.31 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | открыт
67 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 10.47 |  | 4.84 | 5.63 |  |  | 10.47 | 0 | 6.62 | -3.85 | -3.85 | unavailable | 0.94 | 67 | SS 110/6 Kinoplyonka | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 3.0362 | 13.5062 |  |  | 13.5062 | 0 | 6.62 | -6.8862 | -6.8862 | unavailable
68 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.23 | [5 empty] | 1.23 | 0 | 6.62 | 5.39 | 5.39 | открыт | 0.98 | 68 | SS 110/35/10 Klimatino | SS 110/35/10 Klimatino | 6,3+6,3 | 0 |  | 1.3611 |  |  | 1.3611 | 0 | 6.62 | 5.2589 | 5.2589 | открыт
| Nom. capacity MV, МVА | 0+6,3 |  |  | 0.24 |  | Т-2: 0.24; Min 7: 0.24; Min 8: 0; Min 9: 6.62; Min 10: 6.38 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 0+6,3 | 0 |  | 0.3384 |  |  | 0.3384 | 0 | 6.62 | 6.2816
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 0.99 |  | Т-1: 0; Т-2: 0.99; Min 7: 0.99; Min 8: 0; Min 9: 6.62; Min 10: 5.63 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 6,3+6,3 | 0.032 | 0.032653 | 1.0227 |  |  | 1.0227 | 0 | 6.62 | 5.5973
69 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 8.12 |  |  |  | 0.52 | 120 | 7.6 | 0 | 6.62 | -0.98 | -0.98 | unavailable | 0.95 | 69 | SS 110/35/10 Nila | SS 110/35/10 Nila | 6,3+6,3 | 0 |  | 29.1016 | 0.52 | 120 | 28.5816 | 0 | 6.62 | -21.9616 | -21.9616 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 6.01 |  | Т-1: 3.06; Т-2: 2.95; Min 7: 6.01; Min 8: 0; Min 9: 6.62; Min 10: 0.61 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 6,3+6,3 | 0 |  | 12.064 |  |  | 12.064 | 0 | 6.62 | -5.444
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.11 |  | 1.08 | 1.03 | 0.52 | 120 | 1.59 | 0 | 6.62 | 5.03 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 6,3+6,3 | 14.1812 | 14.9276 | 17.0376 | 0.52 | 120 | 16.5176 | 0 | 6.62 | -9.8976
70 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 23.82 | [5 empty] | 23.82 | 0 | 26.25 | 2.43 | 2.43 | available | 0.94 | 70 | SS 110/35/6 Pereslavl | SS 110/35/6 Pereslavl | 25+25 | 0 |  | 37.8744 |  |  | 37.8744 | 0 | 26.25 | -11.6244 | -11.6244 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.23 |  | Т-1: 3.58; Т-2: 6.65; Min 7: 10.23; Min 8: 0; Min 9: 26.25; Min 10: 16.02 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 25+25 | 0 |  | 23.5334 |  |  | 23.5334 | 0 | 26.25 | 2.7166
| Nom. capacity LV, МVА | 25+25 |  |  | 13.59 |  | Т-1: 5.97; Т-2: 7.62; Min 7: 13.59; Min 8: 0; Min 9: 26.25; Min 10: 12.66 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 25+25 | 0.706 | 0.75106 | 14.3411 |  |  | 14.3411 | 0 | 26.25 | 11.9089
71 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.68 |  | 1.01 | 0.67 |  |  | 1.68 | 0 | 2.63 | 0.95 | 0.95 | открыт | 0.97 | 71 | SS 110/10 Ploski | SS 110/10 Ploski | 2,5+2,5 | 0.4595 | 0.47371 | 2.1537 |  |  | 2.1537 | 0 | 2.63 | 0.47629 | 0.47629 | открыт
72 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 20.85 | [5 empty] | 20.85 | 0 | 21 | 0.15 | 0.15 | available | 0.95 | 72 | SS 110/35/10 Rostov | SS 110/35/10 Rostov | 20+25 | 0 |  | 25.116 |  |  | 25.116 | 0 | 21 | -4.116 | -4.116 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.67 |  | Т-1: 0; Т-2: 1.67; Min 7: 1.67; Min 8: 0; Min 9: 21; Min 10: 19.33 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 20+25 | 0 |  | 2.1475 |  |  | 2.1475 | 0 | 21 | 18.8525
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.18 |  | Т-1: 9.95; Т-2: 9.23; Min 7: 19.18; Min 8: 0; Min 9: 21; Min 10: 1.82 |  | Nom. Capacity LV, МVА | Nom. Capacity LV, МVА | 20+25 | 3.599 | 3.7884 | 22.9684 |  |  | 22.9684 | 0 | 21 | -1.9684
73 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.66 | [5 empty] | 7.66 | 0 | 6.62 | -1.04 | -1.04 | unavailable | 0.94 | 73 | SS 110/35/10 Technical school | SS 110/35/10 Technical school | 6,3+6,3 | 0 |  | 15.4371 |  |  | 15.4371 | 0 | 6.62 | -8.8171 | -8.8171 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.45 |  | Т-1: 4.45; Т-2: 0; Min 7: 4.45; Min 8: 0; Min 9: 6.62; Min 10: 2.17 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 6,3+6,3 | 0 |  | 9.6079 |  |  | 9.6079 | 0 | 6.62 | -2.9879
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.21 |  | Т-1: 1.68; Т-2: 1.53; Min 7: 3.21; Min 8: 0; Min 9: 6.62; Min 10: 3.41 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 6,3+6,3 | 2.462 | 2.6191 | 5.8291 |  |  | 5.8291 | 0 | 6.62 | 0.79085
74 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 22.29 | [5 empty] | 22.29 | 0 | 26.25 | 3.96 | 3.96 | available | 0.93 | 74 | SS 110/35/10 Uglich | SS 110/35/10 Uglich | 25+25 | 0 |  | 38.0194 |  |  | 38.0194 | 0 | 26.25 | -11.7694 | -11.7694 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.04 |  | Т-1: 6.47; Т-2: 11.57; Min 7: 18.04; Min 8: 0; Min 9: 26.25; Min 10: 8.21 |  | Nom. capacidty MV, МVА | Nom. capacidty MV, МVА | 25+25 | 0 |  | 27.4662 |  |  | 27.4662 | 0 | 26.25 | -1.2162
| Nom. capacity LV, МVА | 25+25 |  |  | 4.25 |  | Т-1: 2.34; Т-2: 1.91; Min 7: 4.25; Min 8: 0; Min 9: 26.25; Min 10: 22 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 25+25 | 5.862 | 6.3032 | 10.5532 |  |  | 10.5532 | 0 | 26.25 | 15.6968
75 | SS 110/10 Ustye | 10+10 | 10 | 10 | 3.87 |  | 2.23 | 1.64 | 0.727 | 120 | 3.143 | 0 | 10.5 | 7.357 | 7.357 | открыт | 0.9 | 75 | SS 110/10 Ustye | SS 110/10 Ustye | 10+10 | 0.9489 | 1.0543 | 4.9243 | 0.727 | 120 | 4.1973 | 0 | 10.5 | 6.3027 | 6.3027 | открыт
76 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 2.16 |  | 1.17 | 0.99 | 0.953 | 120 | 1.207 | 0 | 10.5 | 9.293 | 9.293 | открыт | 0.93 | 76 | SS 110/10 Shurskol | SS 110/10 Shurskol | 10+10 | 0.095 | 0.10215 | 2.2622 | 0.953 | 120 | 1.3092 | 0 | 10.5 | 9.1908 | 9.1908 | открыт
77 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 6.84 |  | 3.72 | 3.12 | 0.935 | 120 | 5.905 | 0 | 10.5 | 4.595 | 4.595 | открыт | 0.89 | 77 | SS 110/10 Yur.Sloboda | SS 110/10 Yur.Sloboda | 10+10 | 1.8862 | 2.1193 | 8.9593 | 0.935 | 120 | 8.0243 | 0 | 10.5 | 2.4757 | 2.4757 | открыт
78 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.69 |  | 0.09 | 0.6 |  |  | 0.69 | 0 | 2.63 | 1.94 | 1.94 | открыт | 0.99 | 78 | SS 35/10 Aleshkino | SS 35/10 Aleshkino | 2,5+2,5 | 0.023 | 0.023232 | 0.71323 |  |  | 0.71323 | 0 | 2.63 | 1.9168 | 1.9168 | открыт
79 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.03 |  | 1.03 | 0 |  |  | 1.03 | 0 | 1.68 | 0.65 | 0.65 | available | 0.98 | 79 | SS 35/6 Batki | SS 35/6 Batki | 1,6+1,6 | 0.814 | 0.83061 | 1.8606 |  |  | 1.8606 | 0 | 1.68 | -0.18061 | -0.18061 | unavailable
80 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.19 |  | 0.19 |  | 3.031 | 1 сутки | 0.19 | 0 | 3.031 | 2.841 | 2.841 | открыт | 0.95 | 80 | SS 35/10 Beregovaya | SS 35/10 Beregovaya | 1,6 | 0.057 | 0.06 | 0.25 | 3.031 | 1 сутки | 0.25 | 0 | 3.031 | 2.781 | 2.781 | открыт
81 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.35 |  | 1.12 | 0.23 | 0.242 |  | 1.108 | 0 | 2.63 | 1.522 | 1.522 | открыт | 0.96 | 81 | SS 35/10 Berendeevo | SS 35/10 Berendeevo | 2,5+2,5 | 0.137 | 0.14271 | 1.4927 | 0.242 |  | 1.2507 | 0 | 2.63 | 1.3793 | 1.3793 | открыт
82 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.48 |  | 0.24 | 0.24 | 0.329 | 120 | 0.151 | 0 | 1.68 | 1.529 | 1.529 | открыт | 0.997 | 82 | SS 35/10 Vorzha | SS 35/10 Vorzha | 1,8+1,6 | 0.03 | 0.03009 | 0.51009 | 0.329 | 120 | 0.18109 | 0 | 1.68 | 1.4989 | 1.4989 | открыт
83 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 |  | 0.48 | 0.32 | 0.52 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | открыт | 0.84 | 83 | SS 35/10 Voshchazhnikovo | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.945 | 1.125 | 1.925 | 0.52 | 120 | 1.405 | 0 | 1.68 | 0.275 | 0.275 | открыт
84 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.44 |  | 0.3 | 2.14 |  |  | 2.44 | 0 | 2.63 | 0.19 | 0.19 | available | 0.96 | 84 | SS 35/10 Glebovo | SS 35/10 Glebovo | 2,5+2,5 | 3.4881 | 3.6334 | 6.0734 |  |  | 6.0734 | 0 | 2.63 | -3.4434 | -3.4434 | unavailable
85 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 1.05 |  | 0.57 | 0.48 |  |  | 1.05 | 0 | 2.63 | 1.58 | 1.58 | открыт | 0.91 | 85 | SS 35/10 Gorki | SS 35/10 Gorki | 2,5+2,5 | 0.268 | 0.29451 | 1.3445 |  |  | 1.3445 | 0 | 2.63 | 1.2855 | 1.2855 | открыт
86 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.19 |  | 0.73 | 0.46 |  |  | 1.19 | 0 | 1.68 | 0.49 | 0.49 | открыт | 0.98 | 86 | SS 35/10 Dmitrianovo | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.072 | 0.073469 | 1.2635 |  |  | 1.2635 | 0 | 1.68 | 0.41653 | 0.41653 | открыт
87 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.16 |  | 0.47 | 0.69 |  |  | 1.16 | 0 | 1.68 | 0.52 | 0.52 | открыт | 0.95 | 87 | SS 35/10 Zaozerye | SS 35/10 Zaozerye | 2,5+1,6 | 0.202 | 0.21263 | 1.3726 |  |  | 1.3726 | 0 | 1.68 | 0.30737 | 0.30737 | открыт
88 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.38 |  | 0.95 | 0.43 |  |  | 1.38 | 0 | 2.63 | 1.25 | 1.25 | открыт | 0.94 | 88 | SS 35/10 Ilyinskoe | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.1795 | 0.19096 | 1.571 |  |  | 1.571 | 0 | 2.63 | 1.059 | 1.059 | открыт
89 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.03 |  | 0.68 | 1.35 |  |  | 2.03 | 0 | 6.62 | 4.59 | 4.59 | открыт | 0.96 | 89 | SS 35/10 Kibernetik | SS 35/10 Kibernetik | 6,3+6,3 | 1.245 | 1.2969 | 3.3269 |  |  | 3.3269 | 0 | 6.62 | 3.2931 | 3.2931 | открыт
90 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.34 |  | 0.34 |  | 0.588 | 1 сутки | 0.34 | 0 | 0.588 | 0.248 | 0.248 | открыт | 0.94 | 90 | SS 35/10 Klementyevo | SS 35/10 Klementyevo | 1,6 | 0 | 0 | 0.34 | 0.588 | 1 сутки | 0.34 | 0 | 0.588 | 0.248 | 0.248 | открыт
91 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 2.28 |  | 0.66 | 1.62 | 0.866 | 120 | 1.414 | 0 | 4.2 | 2.786 | 2.786 | available | 0.97 | 91 | SS 35/10 Krasnoe | SS 35/10 Krasnoe | 4,0+4,0 | 3.46 | 3.567 | 5.847 | 0.866 | 120 | 4.981 | 0 | 4.2 | -0.78101 | -0.78101 | unavailable
92 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 |  | 1.23 | 0.4 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.78 | 92 | SS 35/10 Kulakovo | SS 35/10 Kulakovo | 2,5+2,5 | 1.0848 | 1.3908 | 3.0208 |  |  | 3.0208 | 0 | 2.63 | -0.39077 | -0.39077 | unavailable
93 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.29 |  | 1.45 | 0.84 |  |  | 2.29 | 0 | 2.63 | 0.34 | 0.34 | available | 0.99 | 93 | SS 35/6 Kupan | SS 35/6 Kupan | 2,5+2,5 | 1.3663 | 1.3801 | 3.6701 |  |  | 3.6701 | 0 | 2.63 | -1.0401 | -1.0401 | unavailable
94 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.98 |  | 0.57 | 0.41 | 0.537 | 120 | 0.443 | 0 | 2.63 | 2.187 | 2.187 | открыт | 0.96 | 94 | SS 35/10 Markovo | SS 35/10 Markovo | 2,5+2,5 | 0.245 | 0.25521 | 1.2352 | 0.537 | 120 | 0.69821 | 0 | 2.63 | 1.9318 | 1.9318 | открыт
95 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 2.94 |  | 1.33 | 1.61 |  |  | 2.94 | 0 | 4.2 | 1.26 | 1.26 | available | 0.92 | 95 | SS 35/10 Nagorye | SS 35/10 Nagorye | 4,0+4,0 | 3.156 | 3.4304 | 6.3704 |  |  | 6.3704 | 0 | 4.2 | -2.1704 | -2.1704 | unavailable
96 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 1.79 |  | 1.14 | 0.65 | 0.07 | 120 | 1.72 | 0 | 4.2 | 2.48 | 2.48 | открыт | 0.94 | 96 | SS 35/10 Porechye | SS 35/10 Porechye | 4,0+4,0 | 0.309 | 0.32872 | 2.1187 | 0.07 | 120 | 2.0487 | 0 | 4.2 | 2.1513 | 2.1513 | открыт
97 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 0.98 |  | 0.74 | 0.24 |  |  | 0.98 | 0 | 2.63 | 1.65 | 1.65 | открыт | 0.98 | 97 | SS 35/10 Pruzhinino | SS 35/10 Pruzhinino | 2,5+2,5 | 0.36 | 0.36735 | 1.3473 |  |  | 1.3473 | 0 | 2.63 | 1.2827 | 1.2827 | открыт
98 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.35 |  | 0.29 | 0.06 | 0.02 | 120 | 0.33 | 0 | 2.63 | 2.3 | 2.3 | открыт | 0.81 | 98 | SS 35/10 Ramenye | SS 35/10 Ramenye | 2,5+2,5 | 0.131 | 0.16173 | 0.51173 | 0.02 | 120 | 0.49173 | 0 | 2.63 | 2.1383 | 2.1383 | открыт
99 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.36 |  | 0.91 | 0.45 |  |  | 1.36 | 0 | 2.63 | 1.27 | 1.27 | открыт | 0.95 | 99 | SS 35/10 Ryazantsevo | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.169 | 0.17789 | 1.5379 |  |  | 1.5379 | 0 | 2.63 | 1.0921 | 1.0921 | открыт
100 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.35 |  | 0.37 | 0.98 |  |  | 1.35 | 0 | 1.05 | -0.3 | -0.3 | unavailable | 0.98 | 100 | SS 35/10 Saraevo | SS 35/10 Saraevo | 1+1,6 | 0.924 | 0.94286 | 2.2929 |  |  | 2.2929 | 0 | 1.05 | -1.2429 | -1.2429 | unavailable
101 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.08 |  | 0.3 | 0.78 | 0.693 | 120 | 0.387 | 0 | 2.63 | 2.243 | 2.243 | открыт | 0.96 | 101 | SS 35/10 Selifontovo | SS 35/10 Selifontovo | 2,5+2,5 | 1.736 | 1.8083 | 2.8883 | 0.693 | 120 | 2.1953 | 0 | 2.63 | 0.43467 | 0.43467 | открыт
102 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 1.12 |  | 0.32 | 0.8 | 0.07 | 120 | 1.05 | 0 | 4.2 | 3.15 | 3.15 | открыт | 0.96 | 102 | SS 35/10 Semibratovo | SS 35/10 Semibratovo | 4,0+4,0 | 0.318 | 0.33125 | 1.4512 | 0.07 | 120 | 1.3813 | 0 | 4.2 | 2.8188 | 2.8188 | открыт
103 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 |  | 0.03 | 1.08 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 0.96 | 103 | SS 35/10 Skomorokhovo | SS 35/10 Skomorokhovo | 1,6+1,6 | 3.5716 | 3.7204 | 4.8304 |  |  | 4.8304 | 0 | 1.68 | -3.1504 | -3.1504 | unavailable
104 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.16 |  | 1.16 |  | 0.918 | 1 day and night | 1.16 | 0 | 0.918 | -0.242 | -0.242 | unavailable | 0.93 | 104 | SS 35/10 Solomidino | SS 35/10 Solomidino | 2.5 | 2.102 | 2.2602 | 3.4202 | 0.918 | 1 day and night | 3.4202 | 0 | 0.918 | -2.5022 | -2.5022 | unavailable
105 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.69 |  | 0.61 | 1.08 | 0.277 | 120 | 1.413 | 0 | 4.2 | 2.787 | 2.787 | открыт | 0.82 | 105 | SS 35/10 Stavotino | SS 35/10 Stavotino | 4,0+4,0 | 1.6645 | 2.0299 | 3.7199 | 0.277 | 120 | 3.4429 | 0 | 4.2 | 0.75712 | 0.75712 | открыт
106 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 |  | 0.25 | 0.03 | 0.02 | 120 | 0.26 | 0 | 2.63 | 2.37 | 2.37 | открыт | 0.97 | 106 | SS 35/10 Urusovo | SS 35/10 Urusovo | 2,5+2,5 | 0.055 | 0.056701 | 0.3367 | 0.02 | 120 | 0.3167 | 0 | 2.63 | 2.3133 | 2.3133 | открыт
107 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 |  | 0.34 | 1.29 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.93 | 107 | SS 35/10 Filimonovo | SS 35/10 Filimonovo | 2,5+2,5 | 1.792 | 1.9269 | 3.5569 |  |  | 3.5569 | 0 | 2.63 | -0.92688 | -0.92688 | unavailable
108 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 |  | 0.09 | 0.19 |  |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 | открыт | 0.89 | 108 | SS 35/10 Choporovo | SS 35/10 Choporovo | 2,5+2,5 | 0.164 | 0.18427 | 0.46427 |  |  | 0.46427 | 0 | 2.63 | 2.1657 | 2.1657 | открыт
109 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 |  | 0.48 | 0.51 | 0.277 | 120 | 0.713 | 0 | 2.63 | 1.917 | 1.917 | открыт | 0.73 | 109 | SS 35/10 Shchurovo | SS 35/10 Shchurovo | 2,5+2,5 | 0.074 | 0.10137 | 1.0914 | 0.277 | 120 | 0.81437 | 0 | 2.63 | 1.8156 | 1.8156 | открыт
110 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.9 |  | 0.87 | 1.03 |  |  | 1.9 | 0 | 10.5 | 8.6 | 8.6 | открыт | 0.8 | 110 | SS 35/10 Neksans | SS 35/10 Neksans | 10+10 | 6.5 | 8.125 | 10.025 |  |  | 10.025 | 0 | 10.5 | 0.475 | 0.475 | открыт
111 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.67 |  | 5.99 | 4.68 |  |  | 10.67 | 0 | 10.5 | -0.17 | -0.17 | unavailable | 0.92 | 111 | SS 35/6 Pribrezhnaya | SS 35/6 Pribrezhnaya | 10+10 | 0.8258 | 0.89761 | 11.5676 |  |  | 11.5676 | 0 | 10.5 | -1.0676 | -1.0676 | unavailable
112 | SS 110/10 Tishino | 25+25 | 25 | 25 | 20.15 |  | 12.46 | 7.69 |  |  | 20.15 | 0 | 26.25 | 6.1 | 6.1 | открыт | 0.99 | 112 | SS 110/10 Tishino | SS 110/10 Tishino | 25+25 | 0.0938 | 0.094747 | 20.2447 |  |  | 20.2447 | 0 | 26.25 | 6.0053 | 6.0053 | открыт
113 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.6 |  | 0.12 | 1.48 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | открыт | 0.99 | 113 | SS 110/10 Product pipeline | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 0 | 1.6 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | открыт
114 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.16 |  | 0.73 | 1.43 | 0.052 | 120 | 2.108 | 0 | 6.62 | 4.512 | 4.512 | открыт | 0.92 | 114 | SS 110/10 Nekouz | SS 110/10 Nekouz | 6,3+6,3 | 0.042 | 0.045652 | 2.2057 | 0.052 | 120 | 2.1537 | 0 | 6.62 | 4.4663 | 4.4663 | открыт
115 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 16.94 |  | 8.43 | 8.51 |  |  | 16.94 | 0 | 26.25 | 9.31 | 9.31 | открыт | 0.94 | 115 | SS 110/6 Yuzhnaya | SS 110/6 Yuzhnaya | 25+25 | 0.09926 | 0.1056 | 17.0456 |  |  | 17.0456 | 0 | 26.25 | 9.2044 | 9.2044 | открыт
116 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.69 |  | 3.16 | 2.53 | 0.52 | 120 | 5.17 | 0 | 10.5 | 5.33 | 5.33 | открыт | 0.95 | 116 | SS 110/10 Optika | SS 110/10 Optika | 10+10 | 0.513 | 0.54 | 6.23 | 0.52 | 120 | 5.71 | 0 | 10.5 | 4.79 | 4.79 | открыт
117 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 10.43 |  | 5.78 | 4.65 |  |  | 10.43 | 0 | 16.8 | 6.37 | 6.37 | открыт | 0.95 | 117 | SS 110/6 Poligrafmash | SS 110/6 Poligrafmash | 16+16 | 0 | 0 | 10.43 |  |  | 10.43 | 0 | 16.8 | 6.37 | 6.37 | открыт
118 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 34.46 |  | 17.83 | 16.63 |  |  | 34.46 | 0 | 66.15 | 31.69 | 31.69 | открыт | 0.87 | 118 | SS 110/6/6 Zapadnaya | SS 110/6/6 Zapadnaya | 63+63 | 0.28804 | 0.33108 | 34.7911 |  |  | 34.7911 | 0 | 66.15 | 31.3589 | 31.3589 | открыт
119 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 15.13 | [5 empty] | 15.13 | 0 | 42 | 26.87 | 26.87 | открыт | 0.84 | 119 | SS 110/35/6 Volzhskaya | SS 110/35/6 Volzhskaya | 40+40 | 0 | 0 | 15.3169 |  |  | 15.3169 | 0 | 42 | 26.6831 | 26.6831 | открыт
| Nom. capacity MV, МVА | 40+40 |  |  | 0 |  | Т-1: 0; Т-2: 0; Min 8: 0 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 40+40 | 0 | [5 empty] | 0
| Nom. capacity LV, МVА | 40+40 |  |  | 15.13 |  | Т-1: 6.49; Т-2: 8.64; Min 7: 15.13; Min 8: 0; Min 9: 42; Min 10: 26.87 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 40+40 | 0.157 | 0.1869 | 15.3169 |  |  | 15.3169 | 0 | 42 | 26.6831
120 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.04 | [5 empty] | 14.04 | 0 | 16.8 | 2.76 | 2.76 | открыт | 0.96 | 120 | SS 110/35/6 Levoberezhnaya | SS 110/35/6 Levoberezhnaya | 16+16 | 0 |  | 16.02 |  |  | 16.02 | 0 | 16.8 | 0.78004 | 0.78004 | открыт
| Nom. capacity MV, МVА | 16+16 |  |  | 8.62 |  | Т-1: 3.92; Т-2: 4.7; Min 7: 8.62; Min 8: 0; Min 9: 16.8; Min 10: 8.18 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 16+16 | 0 |  | 10.5572 |  |  | 10.5572 | 0 | 16.8 | 6.2428
| Nom. capacity LV, МVА | 16+16 |  |  | 5.42 |  | Т-1: 2.28; Т-2: 3.14; Min 7: 5.42; Min 8: 0; Min 9: 16.8; Min 10: 11.38 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 16+16 | 0.041 | 0.042708 | 5.4627 |  |  | 5.4627 | 0 | 16.8 | 11.3373
121 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.7 | [5 empty] | 1.7 | 0 | 7.88 | 6.18 | 6.18 | открыт | 0.93 | 121 | SS 110/35/10 Pishchalkino | SS 110/35/10 Pishchalkino | 7,5+7,5 | 0 |  | 1.7 |  |  | 1.7 | 0 | 7.88 | 6.18 | 6.18 | открыт
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 0.95 |  | Т-1: 0.95; Т-2: 0; Min 7: 0.95; Min 8: 0; Min 9: 7.88; Min 10: 6.93 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 7,5+7,5 | 0 |  | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.75 |  | Т-1: 0.62; Т-2: 0.13; Min 7: 0.75; Min 8: 0; Min 9: 7.88; Min 10: 7.13 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13
122 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.5 |  | 2.8 | 2.7 |  |  | 5.5 | 0 | 10.5 | 5 | 5 | открыт | 0.93 | 122 | SS 110/6 Dock yard | SS 110/6 Dock yard | 10+10 | 0.187 | 0.20108 | 5.7011 |  |  | 5.7011 | 0 | 10.5 | 4.7989 | 4.7989 | открыт
123 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.62 |  | 2.97 | 0.65 |  |  | 3.62 | 0 | 6.62 | 3 | 3 | открыт | 0.96 | 123 | SS 110/6 Selekhovo | SS 110/6 Selekhovo | 6,3+6,3 | 0.78 | 0.8125 | 4.4325 |  |  | 4.4325 | 0 | 6.62 | 2.1875 | 2.1875 | открыт
124 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.29 |  | 1.32 | 0.97 |  |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | открыт | 0.91 | 124 | SS 35/6 Kamenniki | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 0.16374 | 2.4537 |  |  | 2.4537 | 0 | 4.2 | 1.7463 | 1.7463 | открыт
125 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.6 |  | 0.44 | 0.16 |  |  | 0.6 | 0 | 1.68 | 1.08 | 1.08 | открыт | 0.94 | 125 | SS 35/10 Shashkovo | SS 35/10 Shashkovo | 1,6+1,6 | 0.291 | 0.30957 | 0.90957 |  |  | 0.90957 | 0 | 1.68 | 0.77043 | 0.77043 | открыт
126 | SS 110/6 Veretye | 25+25 | 25 | 25 | 17.82 |  | 9.16 | 8.66 |  |  | 17.82 | 0 | 26.25 | 8.43 | 8.43 | открыт | 0.92 | 126 | SS 110/6 Veretye | SS 110/6 Veretye | 25+25 | 0.5215 | 0.56685 | 18.3868 |  |  | 18.3868 | 0 | 26.25 | 7.8632 | 7.8632 | открыт
127 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.29 |  | 1.5 | 0.79 | 0.52 | 120 | 1.77 | 0 | 4.2 | 2.43 | 2.43 | available | 0.96 | 127 | SS 35/10 Nikolo-Korma | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.5808 | 2.6883 | 4.9783 | 0.52 | 120 | 4.4583 | 0 | 4.2 | -0.25833 | -0.25833 | unavailable
128 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.26 |  | 0.7 | 0.56 | 0.035 | 120 | 1.225 | 0 | 2.63 | 1.405 | 1.405 | открыт | 0.94 | 128 | SS 35/10 Arefino | SS 35/10 Arefino | 2,5+2,5 | 0.113 | 0.12021 | 1.3802 | 0.035 | 120 | 1.3452 | 0 | 2.63 | 1.2848 | 1.2848 | открыт
129 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.72 |  | 0.07 | 0.65 |  |  | 0.72 | 0 | 1.68 | 0.96 | 0.96 | открыт | 0.92 | 129 | SS 35/10 Knyazevo | SS 35/10 Knyazevo | 1,6+2,5 | 0.162 | 0.17609 | 0.89609 |  |  | 0.89609 | 0 | 1.68 | 0.78391 | 0.78391 | открыт
130 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.55 |  | 0.31 | 0.24 | 0.242 | 120 | 0.308 | 0 | 1.68 | 1.372 | 1.372 | открыт | 0.99 | 130 | SS 35/10 Pokrov | SS 35/10 Pokrov | 1,6+1,6 | 0.019 | 0.019192 | 0.56919 | 0.242 | 120 | 0.32719 | 0 | 1.68 | 1.3528 | 1.3528 | открыт
131 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 |  | 0.61 | 0.24 | 0.017 | 120 | 0.833 | 0 | 2.63 | 1.797 | 1.797 | открыт | 0.85 | 131 | SS 35/10 Anikovo | SS 35/10 Anikovo | 2,5+2,5 | 0.021 | 0.024706 | 0.87471 | 0.017 | 120 | 0.85771 | 0 | 2.63 | 1.7723 | 1.7723 | открыт
132 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 0.86 |  | 0.54 | 0.32 |  |  | 0.86 | 0 | 2.63 | 1.77 | 1.77 | открыт | 0.91 | 132 | SS 35/10 Novoe selo | SS 35/10 Novoe selo | 2,5+2,5 | 0.536 | 0.58901 | 1.449 |  |  | 1.449 | 0 | 2.63 | 1.181 | 1.181 | открыт
133 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 5.63 |  | 3.26 | 2.37 |  |  | 5.63 | 0 | 6.62 | 0.99 | 0.99 | открыт | 0.95 | 133 | SS 35/10 Bolshoe selo | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.9165 | 0.96474 | 6.5947 |  |  | 6.5947 | 0 | 6.62 | 0.025263 | 0.025263 | открыт
134 | SS 35/10 Breytovo | 6,3+6,3 | 6.3 | 6.3 | 4.34 |  | 2.01 | 2.33 |  |  | 4.34 | 0 | 6.62 | 2.28 | 2.28 | открыт | 0.95 | 134 | SS 35/10 Breytovo | SS 35/10 Breytovo | 6,3+6,3 | 1.191 | 1.2537 | 5.5937 |  |  | 5.5937 | 0 | 6.62 | 1.0263 | 1.0263 | открыт
135 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 |  | 0.16 | 0.52 | 0.208 | 120 | 0.472 | 0 | 1.68 | 1.208 | 1.208 | открыт | 0.94 | 135 | SS 35/10 Stanilovo | SS 35/10 Stanilovo | 1,6+1,6 | 0.018 | 0.019149 | 0.69915 | 0.208 | 120 | 0.49115 | 0 | 1.68 | 1.1889 | 1.1889 | открыт
136 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 1.01 |  | 0.31 | 0.7 | 0.173 | 120 | 0.837 | 0 | 2.63 | 1.793 | 1.793 | открыт | 0.92 | 136 | SS 35/10 Znamovo | SS 35/10 Znamovo | 2,5+2,5 | 0.045 | 0.048913 | 1.0589 | 0.173 | 120 | 0.88591 | 0 | 2.63 | 1.7441 | 1.7441 | открыт
137 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 1.14 |  | 0.63 | 0.51 |  |  | 1.14 | 0 | 2.63 | 1.49 | 1.49 | открыт | 0.94 | 137 | SS 35/10 Rozhdestvenno | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.185 | 0.19681 | 1.3368 |  |  | 1.3368 | 0 | 2.63 | 1.2932 | 1.2932 | открыт
138 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.55 |  | 0.25 | 0.3 |  |  | 0.55 | 0 | 2.63 | 2.08 | 2.08 | открыт | 0.99 | 138 | SS 35/10 Zapolye | SS 35/10 Zapolye | 2,5+2,5 | 0.177 | 0.17879 | 0.72879 |  |  | 0.72879 | 0 | 2.63 | 1.9012 | 1.9012 | открыт
139 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.25 |  | 0.55 | 0.7 | 0.329 | 120 | 0.921 | 0 | 1.68 | 0.759 | 0.759 | открыт | 0.93 | 139 | SS 35/10 Tikhmenevo | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.177 | 0.19032 | 1.4403 | 0.329 | 120 | 1.1113 | 0 | 1.68 | 0.56868 | 0.56868 | открыт
140 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.24 |  | 0.17 | 0.07 | 0.052 | 120 | 0.188 | 0 | 1.68 | 1.492 | 1.492 | открыт | 0.64 | 140 | SS 35/10 Latskoe | SS 35/10 Latskoe | 1,6+2,5 | 0.007 | 0.010937 | 0.25094 | 0.052 | 120 | 0.19894 | 0 | 1.68 | 1.4811 | 1.4811 | открыт
141 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.21 |  | 0.81 | 0.4 | 0.156 | 120 | 1.054 | 0 | 2.63 | 1.576 | 1.576 | открыт | 0.93 | 141 | SS 35/10 Borok | SS 35/10 Borok | 2,5+4,0 | 0.279 | 0.3 | 1.51 | 0.156 | 120 | 1.354 | 0 | 2.63 | 1.276 | 1.276 | открыт
142 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.57 |  | 2.28 | 1.29 |  |  | 3.57 | 0 | 6.62 | 3.05 | 3.05 | открыт | 0.94 | 142 | SS 35/10 Myshkin | SS 35/10 Myshkin | 6,3+6,3 | 1.599 | 1.7011 | 5.2711 |  |  | 5.2711 | 0 | 6.62 | 1.3489 | 1.3489 | открыт
143 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 1.9 |  | 0.91 | 0.99 |  |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | открыт | 0.95 | 143 | SS 110/10 Volga | SS 110/10 Volga | 5,6+6,3 | 0.19 | 0.2 | 2.1 |  |  | 2.1 | 0 | 5.88 | 3.78 | 3.78 | открыт
144 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 1.35 |  | 0.67 | 0.68 | 0.104 | 120 | 1.246 | 0 | 2.63 | 1.384 | 1.384 | открыт | 0.95 | 144 | SS 35/10 Krasnaya Gorka | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.8677 | 0.91337 | 2.2634 | 0.104 | 120 | 2.1594 | 0 | 2.63 | 0.47063 | 0.47063 | открыт
145 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 22.48 | [5 empty] | 22.48 | 0 | 26.25 | 3.77 | 3.77 | открыт | 0.79 | 145 | SS 110/35/6 Vostochnaya | SS 110/35/6 Vostochnaya | 25+25 | 0 | 0 | 25.4207 |  |  | 25.4207 | 0 | 26.25 | 0.82935 | 0.82935 | открыт
| Nom. capacity MV, МVА | 25+25 |  |  | 4.51 |  | Т-1: 4.51; Т-2: 0; Min 7: 4.51; Min 8: 0; Min 9: 26.25; Min 10: 21.74 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 25+25 | 0 |  | 6.9463 |  |  | 6.9463 | 0 | 26.25 | 19.3037
| Nom. capacity LV, МVА | 25+25 |  |  | 17.97 |  | Т-1: 10.14; Т-2: 7.83; Min 7: 17.97; Min 8: 0; Min 9: 26.25; Min 10: 8.28 |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 25+25 | 0.39842 | 0.50433 | 18.4743 |  |  | 18.4743 | 0 | 26.25 | 7.7757
146 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 7.7 |  |  |  | 1.126 | 120 | 6.574 | 0 | 10.5 | 3.926 | 3.926 | открыт | 0.93 | 146 | SS 110/35/10 Zalesye | SS 110/35/10 Zalesye | 10+10 | 0 |  | 8.2339 | 1.126 | 120 | 7.1079 | 0 | 10.5 | 3.3921 | 3.3921 | открыт
| Nom. capacity MV, МVА | 10+10 |  |  | 1.16 |  | Т-1: 0.32; Т-2: 0.84; Min 7: 1.16; Min 8: 0; Min 9: 10.5; Min 10: 9.34 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 1.2089 |  |  | 1.2089 | 0 | 10.5 | 9.2911
| Nom. capacity LV, МVА | 10+10 |  |  | 6.54 |  | 3.01 | 3.53 | 1.126 | 120 | 5.414 | 0 | 10.5 | 5.086 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 0.451 | 0.48495 | 7.0249 | 1.126 | 120 | 5.8989 | 0 | 10.5 | 4.6011
147 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.39 |  | 1.64 | 0.75 |  |  | 2.39 | 0 | 6.62 | 4.23 | 4.23 | открыт | 0.88 | 147 | SS 110/10 Lugovaya | SS 110/10 Lugovaya | 6,3+6,3 | 0.3585 | 0.40739 | 2.7974 |  |  | 2.7974 | 0 | 6.62 | 3.8226 | 3.8226 | открыт
148 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 8.8 |  |  |  | 1.057 | 120 | 7.743 | 0 | 10.5 | 2.757 | 2.757 | открыт | 0.92 | 148 | SS 110/35/10 Lom | SS 110/35/10 Lom | 10+10 | 0 |  | 11.4884 | 1.057 | 120 | 10.4314 | 0 | 10.5 | 0.068627 | 0.068627 | открыт
| Nom. capacity MV, МVА | 10+10 |  |  | 6.73 |  | Т-1: 4.25; Т-2: 2.48; Min 7: 6.73; Min 8: 0; Min 9: 10.5; Min 10: 3.77 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 8.7492 |  |  | 8.7492 | 0 | 10.5 | 1.7508
| Nom. capacity LV, МVА | 10+10 |  |  | 2.07 |  | 1.65 | 0.42 | 1.057 | 120 | 1.013 | 0 | 10.5 | 9.487 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 0.6156 | 0.66913 | 2.7391 | 1.057 | 120 | 1.6821 | 0 | 10.5 | 8.8179
149 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.66 |  | 0.43 | 0.23 |  |  | 0.66 | 0 | 1.68 | 1.02 | 1.02 | открыт | 0.91 | 149 | SS 35/10 Varegovo | SS 35/10 Varegovo | 1,6+2,5 | 0.4236 | 0.46549 | 1.1255 |  |  | 1.1255 | 0 | 1.68 | 0.55451 | 0.55451 | открыт
150 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 6.79 |  |  |  | 0.208 | 120 | 6.582 | 0 | 10.5 | 3.918 | 3.918 | открыт | 0.97 | 150 | SS 110/35/10 Shestikhino | SS 110/35/10 Shestikhino | 10+10 | 0 |  | 9.4924 | 0.208 | 120 | 9.2844 | 0 | 10.5 | 1.2156 | 1.2156 | открыт
| Nom. capacity MV, МVА | 10+10 |  |  | 6.24 |  | Т-1: 1.98; Т-2: 4.26; Min 7: 6.24; Min 8: 0; Min 9: 10.5; Min 10: 4.26 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10+10 | 0 |  | 8.8022 |  |  | 8.8022 | 0 | 10.5 | 1.6978
| Nom. capacity LV, МVА | 10+10 |  |  | 0.55 |  | 0.27 | 0.28 | 0.208 | 120 | 0.342 | 0 | 10.5 | 10.158 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10+10 | 0.136 | 0.14021 | 0.69021 | 0.208 | 120 | 0.48221 | 0 | 10.5 | 10.0178
151 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | 2.53 |  | Min 8: 0; Min 11: 1.482; Min 12: открыт; Min 13: 0.94 | 151 | SS 110/35/10 Kryukovo | SS 110/35/10 Kryukovo | 6.3 | 0 |  | 3.4146 |  |  |  | 0 |  |  | 1.448 | открыт
| Nom. capacidty MV, МVА | 6.3 |  |  | 2.28 |  | Т-1: 2.28; Min 8: 0 |  | Nom. capacidty MV, МVА | Nom. capacidty MV, МVА | 6.3 | 0 |  | 3.1305 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.25 |  | 0.25 |  | 1.732 | 1 сутки | 0.25 | 0 | 1.732 | 1.482 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 6.3 | 0.032 | 0.034043 | 0.28404 | 1.732 | 1 сутки | 0.28404 | 0 | 1.732 | 1.448
152 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.56 |  | 0.56 |  | 1.455 | 1 сутки | 0.56 | 0 | 1.455 | 0.895 | 0.895 | открыт | 0.96 | 152 | SS 35/10 Beloe | SS 35/10 Beloe | 2.5 | 0.037 | 0.038542 | 0.59854 | 1.455 | 1 сутки | 0.59854 | 0 | 1.455 | 0.85646 | 0.85646 | открыт
153 | SS 110/35/10 Glebovo | 10 | 10 |  | 5.5 |  | Min 8: 0; Min 11: -2.276; Min 12: unavailable; Min 13: 0.96 | 153 | SS 110/35/10 Glebovo | SS 110/35/10 Glebovo | 10 | 0 |  | 8.6236 |  |  |  | 0 |  |  | -3.8651 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | 2.41 |  | Т-1: 2.41; Min 8: 0 |  | Nom. capacity MV, МVА | Nom. capacity MV, МVА | 10 | 0 |  | 3.9445 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.09 |  | 3.09 |  | 0.814 | 1 сутки | 3.09 | 0 | 0.814 | -2.276 |  |  |  |  | Nom. capacity LV, МVА | Nom. capacity LV, МVА | 10 | 1.5255 | 1.5891 | 4.6791 | 0.814 | 1 сутки | 4.6791 | 0 | 0.814 | -3.8651
154 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.48 |  | 1.03 | 0.45 |  |  | 1.48 | 0 | 1.89 | 0.41 | 0.41 | открыт | 0.85 | 154 | SS 35/6 Pesochnoye | SS 35/6 Pesochnoye | 1,8+1,8 | 0.026 | 0.030588 | 1.5106 |  |  | 1.5106 | 0 | 1.89 | 0.37941 | 0.37941 | открыт
155 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.52 |  | 0.15 | 0.37 | 0.035 |  | 0.485 | 0 | 2.63 | 2.145 | 2.145 | открыт | 0.98 | 155 | SS 35/10 Demino | SS 35/10 Demino | 2,5+2,5 | 0.003 | 0.0030612 | 0.52306 | 0.035 |  | 0.48806 | 0 | 2.63 | 2.1419 | 2.1419 | открыт
156 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 17.89 |  | 17.05 | 0.84 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26 | открыт | 0.999 | 156 | SS 110/6 KS-18 | SS 110/6 KS-18 | 63+63 | 0 | 0 | 17.89 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26 | открыт
157 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.25 |  | 0.25 |  | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable | 1 | 157 | SS 35/6 Makeikha | SS 35/6 Makeikha | 1.6 | 0 | 0 | 0.25 | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable
158 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 0.87 |  | 0.87 |  | 1.143 | 1 сутки | 0.87 | 0 | 1.143 | 0.273 | 0.273 | открыт | 0.94 | 158 | SS 35/10 Ermakovo | SS 35/10 Ermakovo | 1.6 | 0.21 | 0.2234 | 1.0934 | 1.143 | 1 сутки | 1.0934 | 0 | 1.143 | 0.049596 | 0.049596 | открыт
159 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.78 |  | 0.78 |  | 0.814 | 1 day and night | 0.78 | 0 | 0.814 | 0.034 | 0.034 | available | 0.93 | 159 | SS 35/10 Milyushino | SS 35/10 Milyushino | 1.6 | 1.152 | 1.2387 | 2.0187 | 0.814 | 1 day and night | 2.0187 | 0 | 0.814 | -1.2047 | -1.2047 | unavailable
160 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.62 |  | 0.62 |  | 0.606 | 1 day and night | 0.62 | 0 | 0.606 | -0.014 | -0.014 | unavailable | 0.87 | 160 | SS 35/10 Sutka | SS 35/10 Sutka | 2.5 | 0.032 | 0.036782 | 0.65678 | 0.606 | 1 day and night | 0.65678 | 0 | 0.606 | -0.050782 | -0.050782 | unavailable
161 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.58 |  | 0.58 |  | 0.572 | 1 day and night | 0.58 | 0 | 0.572 | -0.008 | -0.008 | unavailable | 0.83 | 161 | SS 35/10 Sit | SS 35/10 Sit | 1.6 | 0.438 | 0.52771 | 1.1077 | 0.572 | 1 day and night | 1.1077 | 0 | 0.572 | -0.53571 | -0.53571 | unavailable
162 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 0.82 |  | 0.82 |  | 0.901 | 1 day and night | 0.82 | 0 | 0.901 | 0.081 | 0.081 | available | 0.95 | 162 | SS 35/10 Gorelovo | SS 35/10 Gorelovo | 1.6 | 0.643 | 0.67684 | 1.4968 | 0.901 | 1 day and night | 1.4968 | 0 | 0.901 | -0.59584 | -0.59584 | unavailable
163 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.75 |  | 0.75 |  | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable | 0.91 | 163 | SS 35/6 Pishchalkino | SS 35/6 Pishchalkino | 1.6 | 0 | 0 | 0.75 | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable
164 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 |  | 0.02 |  | 0 | 1 day and night | 0.02 | 0 | 0 | -0.02 | -0.02 | unavailable | 0.89 | 164 | SS 35/6 Varegovo | SS 35/6 Varegovo | 1.6 | 0.01 | 0.011236 | 0.031236 | 0 | 1 day and night | 0.031236 | 0 | 0 | -0.031236 | -0.031236 | unavailable
165 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.39 |  | 1.39 |  | 1.351 | 1 day and night | 1.39 | 0 | 1.351 | -0.039 | -0.039 | unavailable | 0.94 | 165 | SS 35/10 Levoberezhnaya | SS 35/10 Levoberezhnaya | 4 | 1.926 | 2.0489 | 3.4389 | 1.351 | 1 day and night | 3.4389 | 0 | 1.351 | -2.0879 | -2.0879 | unavailable
166 | SS 110/10 Depot | 16 | 16 |  | 4.34 |  | 4.34 |  | 4.34 | 1 сутки | 4.34 | 0 | 4.34 | 0 | 0 | открыт | 0.98 | 166 | SS 110/10 Depot | SS 110/10 Depot | 16 | 0 | 0 | 4.34 | 4.34 | 1 сутки | 4.34 | 0 | 4.34 | 0 | 0
| Total: | 2914.7 | 1489.4 | 1425.3 | 873.93 | [13 empty] | Total: | Total: | 2914.7 |  |  | 1063.9438
| deficit | [5 empty] | Min 11: 16.409 |  | deficit | deficit | [10 empty] | 38.6262
| proficit | [5 empty] | Min 11: 671.799 |  | proficit | proficit | [10 empty] | 365.0215
[19 empty] | SS 110/6 Kinoplenka* |  | When referring to the power per the issued Technical Specifications the output power of 8780 kW is not specified, as no average power value (there is no clarity on the power flows).
-126.39
Deputy Director for Technical
Issues - Chief Engineer
Note on H195: Т2
Note on H215: Т3
Note on H216: Т1
Note on H217: Т3
Note on H218: Т3
Note on I195: Т3

## Total current deficit Winter
The list of closed supply centers of IDGC of Centre according to winter load measurements in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class | [5 empty] | Current deficit, MVA
Yarenergo
1 | SS 35/10 Mikhaylovsky | 6.3 |  |  |  |  | -1.24
2 | SS 35/10 Wave | 4,0+2,5 |  |  |  |  | -0.01
3 | SS 35/6 Zavolzhsky | 10+10 |  |  |  |  | -0.54
4 | SS 110/35/6 Pavlovsk | 20+25 |  |  |  |  | -4.52
5 | SS 35/6 Kelnot | 4,0 |  |  |  |  | -0.16
6 | SS 110/6 Film | 6,3+10 |  |  |  |  | -3.85
7 | SS 110/35/10 Niles | 6,3+6,3 |  |  |  |  | -0.98
8 | SS 110/35/10 Technical school | 6,3+6,3 |  |  |  |  | -1.04
9 | SS 35/10 Sarayevo | 1+1,6 |  |  |  |  | -0.3
10 | SS 35/10 Solomidino | 2.5 | 3.48 | 3.48 | 0 | 2.63 | -0.242
11 | SS 35/6 Coastal | 10+10 | 11.67 | 11.67 | 0 | 10.5 | -0.17
12 | SS 110/35/10 Glebovo | 10 | 25.25 | 25.25 | 0 | 21 | -2.276
13 | SS 35/6 Makeiha | 1.6 | 45.91 | 45.91 | 0 | 42 | -0.25
14 | SS 35/10 Sutka | 2.5 | 6.83 | 6.83 | 0 | 6.62 | -0.014
15 | SS 35/10 Sit | 1.6 |  |  |  |  | -0.008
16 | SS 35/6 Pishchalkino | 1.6 |  |  |  |  | -0.75
17 | SS 35/6 Varegovo | 1.6 |  |  |  |  | -0.02
18 | SS 35/10 Left-bank | 4 |  |  |  |  | -0.039
Total current deficit (winter) | [6 empty] | 16.409
Supply Centers, which are not taken into account due to their insignificant load

## Total expected deficit Winter
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit, MVA | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Yarenergo
1 | SS 35/10 Mihajlovsky | 6.3 |  | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -1.2431 | unavailable
2 | SS 35/10 Shirine | 4 | 0.2 | 3.26 |  |  | 3.26 | 0 | 2.63 | -0.63 | -0.19289 | unavailable
3 | SS 110/35/10 Abbakumtsevo | 10+10 | 1.8815 | 12.1915 |  |  | 12.1915 | 0 | 10.5 | -1.6915 | -11.7722 | unavailable
4 | SS 35/10 Vatolino | 4,0+4,0 | 4.6946 | 42.2246 |  |  | 42.2246 | 0 | 42 | -0.22459 | -5.1181 | unavailable
5 | SS 35/10 Wave | 4,0+2,5 | 0.432 | 12.102 |  |  | 12.102 | 0 | 10.5 | -1.602 | -0.01 | unavailable
6 | SS 35/10 Guzitsino | 4,0+4,0 | 8.5515 | 25.2515 |  |  | 25.2515 | 0 | 21 | -4.2515 | -3.1753 | unavailable
7 | SS 35/10 Dorozhaevo | 1,6+1,6 | Мин. 12: -1.4352; Мин. 13: unavailable
8 | SS 35/6 Zavolzhsky | 10+10 | Мин. 12: -0.71714; Мин. 13: unavailable
9 | SS 35/10 Kurba | 2,5+2,5 | Мин. 12: -0.19404; Мин. 13: unavailable
10 | SS 35/10 Modelovo-2 | 6,3+6,3 | Мин. 12: -3.9702; Мин. 13: unavailable
11 | SS 110/35/6 Pavlovsk | 20+25 | Мин. 12: -4.9637; Мин. 13: unavailable
12 | SS 35/10 Dispensary | 2,5+2,5 | Мин. 12: -0.80535; Мин. 13: unavailable
13 | SS 35/6 Chebakovo | 2,5+2,5 | Мин. 12: -0.7896; Мин. 13: unavailable
14 | SS 110/35/10 Borisogleb | 16+10 | 2.027 | 3.237 | 0.39 | 120 | 2.847 | 0 | 2.63 | -0.217 | -3.1819 | unavailable
15 | SS 110/6 Film | 6,3+10 | 0.01 | 6.84 |  |  | 6.84 | 0 | 6.62 | -0.22 | -6.8862 | unavailable
16 | SS 110/35/10 Niles | 6,3+6,3 | 23.7523 | 39.9523 |  |  | 39.9523 | 0 | 26.25 | -13.7023 | -21.9616 | unavailable
17 | SS 110/35/6 Pereslavl | 25+25 | 0.587 | 10.157 |  |  | 10.157 | 0 | 6.62 | -3.537 | -11.6244 | unavailable
18 | SS 110/35/10 Rostov | 20+25 | 7.5755 | 9.3555 | 0.37 | 120 | 8.9855 | 0 | 6.62 | -2.3655 | -4.12 | unavailable
19 | SS 110/35/10 Technical school | 6,3+6,3 | 14.4054 | 27.9154 |  |  | 27.9154 | 0 | 26.25 | -1.6654 | -8.82 | unavailable
20 | SS 110/35/10 Uglich | 25+25 | 3.4781 | 21.7981 |  |  | 21.7981 | 0 | 21 | -0.7981 | -11.7694 | unavailable
21 | SS 35/6 Fathers | 1,6+1,6 | 25.538 | 30.568 |  |  | 30.568 | 0 | 26.25 | -4.318 | -0.18061 | unavailable
22 | SS 35/10 Glebovo | 2,5+2,5 | 1.645 | 4.405 |  |  | 4.405 | 0 | 2.63 | -1.775 | -3.4434 | unavailable
23 | SS 35/10 Kulakovo | 2,5+2,5 | 0.273 | 2.723 |  |  | 2.723 | 0 | 2.63 | -0.093 | -0.39077 | unavailable
24 | SS 35/6 Kupan | 2,5+2,5 | 2.193 | 3.283 | 0.3 | 120 | 2.983 | 0 | 2.63 | -0.353 | -1.0401 | unavailable
25 | SS 35/10 Uplands | 4,0+4,0 | Мин. 12: -2.1704; Мин. 13: unavailable
26 | SS 35/10 Sarajevo | 1+1,6 | Мин. 12: -1.2429; Мин. 13: unavailable
27 | SS 35/10 Skomorohovo | 1,6+1,6 | Мин. 12: -3.1504; Мин. 13: unavailable
28 | SS 35/10 Solomidino | 2.5 | Мин. 12: -2.5022; Мин. 13: unavailable
29 | SS 35/6 Coastal | 10+10 | Мин. 12: -1.0676; Мин. 13: unavailable
30 | SS 110/35/10 Glebovo | 10 | Мин. 12: -3.8651; Мин. 13: unavailable
31 | SS 35/6 Makeiha | 1.6 | Мин. 12: -0.25; Мин. 13: unavailable
32 | SS 35/10 Miljushino | 1.6 | Мин. 12: -1.2047; Мин. 13: unavailable
33 | SS 35/10 Sutka | 2.5 | Мин. 12: -0.050782; Мин. 13: unavailable
34 | SS 35/10 Sit | 1.6 | Мин. 12: -0.53571; Мин. 13: unavailable
35 | SS 35/10 Gorelovo | 1.6 | Мин. 12: -0.59584; Мин. 13: unavailable
36 | SS 35/6 Pishchalkino | 1.6 | Мин. 12: -0.75; Мин. 13: unavailable
37 | SS 35/6 Varegovo | 1.6 | Мин. 12: -0.031236; Мин. 13: unavailable
38 | SS 35/10 Left-bank | 4 | Мин. 12: -2.0879; Мин. 13: unavailable
39 | SS 35/10 Krasnoye | 4,0+4,0 | Мин. 12: -0.78101; Мин. 13: unavailable
40 | SS 35/10 Filimonovo | 2,5+2,5 | Мин. 12: -0.92688; Мин. 13: unavailable
41 | SS 35/10 Ananyino | 2,5+2,5 | Мин. 12: -0.71897; Мин. 13: unavailable
42 | SS 35/6 Kelnot | 4,0 | Мин. 12: -0.16; Мин. 13: unavailable
43 | SS35/10Nikolo-Korma | 4,0+4,0 | Мин. 12: -0.25833; Мин. 13: unavailable
| Total: |  | Мин. 12: -130.1553