## Yarenergo
[13 empty] | table 1 | [13 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | available | 1 | SS 35/10 Matveevo | 1.6 | 0.025 | 0.285 | 0.779 | 1 day and night | 0.285 | 0 | 0.779 | 0.494 | 0.494 | available
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | available | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | available
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | unavailable | 3 | SS 35/10 Shirinye | 2.5 | 0.371 | 2.521 | 1.68 | 1 day and night | 2.521 | 0 | 1.68 | -0.841 | -0.841 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | available | 4 | SS 110/10 Pokrov | 2.5 | 0.048 | 0.318 | 1.282 | 1 day and night | 0.318 | 0 | 1.282 | 0.964 | 0.964 | available
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | available | 5 | SS 35/10 Obnora | 1.6 | 0.075 | 0.275 | 1.212 | 1 day and night | 0.275 | 0 | 1.212 | 0.937 | 0.937 | available
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | available | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 25.0651 |  |  | 25.0651 | 0 | 10.5 | -14.5651 | -14.5651 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 19.4897 |  |  | 19.4897 | 0 | 10.5 | -8.9896
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 3.6055 | 5.5755 |  |  | 5.5755 | 0 | 10.5 | 4.9245
7 | SS 35/10 Ananyino | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 2.625 | 1.315 | 1.315 | available | 7 | SS 35/10 Ananyino | 2,5+2,5 | 1.245 | 2.555 |  |  | 2.555 | 0 | 2.625 | 0.07 | 0.07 | available
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | available | 8 | SS 110/10/10 Bragino | 40+40 | 4.224 | 39.134 | 2.338 | 120 | 36.796 | 0 | 42 | 5.204 | 5.204 | available
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | available | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 1.2725 | 3.3025 | 0.554 | 120 | 2.7485 | 0 | 4.2 | 1.4515 | 1.4515 | available
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | available | 10 | SS 35/10 Vatolino | 4,0+4,0 | 4.867 | 8.287 |  |  | 8.287 | 0 | 4.2 | -4.087 | -4.087 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | available | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.091258 | 4.2113 |  |  | 4.2113 | 0 | 6.62 | 2.4087 | 2.4087 | available
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | available | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.194 | 2.164 |  |  | 2.164 | 0 | 4.2 | 2.036 | 2.036 | available
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | available | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.077 | 0.787 |  |  | 0.787 | 0 | 1.68 | 0.893 | 0.893 | available
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | available | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 3.3104 | 4.4804 |  |  | 4.4804 | 0 | 4.2 | -0.2804 | -0.2804 | unavailable
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | available | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | available
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | available | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.384 | 2.594 | 0.139 | 120 | 2.455 | 0 | 2.63 | 0.175 | 0.175 | available
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | available | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.143 | 0.803 | 0.329 | 120 | 0.474 | 0 | 2.63 | 2.156 | 2.156 | available
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | available | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 1.0985 | 3.7085 | 0.312 | 120 | 3.3965 | 0 | 4.2 | 0.8035 | 0.8035 | available
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | available | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 5.9579 | 8.8279 | 0.866 | 120 | 7.9619 | 0 | 4.2 | -3.7619 | -3.7619 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | available | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0.011 | 2.571 |  |  | 2.571 | 0 | 6.62 | 4.049 | 4.049 | available
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | available | 21 | SS 110/6 Depo | 16+16 | 2.7285 | 9.7985 |  |  | 9.7985 | 0 | 16.8 | 7.0015 | 7.0015 | available
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | available | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 2.144 | 3.734 | 1.039 | 120 | 2.695 | 0 | 1.68 | -1.015 | -1.015 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | available | 23 | SS 110/10 Druzhba | 16+16 | 0.9493 | 6.4593 | 1.932 | 120 | 4.5273 | 0 | 16.8 | 12.2727 | 12.2727 | available
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | available | 24 | SS 35/10 Dubki | 6,3+6,3 | 1.5445 | 6.4145 | 1.386 | 120 | 5.0285 | 0 | 6.62 | 1.5915 | 1.5915 | available
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | available | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.6005 | 1.8305 |  |  | 1.8305 | 0 | 2.63 | 0.7995 | 0.7995 | available
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | available | 26 | SS 35/6 Zavolzhskaya | 10+10 | 0.7921 | 10.5121 |  |  | 10.5121 | 0 | 10.5 | -0.012098 | -0.012098 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | available | 27 | SS 110/6/6 Institutskaya | 40+40 | 2.5747 | 34.4047 |  |  | 34.4047 | 0 | 42 | 7.5953 | 7.5953 | available
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | available | 28 | SS 35/10 Koza | 1,6+1,6 | 0.078 | 0.378 | 0.052 | 120 | 0.326 | 0 | 1.68 | 1.354 | 1.354 | available
29 | SS 110/35/6 Konstantinovo | 15+16 | 15 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 15.75 | 5.211 | 5.211 | available | 29 | SS 110/35/6 Konstantinovo | 15+16 |  | 13.7762 | 0.021 | 120 | 13.7553 | 0 | 15.75 | 1.9948 | 1.9948 | available
| Nom. capacity MV, МVА | 15+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 15.75 | 8.28 |  |  |  | Nom. capacity MV, МVА | 15+16 |  | 10.0922 |  |  | 10.0922 | 0 | 15.75 | 5.6578
| Nom. capacity LV, МVА | 15+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 15.75 | 12.681 |  |  |  | Nom. capacity LV, МVА | 15+16 | 0.594 | 3.684 | 0.021 | 120 | 3.663 | 0 | 15.75 | 12.087
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | available | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.58 | 3.06 | 0.242 | 120 | 2.818 | 0 | 2.63 | -0.188 | -0.188 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | available | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.993 | 9.073 | 1.212 | 120 | 7.861 | 0 | 10.5 | 2.639 | 2.639 | available
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | available | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 8.1987 | 14.0487 | 2.338 | 120 | 11.7107 | 0 | 6.62 | -5.0907 | -5.0907 | unavailable
33 | SS 35/10 Nekrasovo | 16+16 | 16 | 16 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 16.8 | 5.63 | 5.63 | available | 33 | SS 35/10 Nekrasovo | 16+16 | 3.9454 | 15.1154 |  |  | 15.1154 | 0 | 16.8 | 1.6846 | 1.6846 | available
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | available | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.127 | 0.857 | 0.398 | 120 | 0.459 | 0 | 2.63 | 2.171 | 2.171 | available
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | available | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.9823 |  |  | 22.9823 | 0 | 26.25 | 3.2677 | 3.2677 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 8.4123 |  |  | 8.4123 | 0 | 26.25 | 17.8377
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.3 | 14.57 |  |  | 14.57 | 0 | 26.25 | 11.68
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | available | 36 | SS 110/6/6 Orion | 40+40 | 0.67533 | 15.3853 |  |  | 15.3853 | 0 | 42 | 26.6147 | 26.6147 | available
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | unavailable | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 24.156 |  |  | 24.156 | 0 | 21 | -3.156 | -3.156 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.2592 |  |  | 6.2592 | 0 | 21 | 14.7408
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.046702 | 17.8967 |  |  | 17.8967 | 0 | 21 | 3.1033
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | available | 38 | SS 110/10 Pereval | 16+16 | 7.8231 | 16.3331 |  |  | 16.3331 | 0 | 16.8 | 0.46689 | 0.46689 | available
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | available | 39 | SS 110/6/6 Perekop | 25+25 | 0.5287 | 10.8587 |  |  | 10.8587 | 0 | 26.25 | 15.3913 | 15.3913 | available
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | available | 40 | SS 110/6/6 Poligraf | 40+40 | 2.2719 | 36.2419 |  |  | 36.2419 | 0 | 42 | 5.7581 | 5.7581 | available
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | available | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.8865 | 0.52 | 120 | 4.3665 | 0 | 10.5 | 6.1335 | 6.1335 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 1.195 |  |  | 1.195 | 0 | 10.5 | 9.305
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.8715 | 3.6915 | 0.52 | 120 | 3.1715 | 0 | 10.5 | 7.3285
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | available | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.8553 | 3.9053 | 0.26 | 120 | 3.6453 | 0 | 2.63 | -1.0153 | -1.0153 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | available | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.045 | 0.275 | 0.052 | 120 | 0.223 | 0 | 2.63 | 2.407 | 2.407 | available
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | available | 44 | SS 110/6/6 Severnaya | 63+63 | 4.662 | 42.652 |  |  | 42.652 | 0 | 66.15 | 23.498 | 23.498 | available
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | available | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.677 | 2.017 | 0.987 | 120 | 1.03 | 0 | 2.63 | 1.6 | 1.6 | available
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | available | 46 | SS 110/6 Tormoznaya | 16+16 | 0.18757 | 14.6956 |  |  | 14.6956 | 0 | 16.8 | 2.1044 | 2.1044 | available
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | available | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.02 | 0.36 | 0.277 | 120 | 0.083 | 0 | 2.63 | 2.547 | 2.547 | available
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | available | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.554 | 1.244 | 0.191 | 120 | 1.053 | 0 | 2.63 | 1.577 | 1.577 | available
50 | SS 35/10 Tutaev-35 | 10+10 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 10.5 | 3.24 | 3.24 | available | 50 | SS 35/10 Tutaev-35 | 10+10 | 0.585 | 7.845 |  |  | 7.845 | 0 | 10.5 | 2.655 | 2.655 | available
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | available | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.3434 | 1.0634 |  |  | 1.0634 | 0 | 2.63 | 1.5666 | 1.5666 | available
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | available | 52 | SS 35/10 Urozhay | 4,0+4,0 | 1.282 | 2.862 | 0.346 | 120 | 2.516 | 0 | 4.2 | 1.684 | 1.684 | available
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | MVA 4: 2.92; Min 11: 2.83; Min 12: available | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8525 |  |  |  | 0 |  |  | 2.7675 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 2.13; MVA Т-2: 2.13 |  | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0625 | 0.8525 | 0.26 | 120 | 0.5925 | 0 | 3.36 | 2.7675
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | available | 54 | SS 110/10 Chayka | 25+25 | 2.0047 | 21.3847 |  |  | 21.3847 | 0 | 26.25 | 4.8653 | 4.8653 | available
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | available | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.007 | 3.577 | 0.156 | 120 | 3.421 | 0 | 2.63 | -0.791 | -0.791 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 1.2355 | 2.6655 |  |  | 2.6655 | 0 | 4.2 | 1.5345 | 1.5345 | available
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | available | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 4.3715 | 36.3515 |  |  | 36.3515 | 0 | 42 | 5.6485 | 5.6485 | available
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | available | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.9775 | 7.8575 |  |  | 7.8575 | 0 | 26.25 | 18.3925 | 18.3925 | available
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | available | 59 | ПС 110/6/6 Kotorosl | 25+25 | 0.71255 | 6.7525 |  |  | 6.7525 |  | 26.25 | 19.4975 | 19.4975 | available
60 | SS 35/6 Kelnot | 4 | 4 |  | 0.29 | 0.29 |  | 4.2 | 1 day and night | 0.29 | 0 | 4.2 | 3.91 | 3.91 | available | 60 | SS 35/6 Kelnot | 4 | 0 | 0.29 | 4.2 | 1 day and night | 0.29 |  | 4.2 | 3.91 | 3.91 | available
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | available | 61 | SS 110/10 Altynovo | 6,3+6,3 | 1.8233 | 5.1233 |  |  | 5.1233 | 0 | 6.62 | 1.4967 | 1.4967 | available
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | available | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 12.8413 |  |  | 12.8413 | 0 | 10.5 | -2.3412 | -2.3412 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 5.821 |  |  | 5.821 | 0 | 10.5 | 4.679
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Nom. capacity LV, МVА | 16+10 | 2.5702 | 7.0202 |  |  | 7.0202 | 0 | 10.5 | 3.4798
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | available | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 4.2915 | 0.537 | 120 | 3.7545 | 0 | 10.5 | 6.7455 | 6.7455 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.3205 |  |  | 2.3205 | 0 | 10.5 | 8.1795
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.671 | 1.971 | 0.537 | 120 | 1.434 | 0 | 10.5 | 9.066
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | available | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | available
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | unavailable | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | unavailable
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | available | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.7855 |  |  | 1.7855 | 0 | 6.62 | 4.8345 | 4.8345 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 0.36; MVA Т-2: 0.36; Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.3965 |  |  | 0.3965 | 0 | 6.62 | 6.2235
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.049 | 1.389 |  |  | 1.389 | 0 | 6.62 | 5.231
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | unavailable | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 29.8074 | 0.97 | 120 | 28.8374 | 0 | 6.62 | -22.2174 | -22.2174 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.8392 |  |  | 11.8392 | 0 | 6.62 | -5.2192
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 15.2782 | 17.9682 | 0.97 | 120 | 16.9982 | 0 | 6.62 | -10.3782
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | available | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 37.669 |  |  | 37.669 | 0 | 26.25 | -11.419 | -11.419 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 22.798 |  |  | 22.798 | 0 | 26.25 | 3.452
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.541 | 14.871 |  |  | 14.871 | 0 | 26.25 | 11.379
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | available | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.6385 | 2.3985 |  |  | 2.3985 | 0 | 2.63 | 0.2315 | 0.2315 | available
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | unavailable | 71 | SS 110/35/10 Rostov | 20+25 |  | 24.8885 |  |  | 24.8885 | 0 | 21 | -3.8885 | -3.8885 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 2.2595 |  |  | 2.2595 | 0 | 21 | 18.7405
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 3.079 | 22.629 |  |  | 22.629 | 0 | 21 | -1.629
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | unavailable | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 13.5616 |  |  | 13.5616 | 0 | 6.62 | -6.9416 | -6.9416 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 7.8625 |  |  | 7.8625 | 0 | 6.62 | -1.2426
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.209 | 5.699 |  |  | 5.699 | 0 | 6.62 | 0.921
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | available | 73 | SS 110/35/10 Uglich | 25+25 |  | 35.3775 |  |  | 35.3775 | 0 | 26.25 | -9.1275 | -9.1275 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 25.9865 |  |  | 25.9865 | 0 | 26.25 | 0.2635
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 4.801 | 9.391 |  |  | 9.391 | 0 | 26.25 | 16.859
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | available | 74 | SS 110/10 Ustye | 10+10 | 0.423 | 4.773 | 0.797 | 120 | 3.976 | 0 | 10.5 | 6.524 | 6.524 | available
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | available | 75 | SS 110/10 Shurskol | 10+10 | 0.106 | 1.446 | 0.97 | 120 | 0.476 | 0 | 10.5 | 10.024 | 10.024 | available
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | available | 76 | SS 110/10 Yur.Sloboda | 10+10 | 2.1121 | 9.2821 | 0.866 | 120 | 8.4161 | 0 | 10.5 | 2.0839 | 2.0839 | available
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.114 | 1.044 |  |  | 1.044 | 0 | 2.63 | 1.586 | 1.586 | available
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | available | 78 | SS 35/6 Batki | 1,6+1,6 | 0.895 | 2.035 |  |  | 2.035 | 0 | 1.68 | -0.355 | -0.355 | unavailable
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | available | 79 | SS 35/10 Beregovaya | 1,6 | 0.023 | 0.203 | 3.031 | 1 day and night | 0.203 | 0 | 3.031 | 2.828 | 2.828 | available
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | available | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.152 | 1.912 | 0.225 |  | 1.687 | 0 | 2.63 | 0.943 | 0.943 | available
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | available | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.026 | 0.526 | 0.087 | 120 | 0.439 | 0 | 1.68 | 1.241 | 1.241 | available
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.155 | 1.905 | 0.52 | 120 | 1.385 | 0 | 1.68 | 0.295 | 0.295 | available
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | available | 83 | SS 35/10 Glebovo | 2,5+2,5 | 4.627 | 6.707 |  |  | 6.707 | 0 | 2.63 | -4.077 | -4.077 | unavailable
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.426 | 1.356 |  |  | 1.356 | 0 | 2.63 | 1.274 | 1.274 | available
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.156 | 1.266 |  |  | 1.266 | 0 | 1.68 | 0.414 | 0.414 | available
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | available | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.154 | 1.694 |  |  | 1.694 | 0 | 1.68 | -0.014 | -0.014 | unavailable
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | available | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.1515 | 1.6415 |  |  | 1.6415 | 0 | 2.63 | 0.9885 | 0.9885 | available
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | available | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 1.347 | 3.587 |  |  | 3.587 | 0 | 6.62 | 3.033 | 3.033 | available
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | available | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | available
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | available | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.777 | 3.507 | 0.953 | 120 | 2.554 | 0 | 4.2 | 1.646 | 1.646 | available
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | available | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.49275 | 1.8428 |  |  | 1.8428 | 0 | 2.63 | 0.78725 | 0.78725 | available
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | available | 92 | SS 35/6 Kupan | 2,5+2,5 | 1.4747 | 4.0547 |  |  | 4.0547 | 0 | 2.63 | -1.4247 | -1.4247 | unavailable
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | available | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.387 | 1.377 | 0.502 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | available
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | available | 94 | SS 35/10 Nagorye | 4,0+4,0 | 2.084 | 5.574 |  |  | 5.574 | 0 | 4.2 | -1.374 | -1.374 | unavailable
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | available | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.343 | 2.473 | 0.087 | 120 | 2.386 | 0 | 4.2 | 1.814 | 1.814 | available
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | available | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.5415 | 1.6515 |  |  | 1.6515 | 0 | 2.63 | 0.9785 | 0.9785 | available
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | available | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.052 | 0.962 | 0.035 | 120 | 0.927 | 0 | 2.63 | 1.703 | 1.703 | available
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | available | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.149 | 1.429 |  |  | 1.429 | 0 | 2.63 | 1.201 | 1.201 | available
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | unavailable | 99 | SS 35/10 Saraevo | 1+1,6 | 0.565 | 1.885 |  |  | 1.885 | 0 | 1.05 | -0.835 | -0.835 | unavailable
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | available | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 1.951 | 3.401 | 0.953 | 120 | 2.448 | 0 | 2.63 | 0.182 | 0.182 | available
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | available | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.327 | 0.947 | 0.052 | 120 | 0.895 | 0 | 4.2 | 3.305 | 3.305 | available
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | available | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 2.0741 | 3.1741 |  |  | 3.1741 | 0 | 1.68 | -1.4941 | -1.4941 | unavailable
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | unavailable | 103 | SS 35/10 Solomidino | 2.5 | 2.55 | 3.75 | 0.866 | 1 day and night | 3.75 | 0 | 0.866 | -2.884 | -2.884 | unavailable
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | available | 104 | SS 35/10 Stavotino | 4,0+4,0 | 1.5758 | 3.0458 | 0.346 | 120 | 2.6998 | 0 | 4.2 | 1.5002 | 1.5002 | available
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | available | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.049 | 0.449 | 0.052 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | available
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | available | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 1.023 | 1.873 |  |  | 1.873 | 0 | 2.63 | 0.757 | 0.757 | available
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | available | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.353 | 0.733 |  |  | 0.733 | 0 | 2.63 | 1.897 | 1.897 | available
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | available | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.087 | 1.197 | 0.242 | 120 | 0.955 | 0 | 2.63 | 1.675 | 1.675 | available
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | available | 109 | SS 35/10 Neksans | 10+10 | 6.5 | 8.43 |  |  | 8.43 | 0 | 10.5 | 2.07 | 2.07 | available
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | unavailable | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.675 | 11.375 |  |  | 11.375 | 0 | 10.5 | -0.875 | -0.875 | unavailable
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | available | 111 | SS 110/10 Tishino | 25+25 | 0.203 | 18.453 |  |  | 18.453 | 0 | 26.25 | 7.797 | 7.797 | available
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | available | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.045 | 2.405 | 0.069 | 120 | 2.336 | 0 | 6.62 | 4.284 | 4.284 | available
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | available | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.12302 | 20.153 |  |  | 20.153 | 0 | 26.25 | 6.097 | 6.097 | available
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | available | 115 | SS 110/10 Optika | 10+10 | 0.5384 | 5.9284 | 0.26 | 120 | 5.6684 | 0 | 10.5 | 4.8316 | 4.8316 | available
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | available | 116 | SS 110/6 Poligrafmash | 16+16 | 0.024 | 7.784 |  |  | 7.784 | 0 | 16.8 | 9.016 | 9.016 | available
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | available | 117 | SS 110/6/6 Zapadnaya | 63+63 | 2.2334 | 30.1334 |  |  | 30.1334 | 0 | 66.15 | 36.0166 | 36.0166 | available
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | available | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.994 |  |  | 10.994 | 0 | 42 | 31.006 | 31.006 | available
| Nom. capacity MV, МVА | 40+40 |  |  | MVA 4: 0; MVA Т-1: 0; MVA Т-2: 0 |  | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.244 | 10.994 |  |  | 10.994 | 0 | 42 | 31.006
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | available | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 16.1085 |  |  | 16.1085 | 0 | 16.8 | 0.6915 | 0.6915 | available
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 11.1015 |  |  | 11.1015 | 0 | 16.8 | 5.6985
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.047 | 5.007 |  |  | 5.007 | 0 | 16.8 | 11.793
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | available | 121 | SS 110/6 Dock yard | 10+10 | 0.159 | 5.479 |  |  | 5.479 | 0 | 10.5 | 5.021 | 5.021 | available
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | available | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.955 | 4.375 |  |  | 4.375 | 0 | 6.62 | 2.245 | 2.245 | available
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | available | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.164 | 2.464 |  |  | 2.464 | 0 | 4.2 | 1.736 | 1.736 | available
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | available | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.391 | 1.071 |  |  | 1.071 | 0 | 1.68 | 0.609 | 0.609 | available
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | available | 125 | SS 110/6 Veretye | 25+25 | 0.70816 | 22.0682 |  |  | 22.0682 | 0 | 26.25 | 4.1818 | 4.1818 | available
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | available | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.5388 | 5.3388 | 0.554 | 120 | 4.7848 | 0 | 4.2 | -0.5848 | -0.5848 | unavailable
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | available | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.092 | 1.292 | 0.017 | 120 | 1.275 | 0 | 2.63 | 1.355 | 1.355 | available
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | available | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.117 | 0.937 |  |  | 0.937 | 0 | 1.68 | 0.743 | 0.743 | available
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | available | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.017 | 0.607 | 0.294 | 120 | 0.313 | 0 | 1.68 | 1.367 | 1.367 | available
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | available | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | available
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | available | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.635 | 1.945 |  |  | 1.945 | 0 | 2.63 | 0.685 | 0.685 | available
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | available | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 1.1609 | 5.4709 |  |  | 5.4709 | 0 | 6.62 | 1.1491 | 1.1491 | available
133 | SS 35/10 Breytovo | 6,3+6,3 | 6.3 | 6.3 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 6.62 | 2.02 | 2.02 | available | 133 | SS 35/10 Breytovo | 6,3+6,3 | 1.749 | 6.349 |  |  | 6.349 | 0 | 6.62 | 0.271 | 0.271 | available
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | available | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.028 | 1.088 | 0.208 | 120 | 0.88 | 0 | 1.68 | 0.8 | 0.8 | available
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | available | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.104 | 1.014 | 0.173 | 120 | 0.841 | 0 | 2.63 | 1.789 | 1.789 | available
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | available | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.073 | 1.033 |  |  | 1.033 | 0 | 2.63 | 1.597 | 1.597 | available
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | available | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.202 | 0.742 |  |  | 0.742 | 0 | 2.63 | 1.888 | 1.888 | available
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | available | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.179 | 1.579 | 0.364 | 120 | 1.215 | 0 | 1.68 | 0.465 | 0.465 | available
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | available | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.02 | 0.24 | 0.017 | 120 | 0.223 | 0 | 1.68 | 1.457 | 1.457 | available
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | available | 140 | SS 35/10 Borok | 2,5+4,0 | 0.456 | 2.016 | 0.277 | 120 | 1.739 | 0 | 2.63 | 0.891 | 0.891 | available
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | available | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.905 | 4.665 |  |  | 4.665 | 0 | 6.62 | 1.955 | 1.955 | available
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | available | 142 | SS 110/10 Volga | 5,6+6,3 | 0.19 | 2.32 |  |  | 2.32 | 0 | 5.88 | 3.56 | 3.56 | available
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | available | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.884 | 2.974 | 0.104 | 120 | 2.87 | 0 | 2.63 | -0.24 | -0.24 | unavailable
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | available | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 22.8338 |  |  | 22.8338 | 0 | 26.25 | 3.4162 | 3.4162 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 6.0254 |  |  | 6.0254 | 0 | 26.25 | 20.2246
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.39842 | 16.8084 |  |  | 16.8084 | 0 | 26.25 | 9.4416
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | available | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.234 | 1.212 | 120 | 7.022 | 0 | 10.5 | 3.478 | 3.478 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 0.884 |  |  | 0.884 | 0 | 10.5 | 9.616
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.1 | 7.35 | 1.212 | 120 | 6.138 | 0 | 10.5 | 4.362
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | available | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.389 | 3.239 |  |  | 3.239 | 0 | 6.62 | 3.381 | 3.381 | available
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | available | 147 | SS 110/35/10 Lom | 10+10 |  | 10.4281 | 1.368 | 120 | 9.0601 | 0 | 10.5 | 1.4399 | 1.4399 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 8.2645 |  |  | 8.2645 | 0 | 10.5 | 2.2355
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.6836 | 2.1636 | 1.368 | 120 | 0.7956 | 0 | 10.5 | 9.7044
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | available | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.3986 | 1.1986 |  |  | 1.1986 | 0 | 1.68 | 0.4814 | 0.4814 | available
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | available | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 10.4835 | 0.242 | 120 | 10.2415 | 0 | 10.5 | 0.2585 | 0.2585 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 9.6115 |  |  | 9.6115 | 0 | 10.5 | 0.8885
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.252 | 0.872 | 0.242 | 120 | 0.63 | 0 | 10.5 | 9.87
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | MVA 4: 3.21; Min 11: 1.432; Min 12: available | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.6775 |  |  |  | 0 |  |  | 1.417 | available
| Nom. capacidty MV, МVА | 6.3 |  |  | MVA 4: 2.91; MVA Т-1: 2.91 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.3625 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.015 | 0.315 | 1.732 | 1 day and night | 0.315 | 0 | 1.732 | 1.417
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | available | 151 | SS 35/10 Beloe | 2.5 | 0.065 | 0.775 | 1.472 | 1 day and night | 0.775 | 0 | 1.472 | 0.697 | 0.697 | available
152 | SS 110/35/10 Glebovo | 10 | 10 |  | MVA 4: 6.05; Min 11: -2.505; Min 12: unavailable | 152 | SS 110/35/10 Glebovo | 10 |  | 9.6114 |  |  |  | 0 |  |  | -4.618 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | MVA 4: 2.87; MVA Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 4.3184 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 2.113 | 5.293 | 0.675 | 1 day and night | 5.293 | 0 | 0.675 | -4.618
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | available | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | available
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | available | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | available
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | available | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | available
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | available | 157 | SS 35/10 Ermakovo | 1.6 | 0.259 | 1.279 | 1.212 | 1 day and night | 1.279 | 0 | 1.212 | -0.067 | -0.067 | unavailable
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | available | 158 | SS 35/10 Milyushino | 1.6 | 1.226 | 2.066 | 0.918 | 1 day and night | 2.066 | 0 | 0.918 | -1.148 | -1.148 | unavailable
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | unavailable | 159 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 day and night | 0.779 | 0 | 0.554 | -0.225 | -0.225 | unavailable
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | available | 160 | SS 35/10 Sit | 1.6 | 0.546 | 1.216 | 0.68 | 1 day and night | 1.216 | 0 | 0.68 | -0.536 | -0.536 | unavailable
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | unavailable | 161 | SS 35/10 Gorelovo | 1.6 | 0.618 | 1.818 | 0.901 | 1 day and night | 1.818 | 0 | 0.901 | -0.917 | -0.917 | unavailable
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | available | 164 | SS 35/10 Levoberezhnaya | 4 | 1.2036 | 2.5136 | 1.334 | 1 day and night | 2.5136 |  | 1.334 | -1.1796 | -1.1796 | unavailable
| Total: | 2869.8 | 1458.2 | 1411.6 | MVA 4: 885.648 |  | Total: | 2857.9 | а | 1076.988
| deficit |  |  |  | Min 11: 15.144 |  | deficit | [9 empty] | 119.776
| proficit |  |  |  | Min 11: 654.125 |  | proficit | [9 empty] | 523.867
|  | 0.5277 | [15 empty] | 4.191
|  | 22.7392 | [15 empty] | 18.884
Deputy director for technical
[17 empty] | policy - Chief Engineer | [8 empty] | E.V. Turapin
Note on G193: Т2
Note on G213: Т3
Note on G215: Т3
Note on H193: Т3

## Свод тек.деф.зима (hidden)
Перечень закрытых центров питания ОАО "МРСК Центра" по зимним нагрузкам 2010 года (текущий дефицит мощности).
№п/п | Наименование объекта центра питания, класс напряжения | [5 empty] | Текущий дефицит , МВА
Ярэнерго
1 | ПС 35/10 Ширинье | 2.5 |  |  |  |  | -0.47
2 | ПС 110/35/6 Павловская | 20+25 |  |  |  |  | -2.56
3 | ПС 110/6 Кинопленка | 6,3+10 |  |  |  |  | -3.28
4 | ПС 110/35/10 Нила | 6,3+6,3 |  |  |  |  | -2.76
5 | ПС 110/35/10 Ростов | 20+25 |  |  |  |  | -0.21
6 | ПС 110/35/10 Техникум | 6,3+6,3 | 3.48 | 3.48 | 0 | 2.63 | -1
7 | ПС 35/10 Сараево | 1+1,6 | 11.67 | 11.67 | 0 | 10.5 | -0.27
8 | ПС 35/10 Соломидино | 2.5 | 25.25 | 25.25 | 0 | 21 | -0.334
9 | ПС 35/6 Прибрежная | 10+10 | 45.91 | 45.91 | 0 | 42 | -0.2
10 | ПС 110/35/10 Глебово | 10 |  |  |  |  | -2.505
11 | ПС 35/10 Сутка | 2.5 |  |  |  |  | -0.186
12 | ПС 35/10 Горелово | 1.6 |  |  |  |  | -0.299
Итого текущий дефицит (зима) | [6 empty] | -14.074

## Свод ожид.деф.зима (hidden)
Перечень закрытых центров питания ОАО "МРСК Центра" по зимним нагрузкам 2010 года (ожидаемый дефицит мощности).
№п/п | Наименование объекта центра питания, класс напряжения |  | Текущий дефицит , МВА
Ярэнерго
1 | ПС 35/10 Ширинье | 2.5 | -0.841
2 | ПС 110/35/10 Аббакумцево | 10+10 | -14.565
3 | ПС 35/10 Ватолино | 4,0+4,0 | -4.087
4 | ПС 35/10 Возрождение | 4,0+4,0 | -0.28
5 | ПС 35/10 Гузицино | 4,0+4,0 | -3.762
6 | ПС 35/10 Дорожаево | 1,6+1,6 | -1.015
7 | ПС 35/6 Заволжская | 10+10 | -0.012
8 | ПС 35/10 Курба | 2,5+2,5 | -0.188
9 | ПС 35/10 Моделово-2 | 6,3+6,3 | -5.091
10 | ПС 110/35/6 Павловская | 20+25 | -3.156
11 | ПС 35/10 Профилакторий | 2,5+2,5 | -1.015
12 | ПС 35/6 Чебаково | 2,5+2,5 | -0.791
13 | ПС 110/35/10 Борисоглеб | 16+10 | -2.341
14 | ПС 110/6 Кинопленка | 6,3+10 | -6.134
15 | ПС 110/35/10 Нила | 6,3+6,3 | -22.217
16 | ПС 110/35/6 Переславль | 25+25 | -11.419
17 | ПС 110/35/10 Ростов | 20+25 | -3.889
18 | ПС 110/35/10 Техникум | 6,3+6,3 | -6.942
19 | ПС 110/35/10 Углич | 25+25 | -9.128
20 | ПС 35/6 Батьки | 1,6+1,6 | -0.355
21 | ПС 35/10 Глебово | 2,5+2,5 | -4.077
22 | ПС 35/10 Заозерье | 2,5+1,6 | -0.014
23 | ПС 35/6 Купань | 2,5+2,5 | -1.425
24 | ПС 35/10 Нагорье | 4,0+4,0 | -1.374
25 | ПС 35/10 Сараево | 1+1,6 | -0.835
26 | ПС 35/10 Скоморохово | 1,6+1,6 | -1.494
27 | ПС 35/10 Соломидино | 2.5 | -2.884
28 | ПС 35/6 Прибрежная | 10+10 | -0.875
29 | ПС 35/10 Николо-Корма | 4,0+4,0 | -0.585
30 | ПС 35/10 Красная горка | 4,0+2,5 | -0.24
31 | ПС 110/35/10 Глебово | 10 | -4.618
32 | ПС 35/10 Ермаково | 1.6 | -0.067
33 | ПС 35/10 Милюшино | 1.6 | -1.148
34 | ПС 35/10 Сутка | 2.5 | -0.225
35 | ПС 35/10 Сить | 1.6 | -0.536
36 | ПС 35/10 Горелово | 1.6 | -0.917
37 | ПС 35/10 Левобережная | 4 | -1.18
Итого текущий дефицит (зима) |  |  | -119.722

## Расчет (hidden)
Перечень закрытых центров питания ОАО "МРСК Центра" по зимним нагрузкам 2010 года (текущий дефицит мощности).
№п/п | Наименование объекта центра питания, класс напряжения | [5 empty] | Текущий дефицит , МВА
Ярэнерго
1 | ПС 35/10 Ширинье | 2.5 |  |  |  |  | -0.47 | 2011 | 1.6
2 | ПС 35/10 Некрасово | 10+10 |  |  |  |  | -0.67 | 2011 | 32
3 | ПС 110/35/6 Павловская | 20+25 |  |  |  |  | -2.56 | 2012
4 | ПС 35/10 Тутаев-35 | 6,3+6,3 |  |  |  |  | -0.64 | 2012 | 20
5 | ПС 110/6 Кинопленка | 6,3+10 |  |  |  |  | -3.28 | 2011 | 16
6 | ПС 110/35/10 Нила | 6,3+6,3 |  |  |  |  | -2.76 | 2011 | 32
7 | ПС 110/35/10 Ростов | 20+25 |  |  |  |  | -0.21 | 2012 | 25
8 | ПС 110/35/10 Техникум | 6,3+6,3 | 3.48 | 3.48 | 0 | 2.63 | -1 | 2011 | 20
9 | ПС 35/10 Сараево | 1+1,6 | 11.67 | 11.67 | 0 | 10.5 | -0.27 | 2011 | 1.6
10 | ПС 35/10 Соломидино | 2.5 | 25.25 | 25.25 | 0 | 21 | -0.334 | 2012 | 1.6
11 | ПС 35/6 Прибрежная | 10+10 | 45.91 | 45.91 | 0 | 42 | -0.2 | 2011
12 | ПС 35/10 Брейтово | 6,3+4,0 | 6.83 | 6.83 | 0 | 6.62 | -0.4 | 2011 | 6.3
13 | ПС 110/35/10 Глебово | 10 |  |  |  |  | -2.505 | 2014 | 10
14 | ПС 35/10 Сутка | 2.5 |  |  |  |  | -0.186 | 2012 | 1.6
15 | ПС 35/10 Горелово | 1.6 |  |  |  |  | -0.299 | 2012 | 1
Итого текущий дефицит (зима) | [6 empty] | -15.784
2910.9
0.3109
22.2729