## брянск 3
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kv Lopandino | 6.3 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 1 | SS 110/10 kv Lopandino | 6.3 | 0 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
2 | SS 110/35/10 kv Nerussa | 16 | 3.8 | 3.4 | 24 hours | 0.4 | 0 | 16.8 | 16.4 | 15.1 | opened | 2 | SS 110/35/10 kv Nerussa | 16 | 0.051 | 3.851 | 2.6 | 24 hours | 1.251 | 0 | 16.8 | 15.549 | 15.1 | opened
| Nom. capacity MV, MVA | 16 | 1.7 | 1.5 | 24 hours | 0.2 | 0 | 16.8 | 15.1 |  |  |  | Nom. capacity MV, MVA | 16 |  | 1.7 | 1.5 | 24 hours | 0.2 | 0 | 16.8 | 15.1
| Nom. capacity LV, MVA | 16 | 2.1 | 1.9 | 24 hours | 0.2 | 0 | 16.8 | 16.6 |  |  |  | Nom. capacity LV, MVA | 16 | 0.051 | 2.151 | 1.1 | 24 hours | 1.051 | 0 | 16.8 | 15.749
3 | SS 110/6 kv Svenskaya | 6.3 | 1.602 | 1.5 | 24 hours | 0.102 | 0 | 6.615 | 6.513 | 6.513 | opened | 3 | SS 110/6 kv Svenskaya | 6.3 | 0.053 | 1.655 | 1.5 | 24 hours | 0.155 | 0 | 6.615 | 6.46 | 6.46 | opened
4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.016 | 0.377 | 0.361 | 24 hours | 0.016 | 0 | 6.615 | 6.599 | 6.599 | opened
5 | SS 110/6 kv Energoremont | 10 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 5 | SS 110/6 kv Energoremont | 10 | 0 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.02 | 0.691 | 0.671 | 24 hours | 0.02 | 0 | 10.5 | 10.48 | 10.48 | opened
2 | SS 110/10 kv Glybochka | 2.5 | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 2 | SS 110/10 kv Glybochka | 2.5 | 0.027 | 1.252 | 1.225 | 24 hours | 0.027 | 0 | 2.625 | 2.598 | 2.598 | opened
3 | SS 110/10 kv Desyatukha | 6.3 | 1.191 | 1.187 | 24 hours | 0.004 | 0 | 6.615 | 6.611 | 6.611 | opened | 3 | SS 110/10 kv Desyatukha | 6.3 | 0.026 | 1.217 | 1.187 | 24 hours | 0.03 | 0 | 6.615 | 6.585 | 6.585 | opened
4 | SS 110/35/10 kv Ivaytenki | 6.3 | 1.6 | 1.6 | 24 hours | 0 | 0 | 6.615 | 6.615 | 5.915 | opened | 4 | SS 110/35/10 kv Ivaytenki | 6.3 | 0.03 | 1.63 | 1.6 | 24 hours | 0.03 | 0 | 6.615 | 6.585 | 5.915 | opened
| Nom. capacity MV, MVA | 6.3 | 0.7 | 0.9 | 24 hours | 0 | 0 | 6.615 | 5.915 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.7 | 0.9 | 24 hours | 0 | 0 | 6.615 | 5.915
| Nom. capacity LV, MVA | 6.3 | 0.9 | 0.7 | 24 hours | 0.2 | 0 | 6.615 | 6.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.03 | 0.93 | 0.7 | 24 hours | 0.23 | 0 | 6.615 | 6.385
5 | SS 110/35/10 kv Lugovaya | 16 | 5.4 | 4.7 | 24 hours | 0.7 | 0 | 16.8 | 16.1 | 12.1 | opened | 5 | SS 110/35/10 kv Lugovaya | 16 | 0.06 | 5.46 | 4.7 | 24 hours | 0.76 | 0 | 16.8 | 16.04 | 12.1 | opened
| Nom. capacity MV, MVA | 16 | 4.7 | 3.8 | 24 hours | 0.9 | 0 | 16.8 | 12.1 |  |  |  | Nom. capacity MV, MVA | 16 |  | 4.7 | 3.8 | 24 hours | 0.9 | 0 | 16.8 | 12.1
| Nom. capacity LV, MVA | 16 | 0.7 | 0.9 | 24 hours | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.06 | 0.76 | 0.9 | 24 hours | 0 | 0 | 16.8 | 16.8
6 | SS 110/35/10 kv Plyuskovo | 6.3 | 2.2 | 2.1 | 24 hours | 0.1 | 0 | 6.615 | 6.515 | 5.615 | opened | 6 | SS 110/35/10 kv Plyuskovo | 6.3 | 0.098 | 2.298 | 2.1 | 24 hours | 0.198 | 0 | 6.615 | 6.417 | 5.615 | opened
| Nom. capacity MV, MVA | 6.3 | 1 | 1.1 | 24 hours | 0 | 0 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1 | 1.1 | 24 hours | 0 | 0 | 6.615 | 5.615
| Nom. capacity LV, MVA | 6.3 | 1.2 | 1 | 24 hours | 0.2 | 0 | 6.615 | 6.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.098 | 1.298 | 1 | 24 hours | 0.298 | 0 | 6.615 | 6.317
7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.019 | 0.419 | 0.419 | 24 hours | 0.419 | 0 | 0.419 | 0 | 0 | opened
8 | SS 35/10 kv Altukhovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 8 | SS 35/10 kv Altukhovskaya | 1.6 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
9 | SS 35/10 kv Domashovo | 2.5 | 0.522 | 0.522 | 24 hours | 0.522 | 0 | 0.522 | 0 | 0 | opened | 9 | SS 35/10 kv Domashovo | 2.5 | 0.404 | 0.926 | 0.926 | 24 hours | 0.926 | 0 | 0.926 | 0 | 0 | opened
10 | SS 35/6 kv Dronovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 10 | SS 35/6 kv Dronovskaya | 2.5 | 0.001 | 0.601 | 0.601 | 24 hours | 0.601 | 0 | 0.601 | 0 | 0 | opened
11 | SS 35/10 kv Kokorevskaya | 4 | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened | 11 | SS 35/10 kv Kokorevskaya | 4 | 0.003 | 0.903 | 0.903 | 24 hours | 0.903 | 0 | 0.903 | 0 | 0 | opened
12 | SS 35/6 kv Malopolpinskaya | 4 | 0.447 | 0.447 | 24 hours | 0.447 | 0 | 0.447 | 0 | 0 | opened | 12 | SS 35/6 kv Malopolpinskaya | 4 | 0.059 | 0.506 | 0.506 | 24 hours | 0.506 | 0 | 0.506 | 0 | 0 | opened
13 | SS 35/10 kv Morachevskaya | 1.6 | 0.316 | 0.316 | 24 hours | 0.316 | 0 | 0.316 | 0 | 0 | opened | 13 | SS 35/10 kv Morachevskaya | 1.6 | 0.016 | 0.332 | 0.332 | 24 hours | 0.332 | 0 | 0.332 | 0 | 0 | opened
14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.66 | 0.66 | 24 hours | 0.66 | 0 | 0.66 | 0 | 0 | opened | 14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.002 | 0.662 | 0.662 | 24 hours | 0.662 | 0 | 0.662 | 0 | 0 | opened
15 | SS 35/10 kv Svetovo | 2.5 | 0.375 | 0.375 | 24 hours | 0.375 | 0 | 0.375 | 0 | 0 | opened | 15 | SS 35/10 kv Svetovo | 2.5 | 0 | 0.375 | 0.375 | 24 hours | 0.375 | 0 | 0.375 | 0 | 0 | opened
16 | SS 35/10 kv Seshcha | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 16 | SS 35/10 kv Seshcha | 2.5 | 0.01 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 | opened
17 | SS 35/10 kv Sovkhoznaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 17 | SS 35/10 kv Sovkhoznaya | 4 | 0 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
18 | SS 35/10 kv Strachevskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 18 | SS 35/10 kv Strachevskaya | 2.5 | 0.038 | 0.638 | 0.638 | 24 hours | 0.638 | 0 | 0.638 | 0 | 0 | opened
19 | SS 35/10 kv Strashevichi | 4 | 0.732 | 0.732 | 24 hours | 0.732 | 0 | 0.732 | 0 | 0 | opened | 19 | SS 35/10 kv Strashevichi | 4 | 1.138 | 1.87 | 1.87 | 24 hours | 1.87 | 0 | 1.87 | 0 | 0 | opened
20 | SS 35/10 kv Usozhskaya | 2.5 | 0.886 | 0.886 | 24 hours | 0.886 | 0 | 0.886 | 0 | 0 | opened | 20 | SS 35/10 kv Usozhskaya | 2.5 | 0.03 | 0.916 | 0.916 | 24 hours | 0.916 | 0 | 0.916 | 0 | 0 | opened
21 | SS 35/10 kv Kharinovskaya | 1 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened | 21 | SS 35/10 kv Kharinovskaya | 1 | 0 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened
22 | SS 35/10 kv Kharitonovskaya | 4 | 0.762 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | 0 | 0 | opened | 22 | SS 35/10 kv Kharitonovskaya | 4 | 0.1 | 0.862 | 0.862 | 24 hours | 0.862 | 0 | 0.862 | 0 | 0 | opened
23 | SS 35/10 kv Divovka | 2.5 | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened | 23 | SS 35/10 kv Divovka | 2.5 | 0.005 | 0.637 | 0.637 | 24 hours | 0.637 | 0 | 0.637 | 0 | 0 | opened
24 | SS 35/10 kv Molodkovo | 1 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 24 | SS 35/10 kv Molodkovo | 1 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.412 | 0.412 | 24 hours | 0.412 | 0 | 0.412 | 0 | 0 | opened | 25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.014 | 0.426 | 0.426 | 24 hours | 0.426 | 0 | 0.426 | 0 | 0 | opened
26 | SS 35/10 kv Radutinskaya | 1.6 | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened | 26 | SS 35/10 kv Radutinskaya | 1.6 | 0.022 | 0.561 | 0.561 | 24 hours | 0.561 | 0 | 0.561 | 0 | 0 | opened
27 | SS 35/6 kv Ushchepye | 1.6 | 0.625 | 0.625 | 24 hours | 0.625 | 0 | 0.625 | 0 | 0 | opened | 27 | SS 35/6 kv Ushchepye | 1.6 | 0.017 | 0.642 | 0.642 | 24 hours | 0.642 | 0 | 0.642 | 0 | 0 | opened
28 | SS 35/10 kv Ushchepye | 1.6 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened | 28 | SS 35/10 kv Ushchepye | 1.6 | 0 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened
29 | SS 35/10 kv Yakovskaya | 2.5 | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened | 29 | SS 35/10 kv Yakovskaya | 2.5 | 0.034 | 0.617 | 0.617 | 24 hours | 0.617 | 0 | 0.617 | 0 | 0 | opened
30 | SS 110/35/6 kv Aksinino | 40+40 | 21.1 | 0 | 0 | 21.1 | 0 | 42 | 20.9 | 20.9 | opened | 30 | SS 110/35/6 kv Aksinino | 40+40 | 0.005 | 21.105 | 0 | 0 | 21.105 | 0 | 42 | 20.895 | 20.895 | opened
| Nom. capacity MV, MVA | 40+40 | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5
| Nom. capacity LV, MVA | 40+40 | 17.6 | 0 | 0 | 17.6 | 0 | 42 | 24.4 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.005 | 17.605 | 0 | 0 | 17.605 | 0 | 42 | 24.395
31 | SS 110/10 kv Airport | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 31 | SS 110/10 kv Airport | 6,3+6,3 | 0.008 | 0.908 | 0 | 0 | 0.908 | 0 | 6.615 | 5.707 | 5.707 | opened
32 | SS 110/6 kv Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed | 32 | SS 110/6 kv Bezhitskaya | 25+40 | 3.182 | 37.752 | 0 | 0 | 37.752 | 0 | 26.25 | -11.502 | -11.502 | closed
33 | SS 110/6 kv Water intake | 6,3+6,3 | 1.938 | 0 | 0 | 1.938 | 0 | 6.615 | 4.677 | 4.677 | opened | 33 | SS 110/6 kv Water intake | 6,3+6,3 | 0.842 | 2.78 | 0 | 0 | 2.78 | 0 | 6.615 | 3.835 | 3.835 | opened
34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed | 34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 0.806 | 26.366 | 1.5 | 12 hours | 24.866 | 0 | 16.8 | -8.066 | -8.066 | closed
35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138 | -0.138 | closed | 35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 0.613 | 4.951 | 0 | 0 | 4.951 | 0 | 4.2 | -0.751 | -0.751 | closed
36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 44.04 | 0 | 0 | 44.04 | 0 | 42 | -2.04 | -2.04 | closed | 36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 3.654 | 47.694 | 0 | 0 | 47.694 | 0 | 42 | -5.694 | -5.694 | closed
| Nom. capacity MV, MVA | 40+63 | 22.42 | 0 | 0 | 22.42 | 0 | 42 | 19.58 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 22.42 | 0 | 0 | 22.42 | 0 | 42 | 19.58
| Nom. capacity LV, MVA | 40+63 | 21.62 | 0 | 0 | 21.62 | 0 | 42 | 20.38 |  |  |  | Nom. capacity LV, MVA | 40+63 | 3.654 | 25.274 | 0 | 0 | 25.274 | 0 | 42 | 16.726
37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened | 37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 0.058 | 9.428 | 0 | 0 | 9.428 | 0 | 16.8 | 7.372 | 7.372 | opened
| Nom. capacity MV, MVA | 16+16 | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33
| Nom. capacity LV, MVA | 16+16 | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.058 | 3.958 | 0 | 0 | 3.958 | 0 | 16.8 | 12.842
38 | SS 110/35/6 kv Dyadkovksya | 25+25 | 36.58 | 9.19 | 12 hours | 27.39 | 0 | 26.25 | -1.14 | -1.14 | closed | 38 | SS 110/35/6 kv Dyadkovksya | 25+25 | 0.012 | 36.592 | 8.9 | 12 hours | 27.692 | 0 | 26.25 | -1.442 | -1.442 | closed
| Nom. capacity MV, MVA | 25+25 | 9.19 | 9.19 | 12 hours | 0 | 0 | 26.25 | 17.06 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 9.19 | 8.9 | 12 hours | 0.29 | 0 | 26.25 | 17.06
| Nom. capacity LV, MVA | 25+25 | 27.39 | 0 | 0 | 27.39 | 0 | 26.25 | -1.14 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.012 | 27.402 | 0 | 0 | 27.402 | 0 | 26.25 | -1.152
39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | opened | 39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 0.138 | 15.838 | 5.2 | 6 hours | 10.638 | 0 | 16.8 | 6.162 | 6.162 | opened
| Nom. capacity MV, MVA | 16+25 | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8
| Nom. capacity LV, MVA | 16+25 | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.138 | 8.838 | 0 | 0 | 8.838 | 0 | 16.8 | 7.962
40 | SS 110/6 kv Zarechnaya | 10+10 | 8.27 | 0 | 0 | 8.27 | 0 | 10.5 | 2.23 | 2.23 | opened | 40 | SS 110/6 kv Zarechnaya | 10+10 | 1.183 | 9.453 | 0 | 0 | 9.453 | 0 | 10.5 | 1.047 | 1.047 | opened
41 | SS 110/35/6 kv Ivotskaya | 25+25 | 9.98 | 2.68 | 6 hours | 7.3 | 0 | 26.25 | 18.95 | 18.95 | opened | 41 | SS 110/35/6 kv Ivotskaya | 25+25 | 0 | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened
| Nom. capacity MV, MVA | 25+25 | 6.36 | 2.68 | 6 hours | 3.68 | 0 | 26.25 | 19.89 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89
| Nom. capacity LV, MVA | 25+25 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kv Kamvolnaya | 16+25 | 17.92 | 0 | 0 | 17.92 | 0 | 16.8 | -1.12 | -1.12 | closed | 42 | SS 110/6 kv Kamvolnaya | 16+25 | 0.965 | 18.885 | 0 | 0 | 18.885 | 0 | 16.8 | -2.085 | -2.085 | closed
43 | SS 110/6 kv Karachevskaya | 16+25 | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened | 43 | SS 110/6 kv Karachevskaya | 16+25 | 0.217 | 11.117 | 0 | 0 | 11.117 | 0 | 16.8 | 5.683 | 5.683 | opened
44 | SS 110/6 kv Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed | 44 | SS 110/6 kv Karachizhskaya | 10+10 | 0.457 | 18.737 | 0 | 0 | 18.737 | 0 | 10.5 | -8.237 | -8.237 | closed
45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 0.112 | 7.212 | 1.4 | 6 hours | 5.812 | 0 | 10.5 | 4.688 | 4.688 | opened
| Nom. capacity MV, MVA | 10+16 | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6
| Nom. capacity LV, MVA | 10+16 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.112 | 5.312 | 0 | 0 | 5.312 | 0 | 10.5 | 5.188
46 | SS 110/35/10 kv Komarichi | 16+16 | 11.6 | 3.7 | 6 hours | 7.9 | 0 | 16.8 | 8.9 | 8.9 | opened | 46 | SS 110/35/10 kv Komarichi | 16+16 | 0.036 | 11.636 | 3.7 | 6 hours | 7.936 | 0 | 16.8 | 8.864 | 8.864 | opened
| Nom. capacity MV, MVA | 16+16 | 6.7 | 3.7 | 6 hours | 3 | 0 | 16.8 | 10.1 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.7 | 3.7 | 6 hours | 3 | 0 | 16.8 | 10.1
| Nom. capacity LV, MVA | 16+16 | 4.9 | 0 | 0 | 4.9 | 0 | 16.8 | 11.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.036 | 4.936 | 0 | 0 | 4.936 | 0 | 16.8 | 11.864
47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 1.015 | 0 | 0 | 1.015 | 0 | 2.625 | 1.61 | 1.61 | opened | 47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 0.01 | 1.025 | 0 | 0 | 1.025 | 0 | 2.625 | 1.6 | 1.6 | opened
48 | SS 110/6 kv Mamonovskaya | 10+16 | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed | 48 | SS 110/6 kv Mamonovskaya | 10+16 | 2.307 | 17.597 | 0 | 0 | 17.597 | 0 | 10.5 | -7.097 | -7.097 | closed
49 | SS 110/35/10 kv Maritskaya | 10+16 | 5.5 | 4.5 | 6 hours | 1 | 0 | 10.5 | 9.5 | 6.1 | opened | 49 | SS 110/35/10 kv Maritskaya | 10+16 | 0.128 | 5.628 | 4.5 | 6 hours | 1.128 | 0 | 10.5 | 9.372 | 6.1 | opened
| Nom. capacity MV, MVA | 10+16 | 4.4 | 4.5 | 6 hours | 0 | 0 | 10.5 | 6.1 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 4.4 | 4.5 | 6 hours | 0 | 0 | 10.5 | 6.1
| Nom. capacity LV, MVA | 10+16 | 1.1 | 0 | 0 | 1.1 | 0 | 10.5 | 9.4 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.128 | 1.228 | 0 | 0 | 1.228 | 0 | 10.5 | 9.272
50 | SS 110/6 kv Michurinskaya | 6,3+10 | 2.504 | 0 | 0 | 2.504 | 0 | 6.615 | 4.111 | 4.111 | opened | 50 | SS 110/6 kv Michurinskaya | 6,3+10 | 0.648 | 3.152 | 0 | 0 | 3.152 | 0 | 6.615 | 3.463 | 3.463 | opened
51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 2.567 | 0 | 0 | 2.567 | 0 | 6.615 | 4.048 | 4.048 | opened | 51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 0.033 | 2.6 | 0 | 0 | 2.6 | 0 | 6.615 | 4.015 | 4.015 | opened
52 | SS 110/10 kv Polpinskaya | 16+16 | 4.7 | 0 | 0 | 4.7 | 0 | 16.8 | 12.1 | 12.1 | opened | 52 | SS 110/10 kv Polpinskaya | 16+16 | 0.129 | 4.829 | 0 | 0 | 4.829 | 0 | 16.8 | 11.971 | 11.971 | opened
53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 36.96 | 0 | 0 | 36.96 | 0 | 59.85 | 22.89 | 22.89 | opened | 53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 15.228 | 52.188 | 0 | 0 | 52.188 | 0 | 59.85 | 7.662 | 7.662 | opened
54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened | 54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 0.178 | 42.578 | 0 | 0 | 42.578 | 0 | 75.075 | 32.497 | 32.497 | opened
55 | SS 110/10 kv Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened | 55 | SS 110/10 kv Teplichnaya | 10+10 | 0.19 | 5.09 | 0 | 0 | 5.09 | 0 | 10.5 | 5.41 | 5.41 | opened
56 | SS 110/6 kv Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened | 56 | SS 110/6 kv Uritskaya | 20+20 | 0 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened
57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened | 57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 0.16 | 14.22 | 4.8 | 6 hours | 9.42 | 0 | 16.8 | 7.38 | 7.38 | opened
| Nom. capacity MV, MVA | 16+16 | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98
| Nom. capacity LV, MVA | 16+16 | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.16 | 9.4 | 0 | 0 | 9.4 | 0 | 16.8 | 7.4
58 | SS 110/6 kv Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed | 58 | SS 110/6 kv Yuzhnaya | 16+25 | 0.238 | 19.668 | 0 | 0 | 19.668 | 0 | 16.8 | -2.868 | -2.868 | closed
59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened | 59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 0.022 | 1.519 | 0 | 0 | 1.519 | 0 | 2.625 | 1.106 | 1.106 | opened
60 | SS 110/6 kv Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened | 60 | SS 110/6 kv Belaya Berezka | 16+25 | 0 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened
61 | SS 110/10 kv Valuets | 4+6,3 | 1.208 | 0 | 0 | 1.208 | 0 | 4.2 | 2.992 | 2.992 | opened | 61 | SS 110/10 kv Valuets | 4+6,3 | 0.107 | 1.315 | 0 | 0 | 1.315 | 0 | 4.2 | 2.885 | 2.885 | opened
62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 2.1 | 0.54 | 3 hours | 1.56 | 0 | 42 | 40.44 | 40.1 | opened | 62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 0 | 2.1 | 0.54 | 3 hours | 1.56 | 0 | 42 | 40.44 | 40.1 | opened
| Nom. capacity MV, MVA | 10+6,3 | 0.2 | 0.54 | 3 hours | 0 | 0 | 42 | 41.8 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.2 | 0.54 | 3 hours | 0 | 0 | 42 | 41.8
| Nom. capacity LV, MVA | 10+6,3 | 1.9 | 0 | 0 | 1.9 | 0 | 42 | 40.1 |  |  |  | Nom. capacity LV, MVA | 10+6,3 |  | 1.9 | 0 | 0 | 1.9 | 0 | 42 | 40.1
63 | SS 110/6 kv Vysokoe | 40+40 | 31.467 | 0 | 0 | 31.467 | 0 | 42 | 10.533 | 10.533 | opened | 63 | SS 110/6 kv Vysokoe | 40+40 | 0.029 | 31.496 | 0 | 0 | 31.496 | 0 | 42 | 10.504 | 10.504 | opened
64 | SS 110/10 kv Zalineynaya | 10+6,3 | 3.931 | 0 | 0 | 3.931 | 0 | 6.615 | 2.684 | 2.684 | opened | 64 | SS 110/10 kv Zalineynaya | 10+6,3 | 0.163 | 4.094 | 0 | 0 | 4.094 | 0 | 6.615 | 2.521 | 2.521 | opened
65 | SS 110/6 kv Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened | 65 | SS 110/6 kv Zapadnaya | 10+10 | 0.016 | 10.516 | 0 | 0 | 10.516 | 0 | 10.5 | -0.016 | -0.016 | opened
66 | SS 110/35/10 kv Klimovo | 16+16 | 10.2 | 1.64 | 6 hours | 8.56 | 0 | 42 | 33.44 | 33.44 | opened | 66 | SS 110/35/10 kv Klimovo | 16+16 | 0.158 | 10.358 | 1.64 | 6 hours | 8.718 | 0 | 42 | 33.282 | 33.282 | opened
| Nom. capacity MV, MVA | 16+16 | 3.1 | 1.64 | 6 hours | 1.46 | 0 | 42 | 38.9 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.1 | 1.64 | 6 hours | 1.46 | 0 | 42 | 38.9
| Nom. capacity LV, MVA | 16+16 | 7.1 | 0 | 0 | 7.1 | 0 | 42 | 34.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.158 | 7.258 | 0 | 0 | 7.258 | 0 | 42 | 34.742
67 | SS 110/35/6 kv Kozhany | 10+10 | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened | 67 | SS 110/35/6 kv Kozhany | 10+10 | 0.009 | 3.873 | 3.12 | 6 hours | 0.753 | 0 | 42 | 41.247 | 38.884 | opened
| Nom. capacity MV, MVA | 10+10 | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884
| Nom. capacity LV, MVA | 10+10 | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.009 | 0.757 | 0 | 0 | 0.757 | 0 | 42 | 41.243
68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 0.109 | 1.374 | 0 | 0 | 1.374 | 0 | 2.625 | 1.251 | 1.251 | opened
69 | SS 110/35/10 kv Pogar | 16+16+16 | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened | 69 | SS 110/35/10 kv Pogar | 16+16+16 | 0.158 | 10.71 | 1.8 | 6 hours | 8.91 | 0 | 42 | 33.09 | 33.09 | opened
| Nom. capacity MV, MVA | 16+16 | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197
| Nom. capacity LV, MVA | 16+16 | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.158 | 8.907 | 0 | 0 | 8.907 | 0 | 42 | 33.093
70 | SS 110/35/10 kv Pochepskaya | 16+25 | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened | 70 | SS 110/35/10 kv Pochepskaya | 16+25 | 1.851 | 14.846 | 2.21 | 3 hours | 12.636 | 0 | 42 | 29.364 | 29.362 | opened
| Nom. capacity MV, MVA | 16+25 | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792
| Nom. capacity LV, MVA | 16+25 | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213 |  |  |  | Nom. capacity LV, MVA | 16+25 | 1.851 | 12.638 | 0 | 0 | 12.638 | 0 | 42 | 29.362
71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened | 71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.006 | 0.545 | 0 | 0 | 0.545 | 0 | 2.625 | 2.08 | 2.08 | opened
72 | SS 110/35/10 kv Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened | 72 | SS 110/35/10 kv Starodub | 16+16 | 0.021 | 12.585 | 7.34 | 6 hours | 5.245 | 0 | 42 | 36.755 | 34.665 | opened
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.021 | 5.25 | 0 | 0 | 5.25 | 0 | 42 | 36.75
73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.976 | 0 | 0 | 0.976 | 0 | 6.615 | 5.639 | 5.639 | opened | 73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.045 | 1.021 | 0 | 0 | 1.021 | 0 | 6.615 | 5.594 | 5.594 | opened
74 | SS 110/35/6 kv Surazh | 16+16 | 18.6 | 3.04 | 6 hours | 15.56 | 0 | 42 | 26.44 | 26.4 | opened | 74 | SS 110/35/6 kv Surazh | 16+16 | 0 | 18.6 | 3.04 | 6 hours | 15.56 | 0 | 42 | 26.44 | 26.4 | opened
| Nom. capacity MV, MVA | 16+16 | 3 | 3.04 | 6 hours | -0.04 | 0 | 42 | 39 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3 | 3.04 | 6 hours | -0.04 | 0 | 42 | 39
| Nom. capacity LV, MVA | 16+16 | 15.6 | 0 | 0 | 15.6 | 0 | 42 | 26.4 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 15.6 | 0 | 0 | 15.6 | 0 | 42 | 26.4
75 | SS 110/10 kv Trubchevsk | 16+10 | 7.871 | 0 | 0 | 7.871 | 0 | 10.5 | 2.629 | 2.629 | opened | 75 | SS 110/10 kv Trubchevsk | 16+10 | 0.364 | 8.235 | 0 | 0 | 8.235 | 0 | 10.5 | 2.265 | 2.265 | opened
76 | SS 110/10 kv Shelomy | 6,3+6,3 | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened | 76 | SS 110/10 kv Shelomy | 6,3+6,3 | 0.011 | 1.016 | 0 | 0 | 1.016 | 0 | 6.615 | 5.599 | 5.599 | opened
77 | SS 110/35/6 kv Yubileynaya | 16+16 | 14.3 | 6.45 | 3 hours | 7.85 | 0 | 42 | 34.15 | 34 | opened | 77 | SS 110/35/6 kv Yubileynaya | 16+16 | 3.523 | 17.823 | 6.45 | 3 hours | 11.373 | 0 | 42 | 30.627 | 30.477 | opened
| Nom. capacity MV, MVA | 16+16 | 6.3 | 6.45 | 3 hours | 0 | 0 | 42 | 35.7 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.3 | 6.45 | 3 hours | 0 | 0 | 42 | 35.7
| Nom. capacity LV, MVA | 16+16 | 8 | 0 | 0 | 8 | 0 | 42 | 34 |  |  |  | Nom. capacity LV, MVA | 16+16 | 3.523 | 11.523 | 0 | 0 | 11.523 | 0 | 42 | 30.477
78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened | 78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 0 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened
79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 3.828 | 0 | 0 | 3.828 | 0 | 6.615 | 2.787 | 2.787 | opened | 79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 0.008 | 3.836 | 0 | 0 | 3.836 | 0 | 6.615 | 2.779 | 2.779 | opened
80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened | 80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
81 | SS 35/6 kv Bytosh | 3,2+6,3 | 2.708 | 0 | 0 | 2.708 | 0 | 3.36 | 0.652 | 0.652 | opened | 81 | SS 35/6 kv Bytosh | 3,2+6,3 | 0 | 2.708 | 0 | 0 | 2.708 | 0 | 3.36 | 0.652 | 0.652 | opened
82 | SS 35/6 kv Velyaminovskaya | 4+4 | 2.021 | 0 | 0 | 2.021 | 0 | 4.2 | 2.179 | 2.179 | opened | 82 | SS 35/6 kv Velyaminovskaya | 4+4 | 0.011 | 2.032 | 0 | 0 | 2.032 | 0 | 4.2 | 2.168 | 2.168 | opened
83 | SS 35/6 kv Vetma | 2,5+2,5 | 0.21 | 0 | 0 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 83 | SS 35/6 kv Vetma | 2,5+2,5 | 0 | 0.21 | 0 | 0 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
84 | SS 35/6 kv Volodarskaya | 10+6,3 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed | 84 | SS 35/6 kv Volodarskaya | 10+6,3 | 0 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed
85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 1.353 | 0 | 0 | 1.353 | 0 | 2.625 | 1.272 | 1.272 | opened | 85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 0.013 | 1.366 | 0 | 0 | 1.366 | 0 | 2.625 | 1.259 | 1.259 | opened
86 | SS 35/6 kv Gorodskaya | 10+10 | 12.14 | 0 | 0 | 12.14 | 0 | 10.5 | -1.64 | -1.64 | closed | 86 | SS 35/6 kv Gorodskaya | 10+10 | 0 | 12.14 | 0 | 0 | 12.14 | 0 | 10.5 | -1.64 | -1.64 | closed
87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.017 | 0.617 | 0 | 0 | 0.617 | 0 | 4.2 | 3.583 | 3.583 | opened
88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0.316 | 0 | 0 | 0.316 | 0 | 1.68 | 1.364 | 1.364 | opened | 88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0 | 0.316 | 0 | 0 | 0.316 | 0 | 1.68 | 1.364 | 1.364 | opened
89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 0.037 | 1.737 | 0 | 0 | 1.737 | 0 | 4.2 | 2.463 | 2.463 | opened
90 | SS 35/10 kv Igritskaya | 4+6,3 | 2.084 | 0 | 0 | 2.084 | 0 | 4.2 | 2.116 | 2.116 | opened | 90 | SS 35/10 kv Igritskaya | 4+6,3 | 0.054 | 2.138 | 0 | 0 | 2.138 | 0 | 4.2 | 2.062 | 2.062 | opened
91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.141 | 0 | 0 | 0.141 | 0 | 1.05 | 0.909 | 0.909 | opened | 91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.008 | 0.149 | 0 | 0 | 0.149 | 0 | 1.05 | 0.901 | 0.901 | opened
92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened | 92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.01 | 0.31 | 0 | 0 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.825 | 0 | 0 | 0.825 | 0 | 2.625 | 1.8 | 1.8 | opened | 93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.015 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
94 | SS 35/10 kv Luna | 1,6+1,6 | 1.105 | 0 | 0 | 1.105 | 0 | 1.68 | 0.575 | 0.575 | opened | 94 | SS 35/10 kv Luna | 1,6+1,6 | 0 | 1.105 | 0 | 0 | 1.105 | 0 | 1.68 | 0.575 | 0.575 | opened
95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 6.18 | 0 | 0 | 6.18 | 0 | 6.615 | 0.435 | 0.435 | opened | 95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 0.01 | 6.19 | 0 | 0 | 6.19 | 0 | 6.615 | 0.425 | 0.425 | opened
96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.027 | 0.827 | 0 | 0 | 0.827 | 0 | 1.68 | 0.853 | 0.853 | opened
97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.212 | 0 | 0 | 0.212 | 0 | 1.68 | 1.468 | 1.468 | opened | 97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.005 | 0.217 | 0 | 0 | 0.217 | 0 | 1.68 | 1.463 | 1.463 | opened
98 | SS 35/10 kv Norinskaya | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 98 | SS 35/10 kv Norinskaya | 4+4 | 0.02 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | opened
99 | SS 35/6 kv Paltso | 4+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened | 99 | SS 35/6 kv Paltso | 4+2,5 | 0.007 | 0.454 | 0 | 0 | 0.454 | 0 | 2.625 | 2.171 | 2.171 | opened
100 | SS 35/6 kv Pobeda | 4+4 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened | 100 | SS 35/6 kv Pobeda | 4+4 | 0.435 | 4.105 | 0 | 0 | 4.105 | 0 | 4.2 | 0.095 | 0.095 | opened
101 | SS 35/10 kv Pogreby | 4+4 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened | 101 | SS 35/10 kv Pogreby | 4+4 | 0.01 | 1.01 | 0 | 0 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened
102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened | 102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 0.11 | 1.11 | 0 | 0 | 1.11 | 0 | 1.68 | 0.57 | 0.57 | opened
103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
104 | SS 35/10 kv Rognedinskaya | 4+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened | 104 | SS 35/10 kv Rognedinskaya | 4+6,3 | 0.025 | 1.625 | 0 | 0 | 1.625 | 0 | 4.2 | 2.575 | 2.575 | opened
105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.86 | 0 | 0 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.01 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened
106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened | 106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 0.231 | 4.031 | 0 | 0 | 4.031 | 0 | 6.615 | 2.584 | 2.584 | opened
107 | SS 35/6 kc Seshcha | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed | 107 | SS 35/6 kc Seshcha | 1,6+4 | 0.042 | 2.042 | 0 | 0 | 2.042 | 0 | 1.68 | -0.362 | -0.362 | closed
108 | SS 35/6 kv Star | 10+10 | 3.84 | 0 | 0 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened | 108 | SS 35/6 kv Star | 10+10 | 0 | 3.84 | 0 | 0 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened
109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.721 | 0 | 0 | 0.721 | 0 | 2.625 | 1.904 | 1.904 | opened | 109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.054 | 0.775 | 0 | 0 | 0.775 | 0 | 2.625 | 1.85 | 1.85 | opened
110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.584 | 0 | 0 | 0.584 | 0 | 1.68 | 1.096 | 1.096 | opened | 110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.055 | 0.639 | 0 | 0 | 0.639 | 0 | 1.68 | 1.041 | 1.041 | opened
111 | SS 35/6 kv Fokinskaya | 16+16+16 | 22.62 | 0 | 0 | 22.62 | 0 | 33.6 | 10.98 | 10.98 | opened | 111 | SS 35/6 kv Fokinskaya | 16+16+16 | 1.226 | 23.846 | 0 | 0 | 23.846 | 0 | 33.6 | 9.754 | 9.754 | opened
112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened | 112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 3.785 | 12.085 | 0 | 0 | 12.085 | 0 | 12.495 | 0.41 | 0.41 | opened
113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened | 113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.052 | 0.982 | 0 | 0 | 0.982 | 0 | 2.625 | 1.643 | 1.643 | opened
114 | SS 35/10 kv Abarinskaya | 4+4 | 0.835 | 0 | 0 | 0.835 | 0 | 4.2 | 3.365 | 3.365 | opened | 114 | SS 35/10 kv Abarinskaya | 4+4 | 0.09 | 0.925 | 0 | 0 | 0.925 | 0 | 4.2 | 3.275 | 3.275 | opened
115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened | 115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.008 | 0.938 | 0 | 0 | 0.938 | 0 | 2.625 | 1.687 | 1.687 | opened
116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0.6 | opened | 116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 0.041 | 1.121 | 0 | 0 | 1.121 | 0 | 1.68 | 0.559 | 0 | opened
117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.022 | 0.522 | 0 | 0 | 0.522 | 0 | 1.68 | 1.158 | 1.158 | opened
118 | SS 35/6 kv Water intake | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 118 | SS 35/6 kv Water intake | 2,5+2,5 | 0 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
119 | SS 35/10 kv Voronok | 2,5+3,2 | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened | 119 | SS 35/10 kv Voronok | 2,5+3,2 | 0.033 | 1.503 | 0 | 0 | 1.503 | 0 | 2.625 | 1.122 | 1.122 | opened
120 | SS 35/10 kv Gordeevka | 4+4 | 2.3 | 0 | 0 | 2.3 | 0 | 4.2 | 1.9 | 1.9 | opened | 120 | SS 35/10 kv Gordeevka | 4+4 | 0.066 | 2.366 | 0 | 0 | 2.366 | 0 | 4.2 | 1.834 | 1.834 | opened
121 | SS 35/10 kv Gridenki | 2,5+3,2 | 1.533 | 0 | 0 | 1.533 | 0 | 2.625 | 1.092 | 1.092 | opened | 121 | SS 35/10 kv Gridenki | 2,5+3,2 | 0.113 | 1.646 | 0 | 0 | 1.646 | 0 | 2.625 | 0.979 | 0.979 | opened
122 | SS 35/10 kv Zavodskaya | 4+2,5 | 1.12 | 0 | 0 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | opened | 122 | SS 35/10 kv Zavodskaya | 4+2,5 | 0.005 | 1.125 | 0 | 0 | 1.125 | 0 | 2.625 | 1.5 | 1.5 | opened
123 | SS 35/10 kv Istopki | 1,6+1,6 | 1.106 | 0 | 0 | 1.106 | 0 | 1.68 | 0.574 | 0.574 | opened | 123 | SS 35/10 kv Istopki | 1,6+1,6 | 0.01 | 1.116 | 0 | 0 | 1.116 | 0 | 1.68 | 0.564 | 0.564 | opened
124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.899 | 0 | 0 | 0.899 | 0 | 1.68 | 0.781 | 0.781 | opened | 124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.029 | 0.928 | 0 | 0 | 0.928 | 0 | 1.68 | 0.752 | 0.752 | opened
125 | SS 35/10 kv Kivay | 2,5+2,5 | 1.931 | 0 | 0 | 1.931 | 0 | 2.625 | 0.694 | 0.694 | opened | 125 | SS 35/10 kv Kivay | 2,5+2,5 | 0.03 | 1.961 | 0 | 0 | 1.961 | 0 | 2.625 | 0.664 | 0.664 | opened
126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.762 | 0 | 0 | 0.762 | 0 | 1.68 | 0.918 | 0.918 | opened | 126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.041 | 0.803 | 0 | 0 | 0.803 | 0 | 1.68 | 0.877 | 0.877 | opened
127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 1.329 | 0 | 0 | 1.329 | 0 | 1.68 | 0.351 | 0.351 | opened | 127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 0.016 | 1.345 | 0 | 0 | 1.345 | 0 | 1.68 | 0.335 | 0.335 | opened
128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.018 | 0.378 | 0 | 0 | 0.378 | 0 | 2.625 | 2.247 | 2.247 | opened
129 | SS 35/10 kv Mglinskaya | 4+4 | 3.899 | 0 | 0 | 3.899 | 0 | 4.2 | 0.301 | 0.301 | opened | 129 | SS 35/10 kv Mglinskaya | 4+4 | 0.037 | 3.936 | 0 | 0 | 3.936 | 0 | 4.2 | 0.264 | 0.264 | opened
130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.632 | 0 | 0 | 0.632 | 0 | 1.68 | 1.048 | 1.048 | opened | 130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.021 | 0.653 | 0 | 0 | 0.653 | 0 | 1.68 | 1.027 | 1.027 | opened
131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.001 | 0.581 | 0 | 0 | 0.581 | 0 | 2.625 | 2.044 | 2.044 | opened
132 | SS 35/10 kv Putevaya | 6,3+6,3 | 5.767 | 0 | 0 | 5.767 | 0 | 6.615 | 0.848 | 0.848 | opened | 132 | SS 35/10 kv Putevaya | 6,3+6,3 | 0.06 | 5.827 | 0 | 0 | 5.827 | 0 | 6.615 | 0.788 | 0.788 | opened
133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 1.369 | 0 | 0 | 1.369 | 0 | 2.625 | 1.256 | 1.256 | opened | 133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 0.07 | 1.439 | 0 | 0 | 1.439 | 0 | 2.625 | 1.186 | 1.186 | opened
134 | SS 35/10 kv Slava | 2,5+1,6 | 1.325 | 0 | 0 | 1.325 | 0 | 1.68 | 0.355 | 0.355 | opened | 134 | SS 35/10 kv Slava | 2,5+1,6 | 0.023 | 1.348 | 0 | 0 | 1.348 | 0 | 1.68 | 0.332 | 0.332 | opened
135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 3.22 | 0 | 0 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened | 135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 0.086 | 3.306 | 0 | 0 | 3.306 | 0 | 6.615 | 3.309 | 3.309 | opened
136 | SS 35/10 kv Solovyevka | 1,6+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened | 136 | SS 35/10 kv Solovyevka | 1,6+1,6 | 0.005 | 0.455 | 0 | 0 | 0.455 | 0 | 1.68 | 1.225 | 1.225 | opened
137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened | 137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.015 | 0.462 | 0 | 0 | 0.462 | 0 | 2.625 | 2.163 | 2.163 | opened
138 | SS 35/6 kv Tembr | 4+4+3,2 | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened | 138 | SS 35/6 kv Tembr | 4+4+3,2 | 0.075 | 7.005 | 0 | 0 | 7.005 | 0 | 7.56 | 0.555 | 0.555 | opened
139 | SS 35/10 kv Churovichi | 2,5+4 | 0.978 | 0 | 0 | 0.978 | 0 | 2.625 | 1.647 | 1.647 | opened | 139 | SS 35/10 kv Churovichi | 2,5+4 | 0.038 | 1.016 | 0 | 0 | 1.016 | 0 | 2.625 | 1.609 | 1.609 | opened
140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 0.041 | 1.071 | 0 | 0 | 1.071 | 0 | 2.625 | 1.554 | 1.554 | opened
| Total: | 2274.8 | 776.924 | [8 empty] | 2: Total:; 3: 2274.8; 4: 47.693; 5: 824.617
| deficit | [8 empty] | -41.913 |  | 2: deficit; Мin. 12: -54.479
| proficit | [8 empty] | 673.5 |  | 2: proficit; Мin. 12: 673.439

## Белгород 3
[13 empty] | Table 1 | [12 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [10 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | P | Q | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
[5 empty] | MVA | MVA | Min. | [11 empty] | MVA | min.
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 1523 | 679 | 1.6675 | 1.457 | 45 | 1.457 | 0 | 1.457 | -0.2105 | -0.57942 |  | 1 | SS-110/35/10kv D.Polyana | 6.3 | 0 | 1.6675 | 1.457 | 45 | 0.2105 | 0 | 1.457 | -0.2105 | -0.57942
| Sн. MV, МVА | 6.3 | 513 | 301 | 0.59479 | 0.958 |  | 0.958 | 0 | 0.958 | 0.36321 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0.59479 | 0.958 |  | -0.36321 | 0 | 0.958 | 0.36321
| Sн. LV, МVА | 6.3 | 1010 | 378 | 1.0784 | 0.499 |  | 0.499 | 0 | 0.499 | -0.57942 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 1.0784 | 0.499 |  | 0.57942 | 0 | 0.499 | -0.57942
2 | SS-110/35/10kv Konshino | 6.3 | 375 | 154 | 0.40539 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01539 | -0.01539 |  | 2 | SS-110/35/10kv Konshino | 6.3 | 0 | 0.40539 | 0.39 | 20 | 0.01539 | 0 | 0.39 | -0.01539 | -0.01539
| Sн. MV, МVА | 6.3 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 375 | 154 | 0.40539 | 0.39 |  | 0.39 | 0 | 0.39 | -0.01539 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.40539 | 0.39 |  | 0.01539 | 0 | 0.39 | -0.01539
3 | SS-110/35/10kv Orositelnaya | 16 | 11884 | 2898 | 12.2322 | 11.607 | 120 | 11.607 | 0 | 11.607 | -0.62525 | -0.90525 |  | 3 | SS-110/35/10kv Orositelnaya | 16 | 0 | 12.2322 | 11.607 | 120 | 0.62525 | 0 | 11.607 | -0.62525 | -0.90525
| Sн. MV, МVА | 16 | 9059 | 2898 | 9.5113 | 8.606 |  | 8.606 | 0 | 8.606 | -0.90525 |  |  |  | Sн. MV, МVА | 16 | 0 | 9.5113 | 8.606 |  | 0.90525 | 0 | 8.606 | -0.90525
| Sн. LV, МVА | 16 | 2825 |  | 2.825 | 3.001 |  | 3.001 | 0 | 3.001 | 0.176 |  |  |  | Sн. LV, МVА | 16 | 0 | 2.825 | 3.001 |  | -0.176 | 0 | 3.001 | 0.176
4 | SS-110/35/6kv Pishcheprom | 25 | 6036 | 1850 | 6.3131 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.36586 | -0.24769 |  | 4 | SS-110/35/6kv Pishcheprom | 25 | 0.015 | 6.3281 | 6.679 | 120 | -0.35086 | 0 | 6.679 | 0.35086 | -0.24769
| Sн. MV, МVА | 12.5 | 2171 | 662 | 2.2697 | 2.022 |  | 2.022 | 0 | 2.022 | -0.24769 |  |  |  | Sн. MV, МVА | 12.5 | 0 | 2.2697 | 2.022 |  | 0.24769 | 0 | 2.022 | -0.24769
| Sн. LV, МVА | 12.5 | 3865 | 1188 | 4.0435 | 4.657 |  | 4.657 | 0 | 4.657 | 0.61354 |  |  |  | Sн. LV, МVА | 12.5 | 0.015 | 4.0585 | 4.657 |  | -0.59854 | 0 | 4.657 | 0.59854
5 | SS-110/35/10kv Rovenki | 16 | 2453 | 976 | 2.64 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.79996 | 0.79996 |  | 5 | SS-110/35/10kv Rovenki | 16 | 0 | 2.64 | 3.44 | 120 | -0.79996 | 0 | 3.44 | 0.79996 | 0.79996
| Sн. MV, МVА | 16 | 2 | 34 | 0.034059 | 4 |  | 4 | 0 | 4 | 3.9659 |  |  |  | Sн. MV, МVА | 16 | 0 | 0.034059 | 4 |  | -3.9659 | 0 | 4 | 3.9659
| Sн. LV, МVА | 16 | 2451 | 942 | 2.6258 | 3.44 |  | 3.44 | 0 | 3.44 | 0.81421 |  |  |  | Sн. LV, МVА | 16 | 0 | 2.6258 | 3.44 |  | -0.81421 | 0 | 3.44 | 0.81421
6 | SS-110/35/10kv Serebryanka | 10 | 1181 | 534 | 1.2961 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.48388 | 0 |  | 6 | SS-110/35/10kv Serebryanka | 10 | 0 | 1.2961 | 1.78 | 45 | -0.48388 | 0 | 1.78 | 0.48388 | 0
| Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1181 | 534 | 1.2961 | 1.78 |  | 1.78 | 0 | 1.78 | 0.48388 |  |  |  | Sн. LV, MVА | 10 | 0 | 1.2961 | 1.78 |  | -0.48388 | 0 | 1.78 | 0.48388
7 | SS-35/10kv Afanasyevka | 1.6 | 868 | 280 | 0.91204 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.26564 | -0.26564 |  | 7 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.91204 | 0.6464 | 45 | 0.26564 | 0 | 0.6464 | -0.26564 | -0.26564
8 | SS-35/10kv Borisovka | 1.6 | 576 | 192 | 0.60716 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.076343 | 0.076343 |  | 8 | SS-35/10kv Borisovka | 1.6 | 0 | 0.60716 | 0.6835 | 45 | -0.076343 | 0 | 0.6835 | 0.076343 | 0.076343
9 | SS-35/10kv Borisy | 1.6 | 432 | 234 | 0.4913 | 0 | 20 | 0 | 0 | 0 | -0.4913 | -0.4913 |  | 9 | SS-35/10kv Borisy | 1.6 | 0.39 | 0.8813 | 0 | 20 | 0.8813 | 0 | 0 | -0.8813 | -0.8813
10 | SS-35/10kv Gostishchevo | 4 | 3792 | 1440 | 4.0562 | 2.64 | 80 | 2.64 | 0 | 2.64 | -1.4162 | -1.4162 |  | 10 | SS-35/10kv Gostishchevo | 4 | 0 | 4.0562 | 2.64 | 80 | 1.4162 | 0 | 2.64 | -1.4162 | -1.4162
11 | SS-35/10kv Gruzskoe | 1.6 | 606 | 264 | 0.66101 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.38899 | 0.38899 |  | 11 | SS-35/10kv Gruzskoe | 1.6 | 0 | 0.66101 | 1.05 | 80 | -0.38899 | 0 | 1.05 | 0.38899 | 0.38899
12 | SS-35/10kv Zemsnaryad | 1.6 | 14 | 14 | 0.019799 | 0 |  | 0 | 0 | 0 | -0.019799 | -0.019799 |  | 12 | SS-35/10kv Zemsnaryad | 1.6 | 0 | 0.019799 | 0 |  | 0.019799 | 0 | 0 | -0.019799 | -0.019799
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 360 | 112 | 0.37702 | 0 |  | 0 | 0 | 0 | -0.37702 | -0.37702 |  | 13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.37702 | 0 |  | 0.37702 | 0 | 0 | -0.37702 | -0.37702
14 | SS-35/10kv Kamyzino | 2.5 | 992 | 392 | 1.0666 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.52564 | -0.52564 |  | 14 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.0666 | 0.541 | 45 | 0.52564 | 0 | 0.541 | -0.52564 | -0.52564
15 | SS-35/10kv Koloskovo | 2.5 | 2000 | 624 | 2.0951 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.43248 | -0.43248 |  | 15 | SS-35/10kv Koloskovo | 2.5 | 0 | 2.0951 | 1.6626 | 45 | 0.43248 | 0 | 1.6626 | -0.43248 | -0.43248
16 | SS-35/10jkv Kryukovo | 2.5 | 1584 | 492 | 1.6587 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.10865 | -0.10865 |  | 16 | SS-35/10jkv Kryukovo | 2.5 | 0 | 1.6587 | 1.55 | 45 | 0.10865 | 0 | 1.55 | -0.10865 | -0.10865
17 | SS-35/10kv Kushchino | 1.6 | 384 | 144 | 0.41011 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | -1.218e-05 | -1.218e-05 |  | 17 | SS-35/10kv Kushchino | 1.6 | 0 | 0.41011 | 0.4101 | 80 | 1.218e-05 | 0 | 0.4101 | -1.218e-05 | -1.218e-05
18 | SS-35/10kv Lopukhinka | 2.5 | 384 | 160 | 0.416 | 0.407 | 20 | 0.407 | 0 | 0.407 | -0.009 | -0.009 |  | 18 | SS-35/10kv Lopukhinka | 2.5 | 0 | 0.416 | 0.407 | 20 | 0.009 | 0 | 0.407 | -0.009 | -0.009
19 | SS-35/10kv Malakeevo | 2.5 | 1296 | 648 | 1.449 | 1.38 | 120 | 1.38 | 0 | 1.38 | -0.068972 | -0.068972 |  | 19 | SS-35/10kv Malakeevo | 2.5 | 0 | 1.449 | 1.38 | 120 | 0.068972 | 0 | 1.38 | -0.068972 | -0.068972
20 | SS-35/10kv Murom | 2.5 | 1336 | 432 | 1.4041 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.13589 | 0.13589 |  | 20 | SS-35/10kv Murom | 2.5 | 0.0487 | 1.4528 | 1.54 | 45 | -0.087192 | 0 | 1.54 | 0.087192 | 0.087192
21 | SS-35/10kv Nikolaevka | 2.5 | 664 | 288 | 0.72377 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.059068 | -0.059068 |  | 21 | SS-35/10kv Nikolaevka | 2.5 | 0 | 0.72377 | 0.6647 | 45 | 0.059068 | 0 | 0.6647 | -0.059068 | -0.059068
22 | SS-35/10kv Nikolskoe | 4 | 1776 | 396 | 1.8196 | 0.78 | 120 | 0.78 | 0 | 0.78 | -1.0396 | -1.0396 |  | 22 | SS-35/10kv Nikolskoe | 4 | 0 | 1.8196 | 0.78 | 120 | 1.0396 | 0 | 0.78 | -1.0396 | -1.0396
23 | SS-35/10kv Pokrovka | 4 | 708 | 300 | 0.76894 | 0.722 | 45 | 0.722 | 0 | 0.722 | -0.046937 | -0.046937 |  | 23 | SS-35/10kv Pokrovka | 4 | 0.168 | 0.93694 | 0.722 | 45 | 0.21494 | 0 | 0.722 | -0.21494 | -0.21494
24 | SS-35/10kv Pyatnitskoe | 4 | 2441 | 768 | 2.559 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.71897 | -0.71897 |  | 24 | SS-35/10kv Pyatnitskoe | 4 | 0 | 2.559 | 1.84 | 80 | 0.71897 | 0 | 1.84 | -0.71897 | -0.71897
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 94 | 151 | 0.17787 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.4981 | 1.4981 |  | 25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0 | 0.17787 | 1.676 | 80 | -1.4981 | 0 | 1.676 | 1.4981 | 1.4981
26 | SS-35/10kv Svistovka | 2.5 | 616 | 304 | 0.68693 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.0002706 | 0.0002706 |  | 26 | SS-35/10kv Svistovka | 2.5 | 0 | 0.68693 | 0.6872 | 45 | -0.0002706 | 0 | 0.6872 | 0.0002706 | 0.0002706
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 688 | 244 | 0.72999 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | -0.0061863 | -0.0061863 |  | 27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0 | 0.72999 | 0.7238 | 120 | 0.0061863 | 0 | 0.7238 | -0.0061863 | -0.0061863
28 | SS-35/10kv Kharkovskoe | 2.5 | 660 | 304 | 0.72665 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | -0.046947 | -0.046947 |  | 28 | SS-35/10kv Kharkovskoe | 2.5 | 0 | 0.72665 | 0.6797 | 120 | 0.046947 | 0 | 0.6797 | -0.046947 | -0.046947
29 | SS-35/10kv Tserkovnaya | 2.5 | 1112 | 288 | 1.1487 | 1 | 80 | 1 | 0 | 1 | -0.14869 | -0.14869 |  | 29 | SS-35/10kv Tserkovnaya | 2.5 | 0 | 1.1487 | 1 | 80 | 0.14869 | 0 | 1 | -0.14869 | -0.14869
Two- and more transformer substations | [13 empty] | 1: Two- and more transformer substations
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 13361 | 7836 | 15.4893 | 3.561 | 45 | 11.9283 | 0 | 16.8 | 4.8717 | 4.8717 |  | 30 | SS-110/6kv Automobile maintenance plant | 16+16 | 0.03 | 15.5193 | 3.561 | 45 | 11.9583 | 0 | 16.8 | 4.8417 | 4.8417
31 | SS-110/35/10kv Aydar | 16+10 | 9152 | 3513 | 9.8031 | 8.95 | 120 | 0.85307 | 0 | 10.5 | 9.6469 | 9.6416 |  | 31 | SS-110/35/10kv Aydar | 16+10 | 0 | 9.8031 | 8.95 | 120 | 0.85307 | 0 | 10.5 | 9.6469 | 9.6416
| Sн. MV, МVА | 16+10 | 7582 | 2985 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416
| Sн. LV, МVА | 16+10 | 1570 | 528 | 1.6564 | 1.66 |  | -0.003593 | 0 | 10.5 | 10.5036 |  |  |  | Sн. LV, МVА | 16+10 | 0 | 1.6564 | 1.66 |  | -0.003593 | 0 | 10.5 | 10.5036
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12411 | 4290 | 13.1315 | 8.37 | 80 | 4.7615 | 0 | 16.8 | 12.0385 | 12.0385 |  | 32 | SS-110/35/10kv Alexandrovka | 16+16 | 0 | 13.1315 | 8.37 | 80 | 4.7615 | 0 | 16.8 | 12.0385 | 12.0385
| Sн. MV, МVА | 16+16 | 6573 | 2264 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545
| Sн. LV, МVА | 16+16 | 5838 | 2026 | 6.1796 | 1.673 |  | 4.5066 | 0 | 16.8 | 12.2934 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 6.1796 | 1.673 |  | 4.5066 | 0 | 16.8 | 12.2934
33 | SS-110/35/10kv Alexeevka | 25+25+25 | 39765 | 17571 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479 |  | 33 | SS-110/35/10kv Alexeevka | 25+25+25 | 0 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479
| Sн. MV, МVА | 25+25+25 | 16965 | 8691 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404 |  |  |  | Sн. MV, МVА | 25+25+25 | 0 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404
| Sн. LV, МVА | 25+25+25 | 22800 | 8880 | 24.4682 | 2.22 |  | 22.2482 | 0 | 52.5 | 30.2518 |  |  |  | Sн. LV, МVА | 25+25+25 | 0.03 | 24.4982 | 2.22 |  | 22.2782 | 0 | 52.5 | 30.2218
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 10006 | 3960 | 10.7611 | 8.87 | 45 | 1.8911 | 0 | 10.5 | 8.6089 | 8.6089 |  | 34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 0 | 10.7611 | 8.87 | 45 | 1.8911 | 0 | 10.5 | 8.6089 | 8.6089
| Sн. MV, МVА | 10+16 | 9416 | 3776 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221
| Sн. LV, МVА | 10+16 | 590 | 184 | 0.61803 | 0 |  | 0.61803 | 0 | 10.5 | 9.882 |  |  |  | Sн. LV, МVА | 10+16 | 0 | 0.61803 | 0 |  | 0.61803 | 0 | 10.5 | 9.882
35 | SS-110/6kv Belgorod-1 | 40+48 | 42786 | 13076 | 44.7395 | 0 | 120 | 44.7395 | 0 | 42 | -2.7395 | -2.7395 |  | 35 | SS-110/6kv Belgorod-1 | 40+48 | 0.165 | 44.9045 | 0 | 120 | 44.9045 | 0 | 42 | -2.9045 | -2.9045
36 | SS-110/35/10kv Borisovka | 16+16 | 11354 | 4570 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8462 |  | 36 | SS-110/35/10kv Borisovka | 16+16 | 0 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8322
| Sн. MV, МVА | 16+8 | 4826 | 2482 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062
| Sн. LV, МVА | 16+8 | 6528 | 2088 | 6.8538 | 3.3 |  | 3.5538 | 0 | 8.4 | 4.8462 |  |  |  | Sн. LV, МVА | 16+8 | 0.014 | 6.8678 | 3.3 |  | 3.5678 | 0 | 8.4 | 4.8322
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9651 | 3834 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887 |  | 37 | SS-110/35/10kv V.Pokrovka | 10+10 | 0 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887
| Sн. MV, МVА | 10+10 | 8148 | 3354 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887
| Sн. LV, МVА | 10+10 | 1503 | 480 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222
38 | SS-110/35/10kv Veydelevka | 10+10 | 9151 | 3160 | 9.6812 | 8.83 | 120 | 0.85124 | 0 | 10.5 | 9.6488 | 9.1219 |  | 38 | SS-110/35/10kv Veydelevka | 10+10 | 0.015 | 9.6962 | 8.83 | 120 | 0.86624 | 0 | 10.5 | 9.6338 | 9.1219
| Sн. MV, МVА | 10+10 | 4999 | 1858 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219
| Sн. LV, МVА | 10+10 | 4152 | 1302 | 4.3514 | 4.875 |  | -0.52364 | 0 | 10.5 | 11.0236 |  |  |  | Sн. LV, МVА | 10+10 | 0.015 | 4.3664 | 4.875 |  | -0.50864 | 0 | 10.5 | 11.0086
39 | SS-110/6kv Vitamin plant | 25+25 | 13429 | 6832 | 15.067 | 1.46 | 45 | 13.607 | 0 | 26.25 | 12.643 | 12.643 |  | 39 | SS-110/6kv Vitamin plant | 25+25 | 0.179 | 15.246 | 1.46 | 45 | 13.786 | 0 | 26.25 | 12.464 | 12.464
40 | SS-110/35/10kv Volokonovka | 25+25 | 18812 | 6807 | 20.0057 | 10.651 | 120 | 9.3547 | 0 | 26.25 | 16.8953 | 16.8953 |  | 40 | SS-110/35/10kv Volokonovka | 25+25 | 0 | 20.0057 | 10.651 | 120 | 9.3547 | 0 | 26.25 | 16.8953 | 16.8953
| Sн. MV, МVА | 25+25 | 10517 | 4038 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604
| Sн. LV, МVА | 25+25 | 8295 | 2769 | 8.745 | 2.075 |  | 6.67 | 0 | 26.25 | 19.58 |  |  |  | Sн. LV, МVА | 25+25 | 0.051 | 8.796 | 2.075 |  | 6.721 | 0 | 26.25 | 19.529
41 | SS-110/35/6kv Vostochnaya | 25+25 | 37165 | 16321 | 40.5908 | 25.07 | 120 | 15.5208 | 0 | 26.25 | 10.7292 | 6.2914 |  | 41 | SS-110/35/6kv Vostochnaya | 25+25 | 1.181 | 41.7718 | 25.07 | 120 | 16.7018 | 0 | 26.25 | 9.5482 | 5.1104
| Sн. MV, МVА | 25+25 | 16029 | 5536 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919
| Sн. LV, МVА | 25+25 | 21136 | 10785 | 23.7286 | 3.77 |  | 19.9586 | 0 | 26.25 | 6.2914 |  |  |  | Sн. LV, МVА | 25+25 | 1.181 | 24.9096 | 3.77 |  | 21.1396 | 0 | 26.25 | 5.1104
42 | SS-110/10/6kv Golofeevka | 25+25 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 26.25 | 23.6599 | 10.5349 |  | 42 | SS-110/10/6kv Golofeevka | 25+25 | 0 | 2.5901 | 0 |  | 2.5901 | 0 | 26.25 | 23.6599 | 10.5349
| Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  |  | Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125
| Sн. LV, МVА | 12,5+12,5 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 13.125 | 10.5349 |  |  |  | Sн. LV, МVА | 12,5+12,5 | 0 | 2.5901 | 0 |  | 2.5901 | 0 | 13.125 | 10.5349
43 | SS-110/10kv Gotnya | 16+16 | 8388 | 3608 | 9.1311 | 6.43 | 120 | 2.7011 | 0 | 16.8 | 14.0989 | 14.0989 |  | 43 | SS-110/10kv Gotnya | 16+16 | 0.051 | 9.1821 | 6.43 | 120 | 2.7521 | 0 | 16.8 | 14.0479 | 14.0479
44 | SS-110/35/10kv Grayvoron | 16+16 | 13281 | 5063 | 14.2133 | 13.953 | 80 | 0.26034 | 0 | 16.8 | 16.5397 | 14.4501 |  | 44 | SS-110/35/10kv Grayvoron | 16+16 | 0 | 14.2133 | 13.953 | 80 | 0.26034 | 0 | 16.8 | 16.5397 | 14.4501
| Sн. MV, МVА | 16+16 | 8161 | 3347 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823
| Sн. LV, МVА | 16+16 | 5120 | 1716 | 5.3999 | 3.05 |  | 2.3499 | 0 | 16.8 | 14.4501 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 5.3999 | 3.05 |  | 2.3499 | 0 | 16.8 | 14.4501
45 | SS-110/6kv Donets | 40+40 | 26016 | 7584 | 27.0989 | 6.73 | 120 | 20.3689 | 0 | 42 | 21.6311 | 21.6311 |  | 45 | SS-110/6kv Donets | 40+40 | 0.04 | 27.1389 | 6.73 | 120 | 20.4089 | 0 | 42 | 21.5911 | 21.5911
46 | SS-110/10kv Dubovoe | 40+40 | 23785 | 4642 | 24.2337 | 11.23 | 120 | 13.0037 | 0 | 42 | 28.9963 | 28.9963 |  | 46 | SS-110/10kv Dubovoe | 40+40 | 0.766 | 24.9997 | 11.23 | 120 | 13.7697 | 0 | 42 | 28.2303 | 28.2303
47 | SS-110/35/6kv Zhuravliki | 40+25 | 23335 | 7691 | 24.5698 | 12.4 | 120 | 12.1698 | 0 | 42 | 29.8302 | 29.8302 |  | 47 | SS-110/35/6kv Zhuravliki | 40+25 | 0 | 24.5698 | 12.4 | 120 | 12.1698 | 0 | 42 | 29.8302 | 29.8302
| Sн. MV, МVА | 40+25 | 16567 | 6202 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372 |  |  |  | Sн. MV, МVА | 40+25 | 0 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372
| Sн. LV, МVА | 40+25 | 6768 | 1489 | 6.9299 | 6.173 |  | 0.75686 | 0 | 42 | 41.2431 |  |  |  | Sн. LV, МVА | 40+25 | 0 | 6.9299 | 6.173 |  | 0.75686 | 0 | 42 | 41.2431
48 | SS-110/10kv Zapadnaya | 16+16 | 15459 | 3295 | 15.8063 | 1.249 | 80 | 14.5573 | 0 | 16.8 | 2.2427 | 2.2427 |  | 48 | SS-110/10kv Zapadnaya | 16+16 | 0.48 | 16.2863 | 1.249 | 80 | 15.0373 | 0 | 16.8 | 1.7627 | 1.7627
49 | SS-110/35/10kv Ivnya | 10+10 | 5960 | 2270 | 6.3777 | 6.16 | 80 | 0.21766 | 0 | 10.5 | 10.2823 | 10.2823 |  | 49 | SS-110/35/10kv Ivnya | 10+10 | 0.025 | 6.4027 | 6.16 | 80 | 0.24266 | 0 | 10.5 | 10.2573 | 10.2573
| Sн. MV, МVА | 10+10 | 2266 | 1008 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949
| Sн. LV, МVА | 10+10 | 3694 | 1262 | 3.9036 | 3.785 |  | 0.11862 | 0 | 10.5 | 10.3814 |  |  |  | Sн. LV, МVА | 10+10 | 0.025 | 3.9286 | 3.785 |  | 0.14362 | 0 | 10.5 | 10.3564
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 16357 | 6666 | 17.6632 | 7.7116 | 120 | 9.9516 | 0 | 16.8 | 6.8484 | 6.8484 |  | 50 | SS-110/35/10kv K.Gvardiya | 16+16 | 0.036 | 17.6992 | 7.7116 | 120 | 9.9876 | 0 | 16.8 | 6.8124 | 6.8124
| Sн. MV, МVА | 16+16 | 8971 | 4110 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863
| Sн. LV, МVА | 16+16 | 7386 | 2556 | 7.8158 | 2.8576 |  | 4.9582 | 0 | 16.8 | 11.8418 |  |  |  | Sн. LV, МVА | 16+16 | 0.036 | 7.8518 | 2.8576 |  | 4.9942 | 0 | 16.8 | 11.8058
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 12571 | 3927 | 13.1701 | 9.65 | 80 | 3.5201 | 0 | 26.25 | 22.7299 | 18.8414 |  | 51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 0 | 13.1701 | 9.65 | 80 | 3.5201 | 0 | 26.25 | 22.7299 | 18.8414
| Sн. MV, МVА | 25+25 | 1720 | 404 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672
| Sн. LV, МVА | 25+25 | 10851 | 3523 | 11.4086 | 4 |  | 7.4086 | 0 | 26.25 | 18.8414 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 11.4086 | 4 |  | 7.4086 | 0 | 26.25 | 18.8414
52 | SS-110/35/10kv Korocha | 16+16+16 | 20632 | 7838 | 22.0707 | 2.019 | 20 | 20.0517 | 0 | 21 | 0.94835 | 0.94835 |  | 52 | SS-110/35/10kv Korocha | 16+16+16 | 0.027 | 22.0977 | 2.019 | 20 | 20.0787 | 0 | 21 | 0.92135 | 0.92135
| Sн. MV, МVА | 16+16+16 | 8114 | 2802 | 8.5842 | 1.719 |  | 6.8652 | 0 | 21 | 14.1348 |  |  |  | Sн. MV, МVА | 16+16+16 | 0 | 8.5842 | 1.719 |  | 6.8652 | 0 | 21 | 14.1348
| Sн. LV, МVА | 16+16+16 | 12518 | 5036 | 13.493 | 0.3 |  | 13.193 | 0 | 21 | 7.807 |  |  |  | Sн. LV, МVА | 16+16+16 | 0.027 | 13.52 | 0.3 |  | 13.22 | 0 | 21 | 7.78
53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 9903 | 3556 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359 |  | 53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 0 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359
| Sн. MV, МVА | 10+10 | 4393 | 1542 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642
| Sн. LV, МVА | 10+10 | 5510 | 2014 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715
54 | SS-110/10/10kv Mayskaya | 40+40 | 2581 | 670 | 2.6665 |  |  | 2.6665 | 0 | 42 | 39.3335 | 39.3335 |  | 54 | SS-110/10/10kv Mayskaya | 40+40 | 0.035 | 2.7015 |  |  | 2.7015 | 0 | 42 | 39.2985 | 39.2985
55 | SS-110/35/10kv Maximovka | 16+16 | 7328 | 4264 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792 |  | 55 | SS-110/35/10kv Maximovka | 16+16 | 0 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792
| Sн. MV, МVА | 16+16 | 6384 | 3830 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042
| Sн. LV, МVА | 16+16 | 944 | 434 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792
56 | SS-110/35/10kv N.Oskol | 25+31,5 | 21159 | 8583 | 22.8336 | 9.119 | 80 | 13.7146 | 0 | 26.25 | 12.5354 | 12.5354 |  | 56 | SS-110/35/10kv N.Oskol | 25+31,5 | 3.46 | 26.2936 | 9.119 | 80 | 17.1746 | 0 | 26.25 | 9.0754 | 9.0754
| Sн. MV, МVА | 25+31,5 | 7395 | 3599 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557 |  |  |  | Sн. MV, МVА | 25+31,5 | 0 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557
| Sн. LV, МVА | 25+31,5 | 13764 | 4984 | 14.6386 | 1.289 |  | 13.3496 | 0 | 26.25 | 12.9004 |  |  |  | Sн. LV, МVА | 25+31,5 | 3.46 | 18.0986 | 1.289 |  | 16.8096 | 0 | 26.25 | 9.4404
57 | SS-110/10kv Obukhovskaya | 25+25 | 2272 | 372 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477 |  | 57 | SS-110/10kv Obukhovskaya | 25+25 | 0 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477
58 | SS-110/6kv Ochistnye | 16+16 | 5231 | 2499 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027 |  | 58 | SS-110/6kv Ochistnye | 16+16 | 0 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027
59 | SS-110/10kv Promyshlennaya | 25+25 | 15509 | 7413 | 17.1896 | 0 |  | 17.1896 | 0 | 26.25 | 9.0604 | 9.0604 |  | 59 | SS-110/10kv Promyshlennaya | 25+25 | 0 | 17.1896 | 0 |  | 17.1896 | 0 | 26.25 | 9.0604 | 9.0604
60 | SS-110/10kv Poultry plant | 16+16 | 9980 | 5649 | 11.4679 | 1.296 | 80 | 10.1719 | 0 | 16.8 | 6.6281 | 6.6281 |  | 60 | SS-110/10kv Poultry plant | 16+16 | 2 | 13.4679 | 1.296 | 80 | 12.1719 | 0 | 16.8 | 4.6281 | 4.6281
61 | SS-110/10kv Pushkarnaya | 40+40 | 33540 | 9360 | 34.8216 | 0 | 60 | 34.8216 | 0 | 42 | 7.1784 | 7.1784 |  | 61 | SS-110/10kv Pushkarnaya | 40+40 | 0.065 | 34.8866 | 0 | 60 | 34.8866 | 0 | 42 | 7.1134 | 7.1134
62 | SS-110/35/10kv Rakitnoe | 10+10 | 10160 | 3946 | 10.8994 | 8.98 | 120 | 1.9194 | 0 | 10.5 | 8.5806 | 7.7972 |  | 62 | SS-110/35/10kv Rakitnoe | 10+10 | 0.075 | 10.9744 | 8.98 | 120 | 1.9944 | 0 | 10.5 | 8.5056 | 7.7222
| Sн. MV, МVА | 10+10 | 4944 | 3154 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426
| Sн. LV, МVА | 10+10 | 5216 | 792 | 5.2758 | 2.573 |  | 2.7028 | 0 | 10.5 | 7.7972 |  |  |  | Sн. LV, МVА | 10+10 | 0.075 | 5.3508 | 2.573 |  | 2.7778 | 0 | 10.5 | 7.7222
63 | SS-110/35/6kv Rudnik | 25+25 | 16284 | 8685 | 18.4553 | 10.46 | 45 | 7.9953 | 0 | 26.25 | 18.2547 | 18.2547 |  | 63 | SS-110/35/6kv Rudnik | 25+25 | 0 | 18.4553 | 10.46 | 45 | 7.9953 | 0 | 26.25 | 18.2547 | 18.2547
| Sн. MV, МVА | 25+25 | 10147 | 5511 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163
| Sн. LV, МVА | 25+25 | 6137 | 3174 | 6.9092 | 0 |  | 6.9092 | 0 | 26.25 | 19.3408 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 6.9092 | 0 |  | 6.9092 | 0 | 26.25 | 19.3408
64 | SS-110/10kv Severnaya | 40+40 | 12059 | 3183 | 12.472 | 3.312 | 45 | 9.16 | 0 | 42 | 32.84 | 32.84 |  | 64 | SS-110/10kv Severnaya | 40+40 | 5.313 | 17.785 | 3.312 | 45 | 14.473 | 0 | 42 | 27.527 | 27.527
65 | SS-110/35/10kv Skorodnoe | 16+16 | 11370 | 3385 | 11.8632 | 10.36 | 120 | 1.5032 | 0 | 16.8 | 15.2968 | 15.2968 |  | 65 | SS-110/35/10kv Skorodnoe | 16+16 | 0 | 11.8632 | 10.36 | 120 | 1.5032 | 0 | 16.8 | 15.2968 | 15.2968
| Sн. MV, МVА | 16+16 | 7443 | 2214 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967
| Sн. LV, МVА | 16+16 | 3927 | 1171 | 4.0979 | 2.798 |  | 1.2999 | 0 | 16.8 | 15.5001 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 4.0979 | 2.798 |  | 1.2999 | 0 | 16.8 | 15.5001
66 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 27161 | 10201 | 29.0135 | 0 |  | 29.0135 | 0 | 47.25 | 18.2365 | 18.2365 |  | 66 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 2.437 | 31.4505 | 0 |  | 31.4505 | 0 | 47.25 | 15.7995 | 15.7995
| Sн. MV, МVА | 20+25+25 | 5305 | 2289 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722 |  |  |  | Sн. MV, МVА | 20+25+25 | 0 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722
| Sн. LV, МVА | 20+25+25 | 21856 | 7912 | 23.244 | 0 |  | 23.244 | 0 | 47.25 | 24.006 |  |  |  | Sн. LV, МVА | 20+25+25 | 2.437 | 25.681 | 0 |  | 25.681 | 0 | 47.25 | 21.569
67 | SS-110/35/10kv Streletskaya | 16+16 | 6052 | 1769 | 6.3052 | 2.23 | 80 | 4.0752 | 0 | 16.8 | 12.7248 | 4.3575 |  | 67 | SS-110/35/10kv Streletskaya | 16+16 | 0.03 | 6.3352 | 2.23 | 80 | 4.1052 | 0 | 16.8 | 12.6948 | 4.3275
| Sн. MV, МVА | 16+8 | 7 | 95 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047
| Sн. LV, МVА | 16+8 | 6045 | 1674 | 6.2725 | 2.23 |  | 4.0425 | 0 | 8.4 | 4.3575 |  |  |  | Sн. LV, МVА | 16+8 | 0.03 | 6.3025 | 2.23 |  | 4.0725 | 0 | 8.4 | 4.3275
68 | SS-110/6kv Stroitel | 15+15 | 14665 | 5743 | 15.7494 | 0 |  | 15.7494 | 0 | 15.75 | 0.00057861 | 0.00057861 |  | 68 | SS-110/6kv Stroitel | 15+15 | 0.253 | 16.0024 | 0 |  | 16.0024 | 0 | 15.75 | -0.25242 | -0.25242
69 | SS-110/35/10kv Tomarovka | 16+16 | 12522 | 4336 | 13.2515 | 3.46 | 45 | 9.7915 | 0 | 16.8 | 7.0085 | 7.0085 |  | 69 | SS-110/35/10kv Tomarovka | 16+16 | 0 | 13.2515 | 3.46 | 45 | 9.7915 | 0 | 16.8 | 7.0085 | 7.0085
| Sн. MV, МVА | 16+16 | 4590 | 1614 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945
| Sн. LV, МVА | 16+16 | 7932 | 2722 | 8.3861 | 0 |  | 8.3861 | 0 | 16.8 | 8.4139 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 8.3861 | 0 |  | 8.3861 | 0 | 16.8 | 8.4139
70 | SS-110/6kv Chemical plant | 32+32 | 8580 | 3308 | 9.1956 | 5.56 | 45 | 3.6356 | 0 | 33.6 | 29.9644 | 29.9644 |  | 70 | SS-110/6kv Chemical plant | 32+32 | 0 | 9.1956 | 5.56 | 45 | 3.6356 | 0 | 33.6 | 29.9644 | 29.9644
71 | SS-110/10kv Tsentralnaya | 40+40 | 31170 | 5706 | 31.688 | 0 |  | 31.688 | 0 | 42 | 10.312 | 10.312 |  | 71 | SS-110/10kv Tsentralnaya | 40+40 | 0.042 | 31.73 | 0 |  | 31.73 | 0 | 42 | 10.27 | 10.27
72 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23134 | 8712 | 24.7201 | 20.54 | 80 | 4.1801 | 0 | 26.25 | 22.0699 | 22.0699 |  | 72 | SS-110/35/10kv Cheremoshnoe | 25+25 | 0 | 24.7201 | 20.54 | 80 | 4.1801 | 0 | 26.25 | 22.0699 | 22.0699
| Sн. MV, МVА | 25+25 | 21521 | 7872 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105
| Sн. LV, МVА | 25+25 | 1613 | 840 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314
73 | SS-110/35/10kv Chernyanka | 16+16 | 16319 | 6059 | 17.4075 | 5.969 | 120 | 11.4385 | 0 | 16.8 | 5.3615 | 5.3615 |  | 73 | SS-110/35/10kv Chernyanka | 16+16 | 0.09 | 17.4975 | 5.969 | 120 | 11.5285 | 0 | 16.8 | 5.2715 | 5.2715
| Sн. MV, МVА | 16+16 | 7422 | 3146 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078
| Sн. LV, МVА | 16+16 | 8897 | 2913 | 9.3617 | 0 |  | 9.3617 | 0 | 16.8 | 7.4383 |  |  |  | Sн. LV, МVА | 16+16 | 0.09 | 9.4517 | 0 |  | 9.4517 | 0 | 16.8 | 7.3483
74 | SS-110/35/6kv Shebekino | 40+40 | 27508 | 12250 | 30.1123 | 16.65 | 120 | 13.4623 | 0 | 42 | 28.5377 | 28.5377 |  | 74 | SS-110/35/6kv Shebekino | 40+40 | 0.486 | 30.5983 | 16.65 | 120 | 13.9483 | 0 | 42 | 28.0517 | 28.0517
| Sн. MV, МVА | 40+40 | 15624 | 7736 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477
| Sн. LV, МVА | 40+40 | 11884 | 4514 | 12.7124 | 4.968 |  | 7.7444 | 0 | 42 | 34.2556 |  |  |  | Sн. LV, МVА | 40+40 | 0.486 | 13.1984 | 4.968 |  | 8.2304 | 0 | 42 | 33.7696
75 | SS-110/10kv Sheino | 3,2+10 | 2394 | 805 | 2.5257 | 0 |  | 2.5257 | 0 | 3.36 | 0.83428 | 0.83428 |  | 75 | SS-110/10kv Sheino | 3,2+10 | 0.179 | 2.7047 | 0 |  | 2.7047 | 0 | 3.36 | 0.65528 | 0.65528
76 | SS-110/10/6kv Yuzhnaya | 40+40 | 44406 | 12168 | 46.0429 | 12.94 | 120 | 33.1029 | 0 | 42 | 8.8971 | 8.8971 |  | 76 | SS-110/10/6kv Yuzhnaya | 40+40 | 1.674 | 47.7169 | 12.94 | 120 | 34.7769 | 0 | 42 | 7.2231 | 7.2231
| Sн. MV, МVА | 40+40 | 7092 | 1440 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833
| Sн. LV, МVА | 40+40 | 37314 | 10728 | 38.8256 | 9.52 |  | 29.3056 | 0 | 42 | 12.6944 |  |  |  | Sн. LV, МVА | 40+40 | 1.674 | 40.4996 | 9.52 |  | 30.9796 | 0 | 42 | 11.0204
77 | SS-35/10kv Aleynikovo | 2,5+2,5 | 776 | 312 | 0.83637 | 0.43267 | 120 | 0.40371 | 0 | 2.625 | 2.2213 | 2.2213 |  | 77 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0 | 0.83637 | 0.43267 | 120 | 0.40371 | 0 | 2.625 | 2.2213 | 2.2213
78 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 928 | 280 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | 2.1221 |  | 78 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 1.29 | 2.2593 | 0.46639 | 120 | 1.7929 | 0 | 2.625 | 0.83207 | 0.83207
79 | SS-35/10kv Alexeevka (kor.) | 4+4 | 872 | 312 | 0.92614 | 0 |  | 0.92614 | 0 | 4.2 | 3.2739 | 3.2739 |  | 79 | SS-35/10kv Alexeevka (kor.) | 4+4 | 0.03 | 0.95614 | 0 |  | 0.95614 | 0 | 4.2 | 3.2439 | 3.2439
80 | SS-35/10kv Annovka | 2,5+2,5 | 1014 | 366 | 1.078 | 0.44652 | 80 | 0.63151 | 0 | 2.625 | 1.9935 | 1.9935 |  | 80 | SS-35/10kv Annovka | 2,5+2,5 | 0.015 | 1.093 | 0.44652 | 80 | 0.64651 | 0 | 2.625 | 1.9785 | 1.9785
81 | SS-35/10kv Artelnoe | 6,3+6,3 | 3332 | 2520 | 4.1776 | 0.55 | 45 | 3.6276 | 0 | 6.615 | 2.9874 | 2.9874 |  | 81 | SS-35/10kv Artelnoe | 6,3+6,3 | 0 | 4.1776 | 0.55 | 45 | 3.6276 | 0 | 6.615 | 2.9874 | 2.9874
82 | SS-35/10kv B.Dvory | 4+4 | 2632 | 912 | 2.7855 | 1.191 | 120 | 1.5945 | 0 | 4.2 | 2.6055 | 2.6055 |  | 82 | SS-35/10kv B.Dvory | 4+4 | 0 | 2.7855 | 1.191 | 120 | 1.5945 | 0 | 4.2 | 2.6055 | 2.6055
83 | SS-35/10kv B.Ivanovka | 4+4 | 1136 | 448 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037 |  | 83 | SS-35/10kv B.Ivanovka | 4+4 | 0 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037
84 | SS-35/10kv B.Kolodez | 2,5+2,5 | 1032 | 420 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586 |  | 84 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586
85 | SS-35/10kv B.Ples | 2,5+2,5 | 808 | 408 | 0.90517 | 0.606 | 45 | 0.29917 | 0 | 2.625 | 2.3258 | 2.3258 |  | 85 | SS-35/10kv B.Ples | 2,5+2,5 | 0 | 0.90517 | 0.606 | 45 | 0.29917 | 0 | 2.625 | 2.3258 | 2.3258
86 | SS-35/10kv B.Troitsa | 6,3+6,3 | 3564 | 1236 | 3.7722 | 2.83 | 45 | 0.94224 | 0 | 6.615 | 5.6728 | 5.6728 |  | 86 | SS-35/10kv B.Troitsa | 6,3+6,3 | 0.07 | 3.8422 | 2.83 | 45 | 1.0122 | 0 | 6.615 | 5.6028 | 5.6028
87 | SS-35/10kv Belovskoe | 4+4 | 3592 | 1632 | 3.9454 | 1.21 | 80 | 2.7354 | 0 | 4.2 | 1.4646 | 1.4646 |  | 87 | SS-35/10kv Belovskoe | 4+4 | 0 | 3.9454 | 1.21 | 80 | 2.7354 | 0 | 4.2 | 1.4646 | 1.4646
88 | SS-35/10kv Belyanka | 2,5+4 | 1936 | 800 | 2.0948 | 1.3214 | 45 | 0.77338 | 0 | 2.625 | 1.8516 | 1.8516 |  | 88 | SS-35/10kv Belyanka | 2,5+4 | 0 | 2.0948 | 1.3214 | 45 | 0.77338 | 0 | 2.625 | 1.8516 | 1.8516
89 | SS-35/10kv Bessonovka | 6,3+6,3 | 6464 | 2896 | 7.0831 | 0.918 | 120 | 6.1651 | 0 | 6.615 | 0.44991 | 0.44991 |  | 89 | SS-35/10kv Bessonovka | 6,3+6,3 | 0 | 7.0831 | 0.918 | 120 | 6.1651 | 0 | 6.615 | 0.44991 | 0.44991
90 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 1208 | 368 | 1.2628 | 0.522 | 45 | 0.74081 | 0 | 1.68 | 0.93919 | 0.93919 |  | 90 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0 | 1.2628 | 0.522 | 45 | 0.74081 | 0 | 1.68 | 0.93919 | 0.93919
91 | SS-35/10kv V.Mikhailovka | 4+4 | 2544 | 1200 | 2.8128 | 1.45 | 80 | 1.3628 | 0 | 4.2 | 2.8372 | 2.8372 |  | 91 | SS-35/10kv V.Mikhailovka | 4+4 | 0 | 2.8128 | 1.45 | 80 | 1.3628 | 0 | 4.2 | 2.8372 | 2.8372
92 | SS-35/10kv Varvarovka | 2,5+2,5 | 1820 | 844 | 2.0062 | 1.0795 | 120 | 0.92663 | 0 | 2.625 | 1.6984 | 1.6984 |  | 92 | SS-35/10kv Varvarovka | 2,5+2,5 | 0 | 2.0062 | 1.0795 | 120 | 0.92663 | 0 | 2.625 | 1.6984 | 1.6984
93 | SS-35/10kv Vengerovka | 2,5+2,5 | 1056 | 324 | 1.1046 | 0.4 | 120 | 0.70459 | 0 | 2.625 | 1.9204 | 1.9204 |  | 93 | SS-35/10kv Vengerovka | 2,5+2,5 | 0 | 1.1046 | 0.4 | 120 | 0.70459 | 0 | 2.625 | 1.9204 | 1.9204
94 | SS-35/10kv Verkhopenye | 2,5+4 | 1448 | 640 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595 |  | 94 | SS-35/10kv Verkhopenye | 2,5+4 | 0 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595
95 | SS-35/10kv Viktoropol | 2,5+4 | 1328 | 456 | 1.4041 | 0.95536 | 120 | 0.44875 | 0 | 2.625 | 2.1762 | 2.1762 |  | 95 | SS-35/10kv Viktoropol | 2,5+4 | 0 | 1.4041 | 0.95536 | 120 | 0.44875 | 0 | 2.625 | 2.1762 | 2.1762
96 | SS-35/10kv Vislaya Dubrava | 4+4 | 2616 | 756 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093 |  | 96 | SS-35/10kv Vislaya Dubrava | 4+4 | 0 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093
97 | SS-35/10kv Vladimirovka | 4+4 | 645 | 391 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457 |  | 97 | SS-35/10kv Vladimirovka | 4+4 | 0 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457
98 | SS-35/10kv Water storage | 4+6,3 | 2136 | 420 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281 |  | 98 | SS-35/10kv Water storage | 4+6,3 | 0 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281
99 | SS-35/6kv Vostochnaya | 6,3+6,3 | 4320 | 1469 | 4.5629 | 1.43 | 120 | 3.1329 | 0 | 6.615 | 3.4821 | 3.4821 |  | 99 | SS-35/6kv Vostochnaya | 6,3+6,3 | 0 | 4.5629 | 1.43 | 120 | 3.1329 | 0 | 6.615 | 3.4821 | 3.4821
100 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1926 | 774 | 2.0757 | 0.99513 | 120 | 1.0806 | 0 | 2.625 | 1.5444 | 1.5444 |  | 100 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 0 | 2.0757 | 0.99513 | 120 | 1.0806 | 0 | 2.625 | 1.5444 | 1.5444
101 | SS-35/10kv Glinnoe | 6,3+6,3 | 2432 | 1600 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075 |  | 101 | SS-35/10kv Glinnoe | 6,3+6,3 | 0 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075
102 | SS-35/10kv Golovchino | 2,5+2,5 | 2688 | 996 | 2.8666 | 0.617 | 45 | 2.2496 | 0 | 2.625 | 0.37541 | 0.37541 |  | 102 | SS-35/10kv Golovchino | 2,5+2,5 | 0 | 2.8666 | 0.617 | 45 | 2.2496 | 0 | 2.625 | 0.37541 | 0.37541
103 | SS-35/10kv Gora-Podol | 2,5+4 | 1504 | 516 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434 |  | 103 | SS-35/10kv Gora-Podol | 2,5+4 | 0 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434
104 | SS-35/10kv Gorodishche | 4+4 | 3232 | 1600 | 3.6064 | 0 |  | 3.6064 | 0 | 4.2 | 0.59364 | 0.59364 |  | 104 | SS-35/10kv Gorodishche | 4+4 | 0.037 | 3.6434 | 0 |  | 3.6434 | 0 | 4.2 | 0.55664 | 0.55664
105 | SS-35/10kv Dmitrievka | 4+4 | 1200 | 528 | 1.311 | 0.78237 | 80 | 0.52865 | 0 | 4.2 | 3.6713 | 3.6713 |  | 105 | SS-35/10kv Dmitrievka | 4+4 | 0 | 1.311 | 0.78237 | 80 | 0.52865 | 0 | 4.2 | 3.6713 | 3.6713
106 | SS-35/10kv Dorogoshch | 4+4 | 2600 | 936 | 2.7633 | 1.054 | 45 | 1.7093 | 0 | 4.2 | 2.4907 | 2.4907 |  | 106 | SS-35/10kv Dorogoshch | 4+4 | 0 | 2.7633 | 1.054 | 45 | 1.7093 | 0 | 4.2 | 2.4907 | 2.4907
107 | SS-35/10kv Dragunka | 2,5+2,5 | 912 | 352 | 0.97757 | 0.62999 | 80 | 0.34758 | 0 | 2.625 | 2.2774 | 2.2774 |  | 107 | SS-35/10kv Dragunka | 2,5+2,5 | 0.86 | 1.8376 | 0.62999 | 80 | 1.2076 | 0 | 2.625 | 1.4174 | 1.4174
108 | SS-35/10kv Zhuravlevka | 2,5+4 | 1216 | 336 | 1.2616 | 0.274 | 80 | 0.98757 | 0 | 2.625 | 1.6374 | 1.6374 |  | 108 | SS-35/10kv Zhuravlevka | 2,5+4 | 0.1 | 1.3616 | 0.274 | 80 | 1.0876 | 0 | 2.625 | 1.5374 | 1.5374
109 | SS-35/6kv Zhuravliki | 10+10 | 7464 | 2112 | 7.7571 | 4.051 | 120 | 3.7061 | 0 | 10.5 | 6.7939 | 6.7939 |  | 109 | SS-35/6kv Zhuravliki | 10+10 | 0.0408 | 7.7979 | 4.051 | 120 | 3.7469 | 0 | 10.5 | 6.7531 | 6.7531
110 | SS-35/10kv Zavidovka | 2,5+2,5 | 606 | 282 | 0.6684 | 0.42 | 80 | 0.2484 | 0 | 2.625 | 2.3766 | 2.3766 |  | 110 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.75 | 1.4184 | 0.42 | 80 | 0.9984 | 0 | 2.625 | 1.6266 | 1.6266
111 | SS-35/6kv Zapadnaya | 10+10+10 | 6552 | 3360 | 7.3633 | 1.707 | 120 | 5.6563 | 0 | 21 | 15.3437 | 15.3437 |  | 111 | SS-35/6kv Zapadnaya | 10+10+10 | 0 | 7.3633 | 1.707 | 120 | 5.6563 | 0 | 21 | 15.3437 | 15.3437
112 | SS-35/10kv Zozuli | 6,3+6,3 | 5744 | 3088 | 6.5214 | 3.88 | 80 | 2.6414 | 0 | 6.615 | 3.9736 | 3.9736 |  | 112 | SS-35/10kv Zozuli | 6,3+6,3 | 0.014 | 6.5354 | 3.88 | 80 | 2.6554 | 0 | 6.615 | 3.9596 | 3.9596
113 | SS-35/10kv Ivitsa | 2,5+2,5 | 1192 | 392 | 1.2548 | 0.58603 | 80 | 0.66877 | 0 | 2.625 | 1.9562 | 1.9562 |  | 113 | SS-35/10kv Ivitsa | 2,5+2,5 | 0 | 1.2548 | 0.58603 | 80 | 0.66877 | 0 | 2.625 | 1.9562 | 1.9562
114 | SS-35/10kv Ilovka | 4+4 | 2872 | 904 | 3.0109 | 2.056 | 45 | 0.95491 | 0 | 4.2 | 3.2451 | 3.2451 |  | 114 | SS-35/10kv Ilovka | 4+4 | 0 | 3.0109 | 2.056 | 45 | 0.95491 | 0 | 4.2 | 3.2451 | 3.2451
115 | SS-35/10kv Istobnoe | 4+2,5 | 1224 | 632 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868 |  | 115 | SS-35/10kv Istobnoe | 4+2,5 | 0 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868
116 | SS-35/10kv Kazatskaya | 2,5+4 | 1589 | 525 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229 |  | 116 | SS-35/10kv Kazatskaya | 2,5+4 | 0 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229
117 | SS-35/10kv Kazinka | 4+4 | 2412 | 672 | 2.5039 | 0.736 | 120 | 1.7679 | 0 | 4.2 | 2.4321 | 2.4321 |  | 117 | SS-35/10kv Kazinka | 4+4 | 0 | 2.5039 | 0.736 | 120 | 1.7679 | 0 | 4.2 | 2.4321 | 2.4321
118 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1040 | 360 | 1.1005 | 0.712 | 120 | 0.38855 | 0 | 2.625 | 2.2365 | 2.2365 |  | 118 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 0 | 1.1005 | 0.712 | 120 | 0.38855 | 0 | 2.625 | 2.2365 | 2.2365
119 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3132 | 1536 | 3.4884 | 0.7035 | 120 | 2.7849 | 0 | 6.615 | 3.8301 | 3.8301 |  | 119 | SS-35/10kv Kirovskaya | 6,3+6,3 | 0 | 3.4884 | 0.7035 | 120 | 2.7849 | 0 | 6.615 | 3.8301 | 3.8301
120 | SS-35/10kv Kotovo | 2,5+2,5 | 2672 | 768 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928 |  | 120 | SS-35/10kv Kotovo | 2,5+2,5 | 0 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928
121 | SS-35/10kv Kochetovka | 2,5+4 | 858 | 294 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466 |  | 121 | SS-35/10kv Kochetovka | 2,5+4 | 0 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466
122 | SS-35/10kv Krasnoe | 4+2,5 | 1128 | 424 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595 |  | 122 | SS-35/10kv Krasnoe | 4+2,5 | 0 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595
123 | SS-35/10kv Kretovo | 4+2,5 | 1096 | 508 | 1.208 | 0.67818 | 120 | 0.52983 | 0 | 2.625 | 2.0952 | 2.0952 |  | 123 | SS-35/10kv Kretovo | 4+2,5 | 0 | 1.208 | 0.67818 | 120 | 0.52983 | 0 | 2.625 | 2.0952 | 2.0952
124 | SS-35/10kv Kurasovka | 4+4 | 2800 | 1168 | 3.0338 | 1.797 | 80 | 1.2368 | 0 | 4.2 | 2.9632 | 2.9632 |  | 124 | SS-35/10kv Kurasovka | 4+4 | 0 | 3.0338 | 1.797 | 80 | 1.2368 | 0 | 4.2 | 2.9632 | 2.9632
125 | SS-35/6kv Lebedi | 4+5,6 | 4392 | 1469 | 4.6312 | 0.581 | 120 | 4.0502 | 0 | 4.2 | 0.14984 | 0.14984 |  | 125 | SS-35/6kv Lebedi | 4+5,6 | 0 | 4.6312 | 0.581 | 120 | 4.0502 | 0 | 4.2 | 0.14984 | 0.14984
126 | SS-35/6kv Ledovaya | 4+4 | 2578 | 1325 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224 |  | 126 | SS-35/6kv Ledovaya | 4+4 | 0 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224
127 | SS-35/10kv Livenka | 4+4 | 3360 | 2364 | 4.1083 | 1.541 | 120 | 2.5673 | 0 | 4.2 | 1.6327 | 1.6327 |  | 127 | SS-35/10kv Livenka | 4+4 | 0 | 4.1083 | 1.541 | 120 | 2.5673 | 0 | 4.2 | 1.6327 | 1.6327
128 | SS-35/10kv Lubyanoe | 2,5+2,5 | 828 | 336 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981 |  | 128 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981
129 | SS-35/10kv M.Pristan | 6,3+6,3 | 6264 | 2844 | 6.8794 | 1.81 | 45 | 5.0694 | 0 | 6.615 | 1.5456 | 1.5456 |  | 129 | SS-35/10kv M.Pristan | 6,3+6,3 | 0.06 | 6.9394 | 1.81 | 45 | 5.1294 | 0 | 6.615 | 1.4856 | 1.4856
130 | SS-35/10kv М.Troitsa | 2,5+2,5 | 568 | 368 | 0.67679 | 0.60716 | 80 | 0.069632 | 0 | 2.625 | 2.5554 | 2.5554 |  | 130 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.01 | 0.68679 | 0.60716 | 80 | 0.079632 | 0 | 2.625 | 2.5454 | 2.5454
131 | SS-35/10kv Malinovka | 10+10 | 5808 | 3776 | 6.9276 | 1.357 | 120 | 5.5706 | 0 | 10.5 | 4.9294 | 4.9294 |  | 131 | SS-35/10kv Malinovka | 10+10 | 1.233 | 8.1606 | 1.357 | 120 | 6.8036 | 0 | 10.5 | 3.6964 | 3.6964
132 | SS-35/10kv Mandrovo | 2,5+2,5 | 1488 | 438 | 1.5511 | 0.65565 | 80 | 0.89548 | 0 | 2.625 | 1.7295 | 1.7295 |  | 132 | SS-35/10kv Mandrovo | 2,5+2,5 | 0 | 1.5511 | 0.65565 | 80 | 0.89548 | 0 | 2.625 | 1.7295 | 1.7295
133 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1362 | 510 | 1.4544 | 0.643 | 80 | 0.81135 | 0 | 2.625 | 1.8136 | 1.8136 |  | 133 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 0 | 1.4544 | 0.643 | 80 | 0.81135 | 0 | 2.625 | 1.8136 | 1.8136
134 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1110 | 522 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915 |  | 134 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 0 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915
135 | SS-35/10kv N.Derevnya | 6,3+6,3 | 5888 | 1920 | 6.1931 | 2.78 | 120 | 3.4131 | 0 | 6.615 | 3.2019 | 3.2019 |  | 135 | SS-35/10kv N.Derevnya | 6,3+6,3 | 0.274 | 6.4671 | 2.78 | 120 | 3.6871 | 0 | 6.615 | 2.9279 | 2.9279
136 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 3360 | 912 | 3.4816 | 0.842 | 45 | 2.6396 | 0 | 6.615 | 3.9754 | 3.9754 |  | 136 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 0 | 3.4816 | 0.842 | 45 | 2.6396 | 0 | 6.615 | 3.9754 | 3.9754
137 | SS-35/10kv N.Ukolovo | 4+2,5 | 1608 | 764 | 1.7803 | 0.57 | 80 | 1.2103 | 0 | 2.625 | 1.4147 | 1.4147 |  | 137 | SS-35/10kv N.Ukolovo | 4+2,5 | 0 | 1.7803 | 0.57 | 80 | 1.2103 | 0 | 2.625 | 1.4147 | 1.4147
138 | SS-35/10kv N.Khutornoe | 2,5+4 | 294 | 142 | 0.3265 | 0.19 | 80 | 0.1365 | 0 | 2.625 | 2.4885 | 2.4885 |  | 138 | SS-35/10kv N.Khutornoe | 2,5+4 | 0 | 0.3265 | 0.19 | 80 | 0.1365 | 0 | 2.625 | 2.4885 | 2.4885
139 | SS-35/10kv Neminushchee | 4+2,5 | 1474 | 706 | 1.6344 | 0.65147 | 80 | 0.98288 | 0 | 2.625 | 1.6421 | 1.6421 |  | 139 | SS-35/10kv Neminushchee | 4+2,5 | 0 | 1.6344 | 0.65147 | 80 | 0.98288 | 0 | 2.625 | 1.6421 | 1.6421
140 | SS-35/10kv Nechaevka | 4+4 | 1328 | 392 | 1.3846 | 0.451 | 120 | 0.93365 | 0 | 4.2 | 3.2664 | 3.2664 |  | 140 | SS-35/10kv Nechaevka | 4+4 | 0.055 | 1.4396 | 0.451 | 120 | 0.98865 | 0 | 4.2 | 3.2114 | 3.2114
141 | SS-35/10kv Nikitovka | 2,5+2,5 | 1888 | 744 | 2.0293 | 1.4354 | 80 | 0.59387 | 0 | 2.625 | 2.0311 | 2.0311 |  | 141 | SS-35/10kv Nikitovka | 2,5+2,5 | 0 | 2.0293 | 1.4354 | 80 | 0.59387 | 0 | 2.625 | 2.0311 | 2.0311
142 | SS-35/10kv Novenkoe | 4+4 | 2216 | 964 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166 |  | 142 | SS-35/10kv Novenkoe | 4+4 | 0 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166
143 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 7040 | 2384 | 7.4327 | 0.872 | 80 | 6.5607 | 0 | 6.615 | 0.054298 | 0.054298 |  | 143 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.088 | 7.5207 | 0.872 | 80 | 6.6487 | 0 | 6.615 | -0.033702 | -0.033702
144 | SS-35/10kv Orlik | 4+4 | 2172 | 768 | 2.3038 | 0.553 | 80 | 1.7508 | 0 | 4.2 | 2.4492 | 2.4492 |  | 144 | SS-35/10kv Orlik | 4+4 | 0 | 2.3038 | 0.553 | 80 | 1.7508 | 0 | 4.2 | 2.4492 | 2.4492
145 | SS-35/10kv Podolkhi | 2,5+2,5 | 1528 | 664 | 1.666 | 1.1225 | 45 | 0.54355 | 0 | 2.625 | 2.0815 | 2.0815 |  | 145 | SS-35/10kv Podolkhi | 2,5+2,5 | 0 | 1.666 | 1.1225 | 45 | 0.54355 | 0 | 2.625 | 2.0815 | 2.0815
146 | SS-35/10kv Popovka | 6,3+4 | 1152 | 528 | 1.2672 | 0.64636 | 80 | 0.62088 | 0 | 4.2 | 3.5791 | 3.5791 |  | 146 | SS-35/10kv Popovka | 6,3+4 | 0 | 1.2672 | 0.64636 | 80 | 0.62088 | 0 | 4.2 | 3.5791 | 3.5791
147 | SS-35/10kv Prelestnoe | 4+4 | 2268 | 780 | 2.3984 | 0 |  | 2.3984 | 0 | 4.2 | 1.8016 | 1.8016 |  | 147 | SS-35/10kv Prelestnoe | 4+4 | 0.41 | 2.8084 | 0 |  | 2.8084 | 0 | 4.2 | 1.3916 | 1.3916
148 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5357 | 2160 | 5.7761 | 0 |  | 5.7761 | 0 | 6.615 | 0.83892 | 0.83892 |  | 148 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 0 | 5.7761 | 0 |  | 5.7761 | 0 | 6.615 | 0.83892 | 0.83892
149 | SS-35/10kv Prilepy | 2,5+2,5 | 544 | 360 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 |  | 149 | SS-35/10kv Prilepy | 2,5+2,5 | 0 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349
150 | SS-35/10kv Printsevka | 2,5+2,5 | 1502 | 424 | 1.5607 | 0.352 | 120 | 1.2087 | 0 | 2.625 | 1.4163 | 1.4163 |  | 150 | SS-35/10kv Printsevka | 2,5+2,5 | 0 | 1.5607 | 0.352 | 120 | 1.2087 | 0 | 2.625 | 1.4163 | 1.4163
151 | SS-35/10kv Radkovka | 6,3+6,3 | 2624 | 992 | 2.8053 | 0.164 | 45 | 2.6413 | 0 | 6.615 | 3.9737 | 3.9737 |  | 151 | SS-35/10kv Radkovka | 6,3+6,3 | 0.05 | 2.8553 | 0.164 | 45 | 2.6913 | 0 | 6.615 | 3.9237 | 3.9237
152 | SS-35/10kv Razdornoe | 2,5+2,5 | 1314 | 576 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | 1.8523 |  | 152 | SS-35/10kv Razdornoe | 2,5+2,5 | 0.03 | 1.4647 | 0.662 | 80 | 0.8027 | 0 | 2.625 | 1.8223 | 1.8223
153 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1464 | 736 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | 1.8713 |  | 153 | SS-35/10kv Repyakhovka | 2,5+2,5 | 0.015 | 1.6536 | 0.88491 | 80 | 0.76868 | 0 | 2.625 | 1.8563 | 1.8563
154 | SS-35/10kv Rzhevka | 10+10 | 6576 | 3408 | 7.4066 | 2.53 | 45 | 4.8766 | 0 | 10.5 | 5.6234 | 5.6234 |  | 154 | SS-35/10kv Rzhevka | 10+10 | 0 | 7.4066 | 2.53 | 45 | 4.8766 | 0 | 10.5 | 5.6234 | 5.6234
155 | SS-35/10kv Rovenki | 4+4 | 3240 | 1272 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586 |  | 155 | SS-35/10kv Rovenki | 4+4 | 0 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586
156 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1536 | 720 | 1.6964 | 0 |  | 1.6964 | 0 | 2.625 | 0.92862 | 0.92862 |  | 156 | SS-35/10kv Rogovatoe | 2,5+2,5 | 0 | 1.6964 | 0 |  | 1.6964 | 0 | 2.625 | 0.92862 | 0.92862
157 | SS-35/10kv Saprykino | 2,5+2,5 | 384 | 192 | 0.42933 | 0.22751 | 120 | 0.20181 | 0 | 2.625 | 2.4232 | 2.4232 |  | 157 | SS-35/10kv Saprykino | 2,5+2,5 | 0 | 0.42933 | 0.22751 | 120 | 0.20181 | 0 | 2.625 | 2.4232 | 2.4232
158 | SS-35/6kv Severnaya | 6,3+6,3 | 6264 | 1887 | 6.5421 | 4.8049 | 120 | 1.7371 | 0 | 6.615 | 4.8779 | 4.8779 |  | 158 | SS-35/6kv Severnaya | 6,3+6,3 | 0.012 | 6.5541 | 4.8049 | 120 | 1.7491 | 0 | 6.615 | 4.8659 | 4.8659
159 | SS-35/10kv Setishche | 2,5+2,5 | 1830 | 852 | 2.0186 | 1.0621 | 80 | 0.9565 | 0 | 2.625 | 1.6685 | 1.6685 |  | 159 | SS-35/10kv Setishche | 2,5+2,5 | 0.01 | 2.0286 | 1.0621 | 80 | 0.9665 | 0 | 2.625 | 1.6585 | 1.6585
160 | SS-35/10kv Slonovka | 4+4 | 2224 | 1392 | 2.6237 | 1.1306 | 120 | 1.4931 | 0 | 4.2 | 2.7069 | 2.7069 |  | 160 | SS-35/10kv Slonovka | 4+4 | 0 | 2.6237 | 1.1306 | 120 | 1.4931 | 0 | 4.2 | 2.7069 | 2.7069
161 | SS-35/6kv St.Oskol -2 | 16+16 | 11806 | 4574 | 12.6611 | 1.21 | 80 | 11.4511 | 0 | 16.8 | 5.3489 | 5.3489 |  | 161 | SS-35/6kv St.Oskol -2 | 16+16 | 0.03 | 12.6911 | 1.21 | 80 | 11.4811 | 0 | 16.8 | 5.3189 | 5.3189
162 | SS-35/10kv Starikovo | 4+4 | 1464 | 660 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394 |  | 162 | SS-35/10kv Starikovo | 4+4 | 0 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394
163 | SS-35/10kv Tavrovo | 10+10 | 8592 | 1296 | 8.6892 | 0.531 | 45 | 8.1582 | 0 | 10.5 | 2.3418 | 2.3418 |  | 163 | SS-35/10kv Tavrovo | 10+10 | 0.21 | 8.8992 | 0.531 | 45 | 8.3682 | 0 | 10.5 | 2.1318 | 2.1318
164 | SS-35/10kv Terebrino | 2,5+2,5 | 1116 | 636 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903 |  | 164 | SS-35/10kv Terebrino | 2,5+2,5 | 0 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903
165 | SS-35/10kv Urazovo | 6,3+6,3 | 4776 | 1524 | 5.0133 | 1.39 | 120 | 3.6233 | 0 | 6.615 | 2.9917 | 2.9917 |  | 165 | SS-35/10kv Urazovo | 6,3+6,3 | 0 | 5.0133 | 1.39 | 120 | 3.6233 | 0 | 6.615 | 2.9917 | 2.9917
166 | SS-35/10kv Utochka | 1,6+2,5 | 682 | 272 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182 |  | 166 | SS-35/10kv Utochka | 1,6+2,5 | 0 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182
167 | SS-35/6kv Fedoseevka | 4+4 | 2160 | 682 | 2.2651 | 0 |  | 2.2651 | 0 | 4.2 | 1.9349 | 1.9349 |  | 167 | SS-35/6kv Fedoseevka | 4+4 | 0 | 2.2651 | 0 |  | 2.2651 | 0 | 4.2 | 1.9349 | 1.9349
168 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 980 | 408 | 1.0615 | 0.78681 | 45 | 0.27473 | 0 | 1.68 | 1.4053 | 1.4053 |  | 168 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0.01 | 1.0715 | 0.78681 | 45 | 0.28473 | 0 | 1.68 | 1.3953 | 1.3953
169 | SS-35/10kv Kholodnoe | 4+4 | 1708 | 516 | 1.7842 | 0 |  | 1.7842 | 0 | 4.2 | 2.4158 | 2.4158 |  | 169 | SS-35/10kv Kholodnoe | 4+4 | 0.015 | 1.7992 | 0 |  | 1.7992 | 0 | 4.2 | 2.4008 | 2.4008
170 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1608 | 1128 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021 |  | 170 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 0 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021
171 | SS-35/10kv Shatalovka | 6,3+6,3 | 1928 | 736 | 2.0637 | 0 |  | 2.0637 | 0 | 6.615 | 4.5513 | 4.5513 |  | 171 | SS-35/10kv Shatalovka | 6,3+6,3 | 0.15 | 2.2137 | 0 |  | 2.2137 | 0 | 6.615 | 4.4013 | 4.4013
172 | SS-35/10kv Shakhovka | 2,5+2,5 | 1596 | 588 | 1.7009 | 0.79066 | 80 | 0.91021 | 0 | 2.625 | 1.7148 | 1.7148 |  | 172 | SS-35/10kv Shakhovka | 2,5+2,5 | 0 | 1.7009 | 0.79066 | 80 | 0.91021 | 0 | 2.625 | 1.7148 | 1.7148
173 | SS-35/10kv Shishino | 4+6,3 | 3456 | 904 | 3.5723 | 1.03 | 80 | 2.5423 | 0 | 4.2 | 1.6577 | 1.6577 |  | 173 | SS-35/10kv Shishino | 4+6,3 | 0.01 | 3.5823 | 1.03 | 80 | 2.5523 | 0 | 4.2 | 1.6477 | 1.6477
174 | SS-35/10kv Yablonovo | 4+4 | 1664 | 688 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278 |  | 174 | SS-35/10kv Yablonovo | 4+4 | 0 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278
175 | SS-35/10kv Yarskoe | 2,5+2,5 | 504 | 264 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025 |  | 175 | SS-35/10kv Yarskoe | 2,5+2,5 | 0 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025
| TOTAL: | 3186.9 |  |  | #N/A | #N/A |  | #N/A | [5 empty] | 2: TOTAL:; 3: 3186.9; 4: #N/A; 5: 1157.304; MVA 6: 453.9275; min. 8: 703.3765
| deficit | [10 empty] | 10.268 |  | 2: deficit; min. 12: 11.278
| proficit | [10 empty] | 878.691 |  | 2: proficit; min. 12: 854.081

## Тамбовэнерго 3
[9 empty] | table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS 110 kv | [11 empty] | 1: SS 110 kv
1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 19.2 |  |  | 19.2 | 0 | 26.25 | 7.05 | 7.05 | opened | 1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 0 | 19.2 |  |  | 19.2 | 0 | 26.25 | 7.05 | 7.05 | opened
2 | SS 110/6 Tambovskaya No.3 | 2*25 | 18.44 |  |  | 18.44 | 0 | 26.25 | 7.81 | 7.81 | opened | 2 | SS 110/6 Tambovskaya No.3 | 2*25 | 0 | 18.44 |  |  | 18.44 | 0 | 26.25 | 7.81 | 7.81 | opened
3 | SS 110/6 Tambovskaya No.5 | 16 + 25 | 16.45 |  |  | 16.45 | 12.5 | 13.125 | -3.32 | -3.32 | closed | 3 | SS 110/6 Tambovskaya No.5 | 16 + 25 | 0 | 16.45 |  |  | 16.45 | 0 | 16.8 | 0.35 | 0.35 | opened
4 | SS 110/6 Tambovskaya No.7 | 2*25 | 21.18 |  |  | 21.18 | 0 | 26.25 | 5.07 | 5.07 | opened | 4 | SS 110/6 Tambovskaya No.7 | 2*25 | 0 | 21.18 |  |  | 21.18 | 0 | 26.25 | 5.07 | 5.07 | opened
5 | SS 110/35/6 Pigment | 2*63 | 33.98 | 27.68 | 80 | 6.3 | 0 | 66.15 | 59.85 | 59.85 | opened | 5 | SS 110/35/6 Pigment | 2*63 | 0 | 33.98 | 27.68 | 80 | 6.3 | 0 | 66.15 | 59.85 | 59.85 | opened
6 | SS 110/6 Tambovskaya No.8 | 40+16 | 13.09 |  |  | 13.09 | 20 | 16.8 | 3.71 | 3.71 | opened | 6 | SS 110/6 Tambovskaya No.8 | 40+16 | 2.24 | 15.33 |  |  | 15.33 | 0 | 16.8 | 1.47 | 1.47 | opened
7 | SS 110/35/6 Malinovskaya | 2*40 | 12.73 | 4.75 | 120 | 7.98 | 0 | 42 | 34.02 | 34.02 | opened | 7 | SS 110/35/6 Malinovskaya | 2*40 | 0 | 12.73 | 4.75 | 120 | 7.98 | 0 | 42 | 34.02 | 34.02 | opened
8 | SS 110/35/10 Tambovskaya No.6 | 2*10 | 9.59 | 1.25 | 120 | 8.34 | 0 | 10.5 | 2.16 | 2.16 | opened | 8 | SS 110/35/10 Tambovskaya No.6 | 2*10 | 2.06 | 11.65 | 1.25 | 120 | 10.4 | 0 | 10.5 | 0.1 | 0.1 | opened
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5.08 | 1.62 | 120 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | opened | 9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 0 | 5.08 | 7.18 | 120 | -2.1 | 0 | 6.615 | 8.715 | 8.715 | opened
10 | SS 110/35/10 Komsomolskaya | 2*10 | 8.81 | 4 | 80 | 4.81 | 0 | 10.5 | 5.69 | 5.69 | opened | 10 | SS 110/35/10 Komsomolskaya | 2*10 | 0.67 | 9.48 | 4 | 80 | 5.48 | 0 | 10.5 | 5.02 | 5.02 | opened
11 | SS 110/10 М.Talinskaya | 10 | 0.68 | 0.52 | 24 hours | 0.16 | 0 | 10.5 | 10.34 | 10.34 | opened | 11 | SS 110/10 М.Talinskaya | 10 | 0 | 0.68 | 0.52 | 24 hours | 0.16 | 0 | 10.5 | 10.34 | 10.34 | opened
12 | SS 110/35/10 Promyshlennaya | 2*40 | 25.61 | 10.2 | 120 | 15.41 | 0 | 42 | 26.59 | 26.59 | opened | 12 | SS 110/35/10 Promyshlennaya | 2*40 | 0.07 | 25.68 | 10.2 | 120 | 15.48 | 0 | 42 | 26.52 | 26.52 | opened
13 | SS 110/35/10 Arzhenskaya | 2*10 | 5.46 | 3.92 | 80 | 1.54 | 0 | 10.5 | 8.96 | 8.96 | opened | 13 | SS 110/35/10 Arzhenskaya | 2*10 | 0 | 5.46 | 3.92 | 80 | 1.54 | 0 | 10.5 | 8.96 | 8.96 | opened
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened | 14 | SS 110/10 Teleshovskaya | 2*2,5 | 0 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
15 | SS 110/6 Oktyabrskaya | 2*25 | 7.83 |  |  | 7.83 | 0 | 26.25 | 18.42 | 18.42 | opened | 15 | SS 110/6 Oktyabrskaya | 2*25 | 0 | 7.83 |  |  | 7.83 | 0 | 26.25 | 18.42 | 18.42 | opened
16 | SS 110/10 Spasskaya | 2*6,3 | 2.43 |  |  | 2.43 | 0 | 6.615 | 4.185 | 4.185 | opened | 16 | SS 110/10 Spasskaya | 2*6,3 | 0 | 2.43 |  |  | 2.43 | 0 | 6.615 | 4.185 | 4.185 | opened
17 | SS 110/35/10 Kuzminskaya | 16+10 | 7.41 | 5.02 | 45 | 2.39 | 0 | 10.5 | 8.11 | 8.11 | opened | 17 | SS 110/35/10 Kuzminskaya | 16+10 | 0 | 7.41 | 5.02 | 45 | 2.39 | 0 | 10.5 | 8.11 | 8.11 | opened
18 | SS 110/35/10 Sampurskaya | 10+16 | 6.73 | 4.33 | 80 | 2.4 | 0 | 10.5 | 8.1 | 8.1 | opened | 18 | SS 110/35/10 Sampurskaya | 10+16 | 2.94 | 9.67 | 4.33 | 80 | 5.34 | 0 | 10.5 | 5.16 | 5.16 | opened
19 | SS 110/6 Leather plant | 2*10 | 1.37 |  |  | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened | 19 | SS 110/6 Leather plant | 2*10 | 0 | 1.37 |  |  | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 17.49 | 3.04 | 120 | 14.45 | 0 | 21 | 6.55 | 6.55 | opened | 20 | SS 110/35/6 Rasskazovskaya | 25+20 | 0 | 17.49 | 3.04 | 120 | 14.45 | 0 | 21 | 6.55 | 6.55 | opened
21 | SS 110/35/10 Volchkovskaya | 2*10 | 3.5 | 0.95 | 120 | 2.55 | 0 | 10.5 | 7.95 | 7.95 | opened | 21 | SS 110/35/10 Volchkovskaya | 2*10 | 0 | 3.5 | 0.95 | 120 | 2.55 | 0 | 10.5 | 7.95 | 7.95 | opened
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 2.89 | 1.66 | 120 | 1.23 | 0 | 6.615 | 5.385 | 5.385 | opened | 22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 0 | 2.89 | 1.66 | 120 | 1.23 | 0 | 6.615 | 5.385 | 5.385 | opened
23 | SS 110/35/10 Khmelevskaya | 2*10 | 3.83 | 0.92 | 120 | 2.91 | 0 | 10.5 | 7.59 | 7.59 | opened | 23 | SS 110/35/10 Khmelevskaya | 2*10 | 0.17 | 4 | 0.92 | 120 | 3.08 | 0 | 10.5 | 7.42 | 7.42 | opened
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.93 | 2.84 | 80 | 3.09 | 0 | 6.615 | 3.525 | 3.525 | opened | 24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 0 | 5.93 | 2.84 | 80 | 3.09 | 0 | 6.615 | 3.525 | 3.525 | opened
25 | SS 110/35/10 Nikiforvskaya | 10+16 | 5.07 | 2.81 | 120 | 2.26 | 0 | 10.5 | 8.24 | 8.24 | opened | 25 | SS 110/35/10 Nikiforvskaya | 10+16 | 0 | 5.07 | 2.81 | 120 | 2.26 | 0 | 10.5 | 8.24 | 8.24 | opened
26 | SS 110/10 N.Seslavinskaya | 2.5 | 0.41 | 0.47 | 24 hours | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened | 26 | SS 110/10 N.Seslavinskaya | 2.5 | 0 | 0.41 | 0.47 | 24 hours | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.39 | 0.19 | 24 hours | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.09 | 0.48 | 0.19 | 24 hours | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 28 | SS 110/10 Ilovayskaya | 2*2,5 | 0 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
29 | SS 110/35/10 Yuzhnaya | 16 | 9.72 | 8.51 | 24 hours | 1.21 | 0 | 16.8 | 15.59 | 15.59 | opened | 29 | SS 110/35/10 Yuzhnaya | 16 | 0 | 9.72 | 8.51 | 24 hours | 1.21 | 0 | 16.8 | 15.59 | 15.59 | opened
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 23.36 | 9.45 | 120 | 13.91 | 0 | 33.075 | 19.165 | 19.165 | opened | 30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 0.24 | 23.6 | 9.45 | 120 | 14.15 | 0 | 33.075 | 18.925 | 18.925 | opened
31 | SS 110/35/10 Sosnovskaya | 2*16 | 7.19 | 6.6 | 80 | 0.59 | 0 | 16.8 | 16.21 | 16.21 | opened | 31 | SS 110/35/10 Sosnovskaya | 2*16 | 0 | 7.19 | 6.6 | 80 | 0.59 | 0 | 16.8 | 16.21 | 16.21 | opened
32 | SS 110/35/10 Pichaevskaya | 2*10 | 3.68 | 4.19 | 80 | -0.51 | 0 | 10.5 | 11.01 | 11.01 | opened | 32 | SS 110/35/10 Pichaevskaya | 2*10 | 0 | 3.68 | 4.19 | 80 | -0.51 | 0 | 10.5 | 11.01 | 11.01 | opened
33 | SS 110/35/10 Algasovskaya | 2*40 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened | 33 | SS 110/35/10 Algasovskaya | 2*40 | 0 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened
34 | SS 110/35/6 Morshanskaya | 40+25 | 16.96 | 7.2005 | 120 | 9.7595 | 0 | 26.25 | 16.4905 | 16.4905 | opened | 34 | SS 110/35/6 Morshanskaya | 40+25 | 0 | 16.96 | 7.2005 | 120 | 9.7595 | 0 | 26.25 | 16.4905 | 16.4905 | opened
35 | SS 110/35/6 Kamvolnaya | 16+25 | 8.19 | 7.2 | 80 | 0.99 | 0 | 16.8 | 15.81 | 15.81 | opened | 35 | SS 110/35/6 Kamvolnaya | 16+25 | 0 | 8.19 | 7.2 | 80 | 0.99 | 0 | 16.8 | 15.81 | 15.81 | opened
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 1.4 | 0.63 | 120 | 0.77 | 0 | 10.5 | 9.73 | 9.73 | opened | 36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 0.35 | 1.75 | 0.63 | 120 | 1.12 | 0 | 10.5 | 9.38 | 9.38 | opened
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 5.21 | 2.05 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened | 37 | SS 110/35/10 Nashchekinskaya | 2*10 | 0 | 5.21 | 2.05 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened
38 | SS 110/10 Shachinskaya | 2.5 | 0.61 | 0.054495 | 24 hours | 0.55551 | 0 | 2.625 | 2.0695 | 2.0695 | opened | 38 | SS 110/10 Shachinskaya | 2.5 | 0 | 0.61 | 0.054495 | 24 hours | 0.55551 | 0 | 2.625 | 2.0695 | 2.0695 | opened
39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 9.88 | 9.027 | 45 | 0.85301 | 0 | 16.8 | 15.947 | 15.947 | opened | 39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 0 | 9.88 | 9.027 | 45 | 0.85301 | 0 | 16.8 | 15.947 | 15.947 | opened
40 | SS 110/35/10 Muchkapskaya | 2*10 | 3.68 | 1.3519 | 120 | 2.3281 | 0 | 10.5 | 8.1719 | 8.1719 | opened | 40 | SS 110/35/10 Muchkapskaya | 2*10 | 0 | 3.68 | 1.3519 | 120 | 2.3281 | 0 | 10.5 | 8.1719 | 8.1719 | opened
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.88 | 0.66667 | 120 | 0.21333 | 0 | 2.625 | 2.4117 | 2.4117 | opened | 41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0 | 0.88 | 0.66667 | 120 | 0.21333 | 0 | 2.625 | 2.4117 | 2.4117 | opened
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.94 | 1.2921 | 120 | 0.64795 | 0 | 10.5 | 9.8521 | 9.8521 | opened | 42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 0 | 1.94 | 1.2921 | 120 | 0.64795 | 0 | 10.5 | 9.8521 | 9.8521 | opened
43 | SS 110/10 Shpikulovskaya | 2*2,5 | 0.68 | 0.61404 | 120 | 0.065965 | 0 | 2.625 | 2.559 | 2.559 | opened | 43 | SS 110/10 Shpikulovskaya | 2*2,5 | 0.21 | 0.89 | 0.61404 | 120 | 0.27596 | 0 | 2.625 | 2.349 | 2.349 | opened
44 | SS 110/35/10 Zherdevskaya | 2*16 | 8.1 | 5.6533 | 80 | 2.4467 | 0 | 16.8 | 14.3533 | 14.3533 | opened | 44 | SS 110/35/10 Zherdevskaya | 2*16 | 0 | 8.1 | 5.6533 | 80 | 2.4467 | 0 | 16.8 | 14.3533 | 14.3533 | opened
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.95 | 0.58824 | 120 | 4.3618 | 0 | 10.5 | 6.1382 | 6.1382 | opened | 45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 0 | 4.95 | 0.58824 | 120 | 4.3618 | 0 | 10.5 | 6.1382 | 6.1382 | opened
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.86 | 0.42105 | 120 | 0.43895 | 0 | 2.625 | 2.1861 | 2.1861 | opened | 46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0 | 0.86 | 0.42105 | 120 | 0.43895 | 0 | 2.625 | 2.1861 | 2.1861 | opened
47 | SS 110/35/10 Tokarevskaya | 2*25 | 8.34 | 6.0846 | 120 | 2.2554 | 0 | 26.25 | 23.9946 | 23.9946 | opened | 47 | SS 110/35/10 Tokarevskaya | 2*25 | 0 | 8.34 | 6.0846 | 120 | 2.2554 | 0 | 26.25 | 23.9946 | 23.9946 | opened
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 1.13 | 0.90918 | 120 | 0.22082 | 0 | 6.615 | 6.3942 | 6.3942 | opened | 48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0 | 1.13 | 0.90918 | 120 | 0.22082 | 0 | 6.615 | 6.3942 | 6.3942 | opened
49 | SS 110/35/10 Mordovskaya | 2*10 | 3.44 | 1.8937 | 120 | 1.5463 | 0 | 10.5 | 8.9537 | 8.9537 | opened | 49 | SS 110/35/10 Mordovskaya | 2*10 | 0.74 | 4.18 | 1.8937 | 120 | 2.2863 | 0 | 10.5 | 8.2137 | 8.2137 | opened
50 | SS 110/35/10 Pavlovskaya | 10 | 1.58 | 1.56 | 24 hours | 0.02 | 0 | 10.5 | 10.48 | 10.48 | opened | 50 | SS 110/35/10 Pavlovskaya | 10 | 0 | 1.58 | 1.56 | 24 hours | 0.02 | 0 | 10.5 | 10.48 | 10.48 | opened
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 13.32 | 5.989 | 120 | 7.331 | 0 | 26.25 | 18.919 | 18.919 | opened | 51 | SS 110/35/10 Kirsanovskaya | 2*25 | 0 | 13.32 | 5.989 | 120 | 7.331 | 0 | 26.25 | 18.919 | 18.919 | opened
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 8.38 | 3.41 | 120 | 4.97 | 0 | 16.8 | 11.83 | 11.83 | opened | 52 | SS 110/35/10 Inzhavinskaya | 2*16 | 0.22 | 8.6 | 3.41 | 120 | 5.19 | 0 | 16.8 | 11.61 | 11.61 | opened
53 | SS 110/35/10 Umyotskaya | 2*10 | 1.03 | 4.5 | 80 | -3.47 | 0 | 10.5 | 13.97 | 13.97 | opened | 53 | SS 110/35/10 Umyotskaya | 2*10 | 0 | 1.03 | 4.5 | 80 | -3.47 | 0 | 10.5 | 13.97 | 13.97 | opened
54 | SS 110/35/10 Kovylskaya | 2*10 | 1.27 | 1.347 | 120 | -0.077 | 0 | 10.5 | 10.577 | 10.577 | opened | 54 | SS 110/35/10 Kovylskaya | 2*10 | 0 | 1.27 | 1.347 | 120 | -0.077 | 0 | 10.5 | 10.577 | 10.577 | opened
55 | SS 110/10 Inokovskaya | 2.5 | 0.16 | 0.184 | 24 hours | -0.024 | 0 | 2.625 | 2.649 | 2.649 | opened | 55 | SS 110/10 Inokovskaya | 2.5 | 0 | 0.16 | 0.184 | 24 hours | -0.024 | 0 | 2.625 | 2.649 | 2.649 | opened
SS 35 kv | [11 empty] | 1: SS 35 kv
56 | SS 35/6 Pervomayskaya | 2*2,5 | 1.64 |  |  | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened | 56 | SS 35/6 Pervomayskaya | 2*2,5 | 0 | 1.64 |  |  | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened
57 | SS 35/10 Picherskaya | 2*2,5 | 0.68 |  |  | 0.68 | 0 | 2.625 | 1.945 | 1.945 | opened | 57 | SS 35/10 Picherskaya | 2*2,5 | 0 | 0.68 |  |  | 0.68 | 0 | 2.625 | 1.945 | 1.945 | opened
58 | SS 35/10 Osinovskaya | 2*2,5 | 1.01 |  |  | 1.01 | 0 | 2.625 | 1.615 | 1.615 | opened | 58 | SS 35/10 Osinovskaya | 2*2,5 | 0 | 1.01 |  |  | 1.01 | 0 | 2.625 | 1.615 | 1.615 | opened
59 | SS 35/10 Koptevskaya | 2*2,5 | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 59 | SS 35/10 Koptevskaya | 2*2,5 | 0 | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
60 | SS 35/10 Sayukinskaya | 2,5+4 | 0.6 | 0.5 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 60 | SS 35/10 Sayukinskaya | 2,5+4 | 0 | 0.6 | 0.5 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
61 | SS 35/10 Zelyonaya-1 | 2*4 | 2.68 |  |  | 2.68 | 0 | 4.2 | 1.52 | 1.52 | opened | 61 | SS 35/10 Zelyonaya-1 | 2*4 | 0 | 2.68 |  |  | 2.68 | 0 | 4.2 | 1.52 | 1.52 | opened
62 | SS 35/10 Pyatiletka | 2*4 | 0.29 |  |  | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened | 62 | SS 35/10 Pyatiletka | 2*4 | 0 | 0.29 |  |  | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened
64 | SS 35/10 Platonovskaya | 2*6,3 | 2.71 | 0.24 | 120 | 2.47 | 0 | 6.615 | 4.145 | 4.145 | opened | 64 | SS 35/10 Platonovskaya | 2*6,3 | 0 | 2.71 | 0.24 | 120 | 2.47 | 0 | 6.615 | 4.145 | 4.145 | opened
65 | SS 35/10 Znamenskaya | 2*4 | 3.53 | 1.54 | 120 | 1.99 | 0 | 4.2 | 2.21 | 2.21 | opened | 65 | SS 35/10 Znamenskaya | 2*4 | 0 | 3.53 | 1.54 | 120 | 1.99 | 0 | 4.2 | 2.21 | 2.21 | opened
66 | SS 35/10 Sukhotinskaya | 2.5 | 0.3 | 0 | 24 hours | 0.3 | 0 | 0 | -0.3 | -0.3 | closed | 66 | SS 35/10 Sukhotinskaya | 2.5 | 0 | 0.3 | 0 | 24 hours | 0.3 | 0 | 0 | -0.3 | -0.3 | closed
67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.91 |  |  | 0.91 | 0 | 1.68 | 0.77 | 0.77 | opened | 67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0 | 0.91 |  |  | 0.91 | 0 | 1.68 | 0.77 | 0.77 | opened
68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.45 | 0.29 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0 | 0.45 | 0.29 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
69 | SS 35/10 Stepnaya | 2*4 | 1.82 | 1.7 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened | 69 | SS 35/10 Stepnaya | 2*4 | 0 | 1.82 | 1.7 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
70 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 1.16 | 0.97 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened | 70 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 0 | 1.16 | 0.97 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened
71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.39 | 0.47 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened | 71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0 | 0.39 | 0.47 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened
72 | SS 35/10 Gorelskaya | 4+6,3 | 2.09 | 1.71 | 80 | 0.38 | 0 | 4.2 | 3.82 | 3.82 | opened | 72 | SS 35/10 Gorelskaya | 4+6,3 | 0.49 | 2.58 | 1.71 | 80 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened
73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.72 |  |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0 | 0.72 |  |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
74 | SS 35/10 Avangardskaya | 2*2,5 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened | 74 | SS 35/10 Avangardskaya | 2*2,5 | 0 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened
75 | SS 35/10 Suravskaya | 1,6+2,5 | 0.54 | 0.45 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 75 | SS 35/10 Suravskaya | 1,6+2,5 | 0 | 0.54 | 0.45 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
76 | SS 35/10 Seleznzyovskaya | 2*4 | 3.78 |  |  | 3.78 | 0 | 4.2 | 0.42 | 0.42 | opened | 76 | SS 35/10 Seleznzyovskaya | 3*4 | 0.82 | 4.6 |  |  | 4.6 | 0 | 8.4 | 3.8 | 3.8 | closed
77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.77 | 0.68 | 80 | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened | 77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 0.07 | 1.84 | 0.68 | 80 | 1.16 | 0 | 1.68 | 0.52 | 0.52 | opened
78 | SS 35/10 Viktorskaya | 2.5 | 0.62 |  |  | 0.62 | 0 | 0 | -0.62 | -0.62 | closed | 78 | SS 35/10 Viktorskaya | 2.5 | 0 | 0.62 |  |  | 0.62 | 0 | 0 | -0.62 | -0.62 | closed
79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.7 |  |  | 0.7 | 0 | 1.68 | 0.98 | 0.98 | opened | 79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0 | 0.7 |  |  | 0.7 | 0 | 1.68 | 0.98 | 0.98 | opened
80 | SS 35/10 Avdeevskaya | 2*2,5 | 0.83 |  |  | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened | 80 | SS 35/10 Avdeevskaya | 2*2,5 | 0 | 0.83 |  |  | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened
81 | SS 35/10 Tatanovskaya | 2*2,5 | 2.49 |  |  | 2.49 | 0 | 2.625 | 0.135 | 0.135 | opened | 81 | SS 35/10 Tatanovskaya | 2*2,5 | 0 | 2.49 |  | 120 | 2.49 | 0 | 2.625 | 0.135 | 0.135 | opened
82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 3.35 | 0.63 | 60 | 2.72 | 0 | 5.25 | 2.53 | 2.53 | opened | 82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 0 | 3.35 | 0.63 | 60 | 2.72 | 0 | 5.25 | 2.53 | 2.53 | opened
83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 5.07 |  |  | 5.07 | 0 | 6.615 | 1.545 | 1.545 | opened | 83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 0 | 5.07 |  |  | 5.07 | 0 | 6.615 | 1.545 | 1.545 | opened
84 | SS 35/10 Bokinskaya | 2*6,3 | 2.19 | 0.92 | 30 | 1.27 | 0 | 6.615 | 5.345 | 5.345 | opened | 84 | SS 35/10 Bokinskaya | 2*6,3 | 0.47 | 2.66 | 0.92 | 30 | 1.74 | 0 | 6.615 | 4.875 | 4.875 | opened
85 | SS 35/10 Stolovskaya | 4 | 0.64 | 0.52 | 24 hours | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened | 85 | SS 35/10 Stolovskaya | 4 | 0 | 0.64 | 0.52 | 24 hours | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
86 | SS 35/10 Tulinovskaya | 2*2,5 | 1.41 |  |  | 1.41 | 0 | 2.625 | 1.215 | 1.215 | opened | 86 | SS 35/10 Tulinovskaya | 2*2,5 | 0 | 1.41 |  |  | 1.41 | 0 | 2.625 | 1.215 | 1.215 | opened
87 | SS 35/6 Macaroni factory | 1.6 | 0.16 |  |  | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 87 | SS 35/6 Macaroni factory | 1.6 | 0 | 0.16 |  |  | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
88 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.27 |  |  | 1.27 | 0 | 1.68 | 0.41 | 0.41 | opened | 88 | SS 35/10 Serebryakovskaya | 2*1,6 | 0 | 1.27 |  |  | 1.27 | 0 | 1.68 | 0.41 | 0.41 | opened
89 | SS 35/10 B.Doroga | 2*1,6 | 0.39 | 0.34 | 60 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened | 89 | SS 35/10 B.Doroga | 2*1,6 | 0.11 | 0.5 | 0.34 | 60 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.64 |  |  | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened | 90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0 | 0.64 |  |  | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
91 | SS 35/10 Vishnevskaya | 2*2,5 | 0.51 | 0.26 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened | 91 | SS 35/10 Vishnevskaya | 2*2,5 | 0 | 0.51 | 0.26 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened
92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.4 | 0.32 | 50 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0 | 0.4 | 0.32 | 50 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
93 | SS 35/10 Glazkovskaya | 2*4 | 0.97 | 0.71 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened | 93 | SS 35/10 Glazkovskaya | 2*4 | 0 | 0.97 | 0.71 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened
94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.08 |  |  | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0 | 0.08 |  |  | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
95 | SS 35/6 Donskaya | 6,3+10 | 4.59 | 3.65 | 24 hours | 0.94 | 0 | 6.615 | 5.675 | 5.675 | opened | 95 | SS 35/6 Donskaya | 6,3+10 | 0 | 4.59 | 3.65 | 24 hours | 0.94 | 0 | 6.615 | 5.675 | 5.675 | opened
96 | SS 35/10 Druzhba | 2.5 | 0.16 | 0.16 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 96 | SS 35/10 Druzhba | 2.5 | 0 | 0.16 | 0.16 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.2 | 0.23 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened | 97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0 | 0.2 | 0.23 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.66 | 0.25 | 120 | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened | 98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0 | 0.66 | 0.25 | 120 | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened
99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.58 | 1.08 | 80 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 0 | 1.58 | 1.08 | 80 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
100 | SS 35/10 KIM | 2,5+4 | 0.6 | 0.74 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened | 100 | SS 35/10 KIM | 2,5+4 | 0.06 | 0.66 | 0.74 | 120 | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened
101 | SS 35/10 Klenskaya | 2*2,5 | 0.24 | 0.22 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 101 | SS 35/10 Klenskaya | 2*2,5 | 0 | 0.24 | 0.22 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.57 | 0.6 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened | 102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0 | 0.57 | 0.6 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
103 | SS 35/10 Komintern | 2*2,5 | 0.42 | 0.22 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 103 | SS 35/10 Komintern | 2*2,5 | 0.71 | 1.13 | 0.22 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | opened
104 | SS 35/10 Kochetovskaya | 6.3 | 0.32 | 0.2 | 24 hours | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened | 104 | SS 35/10 Kochetovskaya | 6.3 | 0 | 0.32 | 0.2 | 24 hours | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened
105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.15 | 0.14 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0 | 0.15 | 0.14 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 1.06 | 0.66 | 24 hours | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 0 | 1.06 | 0.66 | 24 hours | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.39 | 0.28 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened | 107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0 | 0.39 | 0.28 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
108 | SS 35/10 Petrovskaya | 2*4 | 2.9 | 1.2 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 108 | SS 35/10 Petrovskaya | 2*4 | 0 | 2.9 | 1.2 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened
109 | SS 35/10 Prigorodnaya | 2*5,6 | 0.9 | 0.62 | 120 | 0.28 | 0 | 5.88 | 5.6 | 5.6 | opened | 109 | SS 35/10 Prigorodnaya | 2*5,6 | 0 | 0.9 | 0.62 | 120 | 0.28 | 0 | 5.88 | 5.6 | 5.6 | opened
110 | SS 35/6 Progress | 2*10 | 11.35 |  |  | 11.35 | 0 | 10.5 | -0.85 | -0.85 | closed | 110 | SS 35/6 Progress | 2*10 | 0 | 11.35 |  |  | 11.35 | 0 | 10.5 | -0.85 | -0.85 | closed
111 | SS 35/10 Raninskaya | 1.6 | 0.27 | 0.32 | 24 hours | -0.05 | 0 | 1.68 | 1.73 | 1.73 | opened | 111 | SS 35/10 Raninskaya | 1.6 | 0.06 | 0.33 | 0.32 | 24 hours | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
113 | SS 35/10 Saburovskaya | 2*2,5 | 1.65 |  |  | 1.65 | 0 | 2.625 | 0.975 | 0.975 | opened | 113 | SS 35/10 Saburovskaya | 2*2,5 | 0 | 1.65 |  |  | 1.65 | 0 | 2.625 | 0.975 | 0.975 | opened
114 | SS 35/10 Sestryonskaya | 1.6 | 0.11 |  |  | 0.11 | 0 | 0 | -0.11 | -0.11 | closed | 114 | SS 35/10 Sestryonskaya | 1.6 | 0 | 0.11 |  |  | 0.11 | 0 | 0 | -0.11 | -0.11 | closed
115 | SS 35/10 Sitovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 115 | SS 35/10 Sitovskaya | 1.6 | 0 | 0.5 | 0.5 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
116 | SS 35/10 Skobelevskaya | 1.6 | 0.27 | 0.24 | 24 hours | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 116 | SS 35/10 Skobelevskaya | 1.6 | 0 | 0.27 | 0.24 | 24 hours | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
117 | SS 35/10 Ustyinskaya | 2.5 | 1.25 | 1.06 | 24 hours | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 117 | SS 35/10 Ustyinskaya | 2.5 | 0 | 1.25 | 1.06 | 24 hours | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
118 | SS 35/10 Yurlovskaya | 2*2,5 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened | 118 | SS 35/10 Yurlovskaya | 2*2,5 | 0 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened
119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0.63 |  |  | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened | 119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0 | 0.63 |  |  | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
120 | SS 35/10 Agroprom | 2*4 | 1.22 |  |  | 1.22 | 0 | 4.2 | 2.98 | 2.98 | opened | 120 | SS 35/10 Agroprom | 2*4 | 0 | 1.22 |  |  | 1.22 | 0 | 4.2 | 2.98 | 2.98 | opened
121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.28 |  |  | 0.28 | 0 | 1.68 | 1.4 | 1.4 | opened | 121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0 | 0.28 |  |  | 0.28 | 0 | 1.68 | 1.4 | 1.4 | opened
122 | SS 35/10 Vanovskaya | 2*2,5 | 0.1 | 0.07 | 80 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 122 | SS 35/10 Vanovskaya | 2*2,5 | 0 | 0.1 | 0.07 | 80 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
123 | SS 35/10 Vyazhlinskaya | 1.8 | 0.72 | 0.81 | 24 hours | -0.09 | 0 | 1.89 | 1.98 | 1.98 | opened | 123 | SS 35/10 Vyazhlinskaya | 1.8 | 0 | 0.72 | 0.81 | 24 hours | -0.09 | 0 | 1.89 | 1.98 | 1.98 | opened
124 | SS 35/10 Zarechnaya | 2*2,5 | 1.25 |  |  | 1.25 | 0 | 2.625 | 1.375 | 1.375 | opened | 124 | SS 35/10 Zarechnaya | 2*2,5 | 0 | 1.25 |  |  | 1.25 | 0 | 2.625 | 1.375 | 1.375
125 | SS 35/10 Kryukovskaya | 2*2,5 | 0.55 | 0.6593 | 120 | -0.1093 | 0 | 2.625 | 2.7343 | 2.7343 | opened | 125 | SS 35/10 Kryukovskaya | 2*2,5 | 0 | 0.55 | 0.6593 | 120 | -0.1093 | 0 | 2.625 | 2.7343 | 2.7343 | opened
126 | SS 35/6 Korshunovskaya | 2*2,5 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 126 | SS 35/6 Korshunovskaya | 2*2,5 | 0 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
127 | SS 35/6 Lugovaya | 4 | 0.43 | 0.94977 | 24 hours | -0.51977 | 0 | 4.2 | 4.7198 | 4.7198 | opened | 127 | SS 35/6 Lugovaya | 4 | 0 | 0.43 | 0.94977 | 24 hours | -0.51977 | 0 | 4.2 | 4.7198 | 4.7198 | opened
128 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.11 | 0.1467 | 120 | -0.036704 | 0 | 2.625 | 2.6617 | 2.6617 | opened | 128 | SS 35/10 Lyubvinskaya | 2*2,5 | 0 | 0.11 | 0.1467 | 120 | -0.036704 | 0 | 2.625 | 2.6617 | 2.6617 | opened
129 | SS 35/10 Morshanskaya | 2*4 | 2.66 |  |  | 2.66 | 0 | 4.2 | 1.54 | 1.54 | opened | 129 | SS 35/10 Morshanskaya | 2*4 | 0 | 2.66 |  |  | 2.66 | 0 | 4.2 | 1.54 | 1.54 | opened
130 | SS 35/10 Piterskaya | 2.5 | 1.05 | 0.93 | 24 hours | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 130 | SS 35/10 Piterskaya | 2.5 | 0 | 1.05 | 0.93 | 24 hours | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
131 | SS 35/10 Rakshinskaya | 2*4 | 1.95 | 1.6137 | 80 | 0.33626 | 0 | 4.2 | 3.8637 | 3.8637 | opened | 131 | SS 35/10 Rakshinskaya | 2*4 | 0 | 1.95 | 1.6137 | 80 | 0.33626 | 0 | 4.2 | 3.8637 | 3.8637 | opened
132 | SS 35/10 Rybinskaya | 2*2,5 | 0.92 | 1.0536 | 80 | -0.13357 | 0 | 2.625 | 2.7586 | 2.7586 | opened | 132 | SS 35/10 Rybinskaya | 2*2,5 | 0 | 0.92 | 1.0536 | 80 | -0.13357 | 0 | 2.625 | 2.7586 | 2.7586 | opened
133 | SS 35/10 Serpovskaya | 2*2,5 | 0.84 | 0.7 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 133 | SS 35/10 Serpovskaya | 2*2,5 | 0 | 0.84 | 0.7 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
134 | SS 35/10 St.Tomnikovskaya | 1 | 0.1 | 0.092555 | 24 hours | 0.007445 | 0 | 1.05 | 1.0426 | 1.0426 | opened | 134 | SS 35/10 St.Tomnikovskaya | 1 | 0 | 0.1 | 0.092555 | 24 hours | 0.007445 | 0 | 1.05 | 1.0426 | 1.0426 | opened
135 | SS 35/10 Chernitovskaya | 2.5 | 0.54 | 0.39963 | 24 hours | 0.14037 | 0 | 2.625 | 2.4846 | 2.4846 | opened | 135 | SS 35/10 Chernitovskaya | 2.5 | 0 | 0.54 | 0.39963 | 24 hours | 0.14037 | 0 | 2.625 | 2.4846 | 2.4846 | opened
136 | SS 35/10 Bondarskaya | 2*2,5 | 1.53 | 0.93 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 136 | SS 35/10 Bondarskaya | 2*2,5 | 0.65 | 2.18 | 0.93 | 80 | 1.25 | 0 | 2.625 | 1.375 | 1.375 | opened
137 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.5 | 0.53457 | 80 | -0.03457 | 0 | 1.68 | 1.7146 | 1.7146 | opened | 137 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0 | 0.5 | 0.53457 | 80 | -0.03457 | 0 | 1.68 | 1.7146 | 1.7146 | opened
138 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened | 138 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened
139 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.44 | 0.71276 | 120 | -0.27276 | 0 | 2.625 | 2.8978 | 2.8978 | opened | 139 | SS 35/10 Egorovskaya | 2,5+3,2 | 0 | 0.44 | 0.71276 | 120 | -0.27276 | 0 | 2.625 | 2.8978 | 2.8978 | opened
140 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.24 |  |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 140 | SS 35/10 Kershinskaya | 1,6+2,5 | 0 | 0.24 |  |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
141 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.39 | 0.054495 | 120 | 0.3355 | 0 | 1.68 | 1.3445 | 1.3445 | opened | 141 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0 | 0.39 | 0.054495 | 120 | 0.3355 | 0 | 1.68 | 1.3445 | 1.3445 | opened
142 | SS 35/10 Lipovskaya | 2.5 | 0.25 | 0.26988 | 24 hours | -0.01988 | 0 | 2.625 | 2.6449 | 2.6449 | opened | 142 | SS 35/10 Lipovskaya | 2.5 | 0 | 0.25 | 0.26988 | 24 hours | -0.01988 | 0 | 2.625 | 2.6449 | 2.6449 | opened
143 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.13 | 0.11 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 143 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0 | 0.13 | 0.11 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
144 | SS 35/10 Mitropolskaya | 2.5 | 0.2 | 0.28 | 24 hours | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened | 144 | SS 35/10 Mitropolskaya | 2.5 | 0.47 | 0.67 | 0.28 | 24 hours | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
145 | SS 35/10 P.Uglovskaya | 1.6 | 0.36 | 0.35292 | 24 hours | 0.00708 | 0 | 1.68 | 1.6729 | 1.6729 | opened | 145 | SS 35/10 P.Uglovskaya | 1.6 | 0 | 0.36 | 0.35292 | 24 hours | 0.00708 | 0 | 1.68 | 1.6729 | 1.6729 | opened
146 | SS 35/10 Rudovskaya | 2*2,5 | 0.29 |  |  | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened | 146 | SS 35/10 Rudovskaya | 2*2,5 | 0 | 0.29 |  |  | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
147 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.31 | 0.23 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 147 | SS 35/10 V.Yaroslavskaya | 2.5 | 0 | 0.31 | 0.23 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
148 | SS 35/10 Degtyanskaya | 2.5 | 1.16 | 0.9 | 24 hours | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened | 148 | SS 35/10 Degtyanskaya | 2.5 | 0 | 1.16 | 0.9 | 24 hours | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened
149 | SS 35/10 Zelenaya-2 | 1.6 | 0.27 | 0.17992 | 24 hours | 0.09008 | 0 | 1.68 | 1.5899 | 1.5899 | opened | 149 | SS 35/10 Zelenaya-2 | 1.6 | 0 | 0.27 | 0.17992 | 24 hours | 0.09008 | 0 | 1.68 | 1.5899 | 1.5899 | opened
150 | SS 35/10 Kulevatovskaya | 2*4 | 1.99 | 1.81 | 80 | 0.18 | 0 | 4.2 | 4.02 | 4.02 | opened | 150 | SS 35/10 Kulevatovskaya | 2*4 | 0 | 1.99 | 1.81 | 80 | 0.18 | 0 | 4.2 | 4.02 | 4.02 | opened
151 | SS 35/10 Lamskaya | 4+2,5 | 0.46 | 0.20362 | 120 | 0.25638 | 0 | 2.625 | 2.3686 | 2.3686 | opened | 151 | SS 35/10 Lamskaya | 4+2,5 | 0 | 0.46 | 0.20362 | 120 | 0.25638 | 0 | 2.625 | 2.3686 | 2.3686 | opened
152 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.07 |  |  | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 152 | SS 35/10 Gryaznovskaya | 2*2,5 | 0 | 0.07 |  |  | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
153 | SS 35/10 Otyasskaya | 2*2,5 | 0.51 | 0.39963 | 120 | 0.11037 | 0 | 2.625 | 2.5146 | 2.5146 | opened | 153 | SS 35/10 Otyasskaya | 2*2,5 | 0 | 0.51 | 0.39963 | 120 | 0.11037 | 0 | 2.625 | 2.5146 | 2.5146 | opened
154 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.09 | 0.1903 | 24 hours | -0.1003 | 0 | 1.68 | 1.7803 | 1.7803 | opened | 154 | SS 35/10 P.Vasilyevskaya | 1.6 | 0 | 0.09 | 0.1903 | 24 hours | -0.1003 | 0 | 1.68 | 1.7803 | 1.7803 | opened
155 | SS 35/10 Podlesnaya | 2*2,5 | 0.45 | 0.41935 | 120 | 0.030648 | 0 | 2.625 | 2.5944 | 2.5944 | opened | 155 | SS 35/10 Podlesnaya | 2*2,5 | 0 | 0.45 | 0.41935 | 120 | 0.030648 | 0 | 2.625 | 2.5944 | 2.5944 | opened
156 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0.33 | 0.38146 | 120 | -0.051465 | 0 | 2.625 | 2.6765 | 2.6765 | opened | 156 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0 | 0.33 | 0.38146 | 120 | -0.051465 | 0 | 2.625 | 2.6765 | 2.6765 | opened
157 | SS 35/10 Zherdevskaya | 10 | 2.75 | 2.25 | 24 hours | 0.5 | 0 | 10.5 | 10 | 10 | opened | 157 | SS 35/10 Zherdevskaya | 10 | 0 | 2.75 | 2.25 | 24 hours | 0.5 | 0 | 10.5 | 10 | 10 | opened
158 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 158 | SS 35/10 Sukmanovskaya | 2*2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
159 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.49 | 0.29 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 159 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.07 | 0.56 | 0.29 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened
160 | SS 35/10 Artemovskaya | 2*2,5 | 0.54 | 0.35 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 160 | SS 35/10 Artemovskaya | 2*2,5 | 0 | 0.54 | 0.35 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
161 | SS 35/10 RSKhO | 2,5+4 | 1.24 | 1.16 | 80 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 161 | SS 35/10 RSKhO | 2,5+4 | 0 | 1.24 | 1.16 | 80 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
162 | SS 35/10 Maksimovskaya | 2*1,6 | 0.16 | 0.18 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened | 162 | SS 35/10 Maksimovskaya | 2*1,6 | 0 | 0.16 | 0.18 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
163 | SS 35/10 Burnakskaya | 5,6+6,3 | 3.44 |  |  | 3.44 | 0 | 5.88 | 2.44 | 2.44 | opened | 163 | SS 35/10 Burnakskaya | 5,6+6,3 | 0 | 3.44 |  |  | 3.44 | 0 | 5.88 | 2.44 | 2.44 | opened
164 | SS 35/10 Poletaevskaya | 2*4 | 0.29 | 0.19 | 120 | 0.1 | 2.18 | 4.2 | 1.92 | 1.92 | opened | 164 | SS 35/10 Poletaevskaya | 2*4 | 0 | 0.29 | 0.19 | 120 | 0.1 | 2.18 | 4.2 | 1.92 | 1.92 | opened
165 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.71 |  |  | 0.71 | 0 | 4.2 | 3.49 | 3.49 | opened | 165 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.29 | 1 |  |  | 1 | 0 | 4.2 | 3.2 | 3.2 | opened
166 | SS 35/10 Pioner | 1,6+2,5 | 1.16 | 0.72 | 60 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened | 166 | SS 35/10 Pioner | 1,6+2,5 | 0 | 1.16 | 0.72 | 60 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened
167 | SS 35/10 Lvovskaya | 2*2,5 | 0.6 | 0.47 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 167 | SS 35/10 Lvovskaya | 2*2,5 | 0 | 0.6 | 0.47 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
168 | SS 35/10 Nadezhdinskaya | 1.6 | 0.39 | 0.28 | 24 hours | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened | 168 | SS 35/10 Nadezhdinskaya | 1.6 | 0 | 0.39 | 0.28 | 24 hours | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
169 | SS 35/10 Kuleshovskaya | 2.5 | 0.42 | 0.26 | 24 hours | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 169 | SS 35/10 Kuleshovskaya | 2.5 | 0 | 0.42 | 0.26 | 24 hours | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
170 | SS 35/10 Chernyaevskaya | 4+2,5 | 1.51 |  |  | 1.51 | 0 | 2.625 | 1.115 | 1.115 | opened | 170 | SS 35/10 Chernyaevskaya | 4+2,5 | 0 | 1.51 |  |  | 1.51 | 0 | 2.625 | 1.115 | 1.115 | opened
171 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 171 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
172 | SS 35/10 Shulginskaya | 2*4 | 0.77 | 0.02 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened | 172 | SS 35/10 Shulginskaya | 2*4 | 0 | 0.77 | 0.02 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened
173 | SS 35/10 Lavrovskaya | 2*2,5 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 173 | SS 35/10 Lavrovskaya | 2*2,5 | 0 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
174 | SS 35/10 N.Sergievskaya | 3.2 | 0.58 | 0.49 | 24 hours | 0.09 | 0 | 3.36 | 3.27 | 3.27 | opened | 174 | SS 35/10 N.Sergievskaya | 3.2 | 0 | 0.58 | 0.49 | 24 hours | 0.09 | 0 | 3.36 | 3.27 | 3.27 | opened
175 | SS 35/10 Kamenskaya | 2*2,5 | 0.44 |  |  | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened | 175 | SS 35/10 Kamenskaya | 2*2,5 | 0 | 0.44 |  |  | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened
176 | SS 35/10 Protasovskaya | 4+2,5 | 0.38 |  |  | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened | 176 | SS 35/10 Protasovskaya | 4+2,5 | 0 | 0.38 |  |  | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
177 | SS 35/10 Chakinskaya | 4 | 0.72 |  |  | 0.72 | 0 | 0 | -0.72 | -0.72 | closed | 177 | SS 35/10 Chakinskaya | 4 | 0 | 0.72 |  |  | 0.72 | 0 | 0 | -0.72 | -0.72 | closed
178 | SS 35/10 Lukinskaya | 2.5 | 0.26 | 0.22 | 24 hours | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 178 | SS 35/10 Lukinskaya | 2.5 | 0 | 0.26 | 0.22 | 24 hours | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
179 | SS 35/10 Zolotovskaya | 2.5 | 0.38 | 0.37 | 24 hours | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 179 | SS 35/10 Zolotovskaya | 2.5 | 0 | 0.38 | 0.37 | 24 hours | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
180 | SS 35/10 Mozdokskaya | 2.5 | 0.2 |  |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed | 180 | SS 35/10 Mozdokskaya | 2.5 | 0 | 0.2 |  |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed
181 | SS 35/10 Oblovskaya | 2*2,5 | 0.37 | 0.65 | 120 | -0.28 | 0 | 2.625 | 2.905 | 2.905 | opened | 181 | SS 35/10 Oblovskaya | 2*2,5 | 0 | 0.37 | 0.65 | 120 | -0.28 | 0 | 2.625 | 2.905 | 2.905 | opened
182 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 182 | SS 35/10 V.Vershinskaya | 2,5+4 | 0 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
183 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.13 |  |  | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 183 | SS 35/10 Luchevskaya | 2,5+1,6 | 0 | 0.13 |  |  | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
184 | SS 35/10 Olshanskaya | 4+2,5 | 1.28 | 0.32 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened | 184 | SS 35/10 Olshanskaya | 4+2,5 | 0 | 1.28 | 0.32 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
185 | SS 35/10 Pavlodarskaya | 2.5 | 0.41 | 0.1 | 24 hours | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 185 | SS 35/10 Pavlodarskaya | 2.5 | 0 | 0.41 | 0.1 | 24 hours | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
186 | SS 35/10 Berezovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 186 | SS 35/10 Berezovskaya | 2*2,5 | 0 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
187 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 187 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
188 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.3 |  |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 188 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0 | 0.3 |  |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
189 | SS 35/10 Shapkinskaya | 2*4 | 0.51 |  |  | 0.51 | 0 | 4.2 | 3.69 | 3.69 | opened | 189 | SS 35/10 Shapkinskaya | 2*4 | 0 | 0.51 |  |  | 0.51 | 0 | 4.2 | 3.69 | 3.69 | opened
190 | SS 35/10 Maryinskaya | 2*1,6 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened | 190 | SS 35/10 Maryinskaya | 2*1,6 | 0 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
191 | SS 35/10 Irskaya | 1,6+2,5 | 0.34 | 0.345 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | opened | 191 | SS 35/10 Irskaya | 1,6+2,5 | 0 | 0.34 | 0.345 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | opened
192 | SS 35/10 Zavodskaya | 2*4 | 0.73 | 1.25 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | opened | 192 | SS 35/10 Zavodskaya | 2*4 | 0 | 0.73 | 1.25 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | opened
193 | SS 35/10 Kalaisskaya | 2.5 | 0.5 | 0.58 | 24 hours | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened | 193 | SS 35/10 Kalaisskaya | 2.5 | 0 | 0.5 | 0.58 | 24 hours | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened
194 | SS 35/10 Sokolovskaya | 2*2,5 | 1.71 | 1.02 | 80 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened | 194 | SS 35/10 Sokolovskaya | 2*2,5 | 0 | 1.71 | 1.02 | 80 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened
195 | SS 35/10 Veterinarnaya | 2.5 | 0.13 | 0.13 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 195 | SS 35/10 Veterinarnaya | 2.5 | 0 | 0.13 | 0.13 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
196 | SS 35/10 Glukhovskaya | 2.5 | 0.08 | 0.09 | 24 hours | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened | 196 | SS 35/10 Glukhovskaya | 2.5 | 0 | 0.08 | 0.09 | 24 hours | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened
197 | SS 35/10 Orzhevskaya | 2.5 | 0.55 | 0.47 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 197 | SS 35/10 Orzhevskaya | 2.5 | 0 | 0.55 | 0.47 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
198 | SS 35/10 Umyotskaya | 2*4 | 1.64 | 1.54 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened | 198 | SS 35/10 Umyotskaya | 2*4 | 0 | 1.64 | 1.54 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
199 | SS 35/10 Gavrilovskaya | 2*4 | 1.37 | 0.996 | 120 | 0.374 | 0 | 4.2 | 3.826 | 3.826 | opened | 199 | SS 35/10 Gavrilovskaya | 2*4 | 0.29 | 1.66 | 0.996 | 120 | 0.664 | 0 | 4.2 | 3.536 | 3.536 | opened
200 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.73 | 0.76 | 80 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened | 200 | SS 35/10 Peresypkinskaya | 2*2,5 | 0 | 0.73 | 0.76 | 80 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
201 | SS 35/10 Annenskaya | 2*2,5 | 1.18 | 0.806 | 80 | 0.374 | 0 | 2.625 | 2.251 | 2.251 | opened | 201 | SS 35/10 Annenskaya | 2*2,5 | 0 | 1.18 | 0.806 | 80 | 0.374 | 0 | 2.625 | 2.251 | 2.251 | opened
202 | SS 35/10 Filatovskaya | 2*2,5 | 0.5 | 0.33 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 202 | SS 35/10 Filatovskaya | 2*2,5 | 0 | 0.5 | 0.33 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
203 | SS 35/10 Nikitinskaya | 2,5+1,6 | 0.21 | 0.135 | 120 | 0.075 | 0 | 1.68 | 1.605 | 1.605 | opened | 203 | SS 35/10 Nikitinskaya | 2,5+1,6 | 0 | 0.21 | 0.135 | 120 | 0.075 | 0 | 1.68 | 1.605 | 1.605 | opened
204 | SS 35/10 Balykleyskaya | 2*2,5 | 1.28 | 0.414 | 120 | 0.866 | 0 | 2.625 | 1.759 | 1.759 | opened | 204 | SS 35/10 Balykleyskaya | 2*2,5 | 0 | 1.28 | 0.414 | 120 | 0.866 | 0 | 2.625 | 1.759 | 1.759 | opened
205 | SS 35/10 Karavainskaya | 2*1,6 | 0.54 | 0.548 | 80 | -0.008 | 0 | 1.68 | 1.688 | 1.688 | opened | 205 | SS 35/10 Karavainskaya | 2*1,6 | 0 | 0.54 | 0.548 | 80 | -0.008 | 0 | 1.68 | 1.688 | 1.688 | opened
206 | SS 35/10 Poultry plant | 2*2,5 |  |  |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 206 | SS 35/10 Poultry plant | 2*2,5 | 0 | 0 |  |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
207 | SS 35/10 Pavlovskaya | 3.2 | 0.28 | 0.28 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 207 | SS 35/10 Pavlovskaya | 3.2 | 0 | 0.28 | 0.28 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
| Total: | 2441.2 | 544.36 | [8 empty] | 2: Total:; 3: 2445.2; 4: 0; 5: 558.92
| deficit | [8 empty] | -6.12 |  | 2: deficit; 4: 0; Min. 12: -2.8
| proficit | [8 empty] | 949.557 |  | 2: proficit; 4: 0; Min. 12: 945.107

## Тверьэнерго 3
Table 1 | [22 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | Примечание | Процент загрузки к номинальной мощности, % | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note | Примечание | Процент загрузки к номинальной мощности, % | ПО
|  | Installed power capacity of transformers Sуst. including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA | [6 empty] | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [13 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 13 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 14 | 15
1 | SS Alekseykovo 35/10 kv | 1.6 | 0.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.2 | 0.2 |  |  | 41.6667 | 1 | SS Alekseykovo 35/10 kv | 1.6 | 0 | 0.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.2 | 0.2 |  |  | 41.6667 | Бежецкие Электрические сети
2 | SS Belyznitsy 35/10 kv | 2.5 | 0.5 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.9 | 0.9 |  |  | 19.0476 | 2 | SS Belyznitsy 35/10 kv | 2.5 | 0 | 0.5 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.9 | 0.9 |  |  | 19.0476 | Бежецкие Электрические сети
3 | SS Borisovskoe 35/10 kv | 1 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 19.0476 | 3 | SS Borisovskoe 35/10 kv | 1 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 19.0476 | Бежецкие Электрические сети
4 | SS Vysokusha 35/10 kv | 2.5 | 0.2 | 0.89 | 24 hours | 0.89 | 0 | 0.89 | 0.69 | 0.69 |  |  | 7.619 | 4 | SS Vysokusha 35/10 kv | 2.5 | 0 | 0.2 | 0.89 | 24 hours | 0.89 | 0 | 0.89 | 0.69 | 0.69 |  |  | 7.619 | Бежецкие Электрические сети
5 | SS Hotel 35/10 kv | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | 5 | SS Hotel 35/10 kv | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | Бежецкие Электрические сети
6 | SS Grigorovo 35/10 kv | 2.5 | 0.2 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | 0.61 | 0.61 |  |  | 7.619 | 6 | SS Grigorovo 35/10 kv | 2.5 | 0 | 0.2 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | 0.61 | 0.61 |  |  | 7.619 | Бежецкие Электрические сети
7 | SS Deledino 35/10 kv | 4 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 4.7619 | 7 | SS Deledino 35/10 kv | 4 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 4.7619 | Бежецкие Электрические сети
8 | SS Zaramenye 35/10 kv | 1.6 | 0.45 | 1 | 24 hours | 1 | 0 | 1 | 0.55 | 0.55 |  |  | 26.7857 | 8 | SS Zaramenye 35/10 kv | 1.6 | 0 | 0.45 | 1 | 24 hours | 1 | 0 | 1 | 0.55 | 0.55 |  |  | 26.7857 | Бежецкие Электрические сети
9 | SS Zoby 35/10 kv | 4 | 0.2 | 2.9 | 24 hours | 2.9 | 0 | 2.9 | 2.7 | 2.7 |  |  | 4.7619 | 9 | SS Zoby 35/10 kv | 4 | 0 | 0.2 | 2.9 | 24 hours | 2.9 | 0 | 2.9 | 2.7 | 2.7 |  |  | 4.7619 | Бежецкие Электрические сети
10 | SS Koy 35/10 kv | 1.6 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 11.9048 | 10 | SS Koy 35/10 kv | 1.6 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 11.9048 | Бежецкие Электрические сети
11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.16 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1.04 | 1.04 |  |  | 9.5238 | 11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.125 | 0.285 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.915 | 0.915 |  |  | 16.9643 | Бежецкие Электрические сети
12 | SS Litvinovo 35/10 kv | 4 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  |  | 4.7619 | 12 | SS Litvinovo 35/10 kv | 4 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  |  | 4.7619 | Бежецкие Электрические сети
13 | SS Loshchemlya 35/10 kv | 2.5 | 0.4 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.4 | 0.4 |  |  | 15.2381 | 13 | SS Loshchemlya 35/10 kv | 2.5 | 0 | 0.4 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.4 | 0.4 |  |  | 15.2381 | Бежецкие Электрические сети
14 | SS Lyubegoshchi 35/10 kv | 1.8 | 0.4 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.9 | 0.9 |  |  | 21.164 | 14 | SS Lyubegoshchi 35/10 kv | 1.8 | 0 | 0.4 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.9 | 0.9 |  |  | 21.164 | Бежецкие Электрические сети
15 | SS Martynovo 35/10 kv | 1.6 | 0.2 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.53 | 0.53 |  |  | 11.9048 | 15 | SS Martynovo 35/10 kv | 1.6 | 0 | 0.2 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.53 | 0.53 |  |  | 11.9048 | Бежецкие Электрические сети
16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0.36 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.94 | 0.94 |  |  | 13.7143 | 16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0 | 0.36 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.94 | 0.94 |  |  | 13.7143 | Бежецкие Электрические сети
17 | SS Morozovo 35/10 kv | 2.5 | 0.3 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.6 | 0.6 |  |  | 11.4286 | 17 | SS Morozovo 35/10 kv | 2.5 | 0 | 0.3 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.6 | 0.6 |  |  | 11.4286 | Бежецкие Электрические сети
18 | SS Popovka 35/10 kv | 1 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 |  |  | 9.5238 | 18 | SS Popovka 35/10 kv | 1 | 0 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 |  |  | 9.5238 | Бежецкие Электрические сети
19 | SS Romantsevo 35/10 kv | 4 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 4.7619 | 19 | SS Romantsevo 35/10 kv | 4 | 0.026875 | 0.22687 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.47313 | 0.47313 |  |  | 5.4018 | Бежецкие Электрические сети
20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 |  |  | 7.619 | 20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 |  |  | 7.619 | Бежецкие Электрические сети
21 | SS Sukromny 35/10 kv | 1.6 | 0.8 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | -0.1 | -0.1 | MS is closed | MS is closed | 47.619 | 21 | SS Sukromny 35/10 kv | 1.6 | 0 | 0.8 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | -0.1 | -0.1 | MS is closed | MS is closed | 47.619 | Бежецкие Электрические сети
22 | SS Tebleshi 35/10 kv | 2.5 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  |  | 7.619 | 22 | SS Tebleshi 35/10 kv | 2.5 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  |  | 7.619 | Бежецкие Электрические сети
23 | SS Trestna 35/10 kv | 2.5 | 0.2 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.3 | 1.3 |  |  | 7.619 | 23 | SS Trestna 35/10 kv | 2.5 | 0 | 0.2 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.3 | 1.3 |  |  | 7.619 | Бежецкие Электрические сети
24 | SS Fralyovo 35/10 kv | 4 | 1.3 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.3 | 0.3 |  |  | 30.9524 | 24 | SS Fralyovo 35/10 kv | 4 | 0 | 1.3 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.3 | 0.3 |  |  | 30.9524 | Бежецкие Электрические сети
25 | SS Chamerovo 35/10 kv | 1.8 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 |  |  | 37.037 | 25 | SS Chamerovo 35/10 kv | 1.8 | 0.25 | 0.95 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | -0.25 | -0.25 | MS is closed | MS is closed | 50.2646 | Бежецкие Электрические сети
26 | SS Akhmatovo 110/10 kv | 2.5 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 7.619 | 26 | SS Akhmatovo 110/10 kv | 2.5 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 7.619 | Бежецкие Электрические сети
27 | SS Kladovo 110/10 kv | 6.3 | 1 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.6 | 0.6 |  |  | 15.1172 | 27 | SS Kladovo 110/10 kv | 6.3 | 0 | 1 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.6 | 0.6 |  |  | 15.1172 | Бежецкие Электрические сети
28 | SS Laptikha 110/10 kv | 2.5 | 0.5 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.4 | 0.4 |  |  | 19.0476 | 28 | SS Laptikha 110/10 kv | 2.5 | 0 | 0.5 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.4 | 0.4 |  |  | 19.0476 | Бежецкие Электрические сети
29 | SS Malyshevo 110/10 kv | 2.5 | 0.8 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.1 | 0.1 |  |  | 30.4762 | 29 | SS Malyshevo 110/10 kv | 2.5 | 0.03125 | 0.83125 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.06875 | 0.06875 |  |  | 31.6667 | Бежецкие Электрические сети
30 | SS Start 10/10 kv | 16 | 1.8 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 0.9 | 0.9 |  |  | 10.7143 | 30 | SS Start 10/10 kv | 16 | 0.0375 | 1.8375 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 0.8625 | 0.8625 |  |  | 10.9375 | Бежецкие Электрические сети
31 | SS Rassvet 110/35 kv | 10 | 4.7 | 5 | 24 hours | 5 | 0 | 5 | 0.3 | 0.3 |  |  | 44.7619 | 31 | SS Rassvet 110/35 kv | 10 | 0.475 | 5.175 | 5 | 24 hours | 5 | 0 | 5 | -0.175 | -0.175 | MS is closed | MS is closed | 49.2857 | Бежецкие Электрические сети
32 | SS Ivanovo 110/35/10 kv | 6.3 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6 | -0.7 | MS is closed | MS is closed | 12.0937 | 32 | SS Ivanovo 110/35/10 kv | 6.3 | 0.25 | 1.05 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.35 | -0.95 | MS is closed | MS is closed | 15.873 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 6.3 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 6.3 | 0.25 | 0.95 | 0 |  | 0 | 0 | 0 | -0.95 |  |  | MS is closed
| Nom. capacity LV, MVA | 6.3 | 0.1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.3 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.3 |  |  | MS is closed
33 | SS Kesma 110/35/10 kv | 6.3 | 0.9 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.5 | -0.3 | MS is closed | MS is closed | 13.6054 | 33 | SS Kesma 110/35/10 kv | 6.3 | 0 | 0.9 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.5 | -0.3 | MS is closed | MS is closed | 13.6054 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 6.3 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 |  |  | MS is closed
| Nom. capacity LV, MVA | 6.3 | 0.6 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.8 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.6 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.8 |  |  | MS is closed
34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | -0.2 | MS is closed | MS is closed | 8.5034 | 34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | -0.2 | MS is closed | MS is closed | 8.5034 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 5.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 5.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 |  |  | MS is closed
| Nom. capacity LV, MVA | 5.6 | 0.3 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.9 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 5.6 | 0 | 0.3 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.9 |  |  | MS is closed
35 | SS Topalki 110/35/10 kv | 6.3 | 2.4 | 3.9 | 24 hours | 3.9 | 0 | 3.9 | 1.5 | 0.6 |  |  | 36.2812 | 35 | SS Topalki 110/35/10 kv | 6.3 | 0.075 | 2.475 | 3.9 | 24 hours | 3.9 | 0 | 3.9 | 1.425 | 0.6 |  |  | 37.415 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 6.3 | 2.1 | 3 | 24 hours | 3 | 0 | 3 | 0.9 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.075 | 2.175 | 3 | 24 hours | 3 | 0 | 3 | 0.825 |  | 0
| Nom. capacity LV, MVA | 6.3 | 0.3 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.6 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.3 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.6 |  | 0
36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0.1 | 0.7 | 24 hours | -0.6 | 0 | 1.05 | 1.65 | 1.65 |  |  | 9.5238 | 36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0 | 0.1 | 0.7 | 24 hours | -0.6 | 0 | 1.05 | 1.65 | 1.65 |  |  | 9.5238 | Бежецкие Электрические сети
37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 1.8 | 1.4 | 24 hours | 0.4 | 0 | 1.68 | 1.28 | 1.28 |  |  | 107.1429 | 37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 0.075 | 1.875 | 1.4 | 24 hours | 0.475 | 0 | 1.68 | 1.205 | 1.205 |  |  | 111.6071 | Бежецкие Электрические сети
38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 4.7 | 1.6 | 24 hours | 3.1 | 0 | 4.2 | 1.1 | 1.1 |  |  | 111.9048 | 38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 0.0625 | 4.7625 | 1.6 | 24 hours | 3.1625 | 0 | 4.2 | 1.0375 | 1.0375 |  |  | 113.3929 | Бежецкие Электрические сети
39 | SS Molokovo 35/10 kv | 2,5+4,0 | 1.7 | 1.8 | 24 hours | -0.1 | 0 | 2.63 | 2.73 | 2.73 |  |  | 64.6388 | 39 | SS Molokovo 35/10 kv | 2,5+4,0 | 0 | 1.7 | 1.8 | 24 hours | -0.1 | 0 | 2.63 | 2.73 | 2.73 |  |  | 64.6388 | Бежецкие Электрические сети
40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 |  |  | 11.4068 | 40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 |  |  | 11.4068 | Бежецкие Электрические сети
41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 1.2 | 1.4 | 24 hours | -0.2 | 0 | 1.68 | 1.88 | 1.88 |  |  | 71.4286 | 41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 0 | 1.2 | 1.4 | 24 hours | -0.2 | 0 | 1.68 | 1.88 | 1.88 |  |  | 71.4286 | Бежецкие Электрические сети
42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 4.1 | 1.8 | 24 hours | 2.3 | 0 | 3.4 | 1.1 | 1.1 |  |  | 120.5882 | 42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 0.475 | 4.575 | 1.8 | 24 hours | 2.775 | 0 | 3.4 | 0.625 | 0.625 |  |  | 134.5588 | Бежецкие Электрические сети
43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0.7 | 0.7 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 41.6667 | 43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0 | 0.7 | 0.7 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 41.6667 | Бежецкие Электрические сети
44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0.7 | 1 | 24 hours | -0.3 | 0 | 6.62 | 6.92 | 6.92 |  |  | 10.574 | 44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0 | 0.7 | 1 | 24 hours | -0.3 | 0 | 6.62 | 6.92 | 6.92 |  |  | 10.574 | Бежецкие Электрические сети
45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 4.9 | 0.2 | 24 hours | 4.7 | 0 | 6.62 | 1.92 | 1.72 |  |  | 74.0181 | 45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 0 | 4.9 | 0.2 | 24 hours | 4.7 | 0 | 6.62 | 1.92 | 1.72 |  |  | 74.0181 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0.2 | 24 hours | -0.2 | 0 | 6.62 | 6.82 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0.2 | 24 hours | -0.2 | 0 | 6.62 | 6.82 |  | 0
| Nom. capacity LV, MVA | 6,3+6,3 | 4.9 | 0 |  | 4.9 | 0 | 6.62 | 1.72 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 4.9 | 0 |  | 4.9 | 0 | 6.62 | 1.72 |  | 0
46 | SS DVP 110/35/10 kv | 25,0+25,0 | 9.5 | 2.5 | 24 hours | 7 | 0 | 26.3 | 19.3 | 19.3 |  |  | 36.1217 | 46 | SS DVP 110/35/10 kv | 25,0+25,0 | 0 | 9.5 | 2.5 | 24 hours | 7 | 0 | 26.3 | 19.3 | 19.3 |  |  | 36.1217 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 25,0+25,0 | 5.3 | 2.5 | 24 hours | 2.8 | 0 | 26.3 | 23.5 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0 | 5.3 | 2.5 | 24 hours | 2.8 | 0 | 26.3 | 23.5 |  | 0
| Nom. capacity LV, MVA | 25,0+25,0 | 4.2 | 0 |  | 4.2 | 0 | 26.3 | 22.1 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0 | 4.2 | 0 |  | 4.2 | 0 | 26.3 | 22.1 |  | 0
47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 6 | 5.6 | 24 hours | 0.4 | 0 | 10.5 | 10.1 | 4.7 |  |  | 57.1429 | 47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 0 | 6 | 5.6 | 24 hours | 0.4 | 0 | 10.5 | 10.1 | 4.7 |  |  | 57.1429 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 10,0+10,0 | 0.2 | 5.6 | 24 hours | -5.4 | 0 | 10.5 | 15.9 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.2 | 5.6 | 24 hours | -5.4 | 0 | 10.5 | 15.9 |  | 0
| Nom. capacity LV, MVA | 10,0+10,0 | 5.8 | 0 |  | 5.8 | 0 | 10.5 | 4.7 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 5.8 | 0 |  | 5.8 | 0 | 10.5 | 4.7 |  | 0
48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 3.3 | 5.6 | 24 hours | -2.3 | 0 | 6.62 | 8.92 | 6.32 |  |  | 49.8489 | 48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 0 | 3.3 | 5.6 | 24 hours | -2.3 | 0 | 6.62 | 8.92 | 6.32 |  |  | 49.8489 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 6,3+6,3 | 3 | 5.6 | 24 hours | -2.6 | 0 | 6.62 | 9.22 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 3 | 5.6 | 24 hours | -2.6 | 0 | 6.62 | 9.22 |  | 0
| Nom. capacity LV, MVA | 6,3+6,3 | 0.3 | 0 |  | 0.3 | 0 | 6.62 | 6.32 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.3 | 0 |  | 0.3 | 0 | 6.62 | 6.32 |  | 0
49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 5.5 | 6 | 24 hours | -0.5 | 0 | 10.5 | 11 | 9.5 |  |  | 52.381 | 49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 0.125 | 5.625 | 6 | 24 hours | -0.375 | 0 | 10.5 | 10.875 | 9.5 |  |  | 53.5714 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 10,0+10,0 | 3.2 | 4.7 | 24 hours | -1.5 | 0 | 10.5 | 12 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0.125 | 3.325 | 4.7 | 24 hours | -1.375 | 0 | 10.5 | 11.875 |  | 0
| Nom. capacity LV, MVA | 10,0+10,0 | 2.3 | 1.3 | 24 hours | 1 | 0 | 10.5 | 9.5 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 2.3 | 1.3 | 24 hours | 1 | 0 | 10.5 | 9.5 |  | 0
50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 19.2 | 4.8 | 24 hours | 14.4 | 0 | 26.3 | 11.9 | 11.9 |  |  | 73.0038 | 50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 0.064375 | 19.2644 | 4.8 | 24 hours | 14.4644 | 0 | 26.3 | 11.8356 | 11.8356 |  |  | 73.2486 | Бежецкие Электрические сети
| Nom. capacity MV, MVA | 25,0+25,0 | 6.4 | 4.8 | 24 hours | 1.6 | 0 | 26.3 | 24.7 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0.026875 | 6.4269 | 4.8 | 24 hours | 1.6269 | 0 | 26.3 | 24.6731 |  | 0
| Nom. capacity LV, MVA | 25,0+25,0 | 12.8 | 0 |  | 12.8 | 0 | 26.3 | 13.5 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0.0375 | 12.8375 | 0 |  | 12.8375 | 0 | 26.3 | 13.4625 |  | 0
51 | SS Belsky Karyer 35/6 kv | 4 | 0.158 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.148 | -0.148 | MS is closed | MS is closed | 3.7619 | 51 | SS Belsky Karyer 35/6 kv | 4 | 0 | 0.158 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.148 | -0.148 | MS is closed | MS is closed | 3.7619 | Вышневолоцкие Электрические сети
52 | SS Dubrovka 35/10 kv | 1.6 | 0.183 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.067 | 0.067 |  |  | 10.8929 | 52 | SS Dubrovka 35/10 kv | 1.6 | 0 | 0.183 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.067 | 0.067 |  |  | 10.8929 | Вышневолоцкие Электрические сети
53 | SS Zhilotkovo 35/10 kv | 1.8 | 0.088 | 0 |  | 0 | 0 | 0 | -0.088 | -0.088 | MS is closed | MS is closed | 4.6561 | 53 | SS Zhilotkovo 35/10 kv | 1.8 | 0 | 0.088 | 0 |  | 0 | 0 | 0 | -0.088 | -0.088 | MS is closed | MS is closed | 4.6561 | Вышневолоцкие Электрические сети
54 | SS Kopachevo 35/10 kv | 1.6 | 0.476 | 0.476 | 24 hours | 0.476 | 0 | 0.476 | 0 | 0 |  |  | 28.3333 | 54 | SS Kopachevo 35/10 kv | 1.6 | 0 | 0.476 | 0.476 | 24 hours | 0.476 | 0 | 0.476 | 0 | 0 |  |  | 28.3333 | Вышневолоцкие Электрические сети
55 | SS Kuznetsovo 35/10 kv | 1.6 | 0.641 | 0.641 | 24 hours | 0.641 | 0 | 0.641 | 0 | 0 |  |  | 38.1548 | 55 | SS Kuznetsovo 35/10 kv | 1.6 | 0 | 0.641 | 0.641 | 24 hours | 0.641 | 0 | 0.641 | 0 | 0 |  |  | 38.1548 | Вышневолоцкие Электрические сети
56 | SS Luzhnikovo 35/10 kv | 2.5 | 0.122 | 0.122 | 24 hours | 0.122 | 0 | 0.122 | 0 | 0 |  |  | 4.6476 | 56 | SS Luzhnikovo 35/10 kv | 2.5 | 0 | 0.122 | 0.122 | 24 hours | 0.122 | 0 | 0.122 | 0 | 0 |  |  | 4.6476 | Вышневолоцкие Электрические сети
57 | SS Nasakino 35/10 kv | 0.56 | 0.086 | 0 |  | 0 | 0 | 0 | -0.086 | -0.086 | MS is closed | MS is closed | 14.6259 | 57 | SS Nasakino 35/10 kv | 0.56 | 0 | 0.086 | 0 |  | 0 | 0 | 0 | -0.086 | -0.086 | MS is closed | MS is closed | 14.6259 | Вышневолоцкие Электрические сети
58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 0.908 | 0.908 | 24 hours | 0.908 | 0 | 0.908 | 0 | 0 |  |  | 3.459 | 58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 0 | 0.908 | 0.908 | 24 hours | 0.908 | 0 | 0.908 | 0 | 0 |  |  | 3.459 | Вышневолоцкие Электрические сети
59 | SS Porozhki 35/10 kv | 1 | 0.381 | 0.381 | 24 hours | 0.381 | 0 | 0.381 | 0 | 0 |  |  | 36.2857 | 59 | SS Porozhki 35/10 kv | 1 | 0.03125 | 0.41225 | 0.381 | 24 hours | 0.381 | 0 | 0.381 | -0.03125 | -0.03125 | MS is closed | MS is closed | 39.2619 | Вышневолоцкие Электрические сети
60 | SS Kh.B.K. 35/6 kv | 4 | 3.651 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -2.751 | -2.751 | MS is closed | MS is closed | 86.9286 | 60 | SS Kh.B.K. 35/6 kv | 4 | 0 | 3.651 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -2.751 | -2.751 | MS is closed | MS is closed | 86.9286 | Вышневолоцкие Электрические сети
61 | SS no.5 35/6 kv | 1.0+1.6 | 0.804 | 0 |  | 0.804 | 0 | 1.05 | 0.246 | 0.246 |  |  | 76.5714 | 61 | SS no.5 35/6 kv | 1.0+1.6 | 0 | 0.804 | 0 |  | 0.804 | 0 | 1.05 | 0.246 | 0.246 |  |  | 76.5714 | Вышневолоцкие Электрические сети
62 | SS the 9th January 35/10 kv | 6,3+10 | 3.695 | 0 |  | 3.695 | 0 | 6.62 | 2.925 | 2.925 |  |  | 55.8157 | 62 | SS the 9th January 35/10 kv | 6,3+10 | 0 | 3.695 | 0 |  | 3.695 | 0 | 6.62 | 2.925 | 2.925 |  |  | 55.8157 | Вышневолоцкие Электрические сети
63 | SS AKU 35/6 kv | 3,2+4 | 1.264 | 0.2 | 120 | 1.064 | 0 | 3.36 | 2.296 | 2.296 |  |  | 37.619 | 63 | SS AKU 35/6 kv | 3,2+4 | 0 | 1.264 | 0.2 | 120 | 1.064 | 0 | 3.36 | 2.096 | 2.096 |  |  | 37.619 | Вышневолоцкие Электрические сети
64 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0.052 | 0 |  | 0.052 | 0 | 1.05 | 0.998 | 0.998 |  |  | 4.9524 | 64 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0 | 0.052 | 0 |  | 0.052 | 0 | 1.05 | 0.998 | 0.998 |  |  | 4.9524 | Вышневолоцкие Электрические сети
65 | SS B-4 110/6 kv | 10+10 | 5.363 | 0 |  | 5.363 | 0 | 10.5 | 5.137 | 5.137 |  |  | 51.0762 | 65 | SS B-4 110/6 kv | 10+10 | 0 | 5.363 | 0 |  | 5.363 | 0 | 10.5 | 5.137 | 5.137 |  |  | 51.0762 | Вышневолоцкие Электрические сети
66 | SS Borisovo 35/6 kv | 3.2+3.2 | 3.765 | 0 |  | 3.765 | 0 | 3.36 | -0.405 | -0.405 | MS is closed | MS is closed | 112.0536 | 66 | SS Borisovo 35/6 kv | 3.2+3.2 | 0 | 3.765 | 0 |  | 3.765 | 0 | 3.36 | -0.405 | -0.405 | MS is closed | MS is closed | 112.0536 | Вышневолоцкие Электрические сети
67 | SS Borovno 35/10 kv | 2.5+2.5 | 0.787 | 0.2 | 120 | 0.587 | 0 | 2.63 | 2.043 | 2.043 |  |  | 29.924 | 67 | SS Borovno 35/10 kv | 2.5+2.5 | 0 | 0.787 | 0.2 | 120 | 0.587 | 0 | 2.63 | 2.043 | 2.043 |  |  | 29.924 | Вышневолоцкие Электрические сети
68 | SS Bushevets 110/10 kv | 6.3+6.3 | 0.388 | 0 |  | 0.388 | 0 | 6.62 | 6.232 | 6.232 |  |  | 5.861 | 68 | SS Bushevets 110/10 kv | 6.3+6.3 | 0 | 0.388 | 0 |  | 0.388 | 0 | 6.62 | 6.232 | 6.232 |  |  | 5.861 | Вышневолоцкие Электрические сети
69 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 3.563 | 0 |  | 3.563 | 0 | 6.62 | 3.057 | 3.057 |  |  | 53.8218 | 69 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 0.25 | 3.813 | 0 |  | 3.813 | 0 | 6.62 | 2.807 | 2.807 |  |  | 57.5982 | Вышневолоцкие Электрические сети
70 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0.733 | 0 |  | 0.733 | 0 | 1.68 | 0.947 | 0.947 |  |  | 43.631 | 70 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0.1 | 0.833 | 0 |  | 0.833 | 0 | 1.68 | 0.847 | 0.847 |  |  | 49.5833 | Вышневолоцкие Электрические сети
71 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0.654 | 0.4 | 120 | 0.254 | 0 | 1.68 | 1.426 | 1.426 |  |  | 38.9286 | 71 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0.075 | 0.729 | 0.4 | 120 | 0.329 | 0 | 1.68 | 1.351 | 1.351 |  |  | 43.3929 | Вышневолоцкие Электрические сети
72 | SS Gorodok 35/10 kv | 1.6+1.6 | 0.904 | 0 |  | 0.904 | 0 | 1.68 | 0.776 | 0.776 |  |  | 53.8095 | 72 | SS Gorodok 35/10 kv | 1.6+1.6 | 0 | 0.904 | 0 |  | 0.904 | 0 | 1.68 | 0.776 | 0.776 |  |  | 53.8095 | Вышневолоцкие Электрические сети
73 | SS DOZ 35/10 kv | 4+4 | 3.459 | 0 |  | 3.459 | 0 | 4.2 | 0.741 | 0.741 |  |  | 82.3571 | 73 | SS DOZ 35/10 kv | 4+4 | 0 | 3.459 | 0 |  | 3.459 | 0 | 4.2 | 0.741 | 0.741 |  |  | 82.3571 | Вышневолоцкие Электрические сети
74 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.536 | 0 |  | 0.536 | 0 | 1.68 | 1.144 | 1.144 |  |  | 31.9048 | 74 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.125 | 0.661 | 0 |  | 0.661 | 0 | 1.68 | 1.019 | 1.019 |  |  | 39.3452 | Вышневолоцкие Электрические сети
75 | SS Esenovichi 35/10 kv | 1.8+2.5 | 1.144 | 0 |  | 1.144 | 0 | 1.89 | 0.746 | 0.746 |  |  | 60.5291 | 75 | SS Esenovichi 35/10 kv | 1.8+2.5 | 0 | 1.144 | 0 |  | 1.144 | 0 | 1.89 | 0.746 | 0.746 |  |  | 60.5291 | Вышневолоцкие Электрические сети
76 | SS Plant of reinforced concrete products 35/10 kv | 6.3+6.3 | 0.245 | 0 |  | 0.245 | 0 | 6.62 | 6.375 | 6.375 |  |  | 3.7009 | 76 | SS Plant of reinforced concrete products 35/10 kv | 6.3+6.3 | 0 | 0.245 | 0 |  | 0.245 | 0 | 6.62 | 6.375 | 6.375 |  |  | 3.7009 | Вышневолоцкие Электрические сети
77 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0.847 | 0.2 | 120 | 0.647 | 0 | 6.62 | 5.973 | 5.973 |  |  | 12.7946 | 77 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0 | 0.847 | 0.2 | 120 | 0.647 | 0 | 6.62 | 5.973 | 5.973 |  |  | 12.7946 | Вышневолоцкие Электрические сети
78 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0.471 | 0.471 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 17.9087 | 78 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0 | 0.471 | 0.471 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 17.9087 | Вышневолоцкие Электрические сети
79 | SS Kozlovo 35/10 kv | 1.8+4 | 0.76 | 0 |  | 0.76 | 0 | 1.89 | 1.13 | 1.13 |  |  | 40.2116 | 79 | SS Kozlovo 35/10 kv | 1.8+4 | 0 | 0.76 | 0 |  | 0.76 | 0 | 1.89 | 1.13 | 1.13 |  |  | 40.2116 | Вышневолоцкие Электрические сети
80 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0.457 | 0 |  | 0.457 | 0 | 1.68 | 1.223 | 1.223 |  |  | 27.2024 | 80 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0 | 0.457 | 0 |  | 0.457 | 0 | 1.68 | 1.223 | 1.223 |  |  | 27.2024 | Вышневолоцкие Электрические сети
81 | SS Krasny May 35/6 kv | 10+10 | 2.357 | 0 |  | 2.357 | 0 | 10.5 | 8.143 | 8.143 |  |  | 22.4476 | 81 | SS Krasny May 35/6 kv | 10+10 | 0 | 2.357 | 0 |  | 2.357 | 0 | 10.5 | 8.143 | 8.143 |  |  | 22.4476 | Вышневолоцкие Электрические сети
82 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 1.113 | 0.2 | 120 | 0.913 | 0 | 3.36 | 2.447 | 2.447 |  |  | 33.125 | 82 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 0 | 1.113 | 0.2 | 120 | 0.913 | 0 | 3.36 | 2.447 | 2.447 |  |  | 33.125 | Вышневолоцкие Электрические сети
83 | SS Lukino 35/10 kv | 2.5+1.6 | 0.276 | 0 |  | 0.276 | 0 | 1.68 | 1.404 | 1.404 |  |  | 16.4286 | 83 | SS Lukino 35/10 kv | 2.5+1.6 | 0 | 0.276 | 0 |  | 0.276 | 0 | 1.68 | 1.404 | 1.404 |  |  | 16.4286 | Вышневолоцкие Электрические сети
84 | SS Makarovo 35/6 kv | 4+4 | 1.051 | 0.1 | 120 | 0.951 | 0 | 4.2 | 3.249 | 3.249 |  |  | 25.0238 | 84 | SS Makarovo 35/6 kv | 4+4 | 0 | 1.051 | 0.1 | 120 | 0.951 | 0 | 4.2 | 3.249 | 3.249 |  |  | 25.0238 | Вышневолоцкие Электрические сети
85 | SS Mankhino 110/10 kv | 2.5+2.5 | 0.159 | 0 |  | 0.159 | 0 | 2.63 | 2.471 | 2.471 |  |  | 6.0456 | 85 | SS Mankhino 110/10 kv | 2.5+2.5 | 0 | 0.159 | 0 |  | 0.159 | 0 | 2.63 | 2.471 | 2.471 |  |  | 6.0456 | Вышневолоцкие Электрические сети
86 | SS Moldino 35/10 kv | 1+1 | 0.459 | 0.459 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 |  |  | 43.7143 | 86 | SS Moldino 35/10 kv | 1+1 | 0 | 0.459 | 0.459 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 |  |  | 43.7143 | Вышневолоцкие Электрические сети
87 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0.764 | 0.764 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 |  |  | 72.7619 | 87 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0 | 0.764 | 0.764 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 |  |  | 72.7619 | Вышневолоцкие Электрические сети
88 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0.336 | 0 |  | 0.336 | 0 | 1.68 | 1.344 | 1.344 |  |  | 20 | 88 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0 | 0.336 | 0 |  | 0.336 | 0 | 1.68 | 1.344 | 1.344 |  |  | 20 | Вышневолоцкие Электрические сети
89 | SS OEZ 35/6 kv | 2.5+5.6 | 2.237 | 2.237 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 85.057 | 89 | SS OEZ 35/6 kv | 2.5+5.6 | 0 | 2.237 | 2.237 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 85.057 | Вышневолоцкие Электрические сети
90 | SS Plotichno 35/10 kv | 1.8+1.6 | 0.319 | 0 |  | 0.319 | 0 | 1.68 | 1.361 | 1.361 |  |  | 18.9881 | 90 | SS Plotichno 35/10 kv | 1.8+1.6 | 0 | 0.319 | 0 |  | 0.319 | 0 | 1.68 | 1.361 | 1.361 |  |  | 18.9881 | Вышневолоцкие Электрические сети
91 | SS Popovo 35/10 kv | 1+1 | 0.547 | 0 |  | 0.547 | 0 | 1.05 | 0.503 | 0.503 |  |  | 52.0952 | 91 | SS Popovo 35/10 kv | 1+1 | 0 | 0.547 | 0 |  | 0.547 | 0 | 1.05 | 0.503 | 0.503 |  |  | 52.0952 | Вышневолоцкие Электрические сети
92 | SS Proletary 35/10 kv | 2.5+2.5 | 2.543 | 0.7 | 120 | 1.843 | 0 | 2.63 | 0.787 | 0.787 |  |  | 96.692 | 92 | SS Proletary 35/10 kv | 2.5+2.5 | 0.125 | 2.668 | 0.7 | 120 | 1.968 | 0 | 2.63 | 0.662 | 0.662 |  |  | 101.4449 | Вышневолоцкие Электрические сети
93 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0.292 | 0 |  | 0.292 | 0 | 2.63 | 2.338 | 2.338 |  |  | 11.1027 | 93 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0 | 0.292 | 0 |  | 0.292 | 0 | 2.63 | 2.338 | 2.338 |  |  | 11.1027 | Вышневолоцкие Электрические сети
94 | SS Ryad 35/10 kv | 2.5+2.5 | 0.56 | 0.3 | 120 | 0.26 | 0 | 2.63 | 2.37 | 2.37 |  |  | 21.2928 | 94 | SS Ryad 35/10 kv | 2.5+2.5 | 0 | 0.56 | 0.3 | 120 | 0.26 | 0 | 2.63 | 2.37 | 2.37 |  |  | 21.2928 | Вышневолоцкие Электрические сети
95 | Ss Seglino 35/10 kv | 1.6+1.6 | 0.381 | 0 |  | 0.381 | 0 | 1.68 | 1.299 | 1.299 |  |  | 22.6786 | 95 | Ss Seglino 35/10 kv | 1.6+1.6 | 0 | 0.381 | 0 |  | 0.381 | 0 | 1.68 | 1.299 | 1.299 |  |  | 22.6786 | Вышневолоцкие Электрические сети
96 | SS Soroki 35/10 kv | 2.5+2.5 | 0.482 | 0 |  | 0.482 | 0 | 2.63 | 2.148 | 2.148 |  |  | 18.327 | 96 | SS Soroki 35/10 kv | 2.5+2.5 | 0 | 0.482 | 0 |  | 0.482 | 0 | 2.63 | 2.148 | 2.148 |  |  | 18.327 | Вышневолоцкие Электрические сети
97 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0.701 | 0.701 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 41.7262 | 97 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0 | 0.701 | 0.701 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 41.7262 | Вышневолоцкие Электрические сети
98 | SS Timkovo 35/10 kv | 1.6+1.6 | 0.798 | 0 |  | 0.798 | 0 | 1.68 | 0.882 | 0.882 |  |  | 47.5 | 98 | SS Timkovo 35/10 kv | 1.6+1.6 | 0 | 0.798 | 0 |  | 0.798 | 0 | 1.68 | 0.882 | 0.882 |  |  | 47.5 | Вышневолоцкие Электрические сети
99 | SS Firovo 35/10 kv | 2.5+2.5 | 1.797 | 1.797 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 68.327 | 99 | SS Firovo 35/10 kv | 2.5+2.5 | 0 | 1.797 | 1.797 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 68.327 | Вышневолоцкие Электрические сети
100 | SS Yubileynaya 35/6 kv | 7.5+10 | 6.577 | 0.9 | 120 | 5.677 | 0 | 8.17 | 2.493 | 2.493 |  |  | 80.5018 | 100 | SS Yubileynaya 35/6 kv | 7.5+10 | 0.0975 | 6.6745 | 0.9 | 120 | 5.7745 | 0 | 8.17 | 2.3955 | 2.3955 |  |  | 81.6952 | Вышневолоцкие Электрические сети
101 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0.217 | 0.217 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 8.251 | 101 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0 | 0.217 | 0.217 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 |  |  | 8.251 | Вышневолоцкие Электрические сети
102 | SS Brusovo 110/35/10 kv | 10+10 | 2.523 | 3.677 | 120 | -1.154 | 0 | 10.5 | 11.654 | 10.5 |  |  | 24.0286 | 102 | SS Brusovo 110/35/10 kv | 10+10 | 0.3 | 2.823 | 3.677 | 120 | -0.854 | 0 | 10.5 | 11.354 | 10.5 |  |  | 26.8857 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 10+10 | 1.877 | 1.877 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.877 | 1.877 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0
| Nom. capacity LV, MVA | 10+10 | 0.646 | 1.8 | 120 | -1.154 | 0 | 10.5 | 11.654 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.3 | 0.946 | 1.8 | 120 | -0.854 | 0 | 10.5 | 11.354 |  | 0
103 | SS Vypozovo 110/35/6 kv | 10+10 | 2.857 | 5.042 | 120 | -2.185 | 0 | 10.5 | 12.685 | 10.5 |  |  | 27.2095 | 103 | SS Vypozovo 110/35/6 kv | 10+10 | 0 | 2.857 | 5.042 | 120 | -2.185 | 0 | 10.5 | 12.685 | 10.5 |  |  | 27.2095 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 10+10 | 1.342 | 1.342 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.342 | 1.342 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0
| Nom. capacity LV, MVA | 10+10 | 1.515 | 3.7 | 120 | -2.185 | 0 | 10.5 | 12.685 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 1.515 | 3.7 | 120 | -2.185 | 0 | 10.5 | 12.685 |  | 0
104 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 31.51 | 19.6 | 120 | 11.91 | 0 | 42 | 30.09 | 28.472 |  |  | 75.0238 | 104 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 0.4825 | 31.9925 | 19.6 | 120 | 12.3925 | 0 | 42 | 29.6075 | 28.1245 |  |  | 76.1726 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 40+40 | 24.328 | 10.8 | 120 | 13.528 | 0 | 42 | 28.472 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.3475 | 24.6755 | 10.8 | 120 | 13.8755 | 0 | 42 | 28.1245 |  | 0
| Nom. capacity LV, MVA | 40+40 | 7.182 | 8.8 | 120 | -1.618 | 0 | 42 | 43.618 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.135 | 7.317 | 8.8 | 120 | -1.483 | 0 | 42 | 43.483 |  | 0
105 | SS Kasharovo 110/35/10-6 kv | 25+20 | 10.329 | 8.589 | 120 | 1.74 | 0 | 21 | 19.26 | 19.26 |  |  | 49.1857 | 105 | SS Kasharovo 110/35/10-6 kv | 25+20 | 0 | 10.329 | 8.589 | 120 | 1.74 | 0 | 21 | 19.26 | 19.26 |  |  | 49.1857 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 25+20 | 4.289 | 4.289 | 120 | 0 | 0 | 21 | 21 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+20 | 0 | 4.289 | 4.289 | 120 | 0 | 0 | 21 | 21 |  | 0
| Nom. capacity LV, MVA | 25+20 | 6.04 | 4.3 | 120 | 1.74 | 0 | 21 | 19.26 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25+20 | 0 | 6.04 | 4.3 | 120 | 1.74 | 0 | 21 | 19.26 |  | 0
106 | SS Spirovo 110/35/10 kv | 16+16 | 2.569 | 1.673 | 120 | 0.896 | 0 | 16.8 | 15.904 | 15.904 |  |  | 15.2917 | 106 | SS Spirovo 110/35/10 kv | 16+16 | 0 | 2.569 | 1.673 | 120 | 0.896 | 0 | 16.8 | 15.904 | 15.904 |  |  | 15.2917 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 16+16 | 1.073 | 1.073 |  | 0 | 0 | 16.8 | 16.8 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0 | 1.073 | 1.073 |  | 0 | 0 | 16.8 | 16.8 |  | 0
| Nom. capacity LV, MVA | 16+16 | 1.496 | 0.6 | 120 | 0.896 | 0 | 16.8 | 15.904 |  | 0 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 1.496 | 0.6 | 120 | 0.896 | 0 | 16.8 | 15.904 |  | 0
107 | SS Trud 110/35/10 kv | 16+16 | 5.056 | 4.862 | 120 | 0.194 | 0 | 16.8 | 16.606 | 16.606 |  |  | 30.0952 | 107 | SS Trud 110/35/10 kv | 16+16 | 0.25 | 5.306 | 4.862 | 120 | 0.444 | 0 | 16.8 | 16.356 | 16.356 |  |  | 31.5833 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 16+16 | 4.862 | 4.862 | 120 | 0 | 0 | 16.8 | 16.8 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.25 | 5.112 | 4.862 | 120 | 0.25 | 0 | 16.8 | 16.55 |  | 0
| Nom. capacity LV, MVA | 16+16 | 0.194 | 0 |  | 0.194 | 0 | 16.8 | 16.606 |  | 0 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 0.194 | 0 |  | 0.194 | 0 | 16.8 | 16.606 |  | 0
108 | SS Udomlya 110/35/10 kv | 25+25 | 18.159 | 18.891 | 120 | -0.732 | 0 | 26.25 | 26.982 | 26.25 |  |  | 69.1771 | 108 | SS Udomlya 110/35/10 kv | 25+25 | 4.6353 | 22.7943 | 18.891 | 120 | 3.9032 | 0 | 26.25 | 22.3468 | 21.6648 |  |  | 86.8352 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 25+25 | 11.691 | 11.691 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+25 | 4.5853 | 16.2763 | 11.691 | 120 | 4.5853 | 0 | 26.25 | 21.6648 |  | 0
| Nom. capacity LV, MVA | 25+25 | 6.468 | 7.2 | 120 | -0.732 | 0 | 26.25 | 26.982 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.05 | 6.518 | 7.2 | 120 | -0.682 | 0 | 26.25 | 26.932 |  | 0
109 | SS Kholokholenka 110/35/10 kv | 6.3+6.3 | 3.284 | 2.491 | 120 | 0.793 | 0 | 6.62 | 5.827 | 5.827 |  |  | 49.6073 | 109 | SS Kholokholenka 110/35/10 kv | 6.3+6.3 | 0.1 | 3.384 | 2.491 | 120 | 0.893 | 0 | 6.62 | 5.727 | 5.727 |  |  | 51.1178 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 6,3+6,3 | 2.491 | 2.491 | 120 | 0 | 0 | 6.62 | 6.62 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.1 | 2.591 | 2.491 | 120 | 0.1 | 0 | 6.62 | 6.52 |  | 0
| Nom. capacity LV, MVA | 6,3+6,3 | 0.793 | 0 |  | 0.793 | 0 | 6.62 | 5.827 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.793 | 0 |  | 0.793 | 0 | 6.62 | 5.827 |  | 0
110 | SS Leontyevo 110/35/10 kv | 25+25 | 4.668 | 4.546 | 120 | 0.122 | 0 | 26.25 | 26.128 | 26.128 |  |  | 17.7829 | 110 | SS Leontyevo 110/35/10 kv | 25+25 | 0 | 4.668 | 4.546 | 120 | 0.122 | 0 | 6.62 | 6.498 | 6.498 |  |  | 70.5136 | Вышневолоцкие Электрические сети
| Nom. capacity MV, MVA | 25+25 | 4.546 | 4.546 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+25 | 0 | 4.546 | 4.546 | 120 | 0 | 0 | 6.62 | 6.62 |  | 0
| Nom. capacity LV, MVA | 25+25 | 0.122 | 0 |  | 0.122 | 0 | 26.25 | 26.128 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 0.122 | 0 |  | 0.122 | 0 | 6.62 | 6.498 |  | 0
111 | 35/6 kv Mikrorayonnaya | 6.3 | 2.7016 | 2.7016 | 24 hours | 2.7016 | 0 | 2.7016 | 0 | 0 |  |  | 40.84 | 111 | 35/6 kv Mikrorayonnaya | 6.3 | 0 | 2.7016 | 2.7016 | 24 hours | 2.7016 | 0 | 2.7016 | 0 | 0 |  |  | 40.84 | Кимрские Электрические сети
112 | 35/10 kv Barykovo | 2,5 +2,5 | 0.96274 | 0 |  | 0.96274 | 0 | 2.625 | 1.6623 | 1.6623 |  |  | 36.676 | 112 | 35/10 kv Barykovo | 2,5 +2,5 | 0.21875 | 1.1815 | 0 |  | 1.1815 | 0 | 2.625 | 1.4435 | 1.4435 |  |  | 45.0093 | Кимрские Электрические сети
113 | 35/10 kv B.Gorodok | 5,6 +6,3 | 3.7777 | 0 |  | 3.7777 | 0 | 5.88 | 2.1023 | 2.1023 |  |  | 64.2466 | 113 | 35/10 kv B.Gorodok | 5,6 +6,3 | 0.0625 | 3.8402 | 0 |  | 3.8402 | 0 | 5.88 | 2.0398 | 2.0398 |  |  | 65.3095 | Кимрские Электрические сети
114 | 35/10 kv Vega | 2,5 +2,5 | 0.76293 | 0 |  | 0.76293 | 0 | 2.625 | 1.8621 | 1.8621 |  |  | 29.064 | 114 | 35/10 kv Vega | 2,5 +2,5 | 0.125 | 0.88793 | 0 |  | 0.88793 | 0 | 2.625 | 1.7371 | 1.7371 |  |  | 33.8259 | Кимрские Электрические сети
115 | 35/10 kv Volga | 6,3+6,3 | 5.9711 | 0 |  | 5.9711 | 0 | 6.615 | 0.64393 | 0.64393 |  |  | 90.2656 | 115 | 35/10 kv Volga | 6,3+6,3 | 0 | 5.9711 | 0 |  | 5.9711 | 0 | 6.615 | 0.64393 | 0.64393 |  |  | 90.2656 | Кимрские Электрические сети
116 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 2.3542 | 0 |  | 2.3542 | 0 | 2.625 | 0.27082 | 0.27082 |  |  | 89.6832 | 116 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 0.25 | 2.6042 | 0 |  | 2.6042 | 0 | 2.625 | 0.020816 | 0.020816 |  |  | 99.207 | Кимрские Электрические сети
117 | 35/10 kv Kalyazin | 6,3 +6,3 | 7.7753 | 0 |  | 7.7753 | 0 | 6.615 | -1.1603 | -1.1603 | MS is closed | MS is closed | 117.5406 | 117 | 35/10 kv Kalyazin | 6,3 +6,3 | 1.9238 | 9.6991 | 0 |  | 9.6991 | 0 | 6.615 | -3.0841 | -3.0841 | MS is closed | MS is closed | 146.6223 | Кимрские Электрические сети
118 | 35/10 kv Kimry | 16,0+16,0 | 8.4843 | 0 |  | 8.4843 | 0 | 16.8 | 8.3157 | 8.3157 |  |  | 50.5016 | 118 | 35/10 kv Kimry | 16,0+16,0 | 0 | 8.4843 | 0 |  | 8.4843 | 0 | 16.8 | 8.3157 | 8.3157 |  |  | 50.5016 | Кимрские Электрические сети
119 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0.78109 | 0 |  | 0.78109 | 0 | 2.625 | 1.8439 | 1.8439 |  |  | 29.756 | 119 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0 | 0.78109 | 0 |  | 0.78109 | 0 | 2.625 | 1.8439 | 1.8439 |  |  | 29.756 | Кимрские Электрические сети
120 | 35/10 kv Kurortnaya | 4,0 +4,0 | 2.4523 | 0 |  | 2.4523 | 0 | 4.2 | 1.7477 | 1.7477 |  |  | 58.3875 | 120 | 35/10 kv Kurortnaya | 4,0 +4,0 | 0.32625 | 2.7785 | 0 |  | 2.7785 | 0 | 4.2 | 1.4215 | 1.4215 |  |  | 66.1554 | Кимрские Электрические сети
121 | 35/10 kv Mayak | 6,3 +6,3 | 3.9432 | 0 |  | 3.9432 | 0 | 6.615 | 2.6718 | 2.6718 |  |  | 59.6095 | 121 | 35/10 kv Mayak | 6,3 +6,3 | 0.925 | 4.8682 | 0 |  | 4.8682 | 0 | 6.615 | 1.7468 | 1.7468 |  |  | 73.5929 | Кимрские Электрические сети
122 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 3.0699 | 0 |  | 3.0699 | 0 | 4.2 | 1.1301 | 1.1301 |  |  | 73.0925 | 122 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 0 | 3.0699 | 0 |  | 3.0699 | 0 | 4.2 | 1.1301 | 1.1301 |  |  | 73.0925 | Кимрские Электрические сети
123 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0.6837 | 0 |  | 0.6837 | 0 | 1.89 | 1.2063 | 1.2063 |  |  | 36.1744 | 123 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0.0375 | 0.7212 | 0 |  | 0.7212 | 0 | 1.89 | 1.1688 | 1.1688 |  |  | 38.1585 | Кимрские Электрические сети
124 | 35/10 kv Neklyudovo | 1,6 +1,6 | 1.7257 | 0 |  | 1.7257 | 0 | 1.68 | -0.045675 | -0.045675 | MS is closed | MS is closed | 102.7188 | 124 | 35/10 kv Neklyudovo | 1,6 +1,6 | 0.075 | 1.8007 | 0 |  | 1.8007 | 0 | 1.68 | -0.12068 | -0.12068 | MS is closed | MS is closed | 107.183 | Кимрские Электрические сети
125 | 35/10 kv Nerl | 4,0 +2,5 | 1.8347 | 0 |  | 1.8347 | 0 | 2.625 | 0.79034 | 0.79034 |  |  | 69.892 | 125 | 35/10 kv Nerl | 4,0 +2,5 | 0.24375 | 2.0784 | 0 |  | 2.0784 | 0 | 2.625 | 0.54658 | 0.54658 |  |  | 79.1777 | Кимрские Электрические сети
126 | 35/10 kv Plutkovo | 2,5 +2,5 | 1.3624 | 0 |  | 1.3624 | 0 | 2.625 | 1.2626 | 1.2626 |  |  | 51.9 | 126 | 35/10 kv Plutkovo | 2,5 +2,5 | 0.375 | 1.7374 | 0 |  | 1.7374 | 0 | 2.625 | 0.88762 | 0.88762 |  |  | 66.1857 | Кимрские Электрические сети
127 | 35/10 kv Savtsino | 2,5 +2,5 | 0.23614 | 0 |  | 0.23614 | 0 | 2.625 | 2.3889 | 2.3889 |  |  | 8.996 | 127 | 35/10 kv Savtsino | 2,5 +2,5 | 0 | 0.23614 | 0 |  | 0.23614 | 0 | 2.625 | 2.3889 | 2.3889 |  |  | 8.996 | Кимрские Электрические сети
128 | 35/10 kv Sotskoe | 1,6 +2,5 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 |  |  | 27.0312 | 128 | 35/10 kv Sotskoe | 1,6 +2,5 | 0 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 |  |  | 27.0312 | Кимрские Электрические сети
129 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0.27248 | 0 |  | 0.27248 | 0 | 2.625 | 2.3525 | 2.3525 |  |  | 10.38 | 129 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0 | 0.27248 | 0 |  | 0.27248 | 0 | 2.625 | 2.3525 | 2.3525 |  |  | 10.38 | Кимрские Электрические сети
130 | 35/10 kv Ulanovo | 1,6 +1,6 | 1.7092 | 0 |  | 1.7092 | 0 | 1.68 | -0.02924 | -0.02924 | MS is closed | MS is closed | 101.7405 | 130 | 35/10 kv Ulanovo | 1,6 +1,6 | 0 | 1.7092 | 0 |  | 1.7092 | 0 | 1.68 | -0.02924 | -0.02924 | MS is closed | MS is closed | 101.7405 | Кимрские Электрические сети
131 | 35/10 kv Unitsy | 4,0 +4,0 | 0.2339 | 0 |  | 0.2339 | 0 | 4.2 | 3.9661 | 3.9661 |  |  | 5.569 | 131 | 35/10 kv Unitsy | 4,0 +4,0 | 0 | 0.2339 | 0 |  | 0.2339 | 0 | 4.2 | 3.9661 | 3.9661 |  |  | 5.569 | Кимрские Электрические сети
132 | 35/10 kv Fenevo | 2,5 +2,5 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 |  |  | 9.8 | 132 | 35/10 kv Fenevo | 2,5 +2,5 | 0 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 |  |  | 9.8 | Кимрские Электрические сети
133 | 35/10 kv Frolovo | 2,5 +2,5 | 0.8996 | 0 |  | 0.8996 | 0 | 2.625 | 1.7254 | 1.7254 |  |  | 34.2705 | 133 | 35/10 kv Frolovo | 2,5 +2,5 | 0.1875 | 1.0871 | 0 |  | 1.0871 | 0 | 2.625 | 1.5379 | 1.5379 |  |  | 41.4133 | Кимрские Электрические сети
134 | 110/10 kv Zarnitsa | 10,0+10,0 | 0.10899 | 0 |  | 0.10899 | 0 | 10.5 | 10.391 | 10.391 |  |  | 1.038 | 134 | 110/10 kv Zarnitsa | 10,0+10,0 | 0 | 0.10899 | 0 |  | 0.10899 | 0 | 10.5 | 10.391 | 10.391 |  |  | 1.038 | Кимрские Электрические сети
135 | 110/10 kv Zobnino | 2,5 +2,5 | 0.83236 | 0 |  | 0.83236 | 0 | 2.625 | 1.7926 | 1.7926 |  |  | 31.709 | 135 | 110/10 kv Zobnino | 2,5 +2,5 | 0 | 0.83236 | 0 |  | 0.83236 | 0 | 2.625 | 1.7926 | 1.7926 |  |  | 31.709 | Кимрские Электрические сети
136 | 110/10 kv Inyakino | 25,0+25,0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 |  |  | 0.88642 | 136 | 110/10 kv Inyakino | 25,0+25,0 | 0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 |  |  | 0.88642 | Кимрские Электрические сети
137 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 |  |  | 2.1341 | 137 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 |  |  | 2.1341 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  | 0
| Nom. capacity LV, MVA | 6,3+6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 |  | 0
138 | 110/35/10 kv Borki | 40,0+25,0 | 25.0829 | 0 |  | 25.0829 | 0 | 26.25 | 1.1671 | 1.1671 |  |  | 95.5537 | 138 | 110/35/10 kv Borki | 40,0+25,0 | 1.15 | 26.2329 | 0 |  | 26.2329 | 0 | 26.25 | 0.017143 | 0.017143 |  |  | 99.9347 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 40,0+25,0 | 21.4646 | 0 |  | 21.4646 | 0 | 26.25 | 4.7854 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40,0+25,0 | 0.9875 | 22.4521 | 0 |  | 22.4521 | 0 | 26.25 | 3.7979 |  | 0
| Nom. capacity LV, MVA | 40,0+25,0 | 3.6183 | 0 |  | 3.6183 | 0 | 26.25 | 22.6317 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40,0+25,0 | 0.1625 | 3.7808 | 0 |  | 3.7808 | 0 | 26.25 | 22.4692 |  | 0
139 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 5.0827 | 3.0107 | 24 hours | 2.0721 | 0 | 6.615 | 4.5429 | 4.5429 |  |  | 76.8366 | 139 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 0.10625 | 5.189 | 3.0107 | 24 hours | 2.1783 | 0 | 6.615 | 4.4367 | 4.4367 |  |  | 78.4428 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 6,3 +6,3 | 3.0107 | 3.0107 | 24 hours | 0 | 0 | 6.615 | 6.615 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0.075 | 3.0857 | 3.0107 | 24 hours | 0.075 | 0 | 6.615 | 6.54 |  | 0
| Nom. capacity LV, MVA | 6,3 +6,3 | 2.0721 | 0 |  | 2.0721 | 0 | 6.615 | 4.5429 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0.03125 | 2.1033 | 0 |  | 2.1033 | 0 | 6.615 | 4.5117 |  | 0
140 | 110/35/10 kv Goritsy | 6,3 +6,3 | 2.8396 | 0.14067 | 24 hours | 2.699 | 0 | 6.615 | 3.916 | 3.916 |  |  | 42.927 | 140 | 110/35/10 kv Goritsy | 6,3 +6,3 | 0 | 2.8396 | 0.14067 | 24 hours | 2.699 | 0 | 6.615 | 3.916 | 3.916 |  |  | 42.927 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 6,3 +6,3 | 0.14067 | 0.14067 | 24 hours | 0 | 0 | 6.615 | 6.615 |  | 0 |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0 | 0.14067 | 0.14067 | 24 hours | 0 | 0 | 6.615 | 6.615 |  | 0
| Nom. capacity LV, MVA | 6,3 +6,3 | 2.699 | 0 |  | 2.699 | 0 | 6.615 | 3.916 |  | 0 |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0 | 2.699 | 0 |  | 2.699 | 0 | 6.615 | 3.916 |  | 0
141 | 110/35/10 kv Luch | 16,0+16,0 | 21.0503 | 0 |  | 21.0503 | 0 | 16.8 | -4.2503 | -4.2503 | MS is closed | MS is closed | 125.2996 | 141 | 110/35/10 kv Luch | 16,0+16,0 | 6.2862 | 27.3366 | 0 |  | 27.3366 | 0 | 16.8 | -10.5366 | -10.5366 | MS is closed | MS is closed | 162.7177 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 16,0+16,0 | 16.4718 | 0 |  | 16.4718 | 0 | 16.8 | 0.32821 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 16,0+16,0 | 2.4613 | 18.933 | 0 |  | 18.933 | 0 | 16.8 | -2.133 |  |  | MS is closed
| Nom. capacity LV, MVA | 16,0+16,0 | 4.5785 | 0 |  | 4.5785 | 0 | 16.8 | 12.2215 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 16,0+16,0 | 3.825 | 8.4035 | 0 |  | 8.4035 | 0 | 16.8 | 8.3965 |  |  | MS is closed
142 | 110/35/10 kv Prostor | 25,0+16,0 | 13.2041 | 0.4178 | 24 hours | 12.7863 | 0 | 16.8 | 4.0137 | 4.0137 |  |  | 78.5957 | 142 | 110/35/10 kv Prostor | 25,0+16,0 | 0.94 | 14.1441 | 0.4178 | 24 hours | 13.7263 | 0 | 16.8 | 3.0737 | 3.0737 |  |  | 84.1909 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 25,0+16,0 | 5.1265 | 0.4178 | 24 hours | 4.7087 | 0 | 16.8 | 12.0913 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25,0+16,0 | 0.7325 | 5.859 | 0.4178 | 24 hours | 5.4412 | 0 | 16.8 | 11.3588 |  | 0
| Nom. capacity LV, MVA | 25,0+16,0 | 8.0776 | 0 |  | 8.0776 | 0 | 16.8 | 8.7224 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25,0+16,0 | 0.2075 | 8.2851 | 0 |  | 8.2851 | 0 | 16.8 | 8.5149 |  | 0
143 | 110/35/10 kv Raduga | 40,0+25,0 | 31.2519 | 0.16348 | 24 hours | 31.0884 | 0 | 26.25 | -4.8384 | -4.8384 | MS is closed | MS is closed | 119.0547 | 143 | 110/35/10 kv Raduga | 40,0+25,0 | 1.5375 | 32.7894 | 0.16348 | 24 hours | 32.6259 | 0 | 26.25 | -6.3759 | -6.3759 | MS is closed | MS is closed | 124.9118 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 40,0+25,0 | 21.3404 | 0.16348 | 24 hours | 21.1769 | 0 | 26.25 | 5.0731 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 40,0+25,0 | 0.25 | 21.5904 | 0.16348 | 24 hours | 21.4269 | 0 | 26.25 | 4.8231 |  |  | MS is closed
| Nom. capacity LV, MVA | 40,0+25,0 | 9.9114 | 0 |  | 9.9114 | 0 | 26.25 | 16.3386 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 40,0+25,0 | 1.2875 | 11.1989 | 0 |  | 11.1989 | 0 | 26.25 | 15.0511 |  |  | MS is closed
144 | 110/35/10 kv Roshcha | 10,0+10,0 | 4.4695 | 0.3633 | 24 hours | 4.1062 | 0 | 10.5 | 6.3938 | 6.3938 |  |  | 42.5669 | 144 | 110/35/10 kv Roshcha | 10,0+10,0 | 0.8875 | 5.357 | 0.3633 | 24 hours | 4.9937 | 0 | 10.5 | 5.5063 | 5.5063 |  |  | 51.0192 | Кимрские Электрические сети
| Nom. capacity MV, MVA | 10,0+10,0 | 0.88937 | 0.3633 | 24 hours | 0.52607 | 0 | 10.5 | 9.9739 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.88937 | 0.3633 | 24 hours | 0.52607 | 0 | 10.5 | 9.9739 |  | 0
| Nom. capacity LV, MVA | 10,0+10,0 | 3.5801 | 0 |  | 3.5801 | 0 | 10.5 | 6.9199 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0.8875 | 4.4676 | 0 |  | 4.4676 | 0 | 10.5 | 6.0324 |  | 0
145 | SS 110/10 kv Bibirevo | 2.5 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 |  |  | 3.8095 | 145 | SS 110/10 kv Bibirevo | 2.5 | 0 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 |  |  | 3.8095 | Нелидовские Электрические сети
146 | SS 35/10 kv Bor | 1.6 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 17.8571 | 146 | SS 35/10 kv Bor | 1.6 | 0 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 17.8571 | Нелидовские Электрические сети
147 | SS 110/10 kv Vorobyi | 2.5 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 11.4286 | 147 | SS 110/10 kv Vorobyi | 2.5 | 0 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 11.4286 | Нелидовские Электрические сети
148 | SS 35/10 kv Glazomichi | 2.5 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | MS is closed | 3.8095 | 148 | SS 35/10 kv Glazomichi | 2.5 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | MS is closed | 3.8095 | Нелидовские Электрические сети
149 | SS 35/10 kv Zharki | 10 | 2.2 | 0 |  | 0 | 0 | 0 | -2.2 | -2.2 | MS is closed | MS is closed | 20.9524 | 149 | SS 35/10 kv Zharki | 10 | 0.065 | 2.265 | 0 |  | 0 | 0 | 0 | -2.265 | -2.265 | MS is closed | MS is closed | 21.5714
150 | SS 35/10 kv Zemtsy | 2.5 | 0.5 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.1 | 0.1 |  |  | 19.0476 | 150 | SS 35/10 kv Zemtsy | 2.5 | 0.12375 | 0.62375 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | -0.02375 | -0.02375 | MS is closed | MS is closed | 23.7619
151 | SS 35/10 kv Kovalevo | 2.5 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 7.619 | 151 | SS 35/10 kv Kovalevo | 2.5 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  |  | 7.619 | Нелидовские Электрические сети
152 | SS 35/10 kv Korotyshi | 1.6 | 0.3 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.3 | 0.3 |  |  | 17.8571 | 152 | SS 35/10 kv Korotyshi | 1.6 | 0 | 0.3 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.3 | 0.3 |  |  | 17.8571 | Нелидовские Электрические сети
153 | SS 110/10 kv Monino | 6.3 | 1.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | -0.6 | -0.6 | MS is closed | MS is closed | 19.6523 | 153 | SS 110/10 kv Monino | 6.3 | 0.165 | 1.465 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | -0.765 | -0.765 | MS is closed | MS is closed | 22.1466 | Нелидовские Электрические сети
154 | SS 35/10 kv Ozerets | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | 154 | SS 35/10 kv Ozerets | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | Нелидовские Электрические сети
155 | SS 35/10 kv Pozhnya | 1.6 | 0.2 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.6 | 0.6 |  |  | 11.9048 | 155 | SS 35/10 kv Pozhnya | 1.6 | 0 | 0.2 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.6 | 0.6 |  |  | 11.9048 | Нелидовские Электрические сети
156 | SS 35/10 kv Polovtsovo | 1.6 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 |  |  | 17.8571 | 156 | SS 35/10 kv Polovtsovo | 1.6 | 0 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 |  |  | 17.8571 | Нелидовские Электрические сети
157 | SS 110/10 kv Ponizovye | 2.5 | 0.4 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | -0.2 | -0.2 | MS is closed | MS is closed | 15.2381 | 157 | SS 110/10 kv Ponizovye | 2.5 | 0 | 0.4 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | -0.2 | -0.2 | MS is closed | MS is closed | 15.2381 | Нелидовские Электрические сети
158 | SS 35/10 kv Sinkovo | 1 | 0.2 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0.2 | 0.2 |  |  | 19.0476 | 158 | SS 35/10 kv Sinkovo | 1 | 0.1 | 0.3 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0.1 | 0.1 |  |  | 28.5714 | Нелидовские Электрические сети
159 | SS 35/10 kv Ulin | 1.6 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed | MS is closed | 17.8571 | 159 | SS 35/10 kv Ulin | 1.6 | 0 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed | MS is closed | 17.8571 | Нелидовские Электрические сети
160 | SS 35/10 kv Kavelshchino | 2.5 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  |  | 7.619 | 160 | SS 35/10 kv Kavelshchino | 2.5 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  |  | 7.619 | Нелидовские Электрические сети
161 | SS 35/10 kv Bologovo | 1,6+2,5 | 0.4 | 0.4 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 23.8095 | 161 | SS 35/10 kv Bologovo | 1,6+2,5 | 0 | 0.4 | 0.4 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 23.8095 | Нелидовские Электрические сети
162 | SS 35/10 kv Verkhovye | 1+2,5 | 0.2 | 0.8 | 120 | -0.6 | 0 | 1.05 | 1.65 | 1.65 |  |  | 19.0476 | 162 | SS 35/10 kv Verkhovye | 1+2,5 | 0 | 0.2 | 0.8 | 120 | -0.6 | 0 | 1.05 | 1.65 | 1.65 |  |  | 19.0476 | Нелидовские Электрические сети
163 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0.4 | 0.4 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 23.8095 | 163 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0 | 0.4 | 0.4 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  | 23.8095 | Нелидовские Электрические сети
164 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0.3 | 0.3 | 120 | 0 | 0 | 2.65 | 2.65 | 2.65 |  |  | 11.3208 | 164 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0 | 0.3 | 0.3 | 120 | 0 | 0 | 2.65 | 2.65 | 2.65 |  |  | 11.3208 | Нелидовские Электрические сети
165 | SS 35/10 kv Ilyino | 1,6+1,6 | 0.8 | 0.3 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 |  |  | 47.619 | 165 | SS 35/10 kv Ilyino | 1,6+1,6 | 0 | 0.8 | 0.3 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 |  |  | 47.619 | Нелидовские Электрические сети
166 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0.8 | 0.1 | 120 | 0.7 | 0 | 1.68 | 0.98 | 0.98 |  |  | 47.619 | 166 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0 | 0.8 | 0.1 | 120 | 0.7 | 0 | 1.68 | 0.98 | 0.98 |  |  | 47.619 | Нелидовские Электрические сети
167 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 4.5 | 1.5 | 120 | 3 | 0 | 5.88 | 2.88 | 2.88 |  |  | 76.5306 | 167 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 0 | 4.5 | 1.5 | 120 | 3 | 0 | 5.88 | 2.88 | 2.88 |  |  | 76.5306 | Нелидовские Электрические сети
168 | SS 35/10 kv St. Toropa | 4+4 | 2.6 | 0 |  | 2.6 | 0 | 4.5 | 1.9 | 1.9 |  |  | 57.7778 | 168 | SS 35/10 kv St. Toropa | 4+4 | 0 | 2.6 | 0 |  | 2.6 | 0 | 4.5 | 1.9 | 1.9 |  |  | 57.7778 | Нелидовские Электрические сети
169 | SS 110/35/10 kv Andreapol | 10+10 | 7.8 | 0.4 | 120 | 7.4 | 0 | 10.5 | 3.1 | 3.1 |  |  | 74.2857 | 169 | SS 110/35/10 kv Andreapol | 10+10 | 3.925 | 11.725 | 0.4 | 120 | 11.325 | 0 | 10.5 | -0.825 | -0.825 | MS is closed | MS is closed | 111.6667 | Нелидовские Электрические сети
| Nom. capacity MV, MVA | 10+10 | 0.9 | 0 |  | 0.9 | 0 | 10.5 | 9.6 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.1375 | 1.0375 | 0 |  | 1.0375 | 0 | 10.5 | 9.4625 |  |  | MS is closed
| Nom. capacity LV, MVA | 10+10 | 6.9 | 0.4 | 120 | 6.5 | 0 | 10.5 | 4 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10+10 | 3.7875 | 10.6875 | 0.4 | 120 | 10.2875 | 0 | 10.5 | 0.2125 |  |  | MS is closed
170 | SS 110/35/10 kv Bely | 16+10 | 5.2 | 0.3 | 120 | 4.9 | 0 | 10.5 | 5.6 | 5.6 |  |  | 49.5238 | 170 | SS 110/35/10 kv Bely | 16+10 | 0.065 | 5.265 | 0.3 | 120 | 4.965 | 0 | 10.5 | 5.535 | 5.535 |  |  | 50.1429 | Нелидовские Электрические сети
| Nom. capacity MV, MVA | 16+10 | 2.9 | 0 |  | 2.9 | 0 | 10.5 | 7.6 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.065 | 2.965 | 0 |  | 2.965 | 0 | 10.5 | 7.535 |  | 0
| Nom. capacity LV, MVA | 16+10 | 2.3 | 0.3 | 120 | 2 | 0 | 10.5 | 8.5 |  | 0 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0 | 2.3 | 0.3 | 120 | 2 | 0 | 10.5 | 8.5 |  | 0
171 | SS 110/35/10 kv Zapadnaya Dvina | 10+10 | 11.2 | 2.1 | 120 | 9.1 | 0 | 10.5 | 1.4 | 1.4 |  |  | 106.6667 | 171 | SS 110/35/10 kv Zapadnaya Dvina | 10+10 | 0.34125 | 11.5412 | 2.1 | 120 | 9.4413 | 0 | 10.5 | 1.0588 | 1.0588 |  |  | 109.9167 | Нелидовские Электрические сети
| Nom. capacity MV, MVA | 10+10 | 3.1 | 1.6 | 120 | 1.5 | 0 | 10.5 | 9 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.12375 | 3.2237 | 1.6 | 120 | 1.6238 | 0 | 10.5 | 8.8763 |  | 0
| Nom. capacity LV, MVA | 10+10 | 8.1 | 0.5 |  | 7.6 | 0 | 10.5 | 2.9 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.2175 | 8.3175 | 0.5 |  | 7.8175 | 0 | 10.5 | 2.6825 |  | 0
172 | SS 110/35/10 kv Toropets | 16+25 | 18.9 | 1.3 | 120 | 17.6 | 0 | 16.8 | -0.8 | -0.8 | MS is closed | MS is closed | 112.5 | 172 | SS 110/35/10 kv Toropets | 16+25 | 0 | 18.9 | 1.3 | 120 | 17.6 | 0 | 16.8 | -0.8 | -0.8 | MS is closed | MS is closed | 112.5 | Нелидовские Электрические сети
| Nom. capacity MV, MVA | 16+25 | 5.2 | 1 | 120 | 4.2 | 0 | 16.8 | 12.6 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 16+25 | 0 | 5.2 | 1 | 120 | 4.2 | 0 | 16.8 | 12.6 |  |  | MS is closed
| Nom. capacity LV, MVA | 16+25 | 13.7 | 0.3 | 120 | 13.4 | 0 | 16.8 | 3.4 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 16+25 | 0 | 13.7 | 0.3 | 120 | 13.4 | 0 | 16.8 | 3.4 |  |  | MS is closed
173 | SS Bakhmutovo 35/10 kv | 2.5 | 0.78109 | 0.78109 | 120 | 0.78109 | 0 | 0.78109 | 0 | 0 |  |  | 29.756 | 173 | SS Bakhmutovo 35/10 kv | 2.5 | 0 | 0.78109 | 0.78109 | 120 | 0.78109 | 0 | 0.78109 | 0 | 0 |  |  | 29.756 | Ржевские Электрические сети
174 | SS Pyatnitskoe 35/10kv | 2.5 | 0.17646 | 0.17646 | 240 | 0.17646 | 0 | 0.17646 | 0 | 0 |  |  | 6.7223 | 174 | SS Pyatnitskoe 35/10kv | 2.5 | 0 | 0.17646 | 0.17646 | 240 | 0.17646 | 0 | 0.17646 | 0 | 0 |  |  | 6.7223 | Ржевские Электрические сети
175 | SS Karamzino 35/10kv | 1.6 | 0.49045 | 0 |  | 0 | 0 | 0 | -0.49045 | -0.49045 | MS is closed | MS is closed | 29.1938 | 175 | SS Karamzino 35/10kv | 1.6 | 0.075 | 0.56546 | 0 |  | 0 | 0 | 0 | -0.56546 | -0.56546 | MS is closed | MS is closed | 33.658 | Ржевские Электрические сети
176 | SS Kn. Gory 35/10kv | 2.5 | 1.6167 | 0.2 | 240 | 0.2 | 0 | 0.2 | -1.4167 | -1.4167 | MS is closed | MS is closed | 61.588 | 176 | SS Kn. Gory 35/10kv | 2.5 | 0.55 | 2.1667 | 0.2 | 240 | 0.2 | 0 | 0.2 | -1.9667 | -1.9667 | MS is closed | MS is closed | 82.5404 | Ржевские Электрические сети
177 | SS Salino 35/10kv | 2.5 | 0.4671 | 0 |  | 0 | 0 | 0 | -0.4671 | -0.4671 | MS is closed | MS is closed | 17.7943 | 177 | SS Salino 35/10kv | 2.5 | 0 | 0.4671 | 0 |  | 0 | 0 | 0 | -0.4671 | -0.4671 | MS is closed | MS is closed | 17.7943 | Ржевские Электрические сети
178 | SS Gusevo 35/10kv | 2.5 | 0.2159 | 0.2159 | 120 | 0.2159 | 0 | 0.2159 | 0 | 0 |  |  | 8.2249 | 178 | SS Gusevo 35/10kv | 2.5 | 0 | 0.2159 | 0.2159 | 120 | 0.2159 | 0 | 0.2159 | 0 | 0 |  |  | 8.2249 | Ржевские Электрические сети
179 | SS Mol.Tud 35/10kv | 2.5 | 0.58128 | 0.58128 | 120 | 0.58128 | 0 | 0.58128 | 0 | 0 |  |  | 22.144 | 179 | SS Mol.Tud 35/10kv | 2.5 | 0 | 0.58128 | 0.58128 | 120 | 0.58128 | 0 | 0.58128 | 0 | 0 |  |  | 22.144 | Ржевские Электрические сети
180 | SS Ilyenki 35/10kv | 2.5 | 0.28545 | 0.28545 | 120 | 0.28545 | 0 | 0.28545 | 0 | 0 |  |  | 10.8743 | 180 | SS Ilyenki 35/10kv | 2.5 | 0 | 0.28545 | 0.28545 | 120 | 0.28545 | 0 | 0.28545 | 0 | 0 |  |  | 10.8743 | Ржевские Электрические сети
181 | SS Kadenka 35/10kv | 1 | 0.052938 | 0.052938 | 120 | 0.052938 | 0 | 0.052938 | 0 | 0 |  |  | 5.0417 | 181 | SS Kadenka 35/10kv | 1 | 0 | 0.052938 | 0.052938 | 120 | 0.052938 | 0 | 0.052938 | 0 | 0 |  |  | 5.0417 | Ржевские Электрические сети
182 | SS Rodnya 35/10kv | 2.5 | 0.33527 | 0.33527 | 120 | 0.33527 | 0 | 0.33527 | 0 | 0 |  |  | 12.7723 | 182 | SS Rodnya 35/10kv | 2.5 | 0.2375 | 0.57277 | 0.33527 | 120 | 0.33527 | 0 | 0.33527 | -0.2375 | -0.2375 | MS is closed | MS is closed | 21.82 | Ржевские Электрические сети
183 | SS Bernovo 35/10kv | 1.6 | 0.4671 | 0 |  | 0 | 0 | 0 | -0.4671 | -0.4671 | MS is closed | MS is closed | 27.8036 | 183 | SS Bernovo 35/10kv | 1.6 | 0 | 0.4671 | 0 |  | 0 | 0 | 0 | -0.4671 | -0.4671 | MS is closed | MS is closed | 27.8036 | Ржевские Электрические сети
184 | SS RMK 35/10kv | 10+10 | 11.49 | 1.4167 | 240 | 10.0733 | 0 | 10.5 | 0.42667 | 0.42667 |  |  | 109.4286 | 184 | SS RMK 35/10kv | 10+10 | 0 | 11.49 | 1.4167 | 240 | 10.0733 | 0 | 10.5 | 0.42667 | 0.42667 |  |  | 109.4286 | Ржевские Электрические сети
185 | SS Osuga 35/10kv | 2,5+2,5 | 0.28 | 0 |  | 0.28 | 0 | 2.625 | 2.345 | 2.345 |  |  | 10.6667 | 185 | SS Osuga 35/10kv | 2,5+2,5 | 0 | 0.28 | 0 |  | 0.28 | 0 | 2.625 | 2.345 | 2.345 |  |  | 10.6667 | Ржевские Электрические сети
186 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.66 | 0 |  | 1.66 | 0 | 2.625 | 0.965 | 0.965 |  |  | 63.2381 | 186 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.5125 | 3.1725 | 0 |  | 3.1725 | 0 | 2.625 | -0.5475 | -0.5475 | MS is closed | MS is closed | 120.8571 | Ржевские Электрические сети
187 | SS Kleshnevo 35/10kv | 4+4 | 0.8 | 0 |  | 0.8 | 0 | 4.2 | 3.4 | 3.4 |  |  | 19.0476 | 187 | SS Kleshnevo 35/10kv | 4+4 | 1.7625 | 2.5625 | 0 |  | 2.5625 | 0 | 4.2 | 1.6375 | 1.6375 |  |  | 61.0119 | Ржевские Электрические сети
188 | SS Zubtsov 35/10kv | 6,3+6,3 | 9.88 | 1.2333 | 120 | 8.6467 | 0 | 6.615 | -2.0317 | -2.0317 | MS is closed | MS is closed | 149.3575 | 188 | SS Zubtsov 35/10kv | 6,3+6,3 | 5.155 | 15.035 | 1.2333 | 120 | 13.8017 | 0 | 6.615 | -7.1867 | -7.1867 | MS is closed | MS is closed | 227.2865 | Ржевские Электрические сети
189 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 3.98 | 1.5667 | 240 | 2.4133 | 0 | 5.88 | 3.4667 | 3.4667 |  |  | 67.6871 | 189 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 0.0625 | 4.0425 | 1.5667 | 240 | 2.4758 | 0 | 5.88 | 3.4042 | 3.4042 |  |  | 68.75 | Ржевские Электрические сети
190 | SS Stepurino 35/10kv | 4+4 | 1.31 | 0 |  | 1.31 | 0 | 4.2 | 2.89 | 2.89 |  |  | 31.1905 | 190 | SS Stepurino 35/10kv | 4+4 | 0 | 1.31 | 0 |  | 1.31 | 0 | 4.2 | 2.89 | 2.89 |  |  | 31.1905 | Ржевские Электрические сети
191 | SS Maksimovo 35/10kv | 2,5+2,5 | 0.54 | 0.54 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 |  |  | 20.5714 | 191 | SS Maksimovo 35/10kv | 2,5+2,5 | 0 | 0.54 | 0.54 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 |  |  | 20.5714 | Ржевские Электрические сети
192 | SS Lukovnikovo 35/10kv | 4+2,5 | 1.29 | 0 |  | 1.29 | 0 | 2.625 | 1.335 | 1.335 |  |  | 49.1429 | 192 | SS Lukovnikovo 35/10kv | 4+2,5 | 0 | 1.29 | 0 |  | 1.29 | 0 | 2.625 | 1.335 | 1.335 |  |  | 49.1429 | Ржевские Электрические сети
193 | SS NTPF 110/10kv | 6,3+6,3 | 1.09 | 0 |  | 1.09 | 0 | 6.615 | 5.525 | 5.525 |  |  | 16.4777 | 193 | SS NTPF 110/10kv | 6,3+6,3 | 0.75 | 1.84 | 0 |  | 1.84 | 0 | 6.615 | 4.775 | 4.775 |  |  | 27.8156 | Ржевские Электрические сети
194 | SS Mostovaya 110/10kv | 6,3+6,3 | 1.6 | 0.45 | 240 | 1.15 | 0 | 6.615 | 5.465 | 5.465 |  |  | 24.1875 | 194 | SS Mostovaya 110/10kv | 6,3+6,3 | 0.125 | 1.725 | 0.45 | 240 | 1.275 | 0 | 6.615 | 5.34 | 5.34 |  |  | 26.0771 | Ржевские Электрические сети
195 | SS Rzhev 110/35/10kv | 40.5+40 | 47.62 | 4.6882 | 120 | 42.9318 | 0 | 42 | -0.9318 | -0.9318 | MS is closed | MS is closed | 113.381 | 195 | SS Rzhev 110/35/10kv | 40.5+40 | 9.3663 | 56.9862 | 4.6882 | 120 | 52.2981 | 0 | 42 | -10.2981 | -10.2981 | MS is closed | MS is closed | 135.6815 | Ржевские Электрические сети
| Nom. capacity MV, MVA | 40.5+40 | 39.54 | 3.1882 | 120 | 36.3518 | 0 | 42 | 5.6482 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 40.5+40 | 9.1175 | 48.6575 | 3.1882 | 120 | 45.4693 | 0 | 42 | -3.4693 |  |  | MS is closed
| Nom. capacity LV, MVA | 40.5+40 | 8.08 | 1.5 | 120 | 6.58 | 0 | 42 | 35.42 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 40.5+40 | 0.24875 | 8.3287 | 1.5 | 120 | 6.8288 | 0 | 42 | 35.1713 |  |  | MS is closed
196 | SS Chertolino 110/35/10kv | 5,6+6,3 | 1.27 | 0.34667 | 240 | 0.92333 | 0 | 5.88 | 4.9567 | 4.9567 |  |  | 21.5986 | 196 | SS Chertolino 110/35/10kv | 5,6+6,3 | 0.125 | 1.395 | 0.34667 | 240 | 1.0483 | 0 | 5.88 | 4.8317 | 4.8317 |  |  | 23.7245 | Ржевские Электрические сети
| Nom. capacity MV, MVA | 5,6+6,3 | 0.18 | 0.18 | 240 | 0 | 0 | 5.88 | 5.88 |  | 0 |  |  |  | Nom. capacity MV, MVA | 5,6+6,3 | 0 | 0.18 | 0.18 | 240 | 0 | 0 | 5.88 | 5.88 |  | 0
| Nom. capacity LV, MVA | 5,6+6,3 | 1.09 | 0.16667 | 240 | 0.92333 | 0 | 5.88 | 4.9567 |  | 0 |  |  |  | Nom. capacity LV, MVA | 5,6+6,3 | 0.125 | 1.215 | 0.16667 | 240 | 1.0483 | 0 | 5.88 | 4.8317 |  | 0
197 | SS Olenino 110/35/10 | 16+10 | 5.08 | 0.33839 | 120 | 4.7416 | 0 | 10.5 | 5.7584 | 5.7584 |  |  | 48.381 | 197 | SS Olenino 110/35/10 | 16+10 | 0 | 5.08 | 0.33839 | 120 | 4.7416 | 0 | 10.5 | 5.7584 | 5.7584 |  |  | 48.381 | Ржевские Электрические сети
| Nom. capacity MV, MVA | 16+10 | 0.83 | 0.33839 | 120 | 0.49161 | 0 | 10.5 | 10.0084 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0 | 0.83 | 0.33839 | 120 | 0.49161 | 0 | 10.5 | 10.0084 |  | 0
| Nom. capacity LV, MVA | 16+10 | 4.25 |  |  | 4.25 | 0 | 10.5 | 6.25 |  | 0 |  |  | 2: Nom. capacity LV, MVA; 3: 16+10; 4: 0; 5: 4.25; Min. 8: 4.25; Min. 9: 0; Min. 10: 10.5; Min. 11: 6.25; Min. 13: 0
198 | SS Staritsa 110/35/10kv | 16+16 | 13.92 | 5.0738 | 480 | 8.8462 | 0 | 16.8 | 7.9538 | 7.9538 |  |  | 82.8571 | 198 | SS Staritsa 110/35/10kv | 16+16 | 0.55 | 14.47 | 5.0738 | 480 | 9.3962 | 0 | 16.8 | 7.4038 | 7.4038 |  |  | 86.131 | Ржевские Электрические сети
| Nom. capacity MV, MVA | 16+16 | 3.67 | 3.6071 | 480 | 0.0629 | 0 | 16.8 | 16.7371 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.2375 | 3.9075 | 3.6071 | 480 | 0.3004 | 0 | 16.8 | 16.4996 |  | 0
| Nom. capacity LV, MVA | 16+16 | 10.25 | 1.4667 | 240 | 8.7833 | 0 | 16.8 | 8.0167 |  | 0 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.3125 | 10.5625 | 1.4667 | 240 | 9.0958 | 0 | 16.8 | 7.7042 |  | 0
199 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 2.31 |  |  | 2.31 | 0 | 6.615 | 4.305 | 4.305 |  |  | 34.9206 | 199 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 0.2875 | 2.5975 |  |  | 2.5975 | 0 | 6.615 | 4.0175 | 4.0175 |  |  | 39.2668 | Ржевские Электрические сети
| Nom. capacity MV, MVA | 6,3+6,3 | 0 |  |  | 0 | 0 | 6.615 | 6.615 |  | 0 |  |  | 2: Nom. capacity MV, MVA; 3: 6,3+6,3; 4: 0; 5: 0; Min. 8: 0; Min. 9: 0; Min. 10: 6.615; Min. 11: 6.615; Min. 13: 0
| Nom. capacity MV, MVA | 6,3+6,3 | 2.31 |  |  | 2.31 | 0 | 6.615 | 4.305 |  | 0 |  |  | 2: Nom. capacity MV, MVA; 3: 6,3+6,3; 4: 0.2875; 5: 2.5975; Min. 8: 2.5975; Min. 9: 0; Min. 10: 6.615; Min. 11: 4.0175; Min. 13: 0
200 | SS Zolootval 110/10 | 2.5 | 0.27248 | 0.27248 | 24 hours | 0.27248 | 0 | 0.27248 | 0 | 0 |  |  | 10.38 | 200 | SS Zolootval 110/10 | 2.5 | 0.75 | 1.0225 | 0.27248 | 24 hours | 0.27248 | 0 | 0.27248 | -0.75 | -0.75 | MS is closed | MS is closed | 129.8381 | Тверские Электрические сети
201 | SS Krasnogorskaya 35/10 | 1.6 | 1.0691 | 0 |  | 0 | 0 | 0 | -1.0691 | -1.0691 | MS is closed | MS is closed | 63.6393 | 201 | SS Krasnogorskaya 35/10 | 1.6 | 0 | 1.0691 | 0 |  | 0 | 0 | 0 | -1.0691 | -1.0691 | MS is closed | MS is closed | 63.6393 | Тверские Электрические сети
202 | SS Lisitsky Bor 35/10 | 2.5 | 2.1175 | 0 |  | 0 | 0 | 0 | -2.1175 | -2.1175 | MS is closed | MS is closed | 80.6674 | 202 | SS Lisitsky Bor 35/10 | 2.5 | 0.905 | 3.0225 | 0 |  | 0 | 0 | 0 | -3.0225 | -3.0225 | MS is closed | MS is closed | 115.1436 | Тверские Электрические сети
203 | SS No.6 35/10 | 1 | 0.10726 | 0 |  | 0 | 0 | 0 | -0.10726 | -0.10726 | MS is closed | MS is closed | 10.2152 | 204 | SS No.6 35/10 | 1 | 0 | 0.10726 | 0 |  | 0 | 0 | 0 | -0.10726 | -0.10726 | MS is closed | MS is closed | 10.2152 | Тверские Электрические сети
204 | SS No.1 35/6 | 1 | 0.9342 | 0 |  | 0 | 0 | 0 | -0.9342 | -0.9342 | MS is closed | MS is closed | 88.9714 | 205 | SS No.1 35/6 | 1 | 0 | 0.9342 | 0 |  | 0 | 0 | 0 | -0.9342 | -0.9342 | MS is closed | MS is closed | 88.9714 | Тверские Электрические сети
205 | SS No.1 35/10 | 2.5 | 1.903 | 0 |  | 0 | 0 | 0 | -1.903 | -1.903 | MS is closed | MS is closed | 72.4952 |  | SS No.1 35/10 | 2.5 | 0.4375 | 2.3405 | 0 |  | 0 | 0 | 0 | -2.3405 | -2.3405 | MS is closed | MS is closed | 89.1619 | Тверские Электрические сети
206 | SS No.16 35/6 | 1 | 0.26815 | 0 |  | 0 | 0 | 0 | -0.26815 | -0.26815 | MS is closed | MS is closed | 25.5381 | 206 | SS No.16 35/6 | 1 | 0 | 0.26815 | 0 |  | 0 | 0 | 0 | -0.26815 | -0.26815 | MS is closed | MS is closed | 25.5381 | Тверские Электрические сети
207 | SS No.16 35/10 | 2.5 | 2.0362 | 0 |  | 0 | 0 | 0 | -2.0362 | -2.0362 | MS is closed | MS is closed | 77.5699 |  | SS No.16 35/10 | 2.5 | 0 | 2.0362 | 0 |  | 0 | 0 | 0 | -2.0362 | -2.0362 | MS is closed | MS is closed | 77.5699 | Тверские Электрические сети
208 | SS Zolotikha 35/10 | 2.5 | 0.87815 | 0.87815 | 24 hours | 0.87815 | 0 | 0.87815 | 0 | 0 |  |  | 33.4533 | 207 | SS Zolotikha 35/10 | 2.5 | 0 | 0.87815 | 0.87815 | 24 hours | 0.87815 | 0 | 0.87815 | 0 | 0 |  |  | 33.4533 | Тверские Электрические сети
209 | SS Novy Stan 35/10 | 2.5 | 0.355 | 0.355 | 24 hours | 0.355 | 0 | 0.355 | 0 | 0 |  |  | 13.5237 | 208 | SS Novy Stan 35/10 | 2.5 | 0 | 0.355 | 0.355 | 24 hours | 0.355 | 0 | 0.355 | 0 | 0 |  |  | 13.5237 | Тверские Электрические сети
210 | SS Romanovo 35/10 | 2.5 | 0.7484 | 0.7484 | 24 hours | 0.7484 | 0 | 0.7484 | 0 | 0 |  |  | 28.5104 | 209 | SS Romanovo 35/10 | 2.5 | 0 | 0.7484 | 0.7484 | 24 hours | 0.7484 | 0 | 0.7484 | 0 | 0 |  |  | 28.5104 | Тверские Электрические сети
211 | SS Pervitino 35/10 | 1.6 | 0.39236 | 0 |  | 0 | 0 | 0 | -0.39236 | -0.39236 | MS is closed | MS is closed | 23.355 | 210 | SS Pervitino 35/10 | 1.6 | 0 | 0.39236 | 0 |  | 0 | 0 | 0 | -0.39236 | -0.39236 | MS is closed | MS is closed | 23.355 | Тверские Электрические сети
212 | SS No. 8 35/10 | 2.5 | 2.0443 | 0 |  | 0 | 0 | 0 | -2.0443 | -2.0443 | MS is closed | MS is closed | 77.8797 | 211 | SS No. 8 35/10 | 2.5 | 0 | 2.0443 | 0 |  | 0 | 0 | 0 | -2.0443 | -2.0443 | MS is closed | MS is closed | 77.8797 | Тверские Электрические сети
213 | SS Aleksino 35/6 | 2.5 | 1.3494 | 0 |  | 0 | 0 | 0 | -1.3494 | -1.3494 | MS is closed | MS is closed | 51.4057 | 212 | SS Aleksino 35/6 | 2.5 | 1.455 | 2.8044 | 0 |  | 0 | 0 | 0 | -2.8044 | -2.8044 | MS is closed | MS is closed | 106.8343 | Тверские Электрические сети
214 | SS Bezborodovo 35/10 | 2.5 | 2.2706 | 0 |  | 0 | 0 | 0 | -2.2706 | -2.2706 | MS is closed | MS is closed | 86.5 | 213 | SS Bezborodovo 35/10 | 2.5 | 0 | 2.2706 | 0 |  | 0 | 0 | 0 | -2.2706 | -2.2706 | MS is closed | MS is closed | 86.5 | Тверские Электрические сети
215 | SS Medvedikha 110/10 | 2.5 | 0.58682 | 0.58682 | 24 hours | 0.58682 | 0 | 0.58682 | 0 | 0 |  |  | 22.3549 | 214 | SS Medvedikha 110/10 | 2.5 | 0 | 0.58682 | 0.58682 | 24 hours | 0.58682 | 0 | 0.58682 | 0 | 0 |  |  | 22.3549 | Тверские Электрические сети
216 | SS Kivirichi 35/10 | 2.5 | 0.27248 | 0 |  | 0 | 0 | 0 | -0.27248 | -0.27248 | MS is closed | MS is closed | 10.38 | 215 | SS Kivirichi 35/10 | 2.5 | 0 | 0.27248 | 0 |  | 0 | 0 | 0 | -0.27248 | -0.27248 | MS is closed | MS is closed | 10.38 | Тверские Электрические сети
217 | SS Dievo 35/10 | 2.5 | 0.29064 | 0.29064 | 24 hours | 0.29064 | 0 | 0.29064 | 0 | 0 |  |  | 11.072 | 216 | SS Dievo 35/10 | 2.5 | 0 | 0.29064 | 0.29064 | 24 hours | 0.29064 | 0 | 0.29064 | 0 | 0 |  |  | 11.072 | Тверские Электрические сети
218 | SS No.17 35/10 | 4+4 | 1.0432 | 0 |  | 1.0432 | 0 | 2.62 | 1.5768 | 1.5768 |  |  | 39.8164 | 217 | SS No.17 35/10 | 4+4 | 0 | 1.0432 | 0 |  | 1.0432 | 0 | 2.62 | 1.5768 | 1.5768 |  |  | 39.8164 | Тверские Электрические сети
219 | SS Danilovskoe 35/6 | 2,5+6,3 | 1.0354 | 0 |  | 1.0354 | 0 | 2.63 | 1.5946 | 1.5946 |  |  | 39.369 | 203 | SS Danilovskoe 35/6 | 2,5+6,3 | 0 | 0.24375 | 0 |  | 0.24375 | 0 | 2.63 | 2.3862 | 2.3862 |  |  | 9.2681 | Тверские Электрические сети
220 | SS Kushalino 35/10 | 2,5+2,5 | 2.241 | 0 |  | 2.241 | 0 | 2.62 | 0.37896 | 0.37896 |  |  | 85.536 | 218 | SS Kushalino 35/10 | 2,5+2,5 | 0.04375 | 2.2848 | 0 |  | 2.2848 | 0 | 2.62 | 0.33521 | 0.33521 |  |  | 87.2058 | Тверские Электрические сети
221 | SS No.4 35/6 | 5,6+5,6 | 2.0085 | 0 |  | 2.0085 | 0 | 5.88 | 3.8715 | 3.8715 |  |  | 34.1587 | 219 | SS No.4 35/6 | 5,6+5,6 | 0.25 | 2.2585 | 0 |  | 2.2585 | 0 | 5.88 | 3.6215 | 3.6215 |  |  | 38.4104 | Тверские Электрические сети
222 | SS No.13 35/10/6 | 3,2+3,2 | 1.515 | 0 |  | 1.515 | 0 | 3.36 | 1.845 | 1.845 |  |  | 45.0881 | 220 | SS No.13 35/10/6 | 3,2+3,2 | 0.075 | 1.59 | 0 |  | 1.59 | 0 | 3.36 | 1.77 | 1.77 |  |  | 47.3203 | Тверские Электрические сети
223 | SS No.27 35/6 | 10+10 | 14.2569 | 0 |  | 14.2569 | 0 | 10.5 | -3.7569 | -3.7569 | MS is closed | MS is closed | 135.7803 | 221 | SS No.27 35/6 | 10+10 | 0 | 14.2569 | 0 |  | 14.2569 | 0 | 10.5 | -3.7569 | -3.7569 | MS is closed | MS is closed | 135.7803 | Тверские Электрические сети
224 | SS Vagzhanovskaya 35/6 | 16+16 | 20.515 | 0 |  | 20.515 | 0 | 16.8 | -3.715 | -3.715 | MS is closed | MS is closed | 122.1133 | 222 | SS Vagzhanovskaya 35/6 | 16+16 | 0.125 | 20.64 | 0 |  | 20.64 | 0 | 16.8 | -3.84 | -3.84 | MS is closed | MS is closed | 122.8573 | Тверские Электрические сети
225 | SS Plant 1Maya 35/6 | 10+10 | 5.5585 | 0 |  | 5.5585 | 0 | 10.5 | 4.9415 | 4.9415 |  |  | 52.938 | 223 | SS Plant 1Maya 35/6 | 10+10 | 2.5838 | 8.1422 | 0 |  | 8.1422 | 0 | 10.5 | 2.3578 | 2.3578 |  |  | 77.5451 | Тверские Электрические сети
226 | SS Steklovolokno 35/6 | 10+10 | 4.344 | 0 |  | 4.344 | 0 | 10.5 | 6.156 | 6.156 |  |  | 41.3717 | 224 | SS Steklovolokno 35/6 | 10+10 | 1.5913 | 5.9353 | 0 |  | 5.9353 | 0 | 10.5 | 4.5647 | 4.5647 |  |  | 56.5265 | Тверские Электрические сети
227 | SS Sominka 35/10 | 16+16 | 16.199 | 0 |  | 16.199 | 0 | 16.8 | 0.60097 | 0.60097 |  |  | 96.4228 | 225 | SS Sominka 35/10 | 16+16 | 0.23125 | 16.4303 | 0 |  | 16.4303 | 0 | 16.8 | 0.36972 | 0.36972 |  |  | 97.7993 | Тверские Электрические сети
228 | SS Zavolzhskaya 35/6 | 7,5+10 | 6.5034 | 0 |  | 6.5034 | 0 | 7.88 | 1.3766 | 1.3766 |  |  | 82.5307 | 226 | SS Zavolzhskaya 35/6 | 7,5+10 | 0 | 6.5034 | 0 |  | 6.5034 | 0 | 7.88 | 1.3766 | 1.3766 |  |  | 82.5307 | Тверские Электрические сети
229 | SS Kaposhvar 35/10 | 10+10 | 9.6642 | 0 |  | 9.6642 | 0 | 10.5 | 0.83579 | 0.83579 |  |  | 92.0401 | 227 | SS Kaposhvar 35/10 | 10+10 | 0.82088 | 10.4851 | 0 |  | 10.4851 | 0 | 10.5 | 0.014913 | 0.014913 |  |  | 99.858 | Тверские Электрические сети
230 | SS Mamulino 110/10 | 6,3+6,3 | 3.7729 | 0 |  | 3.7729 | 0 | 6.62 | 2.8471 | 2.8471 |  |  | 56.992 | 228 | SS Mamulino 110/10 | 6,3+6,3 | 4.8063 | 8.5791 | 0 |  | 8.5791 | 0 | 6.62 | -1.9591 | -1.9591 | MS is closed | MS is closed | 129.594 | Тверские Электрические сети
231 | SS Glazkovo 110/10 | 6,3+6,3 | 6.8936 | 0 |  | 6.8936 | 0 | 6.62 | -0.27362 | -0.27362 | MS is closed | MS is closed | 104.1332 | 229 | SS Glazkovo 110/10 | 6,3+6,3 | 0.61775 | 7.5114 | 0 |  | 7.5114 | 0 | 6.62 | -0.89137 | -0.89137 | MS is closed | MS is closed | 113.4648 | Тверские Электрические сети
232 | SS Proletarskaya 110/10 | 16+16 | 9.9754 | 0 |  | 9.9754 | 0 | 16.8 | 6.8246 | 6.8246 |  |  | 59.3771 | 230 | SS Proletarskaya 110/10 | 16+16 | 0 | 9.9754 | 0 |  | 9.9754 | 0 | 16.8 | 6.8246 | 6.8246 |  |  | 59.3771 | Тверские Электрические сети
233 | SS Turginovo 35/10 | 6,3+6,3 | 5.0922 | 0 |  | 5.0922 | 0 | 6.62 | 1.5278 | 1.5278 |  |  | 76.921 | 231 | SS Turginovo 35/10 | 6,3+6,3 | 0 | 5.0922 | 0 |  | 5.0922 | 0 | 6.62 | 1.5278 | 1.5278 |  |  | 76.921 | Тверские Электрические сети
234 | SS Sakharovo 35/10 | 2,5+2,5 | 2.6164 | 0 |  | 2.6164 | 0 | 2.62 | 0.0036345 | 0.0036345 |  |  | 99.8613 | 232 | SS Sakharovo 35/10 | 2,5+2,5 | 0.3175 | 2.9339 | 0 |  | 2.9339 | 0 | 2.62 | -0.31387 | -0.31387 | MS is closed | MS is closed | 111.9796 | Тверские Электрические сети
235 | SS Golovino 35/10 | 2,5+2,5 | 1.2774 | 0 |  | 1.2774 | 0 | 2.62 | 1.3426 | 1.3426 |  |  | 48.7569 | 233 | SS Golovino 35/10 | 2,5+2,5 | 0.3625 | 1.6399 | 0 |  | 1.6399 | 0 | 2.62 | 0.98007 | 0.98007 |  |  | 62.5928 | Тверские Электрические сети
236 | SS Kalikino 35/10 | 2+3,2 | 1.7715 | 0 |  | 1.7715 | 0 | 2.1 | 0.32848 | 0.32848 |  |  | 84.3581 | 234 | SS Kalikino 35/10 | 2+3,2 | 0.0575 | 1.829 | 0 |  | 1.829 | 0 | 2.1 | 0.27098 | 0.27098 |  |  | 87.0962 | Тверские Электрические сети
237 | SS Kvakshino 35/10 | 4+4 | 1.0221 | 0 |  | 1.0221 | 0 | 4.2 | 3.1779 | 3.1779 |  |  | 24.3353 | 235 | SS Kvakshino 35/10 | 4+4 | 0 | 1.0221 | 0 |  | 1.0221 | 0 | 4.2 | 3.1779 | 3.1779 |  |  | 24.3353 | Тверские Электрические сети
238 | SS Gorodnya 35/10 | 4+6,3 | 2.9259 | 0 |  | 2.9259 | 0 | 4.2 | 1.2741 | 1.2741 |  |  | 69.6634 | 236 | SS Gorodnya 35/10 | 4+6,3 | 0.075 | 3.0009 | 0 |  | 3.0009 | 0 | 4.2 | 1.1991 | 1.1991 |  |  | 71.4491 | Тверские Электрические сети
239 | SS Ryazanovo 35/10 | 4+4 | 2.5838 | 0 |  | 2.5838 | 0 | 4.2 | 1.6162 | 1.6162 |  |  | 61.518 | 237 | SS Ryazanovo 35/10 | 4+4 | 0 | 2.5838 | 0 |  | 2.5838 | 0 | 4.2 | 1.6162 | 1.6162 |  |  | 61.518 | Тверские Электрические сети
240 | SS Savvatyevo 35/10 | 1,6+2,5 | 0.67816 | 0 |  | 0.67816 | 0 | 1.68 | 1.0018 | 1.0018 |  |  | 40.3667 | 238 | SS Savvatyevo 35/10 | 1,6+2,5 | 0 | 0.67816 | 0 |  | 0.67816 | 0 | 1.68 | 1.0018 | 1.0018 |  |  | 40.3667 | Тверские Электрические сети
241 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0.75134 | 0 |  | 0.75134 | 0 | 1.68 | 0.92866 | 0.92866 |  |  | 44.7226 | 239 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0 | 0.75134 | 0 |  | 0.75134 | 0 | 1.68 | 0.92866 | 0.92866 |  |  | 44.7226 | Тверские Электрические сети
242 | SS Glass plant 35/10 | 2,5+2,5 | 0.70584 | 0 |  | 0.70584 | 0 | 2.63 | 1.9242 | 1.9242 |  |  | 26.838 | 240 | SS Glass plant 35/10 | 2,5+2,5 | 0 | 0.70584 | 0 |  | 0.70584 | 0 | 2.63 | 1.9242 | 1.9242 |  |  | 26.838 | Тверские Электрические сети
243 | SS Grishkino 35/10 | 4+4 | 5.1926 | 0 |  | 5.1926 | 0 | 4.2 | -0.99259 | -0.99259 | MS is closed | MS is closed | 123.6332 | 241 | SS Grishkino 35/10 | 4+4 | 7.3662 | 12.5588 | 0 |  | 12.5588 | 0 | 4.2 | -8.3588 | -8.3588 | MS is closed | MS is closed | 299.0201 | Тверские Электрические сети
244 | SS No.2 35/3 | 1+1 | 0.83282 | 0 |  | 0.83282 | 0 | 1.05 | 0.21718 | 0.21718 |  |  | 79.3164 | 242 | SS No.2 35/3 | 1+1 | 0 | 0.83282 | 0 |  | 0.83282 | 0 | 1.05 | 0.21718 | 0.21718 |  |  | 79.3164 | Тверские Электрические сети
245 | SS No.15 35/10 | 4+4 | 3.4916 | 0 |  | 3.4916 | 0 | 4.2 | 0.70843 | 0.70843 |  |  | 83.1327 | 243 | SS No.15 35/10 | 4+4 | 0 | 3.4916 | 0 |  | 3.4916 | 0 | 4.2 | 0.70843 | 0.70843 |  |  | 83.1327 | Тверские Электрические сети
246 | SS Mednoe 35/10 | 6,3+4 | 3.8125 | 0 |  | 3.8125 | 0 | 4.2 | 0.38751 | 0.38751 |  |  | 90.7735 | 244 | SS Mednoe 35/10 | 6,3+4 | 0.5375 | 4.35 | 0 |  | 4.35 | 0 | 4.2 | -0.14999 | -0.14999 | MS is closed | MS is closed | 103.5711 | Тверские Электрические сети
247 | SS Tolmachi 35/10 | 2,5+1,8 | 1.1357 | 0 |  | 1.1357 | 0 | 1.89 | 0.75426 | 0.75426 |  |  | 60.0923 | 245 | SS Tolmachi 35/10 | 2,5+1,8 | 0 | 1.1357 | 0 |  | 1.1357 | 0 | 1.89 | 0.75426 | 0.75426 |  |  | 60.0923 | Тверские Электрические сети
248 | SS No. 7 35/10 | 1,8+2,5 | 0.528 | 0 |  | 0.528 | 0 | 1.89 | 1.362 | 1.362 |  |  | 27.9363 | 246 | SS No. 7 35/10 | 1,8+2,5 | 0 | 0.528 | 0 |  | 0.528 | 0 | 1.89 | 1.362 | 1.362 |  |  | 27.9363 | Тверские Электрические сети
249 | SS No. 5 35/6 | 5,6+4 | 2.0051 | 0 |  | 2.0051 | 0 | 4.2 | 2.1949 | 2.1949 |  |  | 47.7398 | 247 | SS No. 5 35/6 | 5,6+4 | 0.15 | 2.1551 | 0 |  | 2.1551 | 0 | 4.2 | 2.0449 | 2.0449 |  |  | 51.3112 | Тверские Электрические сети
250 | SS No. 9 35/6 | 5,6+6,3 | 5.7329 | 0 |  | 5.7329 | 0 | 5.88 | 0.14713 | 0.14713 |  |  | 97.4979 | 248 | SS No. 9 35/6 | 5,6+6,3 | 0.2875 | 6.0204 | 0 |  | 6.0204 | 0 | 5.88 | -0.14037 | -0.14037 | MS is closed | MS is closed | 102.3873 | Тверские Электрические сети
251 | SS No. 9 35/10 | 4+6,3 | 3.4168 | 0 |  | 3.4168 | 0 | 4.2 | 0.78316 | 0.78316 |  |  | 81.3533 | 249 | SS No. 9 35/10 | 4+6,3 | 0 | 3.4168 | 0 |  | 3.4168 | 0 | 4.2 | 0.78316 | 0.78316 |  |  | 81.3533 | Тверские Электрические сети
252 | SS No. 10 35/6 | 1,8+1,8 | 1.9073 | 0 |  | 1.9073 | 0 | 1.89 | -0.017325 | -0.017325 | MS is closed | MS is closed | 100.9167 | 250 | SS No. 10 35/6 | 1,8+1,8 | 0.2875 | 2.1948 | 0 |  | 2.1948 | 0 | 1.89 | -0.30483 | -0.30483 | MS is closed | MS is closed | 116.1283 | Тверские Электрические сети
253 | SS No. 11 35/10 kv | 10+6,3 | 5.4961 | 0 |  | 5.4961 | 0 | 6.62 | 1.1239 | 1.1239 |  |  | 83.023 | 251 | SS No. 11 35/10 kv | 10+6,3 | 0.14375 | 5.6399 | 0 |  | 5.6399 | 0 | 6.62 | 0.98013 | 0.98013 |  |  | 85.1945 | Тверские Электрические сети
254 | SS Dm.Gora 35/10 | 2,5+4 | 6.0585 | 0 |  | 6.0585 | 0 | 2.63 | -3.4285 | -3.4285 | MS is closed | MS is closed | 230.3597 | 252 | SS Dm.Gora 35/10 | 2,5+4 | 0 | 6.0585 | 0 |  | 6.0585 | 0 | 2.63 | -3.4285 | -3.4285 | MS is closed | MS is closed | 230.3597 | Тверские Электрические сети
255 | SS ZMI 35/6 | 10+16 | 3.3787 | 0 |  | 3.3787 | 0 | 10.5 | 7.1213 | 7.1213 |  |  | 32.178 | 253 | SS ZMI 35/6 | 10+16 | 0.09625 | 3.4749 | 0 |  | 3.4749 | 0 | 10.5 | 7.0251 | 7.0251 |  |  | 33.0947 | Тверские Электрические сети
256 | SS Izoplit 35/10 | 6,3+6,3 | 1.1807 | 0 |  | 1.1807 | 0 | 6.62 | 5.4393 | 5.4393 |  |  | 17.8357 | 254 | SS Izoplit 35/10 | 6,3+6,3 | 0 | 1.1807 | 0 |  | 1.1807 | 0 | 6.62 | 5.4393 | 5.4393 |  |  | 17.8357 | Тверские Электрические сети
257 | SS Karacharovo 35/10 | 4+6,3 | 1.9722 | 0 |  | 1.9722 | 0 | 4.2 | 2.2278 | 2.2278 |  |  | 46.9571 | 255 | SS Karacharovo 35/10 | 4+6,3 | 100 | 101.9722 | 0 |  | 101.9722 | 0 | 4.2 | -97.7722 | -97.7722 | MS is closed | MS is closed | 2427.9095 | Тверские Электрические сети
258 | SS Kr. Luch 35/6 | 2,5+3,2 | 2.9012 | 0 |  | 2.9012 | 0 | 2.63 | -0.27121 | -0.27121 | MS is closed | MS is closed | 110.3122 | 256 | SS Kr. Luch 35/6 | 2,5+3,2 | 0.36875 | 3.27 | 0 |  | 3.27 | 0 | 2.63 | -0.63996 | -0.63996 | MS is closed | MS is closed | 124.3331 | Тверские Электрические сети
259 | SS Melkovo 35/6 | 1,6+2,5 | 1.2498 | 0 |  | 1.2498 | 0 | 1.68 | 0.43025 | 0.43025 |  |  | 74.39 | 257 | SS Melkovo 35/6 | 1,6+2,5 | 0 | 1.2498 | 0 |  | 1.2498 | 0 | 1.68 | 0.43025 | 0.43025 |  |  | 74.39 | Тверские Электрические сети
260 | SS Selikhovo 35/6 | 2,5+2,5 | 0.9169 | 0 |  | 0.9169 | 0 | 2.63 | 1.7131 | 1.7131 |  |  | 34.8631 | 258 | SS Selikhovo 35/6 | 2,5+2,5 | 0 | 0.9169 | 0 |  | 0.9169 | 0 | 2.63 | 1.7131 | 1.7131 |  |  | 34.8631 | Тверские Электрические сети
261 | SS Mokshino 35/10 | 6,3+6,3 | 3.3908 | 0 |  | 3.3908 | 0 | 6.62 | 3.2292 | 3.2292 |  |  | 51.2205 | 259 | SS Mokshino 35/10 | 6,3+6,3 | 0.9375 | 4.3283 | 0 |  | 4.3283 | 0 | 6.62 | 2.2917 | 2.2917 |  |  | 65.3822 | Тверские Электрические сети
262 | SS Energetik 35/10 | 4+2,5 | 1.6271 | 0 |  | 1.6271 | 0 | 2.63 | 1.0029 | 1.0029 |  |  | 61.8656 | 260 | SS Energetik 35/10 | 4+2,5 | 0 | 1.6271 | 0 |  | 1.6271 | 0 | 2.63 | 1.0029 | 1.0029 |  |  | 61.8656 | Тверские Электрические сети
263 | SS Emmaus 35/10 | 2,5+4 | 2.7092 | 0 |  | 2.7092 | 0 | 2.63 | -0.07918 | -0.07918 | MS is closed | MS is closed | 103.0106 | 261 | SS Emmaus 35/10 | 2,5+4 | 0.0675 | 2.7767 | 0 |  | 2.7767 | 0 | 2.63 | -0.14668 | -0.14668 | MS is closed | MS is closed | 105.5772 | Тверские Электрические сети
264 | SS Yu.-Devichye 35/10 | 4+4 | 3.2179 | 1.6089 | 120 min | 1.6089 | 0 | 4.2 | 2.5911 | 2.5911 |  |  | 76.6159 | 262 | SS Yu.-Devichye 35/10 | 4+4 | 0.7975 | 4.0154 | 1.6089 | 120 min | 2.4064 | 0 | 4.2 | 1.7936 | 1.7936 |  |  | 95.604 | Тверские Электрические сети
265 | SS No.18 35/6 | 10+10+10 | 15.8529 | 0 |  | 15.8529 | 10.5 | 21 | -5.3529 | -5.3529 | MS is closed | MS is closed | 75.4898 | 263 | SS No.18 35/6 | 10+10+10 | 0.06875 | 15.9216 | 0 |  | 15.9216 | 0 | 21 | 5.0784 | 5.0784 |  |  | 75.8172 | Тверские Электрические сети
266 | SS Zatveretskaya 35/6 | 10+10+10 | 14.2392 | 0 |  | 14.2392 | 0 | 21 | 6.7608 | 6.7608 |  |  | 67.8059 | 264 | SS Zatveretskaya 35/6 | 10+10+10 | 0.9625 | 15.2017 | 0 |  | 15.2017 | 0 | 21 | 5.7983 | 5.7983 |  |  | 72.3893 | Тверские Электрические сети
267 | SS Pushkino 110/35/10 | 10 | 6.7778 | 6.7778 | 24 hours | 6.7778 | 0 | 6.7778 | 0 | -0.00473 | MS is closed | MS is closed | 64.5504 | 265 | SS Pushkino 110/35/10 | 10 | 0 | 6.7778 | 6.7778 | 24 hours | 6.7778 | 0 | 6.7778 | 0 | -0.00473 | MS is closed | MS is closed | 64.5504 | Тверские Электрические сети
| Nom. capacity MV, MVA | 8.83 | 6.6031 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0 |  |  | MS is closed |  |  | Nom. capacity MV, MVA | 8.83 | 0 | 6.6031 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0 |  |  | MS is closed
| Nom. capacity LV, MVA | 8.75 | 0.17473 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | -0.00473 |  |  | MS is closed |  |  | Nom. capacity LV, MVA | 8.75 | 0 | 0.17473 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | -0.00473 |  |  | MS is closed
268 | SS Mechanical plant 110/10/6 | 40+40 | 21.9762 | 0 |  | 21.9762 | 0 | 42 | 20.0238 | 9.1668 |  |  | 52.3243 | 266 | SS Mechanical plant 110/10/6 | 40+40 | 0 | 21.9762 | 0 |  | 21.9762 | 0 | 42 | 20.0238 | 9.1668 |  |  | 52.3243 | Тверские Электрические сети
| Nom. capacity MV, MVA | 20+20 | 10.143 | 0 |  | 10.143 | 0 | 21 | 10.857 |  | 0 |  |  |  | Nom. capacity MV, MVA | 20+20 | 0 | 10.143 | 0 |  | 10.143 | 0 | 21 | 10.857 |  | 0
| Nom. capacity LV, MVA | 20+20 | 11.8332 | 0 |  | 11.8332 | 0 | 21 | 9.1668 |  | 0 |  |  |  | Nom. capacity LV, MVA | 20+20 | 0 | 11.8332 | 0 |  | 11.8332 | 0 | 21 | 9.1668 |  | 0
269 | SS Yuzhnaya 110/35/10 | 40+40 | 56.4951 | 25.68 | 120 | 30.8151 | 0 | 42 | 11.1849 | 11.1849 |  |  | 134.5122 | 267 | SS Yuzhnaya 110/35/10 | 40+40 | 1.0702 | 57.5654 | 25.68 | 120 | 31.8854 | 0 | 42 | 10.1146 | 10.1146 |  |  | 137.0604 | Тверские Электрические сети
| Nom. capacity MV, MVA | 40+40 | 29.7599 | 25.48 | 120 | 4.2799 | 0 | 42 | 37.7201 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0 | 29.7599 | 25.48 | 120 | 4.2799 | 0 | 42 | 37.7201 |  | 0
| Nom. capacity LV, MVA | 40+40 | 26.7352 | 0.2 | 120 | 26.5352 | 0 | 42 | 15.4648 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40+40 | 1.0702 | 27.8055 | 0.2 | 120 | 27.6055 | 0 | 42 | 14.3945 |  | 0
270 | SS Severnaya 110/35/10 | 40+40 | 33.5162 | 17.9986 | 120 | 15.5176 | 0 | 42 | 26.4824 | 26.4824 |  |  | 79.8005 | 268 | SS Severnaya 110/35/10 | 40+40 | 9.92 | 43.4362 | 17.9986 | 120 | 25.4376 | 0 | 42 | 16.5624 | 16.5624 |  |  | 103.4196 | Тверские Электрические сети
| Nom. capacity MV, MVA | 40+40 | 17.9986 | 17.9986 | 120 | 0 | 0 | 42 | 42 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40+40 | 1.8225 | 19.8211 | 17.9986 | 120 | 1.8225 | 0 | 42 | 40.1775 |  | 0
| Nom. capacity LV, MVA | 40+40 | 15.5176 | 0 |  | 15.5176 | 0 | 42 | 26.4824 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40+40 | 8.0975 | 23.6151 | 0 |  | 23.6151 | 0 | 42 | 18.3849 |  | 0
271 | SS Lazurnaya 110/35/10 | 40+40 | 29.4156 | 5.64 | 120 | 23.7756 | 0 | 42 | 18.2244 | 18.2244 |  |  | 70.0371 | 269 | SS Lazurnaya 110/35/10 | 40+40 | 11.9712 | 41.3868 | 5.64 | 120 | 35.7468 | 0 | 42 | 6.2532 | 6.2532 |  |  | 98.5401 | Тверские Электрические сети
| Nom. capacity MV, MVA | 40+40 | 17.6613 | 5.64 | 120 | 12.0213 | 0 | 42 | 29.9787 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40+40 | 7.7588 | 25.42 | 5.64 | 120 | 19.78 | 0 | 42 | 22.22 |  | 0
| Nom. capacity LV, MVA | 40+40 | 11.7543 | 0 |  | 11.7543 | 0 | 42 | 30.2457 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40+40 | 4.2125 | 15.9668 | 0 |  | 15.9668 | 0 | 42 | 26.0332 |  | 0
272 | SS Earthmoving machine plant 110/10/6 | 40+40 | 20.404 | 0 |  | 20.404 | 0 | 42 | 21.596 | 5.0646 |  |  | 48.5809 | 270 | SS Earthmoving machine plant 110/10/6 | 40+40 | 3.4919 | 23.8958 | 0 |  | 23.8958 | 0 | 42 | 18.1042 | 4.534 |  |  | 56.8949 | Тверские Электрические сети
| Nom. capacity MV, MVA | 20+20 | 15.9354 | 0 |  | 15.9354 | 0 | 21 | 5.0646 |  | 0 |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.53063 | 16.466 | 0 |  | 16.466 | 0 | 21 | 4.534 |  | 0
| Nom. capacity LV, MVA | 20+20 | 4.4686 | 0 |  | 4.4686 | 0 | 21 | 16.5314 |  | 0 |  |  |  | Nom. capacity LV, MVA | 20+20 | 2.9613 | 7.4298 | 0 |  | 7.4298 | 0 | 21 | 13.5702 |  | 0
273 | SS Mednovsky v-or 110/35/10 | 10+10 | 5.5264 | 5.5264 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 |  |  | 52.6322 | 271 | SS Mednovsky v-or 110/35/10 | 10+10 | 0.67 | 6.1964 | 5.5264 | 120 | 0.67 | 0 | 10.5 | 9.83 | 9.83 |  |  | 59.0132 | Тверские Электрические сети
| Nom. capacity MV, MVA | 10+10 | 3.4772 | 3.4772 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.67 | 4.1472 | 3.4772 | 120 | 0.67 | 0 | 10.5 | 9.83 |  | 0
| Nom. capacity LV, MVA | 10+10 | 2.0492 | 2.0492 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.0492 | 2.0492 | 120 | 0 | 0 | 10.5 | 10.5 |  | 0
274 | SS Likhoslavl 110/35/10 | 25+25 | 21.2816 | 3.9 | 120 | 17.3816 | 0 | 26.25 | 8.8684 | 8.8684 |  |  | 81.0727 | 272 | SS Likhoslavl 110/35/10 | 25+25 | 0.28875 | 21.5703 | 3.9 | 120 | 17.6703 | 0 | 26.25 | 8.5797 | 8.5797 |  |  | 82.1727 | Тверские Электрические сети
| Nom. capacity MV, MVA | 25+25 | 7.958 | 3.9 | 120 | 4.058 | 0 | 26.25 | 22.192 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+25 | 0 | 7.958 | 3.9 | 120 | 4.058 | 0 | 26.25 | 22.192 |  | 0
| Nom. capacity LV, MVA | 25+25 | 13.3236 | 0 |  | 13.3236 | 0 | 26.25 | 12.9264 |  | 0 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.28875 | 13.6123 | 0 |  | 13.6123 | 0 | 26.25 | 12.6377 |  | 0
275 | SS Bezborodovo 110/35/6 | 16+16 | 17.5162 | 2.5 | 120 | 15.0162 | 0 | 16.8 | 1.7837 | 1.7837 |  |  | 104.2634 | 273 | SS Bezborodovo 110/35/6 | 16+16 | 1.0813 | 18.5975 | 2.5 | 120 | 16.0975 | 0 | 16.8 | 0.7025 | 0.7025 |  |  | 110.6994 | Тверские Электрические сети
| Nom. capacity MV, MVA | 16+16 | 17.5162 | 2.5 | 120 | 15.0162 | 0 | 16.8 | 1.7837 |  | 0 |  |  |  | Nom. capacity MV, MVA | 16+16 | 1.0813 | 18.5975 | 2.5 | 120 | 16.0975 | 0 | 16.8 | 0.7025 |  | 0
| Nom. capacity LV, MVA | 16+16 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8 |  | 0 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8 |  | 0
276 | SS Redkino 110/35/6 | 40+40,5 | 34.8971 | 7.76 | 120 | 27.1371 | 0 | 42 | 14.8629 | 14.8629 |  |  | 83.0884 | 274 | SS Redkino 110/35/6 | 40+40,5 | 4.4238 | 39.3209 | 7.76 | 120 | 31.5609 | 0 | 42 | 10.4391 | 10.4391 |  |  | 93.6211 | Тверские Электрические сети
| Nom. capacity MV, MVA | 40+40 | 27.8219 | 7.76 | 120 | 20.0619 | 0 | 42 | 21.9381 |  | 0 |  |  |  | Nom. capacity MV, MVA | 40+40 | 2.5488 | 30.3706 | 7.76 | 120 | 22.6106 | 0 | 42 | 19.3894 |  | 0
| Nom. capacity LV, MVA | 40+40 | 7.0753 | 0 |  | 7.0753 | 0 | 42 | 34.9247 |  | 0 |  |  |  | Nom. capacity LV, MVA | 40+40 | 1.875 | 8.9503 | 0 |  | 8.9503 | 0 | 42 | 33.0497 |  | 0
277 | SS Rameshki 110/35/10 | 25+10 | 6.2334 | 3.65 | 120 | 2.5834 | 0 | 10.5 | 7.9166 | 7.9166 |  |  | 59.3654 | 275 | SS Rameshki 110/35/10 | 25+10 | 0.03125 | 6.2646 | 3.65 | 120 | 2.6146 | 0 | 10.5 | 7.8854 | 7.8854 |  |  | 59.663 | Тверские Электрические сети
| Nom. capacity MV, MVA | 25+10 | 3.006 | 2.25 | 120 | 0.75605 | 0 | 10.5 | 9.744 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+10 | 0 | 3.006 | 2.25 | 120 | 0.75605 | 0 | 10.5 | 9.744 |  | 0
| Nom. capacity MV, MVA | 25+10 | 3.2273 | 1.4 | 120 | 1.8273 | 0 | 10.5 | 8.6727 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+10 | 0.03125 | 3.2586 | 1.4 | 120 | 1.8586 | 0 | 10.5 | 8.6414 |  | 0
278 | SS Tuchevo 110/35/10 | 25+25 | 0.35811 | 0.32178 | 120 | 0.03633 | 0 | 26.25 | 26.2137 | 22.9437 |  |  | 1.3642 | 276 | SS Tuchevo 110/35/10 | 25+25 | 0 | 0.35811 | 0.32178 | 120 | 0.03633 | 0 | 26.25 | 26.2137 | 22.9437 |  |  | 1.3642 | Тверские Электрические сети
| Nom. capacity MV, MVA | 25+25 | 0.32178 | 0.32178 | 120 | 0 | 0 | 23.17 | 23.17 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+25 | 0 | 0.32178 | 0.32178 | 120 | 0 | 0 | 23.17 | 23.17 |  | 0
| Nom. capacity MV, MVA | 25+25 | 0.03633 | 0 |  | 0.03633 | 0 | 22.98 | 22.9437 |  | 0 |  |  |  | Nom. capacity MV, MVA | 25+25 | 0 | 0.03633 | 0 |  | 0.03633 | 0 | 22.98 | 22.9437 |  | 0
279 | SS Strashevichi 35/10 kv | 4 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 |  |  | 11.9048 | 277 | SS Strashevichi 35/10 kv | 4 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 |  |  | 11.9048 | Торжокские Электрические сети
280 | SS Sukromlya 35/10 kv | 2.5 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 11.4286 | 278 | SS Sukromlya 35/10 kv | 2.5 | 0 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 11.4286 | Торжокские Электрические сети
281 | SS Kr. Gorodok 35/10 kv | 0.56 | 0.04 | 0 |  | 0 | 0 | 0 | -0.04 | -0.04 | MS is closed | MS is closed | 6.8027 | 279 | SS Kr. Gorodok 35/10 kv | 0.56 | 0 | 0.04 | 0 |  | 0 | 0 | 0 | -0.04 | -0.04 | MS is closed | MS is closed | 6.8027 | Торжокские Электрические сети
282 | SS Pryamukhino 35/10 kv | 2.5 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 |  |  | 26.6667 | 280 | SS Pryamukhino 35/10 kv | 2.5 | 0 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 |  |  | 26.6667 | Торжокские Электрические сети
283 | SS Pen 35/10 kv | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | 281 | SS Pen 35/10 kv | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | Торжокские Электрические сети
284 | SS Pechnikovo 35/10 kv | 2.5 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 |  |  | 3.8095 | 282 | SS Pechnikovo 35/10 kv | 2.5 | 0 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 |  |  | 3.8095 | Торжокские Электрические сети
285 | SS Maksimkovo 35/10 kv | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 |  |  | 22.8571 | 283 | SS Maksimkovo 35/10 kv | 2.5 | 0 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 |  |  | 22.8571 | Торжокские Электрические сети
286 | SS Filistovo 35/10 kv | 1.6 | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 |  |  | 11.9048 | 284 | SS Filistovo 35/10 kv | 1.6 | 0 | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 |  |  | 11.9048 | Торжокские Электрические сети
287 | SS Okovtsy 35/10 kv | 1 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 28.5714 | 285 | SS Okovtsy 35/10 kv | 1 | 0 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 |  |  | 28.5714 | Торжокские Электрические сети
288 | SS Seliger 35/10 kv | 6.3 | 4.5 | 0 |  | 0 | 0 | 0 | -4.5 | -4.5 | MS is closed | MS is closed | 68.0272 | 286 | SS Seliger 35/10 kv | 6.3 | 0.15 | 4.65 | 0 |  | 0 | 0 | 0 | -4.65 | -4.65 | MS is closed | MS is closed | 70.2948 | Торжокские Электрические сети
289 | SS Moshary 35/10 kv | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | 287 | SS Moshary 35/10 kv | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | MS is closed | 11.9048 | Торжокские Электрические сети
290 | SS Voroshilovo 35/10 kv | 1 | 0.4 | 0 |  | 0 | 0 | 0 | -0.4 | -0.4 | MS is closed | MS is closed | 38.0952 | 288 | SS Voroshilovo 35/10 kv | 1 | 0 | 0.4 | 0 |  | 0 | 0 | 0 | -0.4 | -0.4 | MS is closed | MS is closed | 38.0952 | Торжокские Электрические сети
291 | SS Slautino 35/10 kv | 1.6 | 0.6 | 0 |  | 0 | 0 | 0 | -0.6 | -0.6 | MS is closed | MS is closed | 35.7143 | 289 | SS Slautino 35/10 kv | 1.6 | 0.0375 | 0.6375 | 0 |  | 0 | 0 | 0 | -0.6375 | -0.6375 | MS is closed | MS is closed | 37.9464 | Торжокские Электрические сети
292 | SS Moshki 35/10 kv | 2,5+2,5 | 2.6 | 0 |  | 2.6 | 0 | 2.63 | 0.03 | 0.03 |  |  | 98.8593 | 290 | SS Moshki 35/10 kv | 2,5+2,5 | 0.115 | 2.715 | 0 |  | 2.715 | 0 | 2.63 | -0.085 | -0.085 | MS is closed | MS is closed | 103.2319 | Торжокские Электрические сети
293 | SS Vysokoe 35/10 kv | 4+2,5 | 0.9 | 0 |  | 0.9 | 0 | 2.63 | 1.73 | 1.73 |  |  | 34.2205 | 291 | SS Vysokoe 35/10 kv | 4+2,5 | 0 | 0.9 | 0 |  | 0.9 | 0 | 2.63 | 1.73 | 1.73 |  |  | 34.2205 | Торжокские Электрические сети
294 | SS Bubenye 35/10 kv | 4+4 | 2.8 | 0 |  | 2.8 | 0 | 4.2 | 1.4 | 1.4 |  |  | 66.6667 | 292 | SS Bubenye 35/10 kv | 4+4 | 0.3 | 3.1 | 0 |  | 3.1 | 0 | 4.2 | 1.1 | 1.1 |  |  | 73.8095 | Торжокские Электрические сети
295 | SS B.Vishenye 35/10 kv | 2,5+2,5 | 1.1 | 0 |  | 1.1 | 0 | 2.63 | 1.53 | 1.53 |  |  | 41.8251 | 293 | SS B.Vishenye 35/10 kv | 2,5+2,5 | 0 | 1.1 | 0 |  | 1.1 | 0 | 2.63 | 1.53 | 1.53 |  |  | 41.8251 | Торжокские Электрические сети
296 | SS Budovo 35/10 kv | 2,5+2,5 | 1.4 | 0 |  | 1.4 | 0 | 2.63 | 1.23 | 1.23 |  |  | 53.2319 | 294 | SS Budovo 35/10 kv | 2,5+2,5 | 0 | 1.4 | 0 |  | 1.4 | 0 | 2.63 | 1.23 | 1.23 |  |  | 53.2319 | Торжокские Электрические сети
297 | SS Eltsy 35/10 kv | 4+4 | 0.42 | 0 |  | 0.42 | 0 | 4.2 | 3.78 | 3.78 |  |  | 10 | 295 | SS Eltsy 35/10 kv | 4+4 | 0 | 0.42 | 0 |  | 0.42 | 0 | 4.2 | 3.78 | 3.78 |  |  | 10 | Торжокские Электрические сети
298 | SS Selishche 35/10 kv | 4+4 | 1.7 | 0 |  | 1.7 | 0 | 4.2 | 2.5 | 2.5 |  |  | 40.4762 | 296 | SS Selishche 35/10 kv | 4+4 | 0.11625 | 1.8162 | 0 |  | 1.8162 | 0 | 4.2 | 2.3838 | 2.3838 |  |  | 43.244 | Торжокские Электрические сети
299 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.7 | 0 |  | 0.7 | 0 | 1.68 | 0.98 | 0.98 |  |  | 41.6667 | 297 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.125 | 0.825 | 0 |  | 0.825 | 0 | 1.68 | 0.855 | 0.855 |  |  | 49.1071 | Торжокские Электрические сети
300 | SS Krapivnya 35/10 kv | 2,5+2,5 | 0.5 | 0 |  | 0.5 | 0 | 2.63 | 2.13 | 2.13 |  |  | 19.0114 | 298 | SS Krapivnya 35/10 kv | 2,5+2,5 | 0.25 | 0.75 | 0 |  | 0.75 | 0 | 2.63 | 1.88 | 1.88 |  |  | 28.5171 | Торжокские Электрические сети
301 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 1.7 | 0 |  | 1.7 | 0 | 2.63 | 0.93 | 0.93 |  |  | 64.6388 | 299 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 0 | 1.7 | 0 |  | 1.7 | 0 | 2.63 | 0.93 | 0.93 |  |  | 64.6388 | Торжокские Электрические сети
302 | SS KS-20 110/6 kv | 63+63 | 8.6 | 0 |  | 8.6 | 0 | 66.15 | 57.55 | 57.55 |  |  | 13.0008 | 300 | SS KS-20 110/6 kv | 63+63 | 0 | 8.6 | 0 |  | 8.6 | 0 | 66.15 | 57.55 | 57.55 |  |  | 13.0008 | Торжокские Электрические сети
303 | SS Polygraphical paint 110/10 kv | 10+10 | 6.29 | 0 |  | 6.29 | 0 | 10.5 | 4.21 | 4.21 |  |  | 59.9048 | 301 | SS Polygraphical paint 110/10 kv | 10+10 | 0 | 6.29 | 0 |  | 6.29 | 0 | 10.5 | 4.21 | 4.21 |  |  | 59.9048 | Торжокские Электрические сети
304 | SS NPS Torzhok 110/10 kv | 25+25 | 0.001 | 0 |  | 0.001 | 0 | 26.25 | 26.249 | 26.249 |  |  | 0.0038095 | 302 | SS NPS Torzhok 110/10 kv | 25+25 | 0 | 0.001 | 0 |  | 0.001 | 0 | 26.25 | 26.249 | 26.249 |  |  | 0.0038095 | Торжокские Электрические сети
305 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0.74 | 0 |  | 0.74 | 0 | 2.63 | 1.89 | 1.89 |  |  | 28.1369 | 303 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0 | 0.74 | 0 |  | 0.74 | 0 | 2.63 | 1.89 | 1.89 |  |  | 28.1369 | Торжокские Электрические сети
306 | SS Peno 110/10 kv | 6,3+6,3 | 4.1 | 0 |  | 4.1 | 0 | 6.62 | 2.52 | 2.52 |  |  | 61.9335 | 304 | SS Peno 110/10 kv | 6,3+6,3 | 0.025 | 4.125 | 0 |  | 4.125 | 0 | 6.62 | 2.495 | 2.495 |  |  | 62.3112 | Торжокские Электрические сети
307 | SS Torzhok 110/35/10 kv | 25+40 | 23.9 | 7.8 | 120 | 16.1 | 0 | 26.25 | 10.15 | 10.15 |  |  | 91.0476 | 305 | SS Torzhok 110/35/10 kv | 25+40 | 6.2275 | 30.1275 | 7.8 | 120 | 22.3275 | 0 | 26.25 | 3.9225 | 3.9225 |  |  | 114.7714 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 25+40 | 7.8 | 7.8 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. Capacity MV, MVA | 25+40 | 0.415 | 8.215 | 7.8 | 120 | 0.415 | 0 | 26.25 | 25.835 |  | 0
| Nom. Capacity LV, MVA | 25+40 | 16.1 | 0 |  | 16.1 | 0 | 26.25 | 10.15 |  | 0 |  |  |  | Nom. Capacity LV, MVA | 25+40 | 5.8125 | 21.9125 | 0 |  | 21.9125 | 0 | 26.25 | 4.3375 |  | 0
308 | SS Stroyindustriya 110/35/10 kv | 25+25 | 7.8 | 0.2 | 120 | 7.6 | 0 | 26.25 | 18.65 | 18.65 |  |  | 29.7143 | 306 | SS Stroyindustriya 110/35/10 kv | 25+25 | 0 | 7.8 | 0.2 | 120 | 7.6 | 0 | 26.25 | 18.65 | 18.65 |  |  | 29.7143 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 25+25 | 0.2 | 0.2 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0
| Nom. Capacity LV, MVA | 25+25 | 7.6 | 0 |  | 7.6 | 0 | 26.25 | 18.65 |  | 0 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 7.6 | 0 |  | 7.6 | 0 | 26.25 | 18.65 |  | 0
309 | SS Kuvshinovo 110/35/10 kv | 25+25 | 14.7 | 1.5 | 120 | 13.2 | 0 | 26.25 | 13.05 | 13.05 |  |  | 56 | 307 | SS Kuvshinovo 110/35/10 kv | 25+25 | 0 | 14.7 | 1.5 | 120 | 13.2 | 0 | 26.25 | 13.05 | 13.05 |  |  | 56 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 25+25 | 1.5 | 1.5 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 1.5 | 1.5 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0
| Nom. Capacity LV, MVA | 25+25 | 13.2 | 0 |  | 13.2 | 0 | 26.25 | 13.05 |  | 0 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 13.2 | 0 |  | 13.2 | 0 | 26.25 | 13.05 |  | 0
310 | SS Selizharovo 110/35/10 kv | 16+10 | 8.5 | 0 |  | 8.5 | 0 | 10.5 | 2 | 2 |  |  | 80.9524 | 308 | SS Selizharovo 110/35/10 kv | 16+10 | 1.75 | 10.25 | 0 |  | 10.25 | 0 | 10.5 | 0.25 | 0.25 |  |  | 97.619 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 16+10 | 2.3 | 0 |  | 2.3 | 0 | 10.5 | 8.2 |  | 0 |  |  |  | Nom. Capacity MV, MVA | 16+10 | 0 | 2.3 | 0 |  | 2.3 | 0 | 10.5 | 8.2 |  | 0
| Nom. Capacity LV, MVA | 16+10 | 6.2 | 0 |  | 6.2 | 0 | 10.5 | 4.3 |  | 0 |  |  |  | Nom. Capacity LV, MVA | 16+10 | 1.75 | 7.95 | 0 |  | 7.95 | 0 | 10.5 | 2.55 |  | 0
311 | SS NPS Borisovo 110/35/10 kv | 25+25 | 1.02 | 0.82 | 120 | 0.2 | 0 | 26.25 | 26.05 | 26.05 |  |  | 3.8857 | 309 | SS NPS Borisovo 110/35/10 kv | 25+25 | 0 | 1.02 | 0.82 | 120 | 0.2 | 0 | 26.25 | 26.05 | 26.05 |  |  | 3.8857 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 25+25 | 0.82 | 0.82 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 0.82 | 0.82 | 120 | 0 | 0 | 26.25 | 26.25 |  | 0
| Nom. Capacity LV, MVA | 25+25 | 0.2 | 0 |  | 0.2 | 0 | 26.25 | 26.05 |  | 0 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 0.2 | 0 |  | 0.2 | 0 | 26.25 | 26.05 |  | 0
312 | SS Ostashkov 110/35/10 kv | 25+25 | 18.1 | 0 |  | 18.1 | 0 | 26.25 | 8.15 | 8.15 |  |  | 68.9524 | 310 | SS Ostashkov 110/35/10 kv | 25+25 | 0.375 | 18.475 | 0 |  | 18.475 | 0 | 26.25 | 7.775 | 7.775 |  |  | 70.381 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 25+25 | 2 | 0 |  | 2 | 0 | 26.25 | 24.25 | [5 empty] | Nom. Capacity MV, MVA | 25+25 | 0.25 | 2.25 | 0 |  | 2.25 | 0 | 26.25 | 24 |  | 0
| Nom. Capacity LV, MVA | 25+25 | 16.1 | 0 |  | 16.1 | 0 | 26.25 | 10.15 | [5 empty] | Nom. Capacity LV, MVA | 25+25 | 0.125 | 16.225 | 0 |  | 16.225 | 0 | 26.25 | 10.025 |  | 0
313 | SS N. Rozhok 110/35/10 kv | 10+10 | 12.3 | 0 |  | 12.3 | 0 | 10.5 | -1.8 | -1.8 | MS is closed | MS is closed | 117.1429 | 311 | SS N. Rozhok 110/35/10 kv | 10+10 | 0.278 | 12.578 | 0 |  | 12.578 | 0 | 10.5 | -2.078 | -2.078 | MS is closed | MS is closed | 119.7905 | Торжокские Электрические сети
| Nom. Capacity MV, MVA | 10+10 | 2.6 | 0 |  | 2.6 | 0 | 10.5 | 7.9 |  |  | MS is closed |  |  | Nom. Capacity MV, MVA | 10+10 | 0.15 | 2.75 | 0 |  | 2.75 | 0 | 10.5 | 7.75 |  |  | MS is closed
| Nom. Capacity LV, MVA | 10+10 | 9.7 | 0 |  | 9.7 | 0 | 10.5 | 0.8 |  |  | MS is closed |  |  | Nom. Capacity LV, MVA | 10+10 | 0.128 | 9.828 | 0 |  | 9.828 | 0 | 10.5 | 0.672 |  |  | MS is closed
Total: |  | 3927.42 | 1172.3692 | [10 empty] | 1: Total:; 3: 3927.42; 4: 219.919; 5: 1391.4965
deficit | [9 empty] | -66.1033 |  |  |  | 1: deficit; Min. 12: -201.5555
proficit | [9 empty] | 935.5766 |  |  |  | 1: proficit; Min. 12: 846.2177
[9 empty] | Количество ПС, имеющие загрузку менее 30 % |  |  |  | 137 | Min. 11: Количество ПС, имеющие загрузку менее 30 %; Min. 14: 133
[9 empty] | Количество ПС, имеющие загрузку менее от 30 до 70 % |  |  |  | 102 | Min. 11: Количество ПС, имеющие загрузку менее от 30 до 70 %; Min. 14: 90
[9 empty] | Количество ПС, имеющие загрузку от 70 до 100 % |  |  |  | 49 | Min. 11: Количество ПС, имеющие загрузкуот 70 до 100 %; Min. 14: 51
[9 empty] | Количество ПС, имеющие загрузку более 105 % |  |  |  | 25 | Min. 11: Количество ПС, имеющие загрузку более 105 %; Min. 14: 39
[9 empty] | Количество Закрытых ЦП |  |  |  | 58 | Min. 11: Количество Закрытых ЦП; Min. 14: 71
Note on E154: Перевод нагрузки по 6 кВ на ПС Кимры
Note on E187: ОТКЛЮЧЕНИЕ В-35 Т-1 И Т-2 И перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща ( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on E190: Отключение В-35 Т-2 и Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on E196: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on E199: Перевод нагрузки Т-1 ПС Стоянцы
Note on E202: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская
Note on U154: Перевод нагрузки по 6 кВ на ПС Кимры
Note on U187: ОТКЛЮЧЕНИЕ В-35 Т-1 И Т-2 И перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща ( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on U190: Отключение В-35 Т-2 и Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on U196: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on U199: Перевод нагрузки Т-1 ПС Стоянцы
Note on U202: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская

## Костромаэнерго 3
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer SS | [11 empty] | 1: One-transformer SS
1 | Sandogora 35/6 kv | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | opened | 1 | Sandogora 35/6 kv | 1 | 0.05 | 0.52 | 0.55 | 120 | -0.03 | 0 | 0.55 | 0.03 | 0.03 | opened
2 | Gridino 35/10 kv | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | opened | 2 | Gridino 35/10 kv | 1.8 | 0.479 | 1.209 | 1.2 | 120 | 0.009 | 0 | 1.2 | -0.009 | -0.009 | closed
3 | Novinki 35/10 kv | 1.8 | 0.13 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.31 | 1.31 | opened | 3 | Novinki 35/10 kv | 1.8 | 0.311 | 0.441 | 1.44 | 120 | -0.999 | 0 | 1.44 | 0.999 | 0.999 | opened
4 | Priskokovo 35/10kv | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | opened | 4 | Priskokovo 35/10kv | 2.5 | 0.103 | 1.603 | 1.5 | 120 | 0.103 | 0 | 1.5 | -0.103 | -0.103 | closed
5 | Grigortsevo 110/10 kv | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 5 | Grigortsevo 110/10 kv | 2.5 | 0.014 | 0.264 | 1.5 | 120 | -1.236 | 0 | 1.5 | 1.236 | 1.236 | opened
6 | Klementyevo 110/10 kv | 6.3 | 0.38 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.32 | 3.32 | opened | 6 | Klementyevo 110/10 kv | 6.3 | 0.011 | 0.391 | 3.7 | 120 | -3.309 | 0 | 3.7 | 3.309 | 3.309 | opened
7 | Rudino 35/10 kv | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 7 | Rudino 35/10 kv | 2.5 | 0.002 | 0.252 | 1.5 | 120 | -1.248 | 0 | 1.5 | 1.248 | 1.248 | opened
8 | Stoyankovo 35/10 kv | 1.6 | 0.14 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.58 | 0.58 | opened | 8 | Stoyankovo 35/10 kv | 1.6 | 0.066 | 0.206 | 0.72 | 120 | -0.514 | 0 | 0.72 | 0.514 | 0.514 | opened
9 | Adishchevo 35/10 kv | 4 | 1.35 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.25 | 1.25 | opened | 9 | Adishchevo 35/10 kv | 4 | 0.89 | 2.24 | 2.6 | 120 | -0.36 | 0 | 2.6 | 0.36 | 0.36 | opened
10 | Stolbovo 110/10 kv | 10 | 0.27 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.33 | 4.33 | opened | 10 | Stolbovo 110/10 kv | 10 | 0.011 | 0.281 | 4.6 | 120 | -4.319 | 0 | 4.6 | 4.319 | 4.319 | opened
11 | Raslovo 35/10 kv | 2.5 | 0.54 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.84 | 0.84 | opened | 11 | Raslovo 35/10 kv | 2.5 | 0.31 | 0.85 | 1.38 | 120 | -0.53 | 0 | 1.38 | 0.53 | 0.53 | opened
12 | Andreevskoe 35/10 kv | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | opened | 12 | Andreevskoe 35/10 kv | 1.6 | 0.012 | 0.192 | 0.93 | 120 | -0.738 | 0 | 0.93 | 0.738 | 0.738 | opened
13 | Popadyino 35/10 kv | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | opened | 13 | Popadyino 35/10 kv | 1.6 | 0.118 | 0.338 | 0.88 | 120 | -0.542 | 0 | 0.88 | 0.542 | 0.542 | opened
14 | Elegino 110/10 kv | 2.5 | 0.13 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.85 | 0.85 | opened | 14 | Elegino 110/10 kv | 2.5 | 0.372 | 0.502 | 0.98 | 120 | -0.478 | 0 | 0.98 | 0.478 | 0.478 | opened
15 | Krenyovo 35/10 kv | 2.5 | 0.47 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.03 | 2.03 | opened | 15 | Krenyovo 35/10 kv | 2.5 | 0.069 | 0.539 | 2.5 | 24 hours | -1.961 | 0 | 2.5 | 1.961 | 1.961 | opened
16 | Semyonovskoe 35/10 kv | 1.6 | 0.09 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.51 | 1.51 | opened | 16 | Semyonovskoe 35/10 kv | 1.6 | 0 | 0.09 | 1.6 | 24 hours | -1.51 | 0 | 1.6 | 1.51 | 1.51 | opened
17 | Khimik 35/10 kv | 3.2 | 0.1 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.34 | 1.34 | opened | 17 | Khimik 35/10 kv | 3.2 | 0 | 0.1 | 1.44 | 120 | -1.34 | 0 | 1.44 | 1.34 | 1.34 | opened
18 | N. Beryozovets 35/10 kv | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | opened | 18 | N. Beryozovets 35/10 kv | 2.5 | 0.006 | 0.336 | 0.43 | 120 | -0.094 | 0 | 0.43 | 0.094 | 0.094 | opened
19 | Stepanovo 35/10 kv | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | opened | 19 | Stepanovo 35/10 kv | 4 | 0.061 | 0.381 | 2.32 | 120 | -1.939 | 0 | 2.32 | 1.939 | 1.939 | opened
20 | Gorbachevo 35/10 kv | 1 | 0.11 | 0.78 | 120 | 0.78 | 0 | 0.78 | 0.67 | 0.67 | opened | 20 | Gorbachevo 35/10 kv | 1 | 0 | 0.11 | 0.78 | 120 | -0.67 | 0 | 0.78 | 0.67 | 0.67 | opened
21 | Kalinino 35/10 kv | 1 | 0.11 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.45 | 0.45 | opened | 21 | Kalinino 35/10 kv | 1 | 0 | 0.11 | 0.56 | 120 | -0.45 | 0 | 0.56 | 0.45 | 0.45 | opened
22 | Kuzemino 35/10 kv | 1.6 | 0.23 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.37 | 1.37 | opened | 22 | Kuzemino 35/10 kv | 1.6 | 0 | 0.23 | 1.6 | 24 hours | -1.37 | 0 | 1.6 | 1.37 | 1.37 | opened
23 | Sovega 35/10 kv | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | opened | 23 | Sovega 35/10 kv | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | opened
24 | Lukovtsino 110/10 kv | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | opened | 24 | Lukovtsino 110/10 kv | 2.5 | 0 | 0.19 | 1.38 | 120 | -1.19 | 0 | 1.38 | 1.19 | 1.19 | opened
25 | Fyodorovskoe 110/10 kv | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | opened | 25 | Fyodorovskoe 110/10 kv | 2.5 | 0 | 0.15 | 1.5 | 120 | -1.35 | 0 | 1.5 | 1.35 | 1.35 | opened
26 | Pankratovo 35/10 kv | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | opened | 26 | Pankratovo 35/10 kv | 1 | 0 | 0.06 | 0.39 | 120 | -0.33 | 0 | 0.39 | 0.33 | 0.33 | opened
27 | Petrovskoe 35/10 kv | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | opened | 27 | Petrovskoe 35/10 kv | 1.6 | 0 | 0.32 | 0.77 | 120 | -0.45 | 0 | 0.77 | 0.45 | 0.45 | opened
28 | Kotelnikovo 35/10 kv | 1 | 0.11 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.15 | 0.15 | opened | 28 | Kotelnikovo 35/10 kv | 1 | 0 | 0.11 | 0.26 | 120 | -0.15 | 0 | 0.26 | 0.15 | 0.15 | opened
29 | Legitovo 35/10 kv | 2.5 | 0.31 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.79 | 0.79 | opened | 29 | Legitovo 35/10 kv | 2.5 | 0.019 | 0.329 | 1.1 | 120 | -0.771 | 0 | 1.1 | 0.771 | 0.771 | opened
30 | Sloboda 35/10 kv | 2.5 | 0.05 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 30 | Sloboda 35/10 kv | 2.5 | 0 | 0.05 | 0.85 | 120 | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
31 | Zavrazhye 35/10 kv | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | opened | 31 | Zavrazhye 35/10 kv | 1.6 | 0.083 | 0.373 | 0.74 | 120 | -0.367 | 0 | 0.74 | 0.367 | 0.367 | opened
32 | Okulovo 35/10 kv | 1.6 | 0.16 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.74 | 0.74 | opened | 32 | Okulovo 35/10 kv | 1.6 | 0.297 | 0.457 | 0.9 | 120 | -0.443 | 0 | 0.9 | 0.443 | 0.443 | opened
33 | Chernyshevo 35/10 kv | 4 | 0.57 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.23 | 1.23 | opened | 33 | Chernyshevo 35/10 kv | 4 | 0.087 | 0.657 | 1.8 | 120 | -1.143 | 0 | 1.8 | 1.143 | 1.143 | opened
34 | Yakovlevo 110/35/10 kv | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 | 5.24 | opened | 34 | Yakovlevo 110/35/10 kv | 10 | 0.012 | 0.072 | 5.3 | 120 | -5.228 | 0 | 5.3 | 5.228 | 5.228 | opened
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 |  |  |  | Nom. Capacity LV, MVA | 10 | 0.012 | 0.072 | 5.3 | 120 | -5.228 | 0 | 5.3 | 5.228
35 | Chermenino 35/10 kv | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | opened | 35 | Chermenino 35/10 kv | 1.6 | 0 | 0.07 | 0.86 | 120 | -0.79 | 0 | 0.86 | 0.79 | 0.79 | opened
36 | Nezhitino 35/10 kv | 1 | 0.08 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.46 | 0.46 | opened | 36 | Nezhitino 35/10 kv | 1 | 0.036 | 0.116 | 0.54 | 120 | -0.424 | 0 | 0.54 | 0.424 | 0.424 | opened
37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.45 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.54 | 0.54 | opened | 37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.137 | 0.587 | 0.99 | 120 | -0.403 | 0 | 0.99 | 0.403 | 0.403 | opened
38 | Gusevo 110/10 kv | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | opened | 38 | Gusevo 110/10 kv | 2.5 | 0 | 0.29 | 1.63 | 120 | -1.34 | 0 | 1.63 | 1.34 | 1.34 | opened
39 | Medveditsa 35/10 kv | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | opened | 39 | Medveditsa 35/10 kv | 2.5 | 0 | 0.53 | 1.3 | 120 | -0.77 | 0 | 1.3 | 0.77 | 0.77 | opened
40 | Novinskoe 110/10 kv | 2.5 | 0.03 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.2 | 1.2 | opened | 40 | Novinskoe 110/10 kv | 2.5 | 0 | 0.03 | 1.23 | 120 | -1.2 | 0 | 1.23 | 1.2 | 1.2 | opened
41 | Filino 35/10 kv | 1.6 | 0.25 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.71 | 0.71 | opened | 41 | Filino 35/10 kv | 1.6 | 0.11 | 0.36 | 0.96 | 120 | -0.6 | 0 | 0.96 | 0.6 | 0.6 | opened
42 | Dyakonovo 110/10 kv | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | opened | 42 | Dyakonovo 110/10 kv | 2.5 | 0.092 | 0.372 | 1.13 | 120 | -0.758 | 0 | 1.13 | 0.758 | 0.758 | opened
43 | Oktyabrskaya 110/10 kv | 2.5 | 0.76 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.74 | 1.74 | opened | 43 | Oktyabrskaya 110/10 kv | 2.5 | 0.019 | 0.779 | 2.5 | 24 hours | -1.721 | 0 | 2.5 | 1.721 | 1.721 | opened
44 | Kuzhbal 35/10 kv | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | opened | 44 | Kuzhbal 35/10 kv | 2.5 | 0 | 0.4 | 1.48 | 120 | -1.08 | 0 | 1.48 | 1.08 | 1.08 | opened
45 | Nikolo-Poloma 110/10 kv | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | opened | 45 | Nikolo-Poloma 110/10 kv | 2.5 | 0 | 1.04 | 1.13 | 120 | -0.09 | 0 | 1.13 | 0.09 | 0.09 | opened
46 | Nikola 110/35/10 kv | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87 | 2.87 | opened | 46 | Nikola 110/35/10 kv | 6.3 | 0.018 | 0.298 | 3.15 | 120 | -2.852 | 0 | 3.15 | 2.852 | 2.852 | opened
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0.018 | 0.298 | 3.15 | 120 | -2.852 | 0 | 3.15 | 2.852
47 | Zavetluzhye 35/10 kv | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | opened | 47 | Zavetluzhye 35/10 kv | 1.6 | 0 | 0.11 | 0.67 | 120 | -0.56 | 0 | 0.67 | 0.56 | 0.56 | opened
48 | Talitsa 35/10 kv | 1.6 | 0.26 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.34 | 1.34 | opened | 48 | Talitsa 35/10 kv | 1.6 | 0 | 0.26 | 1.6 | 24 hours | -1.34 | 0 | 1.6 | 1.34 | 1.34 | opened
49 | Khoroshaya 35/10 kv | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | opened | 49 | Khoroshaya 35/10 kv | 2.5 | 0 | 0.06 | 1.95 | 120 | -1.89 | 0 | 1.95 | 1.89 | 1.89 | opened
50 | Zabegaevo 35/10 kv | 1.6 | 0.09 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.79 | 0.79 | opened | 50 | Zabegaevo 35/10 kv | 1.6 | 0 | 0.09 | 0.88 | 120 | -0.79 | 0 | 0.88 | 0.79 | 0.79 | opened
51 | Ilyinskoe 35/10 kv | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | opened | 51 | Ilyinskoe 35/10 kv | 1.6 | 0 | 0.04 | 0.9 | 120 | -0.86 | 0 | 0.9 | 0.86 | 0.86 | opened
52 | Luptyug 35/10 kv | 2.5 | 0.11 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.24 | 1.24 | opened | 52 | Luptyug 35/10 kv | 2.5 | 0 | 0.11 | 1.35 | 120 | -1.24 | 0 | 1.35 | 1.24 | 1.24 | opened
53 | Solovetskoe 35/10 kv | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | opened | 53 | Solovetskoe 35/10 kv | 1.6 | 0.007 | 0.097 | 0.72 | 120 | -0.623 | 0 | 0.72 | 0.623 | 0.623 | opened
54 | Gudkovo 110/10 kv | 2.5 | 0.05 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.33 | 1.33 | opened | 54 | Gudkovo 110/10 kv | 2.5 | 0.006 | 0.056 | 1.38 | 120 | -1.324 | 0 | 1.38 | 1.324 | 1.324 | opened
55 | Shortyug 110/10 kv | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | opened | 55 | Shortyug 110/10 kv | 6.3 | 0.037 | 0.557 | 3.47 | 120 | -2.913 | 0 | 3.47 | 2.913 | 2.913 | opened
56 | Yakshanga 110/10 kv | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | opened | 56 | Yakshanga 110/10 kv | 6.3 | 0.04 | 1.45 | 3.47 | 120 | -2.02 | 0 | 3.47 | 2.02 | 2.02 | opened
57 | Katunino 35/10 kv | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | opened | 57 | Katunino 35/10 kv | 2.5 | 0 | 0.17 | 1.33 | 120 | -1.16 | 0 | 1.33 | 1.16 | 1.16 | opened
58 | Konyovo 35/10 kv | 1.6 | 0.21 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.67 | 0.67 | opened | 58 | Konyovo 35/10 kv | 1.6 | 0 | 0.21 | 0.88 | 120 | -0.67 | 0 | 0.88 | 0.67 | 0.67 | opened
59 | Shekshema 110/10 kv | 6.3 | 0.58 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.92 | 1.92 | opened | 59 | Shekshema 110/10 kv | 6.3 | 0.036 | 0.616 | 2.5 | 24 hours | -1.884 | 0 | 2.5 | 1.884 | 1.884 | opened
60 | Golovino 35/10 kv | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | opened | 60 | Golovino 35/10 kv | 1 | 0 | 0.06 | 0.12 | 120 | -0.06 | 0 | 0.12 | 0.06 | 0.06 | opened
61 | Pishchyovka 35/10 kv | 1 | 0.16 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened | 61 | Pishchyovka 35/10 kv | 1 | 0.04 | 0.2 | 0.45 | 120 | -0.25 | 0 | 0.45 | 0.25 | 0.25 | opened
Two-and more transformer SS | [11 empty] | 1: Two-and more transformer SS
62 | Vasilyovo 110/35/10 kv | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | opened | 62 | Vasilyovo 110/35/10 kv | 10+10 | 3.589 | 5.719 | 0.86 | 120 | 4.859 | 0 | 10.5 | 5.641 | 5.641 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 3.589 | 5.129 | 0.86 | 120 | 4.269 | 0 | 10.5 | 6.231
63 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 7.21 | opened | 63 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 0.333 | 6.453 | 1.15 | 120 | 5.303 | 0 | 12.18 | 6.877 | 6.877 | opened
| Nom. Capacity MV, MVA | 10+10+1,6 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.53 | 1.15 | 120 | 0.38 | 0 | 12.18 | 11.8 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.333 | 1.863 | 1.15 | 120 | 0.713 | 0 | 12.18 | 11.467
64 | Apraksino 35/10 kv | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | opened | 64 | Apraksino 35/10 kv | 2,5+2,5 | 0.952 | 2.682 | 0.425 | 120 | 2.257 | 0 | 2.625 | 0.368 | 0.368 | opened
65 | Borshchino 35/10 kv | 4+4 | 0.56 | 0.62 | 120 | -0.06 | 0 | 4.2 | 4.26 | 4.26 | opened | 65 | Borshchino 35/10 kv | 4+4 | 0.306 | 0.866 | 0.62 | 120 | 0.246 | 0 | 4.2 | 3.954 | 3.954 | opened
66 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.2 | 0.11 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 66 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.02 | 0.22 | 0.11 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
67 | Ilyinskoe 35/10 kv | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | opened | 67 | Ilyinskoe 35/10 kv | 2,5+2,5 | 0.547 | 2.877 | 0.55 | 120 | 2.327 | 0 | 2.625 | 0.298 | 0.298 | opened
68 | Kuznetsovo 35/10 kv | 2,5+2,5 | 1.1 | 0.4 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 68 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.128 | 1.228 | 0.4 | 120 | 0.828 | 0 | 2.625 | 1.797 | 1.797 | opened
69 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.72 | 0.29 | 120 | 0.43 | 0 | 1.68 | 1.25 | 1.25 | opened | 69 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.115 | 0.835 | 0.29 | 120 | 0.545 | 0 | 1.68 | 1.135 | 1.135 | opened
70 | Minskoe 35/10 kv | 2,5+2,5 | 1.3 | 0.43 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | opened | 70 | Minskoe 35/10 kv | 2,5+2,5 | 0.628 | 1.928 | 0.43 | 120 | 1.498 | 0 | 2.625 | 1.127 | 1.127 | opened
71 | Miskovo 35/6 kv | 1,8+1,8 | 0.35 | 0.2 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | opened | 71 | Miskovo 35/6 kv | 1,8+1,8 | 0.044 | 0.394 | 0.2 | 120 | 0.194 | 0 | 1.89 | 1.696 | 1.696 | opened
72 | Nikolskoe 35/6 kv | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | opened | 72 | Nikolskoe 35/6 kv | 4+4 | 0.671 | 3.171 | 0.92 | 120 | 2.251 | 0 | 4.2 | 1.949 | 1.949 | opened
73 | Samet 35/6 kv | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | opened | 73 | Samet 35/6 kv | 1,6+4 | 0.149 | 1.579 | 0 | 0 | 1.579 | 0 | 1.68 | 0.101 | 0.101 | opened
74 | Sukhonogovo 35/10 kv | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | opened | 74 | Sukhonogovo 35/10 kv | 3,2+4 | 0.658 | 3.368 | 0 | 0 | 3.368 | 0 | 3.36 | -0.008 | -0.008 | closed
75 | Sushchevo 35/10 kv | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | opened | 75 | Sushchevo 35/10 kv | 4+4 | 0.23 | 3.91 | 0.76 | 120 | 3.15 | 0 | 4.2 | 1.05 | 1.05 | opened
76 | EMZ 35/6 kv | 1+1 | 0.76 | 0 | 0 | 0.76 | 0 | 1.05 | 0.29 | 0.29 | opened | 76 | EMZ 35/6 kv | 1+1 | 0.006 | 0.766 | 0 | 0 | 0.766 | 0 | 1.05 | 0.284 | 0.284 | opened
77 | Krasnoe 110/35/10 kv | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | opened | 77 | Krasnoe 110/35/10 kv | 16+16 | 2.046 | 14.456 | 0 | 0 | 14.456 | 0 | 16.8 | 2.344 | 2.344 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.046 | 13.686 | 0 | 0 | 13.686 | 0 | 16.8 | 3.114
78 | Isaevo 35/10 kv | 4+4 | 0.77 | 1.03 | 120 | -0.26 | 0 | 4.2 | 4.46 | 4.46 | opened | 78 | Isaevo 35/10 kv | 4+4 | 2.227 | 2.997 | 1.03 | 120 | 1.967 | 0 | 4.2 | 2.233 | 2.233 | opened
79 | Chapaevo 35/10 kv | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 79 | Chapaevo 35/10 kv | 2,5+2,5 | 0.09 | 1.36 | 0.43 | 120 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened
80 | Chernevo 35/10 kv | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | opened | 80 | Chernevo 35/10 kv | 1,8+1,8 | 0.01 | 0.38 | 0.43 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened
81 | Nerekhta-1 110/35/10 kv | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | opened | 81 | Nerekhta-1 110/35/10 kv | 25+25 | 0.506 | 19.016 | 2.75 | 120 | 16.266 | 0 | 26.25 | 9.984 | 9.984 | opened
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.506 | 12.496 | 2.75 | 120 | 9.746 | 0 | 26.25 | 16.504
| Nerekhta-1 110/10 kv | 16+16 | 2.41 | 2.2 | 120 | 0.21 | 0 | 16.8 | 16.59 |  |  |  | Nerekhta-1 110/10 kv | 16+16 | 0 | 2.41 | 2.2 | 120 | 0.21 | 0 | 16.8 | 16.59
82 | Nerekhta-2 110/10/6 kv | 5,6+10 | 0.93 | 1.55 | 120 | -0.62 | 0 | 5.88 | 6.5 | 6.5 | opened | 82 | Nerekhta-2 110/10/6 kv | 5,6+10 | 7.014 | 7.944 | 1.55 | 120 | 6.394 | 0 | 5.88 | -0.514 | -0.514 | closed
83 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.57 | 0.41 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 83 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.098 | 0.668 | 0.41 | 120 | 0.258 | 0 | 1.68 | 1.422 | 1.422 | opened
84 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.36 | 0.23 | 120 | 0.13 | 0 | 6.615 | 6.485 | 6.485 | opened | 84 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.024 | 0.384 | 0.23 | 120 | 0.154 | 0 | 6.615 | 6.461 | 6.461 | opened
85 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 3.89 | 0.76 | 120 | 3.13 | 0 | 6.615 | 3.485 | 3.305 | opened | 85 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 0.055 | 3.945 | 0.76 | 120 | 3.185 | 0 | 6.615 | 3.43 | 3.305 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 3.31 | 0 | 120 | 3.31 | 0 | 6.615 | 3.305 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 3.31 | 0 | 120 | 3.31 | 0 | 6.615 | 3.305
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.58 | 0.76 | 120 | -0.18 | 0 | 6.615 | 6.795 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.055 | 0.635 | 0.76 | 120 | -0.125 | 0 | 6.615 | 6.74
86 | Krasnaya Polyana 110/35/10 kv | 10+10 | 3.91 | 1.28 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | opened | 86 | Krasnaya Polyana 110/35/10 kv | 10+10 | 1.104 | 5.014 | 1.28 | 120 | 3.734 | 0 | 10.5 | 6.766 | 6.766 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78
| Nom. Capacity LV, MVA | 10+10 | 3.19 | 1.28 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.104 | 4.294 | 1.28 | 120 | 3.014 | 0 | 10.5 | 7.486
87 | Igodovo 35/10 kv | 1,6+1,6 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 87 | Igodovo 35/10 kv | 1,6+1,6 | 0.097 | 0.467 | 0.25 | 120 | 0.217 | 0 | 1.68 | 1.463 | 1.463 | opened
88 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 88 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.033 | 0.833 | 0.56 | 120 | 0.273 | 0 | 1.68 | 1.407 | 1.407 | opened
89 | Ostrovskoe 35/10 kv | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 89 | Ostrovskoe 35/10 kv | 2,5+2,5 | 0.089 | 1.409 | 0.52 | 120 | 0.889 | 0 | 2.625 | 1.736 | 1.736 | opened
90 | Sudislavl 110/10 kv | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | opened | 90 | Sudislavl 110/10 kv | 10+10 | 1.343 | 9.483 | 1.8 | 120 | 7.683 | 0 | 10.5 | 2.817 | 2.817 | opened
91 | Voronye 35/10 kv | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 91 | Voronye 35/10 kv | 1,8+1,8 | 0.016 | 0.506 | 0.4 | 120 | 0.106 | 0 | 1.89 | 1.784 | 1.784 | opened
92 | Susanino 110/35/10 kv | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | opened | 92 | Susanino 110/35/10 kv | 10+10 | 0.583 | 4.513 | 1.89 | 120 | 2.623 | 0 | 10.5 | 7.877 | 7.877 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.583 | 4.133 | 1.89 | 120 | 2.243 | 0 | 10.5 | 8.257
93 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.2 | 0.07 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 93 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.018 | 0.218 | 0.07 | 120 | 0.148 | 0 | 2.625 | 2.477 | 2.477 | opened
94 | Airport 110/35/6 kv | 16+16 | 4.17 | 2.88 | 120 | 1.29 | 0 | 16.8 | 15.51 | 15.51 | opened | 94 | Airport 110/35/6 kv | 16+16 | 2.832 | 7.002 | 2.88 | 120 | 4.122 | 0 | 16.8 | 12.678 | 12.678 | opened
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 4.17 | 2.88 | 120 | 1.29 | 0 | 16.8 | 15.51 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.832 | 7.002 | 2.88 | 120 | 4.122 | 0 | 16.8 | 12.678
95 | Vostochnaya-2 110/35/10 kv | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | opened | 95 | Vostochnaya-2 110/35/10 kv | 25+25 | 0.982 | 24.022 | 0.02 | 120 | 24.002 | 0 | 26.25 | 2.248 | 2.248 | opened
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.982 | 4.782 | 0.02 | 120 | 4.762 | 0 | 26.25 | 21.488
96 | Kostroma-3 110/35/10 kv | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | closed | 96 | Kostroma-3 110/35/10 kv | 10+16 | 0.715 | 12.205 | 0 | 120 | 12.205 | 0 | 10.5 | -1.705 | -1.705 | closed
| Nom. Capacity MV, MVA | 10+16 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82
| Nom. Capacity LV, MVA | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 0.715 | 9.525 | 0 | 120 | 9.525 | 0 | 10.5 | 0.975
97 | Yuzhnaya 110/35/10 kv | 25+25 | 10.9 | 0 | 120 | 10.9 | 0 | 26.25 | 15.35 | 15.35 | opened | 97 | Yuzhnaya 110/35/10 kv | 25+25 | 6.172 | 17.072 | 0 | 120 | 17.072 | 0 | 26.25 | 9.178 | 9.178 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8
| Nom. Capacity LV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 6.172 | 11.622 | 0 | 120 | 11.622 | 0 | 26.25 | 14.628
98 | Davydovskaya 110/10 kv | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | opened | 98 | Davydovskaya 110/10 kv | 25+25 | 8.326 | 17.236 | 0.02 | 120 | 17.216 | 0 | 26.25 | 9.034 | 9.034 | opened | put in on 09.2009.
99 | Kostroma-1 110/6 kv | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | opened | 99 | Kostroma-1 110/6 kv | 10+10 | 1.463 | 11.843 | 0 | 0 | 11.843 | 0 | 10.5 | -1.343 | -1.343 | closed
100 | Severnaya 110/6 kv | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | opened | 100 | Severnaya 110/6 kv | 20+25 | 3.943 | 23.183 | 0 | 0 | 23.183 | 0 | 21 | -2.183 | -2.183 | closed
101 | Strommashina 110/6 kv | 40+40 | 9.03 | 0 | 0 | 9.03 | 0 | 42 | 32.97 | 32.97 | opened | 101 | Strommashina 110/6 kv | 40+40 | 1.198 | 10.228 | 0 | 0 | 10.228 | 0 | 42 | 31.772 | 31.772 | opened
102 | Tsentralnaya 110/10/6 kv | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | opened | 102 | Tsentralnaya 110/10/6 kv | 25+25 | 7.02 | 23.46 | 0 | 0 | 23.46 | 0 | 26.25 | 2.79 | 2.79 | opened
103 | Baydarka 35/6 kv | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | opened | 103 | Baydarka 35/6 kv | 6,3+6,3 | 0.729 | 2.719 | 1.2 | 120 | 1.519 | 0 | 6.615 | 5.096 | 5.096 | opened
104 | Volzhskaya 35/6 kv | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 104 | Volzhskaya 35/6 kv | 4+4 | 0.204 | 1.494 | 0.76 | 120 | 0.734 | 0 | 4.2 | 3.466 | 3.466 | opened
105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 22.36 | 0 | 0 | 22.36 | 0 | 17.115 | -5.245 | -5.245 | closed | 105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 1.668 | 24.028 | 0 | 0 | 24.028 | 0 | 17.115 | -6.913 | -6.913 | closed
106 | Karavaevo 35/10 kv | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | opened | 106 | Karavaevo 35/10 kv | 6,3+6,3 | 1.344 | 4.804 | 0 | 0 | 4.804 | 0 | 6.615 | 1.811 | 1.811 | opened
107 | Korkino 35/10 kv | 2,5+2,5 | 1.67 | 0.85 | 120 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | opened | 107 | Korkino 35/10 kv | 2,5+2,5 | 0.374 | 2.044 | 0.85 | 120 | 1.194 | 0 | 2.625 | 1.431 | 1.431 | opened
108 | KPD 110/35/10 kv | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | opened | 108 | KPD 110/35/10 kv | 16+16 | 11.047 | 18.587 | 1.44 | 120 | 17.147 | 0 | 16.8 | -0.347 | -0.347 | closed
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 11.047 | 17.967 | 1.44 | 120 | 16.527 | 0 | 16.8 | 0.273
109 | SM State district power station 110/35/6 kv | 10+16 | 6.48 | 0 | 0 | 6.48 | 0 | 10.5 | 4.02 | 4.02 | opened | 109 | SM State district power station 110/35/6 kv | 10+16 | 2.942 | 9.422 | 0 | 0 | 9.422 | 0 | 10.5 | 1.078 | 1.078 | opened
| Nom. Capacity MV, MVA | 10+16 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88
| Nom. Capacity LV, MVA | 10+16 | 5.86 | 0 | 0 | 5.86 | 0 | 10.5 | 4.64 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 2.942 | 8.802 | 0 | 0 | 8.802 | 0 | 10.5 | 1.698
110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.76 | 0.82 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened | 110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.122 | 0.882 | 0.82 | 120 | 0.062 | 0 | 2.625 | 2.563 | 2.563 | opened
111 | Buy (r) 110/35/10 kv | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | opened | 111 | Buy (r) 110/35/10 kv | 4+10 | 0.201 | 2.071 | 0 | 120 | 2.071 | 0 | 4.2 | 2.129 | 2.129 | opened
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 0 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 |  | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2
112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | opened | 112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 0.748 | 6.998 | 1.2 | 120 | 5.798 | 0 | 6.615 | 0.817 | 0.817 | opened
113 | Zapadnaya 110/10 kv | 10+10 | 5.08 | 2.63 | 120 | 2.45 | 0 | 10.5 | 8.05 | 8.05 | opened | 113 | Zapadnaya 110/10 kv | 10+10 | 0 | 5.08 | 2.63 | 120 | 2.45 | 0 | 10.5 | 8.05 | 8.05 | opened
114 | Dor 35/10 kv | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened | 114 | Dor 35/10 kv | 1,6+1,6 | 0.064 | 0.524 | 0.06 | 120 | 0.464 | 0 | 1.68 | 1.216 | 1.216 | opened
115 | Dyakonovo 35/10 kv | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened | 115 | Dyakonovo 35/10 kv | 1+1 | 0.071 | 0.301 | 0.26 | 120 | 0.041 | 0 | 1.05 | 1.009 | 1.009 | opened
116 | Likurga 35/10 kv | 1,8+1,6 | 0.2 | 0.12 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened | 116 | Likurga 35/10 kv | 1,8+1,6 | 0.001 | 0.201 | 0.12 | 120 | 0.081 | 0 | 1.68 | 1.599 | 1.599 | opened
117 | Shushkodom 35/10 kv | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | opened | 117 | Shushkodom 35/10 kv | 1+1 | 0.012 | 0.302 | 0.06 | 120 | 0.242 | 0 | 1.05 | 0.808 | 0.808 | opened
118 | Novaya 110/35/10 kv | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | opened | 118 | Novaya 110/35/10 kv | 6,3+6,3 | 0.68 | 3.61 | 0.64 | 120 | 2.97 | 0 | 6.615 | 3.645 | 3.645 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.68 | 1.78 | 0.64 | 120 | 1.14 | 0 | 6.615 | 5.475
119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | opened | 119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 0.136 | 1.496 | 0 | 120 | 1.496 | 0 | 6.615 | 5.119 | 5.119 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.136 | 0.966 | 0 | 120 | 0.966 | 0 | 6.615 | 5.649
120 | Loparevo 110/10 kv | 2,5+2,5 | 0.36 | 0.55 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 120 | Loparevo 110/10 kv | 2,5+2,5 | 0.242 | 0.602 | 0.55 | 120 | 0.052 | 0 | 2.625 | 2.573 | 2.573 | opened
121 | Poultry farm 35/10 kv | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened | 121 | Poultry farm 35/10 kv | 4+4 | 0 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened
122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.28 | 0.22 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened | 122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.006 | 0.286 | 0.22 | 120 | 0.066 | 0 | 2.625 | 2.559 | 2.559 | opened
123 | Levkovo 35/10 kv | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | opened | 123 | Levkovo 35/10 kv | 1,6+1,6 | 0.006 | 0.226 | 0.74 | 120 | -0.514 | 0 | 1.68 | 2.194 | 2.194 | opened
124 | Pronino 35/10 kv | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 124 | Pronino 35/10 kv | 4+2,5 | 0.021 | 0.401 | 0.2 | 120 | 0.201 | 0 | 2.625 | 2.424 | 2.424 | opened
125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.2 | 0.13 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.278 | 0.478 | 0.13 | 120 | 0.348 | 0 | 2.625 | 2.277 | 2.277 | opened
126 | Soligalich 110/35/10 kv | 10+10 | 5.27 | 1.7 | 120 | 3.57 | 0 | 10.5 | 6.93 | 6.93 | opened | 126 | Soligalich 110/35/10 kv | 10+10 | 0.856 | 6.126 | 1.7 | 120 | 4.426 | 0 | 10.5 | 6.074 | 6.074 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.94 | 0 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.94 | 0 | 120 | 0.94 | 0 | 10.5 | 9.56
| Nom. Capacity LV, MVA | 10+10 | 4.33 | 1.7 | 120 | 2.63 | 0 | 10.5 | 7.87 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.856 | 5.186 | 1.7 | 120 | 3.486 | 0 | 10.5 | 7.014
127 | Pochinok 35/10 kv | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 127 | Pochinok 35/10 kv | 1,6+2,5 | 0.017 | 0.547 | 0.34 | 120 | 0.207 | 0 | 1.68 | 1.473 | 1.473 | opened
128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | opened | 128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 0.552 | 4.522 | 2.06 | 120 | 2.462 | 0 | 6.615 | 4.153 | 4.153 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.552 | 3.402 | 2.06 | 120 | 1.342 | 0 | 6.615 | 5.273
129 | Suday 35/10 kv | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened | 129 | Suday 35/10 kv | 1,6+1,6 | 0.066 | 1.076 | 0.49 | 120 | 0.586 | 0 | 1.68 | 1.094 | 1.094 | opened
130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 6.09 | 0.38 | 120 | 5.71 | 0 | 6.615 | 0.905 | 0.905 | opened | 130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 0.152 | 6.242 | 0.38 | 120 | 5.862 | 0 | 6.615 | 0.753 | 0.753 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 3.53 | 0 | 120 | 3.53 | 0 | 6.615 | 3.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 3.53 | 0 | 120 | 3.53 | 0 | 6.615 | 3.085
| Nom. Capacity LV, MVA | 6,3+16 | 2.56 | 0.38 | 120 | 2.18 | 0 | 6.615 | 4.435 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.152 | 2.712 | 0.38 | 120 | 2.332 | 0 | 6.615 | 4.283
131 | Palkino 35/10 kv | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened | 131 | Palkino 35/10 kv | 2,5+4 | 0.049 | 0.749 | 0.45 | 120 | 0.299 | 0 | 2.625 | 2.326 | 2.326 | opened
132 | Slovinka 35/10 kv | 1,6+1,6 | 0.11 | 0.1 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 132 | Slovinka 35/10 kv | 1,6+1,6 | 0.006 | 0.116 | 0.1 | 120 | 0.016 | 0 | 1.68 | 1.664 | 1.664 | opened
133 | Kady 110/35/10 kv | 10+10 | 3.48 | 0.69 | 120 | 2.79 | 0 | 10.5 | 7.71 | 7.71 | opened | 133 | Kady 110/35/10 kv | 10+10 | 0.277 | 3.757 | 0.69 | 120 | 3.067 | 0 | 10.5 | 7.433 | 7.433 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.23 | 0 | 120 | 1.23 | 0 | 10.5 | 9.27 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.23 | 0 | 120 | 1.23 | 0 | 10.5 | 9.27
| Nom. Capacity LV, MVA | 10+10 | 2.25 | 0.69 | 120 | 1.56 | 0 | 10.5 | 8.94 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.277 | 2.527 | 0.69 | 120 | 1.837 | 0 | 10.5 | 8.663
134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | opened | 134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.006 | 0.096 | 0.1 | 120 | -0.004 | 0 | 1.68 | 1.684 | 1.684 | opened
135 | Ilyinskoe 110/35/10 kv | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | opened | 135 | Ilyinskoe 110/35/10 kv | 10+10 | 0 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43
136 | Kologriv 35/10 kv | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | opened | 136 | Kologriv 35/10 kv | 4+4 | 0.191 | 2.311 | 1.42 | 120 | 0.891 | 0 | 4.2 | 3.309 | 3.309 | opened
137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.23 | 0.08 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.011 | 0.241 | 0.08 | 120 | 0.161 | 0 | 1.68 | 1.519 | 1.519 | opened
138 | Makaryev-1 110/35/10 kv | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | opened | 138 | Makaryev-1 110/35/10 kv | 10+10 | 0.038 | 7.578 | 0.8 | 120 | 6.778 | 0 | 10.5 | 3.722 | 3.722 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.038 | 2.218 | 0.8 | 120 | 1.418 | 0 | 10.5 | 9.082
139 | Gorchukha 35/10 kv | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened | 139 | Gorchukha 35/10 kv | 2,5+2,5 | 0.03 | 1.22 | 0 | 0 | 1.22 | 0 | 2.625 | 1.405 | 1.405 | opened
140 | Makaryev-2 35/10 kv | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened | 140 | Makaryev-2 35/10 kv | 4+4 | 0.128 | 3.128 | 1.58 | 120 | 1.548 | 0 | 4.2 | 2.652 | 2.652 | opened
141 | Timoshino 35/10 kv | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | opened | 141 | Timoshino 35/10 kv | 1+1 | 0.077 | 0.257 | 0 | 0 | 0.257 | 0 | 1.05 | 0.793 | 0.793 | opened
142 | Unzha 35/10 kv | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | opened | 142 | Unzha 35/10 kv | 1+1,6 | 0 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | opened
143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.12 | 0.32 | 120 | -0.2 | 0 | 1.68 | 1.88 | 1.88 | opened | 143 | Yakimovo 35/10 kv | 1,6+2,5 | 0 | 0.12 | 0.32 | 120 | -0.2 | 0 | 1.68 | 1.88 | 1.88 | opened
144 | BKhZ 110/6 kv | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | opened | 144 | BKhZ 110/6 kv | 25+25 | 0.157 | 2.737 | 0 | 0 | 2.737 | 0 | 26.25 | 23.513 | 23.513 | opened
145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.095 | 0.535 | 0.15 | 120 | 0.385 | 0 | 1.68 | 1.295 | 1.295 | opened
146 | Georgievskoe 35/10 kv | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 146 | Georgievskoe 35/10 kv | 2,5+2,5 | 0.11 | 2.26 | 1.23 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened
147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | opened | 147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 0.568 | 16.618 | 3.6 | 120 | 13.018 | 0 | 48.615 | 35.597 | 35.597 | opened
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.568 | 8.088 | 3.6 | 120 | 4.488 | 0 | 48.615 | 44.127
148 | Vozherovo 35/10 kv | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 148 | Vozherovo 35/10 kv | 1,6+1,6 | 0 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
149 | Matveevo 35/10 kv | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 149 | Matveevo 35/10 kv | 1,8+4 | 0.027 | 0.537 | 0.42 | 120 | 0.117 | 0 | 1.89 | 1.773 | 1.773 | opened
150 | Parfenyevo 35/10 kv | 4+4 | 2.32 | 1.89 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened | 150 | Parfenyevo 35/10 kv | 4+4 | 0.102 | 2.422 | 1.89 | 120 | 0.532 | 0 | 4.2 | 3.668 | 3.668 | opened
151 | Vokhma 110/35/10 kv | 6,3+16 | 5.42 | 0 | 0 | 5.42 | 0 | 6.615 | 1.195 | 1.195 | opened | 151 | Vokhma 110/35/10 kv | 6,3+16 | 0.146 | 5.566 | 0 | 0 | 5.566 | 0 | 6.615 | 1.049 | 1.049 | opened
| Nom. Capacity MV, MVA | 6,3+8 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+8 | 0 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085
| Nom. Capacity LV, MVA | 6,3+8 | 3.89 | 0 | 0 | 3.89 | 0 | 6.615 | 2.725 |  |  |  | Nom. Capacity LV, MVA | 6,3+8 | 0.146 | 4.036 | 0 | 0 | 4.036 | 0 | 6.615 | 2.579
152 | Lapshino 35/10 kv | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 152 | Lapshino 35/10 kv | 2,5+2,5 | 0 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
153 | Spass 35/10 kv | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 153 | Spass 35/10 kv | 1,6+2,5 | 0 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
154 | Bogovarovo 35/10 kv | 2,5+4 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 154 | Bogovarovo 35/10 kv | 2,5+4 | 0.098 | 1.688 | 1 | 120 | 0.688 | 0 | 2.625 | 1.937 | 1.937 | opened
155 | Pavino 110/35/10 kv | 10+6,3 | 1.69 | 0 | 0 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | opened | 155 | Pavino 110/35/10 kv | 10+6,3 | 0.054 | 1.744 | 0 | 0 | 1.744 | 0 | 6.615 | 4.871 | 4.871 | opened
| Nom. Capacity MV, MVA | 10+6,3 | 0.18 | 0 | 0 | 0.18 | 0 | 6.615 | 6.435 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.18 | 0 | 0 | 0.18 | 0 | 6.615 | 6.435
| Nom. Capacity LV, MVA | 10+6,3 | 1.51 | 0 | 0 | 1.51 | 0 | 6.615 | 5.105 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.054 | 1.564 | 0 | 0 | 1.564 | 0 | 6.615 | 5.051
156 | Ledengskaya 35/10 kv | 1,6+4 | 0.07 | 0.07 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 156 | Ledengskaya 35/10 kv | 1,6+4 | 0.011 | 0.081 | 0.07 | 120 | 0.011 | 0 | 1.68 | 1.669 | 1.669 | opened
157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | opened | 157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 0.187 | 2.607 | 0 | 0 | 2.607 | 0 | 6.615 | 4.008 | 4.008 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.187 | 2.487 | 0 | 0 | 2.487 | 0 | 6.615 | 4.128
158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened | 158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 0.111 | 1.881 | 0.75 | 120 | 1.131 | 0 | 4.2 | 3.069 | 3.069 | opened
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.111 | 1.191 | 0.75 | 120 | 0.441 | 0 | 4.2 | 3.759
159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.25 | 0.27 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened | 159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.01 | 0.26 | 0.27 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | opened
160 | Sharya (r) 110/35/6 kv | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | opened | 160 | Sharya (r) 110/35/6 kv | 20+25 | 0.346 | 19.366 | 2 | 120 | 17.366 | 0 | 21 | 3.634 | 3.634 | opened
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.346 | 7.166 | 2 | 120 | 5.166 | 0 | 21 | 15.834
161 | Industrial hub 110/6/6 kv | 25+25 | 3.32 | 2.5 | 120 | 0.82 | 0 | 26.25 | 25.43 | 25.43 | opened | 161 | Industrial hub 110/6/6 kv | 25+25 | 0.025 | 3.345 | 2.5 | 120 | 0.845 | 0 | 26.25 | 25.405 | 25.405 | opened
162 | Krivyachka 35/10 kv | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | opened | 162 | Krivyachka 35/10 kv | 1,6+1 | 0.01 | 0.83 | 0.57 | 120 | 0.26 | 0 | 1.05 | 0.79 | 0.79 | opened
163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.78 | 0 | 0 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.109 | 0.889 | 0 | 0 | 0.889 | 0 | 1.68 | 0.791 | 0.791 | opened
164 | Tsentralnaya 35/6 kv | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | opened | 164 | Tsentralnaya 35/6 kv | 10+10 | 1.262 | 10.222 | 3 | 120 | 7.222 | 0 | 10.5 | 3.278 | 3.278 | opened
| Total over Kostromaenergo | 1705 | 401.12 | [8 empty] | 2: Total over Kostromaenergo; 3: 1705; 5: 488.241
| deficit | [8 empty] | -6.235 |  | 2: deficit; Min. 12: -13.125
| proficit | [8 empty] | 525.81 |  | 2: proficit; Min. 12: 445.634

## Воронежэнерго
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note |  | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity MVA | Current deficit/ proficit, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main substation, MVA | Expected dificit / proficit, MVA
|  |  | MVA | МVА | Мin. | [12 empty] | МVА | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [12 empty] | 1: One-transformer substations
| Power supply system | [11 empty] | 2: Power supply system
1 | No. 44 | 10 | 0.021 | 0 | 0 | 0 | 0 | 0 | -0.021 | -0.021 |  |  | 1 | No. 44 | 10 | 2.07 | 2.091 | 0 | 0 | 2.091 | 0 | 0 | -2.091 | -2.091 | 110/6
2 | No. 7 | 2.5 | 0.483 | 3.5 | 0 | 3.5 | 0 | 3.5 | 3.017 | 3.017 |  |  | 2 | No. 7 | 2.5 | 3.49 | 3.973 | 3.5 | 0 | 0.473 | 0 | 3.5 | -0.473 | -0.473 | 35/6
3 | Stupino | 6.3 | 0.953 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.0845 | 0.0845 |  |  | 3 | Stupino | 6.3 | 0.06 | 1.013 | 1.0375 | 120 | -0.0245 | 0 | 1.0375 | 0.0245 | 0.0245 | 110/10
4 | P.Kommuna | 6.3 | 0.455 | 0.5 | 120 | 0.5 | 0 | 0.5 | 0.045 | 0.045 |  |  | 4 | P.Kommuna | 6.3 | 0 | 0.455 | 0.5 | 120 | -0.045 | 0 | 0.5 | 0.045 | 0.045 | 110/10
5 | No. 38 | 2.5 | 0.327 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.473 | 0.473 |  |  | 5 | No. 38 | 2.5 | 0 | 0.327 | 0.8 | 120 | -0.473 | 0 | 0.8 | 0.473 | 0.473 | 35/10
6 | No. 46 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6 | No. 46 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35/6
7 | Istobnoe | 4 | 0.342 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.018 | 0.018 |  |  | 7 | Istobnoe | 4 | 0.01 | 0.352 | 0.36 | 120 | -0.008 | 0 | 0.36 | 0.008 | 0.008 | 35/10
8 | Rodina | 2.5 | 0.549 | 2.2 | 120 | 2.2 | 0 | 2.2 | 1.651 | 1.651 |  |  | 8 | Rodina | 2.5 | 1.63 | 2.179 | 2.2 | 120 | -0.021 | 0 | 2.2 | 0.021 | 0.021 | 35/10
9 | Vyaznovatovka | 2.5 | 0.352 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.148 | 1.148 |  |  | 9 | Vyaznovatovka | 2.5 | 1.02 | 1.372 | 1.5 | 120 | -0.128 | 0 | 1.5 | 0.128 | 0.128 | 35/10
10 | V.Turovo-1 | 3.2 | 0.927 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.473 | 0.473 |  |  | 10 | V.Turovo-1 | 3.2 | 0.02 | 0.947 | 1.4 | 120 | -0.453 | 0 | 1.4 | 0.453 | 0.453 | 35/10
11 | Semidesyatnoe | 2.5 | 0.69 | 0 | 0 | 0 | 0 | 0 | -0.69 | -0.69 |  |  | 11 | Semidesyatnoe | 2.5 | 0.07 | 0.76 | 0 | 0 | 0.76 | 0 | 0 | -0.76 | -0.76 | 35/10
12 | Arkhangelskoe SPS | 2.5 | 0.872 | 0 | 0 | 0 | 0 | 0 | -0.872 | -0.872 |  |  | 12 | Arkhangelskoe SPS | 2.5 | 0.07 | 0.942 | 0 | 0 | 0.942 | 0 | 0 | -0.942 | -0.942 | 35/10
13 | Khokhol-2 | 2.5 | 1.362 | 0 | 0 | 0 | 0 | 0 | -1.362 | -1.362 |  |  | 13 | Khokhol-2 | 2.5 | 0.11 | 1.472 | 0 | 0 | 1.472 | 0 | 0 | -1.472 | -1.472 | 35/10
14 | N.Olshanka | 4 | 0.697 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | 0.0604 | 0.0604 |  |  | 14 | N.Olshanka | 4 | 0.03 | 0.727 | 0.7574 | 120 | -0.0304 | 0 | 0.7574 | 0.0304 | 0.0304 | 35/10
15 | Troitskoe | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 |  |  | 15 | Troitskoe | 2.5 | 0.01 | 0.43 | 0 | 0 | 0.43 | 0 | 0 | -0.43 | -0.43 | 35/10
16 | Zemlyansk | 4 | 1.007 | 0 | 0 | 0 | 0 | 0 | -1.007 | -1.007 |  |  | 16 | Zemlyansk | 4 | 0.01 | 1.017 | 0 | 0 | 1.017 | 0 | 0 | -1.017 | -1.017 | 35/10
17 | Losevo SPS | 2.5 | 0.708 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.2456 | 0.2456 |  |  | 17 | Losevo SPS | 2.5 | 0 | 0.708 | 0.9536 | 120 | -0.2456 | 0 | 0.9536 | 0.2456 | 0.2456 | 35/10
18 | Verny | 2.5 | 2.089 | 2.15 | 120 | 2.15 | 0 | 2.15 | 0.061 | 0.061 |  |  | 18 | Verny | 2.5 | 0.04 | 2.129 | 2.15 | 120 | -0.021 | 0 | 2.15 | 0.021 | 0.021 | 35/10
19 | Elevator | 2.5 | 1 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.1 | 0.1 |  |  | 19 | Elevator | 2.5 | 0.03 | 1.03 | 1.1 | 120 | -0.07 | 0 | 1.1 | 0.07 | 0.07 | 35/10
20 | Yubileynaya | 4 | 0.999 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.601 | 0.601 |  |  | 20 | Yubileynaya | 4 | 0.07 | 1.069 | 1.6 | 120 | -0.531 | 0 | 1.6 | 0.531 | 0.531 | 35/10
21 | Parusnoe | 4 | 2.672 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.4864 | 0.4864 |  |  | 21 | Parusnoe | 4 | 0.05 | 2.722 | 3.1584 | 120 | -0.4364 | 0 | 3.1584 | 0.4364 | 0.4364 | 35/10
22 | Rogachyovka | 4 | 1.958 | 2.05 | 120 | 2.05 | 0 | 2.05 | 0.092 | 0.092 |  |  | 22 | Rogachyovka | 4 | 0.05 | 2.008 | 2.05 | 120 | -0.042 | 0 | 2.05 | 0.042 | 0.042 | 35/10
23 | Poultry farm Rassvet | 2.5 | 0.262 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.038 | 0.038 |  |  | 23 | Poultry farm Rassvet | 2.5 | 0 | 0.262 | 0.3 | 120 | -0.038 | 0 | 0.3 | 0.038 | 0.038 | 35/10
24 | Dankovo | 2.5 | 0.641 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.258 | 0.258 |  |  | 24 | Dankovo | 2.5 | 0.02 | 0.661 | 0.899 | 120 | -0.238 | 0 | 0.899 | 0.238 | 0.238 | 35/10
25 | Bugaevka | 16 | 7.04 | 14 | 90 | 14 | 0 | 14 | 6.96 | 1.86 |  |  | 25 | Bugaevka | 16 | 0.2 | 7.24 | 14 | 90 | -6.76 | 0 | 14 | 6.76 | 1.66
| Sн. MV, МVА | 16 | 4.9 | 10 | 90 | 10 | 0 | 10 | 5.1 |  |  |  |  | Sн. MV, МVА | 16 | 0 | 4.9 | 10 | 90 | -5.1 | 0 | 10 | 5.1 |  | 110/35/10
| Sн. LV, МVА | 16 | 2.14 | 4 | 90 | 4 | 0 | 4 | 1.86 |  |  |  |  | Sн. LV, МVА | 16 | 0.2 | 2.34 | 4 | 90 | -1.66 | 0 | 4 | 1.66
26 | Dobrino | 10 | 1.22 | 6.6 | 90 | 6.6 | 0 | 6.6 | 5.38 | 1.96 |  |  | 26 | Dobrino | 10 | 0.13 | 1.35 | 6.6 | 90 | -5.25 | 0 | 6.6 | 5.25 | 1.83
| Sн. MV, МVА | 10 | 0.06 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.74 |  |  |  |  | Sн. MV, МVА | 10 | 0 | 0.06 | 5.8 | 90 | -5.74 | 0 | 5.8 | 5.74 |  | 110/35/10
| Sн. LV, МVА | 10 | 1.16 | 3.12 | 90 | 3.12 | 0 | 3.12 | 1.96 |  |  |  |  | Sн. LV, МVА | 10 | 0.13 | 1.29 | 3.12 | 90 | -1.83 | 0 | 3.12 | 1.83
27 | N. Kalitva | 6.3 | 1.64 | 2 | 240 | 2 | 0 | 2 | 0.36 | 0.36 |  |  | 27 | N. Kalitva | 6.3 | 0.28 | 1.92 | 2 | 240 | -0.08 | 0 | 2 | 0.08 | 0.08 | 110/10
28 | Shishovka | 6.3 | 0.64 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.7 | 1.7 |  |  | 28 | Shishovka | 6.3 | 0.25 | 0.89 | 2.34 | 180 | -1.45 | 0 | 2.34 | 1.45 | 1.45 | 110/10
29 | Azovka | 10 | 1.51 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.61 | 1.61 |  |  | 29 | Azovka | 10 | 1.2 | 2.71 | 3.12 | 180 | -0.41 | 0 | 3.12 | 0.41 | 0.41 | 110/10
30 | Yurasovka | 2.5 | 0.63 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.93 | 0.93 |  |  | 30 | Yurasovka | 2.5 | 0.02 | 0.65 | 1.56 | 120 | -0.91 | 0 | 1.56 | 0.91 | 0.91 | 35/10
31 | Nerovnovka | 2.5 | 0.29 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.49 | 0.49 |  |  | 31 | Nerovnovka | 2.5 | 0.02 | 0.31 | 0.78 | 240 | -0.47 | 0 | 0.78 | 0.47 | 0.47 | 35/10
32 | Saprino | 1.8 | 0.3 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.5 | 1.5 |  |  | 32 | Saprino | 1.8 | 0.01 | 0.31 | 1.8 | 120 | -1.49 | 0 | 1.8 | 1.49 | 1.49 | 35/10
33 | Sergeevka | 4 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 |  |  | 33 | Sergeevka | 4 | 0.06 | 0.41 | 0 | 0 | 0.41 | 0 | 0 | -0.41 | -0.41 | 35/10
34 | Stepanovka | 4 | 0.3 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.26 | 1.26 |  |  | 34 | Stepanovka | 4 | 0.02 | 0.32 | 1.56 | 240 | -1.24 | 0 | 1.56 | 1.24 | 1.24 | 35/10
35 | Kolodezhanskaya | 2.5 | 0.29 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.49 | 0.49 |  |  | 35 | Kolodezhanskaya | 2.5 | 0.05 | 0.34 | 0.78 | 180 | -0.44 | 0 | 0.78 | 0.44 | 0.44 | 35/10
36 | Andreevka | 2.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.1 |  |  | 36 | Andreevka | 2.5 | 0.02 | 0.12 | 0 | 0 | 0.12 | 0 | 0 | -0.12 | -0.12 | 35/10
37 | Kulikovka | 4 | 1.63 | 0 | 0 | 0 | 0 | 0 | -1.63 | -1.63 |  |  | 37 | Kulikovka | 4 | 0.23 | 1.86 | 0 | 0 | 1.86 | 0 | 0 | -1.86 | -1.86 | 35/10
38 | Lizinovka | 2.5 | 0.94 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.56 | 1.56 |  |  | 38 | Lizinovka | 2.5 | 0.05 | 0.99 | 2.5 | 240 | -1.51 | 0 | 2.5 | 1.51 | 1.51 | 35/10
39 | Sotnitskaya | 4 | 1.54 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.76 | 0.76 |  |  | 39 | Sotnitskaya | 4 | 0.04 | 1.58 | 2.3 | 120 | -0.72 | 0 | 2.3 | 0.72 | 0.72 | 35/10
40 | Kr. Polyana | 2.5 | 0.32 | 0 | 0 | 0 | 0 | 0 | -0.32 | -0.32 |  |  | 40 | Kr. Polyana | 2.5 | 0.04 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | -0.36 | -0.36 | 35/10
41 | Gumny | 4 | 0.83 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.73 | 0.73 |  |  | 41 | Gumny | 4 | 0.09 | 0.92 | 1.56 | 180 | -0.64 | 0 | 1.56 | 0.64 | 0.64 | 35/10
42 | Uryv | 2.5 | 0.71 | 0 | 0 | 0 | 0 | 0 | -0.71 | -0.71 |  |  | 42 | Uryv | 2.5 | 0.05 | 0.76 | 0 | 0 | 0.76 | 0 | 0 | -0.76 | -0.76 | 35/10
43 | Shubnoe | 2.5 | 0.82 | 1.17 | 180 | 1.17 | 0 | 1.17 | 0.35 | 0.35 |  |  | 43 | Shubnoe | 2.5 | 0.11 | 0.93 | 1.17 | 180 | -0.24 | 0 | 1.17 | 0.24 | 0.24 | 35/10
44 | Zaluzhnoe | 2.5 | 1.61 | 2 | 240 | 2 | 0 | 2 | 0.39 | 0.39 |  |  | 44 | Zaluzhnoe | 2.5 | 0.36 | 1.97 | 2 | 240 | -0.03 | 0 | 2 | 0.03 | 0.03 | 35/10
46 | Anna-2 | 25 | 5.8 | 7.8 | 90 | 7.8 | 0 | 7.8 | 2 | 0.55 |  |  | 45 | Anna-2 | 25 | 0.03 | 5.83 | 7.8 | 90 | -1.97 | 0 | 7.8 | 1.97 | 0.55
| Sн. MV, МVА | 25 | 1.69 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.55 |  |  |  |  | Sн. MV, МVА | 25 | 0 | 1.69 | 2.24 | 90 | -0.55 | 0 | 2.24 | 0.55 |  | 110/35/10
| Sн. LV, МVА | 25 | 4.11 | 5.56 | 90 | 5.56 | 0 | 5.56 | 1.45 |  |  |  |  | Sн. LV, МVА | 25 | 0.03 | 4.14 | 5.56 | 90 | -1.42 | 0 | 5.56 | 1.42
47 | Vostochnaya | 10 | 3.42 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.38 | 1.38 |  |  | 46 | Vostochnaya | 10 | 0.93 | 4.35 | 4.8 | 30 | -0.45 | 0 | 4.8 | 0.45 | 0.45 | 35/6
48 | BolshevikBPS | 6.3 | 1.17 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.29 | 0.29 |  |  | 47 | BolshevikBPS | 6.3 | 0.01 | 1.18 | 1.46 | 60 | -0.28 | 0 | 1.46 | 0.28 | 0.28 | 110/10
49 | Rozhdestvo | 6.3 | 0.7 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.05 | 0.05 |  |  | 48 | Rozhdestvo | 6.3 | 0.02 | 0.72 | 0.75 | 60 | -0.03 | 0 | 0.75 | 0.03 | 0.03 | 110/10
50 | V. Toyda | 6.3 | 0.96 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.44 | 0.44 |  |  | 49 | V. Toyda | 6.3 | 0.01 | 0.97 | 1.4 | 90 | -0.43 | 0 | 1.4 | 0.43 | 0.43 | 110/10
51 | Vostochnaya-1 | 40 | 7.13 | 8.13 | 60 | 8.13 | 0 | 8.13 | 1 | 0.58 |  |  | 50 | Vostochnaya-1 | 40 | 0.92 | 8.05 | 8.13 | 60 | -0.08 | 0 | 8.13 | 0.08 | 0.08
| Sн. MV, МVА | 40 | 5.09 | 5.67 | 60 | 5.67 | 0 | 5.67 | 0.58 |  |  |  |  | Sн. MV, МVА | 40 | 0 | 5.09 | 5.67 | 60 | -0.58 | 0 | 5.67 | 0.58 |  | 110/35/6
| Sн. LV, МVА | 40 | 2.04 | 3.1 | 60 | 3.1 | 0 | 3.1 | 1.06 |  |  |  |  | Sн. LV, МVА | 40 | 0.92 | 2.96 | 3.1 | 60 | -0.14 | 0 | 3.1 | 0.14
52 | Makashevka | 2.5 | 0.34 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.14 | 0.14 |  |  | 51 | Makashevka | 2.5 | 0.02 | 0.36 | 0.48 | 180 | -0.12 | 0 | 0.48 | 0.12 | 0.12 | 35/10
53 | Mirolyubie | 4 | 0.4 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.1 | 0.1 |  |  | 52 | Mirolyubie | 4 | 0 | 0.4 | 0.5 | 60 | -0.1 | 0 | 0.5 | 0.1 | 0.1 | 35/10
54 | V. Zaton | 2.5 | 0 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0.01 | 0.01 |  |  | 53 | V. Zaton | 2.5 | 0 | 0 | 0.01 | 60 | -0.01 | 0 | 0.01 | 0.01 | 0.01 | 35/10
55 | Oktyabrskoe | 2.5 | 0.46 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.21 | 0.21 |  |  | 54 | Oktyabrskoe | 2.5 | 0.03 | 0.49 | 0.67 | 30 | -0.18 | 0 | 0.67 | 0.18 | 0.18 | 35/10
56 | Ilmen | 2.5 | 0.26 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.12 | 0.12 |  |  | 55 | Ilmen | 2.5 | 0.01 | 0.27 | 0.38 | 60 | -0.11 | 0 | 0.38 | 0.11 | 0.11 | 35/10
57 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 |  |  | 56 | Vikhlyaevka | 2.5 | 0 | 0.1 | 0.12 | 120 | -0.02 | 0 | 0.12 | 0.02 | 0.02 | 35/10
58 | N. Elan | 2.5 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 | -0.51 |  |  | 57 | N. Elan | 2.5 | 0 | 0.51 | 0 | 0 | 0.51 | 0 | 0 | -0.51 | -0.51 | 35/10
59 | B. Alabukhi | 2.5 | 0.77 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.16 | 0.16 |  |  | 58 | B. Alabukhi | 2.5 | 0.04 | 0.81 | 0.93 | 90 | -0.12 | 0 | 0.93 | 0.12 | 0.12 | 35/10
60 | Pykhovka | 2.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 |  |  | 59 | Pykhovka | 2.5 | 0 | 0.35 | 0 | 0 | 0.35 | 0 | 0 | -0.35 | -0.35 | 35/10
61 | Е. Koleno | 4 | 2.48 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.85 | 0.85 |  |  | 60 | Е. Koleno | 4 | 0.03 | 2.51 | 3.33 | 120 | -0.82 | 0 | 3.33 | 0.82 | 0.82 | 35/10
62 | Podgornoe BPS | 2.5 | 0.35 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.11 | 0.11 |  |  | 61 | Podgornoe BPS | 2.5 | 0.01 | 0.36 | 0.46 | 180 | -0.1 | 0 | 0.46 | 0.1 | 0.1 | 35/10
63 | Mikhailovka-1 | 4 | 0.2 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.16 | 0.16 |  |  | 62 | Mikhailovka-1 | 4 | 0 | 0.2 | 0.36 | 60 | -0.16 | 0 | 0.36 | 0.16 | 0.16 | 35/10
64 | Mikhailovka | 2.5 | 0.32 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.18 | 0.18 |  |  | 63 | Mikhailovka | 2.5 | 0.01 | 0.33 | 0.5 | 60 | -0.17 | 0 | 0.5 | 0.17 | 0.17 | 35/10
65 | Gnilusha | 4 | 0.72 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.2 | 0.2 |  |  | 64 | Gnilusha | 4 | 0 | 0.72 | 0.92 | 180 | -0.2 | 0 | 0.92 | 0.2 | 0.2 | 35/10
66 | Mayskaya | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | -0.6 | -0.6 |  |  | 65 | Mayskaya | 2.5 | 0 | 0.6 | 0 | 0 | 0.6 | 0 | 0 | -0.6 | -0.6 | 35/10
67 | Khleborodnoe | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 |  |  | 66 | Khleborodnoe | 2.5 | 0.02 | 0.44 | 0 | 0 | 0.44 | 0 | 0 | -0.44 | -0.44 | 35/10
68 | N. Kurlak | 4 | 0.49 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.11 | 0.11 |  |  | 67 | N. Kurlak | 4 | 0 | 0.49 | 0.6 | 120 | -0.11 | 0 | 0.6 | 0.11 | 0.11 | 35/10
69 | Nikolaevka | 4 | 0.48 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.02 | 1.02 |  |  | 68 | Nikolaevka | 4 | 0 | 0.48 | 1.5 | 120 | -1.02 | 0 | 1.5 | 1.02 | 1.02 | 35/10
70 | Vasilyevka BPS | 2.5 | 0.37 | 0.39 | 180 | 0.39 | 0 | 0.39 | 0.02 | 0.02 |  |  | 69 | Vasilyevka BPS | 2.5 | 0.02 | 0.39 | 0.39 | 180 | 0 | 0 | 0.39 | 0 | 0 | 35/10
71 | Avangard | 2.5 | 0.7 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.21 | 0.21 |  |  | 70 | Avangard | 2.5 | 0.01 | 0.71 | 0.91 | 120 | -0.2 | 0 | 0.91 | 0.2 | 0.2 | 35/10
72 | Orlovka | 2.5 | 0.4 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.08 | 0.08 |  |  | 71 | Orlovka | 2.5 | 0 | 0.4 | 0.48 | 90 | -0.08 | 0 | 0.48 | 0.08 | 0.08 | 35/10
73 | N. Chigla | 2.5 | 0.6 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.3 | 0.3 |  |  | 72 | N. Chigla | 2.5 | 0.15 | 0.75 | 0.9 | 120 | -0.15 | 0 | 0.9 | 0.15 | 0.15 | 35/10
74 | Troitskoe-1 | 1.6 | 0.1 | 0.11 | 120 | 0.11 | 0 | 0.11 | 0.01 | 0.01 |  |  | 73 | Troitskoe-1 | 1.6 | 0 | 0.1 | 0.11 | 120 | -0.01 | 0 | 0.11 | 0.01 | 0.01 | 35/10
75 | Tishanka | 2.5 | 1.1 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.41 | 0.41 |  |  | 74 | Tishanka | 2.5 | 0.03 | 1.13 | 1.51 | 120 | -0.38 | 0 | 1.51 | 0.38 | 0.38 | 35/10
76 | Kalacheevskaya | 6.3 | 0.62 | 1 | 24 hours | 1 | 0 | 1 | 0.38 | 0.38 |  |  | 75 | Kalacheevskaya | 6.3 | 0 | 0.62 | 1 | 24 hours | -0.38 | 0 | 1 | 0.38 | 0.38 | 110/10
77 | B.Kazinka | 6.3 | 0.47 | 0 | 0 | 0 | 0 | 0 | -0.47 | -0.47 |  |  | 76 | B.Kazinka | 6.3 | 3.09 | 3.56 | 0 | 0 | 3.56 | 0 | 0 | -3.56 | -3.56
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110/35/10
| Sн. LV, МVА | 6.3 | 0.47 | 0 | 0 | 0 | 0 | 0 | -0.47 |  |  |  |  | Sн. LV, МVА | 6.3 | 3.09 | 3.56 | 0 | 0 | 3.56 | 0 | 0 | -3.56
78 | Derezovka | 6.3 | 0.33 | 0 | 0 | 0 | 0 | 0 | -0.33 | -0.33 |  |  | 77 | Derezovka | 6.3 | 0.07 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | -0.4 | -0.4 | 110/10
79 | Osetrovka | 6.3 | 0.35 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.15 | 1.15 |  |  | 78 | Osetrovka | 6.3 | 2.21 | 2.56 | 1.5 | 24 hours | 1.06 | 0 | 1.5 | -1.06 | -1.06 | 110/10
80 | sovkhoz Radchensky | 10 | 1.27 | 2 | 24 hours | 2 | 0 | 2 | 0.73 | -1.13 |  |  | 79 | sovkhoz Radchensky | 10 | 0.01 | 1.28 | 2 | 24 hours | -0.72 | 0 | 2 | 0.72 | -1.13
| Sн. MV, МVА | 10 | 1.13 | 0 | 24 hours | 0 | 0 | 0 | -1.13 |  |  |  |  | Sн. MV, МVА | 10 | 0 | 1.13 | 0 | 0 | 1.13 | 0 | 0 | -1.13 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.14 | 2 | 24 hours | 2 | 0 | 2 | 1.86 |  |  |  |  | Sн. LV, МVА | 10 | 0.01 | 0.15 | 2 | 24 hours | -1.85 | 0 | 2 | 1.85
81 | Klepovka | 4 | 1.4 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.2 | 0.2 |  |  | 80 | Klepovka | 4 | 0.12 | 1.52 | 1.6 | 120 | -0.08 | 0 | 1.6 | 0.08 | 0.08 | 35/10
82 | Krasnopolye | 4 | 0.28 | 1 | 120 | 1 | 0 | 1 | 0.72 | 0.72 |  |  | 81 | Krasnopolye | 4 | 0.02 | 0.3 | 1 | 120 | -0.7 | 0 | 1 | 0.7 | 0.7 | 35/10
83 | Nikolskoe | 2.5 | 0.4 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.1 | 1.1 |  |  | 82 | Nikolskoe | 2.5 | 0 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
84 | N. Liman | 2.5 | 0.39 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.11 | 1.11 |  |  | 83 | N. Liman | 2.5 | 0.01 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
85 | Bereznyagi | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 |  |  | 84 | Bereznyagi | 2.5 | 0.03 | 0.33 | 1.5 | 45 | -1.17 | 0 | 1.5 | 1.17 | 1.17 | 35/10
86 | Kr.Flot | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 |  |  | 85 | Kr.Flot | 2.5 | 0.08 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
87 | R. Zhuravka | 2.5 | 0.77 | 0 | 0 | 0 | 0 | 0 | -0.77 | -0.77 |  |  | 86 | R. Zhuravka | 2.5 | 0.08 | 0.85 | 0 | 0 | 0.85 | 0 | 0 | -0.85 | -0.85 | 35/10
88 | Gorokhovka | 2.5 | 0.47 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.03 | 1.03 |  |  | 87 | Gorokhovka | 2.5 | 0.04 | 0.51 | 1.5 | 45 | -0.99 | 0 | 1.5 | 0.99 | 0.99 | 35/10
89 | Livenka | 2.5 | 0.45 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0.05 | 0.05 |  |  | 88 | Livenka | 2.5 | 0.05 | 0.5 | 0.5 | 24 hours | 0 | 0 | 0.5 | 0 | 0 | 35/10
90 | R.Buylovka | 2.5 | 0.49 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.01 | 1.01 |  |  | 89 | R.Buylovka | 2.5 | 0.05 | 0.54 | 1.5 | 45 | -0.96 | 0 | 1.5 | 0.96 | 0.96 | 35/10
91 | Shurinovka | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  | 90 | Shurinovka | 2.5 | 0 | 0.29 | 0 | 0 | 0.29 | 0 | 0 | -0.29 | -0.29 | 35/10
92 | Tvyordokhlebovka | 4 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 |  |  | 91 | Tvyordokhlebovka | 4 | 0.03 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | 35/10
93 | Krinitsa | 2.5 | 0.26 | 0 | 0 | 0 | 0 | 0 | -0.26 | -0.26 |  |  | 92 | Krinitsa | 2.5 | 0 | 0.26 | 0 | 0 | 0.26 | 0 | 0 | -0.26 | -0.26 | 35/10
94 | Krasnogorovka | 2.5 | 0.09 | 0 | 0 | 0 | 0 | 0 | -0.09 | -0.09 |  |  | 93 | Krasnogorovka | 2.5 | 0.01 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | 35/10
95 | No. 2 | 25+25 | 19.31 | 4.8 | 120 | 14.51 | 0 | 26.25 | 11.74 | 11.74 |  | 1.05 | 95 | No. 2 | 25+25 | 11.69 | 31 | 4.8 | 120 | 26.2 | 0 | 26.25 | 0.05 | 0.05 | 110/6
96 | No.3 | 6,3 + 10 | 9.426 | 2.5 | 120 | 6.926 | 0 | 6.615 | -0.311 | -0.311 |  | 1.05 | 96 | No.3 | 6,3 + 10 | 0.39 | 9.816 | 2.5 | 120 | 7.316 | 0 | 6.615 | -0.701 | -0.701 | 35/6
97 | No. 4 | 10+10+15 | 10.897 | 0 | 0 | 10.897 | 0 | 21 | 10.103 | 10.103 |  | 1.05 | 97 | No. 4 | 10+10+15 | 0 | 10.897 | 0 | 0 | 10.897 | 0 | 21 | 10.103 | 10.103 | 35/6
98 | No. 6 | 25+32 | 19.125 | 1.6 | 120 | 17.525 | 0 | 26.25 | 8.725 | 8.725 |  | 1.05 | 98 | No. 6 | 25+32 | 3.3 | 22.425 | 1.6 | 120 | 20.825 | 0 | 26.25 | 5.425 | 5.425 | 110/6
99 | No. 8 | 4+4+4 | 5.285 | 0 | 0 | 5.285 | 0 | 8.4 | 3.115 | 3.115 |  | 1.05 | 99 | No. 8 | 4+4+4 | 0.34 | 5.625 | 0 | 0 | 5.625 | 0 | 8.4 | 2.775 | 2.775 | 35/6
100 | No. 9 | 16+25 | 23.02 | 3.3 | 120 | 19.72 | 0 | 16.8 | -2.92 | -2.92 |  | 1.05 | 100 | No. 9 | 16+25 | 10.19 | 33.21 | 3.3 | 120 | 29.91 | 0 | 16.8 | -13.11 | -13.11 | 110/6
101 | No. 10 | 20+20 | 29.97 | 13.3 | 120 | 16.67 | 0 | 21 | 4.33 | 4.33 |  | 1.05 | 101 | No. 10 | 20+20 | 7.38 | 37.35 | 13.3 | 120 | 24.05 | 0 | 21 | -3.05 | -3.05 | 35/6
102 | No. 13 | 6,3+6,3 | 7.047 | 3.7 | 120 | 3.347 | 0 | 6.615 | 3.268 | 3.268 |  | 1.05 | 102 | No. 13 | 6,3+6,3 | 4.41 | 11.457 | 3.7 | 120 | 7.757 | 0 | 6.615 | -1.142 | -1.142 | 35/10
103 | No. 14 | 31,5+31,5 | 16.649 | 1.3 | 120 | 15.349 | 0 | 33.075 | 17.726 | 17.726 |  | 1.05 | 103 | No. 14 | 31,5+31,5 | 0.54 | 17.189 | 1.3 | 120 | 15.889 | 0 | 33.075 | 17.186 | 17.186
| Sн. MV, МVА | 31,5+31,5 | 2.811 | 0 | 0 | 2.811 | 0 | 33.075 | 30.264 |  |  | 1.05 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 2.811 | 0 | 0 | 2.811 | 0 | 33.075 | 30.264 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5 | 13.838 | 1.3 | 120 | 12.538 | 0 | 33.075 | 20.537 |  |  | 1.05 |  | Sн. LV, МVА | 31,5+31,5 | 0.54 | 14.378 | 1.3 | 120 | 13.078 | 0 | 33.075 | 19.997
104 | No. 15 | 40,5+40,5+63,0 | 29.92 | 44.01 | 120 | -14.09 | 0 | 85.05 | 99.14 | 85.05 |  | 1.05 | 104 | No. 15 | 40,5+40,5+63,0 | 0.59 | 30.51 | 44.01 | 120 | -13.5 | 0 | 85.05 | 98.55 | 84.46
| Sн. MV, МVА | 40,5+40,5+63,0 | 29.92 | 44.01 | 120 | -14.09 | 0 | 85.05 | 99.14 |  |  | 1.05 |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 29.92 | 44.01 | 120 | -14.09 | 0 | 85.05 | 99.14 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  | 1.05 |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0.59 | 0.59 | 0 | 0 | 0.59 | 0 | 85.05 | 84.46
105 | No. 16 | 31,5+31,5+40,0 | 54.651 | 4 | 120 | 50.651 | 0 | 66.15 | 15.499 | 15.499 |  | 1.05 | 105 | No. 16 | 31,5+31,5+40,0 | 7.41 | 62.061 | 4 | 120 | 58.061 | 0 | 66.15 | 8.089 | 8.089
| Sн. MV, МVА | 31,5+31,5 | 4.419 | 0 | 0 | 4.419 | 0 | 33.075 | 28.656 |  |  | 1.05 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 4.419 | 0 | 0 | 4.419 | 0 | 33.075 | 28.656 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5+40,0 | 50.232 | 4 | 120 | 46.232 | 0 | 66.15 | 19.918 |  |  | 1.05 |  | Sн. LV, МVА | 31,5+31,5+40,0 | 7.41 | 57.642 | 4 | 120 | 53.642 | 0 | 66.15 | 12.508
106 | No. 18 | 6,3+6,3 | 2.641 | 0 | 0 | 2.641 | 0 | 6.615 | 3.974 | 3.974 |  | 1.05 | 106 | No. 18 | 6,3+6,3 | 0.13 | 2.771 | 0 | 0 | 2.771 | 0 | 6.615 | 3.844 | 3.844 | 110/10
107 | No. 20 | 25,0+6,3+16 | 27.687 | 5.6 | 120 | 22.087 | 0 | 26.25 | 4.163 | -7.811 |  | 1.05 | 107 | No. 20 | 25,0+6,3+16 | 2.22 | 29.907 | 5.6 | 120 | 24.307 | 0 | 26.25 | 1.943 | -10.031
| Sн. MV, МVА | 25,0+16,0 | 7.661 | 0 | 0 | 7.661 | 0 | 26.25 | 18.589 |  |  | 1.05 |  | Sн. MV, МVА | 25+16 | 0 | 7.661 | 0 | 0 | 7.661 | 0 | 26.25 | 18.589 |  | 110/35/10/6
| Sн. LV, МVА | 25,0+6,3 | 20.026 | 5.6 | 120 | 14.426 | 0 | 6.615 | -7.811 |  |  | 1.05 |  | Sн. LV, МVА | 25+6,3 | 2.22 | 22.246 | 5.6 | 120 | 16.646 | 0 | 6.615 | -10.031
108 | No. 21 | 25,0+20,0+40,0 | 36.77 | 4.6 | 120 | 32.17 | 0 | 45 | 12.83 | 12.83 |  | 1.05 | 108 | No. 21 | 25,0+20,0+40,0 | 20.03 | 56.8 | 4.6 | 180 | 52.2 | 0 | 45 | -7.2 | -7.2 | 110/35/6
109 | No. 22 | 10+10 | 4.364 | 1.4 | 120 | 2.964 | 0 | 10.5 | 7.536 | 7.536 |  | 1.05 | 109 | No. 22 | 10+10 | 2.69 | 7.054 | 1.4 | 120 | 5.654 | 0 | 10.5 | 4.846 | 4.846 | 35/6
110 | No. 23 | 7,5+6,3 | 6.974 | 0.8 | 120 | 6.174 | 0 | 6.615 | 0.441 | 0.441 |  | 1.05 | 110 | No. 23 | 7,5+6,3 | 0.75 | 7.724 | 0.8 | 120 | 6.924 | 0 | 6.615 | -0.309 | -0.309 | 35/6
111 | No. 24 | 3,2+4,0 | 2.157 | 0 | 0 | 2.157 | 0 | 3.36 | 1.203 | 1.203 |  | 1.05 | 111 | No. 24 | 3,2+4,0 | 0.04 | 2.197 | 0 | 0 | 2.197 | 0 | 3.36 | 1.163 | 1.163 | 35/6
112 | No. 25 | 40+25 | 34.163 | 3.8 | 120 | 30.363 | 0 | 26.25 | -4.113 | -4.113 |  | 1.05 | 112 | No. 25 | 40+25 | 8.26 | 42.423 | 3.8 | 120 | 38.623 | 0 | 26.25 | -12.373 | -12.373 | 110/6
113 | No. 27 | 32,0+32,0+32,0 | 39.88 | 3.3 | 180 | 36.58 | 0 | 67.2 | 30.62 | 30.62 |  | 1.05 | 113 | No. 27 | 32,0+32,0+32,0 | 17.48 | 57.36 | 3.3 | 180 | 54.06 | 0 | 67.2 | 13.14 | 13.14 | 110/6
114 | No. 28 | 10+10 | 10.897 | 0 | 0 | 10.897 | 0 | 10.5 | -0.397 | -0.397 |  | 1.05 | 114 | No. 28 | 10+10 | 3.45 | 14.347 | 0 | 0 | 14.347 | 0 | 10.5 | -3.847 | -3.847 | 110/10
115 | No.29 | 25+25 | 27.462 | 8.4 | 120 | 19.062 | 0 | 26.25 | 7.188 | 7.188 |  | 1.05 | 115 | No.29 | 25+25 | 3.8 | 31.262 | 8.4 | 120 | 22.862 | 0 | 26.25 | 3.388 | 3.388
| Sн. MV, МVА | 25+25 | 10.862 | 4.2 | 120 | 6.662 | 0 | 26.25 | 19.588 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 10.862 | 4.2 | 120 | 6.662 | 0 | 26.25 | 19.588 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 16.606 | 4.2 | 120 | 12.406 | 0 | 26.25 | 13.844 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 3.8 | 20.406 | 4.2 | 120 | 16.206 | 0 | 26.25 | 10.044
116 | No. 30 | 40+40 | 71.691 | 5.1 | 120 | 66.591 | 0 | 42 | -24.591 | -24.591 |  | 1.05 | 116 | No. 30 | 40+40 | 16.72 | 88.411 | 5.1 | 120 | 83.311 | 0 | 42 | -41.311 | -41.311
| Sн. MV, МVА | 40+40 | 13.35 | 0 | 0 | 13.35 | 0 | 42 | 28.65 |  |  | 1.05 |  | Sн. MV, МVА | 40+40 | 0 | 13.35 | 0 | 0 | 13.35 | 0 | 42 | 28.65 |  | 110/35/10
| Sн. LV, МVА | 40+40 | 58.341 | 5.1 | 120 | 53.241 | 0 | 42 | -11.241 |  |  | 1.05 |  | Sн. LV, МVА | 40+40 | 16.72 | 75.061 | 5.1 | 120 | 69.961 | 0 | 42 | -27.961
117 | No. 32 | 10+16 | 19.754 | 8 | 120 | 11.754 | 0 | 10.5 | -1.254 | -1.254 |  | 1.05 | 117 | No. 32 | 10+16 | 0.96 | 20.714 | 8 | 120 | 12.714 | 0 | 10.5 | -2.214 | -2.214
| Sн. MV, МVА | 10+16 | 16.65 | 8 | 120 | 8.65 | 0 | 10.5 | 1.85 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 16.65 | 8 | 120 | 8.65 | 0 | 10.5 | 1.85 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 3.104 | 0 | 0 | 3.104 | 0 | 10.5 | 7.396 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.96 | 4.064 | 0 | 0 | 4.064 | 0 | 10.5 | 6.436
118 | No. 33 | 4,0+4,0 | 1.318 | 0 | 0 | 1.318 | 0 | 4.2 | 2.882 | 2.882 |  | 1.05 | 118 | No. 33 | 4,0+4,0 | 0.3 | 1.618 | 0 | 0 | 1.618 | 0 | 4.2 | 2.582 | 2.582 | 35/10
119 | No. 34 | 2,5+1,8 | 1.95 | 0 | 0 | 1.95 | 0 | 1.89 | -0.06 | -0.06 |  | 1.05 | 119 | No. 34 | 2,5+1,8 | 0 | 1.95 | 0 | 0 | 1.95 | 0 | 1.89 | -0.06 | -0.06 | 35/6
120 | No.35 | 10+10 | 14.045 | 2.4 | 120 | 11.645 | 0 | 10.5 | -1.145 | -1.145 |  | 1.05 | 120 | No.35 | 10+10 | 0 | 14.045 | 2.4 | 120 | 11.645 | 0 | 10.5 | -1.145 | -1.145 | 35/6
121 | No. 36 | 6,3+10 | 1.259 | 0 | 0 | 1.259 | 0 | 6.615 | 5.356 | 5.356 |  | 1.05 | 121 | No. 36 | 6,3+10 | 3.5 | 4.759 | 0 | 0 | 4.759 | 0 | 6.615 | 1.856 | 1.856 | 110/35/10
122 | No. 39 | 25+25 | 25.936 | 4.1 | 120 | 21.836 | 0 | 26.25 | 4.414 | 4.414 |  | 1.05 | 122 | No. 39 | 25+25 | 2.9 | 28.836 | 4.1 | 120 | 24.736 | 0 | 26.25 | 1.514 | 1.514 | 110/6
123 | No. 41 | 10+10 | 10.654 | 0 | 0 | 10.654 | 0 | 10.5 | -0.154 | -0.154 |  | 1.05 | 123 | No. 41 | 10+10 | 0 | 10.654 | 0 | 0 | 10.654 | 0 | 10.5 | -0.154 | -0.154 | 35/6
124 | No. 42 | 25+40 | 19.65 | 1.6 | 120 | 18.05 | 0 | 26.25 | 8.2 | 8.2 |  | 1.05 | 124 | No. 42 | 25+40 | 8.5 | 28.15 | 1.6 | 120 | 26.55 | 0 | 26.25 | -0.3 | -0.3 | 110/6
125 | No. 43 | 63+63 | 18.602 | 1.6 | 60 | 17.002 | 0 | 66.15 | 49.148 | 49.148 |  | 1.05 | 125 | No. 43 | 63+63 | 8.24 | 26.842 | 1.6 | 60 | 25.242 | 0 | 66.15 | 40.908 | 40.908 | 110/6
126 | No. 45 | 63+63 | 30.741 | 7.1 | 120 | 23.641 | 0 | 66.15 | 42.509 | 42.509 |  | 1.05 | 126 | No. 45 | 63+63 | 28.71 | 59.451 | 7.1 | 120 | 52.351 | 0 | 66.15 | 13.799 | 13.799 | 110/6
127 | No. 47 | 25+25 | 13.35 | 0 | 0 | 13.35 | 0 | 26.25 | 12.9 | 12.9 |  | 1.05 | 127 | No. 47 | 25+25 | 0.03 | 13.38 | 0 | 0 | 13.38 | 0 | 26.25 | 12.87 | 12.87
| Sн. MV, МVА | 25+25 | 7.04 | 0 | 0 | 7.04 | 0 | 26.25 | 19.21 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 7.04 | 0 | 0 | 7.04 | 0 | 26.25 | 19.21 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.31 | 0 | 0 | 6.31 | 0 | 26.25 | 19.94 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.03 | 6.34 | 0 | 0 | 6.34 | 0 | 26.25 | 19.91
128 | Panino | 16+16 | 12.431 | 5.2 | 120 | 7.231 | 0 | 16.8 | 9.569 | 9.569 |  | 1.05 | 128 | Panino | 16+16 | 0.22 | 12.651 | 5.2 | 120 | 7.451 | 0 | 16.8 | 9.349 | 9.349
| Sн. MV, МVА | 16+16 | 6.236 | 5 | 120 | 1.236 | 0 | 16.8 | 15.564 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 6.236 | 5 | 120 | 1.236 | 0 | 16.8 | 15.564 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 6.195 | 0.2 | 120 | 5.995 | 0 | 16.8 | 10.805 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.22 | 6.415 | 0.2 | 120 | 6.215 | 0 | 16.8 | 10.585
129 | Kriusha | 2,5+2,5 | 1.013 | 0 | 0 | 1.013 | 0 | 2.625 | 1.612 | 1.612 |  | 1.05 | 129 | Kriusha | 2,5+2,5 | 0.03 | 1.043 | 0 | 0 | 1.043 | 0 | 2.625 | 1.582 | 1.582 | 35/10
130 | Seed plant | 4+4 | 2.446 | 0 | 0 | 2.446 | 0 | 4.2 | 1.754 | 1.754 |  | 1.05 | 130 | Seed plant | 4+4 | 0.02 | 2.466 | 0 | 0 | 2.466 | 0 | 4.2 | 1.734 | 1.734 | 35/10
131 | Progress | 2,5+10 | 0.534 | 0.5315 | 120 | 0.0025 | 0 | 2.625 | 2.6225 | 2.6225 |  | 1.05 | 131 | Progress | 2,5+10 | 0.01 | 0.544 | 0.5315 | 120 | 0.0125 | 0 | 2.625 | 2.6125 | 2.6125 | 110/35/10
132 | Katukhovka | 2,5+2,5 | 0.784 | 0.385 | 120 | 0.399 | 0 | 2.625 | 2.226 | 2.226 |  | 1.05 | 132 | Katukhovka | 2,5+2,5 | 0.01 | 0.794 | 0.385 | 120 | 0.409 | 0 | 2.625 | 2.216 | 2.216 | 35/10
133 | Kr.Liman | 2,5+4,0 | 1.035 | 0 | 0 | 1.035 | 0 | 2.625 | 1.59 | 1.59 |  | 1.05 | 133 | Kr.Liman | 2,5+4,0 | 0.01 | 1.045 | 0 | 0 | 1.045 | 0 | 2.625 | 1.58 | 1.58 | 35/10
134 | Ivanovka | 1,8+1,6 | 0.327 | 0.36 | 120 | -0.033 | 0 | 1.68 | 1.713 | 1.713 |  | 1.05 | 134 | Ivanovka | 1,8+1,6 | 0 | 0.327 | 0.36 | 120 | -0.033 | 0 | 1.68 | 1.713 | 1.713 | 35/10
135 | Don | 2,5+2,5 | 2.96 | 0 | 0 | 2.96 | 0 | 2.625 | -0.335 | -0.335 |  | 1.05 | 135 | Don | 2,5+2,5 | 0.39 | 3.35 | 0 | 0 | 3.35 | 0 | 2.625 | -0.725 | -0.725 | 35/10
136 | Yablochnoe | 4+4 | 0.363 | 0 | 0 | 0.363 | 0 | 4.2 | 3.837 | 3.837 |  | 1.05 | 136 | Yablochnoe | 4+4 | 0.01 | 0.373 | 0 | 0 | 0.373 | 0 | 4.2 | 3.827 | 3.827 | 35/10
137 | St.Nikolskoe | 2,5+2,5 | 0.944 | 1.227 | 120 | -0.283 | 0 | 2.625 | 2.908 | 2.908 |  | 1.05 | 137 | St.Nikolskoe | 2,5+2,5 | 0.3 | 1.244 | 1.227 | 120 | 0.017 | 0 | 2.625 | 2.608 | 2.608 | 35/10
138 | Rudkino | 4,0+4,0 | 2.761 | 0 | 0 | 2.761 | 0 | 4.2 | 1.439 | 1.439 |  | 1.05 | 138 | Rudkino | 4,0+4,0 | 0.08 | 2.841 | 0 | 0 | 2.841 | 0 | 4.2 | 1.359 | 1.359 | 35/10
139 | Khokhol-1 | 6,3+6,3 | 5.449 | 0 | 0 | 5.449 | 0 | 6.615 | 1.166 | 1.166 |  | 1.05 | 139 | Khokhol-1 | 6,3+6,3 | 1.15 | 6.599 | 0 | 0 | 6.599 | 0 | 6.615 | 0.016 | 0.016 | 35/6
140 | No. 11 | 5,6+6,3 | 3.013 | 0.5 | 120 | 2.513 | 0 | 5.88 | 3.367 | 2.931 |  | 1.05 | 140 | No. 11 | 5,6+6,3 | 0 | 3.013 | 0.5 | 120 | 2.513 | 0 | 5.88 | 3.367 | 2.931
| Sн. MV, МVА | 5,6+6,3 | 0.064 | 0.5 | 120 | -0.436 | 0 | 5.88 | 6.316 |  |  | 1.05 |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.064 | 0.5 | 120 | -0.436 | 0 | 5.88 | 6.316 |  | 110/35/6
| Sн. LV, МVА | 5,6+6,3 | 2.949 | 0 | 0 | 2.949 | 0 | 5.88 | 2.931 |  |  | 1.05 |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.949 | 0 | 0 | 2.949 | 0 | 5.88 | 2.931
141 | Beryozovka | 4+4 | 3.283 | 0 | 0 | 3.283 | 0 | 4.2 | 0.917 | 0.917 |  | 1.05 | 141 | Beryozovka | 4+4 | 0.09 | 3.373 | 0 | 0 | 3.373 | 0 | 4.2 | 0.827 | 0.827 | 35/10
142 | N.Zhivotinnoe | 6,3+6,3 | 5.152 | 1 | 120 | 4.152 | 0 | 6.615 | 2.463 | 2.463 |  | 1.05 | 142 | N.Zhivotinnoe | 6,3+6,3 | 1.52 | 6.672 | 1 | 120 | 5.672 | 0 | 6.615 | 0.943 | 0.943 | 35/10
143 | Ramon-1 | 4+4+4 | 5.43 | 6.85 | 120 | -1.42 | 0 | 8.4 | 9.82 | 9.82 |  | 1.05 | 143 | Ramon-1 | 4+4+4 | 0.86 | 6.29 | 6.85 | 120 | -0.56 | 0 | 8.4 | 8.96 | 8.96 | 35/10/6
144 | Ramon-2 | 16,0+16,0 | 19.859 | 10.48 | 120 | 9.379 | 0 | 16.8 | 7.421 | 7.421 |  | 1.05 | 144 | Ramon-2 | 16,0+16,0 | 4.87 | 24.729 | 10.48 | 120 | 14.249 | 0 | 16.8 | 2.551 | 2.551
| Sн. MV, МVА | 16,0+16,0 | 15.632 | 6.85 | 0 | 8.782 | 0 | 16.8 | 8.018 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 15.632 | 6.85 | 0 | 8.782 | 0 | 16.8 | 8.018 |  | 110/35/10
| Sн. LV, МVА | 16,0+16,0 | 4.227 | 3.63 | 120 | 0.597 | 0 | 16.8 | 16.203 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 4.87 | 9.097 | 3.63 | 120 | 5.467 | 0 | 16.8 | 11.333
145 | Vereyka | 2,5+2,5 | 1.283 | 0 | 0 | 1.283 | 0 | 2.625 | 1.342 | 1.342 |  | 1.05 | 145 | Vereyka | 2,5+2,5 | 0.01 | 1.293 | 0 | 0 | 1.293 | 0 | 2.625 | 1.332 | 1.332 | 35/10
146 | Complex | 10+10 | 5.966 | 3.4 | 180 | 2.566 | 0 | 10.5 | 7.934 | 7.934 |  | 1.05 | 146 | Complex | 10+10 | 0 | 5.966 | 3.4 | 180 | 2.566 | 0 | 10.5 | 7.934 | 7.934
| Sн. MV, МVА | 10+10 | 3.97 | 3.1 | 180 | 0.87 | 0 | 10.5 | 9.63 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 3.97 | 3.1 | 180 | 0.87 | 0 | 10.5 | 9.63 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.996 | 0.3 | 180 | 1.696 | 0 | 10.5 | 8.804 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0 | 1.996 | 0.3 | 180 | 1.696 | 0 | 10.5 | 8.804
147 | N.Veduga | 16+16 | 6.996 | 2.9 | 120 | 4.096 | 0 | 16.8 | 12.704 | 12.704 |  | 1.05 | 147 | N.Veduga | 16+16 | 0 | 6.996 | 2.9 | 120 | 4.096 | 0 | 16.8 | 12.704 | 12.704
| Sн. MV, МVА | 16+16 | 5.47 | 2.9 | 120 | 2.57 | 0 | 16.8 | 14.23 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 5.47 | 2.9 | 120 | 2.57 | 0 | 16.8 | 14.23 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.526 | 0 | 0 | 1.526 | 0 | 16.8 | 15.274 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0 | 1.526 | 0 | 0 | 1.526 | 0 | 16.8 | 15.274
148 | Golosnovka | 2,5+2,5 | 0.499 | 0.512 | 120 | -0.013 | 0 | 2.625 | 2.638 | 2.638 |  | 1.05 | 148 | Golosnovka | 2,5+2,5 | 0.02 | 0.519 | 0.512 | 120 | 0.007 | 0 | 2.625 | 2.618 | 2.618 | 35/10
149 | Medvezhye | 3,2+4,0 | 0.762 | 0 | 0 | 0.762 | 0 | 3.36 | 2.598 | 2.598 |  | 1.05 | 149 | Medvezhye | 3,2+4,0 | 0.11 | 0.872 | 0 | 0 | 0.872 | 0 | 3.36 | 2.488 | 2.488 | 35/10
150 | St.Veduga | 4+4 | 0.968 | 0 | 0 | 0.968 | 0 | 4.2 | 3.232 | 3.232 |  | 1.05 | 150 | St.Veduga | 4+4 | 0.03 | 0.998 | 0 | 0 | 0.998 | 0 | 4.2 | 3.202 | 3.202 | 35/10
151 | M.Pokrovka | 2,5+2,5 | 0.587 | 0 | 0 | 0.587 | 0 | 2.625 | 2.038 | 2.038 |  | 1.05 | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.597 | 0 | 0 | 0.597 | 0 | 2.625 | 2.028 | 2.028 | 35/10
152 | V.Turovo-2 | 2,5+2,5 | 1.299 | 0.7 | 120 | 0.599 | 0 | 2.625 | 2.026 | 2.026 |  | 1.05 | 152 | V.Turovo-2 | 2,5+2,5 | 0.06 | 1.359 | 0.7 | 120 | 0.659 | 0 | 2.625 | 1.966 | 1.966 | 35/10
153 | S.Lipyagi | 3,2+2,5 | 1.679 | 2.9638 | 120 | -1.2848 | 0 | 2.625 | 3.9098 | 3.9098 |  | 1.05 | 153 | S.Lipyagi | 3,2+2,5 | 1.69 | 3.369 | 2.9638 | 120 | 0.4052 | 0 | 2.625 | 2.2198 | 2.2198 | 35/10
154 | N.Devitsk | 25+16 | 7.436 | 8.2225 | 180 | -0.7865 | 0 | 16.8 | 17.5865 | 15.001 |  | 1.05 | 154 | N.Devitsk | 25+16 | 2.66 | 10.096 | 8.2225 | 180 | 1.8735 | 0 | 16.8 | 14.9265 | 14.9265
| Sн. MV, МVА | 25+16 | 4.599 | 2.8 | 180 | 1.799 | 0 | 16.8 | 15.001 |  |  | 1.05 |  | Sн. MV, МVА | 25+16 | 0 | 4.599 | 2.8 | 180 | 1.799 | 0 | 16.8 | 15.001 |  | 110/35/10
| Sн. LV, МVА | 25+16 | 2.837 | 5.393 | 180 | -2.556 | 0 | 16.8 | 19.356 |  |  | 1.05 |  | Sн. LV, МVА | 25+16 | 2.66 | 5.497 | 5.393 | 180 | 0.104 | 0 | 16.8 | 16.696
155 | Repyevka | 4+4 | 2.561 | 0.5 | 120 | 2.061 | 0 | 4.2 | 2.139 | 2.139 |  | 1.05 | 155 | Repyevka | 4+4 | 0.02 | 2.581 | 0.5 | 120 | 2.081 | 0 | 4.2 | 2.119 | 2.119 | 35/10
156 | Krasnolipye | 16+16 | 18.983 | 2.9 | 120 | 16.083 | 0 | 16.8 | 0.717 | 0.717 |  | 1.05 | 156 | Krasnolipye | 16+16 | 0.03 | 19.013 | 2.9 | 120 | 16.113 | 0 | 16.8 | 0.687 | 0.687
| Sн. MV, МVА | 16+16 | 17.639 | 2.7 | 120 | 14.939 | 0 | 16.8 | 1.861 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 17.639 | 2.7 | 120 | 14.939 | 0 | 16.8 | 1.861 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.344 | 0.2 | 120 | 1.144 | 0 | 16.8 | 15.656 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.03 | 1.374 | 0.2 | 120 | 1.174 | 0 | 16.8 | 15.626
157 | Ulyanovka | 6,3+6,3 | 0.392 | 0.04 | 60 | 0.352 | 0 | 6.615 | 6.263 | 6.263 |  | 1.05 | 157 | Ulyanovka | 6,3+6,3 | 0.03 | 0.422 | 0.04 | 60 | 0.382 | 0 | 6.615 | 6.233 | 6.233 | 110/10
158 | МОB | 4+2,5 | 1.325 | 0.6 | 60 | 0.725 | 0 | 2.625 | 1.9 | 1.9 |  | 1.05 | 158 | МОB | 4+2,5 | 0.08 | 1.405 | 0.6 | 60 | 0.805 | 0 | 2.625 | 1.82 | 1.82 | 35/10
159 | L.Rossosh | 6,3+6,3 | 5.81 | 0 | 0 | 5.81 | 0 | 6.615 | 0.805 | 0.805 |  | 1.05 | 159 | L.Rossosh | 6,3+6,3 | 0.24 | 6.05 | 0 | 0 | 6.05 | 0 | 6.615 | 0.565 | 0.565 | 35/10
160 | Kashirskoe | 2,5+2,5 | 0.761 | 0 | 0 | 0.761 | 0 | 2.625 | 1.864 | 1.864 |  | 1.05 | 160 | Kashirskoe | 2,5+2,5 | 0.05 | 0.811 | 0 | 0 | 0.811 | 0 | 2.625 | 1.814 | 1.814 | 35/10
161 | Zaprudskoe | 2,5+2,5 | 1.809 | 0 | 0 | 1.809 | 0 | 2.625 | 0.816 | 0.816 |  | 1.05 | 161 | Zaprudskoe | 2,5+2,5 | 0.13 | 1.939 | 0 | 0 | 1.939 | 0 | 2.625 | 0.686 | 0.686 | 35/10
162 | Moskovskoe | 10+10 | 10.512 | 1.8 | 120 | 8.712 | 0 | 10.5 | 1.788 | 0.773 |  | 1.05 | 162 | Moskovskoe | 10+10 | 0.02 | 10.532 | 1.8 | 120 | 8.732 | 0 | 10.5 | 1.768 | 0.773
| Sн. MV, МVА | 10+10 | 9.727 | 0 | 0 | 9.727 | 0 | 10.5 | 0.773 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 9.727 | 0 | 0 | 9.727 | 0 | 10.5 | 0.773 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.785 | 1.8 | 120 | -1.015 | 0 | 10.5 | 11.515 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.02 | 0.805 | 1.8 | 120 | -0.995 | 0 | 10.5 | 11.495
163 | SemenovkaSPS | 2,5+4,0 | 1.468 | 0 | 0 | 1.468 | 0 | 2.625 | 1.157 | 1.157 |  | 1.05 | 163 | SemenovkaSPS | 2,5+4,0 | 0.01 | 1.478 | 0 | 0 | 1.478 | 0 | 2.625 | 1.147 | 1.147 | 35/10
164 | N. Baygora | 2,5+2,5 | 1.137 | 1.03 | 60 | 0.107 | 0 | 2.625 | 2.518 | 2.518 |  | 1.05 | 164 | N. Baygora | 2,5+2,5 | 0.02 | 1.157 | 1.03 | 60 | 0.127 | 0 | 2.625 | 2.498 | 2.498 | 35/10
165 | Shukavka | 2,5+2,5 | 1.1 | 0.1 | 120 | 1 | 0 | 2.625 | 1.625 | 1.625 |  | 1.05 | 165 | Shukavka | 2,5+2,5 | 0.03 | 1.13 | 0.1 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | 35/10
166 | Uglyanets | 4+2,5 | 2.896 | 0.8 | 120 | 2.096 | 0 | 2.625 | 0.529 | 0.529 |  | 1.05 | 166 | Uglyanets | 4+2,5 | 0.11 | 3.006 | 0.8 | 120 | 2.206 | 0 | 2.625 | 0.419 | 0.419 | 35/10
167 | V.Khava | 16+16 | 11.982 | 0.4 | 120 | 11.582 | 0 | 16.8 | 5.218 | 5.218 |  | 1.05 | 167 | V.Khava | 16+16 | 0.27 | 12.252 | 0.4 | 120 | 11.852 | 0 | 16.8 | 4.948 | 4.948
| Sн. MV, МVА | 16+16 | 4.546 | 0 | 0 | 4.546 | 0 | 16.8 | 12.254 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 4.546 | 0 | 0 | 4.546 | 0 | 16.8 | 12.254 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 7.436 | 0.4 | 120 | 7.036 | 0 | 16.8 | 9.764 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.27 | 7.706 | 0.4 | 120 | 7.306 | 0 | 16.8 | 9.494
168 | Usman-1 | 10,0+6,3 | 9.058 | 0 | 0 | 9.058 | 0 | 6.615 | -2.443 | -2.443 |  | 1.05 | 168 | Usman-1 | 10,0+6,3 | 5.14 | 14.198 | 0 | 0 | 14.198 | 0 | 6.615 | -7.583 | -7.583 | 35/10
169 | Usman-2 | 4+6,3 | 10.456 | 0 | 0 | 10.456 | 0 | 4.2 | -6.256 | -6.256 |  | 1.05 | 169 | Usman-2 | 4+6,3 | 1.71 | 12.166 | 0 | 0 | 12.166 | 0 | 4.2 | -7.966 | -7.966 | 35/10
170 | R.Khava | 4+4 | 4.235 | 0.2 | 120 | 4.035 | 0 | 4.2 | 0.165 | 0.165 |  | 1.05 | 170 | R.Khava | 4+4 | 0.08 | 4.315 | 0.2 | 120 | 4.115 | 0 | 4.2 | 0.085 | 0.085 | 35/10
171 | No. 31 | 16+25 | 24.566 | 5.6 | 120 | 18.966 | 0 | 16.8 | -2.166 | -2.166 |  | 1.05 | 171 | No. 31 | 16+25 | 0.18 | 24.746 | 5.6 | 120 | 19.146 | 0 | 16.8 | -2.346 | -2.346
| Sн. MV, МVА | 16+25 | 16.429 | 5.6 | 120 | 10.829 | 0 | 16.8 | 5.971 |  |  | 1.05 |  | Sн. MV, МVА | 16+25 | 0 | 16.429 | 5.6 | 120 | 10.829 | 0 | 16.8 | 5.971 |  | 110/35/10
| Sн. LV, МVА | 16+25 | 8.137 | 0 | 0 | 8.137 | 0 | 16.8 | 8.663 |  |  | 1.05 |  | Sн. LV, МVА | 16+25 | 0.18 | 8.317 | 0 | 0 | 8.317 | 0 | 16.8 | 8.483
172 | Maslovka | 2,5+4,0 | 3.578 | 0 | 0 | 3.578 | 0 | 2.625 | -0.953 | -0.953 |  | 1.05 | 172 | Maslovka | 2,5+4,0 | 0.43 | 4.008 | 0 | 0 | 4.008 | 0 | 2.625 | -1.383 | -1.383 | 35/10
173 | Podgornaya - district Line Maintenance Service | 16+16 | 7.07 | 1.6 | 180 | 5.47 | 0 | 16.8 | 11.33 | 11.33 |  | 1.05 | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 2.42 | 9.49 | 1.6 | 180 | 7.89 | 0 | 16.8 | 8.91 | 8.91
| Sн. MV, МVА | 16+16 | 3.1 | 1.05 | 180 | 2.05 | 0 | 16.8 | 14.75 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 3.1 | 1.05 | 180 | 2.05 | 0 | 16.8 | 14.75 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 3.97 | 0.55 | 180 | 3.42 | 0 | 16.8 | 13.38 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 2.42 | 6.39 | 0.55 | 180 | 5.84 | 0 | 16.8 | 10.96
174 | Kantemirovka | 10+10 | 9.1 | 1.6 | 60 | 7.5 | 0 | 10.5 | 3 | 3 |  | 1.05 | 174 | Kantemirovka | 10+10 | 1 | 10.1 | 1.6 | 60 | 8.5 | 0 | 10.5 | 2 | 2
| Sн. MV, МVА | 10+10 | 6.28 | 1.4 | 60 | 4.88 | 0 | 10.5 | 5.62 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 6.28 | 1.4 | 60 | 4.88 | 0 | 10.5 | 5.62 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.82 | 0.2 | 60 | 2.62 | 0 | 10.5 | 7.88 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 1 | 3.82 | 0.2 | 60 | 3.62 | 0 | 10.5 | 6.88
175 | Rossosh | 16+16+40 | 24.02 | 2.68 | 120 | 21.34 | 0 | 33.6 | 12.26 | 12.26 |  | 1.05 | 175 | Rossosh | 16+16+40 | 0.39 | 24.41 | 2.68 | 120 | 21.73 | 0 | 33.6 | 11.87 | 11.87
| Sн. MV, МVА | 16+16+40 | 4.17 | 1.9 | 120 | 2.27 | 0 | 33.6 | 31.33 |  |  | 1.05 |  | Sн. MV, МVА | 16+16+40 | 0 | 4.17 | 1.9 | 120 | 2.27 | 0 | 33.6 | 31.33 |  | 110/35/10/6
| Sн. LV, МVА | 16+16+40 | 19.85 | 0.78 | 120 | 19.07 | 0 | 33.6 | 14.53 |  |  | 1.05 |  | Sн. LV, МVА | 16+16+40 | 0.39 | 20.24 | 0.78 | 120 | 19.46 | 0 | 33.6 | 14.14
176 | Kamenka r-naya LPS | 16+16 | 3.31 | 0.97 | 120 | 2.34 | 0 | 16.8 | 14.46 | 14.46 |  | 1.05 | 176 | Kamenka r-naya LPS | 16+16 | 0.41 | 3.72 | 0.97 | 120 | 2.75 | 0 | 16.8 | 14.05 | 14.05
| Sн. MV, МVА | 16+16 | 0.56 | 0 | 120 | 0.56 | 0 | 16.8 | 16.24 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 0.56 | 0 | 120 | 0.56 | 0 | 16.8 | 16.24 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.75 | 0.97 | 120 | 1.78 | 0 | 16.8 | 15.02 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.41 | 3.16 | 0.97 | 120 | 2.19 | 0 | 16.8 | 14.61
177 | Korotoyak | 6,3+10 | 4.23 | 0.47 | 180 | 3.76 | 0 | 6.615 | 2.855 | 2.855 |  | 1.05 | 177 | Korotoyak | 6,3+10 | 0.4 | 4.63 | 0.47 | 180 | 4.16 | 0 | 6.615 | 2.455 | 2.455
| Sн. MV, МVА | 6,3+10 | 1.34 | 0 | 180 | 1.34 | 0 | 6.615 | 5.275 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+10 | 0 | 1.34 | 0 | 180 | 1.34 | 0 | 6.615 | 5.275 |  | 110/35/10
| Sн. LV, МVА | 6,3+10 | 2.89 | 0.47 | 180 | 2.42 | 0 | 6.615 | 4.195 |  |  | 1.05 |  | Sн. LV, МVА | 6,3+10 | 0.4 | 3.29 | 0.47 | 180 | 2.82 | 0 | 6.615 | 3.795
178 | Ostrogozhsk | 40,5+40,5 | 16.8 | 2.4 | 60 | 14.4 | 0 | 42.525 | 28.125 | 28.125 |  | 1.05 | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 16.8 | 2.4 | 60 | 14.4 | 0 | 42.525 | 28.125 | 28.125
| Sн. MV, МVА | 40,5+40,5 | 14.5 | 2.4 | 60 | 12.1 | 0 | 42.525 | 30.425 |  |  | 1.05 |  | Sн. MV, МVА | 40,5+40,5 | 0 | 14.5 | 2.4 | 60 | 12.1 | 0 | 42.525 | 30.425 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225 |  |  | 1.05 |  | Sн. LV, МVА | 40,5+40,5 | 0 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225
179 | Khrenovoe | 16+6,3 | 4.22 | 0 | 0 | 4.22 | 0 | 6.615 | 2.395 | 2.395 |  | 1.05 | 179 | Khrenovoe | 16+6,3 | 0.05 | 4.27 | 0 | 0 | 4.27 | 0 | 6.615 | 2.345 | 2.345
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 |  | Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  | 110/35/10
| Sн. LV, МVА | 16+6,3 | 4.22 | 0 | 0 | 4.22 | 0 | 6.615 | 2.395 |  |  | 1.05 |  | Sн. LV, МVА | 16+6,3 | 0.05 | 4.27 | 0 | 0 | 4.27 | 0 | 6.615 | 2.345
180 | Oil extraction plant | 25+25 | 18.9 | 7.9 | 120 | 11 | 0 | 26.25 | 15.25 | 12.35 |  | 1.05 | 180 | Oil extraction plant | 25+25 | 0.09 | 18.99 | 7.9 | 120 | 11.09 | 0 | 26.25 | 15.16 | 12.26
| Sн. MV, МVА | 25+25 | 5 | 7.9 | 120 | -2.9 | 0 | 26.25 | 29.15 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 5 | 7.9 | 120 | -2.9 | 0 | 26.25 | 29.15 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 13.9 | 0 | 0 | 13.9 | 0 | 26.25 | 12.35 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.09 | 13.99 | 0 | 0 | 13.99 | 0 | 26.25 | 12.26
181 | ANP | 6,3+6,3 | 2.49 | 0.39 | 120 | 2.1 | 0 | 6.615 | 4.515 | 4.515 |  | 1.05 | 181 | ANP | 6,3+6,3 | 2.84 | 5.33 | 0.39 | 120 | 4.94 | 0 | 6.615 | 1.675 | 1.675 | 110/6
182 | St. Kalitva | 6,3+6,3 | 1.16 | 0.86 | 240 | 0.3 | 0 | 6.615 | 6.315 | 6.315 |  | 1.05 | 182 | St. Kalitva | 6,3+6,3 | 0.08 | 1.24 | 0.86 | 240 | 0.38 | 0 | 6.615 | 6.235 | 6.235 | 110/10
183 | Nikanorovka | 2,5+6,3 | 0.43 | 0.5 | 240 | -0.07 | 0 | 2.625 | 2.695 | 2.695 |  | 1.05 | 183 | Nikanorovka | 2,5+6,3 | 0.09 | 0.52 | 0.5 | 240 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | 110/10
184 | Poultry plant | 10+10 | 2.44 | 1 | 120 | 1.44 | 0 | 10.5 | 9.06 | 9.06 |  | 1.05 | 184 | Poultry plant | 10+10 | 0.65 | 3.09 | 1 | 120 | 2.09 | 0 | 10.5 | 8.41 | 8.41 | 110/10
185 | Korshevo | 6,3+6,3 | 0.64 | 0.56 | 120 | 0.08 | 0 | 6.615 | 6.535 | 6.535 |  | 1.05 | 185 | Korshevo | 6,3+6,3 | 0.8 | 1.44 | 0.56 | 120 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | 110/10
186 | Davydovka | 6,3+6,3 | 6.27 | 2.11 | 240 | 4.16 | 0 | 6.615 | 2.455 | 2.455 |  | 1.05 | 186 | Davydovka | 6,3+6,3 | 0.72 | 6.99 | 2.11 | 240 | 4.88 | 0 | 6.615 | 1.735 | 1.735 | 110/10
187 | the 2nd Pyatiletka | 6,3+6,3 | 1 | 0.66 | 120 | 0.34 | 0 | 6.615 | 6.275 | 6.275 |  | 1.05 | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.1 | 1.1 | 0.66 | 120 | 0.44 | 0 | 6.615 | 6.175 | 6.175 | 110/10
188 | Liskinskaya | 10+16 | 2.23 | 0.72 | 120 | 1.51 | 0 | 10.5 | 8.99 | 8.99 |  | 1.05 | 188 | Liskinskaya | 10+16 | 4.28 | 6.51 | 0.72 | 120 | 5.79 | 0 | 10.5 | 4.71 | 4.71 | 110/6
189 | Olkhovatka | 4+4 | 3.64 | 2.55 | 180 | 1.09 | 0 | 4.2 | 3.11 | 3.11 |  | 1.05 | 189 | Olkhovatka | 4+4 | 0.95 | 4.59 | 2.55 | 180 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | 35/10
190 | Shaposhnikovka | 2,5+2,5 | 0.95 | 0.86 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 |  | 1.05 | 190 | Shaposhnikovka | 2,5+2,5 | 0.18 | 1.13 | 0.86 | 180 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | 35/10
191 | Karayashnik | 2,5+2,5 | 0.35 | 0.2875 | 180 | 0.0625 | 0 | 2.625 | 2.5625 | 2.5625 |  | 1.05 | 191 | Karayashnik | 2,5+2,5 | 0.05 | 0.4 | 0.2875 | 180 | 0.1125 | 0 | 2.625 | 2.5125 | 2.5125 | 35/10
192 | Saguny | 2,5+2,5 | 0.97 | 0.91 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 192 | Saguny | 2,5+2,5 | 0.09 | 1.06 | 0.91 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | 35/10
193 | Belogorye | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 |  | 1.05 | 193 | Belogorye | 2,5+2,5 | 0.15 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | 35/10
194 | Taly | 4+4 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 |  | 1.05 | 194 | Taly | 4+4 | 0.12 | 1.28 | 0 | 0 | 1.28 | 0 | 4.2 | 2.92 | 2.92 | 35/10
195 | Titarevka | 2,5+2,5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 |  | 1.05 | 195 | Titarevka | 2,5+2,5 | 0.13 | 0.92 | 0 | 0 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | 35/10
196 | Mitrofanovka | 4+4 | 2.1 | 0 | 0 | 2.1 | 0 | 4.2 | 2.1 | 2.1 |  | 1.05 | 196 | Mitrofanovka | 4+4 | 0.28 | 2.38 | 0 | 0 | 2.38 | 0 | 4.2 | 1.82 | 1.82 | 35/10
197 | Druzhba | 4+4 | 1.72 | 0.44 | 150 | 1.28 | 0 | 4.2 | 2.92 | 2.92 |  | 1.05 | 197 | Druzhba | 4+4 | 0.18 | 1.9 | 0.44 | 150 | 1.46 | 0 | 4.2 | 2.74 | 2.74 | 35/10
198 | AlexandrovkaLPS | 4+4 | 1.94 | 0 | 0 | 1.94 | 0 | 4.2 | 2.26 | 2.26 |  | 1.05 | 198 | AlexandrovkaLPS | 4+4 | 0.1 | 2.04 | 0 | 0 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | 35/10
199 | Tkhorevka | 4+4 | 0.94 | 0.78 | 180 | 0.16 | 0 | 4.2 | 4.04 | 4.04 |  | 1.05 | 199 | Tkhorevka | 4+4 | 0.11 | 1.05 | 0.78 | 180 | 0.27 | 0 | 4.2 | 3.93 | 3.93 | 35/10
200 | Marki | 2,5+2,5 | 0.33 | 0.27 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 200 | Marki | 2,5+2,5 | 0 | 0.33 | 0.27 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
201 | Olkhov Log | 2,5+2,5 | 0.64 | 0.58 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 201 | Olkhov Log | 2,5+2,5 | 0 | 0.64 | 0.58 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
202 | Boldyrevka | 2,5+2,5 | 1.02 | 0 | 0 | 1.02 | 0 | 2.625 | 1.605 | 1.605 |  | 1.05 | 202 | Boldyrevka | 2,5+2,5 | 0.23 | 1.25 | 0 | 0 | 1.25 | 0 | 2.625 | 1.375 | 1.375 | 35/10
203 | Pobeda | 4+4 | 0.36 | 0 | 0 | 0.36 | 0 | 4.2 | 3.84 | 3.84 |  | 1.05 | 203 | Pobeda | 4+4 | 0.05 | 0.41 | 0 | 0 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | 35/10
204 | Lipovka | 4+4 | 1.43 | 0 | 0 | 1.43 | 0 | 4.2 | 2.77 | 2.77 |  | 1.05 | 204 | Lipovka | 4+4 | 0.19 | 1.62 | 0 | 0 | 1.62 | 0 | 4.2 | 2.58 | 2.58 | 35/10
205 | Yudanovka | 2,5+2,5 | 0.9 | 0.81 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 |  | 1.05 | 205 | Yudanovka | 2,5+2,5 | 0.12 | 1.02 | 0.81 | 180 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | 35/10
206 | Mechetka | 2,5+1,6 | 0.42 | 0 | 0 | 0.42 | 0 | 1.68 | 1.26 | 1.26 |  | 1.05 | 206 | Mechetka | 2,5+1,6 | 0.04 | 0.46 | 0 | 0 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | 35/10
207 | Petrovskaya | 4+4 | 1.75 | 0.03 | 180 | 1.72 | 0 | 4.2 | 2.48 | 2.48 |  | 1.05 | 207 | Petrovskaya | 4+4 | 0.96 | 2.71 | 0.03 | 180 | 2.68 | 0 | 4.2 | 1.52 | 1.52 | 35/10
208 | Sr. Ikorets | 4+4 | 3.27 | 0.06 | 120 | 3.21 | 0 | 4.2 | 0.99 | 0.99 |  | 1.05 | 208 | Sr. Ikorets | 4+4 | 0.9 | 4.17 | 0.06 | 120 | 4.11 | 0 | 4.2 | 0.09 | 0.09 | 35/10
209 | the 2nd Storozhevoe | 2,5+2,5 | 0.25 | 0 | 0 | 0.25 | 0 | 2.625 | 2.375 | 2.375 |  | 1.05 | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.35 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | 35/10
210 | Och. Sooruzheniya | 2,5+2,5 | 2.71 | 0.42 | 120 | 2.29 | 0 | 2.625 | 0.335 | 0.335 |  | 1.05 | 210 | Och. Sooruzheniya | 2,5+2,5 | 0.97 | 3.68 | 0.6 | 120 | 3.08 | 0 | 2.625 | -0.455 | -0.455 | 35/6
211 | Borisoglebsk | 25+25 | 18.66 | 15.05 | 240 | 3.61 | 0 | 26.25 | 22.64 | 22.64 |  | 1.05 | 211 | Borisoglebsk | 25+25 | 0 | 18.66 | 24.9 | 240 | -6.24 | 0 | 26.25 | 32.49 | 27.69
| Sн. MV, МVА | 25+25 | 11.7 | 10.9 | 240 | 0.8 | 0 | 26.25 | 25.45 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 11.7 | 16.5 | 240 | -4.8 | 0 | 26.25 | 31.05 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.96 | 4.15 | 240 | 2.81 | 0 | 26.25 | 23.44 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0 | 6.96 | 8.4 | 240 | -1.44 | 0 | 26.25 | 27.69
212 | KamenkaBPS | 10+10 | 4.22 | 2.79 | 180 | 1.43 | 0 | 10.5 | 9.07 | 9.07 |  | 1.05 | 212 | KamenkaBPS | 10+10 | 0.01 | 4.23 | 6.01 | 180 | -1.78 | 0 | 10.5 | 12.28 | 10.73
| Sн. MV, МVА | 10+10 | 3.8 | 2.54 | 180 | 1.26 | 0 | 10.5 | 9.24 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 3.8 | 5.35 | 180 | -1.55 | 0 | 10.5 | 12.05 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.42 | 0.25 | 180 | 0.17 | 0 | 10.5 | 10.33 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 0.43 | 0.66 | 180 | -0.23 | 0 | 10.5 | 10.73
213 | Talovaya | 16+16 | 5.59 | 3.6 | 180 | 1.99 | 0 | 16.8 | 14.81 | 14.81 |  | 1.05 | 213 | Talovaya | 16+16 | 0.08 | 5.67 | 6.39 | 180 | -0.72 | 0 | 16.8 | 17.52 | 15.95
| Sн. MV, МVА | 16+16 | 4.82 | 3.6 | 180 | 1.22 | 0 | 16.8 | 15.58 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 4.82 | 6.39 | 180 | -1.57 | 0 | 16.8 | 18.37 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.08 | 0.85 | 0 | 0 | 0.85 | 0 | 16.8 | 15.95
214 | Anna | 25+25 | 10.28 | 7.8 | 150 | 2.48 | 0 | 26.25 | 23.77 | 23.77 |  | 1.05 | 214 | Anna | 25+25 | 0.14 | 10.42 | 14.11 | 150 | -3.69 | 0 | 26.25 | 29.94 | 27.75
| Sн. MV, МVА | 25+25 | 3.87 | 2.39 | 150 | 1.48 | 0 | 26.25 | 24.77 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 3.87 | 5.37 | 150 | -1.5 | 0 | 26.25 | 27.75 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 6.41 | 5.4 | 150 | 1.01 | 0 | 26.25 | 25.24 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.14 | 6.55 | 8.74 | 150 | -2.19 | 0 | 26.25 | 28.44
215 | ArkhangelskoeBPS | 10+10 | 5.95 | 0.88 | 90 | 5.07 | 0 | 10.5 | 5.43 | 5.43 |  | 1.05 | 215 | ArkhangelskoeBPS | 10+10 | 0.01 | 5.96 | 3.02 | 90 | 2.94 | 0 | 10.5 | 7.56 | 7.43
| Sн. MV, МVА | 10+10 | 2.89 | 0.88 | 90 | 2.01 | 0 | 10.5 | 8.49 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.89 | 3.02 | 90 | -0.13 | 0 | 10.5 | 10.63 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.06 | 0 | 0 | 3.06 | 0 | 10.5 | 7.44 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 3.07 | 0 | 0 | 3.07 | 0 | 10.5 | 7.43
216 | Listopadovka | 10+10 | 3.43 | 1.63 | 90 | 1.8 | 0 | 10.5 | 8.7 | 8.7 |  | 1.05 | 216 | Listopadovka | 10+10 | 0.03 | 3.46 | 3.08 | 90 | 0.38 | 0 | 10.5 | 10.12 | 9.4
| Sн. MV, МVА | 10+10 | 2.36 | 1.63 | 90 | 0.73 | 0 | 10.5 | 9.77 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.36 | 3.08 | 90 | -0.72 | 0 | 10.5 | 11.22 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.07 | 0 | 0 | 1.07 | 0 | 10.5 | 9.43 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.03 | 1.1 | 0 | 0 | 1.1 | 0 | 10.5 | 9.4
217 | V. Karachan | 10+10 | 2.49 | 0.81 | 90 | 1.68 | 0 | 10.5 | 8.82 | 8.82 |  | 1.05 | 217 | V. Karachan | 10+10 | 0.01 | 2.5 | 1.18 | 90 | 1.32 | 0 | 10.5 | 9.18 | 8.92
| Sн. MV, МVА | 10+10 | 0.92 | 0.81 | 90 | 0.11 | 0 | 10.5 | 10.39 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 0.92 | 1.18 | 90 | -0.26 | 0 | 10.5 | 10.76 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.57 | 0 | 0 | 1.57 | 0 | 10.5 | 8.93 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 1.58 | 0 | 0 | 1.58 | 0 | 10.5 | 8.92
218 | Ternovka | 10+10 | 3.56 | 0.66 | 60 | 2.9 | 0 | 10.5 | 7.6 | 7.6 |  | 1.05 | 218 | Ternovka | 10+10 | 0.06 | 3.62 | 1.03 | 60 | 2.59 | 0 | 10.5 | 7.91 | 7.91
| Sн. MV, МVА | 10+10 | 1.21 | 0.66 | 60 | 0.55 | 0 | 10.5 | 9.95 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 1.21 | 1.03 | 60 | 0.18 | 0 | 10.5 | 10.32 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.35 | 0 | 0 | 2.35 | 0 | 10.5 | 8.15 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.06 | 2.41 | 0 | 0 | 2.41 | 0 | 10.5 | 8.09
219 | Narodnoe | 16+10 | 2.98 | 0.6 | 90 | 2.38 | 0 | 10.5 | 8.12 | 8.12 |  | 1.05 | 219 | Narodnoe | 16+10 | 0.06 | 3.04 | 0.93 | 90 | 2.11 | 0 | 10.5 | 8.39 | 8.23
| Sн. MV, МVА | 16+10 | 0.77 | 0.6 | 90 | 0.17 | 0 | 10.5 | 10.33 |  |  | 1.05 |  | Sн. MV, МVА | 16+10 | 0 | 0.77 | 0.93 | 90 | -0.16 | 0 | 10.5 | 10.66 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 2.21 | 0 | 0 | 2.21 | 0 | 10.5 | 8.29 |  |  | 1.05 |  | Sн. LV, МVА | 16+10 | 0.06 | 2.27 | 0 | 0 | 2.27 | 0 | 10.5 | 8.23
220 | N. Khopersk | 10+16 | 7.84 | 1.7 | 120 | 6.14 | 0 | 10.5 | 4.36 | 4.36 |  | 1.05 | 220 | N. Khopersk | 10+16 | 0.29 | 8.13 | 1.95 | 120 | 6.18 | 0 | 10.5 | 4.32 | 4.32
| Sн. MV, МVА | 10+16 | 2.2 | 1.7 | 120 | 0.5 | 0 | 10.5 | 10 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 2.2 | 1.95 | 120 | 0.25 | 0 | 10.5 | 10.25 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 5.64 | 0 | 0 | 5.64 | 0 | 10.5 | 4.86 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.29 | 5.93 | 0 | 0 | 5.93 | 0 | 10.5 | 4.57
221 | Ertil | 10+16 | 6.72 | 2.92 | 180 | 3.8 | 0 | 10.5 | 6.7 | 6.7 |  | 1.05 | 221 | Ertil | 10+16 | 0.08 | 6.8 | 1.4 | 180 | 5.4 | 0 | 10.5 | 5.1 | 5.1
| Sн. MV, МVА | 10+16 | 4.62 | 2.92 | 180 | 1.7 | 0 | 10.5 | 8.8 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 4.62 | 1.4 | 180 | 3.22 | 0 | 10.5 | 7.28 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 2.1 | 0.08 | 0 | 2.02 | 0 | 10.5 | 8.48 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.08 | 2.18 | 0 | 0 | 2.18 | 0 | 10.5 | 8.32
222 | Shchuchye | 6,3+6,3 | 2.03 | 1.09 | 180 | 0.94 | 0 | 6.615 | 5.675 | 5.635 |  | 1.05 | 222 | Shchuchye | 6,3+6,3 | 0.08 | 2.11 | 2.33 | 180 | -0.22 | 0 | 6.615 | 6.835 | 5.825
| Sн. MV, МVА | 6,3+6,3 | 0.8 | 0.84 | 180 | -0.04 | 0 | 6.615 | 6.655 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 0.8 | 1.81 | 180 | -1.01 | 0 | 6.615 | 7.625 |  | 110/35/10
| Sн.LV, МVА | 6,3+6,3 | 1.23 | 0.25 | 180 | 0.98 | 0 | 6.615 | 5.635 |  |  | 1.05 |  | Sн.LV, МVА | 6,3+6,3 | 0.08 | 1.31 | 0.52 | 180 | 0.79 | 0 | 6.615 | 5.825
223 | Dokuchaevo | 10+10 | 1.8 | 0.12 | 120 | 1.68 | 0 | 10.5 | 8.82 | 8.82 |  | 1.05 | 223 | Dokuchaevo | 10+10 | 0.03 | 1.83 | 0.45 | 120 | 1.38 | 0 | 10.5 | 9.12 | 9.12 | 110/10
224 | B. Gribanovka | 16+16 | 6.2 | 0.11 | 30 | 6.09 | 0 | 16.8 | 10.71 | 10.71 |  | 1.05 | 224 | B. Gribanovka | 16+16 | 0.15 | 6.35 | 0.24 | 30 | 6.11 | 0 | 16.8 | 10.69 | 10.69 | 110/10
225 | Khimmash | 16+16 | 4.4 | 4.47 | 240 | -0.07 | 0 | 16.8 | 16.87 | 16.87 |  | 1.05 | 225 | Khimmash | 16+16 | 0 | 4.4 | 7.1 | 240 | -2.7 | 0 | 16.8 | 19.5 | 19.5 | 110/6
226 | Chigorak | 2,5+4 | 0.7 | 0.74 | 90 | -0.04 | 0 | 2.625 | 2.665 | 2.665 |  | 1.05 | 226 | Chigorak | 2,5+4 | 0.11 | 0.81 | 0.96 | 90 | -0.15 | 0 | 2.625 | 2.775 | 2.775 | 35/10
227 | Tretyaki | 4+4 | 0.83 | 0 | 0 | 0.83 | 0 | 4.2 | 3.37 | 3.37 |  | 1.05 | 227 | Tretyaki | 4+4 | 0.03 | 0.86 | 0 | 0 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | 35/10
228 | Gubari | 2,5+2,5 | 0.27 | 0.06 | 180 | 0.21 | 0 | 2.625 | 2.415 | 2.415 |  | 1.05 | 228 | Gubari | 2,5+2,5 | 0.05 | 0.32 | 0.43 | 180 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | 35/10
229 | Tantsyrey | 2,5+2,5 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 |  | 1.05 | 229 | Tantsyrey | 2,5+2,5 | 0.04 | 0.9 | 0 | 0 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | 35/10
230 | Peski | 4+4 | 3.34 | 0 | 0 | 3.34 | 0 | 4.2 | 0.86 | 0.86 |  | 1.05 | 230 | Peski | 4+4 | 0.12 | 3.46 | 0 | 0 | 3.46 | 0 | 4.2 | 0.74 | 0.74 | 35/10
231 | M. Gribanovka | 1,6+1,6 | 0.32 | 0.31 | 30 | 0.01 | 0 | 1.68 | 1.67 | 1.67 |  | 1.05 | 231 | M. Gribanovka | 1,6+1,6 | 0.02 | 0.34 | 0.87 | 30 | -0.53 | 0 | 1.68 | 2.21 | 2.21 | 35/10
232 | N. Karachan | 2,5+2,5 | 0.5 | 0 | 0 | 0.5 | 0 | 2.625 | 2.125 | 2.125 |  | 1.05 | 232 | N. Karachan | 2,5+2,5 | 0 | 0.5 | 0 | 0 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | 35/10
233 | Kozlovka BPS | 4+2,5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 |  | 1.05 | 233 | Kozlovka BPS | 4+2,5 | 0.03 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 | 35/10
234 | K. Otdelets | 2,5+2,5 | 0.46 | 0 | 30 | 0.46 | 0 | 2.625 | 2.165 | 2.165 |  | 1.05 | 234 | K. Otdelets | 2,5+2,5 | 0 | 0.46 | 0.63 | 30 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | 35/10
235 | Esipovo | 2,5+2,5 | 0.67 | 0 | 0 | 0.67 | 0 | 2.625 | 1.955 | 1.955 |  | 1.05 | 235 | Esipovo | 2,5+2,5 | 0.02 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | 35/10
236 | Kiselnov | 2,5+2,5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 |  | 1.05 | 236 | Kiselnov | 2,5+2,5 | 0 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | 35/10
237 | Krasnoe | 6,3+6,3 | 1.85 | 0 | 0 | 1.85 | 0 | 6.615 | 4.765 | 4.765 |  | 1.05 | 237 | Krasnoe | 6,3+6,3 | 0.01 | 1.86 | 0 | 0 | 1.86 | 0 | 6.615 | 4.755 | 4.755 | 35/10
238 | Troitskoe | 2,5+2,5 | 0.42 | 0 | 0 | 0.42 | 0 | 2.625 | 2.205 | 2.205 |  | 1.05 | 238 | Troitskoe | 2,5+2,5 | 0.01 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | 35/10
239 | Ertil-gorod | 6,3+6,3 | 3.55 | 2.45 | 240 | 1.1 | 0 | 6.615 | 5.515 | 5.515 |  | 1.05 | 239 | Ertil-gorod | 6,3+6,3 | 0.06 | 3.61 | 5 | 240 | -1.39 | 0 | 6.615 | 8.005 | 8.005 | 35/10
240 | Rostoshi | 4+4 | 1.47 | 0 | 0 | 1.47 | 0 | 4.2 | 2.73 | 2.73 |  | 1.05 | 240 | Rostoshi | 4+4 | 0 | 1.47 | 0 | 0 | 1.47 | 0 | 4.2 | 2.73 | 2.73 | 35/10
241 | Vvedenka | 2,5+2,5 | 0.35 | 0 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 |  | 1.05 | 241 | Vvedenka | 2,5+2,5 | 0 | 0.35 | 0.48 | 60 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | 35/10
242 | Sadovoe | 4+4 | 1.92 | 0 | 0 | 1.92 | 0 | 4.2 | 2.28 | 2.28 |  | 1.05 | 242 | Sadovoe | 4+4 | 0.03 | 1.95 | 0 | 0 | 1.95 | 0 | 4.2 | 2.25 | 2.25 | 35/10
243 | Rubashevka | 2,5+2,5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 |  | 1.05 | 243 | Rubashevka | 2,5+2,5 | 0 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | 35/10
244 | N. Nadezhdenka | 2,5+2,5 | 0.46 | 0.22 | 180 | 0.24 | 0 | 2.625 | 2.385 | 2.385 |  | 1.05 | 244 | N. Nadezhdenka | 2,5+2,5 | 0 | 0.46 | 0.75 | 180 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | 35/10
245 | Abramovka | 6,3+4 | 3.4 | 0.29 | 120 | 3.11 | 0 | 4.2 | 1.09 | 1.09 |  | 1.05 | 245 | Abramovka | 6,3+4 | 0.04 | 3.44 | 0.52 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | 35/10
246 | Alexandrovka BPS | 2,5+2,5 | 0.9 | 0.64 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 |  | 1.05 | 246 | Alexandrovka BPS | 2,5+2,5 | 0.01 | 0.91 | 1.17 | 120 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | 35/10
247 | N. Troitskaya | 4+4 | 0.3 | 0.2 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 |  | 1.05 | 247 | N. Troitskaya | 4+4 | 0 | 0.3 | 0.34 | 120 | -0.04 | 0 | 4.2 | 4.24 | 4.24 | 35/10
248 | Kalach-1 | 25+25 | 14.75 | 2.2 | 120 | 12.55 | 0 | 26.25 | 13.7 | 13.7 |  | 1.05 | 248 | Kalach-1 | 25+25 | 0.52 | 15.27 | 2.2 | 120 | 13.07 | 0 | 26.25 | 13.18 | 13.18
| Sн. MV, МVА | 25+25 | 6.2 | 1 | 120 | 5.2 | 0 | 26.25 | 21.05 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 6.2 | 1 | 120 | 5.2 | 0 | 26.25 | 21.05 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 8.55 | 1.2 | 120 | 7.35 | 0 | 26.25 | 18.9 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.52 | 9.07 | 1.2 | 120 | 7.87 | 0 | 26.25 | 18.38
249 | Kalach-2 | 16+16 | 7.13 | 2 | 24 hours | 5.13 | 0 | 16.8 | 11.67 | 11.67 |  | 1.05 | 249 | Kalach-2 | 16+16 | 0.54 | 7.67 | 2 | 24 hours | 5.67 | 0 | 16.8 | 11.13 | 11.13 | 110/10
250 | Buturlinovka-1 | 16+16 | 12.94 | 2 | 120 | 10.94 | 0 | 16.8 | 5.86 | 5.86 |  | 1.05 | 250 | Buturlinovka-1 | 16+16 | 0.1 | 13.04 | 2 | 120 | 11.04 | 0 | 16.8 | 5.76 | 5.76
| Sн. MV, МVА | 16+16 | 2.89 | 0 | 0 | 2.89 | 0 | 16.8 | 13.91 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 2.89 | 0 | 0 | 2.89 | 0 | 16.8 | 13.91 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 10.05 | 2 | 120 | 8.05 | 0 | 16.8 | 8.75 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.1 | 10.15 | 2 | 120 | 8.15 | 0 | 16.8 | 8.65
251 | Buturlinovka-2 | 16+6,3 | 5.36 | 1.5 | 120 | 3.86 | 0 | 6.615 | 2.755 | 2.755 |  | 1.05 | 251 | Buturlinovka-2 | 16+6,3 | 0.01 | 5.37 | 1.5 | 120 | 3.87 | 0 | 6.615 | 2.745 | 2.745 | 110/10
252 | N.Kislyai | 10+10 | 6.28 | 1.5 | 120 | 4.78 | 0 | 10.5 | 5.72 | 5.72 |  | 1.05 | 252 | N.Kislyai | 10+10 | 0.4 | 6.68 | 1.5 | 120 | 5.18 | 0 | 10.5 | 5.32 | 5.32
| Sн. MV, МVА | 10+10 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.36 | 1.5 | 120 | 1.86 | 0 | 10.5 | 8.64 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.4 | 3.76 | 1.5 | 120 | 2.26 | 0 | 10.5 | 8.24
253 | Kozlovka CPS | 2,5+6,3 | 1.14 | 1.5 | 45 | -0.36 | 0 | 2.625 | 2.985 | 2.985 |  | 1.05 | 253 | Kozlovka CPS | 2,5+6,3 | 0.18 | 1.32 | 1.5 | 45 | -0.18 | 0 | 2.625 | 2.805 | 2.805 | 110/10
254 | Filippenkovo | 6,3+6,3 | 1.12 | 1.5 | 120 | -0.38 | 0 | 6.615 | 6.995 | 6.995 |  | 1.05 | 254 | Filippenkovo | 6,3+6,3 | 0.05 | 1.17 | 1.5 | 120 | -0.33 | 0 | 6.615 | 6.945 | 6.945 | 110/10
255 | Vorobyovka | 16+16 | 5.85 | 1.5 | 120 | 4.35 | 0 | 16.8 | 12.45 | 12.45 |  | 1.05 | 255 | Vorobyovka | 16+16 | 0.41 | 6.26 | 1.5 | 120 | 4.76 | 0 | 16.8 | 12.04 | 12.04
| Sн. MV, МVА | 16+16 | 3.3 | 0.5 | 120 | 2.8 | 0 | 16.8 | 14 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 3.3 | 0.5 | 120 | 2.8 | 0 | 16.8 | 14 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.55 | 1 | 120 | 1.55 | 0 | 16.8 | 15.25 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.41 | 2.96 | 1 | 120 | 1.96 | 0 | 16.8 | 14.84
256 | Solontsy | 6,3+6,3 | 2.61 | 1 | 24 hours | 1.61 | 0 | 6.615 | 5.005 | 5.005 |  | 1.05 | 256 | Solontsy | 6,3+6,3 | 0.03 | 2.64 | 1 | 24 hours | 1.64 | 0 | 6.615 | 4.975 | 4.975
| Sн. MV, МVА | 6,3+6,3 | 1.71 | 1 | 24 hours | 0.71 | 0 | 6.615 | 5.905 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.71 | 1 | 24 hours | 0.71 | 0 | 6.615 | 5.905 |  | 110/35/10
| Sн. LV, МVА | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 |  |  | 1.05 |  | Sн. LV, МVА | 6,3+6,3 | 0.03 | 0.93 | 0 | 0 | 0.93 | 0 | 6.615 | 5.685
257 | Manino | 16+16 | 2.05 | 1.5 | 24 hours | 0.55 | 0 | 16.8 | 16.25 | 16.25 |  | 1.05 | 257 | Manino | 16+16 | 0.03 | 2.08 | 1.5 | 24 hours | 0.58 | 0 | 16.8 | 16.22 | 16.22
| Sн. MV, МVА | 16+16 | 0.74 | 0.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 0.74 | 0.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.31 | 1 | 24 hours | 0.31 | 0 | 16.8 | 16.49 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.03 | 1.34 | 1 | 24 hours | 0.34 | 0 | 16.8 | 16.46
258 | Petropavlovka | 10+10 | 4.59 | 2 | 120 | 2.59 | 0 | 10.5 | 7.91 | 7.91 |  | 1.05 | 258 | Petropavlovka | 10+10 | 0.22 | 4.81 | 2 | 120 | 2.81 | 0 | 10.5 | 7.69 | 7.69
| Sн. MV, МVА | 10+10 | 2.01 | 1 | 120 | 1.01 | 0 | 10.5 | 9.49 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2 | 1 | 120 | 1 | 0 | 10.5 | 9.5 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.58 | 1 | 120 | 1.58 | 0 | 10.5 | 8.92 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.22 | 2.8 | 1 | 120 | 1.8 | 0 | 10.5 | 8.7
259 | V.Mamon | 16+10 | 5.87 | 2 | 120 | 3.87 | 0 | 10.5 | 6.63 | 6.63 |  | 1.05 | 259 | V.Mamon | 16+10 | 0.62 | 6.49 | 2 | 120 | 4.49 | 0 | 10.5 | 6.01 | 6.01
| Sн. MV, МVА | 16+10 | 2.13 | 0 | 0 | 2.13 | 0 | 10.5 | 8.37 |  |  | 1.05 |  | Sн. MV, МVА | 16+10 | 0 | 2.13 | 0 | 0 | 2.13 | 0 | 10.5 | 8.37 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 3.74 | 2 | 120 | 1.74 | 0 | 10.5 | 8.76 |  |  | 1.05 |  | Sн. LV, МVА | 16+10 | 0.62 | 4.36 | 2 | 120 | 2.36 | 0 | 10.5 | 8.14
260 | N.Mamon | 2,5+6,3 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 |  | 1.05 | 260 | N.Mamon | 2,5+6,3 | 0.08 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | 110/10
261 | Pavlovsk-2 | 25+25 | 19.63 | 1.5 | 120 | 18.13 | 0 | 26.25 | 8.12 | 8.12 |  | 1.05 | 261 | Pavlovsk-2 | 25+25 | 0.08 | 19.71 | 1.5 | 120 | 18.21 | 0 | 26.25 | 8.04 | 8.04
| Sн. MV, МVА | 25+25 | 9.94 | 1.5 | 120 | 8.44 | 0 | 26.25 | 17.81 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 9.94 | 1.5 | 120 | 8.44 | 0 | 26.25 | 17.81 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 9.69 | 0 | 0 | 9.69 | 0 | 26.25 | 16.56 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.08 | 9.77 | 0 | 0 | 9.77 | 0 | 26.25 | 16.48
262 | Bogucharskaya | 16+16 | 9.16 | 2 | 120 | 7.16 | 0 | 16.8 | 9.64 | 9.64 |  | 1.05 | 262 | Bogucharskaya | 16+16 | 2.18 | 11.34 | 2 | 120 | 9.34 | 0 | 16.8 | 7.46 | 7.46
| Sн. MV, МVА | 16+16 | 3.65 | 1 | 120 | 2.65 | 0 | 16.8 | 14.15 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 3.65 | 1 | 120 | 2.65 | 0 | 16.8 | 14.15 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.51 | 1 | 120 | 4.51 | 0 | 16.8 | 12.29 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 2.18 | 7.69 | 1 | 120 | 6.69 | 0 | 16.8 | 10.11
263 | Opornaya | 6,3+6,3 | 1.13 | 1.5 | 120 | -0.37 | 0 | 6.615 | 6.985 | 6.985 |  | 1.05 | 263 | Opornaya | 6,3+6,3 | 1.43 | 2.56 | 1.5 | 120 | 1.06 | 0 | 6.615 | 5.555 | 5.555 | 110/10
264 | Podgornaya CPS | 2,5+2,5 | 0.95 | 1 | 120 | -0.05 | 0 | 2.625 | 2.675 | 2.675 |  | 1.05 | 264 | Podgornaya CPS | 2,5+2,5 | 0.02 | 0.97 | 1 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | 35/10
265 | Bolshevik CPS | 4+2,5 | 2.24 | 1.5 | 45 | 0.74 | 0 | 2.625 | 1.885 | 1.885 |  | 1.05 | 265 | Bolshevik CPS | 4+2,5 | 0.22 | 2.46 | 1.5 | 45 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | 35/10
266 | Semenovka CPS | 2,5+1,8 | 0.84 | 1 | 80 | -0.16 | 0 | 1.89 | 2.05 | 2.05 |  | 1.05 | 266 | Semenovka CPS | 2,5+1,8 | 0.03 | 0.87 | 1 | 80 | -0.13 | 0 | 1.89 | 2.02 | 2.02 | 35/10
267 | Popasnoe | 4+4 | 0.31 | 1.5 | 120 | -1.19 | 0 | 4.2 | 5.39 | 5.39 |  | 1.05 | 267 | Popasnoe | 4+4 | 0.02 | 0.33 | 1.5 | 120 | -1.17 | 0 | 4.2 | 5.37 | 5.37 | 35/10
268 | N.Kriusha | 2,5+2,5 | 1.05 | 1.5 | 45 | -0.45 | 0 | 2.625 | 3.075 | 3.075 |  | 1.05 | 268 | N.Kriusha | 2,5+2,5 | 0.03 | 1.08 | 1.5 | 45 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | 35/10
269 | N.Melovatka | 2,5+2,5 | 1.49 | 1.5 | 45 | -0.01 | 0 | 2.625 | 2.635 | 2.635 |  | 1.05 | 269 | N.Melovatka | 2,5+2,5 | 0.07 | 1.56 | 1.5 | 45 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
270 | Vasilyevka CPS | 4+4 | 0.91 | 1.5 | 120 | -0.59 | 0 | 4.2 | 4.79 | 4.79 |  | 1.05 | 270 | Vasilyevka CPS | 4+4 | 0.06 | 0.97 | 1.5 | 120 | -0.53 | 0 | 4.2 | 4.73 | 4.73 | 35/10
271 | V.Oktyabr | 4+4 | 1.22 | 1.5 | 120 | -0.28 | 0 | 4.2 | 4.48 | 4.48 |  | 1.05 | 271 | V.Oktyabr | 4+4 | 0.19 | 1.41 | 1.5 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | 35/10
272 | V.Arkhangelskoe | 2,5+2,5 | 0.48 | 1.5 | 45 | -1.02 | 0 | 2.625 | 3.645 | 3.645 |  | 1.05 | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.07 | 0.55 | 1.5 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | 35/10
273 | Leshchanaya | 2,5+2,5 | 1.63 | 1.5 | 45 | 0.13 | 0 | 2.625 | 2.495 | 2.495 |  | 1.05 | 273 | Leshchanaya | 2,5+2,5 | 0.18 | 1.81 | 1.5 | 45 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | 35/10
274 | Muzhichye | 4+2,5 | 0.53 | 1.5 | 45 | -0.97 | 0 | 2.625 | 3.595 | 3.595 |  | 1.05 | 274 | Muzhichye | 4+2,5 | 0.11 | 0.64 | 1.5 | 45 | -0.86 | 0 | 2.625 | 3.485 | 3.485 | 35/10
275 | Rudnya | 4+4 | 0.44 | 1.5 | 120 | -1.06 | 0 | 4.2 | 5.26 | 5.26 |  | 1.05 | 275 | Rudnya | 4+4 | 0.03 | 0.47 | 1.5 | 120 | -1.03 | 0 | 4.2 | 5.23 | 5.23 | 35/10
276 | St. Melovaya | 4+4 | 0.85 | 0 | 0 | 0.85 | 0 | 4.2 | 3.35 | 3.35 |  | 1.05 | 276 | St. Melovaya | 4+4 | 0.07 | 0.92 | 0 | 0 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | 35/10
277 | St. Kriusha | 2,5+4 | 1.15 | 0 | 0 | 1.15 | 0 | 2.625 | 1.475 | 1.475 |  | 1.05 | 277 | St. Kriusha | 2,5+4 | 0.04 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | 35/10
278 | Lozovaya | 4+4 | 0.73 | 0 | 0 | 0.73 | 0 | 4.2 | 3.47 | 3.47 |  | 1.05 | 278 | Lozovaya | 4+4 | 0.3 | 1.03 | 0 | 0 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | 35/10
279 | Pavlovsk-1 | 4+4 | 2.17 | 1 | 120 | 1.17 | 0 | 4.2 | 3.03 | 3.03 |  | 1.05 | 279 | Pavlovsk-1 | 4+4 | 0.23 | 2.4 | 1 | 120 | 1.4 | 0 | 4.2 | 2.8 | 2.8 | 35/10
280 | Losevo CPS | 4+4 | 2.98 | 0 | 0 | 2.98 | 0 | 4.2 | 1.22 | 1.22 |  | 1.05 | 280 | Losevo CPS | 4+4 | 0.05 | 3.03 | 0 | 0 | 3.03 | 0 | 4.2 | 1.17 | 1.17 | 35/10
281 | Gavrilsk | 4+4 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 |  | 1.05 | 281 | Gavrilsk | 4+4 | 0.03 | 0.65 | 0 | 0 | 0.65 | 0 | 4.2 | 3.55 | 3.55 | 35/10
282 | Pokrovka | 4+2,5 | 0.98 | 0 | 0 | 0.98 | 0 | 2.625 | 1.645 | 1.645 |  | 1.05 | 282 | Pokrovka | 4+2,5 | 0.02 | 1 | 0 | 0 | 1 | 0 | 2.625 | 1.625 | 1.625 | 35/10
283 | Vorontsovka | 4+4 | 2.57 | 1.5 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 |  | 1.05 | 283 | Vorontsovka | 4+4 | 0.62 | 3.19 | 1.5 | 120 | 1.69 | 0 | 4.2 | 2.51 | 2.51 | 35/10
284 | А.Donskaya | 2,5+2,5 | 1.15 | 1.5 | 45 | -0.35 | 0 | 2.625 | 2.975 | 2.975 |  | 1.05 | 284 | А.Donskaya | 2,5+2,5 | 0.06 | 1.21 | 1.5 | 45 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | 35/10
285 | Petrovka | 2,5+4 | 1.54 | 1.5 | 45 | 0.04 | 0 | 2.625 | 2.585 | 2.585 |  | 1.05 | 285 | Petrovka | 2,5+4 | 0.04 | 1.58 | 1.5 | 45 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | 35/10
286 | Monastyrshchina | 4+4 | 0.9 | 1.5 | 120 | -0.6 | 0 | 4.2 | 4.8 | 4.8 |  | 1.05 | 286 | Monastyrshchina | 4+4 | 0.1 | 1 | 1.5 | 120 | -0.5 | 0 | 4.2 | 4.7 | 4.7 | 35/10
287 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 |  | 1.05 | 287 | Zhuravka | 1,8+2,5 | 0 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | 35/10
288 | Dyachenkovo | 2,5+2,5 | 1.63 | 1.5 | 45 | 0.13 | 0 | 2.625 | 2.495 | 2.495 |  | 1.05 | 288 | Dyachenkovo | 2,5+2,5 | 0.46 | 2.09 | 1.5 | 45 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | 35/10
289 | Radchenskaya | 1,6+2,5 | 0.74 | 0 | 0 | 0.74 | 0 | 1.68 | 0.94 | 0.94 |  | 1.05 | 289 | Radchenskaya | 1,6+2,5 | 0.2 | 0.94 | 0 | 0 | 0.94 | 0 | 1.68 | 0.74 | 0.74 | 35/10
290 | Rossiya | 4+4 | 1.39 | 1.5 | 120 | -0.11 | 0 | 4.2 | 4.31 | 4.31 |  | 1.05 | 290 | Rossiya | 4+4 | 0.08 | 1.47 | 1.5 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | 35/10
291 | Pervomayskaya | 4+4 | 0.39 | 1.5 | 120 | -1.11 | 0 | 4.2 | 5.31 | 5.31 |  | 1.05 | 291 | Pervomayskaya | 4+4 | 0.01 | 0.4 | 1.5 | 120 | -1.1 | 0 | 4.2 | 5.3 | 5.3 | 35/10
292 | Podkolodnovka | 2,5+3,2 | 1.09 | 0 | 0 | 1.09 | 0 | 2.625 | 1.535 | 1.535 |  | 1.05 | 292 | Podkolodnovka | 2,5+3,2 | 0.07 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 | 35/10
293 | Yuzhny | 2,5+2,5 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 |  | 1.05 | 293 | Yuzhny | 2,5+2,5 | 0 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 | 35/10
| TOTAL: |  | 1314.4787 | [6 empty] | 1074.686 |  |  | 2: TOTAL:; min. 12: 851.3615
| deficit | [8 empty] | 66.08 |  |  | 2: deficit; min. 12: 134.59
| proficit | [8 empty] | 1008.606 |  |  | 2: proficit; min. 12: 716.7715

## Смоленскэнерго 3
[9 empty] | table 1 | [11 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Current deficit/ proficit, MVA |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main substation, MVA | Expected dificit / proficit, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.24 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.46 | 0.46 | opened | 1 | Gerchiki 35/10 | 2.5 | 0.4 | 0.64 | 0.7 | 24 hours | -0.06 | 0 | 0.7 | 0.06 | 0.06 | opened
2 | Verkhovye 35/10 | 4 | 0.59 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.77 | 0.77 | opened | 2 | Verkhovye 35/10 | 4 | 0 | 0.59 | 1.36 | 24 hours | -0.77 | 0 | 1.36 | 0.77 | 0.77 | opened
3 | Neykovo 35/10 | 2.5 | 0.14 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.59 | 1.59 | opened | 3 | Neykovo 35/10 | 2.5 | 0 | 0.14 | 1.73 | 24 hours | -1.59 | 0 | 1.73 | 1.59 | 1.59 | opened
4 | Merlino 110/35/10 | 6.3 | 0.34 | 0.34 | 24 hours | 0.34 | 0 | 0.34 | 0 | 0 | opened | 4 | Merlino 110/35/10 | 6.3 | 0 | 0.34 | 0.34 | 24 hours | 0 | 0 | 0.34 | 0 | 0 | opened
| Nom. capacity MV, МVА | 6.3 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0 | 0.1 | 0.1 |  | 0 | 0 | 0.1 | 0
| Nom. capacity LV, МVА | 6.3 | 0.24 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.24 | 0.24 | 24 hours | 0 | 0 | 0.24 | 0
5 | Belyaevo 35/10 | 1.6 | 0.3 | 2.11 | 24 hours | 2.11 | 0 | 2.11 | 1.81 | 1.81 | opened | 5 | Belyaevo 35/10 | 1.6 | 0 | 0.3 | 2.11 | 24 hours | -1.81 | 0 | 2.11 | 1.81 | 1.81 | opened
6 | Zaozerye 35/10 | 1.6 | 0.17 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.68 | 0.68 | opened | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.17 | 0.85 | 24 hours | -0.68 | 0 | 0.85 | 0.68 | 0.68 | opened
7 | Selezni 35/10 | 2.5 | 0.37 | 2.21 | 24 hours | 2.21 | 0 | 2.21 | 1.84 | 1.84 | opened | 7 | Selezni 35/10 | 2.5 | 0 | 0.37 | 2.21 | 24 hours | -1.84 | 0 | 2.21 | 1.84 | 1.84 | opened
8 | Logovo 110/10 | 6.3 | 0.4 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.96 | 0.96 | opened | 8 | Logovo 110/10 | 6.3 | 0 | 0.4 | 1.36 | 24 hours | -0.96 | 0 | 1.36 | 0.96 | 0.96 | opened
9 | Dubrovka 35/10 | 2.5 | 0.24 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 1.12 | 1.12 | opened | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.34 | 1.36 | 24 hours | -1.02 | 0 | 1.36 | 1.02 | 1.02 | opened
10 | Svistovichi 35/10 | 2.5 | 0.28 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.57 | 0.57 | opened | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.28 | 0.85 | 24 hours | -0.57 | 0 | 0.85 | 0.57 | 0.57 | opened
11 | Elsha 35/10 | 1.6 | 0.09 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.76 | 0.76 | opened | 11 | Elsha 35/10 | 1.6 | 0 | 0.09 | 0.85 | 24 hours | -0.76 | 0 | 0.85 | 0.76 | 0.76 | opened
12 | Sapsho 35/10 | 4 | 0.88 | 2.12 | 24 hours | 2.12 | 0 | 2.12 | 1.24 | 1.24 | opened | 12 | Sapsho 35/10 | 4 | 0.18 | 1.06 | 2.12 | 24 hours | -1.06 | 0 | 2.12 | 1.06 | 1.06 | opened
13 | Divo 110/10 | 2.5 | 0.6 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.25 | 0.25 | opened | 13 | Divo 110/10 | 2.5 | 0.14 | 0.74 | 0.85 | 24 hours | -0.11 | 0 | 0.85 | 0.11 | 0.11 | opened
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 24 hours | 1.02 | 0 | 1.02 | 0.57 | 0.57 | opened | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.45 | 1.02 | 24 hours | -0.57 | 0 | 1.02 | 0.57 | 0.57 | opened
15 | Zamoshye 35/10 | 2.5 | 0.07 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.61 | 0.61 | opened | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.07 | 0.68 | 24 hours | -0.61 | 0 | 0.68 | 0.61 | 0.61 | opened
16 | Loino 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 16 | Loino 35/10 | 2.5 | 0 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
17 | Rokot 35/10 | 2.5 | 0.29 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.01 | 1.01 | opened | 17 | Rokot 35/10 | 2.5 | 0 | 0.29 | 1.3 | 24 hours | -1.01 | 0 | 1.3 | 1.01 | 1.01 | opened
18 | Nikontsy 35/10 | 2.5 | 0.15 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.7 | 0.7 | opened | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.15 | 0.85 | 24 hours | -0.7 | 0 | 0.85 | 0.7 | 0.7 | opened
19 | Batishchevo 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.09 | 1.73 | 24 hours | -1.64 | 0 | 1.73 | 1.64 | 1.64 | opened
20 | Vasino 35/10 | 2.5 | 0.31 | 0 | 24 hours | 0 | 0 | 0 | -0.31 | -0.31 | closed | 20 | Vasino 35/10 | 2.5 | 0 | 0.31 | 0 | 24 hours | 0.31 | 0 | 0 | -0.31 | -0.31 | closed
21 | Bulgakovo 35/10 | 2.5 | 0.26 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.47 | 1.47 | opened | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.26 | 1.73 | 24 hours | -1.47 | 0 | 1.73 | 1.47 | 1.47 | opened
22 | Spas-Ugly 35/10 | 1.6 | 0.16 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.52 | 0.52 | opened | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.16 | 0.68 | 24 hours | -0.52 | 0 | 0.68 | 0.52 | 0.52 | opened
23 | Tretyakovo 35/10 | 4 | 0.25 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.3 | 2.3 | opened | 23 | Tretyakovo 35/10 | 4 | 0 | 0.25 | 2.55 | 24 hours | -2.3 | 0 | 2.55 | 2.3 | 2.3 | opened
24 | Velisto 35/10 | 2.5 | 0.09 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.21 | 1.21 | opened | 24 | Velisto 35/10 | 2.5 | 0 | 0.09 | 1.3 | 24 hours | -1.21 | 0 | 1.3 | 1.21 | 1.21 | opened
25 | Baturino 35/10 | 1.6 | 0.1 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.75 | 0.75 | opened | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.28 | 0.85 | 24 hours | -0.57 | 0 | 0.85 | 0.57 | 0.57 | opened
26 | Pechatniki 35/10 | 2.5 | 0.34 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.12 | 3.12 | opened | 26 | Pechatniki 35/10 | 2.5 | 0 | 0.34 | 3.46 | 24 hours | -3.12 | 0 | 3.46 | 3.12 | 3.12 | opened
27 | Garistovo 35/10 | 1.6 | 0.18 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.67 | 0.67 | opened | 27 | Garistovo 35/10 | 1.6 | 0 | 0.18 | 0.85 | 24 hours | -0.67 | 0 | 0.85 | 0.67 | 0.67 | opened
28 | Bezzaboty 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.09 | 1.73 | 24 hours | -1.64 | 0 | 1.73 | 1.64 | 1.64 | opened
29 | Vysokoe 35/10 | 2.5 | 0.2 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.35 | 2.35 | opened | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.2 | 2.55 | 24 hours | -2.35 | 0 | 2.55 | 2.35 | 2.35 | opened
30 | Zaytsevo 35/10 | 1.6 | 0.35 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.5 | 0.5 | opened | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.35 | 0.85 | 24 hours | -0.5 | 0 | 0.85 | 0.5 | 0.5 | opened
31 | Saveevo 35/10 | 2.5 | 0.46 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.39 | 0.39 | opened | 31 | Saveevo 35/10 | 2.5 | 0 | 0.46 | 0.85 | 24 hours | -0.39 | 0 | 0.85 | 0.39 | 0.39 | opened
32 | Gorenovo 35/10 | 1.6 | 0.26 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.29 | 2.29 | opened | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.26 | 2.55 | 24 hours | -2.29 | 0 | 2.55 | 2.29 | 2.29 | opened
33 | Shpunty 35/10 | 2.5 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 33 | Shpunty 35/10 | 2.5 | 0.42 | 0.65 | 0.85 | 24 hours | -0.2 | 0 | 0.85 | 0.2 | 0.2 | opened
34 | Kadino 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 34 | Kadino 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
35 | Стегримово 35/10 | 2.5 | 0.08 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.81 | 2.81 | opened | 35 | Стегримово 35/10 | 2.5 | 0 | 0.08 | 2.89 | 24 hours | -2.81 | 0 | 2.89 | 2.81 | 2.81 | opened
36 | Zhukovo 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
37 | Mikshino 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 37 | Mikshino 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
38 | Petrovichi 35/10 | 2.5 | 0.18 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.37 | 2.37 | opened | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.18 | 2.55 | 24 hours | -2.37 | 0 | 2.55 | 2.37 | 2.37 | opened
39 | Mikulichi 35/10 | 2.5 | 0.51 | 4.59 | 24 hours | 4.59 | 0 | 4.59 | 4.08 | 4.08 | opened | 39 | Mikulichi 35/10 | 2.5 | 0.07 | 0.58 | 4.59 | 24 hours | -4.01 | 0 | 4.59 | 4.01 | 4.01 | opened
40 | Nedeykovichi 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
41 | Posyolki 110/35/10 | 6.3 | 0.71 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.23 | 0.23 | opened | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.71 | 0.94 | 24 hours | -0.23 | 0 | 0.94 | 0.23 | 0.23 | opened
42 | Kuzmichi 35/10 | 2.5 | 0.34 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.39 | 1.39 | opened | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.34 | 1.73 | 24 hours | -1.39 | 0 | 1.73 | 1.39 | 1.39 | opened
43 | Maksheevo 110/10 | 6.3 | 0.41 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.14 | 2.14 | opened | 43 | Maksheevo 110/10 | 6.3 | 0 | 0.41 | 2.55 | 24 hours | -2.14 | 0 | 2.55 | 2.14 | 2.14 | opened
44 | Putkovo 35/10 | 1.8 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 44 | Putkovo 35/10 | 1.8 | 0.06 | 0.29 | 0.85 | 24 hours | -0.56 | 0 | 0.85 | 0.56 | 0.56 | opened
45 | Uspenskoe 35/10 | 2.5 | 0.49 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.06 | 2.06 | opened | 45 | Uspenskoe 35/10 | 2.5 | 0 | 0.49 | 2.55 | 24 hours | -2.06 | 0 | 2.55 | 2.06 | 2.06 | opened
46 | Kalpita 35/10 | 1.6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 46 | Kalpita 35/10 | 1.6 | 0 | 0.06 | 0.85 | 24 hours | -0.79 | 0 | 0.85 | 0.79 | 0.79 | opened
47 | Kasnya 110/10 | 2.5 | 0.32 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.14 | 3.14 | opened | 47 | Kasnya 110/10 | 2.5 | 0 | 0.32 | 3.46 | 24 hours | -3.14 | 0 | 3.46 | 3.14 | 3.14 | opened
48 | Akatovo 35/10 | 1.6 | 1.01 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 1.88 | 1.88 | opened | 48 | Akatovo 35/10 | 1.6 | 1.2 | 2.21 | 2.89 | 24 hours | -0.68 | 0 | 2.89 | 0.68 | 0.68 | opened
49 | Gorki 35/10 | 1.6 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 49 | Gorki 35/10 | 1.6 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.06 | 0.06 | opened | 50 | Druzhba 35/10 | 2.5 | 0 | 0.79 | 0.85 | 24 hours | -0.06 | 0 | 0.85 | 0.06 | 0.06 | opened
51 | NS-21 110/10 | 16 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened
52 | NS-22 110/35/10 | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0 | 0 | opened | 52 | NS-22 110/35/10 | 25 | 1.32 | 3.41 | 3.41 | 24 hours | 0 | 0 | 3.41 | 0 | 0 | opened
| Nom. capacity MV, МVА | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 1.32 | 3.41 | 3.41 | 24 hours | 0 | 0 | 3.41 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.47 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.99 | 2.99 | opened | 53 | Shuyskoe 35/10 | 2.5 | 0.05 | 0.52 | 3.46 | 24 hours | -2.94 | 0 | 3.46 | 2.94 | 2.94 | opened
54 | Torbeevo 110/10 | 6.3 | 0.35 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.54 | 2.54 | opened | 54 | Torbeevo 110/10 | 6.3 | 0.08 | 0.43 | 2.89 | 24 hours | -2.46 | 0 | 2.89 | 2.46 | 2.46 | opened
55 | Leuzdovo 35/10 | 1 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 55 | Leuzdovo 35/10 | 1 | 0.3 | 0.42 | 0.68 | 24 hours | -0.26 | 0 | 0.68 | 0.26 | 0.26 | opened
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.56 | 1.56 | opened | 56 | Maltsevo 35/10 | 2.5 | 0.01 | 0.18 | 1.73 | 24 hours | -1.55 | 0 | 1.73 | 1.55 | 1.55 | opened
57 | Avrora 35/10 | 2.5 | 0.09 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.59 | 0.59 | opened | 57 | Avrora 35/10 | 2.5 | 2.77 | 2.86 | 0.68 | 24 hours | 2.18 | 0 | 0.68 | -2.18 | -2.18 | closed
58 | Bekhteevo 35/10 | 2.5 | 0.08 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.6 | 0.6 | opened | 58 | Bekhteevo 35/10 | 2.5 | 0.07 | 0.15 | 0.68 | 24 hours | -0.53 | 0 | 0.68 | 0.53 | 0.53 | opened
59 | Sereda 35/10 | 2.5 | 0.38 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.3 | 0.3 | opened | 59 | Sereda 35/10 | 2.5 | 0 | 0.38 | 0.68 | 24 hours | -0.3 | 0 | 0.68 | 0.3 | 0.3 | opened
60 | Mikhali 35/10 | 2.5 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 60 | Mikhali 35/10 | 2.5 | 0 | 0.06 | 0.85 | 24 hours | -0.79 | 0 | 0.85 | 0.79 | 0.79 | opened
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 24 hours | 0 | 0 | 0 | -0.06 | -0.06 | closed | 61 | Mytishino 35/10 | 1.6 | 0 | 0.06 | 0 | 24 hours | 0.06 | 0 | 0 | -0.06 | -0.06 | closed
62 | Zakharyevskoe 35/10 | 1.6 | 0.19 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.66 | 0.66 | opened | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.19 | 0.85 | 24 hours | -0.66 | 0 | 0.85 | 0.66 | 0.66 | opened
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 63 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 24 hours | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
64 | Baskakovka 35/10 | 4 | 0.21 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.52 | 1.52 | opened | 64 | Baskakovka 35/10 | 4 | 0 | 0.21 | 1.73 | 24 hours | -1.52 | 0 | 1.73 | 1.52 | 1.52 | opened
65 | Ekimtsevo 110/10 | 2.5 | 0.36 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.37 | 1.37 | opened | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0.36 | 1.73 | 24 hours | -1.37 | 0 | 1.73 | 1.37 | 1.37 | opened
Two-transformer substations | [11 empty] | 1: Two-transformer substations
66 | Smolensk 1 (FPC) 110/35/6 | 40+40 | 41.67 | 5.68 | 120 | 35.99 | 0 | 42 | 6.01 | 6.01 | opened | 66 | Smolensk 1 (FPC) 110/35/6 | 40+40 | 15.25 | 56.92 | 11.3 | 120 | 45.62 | 0 | 42 | -3.62 | -3.62 | closed
| Nom. capavity MV, МVА | 40+40 | 4.9 | 3.76 |  | 1.14 | 0 | 42 | 40.86 |  |  |  | Nom. capavity MV, МVА | 40+40 | 4.48 | 9.38 | 9.38 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 36.77 | 1.92 | 120 | 34.85 | 0 | 42 | 7.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 10.77 | 47.54 | 1.92 | 120 | 45.62 | 0 | 42 | -3.62
67 | Water intake 35/6 | 4+4 | 2.93 | 1.2 | 120 | 1.73 | 0 | 4.2 | 2.47 | 2.47 | opened | 67 | Water intake 35/6 | 4+4 | 2.11 | 5.04 | 1.2 | 120 | 3.84 | 0 | 4.2 | 0.36 | 0.36 | opened
68 | Tychinino 35/10 | 4+4 | 1.1 | 0.91 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened | 68 | Tychinino 35/10 | 4+4 | 0.13 | 1.23 | 0.91 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | opened
69 | Ryabtsevo 35/10 | 4+4 | 2.4 | 0 | 120 | 2.4 | 0 | 4.2 | 1.8 | 1.8 | opened | 69 | Ryabtsevo 35/10 | 4+4 | 2.5 | 4.9 | 0 | 120 | 4.9 | 0 | 4.2 | -0.7 | -0.7 | closed
70 | Smolensk 2 110/6 | 40+40 | 16.21 | 6.41 | 120 | 9.8 | 0 | 42 | 32.2 | 32.2 | opened | 70 | Smolensk 2 110/6 | 40+40 | 1.42 | 17.63 | 6.41 | 120 | 11.22 | 0 | 42 | 30.78 | 30.78 | opened
71 | Vostochnaya 110/6 | 25+16 | 5.71 | 0 | 120 | 5.71 | 0 | 16.8 | 11.09 | 11.09 | opened | 71 | Vostochnaya 110/6 | 25+16 | 0 | 5.71 | 0 | 120 | 5.71 | 0 | 16.8 | 11.09 | 11.09 | opened
72 | Diffuzion 110/6 | 25+25 | 14.69 | 1.06 | 120 | 13.63 | 0 | 26.25 | 12.62 | 12.62 | opened | 72 | Diffuzion 110/6 | 25+25 | 17.39 | 32.08 | 1.06 | 120 | 31.02 | 0 | 26.25 | -4.77 | -4.77 | closed
73 | Zavodskaya 110/35/10 | 16+16 | 17.31 | 17.07 | 120 | 0.24 | 0 | 16.8 | 16.56 | 13.12 | opened | 73 | Zavodskaya 110/35/10 | 16+16 | 14.31 | 31.62 | 22.84 | 120 | 8.78 | 0 | 16.8 | 8.02 | 8.02 | opened
| Nom. capacity MV, МVА | 16+16 | 15.1 | 11.42 |  | 3.68 | 0 | 16.8 | 13.12 |  |  |  | Nom. capacity MV, МVА | 16+16 | 2.09 | 17.19 | 17.19 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.21 | 5.65 | 120 | -3.44 | 0 | 16.8 | 20.24 |  |  |  | Nom. capacity LV, МVА | 16+16 | 12.22 | 14.43 | 5.65 | 120 | 8.78 | 0 | 16.8 | 8.02
74 | Yasennaya 35/6 | 10+10 | 8.98 | 0 | 120 | 8.98 | 0 | 10.5 | 1.52 | 1.52 | opened | 74 | Yasennaya 35/6 | 10+10 | 1.12 | 10.1 | 0 | 120 | 10.1 | 0 | 10.5 | 0.4 | 0.4 | opened
75 | Gnezodovo 35/6 | 7,5+7,5 | 4.32 | 0.42 | 120 | 3.9 | 0 | 7.875 | 3.975 | 3.975 | opened | 75 | Gnezodovo 35/6 | 7,5+7,5 | 1.2 | 5.52 | 0.42 | 120 | 5.1 | 0 | 7.875 | 2.775 | 2.775 | opened
76 | Zapadnaya 110/6 | 25+16 | 13.58 | 0.63 | 120 | 12.95 | 0 | 16.8 | 3.85 | 3.85 | opened | 76 | Zapadnaya 110/6 | 25+16 | 7.97 | 21.55 | 0.63 | 120 | 20.92 | 0 | 16.8 | -4.12 | -4.12 | closed
77 | Katyn 2 110/35/10 | 10+16 | 4.58 | 2.59 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened | 77 | Katyn 2 110/35/10 | 10+16 | 10.67 | 15.25 | 8.35 | 120 | 6.9 | 0 | 10.5 | 3.6 | 3.6 | opened
| Nom. capacity MV, МVА | 10+16 | 2.59 | 2.59 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 5.76 | 8.35 | 8.35 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.99 | 0 | 120 | 1.99 | 0 | 10.5 | 8.51 |  |  |  | Nom. capacity LV, МVА | 10+16 | 4.91 | 6.9 | 0 | 120 | 6.9 | 0 | 10.5 | 3.6
78 | Katyn 1 35/10 | 4+4 | 1.57 | 0.05 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | opened | 78 | Katyn 1 35/10 | 4+4 | 3.1 | 4.67 | 0.05 | 120 | 4.62 | 0 | 4.2 | -0.42 | -0.42 | closed
79 | Lubnya 35/10 | 4+4 | 1.33 | 0.13 | 120 | 1.2 | 0 | 4.2 | 3 | 3 | opened | 79 | Lubnya 35/10 | 4+4 | 2.26 | 3.59 | 0.13 | 120 | 3.46 | 0 | 4.2 | 0.74 | 0.74 | opened
80 | Kozino 110/35/10 | 10+10 | 8.41 | 6.51 | 120 | 1.9 | 0 | 10.5 | 8.6 | 8.6 | opened | 80 | Kozino 110/35/10 | 10+10 | 10.79 | 19.2 | 1.03 | 120 | 18.17 | 0 | 10.5 | -7.67 | -7.67 | closed
| Nom. capacity MV, МVА | 10+10 | 6.5 | 6.5 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 9.56 | 16.06 | 1.02 |  | 15.04 | 0 | 10.5 | -4.54
| Nom. capacity LV, МVА | 10+10 | 1.91 | 0.01 | 120 | 1.9 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.23 | 3.14 | 0.01 | 120 | 3.13 | 0 | 10.5 | 7.37
81 | Odintsovo 35/10 | 6,3+6,3 | 4.55 | 2.15 | 120 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened | 81 | Odintsovo 35/10 | 6,3+6,3 | 8.62 | 13.17 | 2.15 | 120 | 11.02 | 0 | 6.615 | -4.405 | -4.405 | closed
82 | Trudilovo 35/10 | 2,5+2,5 | 1.29 | 0.08 | 120 | 1.21 | 0 | 2.625 | 1.415 | 1.415 | opened | 82 | Trudilovo 35/10 | 2,5+2,5 | 0.78 | 2.07 | 0.08 | 120 | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened
83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 |  | 0 | 0 | 42 | 42 | 42 | opened | 83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 | 0 |  | 0 | 0 | 42 | 42 | 42 | opened
84 | Pronino 110/35/6 | 10+10 | 6.24 | 4.67 | 120 | 1.57 | 0 | 10.5 | 8.93 | 8.93 | opened | 84 | Pronino 110/35/6 | 10+10 | 2.03 | 8.27 | 6.7 | 120 | 1.57 | 0 | 10.5 | 8.93 | 8.93 | opened
| Nom. capacity MV, МVА | 10+10 | 3.48 | 3.48 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.03 | 5.51 | 5.51 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.76 | 1.19 | 120 | 1.57 | 0 | 10.5 | 8.93 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 2.76 | 1.19 | 120 | 1.57 | 0 | 10.5 | 8.93
85 | Olsha 35/10 | 2,5+2,5 | 0.92 | 0 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 85 | Olsha 35/10 | 2,5+2,5 | 1.48 | 2.4 | 0 | 120 | 2.4 | 0 | 2.625 | 0.225 | 0.225 | opened
86 | Krasny bor 35/6 | 4+4 | 2.58 | 0 | 120 | 2.58 | 0 | 4.2 | 1.62 | 1.62 | opened | 86 | Krasny bor 35/6 | 4+4 | 0.54 | 3.12 | 0 | 120 | 3.12 | 0 | 4.2 | 1.08 | 1.08 | opened
87 | Severnaya 110/35/6 | 25+25 | 17.69 | 6.13 | 120 | 11.56 | 0 | 26.25 | 14.69 | 14.69 | opened | 87 | Severnaya 110/35/6 | 25+25 | 6.29 | 23.98 | 10.49 | 120 | 13.49 | 0 | 26.25 | 12.76 | 12.76 | opened
| Nom. capacity MV, МVА | 25+25 | 3.54 | 3.54 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.36 | 7.9 | 7.9 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 14.15 | 2.59 | 120 | 11.56 | 0 | 26.25 | 14.69 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.93 | 16.08 | 2.59 | 120 | 13.49 | 0 | 26.25 | 12.76
88 | Peсhersk 35/6 | 4+4 | 2.59 | 0.34 | 120 | 2.25 | 0 | 4.2 | 1.95 | 1.95 | opened | 88 | Peсhersk 35/6 | 4+4 | 3.27 | 5.86 | 0.34 | 120 | 5.52 | 0 | 4.2 | -1.32 | -1.32 | closed
89 | Kolodnya 35/6 | 6,3+4 | 2.56 | 0 | 120 | 2.56 | 0 | 4.2 | 1.64 | 1.64 | opened | 89 | Kolodnya 35/6 | 6,3+4 | 0.85 | 3.41 | 0 | 120 | 3.41 | 0 | 4.2 | 0.79 | 0.79 | opened
90 | Tsentralnaya 110/10/6 | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18 | 11.18 | opened | 90 | Tsentralnaya 110/10/6 | 25+25 | 3.15 | 23.98 | 7.85 | 120 | 16.13 | 0 | 26.25 | 10.12 | 10.12 | opened
| Nom. capacity MV, МVА | 25+25 | 0 | 0 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 2.09 | 2.09 | 2.09 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.06 | 21.89 | 5.76 | 120 | 16.13 | 0 | 26.25 | 10.12
91 | Chernushki 110/10/6 | 25+25 | 18.02 | 2.12 | 120 | 15.9 | 0 | 26.25 | 10.35 | 10.35 | opened | 91 | Chernushki 110/10/6 | 25+25 | 16.1 | 34.12 | 2.12 | 120 | 32 | 0 | 26.25 | -5.75 | -5.75 | closed
| Nom. capacity MV, МVА | 25+25 | 6.43 | 0 |  | 6.43 | 0 | 26.25 | 19.82 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.92 | 12.35 | 0 |  | 12.35 | 0 | 26.25 | 13.9
| Nom. Capacity LV, МVА | 25+25 | 11.59 | 2.12 | 120 | 9.47 | 0 | 26.25 | 16.78 |  |  |  | Nom. Capacity LV, МVА | 25+25 | 10.18 | 21.77 | 2.12 | 120 | 19.65 | 0 | 26.25 | 6.6
92 | Yuzhnaya 110/35/6 | 40+40 | 32.46 | 7.03 | 120 | 25.43 | 0 | 42 | 16.57 | 16.57 | opened | 92 | Yuzhnaya 110/35/6 | 40+40 | 21.21 | 53.67 | 9.71 | 120 | 43.96 | 0 | 42 | -1.96 | -1.96 | closed
| Nom. capacity MV, МVА | 40+40 | 1.31 | 1.31 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, МVА | 40+40 | 2.68 | 3.99 | 3.99 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 31.15 | 5.72 | 120 | 25.43 | 0 | 42 | 16.57 |  |  |  | Nom. capacity LV, МVА | 40+40 | 18.52 | 49.67 | 5.72 | 120 | 43.95 | 0 | 42 | -1.95
93 | Karyernaya 110/35/6 | 16+16 | 3.21 | 2.39 | 120 | 0.82 | 0 | 16.8 | 15.98 | 15.98 | opened | 93 | Karyernaya 110/35/6 | 16+16 | 4.45 | 7.66 | 5.39 | 120 | 2.27 | 0 | 16.8 | 14.53 | 14.53 | opened
| Nom. capacity MV, МВА | 16+16 | 2.39 | 2.39 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МВА | 16+16 | 3 | 5.39 | 5.39 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0.82 | 0 | 120 | 0.82 | 0 | 16.8 | 15.98 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.45 | 2.27 | 0 | 120 | 2.27 | 0 | 16.8 | 14.53
94 | Koshchino 35/10 | 4+4 | 0.87 | 0.11 | 120 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened | 94 | Koshchino 35/10 | 4+4 | 0.02 | 0.89 | 0.11 | 120 | 0.78 | 0 | 4.2 | 3.42 | 3.42 | opened
95 | Kommunar 35/10 | 2,5+2,5 | 0.67 | 0.03 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened | 95 | Kommunar 35/10 | 2,5+2,5 | 0 | 0.67 | 0.03 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
96 | Kasplya 110/35/10 | 10+10 | 3.4 | 3.07 | 120 | 0.33 | 0 | 10.5 | 10.17 | 10.17 | opened | 96 | Kasplya 110/35/10 | 10+10 | 5.01 | 8.41 | 7.83 | 120 | 0.58 | 0 | 10.5 | 9.92 | 9.92 | opened
| Nom. capacity MV, МVА | 10+10 | 2.21 | 2.21 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.76 | 6.97 | 6.97 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.19 | 0.86 | 120 | 0.33 | 0 | 10.5 | 10.17 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.25 | 1.44 | 0.86 | 120 | 0.58 | 0 | 10.5 | 9.92
97 | Apolye 35/10 | 2,5+2,5 | 0.79 | 0.17 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 97 | Apolye 35/10 | 2,5+2,5 | 0.02 | 0.81 | 0.17 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
98 | Zhukovskaya 35/10 | 4+4 | 1.4 | 0.19 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened | 98 | Zhukovskaya 35/10 | 4+4 | 3.29 | 4.69 | 0.19 | 120 | 4.5 | 0 | 4.2 | -0.3 | -0.3 | closed
99 | Mazaltsevo 110/35/10 | 10+10 | 2.59 | 2.16 | 120 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | opened | 99 | Mazaltsevo 110/35/10 | 10+10 | 6.51 | 9.1 | 8.66 | 120 | 0.44 | 0 | 10.5 | 10.06 | 10.06 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 6.5 | 8.4 | 8.4 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.69 | 0.26 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.01 | 0.7 | 0.26 | 120 | 0.44 | 0 | 10.5 | 10.06
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 100 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
101 | Krasny 110/35/10 | 10+10 | 4.22 | 2.26 | 120 | 1.96 | 0 | 10.5 | 8.54 | 8.54 | opened | 101 | Krasny 110/35/10 | 10+10 | 3.37 | 7.59 | 3.43 | 120 | 4.16 | 0 | 10.5 | 6.34 | 6.34 | opened
| Nom. capacity MV, МVА | 10+10 | 1.8 | 1.8 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.17 | 2.97 | 2.97 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.42 | 0.46 | 120 | 1.96 | 0 | 10.5 | 8.54 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.2 | 4.62 | 0.46 | 120 | 4.16 | 0 | 10.5 | 6.34
102 | Voloelovo 35/10 | 2,5+2,5 | 0.04 | 0.01 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 102 | Voloelovo 35/10 | 2,5+2,5 | 0 | 0.04 | 0.01 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened | 103 | Kryukovo 35/10 | 2,5+2,5 | 0 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened
104 | Miganovo 35/10 | 2,5+2,5 | 1.18 | 0.49 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened | 104 | Miganovo 35/10 | 2,5+2,5 | 1.17 | 2.35 | 0.49 | 120 | 1.86 | 0 | 2.625 | 0.765 | 0.765 | opened
105 | Velizh 110/35/10 | 10+10 | 5.77 | 2.05 | 120 | 3.72 | 0 | 10.5 | 6.78 | 6.78 | opened | 105 | Velizh 110/35/10 | 10+10 | 1.75 | 7.52 | 2.16 | 120 | 5.36 | 0 | 10.5 | 5.14 | 5.14 | opened
| Nom. capacity MV, МVА | 10+10 | 1.38 | 1.38 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.11 | 1.49 | 1.49 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.39 | 0.67 | 120 | 3.72 | 0 | 10.5 | 6.78 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.64 | 6.03 | 0.67 | 120 | 5.36 | 0 | 10.5 | 5.14
106 | Chepli 35/10 | 2,5+2,5 | 0.4 | 0.09 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 106 | Chepli 35/10 | 2,5+2,5 | 0 | 0.4 | 0.09 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
107 | Demidov 110/35/10 | 10+16 | 5.52 | 1.14 | 120 | 4.38 | 0 | 10.5 | 6.12 | 6.12 | opened | 107 | Demidov 110/35/10 | 10+16 | 1.6 | 7.12 | 1.38 | 120 | 5.74 | 0 | 10.5 | 4.76 | 4.76 | opened
| Nom. capacity MV, МVА | 10+16 | 0.96 | 0.96 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.24 | 1.2 | 1.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.56 | 0.18 | 120 | 4.38 | 0 | 10.5 | 6.12 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.36 | 5.92 | 0.18 | 120 | 5.74 | 0 | 10.5 | 4.76
108 | Staroe selo 35/10 | 2,5+2,5 | 0.34 | 0.17 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 108 | Staroe selo 35/10 | 2,5+2,5 | 0 | 0.34 | 0.17 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
109 | Zakrutye 35/10 | 2,5+2,5 | 0.13 | 0 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 109 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.13 | 0 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
110 | Zaborye 35/10 | 1,6+2,5 | 0.34 | 0.21 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 110 | Zaborye 35/10 | 1,6+2,5 | 0 | 0.34 | 0.21 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
111 | Mikhailovskoe 110/35/10 | 10+10 | 1.07 | 0.73 | 120 | 0.34 | 0 | 10.5 | 10.16 | 10.16 | opened | 111 | Mikhailovskoe 110/35/10 | 10+10 | 0.4 | 1.47 | 0.91 | 120 | 0.56 | 0 | 10.5 | 9.94 | 9.94 | opened
| Nom. capacity MV, МVА | 10+10 | 0.31 | 0.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.18 | 0.49 | 0.49 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.76 | 0.42 | 120 | 0.34 | 0 | 10.5 | 10.16 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 0.98 | 0.42 | 120 | 0.56 | 0 | 10.5 | 9.94
112 | Kardymovo 110/35/10 | 10+16 | 5.69 | 3.2 | 120 | 2.49 | 0 | 10.5 | 8.01 | 8.01 | opened | 112 | Kardymovo 110/35/10 | 10+16 | 7.85 | 13.54 | 5.37 | 120 | 8.17 | 0 | 10.5 | 2.33 | 2.33 | opened
| Nom. capacity MV, МVА | 10+16 | 2.58 | 2.58 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 2.17 | 4.75 | 4.75 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.11 | 0.62 | 120 | 1.49 | 0 | 10.5 | 9.01 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.68 | 7.79 | 0.62 | 120 | 7.17 | 0 | 10.5 | 3.33
113 | Sinkovo 35/6 | 4+2,5 | 0.44 | 0.16 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 113 | Sinkovo 35/6 | 4+2,5 | 0 | 0.44 | 0.16 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
114 | Kamenka 35/10 | 2,5+2,5 | 1.4 | 0.42 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened | 114 | Kamenka 35/10 | 2,5+2,5 | 0.94 | 2.34 | 0.42 | 120 | 1.92 | 0 | 2.625 | 0.705 | 0.705 | opened
115 | Solovyevo 35/10 | 4+4 | 0.28 | 0.04 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 115 | Solovyevo 35/10 | 4+4 | 0.13 | 0.41 | 0.04 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened
116 | Rudnya (FPC) 110/35/10 | 10+16 | 8.33 | 1.87 | 120 | 6.46 | 0 | 10.5 | 4.04 | 4.04 | opened | 116 | Rudnya (FPC) 110/35/10 | 10+16 | 2.24 | 10.57 | 2.38 | 120 | 8.19 | 0 | 10.5 | 2.31 | 2.31 | opened
| Nom. capacity MV, МVА | 10+16 | 0.94 | 0.94 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.51 | 1.45 | 1.45 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.39 | 0.93 | 120 | 6.46 | 0 | 10.5 | 4.04 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.73 | 9.12 | 0.93 | 120 | 8.19 | 0 | 10.5 | 2.31
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.2 | 0.75 | 120 | -0.55 | 0 | 2.625 | 3.175 | 3.175 | opened | 117 | Zhichitsy 35/10 | 2,5+2,5 | 0 | 0.2 | 0.75 | 120 | -0.55 | 0 | 2.625 | 3.175 | 3.175 | opened
118 | Mikulino 35/10 | 6,3+6,3 | 0.88 | 1.1 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.835 | opened | 118 | Mikulino 35/10 | 6,3+6,3 | 0.18 | 1.06 | 1.1 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.52 | 0.74 | 120 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | opened | 119 | Lyubavichi 35/10 | 2,5+2,5 | 0.3 | 0.82 | 0.74 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
120 | Kazimirovo 35/10 | 4+4 | 0.12 | 0.02 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened | 120 | Kazimirovo 35/10 | 4+4 | 0.03 | 0.15 | 0.02 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | opened
121 | Golynki 110/35/6 | 25+25 | 4.58 | 2.91 | 120 | 1.67 | 0 | 26.25 | 24.58 | 24.58 | opened | 121 | Golynki 110/35/6 | 25+25 | 5.89 | 10.47 | 8.61 | 120 | 1.86 | 0 | 26.25 | 24.39 | 24.39 | opened
| Nom. Capacity MV, МVА | 25+25 | 2.75 | 2.75 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, МVА | 25+25 | 5.7 | 8.45 | 8.45 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.83 | 0.16 | 120 | 1.67 | 0 | 26.25 | 24.58 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.19 | 2.02 | 0.16 | 120 | 1.86 | 0 | 26.25 | 24.39
122 | Belei 35/10 | 2,5+2,5 | 1.61 | 0.75 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | opened | 122 | Belei 35/10 | 2,5+2,5 | 4.31 | 5.92 | 0.75 | 120 | 5.17 | 0 | 2.625 | -2.545 | -2.545 | closed
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.15 | 1.45 | 120 | 1.7 | 0 | 6.615 | 4.915 | 4.915 | opened | 123 | Ponizovye 110/35/10 | 6,3+6,3 | 0.18 | 3.33 | 1.45 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.39 | 1.39 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 1.39 | 1.39 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.76 | 0.06 | 120 | 1.7 | 0 | 6.615 | 4.915 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.18 | 1.94 | 0.06 | 120 | 1.88 | 0 | 6.615 | 4.735
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 124 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
125 | Safonovo 110/6 | 15+20 | 9.25 | 0.06 | 120 | 9.19 | 0 | 15.75 | 6.56 | 6.56 | opened | 125 | Safonovo 110/6 | 15+20 | 5.42 | 14.67 | 0.06 | 120 | 14.61 | 0 | 15.75 | 1.14 | 1.14 | opened
126 | Gornaya 110/35/6 | 25+25 | 11.7 | 11.58 | 120 | 0.12 | 0 | 26.25 | 26.13 | 26.13 | opened | 126 | Gornaya 110/35/6 | 25+25 | 5.05 | 16.75 | 16.47 | 120 | 0.28 | 0 | 26.25 | 25.97 | 25.97 | opened
| Nom. capacity MV, МVА | 25+25 | 6.91 | 6.91 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.89 | 11.8 | 11.8 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 4.79 | 4.67 | 120 | 0.12 | 0 | 26.25 | 26.13 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.16 | 4.95 | 4.67 | 120 | 0.28 | 0 | 26.25 | 25.97
127 | Water intake 35/6 | 6,3+4 | 1.68 | 0.69 | 120 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | opened | 127 | Water intake 35/6 | 6,3+4 | 1.53 | 3.21 | 0.69 | 120 | 2.52 | 0 | 4.2 | 1.68 | 1.68 | opened
128 | Vadino 35/10 | 4+4 | 1.23 | 0 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened | 128 | Vadino 35/10 | 4+4 | 1.91 | 3.14 | 0 | 120 | 3.14 | 0 | 4.2 | 1.06 | 1.06 | opened
129 | ZSSK 35/6 | 4+4 | 1.61 | 0.75 | 120 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 129 | ZSSK 35/6 | 4+4 | 1.03 | 2.64 | 0.75 | 120 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened
130 | Yanovo 35/10 | 4+6,3 | 0.27 | 0.05 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | opened | 130 | Yanovo 35/10 | 4+6,3 | 0 | 0.27 | 0.05 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | opened
131 | Kapyrevshchina 35/10 | 4+4 | 1.26 | 0.22 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened | 131 | Kapyrevshchina 35/10 | 4+4 | 0 | 1.26 | 0.22 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened
132 | Miropolye 35/10 | 2,5+2,5 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened | 132 | Miropolye 35/10 | 2,5+2,5 | 0 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 3.34 | 1.34 | 120 | 2 | 0 | 5.88 | 3.88 | 1.88 | открыт | 133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.83 | 5.17 | 2.62 | 120 | 2.55 | 0 | 5.88 | 3.33 | 3.33 | opened
| Nom. capacity MV, МVА | 5,6+6,3 | 0.91 | 0.91 |  | 0 | 1 | 5.88 | 4.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 1.28 | 2.19 | 2.19 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.43 | 0.43 | 120 | 2 | 2 | 5.88 | 1.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.55 | 2.98 | 0.43 | 120 | 2.55 | 0 | 5.88 | 3.33
134 | Alferovo 35/10 | 2,5+2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened | 134 | Alferovo 35/10 | 2,5+2,5 | 0.4 | 0.59 | 0.2 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
135 | Kasulino 35/10 | 2,5+2,5 | 0.15 | 0 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened | 135 | Kasulino 35/10 | 2,5+2,5 | 0.52 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | opened
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.28 | 0.15 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.35 | 0.63 | 0.15 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened
137 | Glinka 110/35/10 | 10+6,3 | 2 | 0.44 | 120 | 1.56 | 0 | 6.615 | 5.055 | 3.055 | opened | 137 | Glinka 110/35/10 | 10+6,3 | 0.95 | 2.95 | 0.62 | 120 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.33 | 0.33 |  | 0 | 1 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.18 | 0.51 | 0.51 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.67 | 0.11 | 120 | 1.56 | 2 | 6.615 | 3.055 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.77 | 2.44 | 0.11 | 120 | 2.33 | 0 | 6.615 | 4.285
138 | Dobromino 35/10 | 2,5+2,5 | 0.24 | 0 | 120 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | opened | 138 | Dobromino 35/10 | 2,5+2,5 | 0.14 | 0.38 | 0 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
139 | Bely kholm 35/10 | 1,6+1,6 | 0.09 | 0 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 139 | Bely kholm 35/10 | 1,6+1,6 | 0.04 | 0.13 | 0 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
140 | Dukhovshchina 110/35/10 | 10+10 | 3.26 | 1.89 | 120 | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened | 140 | Dukhovshchina 110/35/10 | 10+10 | 1.67 | 4.93 | 2.94 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened
| Nom. capacity MV, МVА | 10+10 | 1.63 | 1.63 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.05 | 2.68 | 2.68 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.63 | 0.26 | 120 | 1.37 | 0 | 10.5 | 9.13 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.62 | 2.25 | 0.26 | 120 | 1.99 | 0 | 10.5 | 8.51
141 | Zimets 35/10 | 4+4 | 0.3 | 0.06 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 141 | Zimets 35/10 | 4+4 | 0 | 0.3 | 0.06 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened
142 | Beresnevo 35/10 | 1,6+1,6 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 142 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
143 | Prechistoe 110/35/10 | 6,3+6,3 | 1.92 | 0.14 | 120 | 1.78 | 0 | 6.615 | 4.835 | 4.835 | opened | 143 | Prechistoe 110/35/10 | 6,3+6,3 | 0.36 | 2.28 | 0.14 | 120 | 2.14 | 0 | 6.615 | 4.475 | 4.475 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.34 | 0 |  | 1.34 | 0 | 6.615 | 5.275 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 1.7 | 0 |  | 1.7 | 0 | 6.615 | 4.915
| Nom. capacity LV, МVА | 6,3+6,3 | 0.58 | 0.14 | 120 | 0.44 | 0 | 6.615 | 6.175 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.58 | 0.14 | 120 | 0.44 | 0 | 6.615 | 6.175
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 144 | Vorontsovo 35/10 | 2,5+2,5 | 0 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
145 | Ozyorny 35/10 | 6,3+6,3 | 1.32 | 0.01 | 120 | 1.31 | 0 | 6.615 | 5.305 | 5.305 | opened | 145 | Ozyorny 35/10 | 6,3+6,3 | 0.34 | 1.66 | 0.01 | 120 | 1.65 | 0 | 6.615 | 4.965 | 4.965 | opened
146 | Igorevskaya 110/10 | 10+10 | 4.94 | 0 | 120 | 4.94 | 0 | 10.5 | 5.56 | 5.56 | opened | 146 | Igorevskaya 110/10 | 10+10 | 0.6 | 5.54 | 0 | 120 | 5.54 | 0 | 10.5 | 4.96 | 4.96 | opened
147 | Kanyutino 110/35/10 | 5,6+6,3 | 2.78 | 1.68 | 120 | 1.1 | 0 | 5.88 | 4.78 | 4.78 | opened | 147 | Kanyutino 110/35/10 | 5,6+6,3 | 0.49 | 3.27 | 3.1 | 120 | 0.17 | 0 | 5.88 | 5.71 | 5.71 | opened
| Nom. capacity LV, МVА | 5,6+6,3 | 2.4 | 2.4 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.49 | 2.89 | 2.89 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.38 | 0.21 | 120 | 0.17 | 0 | 5.88 | 5.71 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.38 | 0.21 | 120 | 0.17 | 0 | 5.88 | 5.71
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.21 | 0.25 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened | 148 | Bogolyubovo 35/10 | 2,5+2,5 | 0 | 1.21 | 0.25 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
149 | Kholm-Zhirki 35/10 | 2,5+4 | 1.8 | 0.4 | 120 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | opened | 149 | Kholm-Zhirki 35/10 | 2,5+4 | 0.3 | 2.1 | 0.4 | 120 | 1.7 | 0 | 2.625 | 0.925 | 0.925 | opened
150 | Dorogobuzh 1 110/35/10 | 16+16 | 6.74 | 2.85 | 120 | 3.89 | 0 | 16.8 | 12.91 | 12.91 | opened | 150 | Dorogobuzh 1 110/35/10 | 16+16 | 1.23 | 7.97 | 3 | 120 | 4.97 | 0 | 16.8 | 11.83 | 11.83 | opened
| Nom. capacity MV, МVА | 16+16 | 2.33 | 2.33 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.15 | 2.48 | 2.48 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.41 | 0.52 | 120 | 3.89 | 0 | 16.8 | 12.91 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.08 | 5.49 | 0.52 | 120 | 4.97 | 0 | 16.8 | 11.83
151 | Kaskovo 35/10 | 1,6+4 | 0.78 | 0.09 | 120 | 0.69 | 0 | 1.68 | 0.99 | 0.99 | opened | 151 | Kaskovo 35/10 | 1,6+4 | 0 | 0.78 | 0.09 | 120 | 0.69 | 0 | 1.68 | 0.99 | 0.99 | opened
152 | Usvyatye 35/10 | 2,5+4 | 0.89 | 0 | 120 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened | 152 | Usvyatye 35/10 | 2,5+4 | 0 | 0.89 | 0 | 120 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened
153 | Ushakovo 35/10 | 1,6+2,5 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 153 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.16 | 0.04 | 120 | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened | 155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.16 | 0.04 | 120 | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened
156 | Elnya 110/35/10 | 16+16 | 7.26 | 3.03 | 120 | 4.23 | 0 | 16.8 | 12.57 | 12.57 | opened | 156 | Elnya 110/35/10 | 16+16 | 0.41 | 7.67 | 3.1 | 120 | 4.57 | 0 | 16.8 | 12.23 | 12.23 | opened
| Nom. capacity MV, МVА | 16+16 | 2.49 | 2.49 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.07 | 2.56 | 2.56 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.77 | 0.54 | 10 | 4.23 | 0 | 16.8 | 12.57 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.34 | 5.11 | 0.54 | 120 | 4.57 | 0 | 16.8 | 12.23
157 | Pavlovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 157 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
158 | Sharapovo 35/10 | 4+4 | 0.9 | 1 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened | 158 | Sharapovo 35/10 | 4+4 | 0 | 0.9 | 1 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
159 | Korobets 35/10 | 2,5+2,5 | 1.05 | 0.17 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 159 | Korobets 35/10 | 2,5+2,5 | 0 | 1.05 | 0.17 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
160 | Baltuty 35/10 | 2,5+2,5 | 0.53 | 0 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened | 160 | Baltuty 35/10 | 2,5+2,5 | 0.07 | 0.6 | 0 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
161 | Lapino 110/35/10 | 5,6+5,6 | 1.15 | 0.79 | 120 | 0.36 | 0 | 5.88 | 5.52 | 5.52 | opened | 161 | Lapino 110/35/10 | 5,6+5,6 | 0.09 | 1.24 | 0.88 | 120 | 0.36 | 0 | 5.88 | 5.52 | 5.52 | opened
| Nom. capacity MV, МVА | 5,6+5,6 | 0.79 | 0.79 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0.09 | 0.88 | 0.88 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.36 | 0 | 120 | 0.36 | 0 | 5.88 | 5.52 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 5.88 | 5.52
162 | Mutishche 35/10 | 1,6+2,5 | 0.28 | 0.08 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 162 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.28 | 0.08 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
163 | Suetovo 110/35/10 | 6,3+6,3 | 1.91 | 1.56 | 120 | 0.35 | 0 | 6.615 | 6.265 | 6.265 | opened | 163 | Suetovo 110/35/10 | 6,3+6,3 | 1.32 | 3.23 | 2.64 | 120 | 0.59 | 0 | 6.615 | 6.025 | 6.025 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.98 | 0.98 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1.08 | 2.06 | 2.06 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.93 | 0.58 | 120 | 0.35 | 0 | 6.615 | 6.265 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.17 | 0.58 | 120 | 0.59 | 0 | 6.615 | 6.025
164 | Pushkino 35/10 | 2,5+2,5 | 0.56 | 0.04 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 164 | Pushkino 35/10 | 2,5+2,5 | 1.08 | 1.64 | 0.04 | 120 | 1.6 | 0 | 2.625 | 1.025 | 1.025 | opened
165 | Yartsevo 1 110/10 | 40+40 | 13.57 | 5.34 | 120 | 8.23 | 0 | 42 | 33.77 | 33.77 | opened | 165 | Yartsevo 1 110/10 | 40+40 | 5.58 | 19.15 | 5.34 | 120 | 13.81 | 0 | 42 | 28.19 | 28.19 | opened
166 | Yartsevo 2 110/10 | 16+16 | 10.61 | 0.75 | 120 | 9.86 | 0 | 16.8 | 6.94 | 6.94 | opened | 166 | Yartsevo 2 110/10 | 16+16 | 5.42 | 16.03 | 0.75 | 120 | 15.28 | 0 | 16.8 | 1.52 | 1.52 | opened
167 | Saprykino 110/35/10 | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105 | 6.105 | opened | 167 | Saprykino 110/35/10 | 6,3+6,3 | 0.14 | 1.05 | 0.4 | 120 | 0.65 | 0 | 6.615 | 5.965 | 5.965 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.14 | 1.05 | 0.4 | 120 | 0.65 | 0 | 6.615 | 5.965
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.19 | 0 | 120 | 2.19 | 0 | 6.615 | 4.425 | 4.425 | opened | 168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.97 | 3.16 | 0 | 120 | 3.16 | 0 | 6.615 | 3.455 | 3.455 | opened
169 | Egoryevo 35/10 | 6,3+6,3 | 4.65 | 0 | 120 | 4.65 | 0 | 6.615 | 1.965 | 1.965 | opened | 169 | Egoryevo 35/10 | 6,3+6,3 | 0.14 | 4.79 | 0 | 120 | 4.79 | 0 | 6.615 | 1.825 | 1.825 | opened
170 | Shalomino 35/10 | 1,6+2,5 | 0.59 | 0.13 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened | 170 | Shalomino 35/10 | 1,6+2,5 | 0.17 | 0.76 | 0.13 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened
171 | Roslavl 110/35/6 | 25+40 | 26.59 | 1.4 | 120 | 25.19 | 0 | 26.25 | 1.06 | 1.06 | opened | 171 | Roslavl 110/35/6 | 25+40 | 3.87 | 30.46 | 1.4 | 120 | 29.06 | 0 | 26.25 | -2.81 | -2.81 | closed
| Nom. capacity MV, МVА | 25+40 | 11.79 | 1.4 |  | 10.39 | 0 | 26.25 | 15.86 |  |  |  | Nom. capacity MV, МVА | 25+40 | 1.45 | 13.24 | 1.4 |  | 11.84 | 0 | 26.25 | 14.41
| Nom. сapacity LV, МVА | 25+40 | 14.8 | 0 | 120 | 14.8 | 0 | 26.25 | 11.45 |  |  |  | Nom. сapacity LV, МVА | 25+40 | 2.42 | 17.22 | 0 | 120 | 17.22 | 0 | 26.25 | 9.03
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.88 | 0 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | opened | 172 | Meet processing plant 35/6 | 6,3+6,3 | 0.11 | 1.99 | 0 | 120 | 1.99 | 0 | 6.615 | 4.625 | 4.625 | opened
173 | Perenka 35/10 | 4+4 | 0.36 | 0 | 120 | 0.36 | 0 | 4.2 | 3.84 | 3.84 | opened | 173 | Perenka 35/10 | 4+4 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 4.2 | 3.84 | 3.84 | opened
174 | Khoroshevo 35/10 | 2,5+4 | 1.19 | 0 | 120 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened | 174 | Khoroshevo 35/10 | 2,5+4 | 0 | 1.19 | 0 | 120 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened
175 | Lipovka 35/10 | 2,5+2,5 | 0.52 | 0 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 175 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.52 | 0 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
176 | Kirilly 35/10 | 2,5+2,5 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 176 | Kirilly 35/10 | 2,5+2,5 | 1.34 | 2.15 | 0 | 120 | 2.15 | 0 | 2.625 | 0.475 | 0.475 | opened
177 | Desnogorsk 110/35/10 | 25+25 | 17.92 | 3.15 | 120 | 14.77 | 0 | 26.25 | 11.48 | 11.48 | opened | 177 | Desnogorsk 110/35/10 | 25+25 | 1.41 | 19.33 | 3.16 | 120 | 16.17 | 0 | 26.25 | 10.08 | 10.08 | opened
| Nom. capacity MV, МVА | 25+25 | 3.15 | 3.15 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 1.41 | 4.56 | 3.16 |  | 1.4 | 0 | 26.25 | 24.85
| Nom. capacidty LV, МVА | 25+25 | 14.77 | 0 | 120 | 14.77 | 0 | 26.25 | 11.48 |  |  |  | Nom. capacidty LV, МVА | 25+25 | 0 | 14.77 | 0 | 120 | 14.77 | 0 | 26.25 | 11.48
178 | Ekimovichi 35/10 | 4+4 | 2.31 | 0.24 | 120 | 2.07 | 0 | 4.2 | 2.13 | 2.13 | opened | 178 | Ekimovichi 35/10 | 4+4 | 0 | 2.31 | 0.24 | 120 | 2.07 | 0 | 4.2 | 2.13 | 2.13 | opened
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.18 | 0.07 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 179 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.18 | 0.07 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
180 | Kokhany 35/10 | 1,6+1,6 | 0.33 | 0.09 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 180 | Kokhany 35/10 | 1,6+1,6 | 0.09 | 0.42 | 0.09 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
181 | Koski 35/10 | 4+4 | 0.49 | 0 | 120 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | opened | 181 | Koski 35/10 | 4+4 | 0 | 0.49 | 0 | 120 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | opened
182 | Industrialnaya 110/35/6 | 16+16 | 4.43 | 0.7 | 120 | 3.73 | 0 | 16.8 | 13.07 | 4.565 | opened | 182 | Industrialnaya 110/35/6 | 16+16 | 1.42 | 5.85 | 0.7 | 120 | 5.15 | 0 | 16.8 | 11.65 | 5.565 | opened
| Nom. capacity MV, МVА | 16,3+5,3 | 0.7 | 0.7 |  | 0 | 1 | 5.565 | 4.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0 | 0.7 | 0.7 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 3.73 | 0 | 120 | 3.73 | 2 | 11.235 | 5.505 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 1.42 | 5.15 | 0 | 120 | 5.15 | 0 | 11.235 | 6.085
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.88 | 0 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 183 | Astapkovichi 35/10 | 2,5+2,5 | 0 | 0.88 | 0 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.11 | 0.72 | 120 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | opened | 184 | Barsuki 110/35/10 | 6,3+6,3 | 0.28 | 1.39 | 1 | 120 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.72 | 0.72 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.28 | 1 | 1 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.39 | 0 | 120 | 0.39 | 0 | 6.615 | 6.225 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.39 | 0 | 120 | 0.39 | 0 | 6.615 | 6.225
185 | Bogdanovo 35/10 | 4+4 | 0.54 | 0 | 120 | 0.54 | 0 | 4.2 | 3.66 | 3.66 | opened | 185 | Bogdanovo 35/10 | 4+4 | 0.28 | 0.82 | 0 | 120 | 0.82 | 0 | 4.2 | 3.38 | 3.38 | opened
186 | Prigorye 110/35/10 | 10+2,5 | 0.89 | 0.48 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened | 186 | Prigorye 110/35/10 | 10+2,5 | 0.12 | 1.01 | 0.6 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened
| Nom. capacity MV, МVА | 10+2,5 | 0.48 | 0.48 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0.12 | 0.6 | 0.6 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.41 | 0 | 120 | 0.41 | 0 | 2.625 | 2.215 |  |  |  | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 2.625 | 2.215
187 | Bekhovo 35/10 | 2,5+2,5 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened | 187 | Bekhovo 35/10 | 2,5+2,5 | 0.12 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
188 | Pochinok 110/35/10 | 10+16 | 8.99 | 3.63 | 120 | 5.36 | 0 | 10.5 | 5.14 | 5.14 | opened | 188 | Pochinok 110/35/10 | 10+16 | 2.61 | 11.6 | 4.71 | 120 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | opened
| Nom. capacidty MV, МVА | 10+16 | 3.55 | 3.55 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacidty MV, МVА | 10+16 | 1.08 | 4.63 | 4.63 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.44 | 0.08 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.53 | 6.97 | 0.08 | 120 | 6.89 | 0 | 10.5 | 3.61
189 | Divinskaya 35/10 | 4+4 | 1.23 | 0.17 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | opened | 189 | Divinskaya 35/10 | 4+4 | 0.04 | 1.27 | 0.17 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened
190 | Shatalovo 35/10 | 2,5+2,5 | 1.75 | 0 | 120 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | opened | 190 | Shatalovo 35/10 | 2,5+2,5 | 0 | 1.75 | 0 | 120 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | opened
191 | Panskaya 35/10 | 6,3+6,3 | 1.48 | 0 | 120 | 1.48 | 0 | 6.615 | 5.135 | 5.135 | opened | 191 | Panskaya 35/10 | 6,3+6,3 | 1.04 | 2.52 | 0 | 120 | 2.52 | 0 | 6.615 | 4.095 | 4.095 | opened
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.28 | 1.44 | 120 | 1.84 | 0 | 6.615 | 4.775 | 4.775 | opened | 192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.63 | 6.91 | 2.44 | 120 | 4.47 | 0 | 6.615 | 2.145 | 2.145 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.99 | 0.99 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1 | 1.99 | 1.99 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.29 | 0.45 | 120 | 1.84 | 0 | 6.615 | 4.775 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.63 | 4.92 | 0.45 | 120 | 4.47 | 0 | 6.615 | 2.145
193 | Belik 35/10 | 2,5+2,5 | 0.22 | 0.33 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened | 193 | Belik 35/10 | 2,5+2,5 | 0 | 0.22 | 0.33 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened
194 | Pervomayskaya 35/10 | 4+4 | 1.4 | 0 | 120 | 1.4 | 0 | 4.2 | 2.8 | 2.8 | opened | 194 | Pervomayskaya 35/10 | 4+4 | 0.73 | 2.13 | 0 | 120 | 2.13 | 0 | 4.2 | 2.07 | 2.07 | opened
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.84 | 2.07 | 120 | -0.23 | 0 | 6.615 | 6.845 | 6.255 | opened | 195 | Vaskovo 110/35/10 | 6,3+6,3 | 0.28 | 2.12 | 1.76 | 120 | 0.36 | 0 | 6.615 | 6.255 | 6.255 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.27 | 1.27 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.28 | 1.55 | 1.55 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.57 | 0.21 | 120 | 0.36 | 0 | 6.615 | 6.255 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.57 | 0.21 | 120 | 0.36 | 0 | 6.615 | 6.255
196 | Strigino 35/10 | 2,5+2,5 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 196 | Strigino 35/10 | 2,5+2,5 | 0 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
197 | Komintern 35/10 | 2,5+2,5 | 0.58 | 0 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 197 | Komintern 35/10 | 2,5+2,5 | 0 | 0.58 | 0 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
198 | Monastyrshchina 110/35/10 | 10+10 | 4.37 | 1.9 | 120 | 2.47 | 0 | 10.5 | 8.03 | 8.03 | opened | 198 | Monastyrshchina 110/35/10 | 10+10 | 0.13 | 4.5 | 1.9 | 120 | 2.6 | 0 | 10.5 | 7.9 | 7.9 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.47 | 0 | 120 | 2.47 | 0 | 10.5 | 8.03 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.13 | 2.6 | 0 | 120 | 2.6 | 0 | 10.5 | 7.9
199 | N.Mikhailov 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened | 199 | N.Mikhailov 35/10 | 4+4 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
200 | Tatarsk 35/10 | 3,2+4 | 0.81 | 0 | 120 | 0.81 | 0 | 3.36 | 2.55 | 2.55 | opened | 200 | Tatarsk 35/10 | 3,2+4 | 0 | 0.81 | 0 | 120 | 0.81 | 0 | 3.36 | 2.55 | 2.55 | opened
201 | Turki 35/10 | 1,6+1,6 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened | 201 | Turki 35/10 | 1,6+1,6 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened
202 | Sozh 35/10 | 4+4 | 0.52 | 0 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | opened | 202 | Sozh 35/10 | 4+4 | 0 | 0.52 | 0 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | opened
203 | Khislavichi 110/35/10 | 16+16 | 4.11 | 1.61 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | opened | 203 | Khislavichi 110/35/10 | 16+16 | 0.49 | 4.6 | 1.81 | 120 | 2.79 | 0 | 16.8 | 14.01 | 14.01 | opened
| Nom. capacity MV, МVА | 16+16 | 1.43 | 1.43 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.2 | 1.63 | 1.63 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.68 | 0.18 | 120 | 2.5 | 0 | 16.8 | 14.3 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.29 | 2.97 | 0.18 | 120 | 2.79 | 0 | 16.8 | 14.01
204 | Gorodishche 35/10 | 1,8+2,5 | 0.82 | 0 | 120 | 0.82 | 0 | 1.89 | 1.07 | 1.07 | opened | 204 | Gorodishche 35/10 | 1,8+2,5 | 0 | 0.82 | 0 | 120 | 0.82 | 0 | 1.89 | 1.07 | 1.07 | opened
205 | Komarovka 35/10 | 4+4 | 0.32 | 0.02 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 205 | Komarovka 35/10 | 4+4 | 0 | 0.32 | 0.02 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
206 | Cherepovo 35/10 | 2,5+2,5 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened | 206 | Cherepovo 35/10 | 2,5+2,5 | 0.05 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
207 | Studenets 35/10 | 1,6+2,5 | 0.34 | 0.01 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened | 207 | Studenets 35/10 | 1,6+2,5 | 0.15 | 0.49 | 0.01 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened
208 | Shumyachi 110/35/10 | 10+10 | 4.8 | 3.36 | 120 | 1.44 | 0 | 10.5 | 9.06 | 9.06 | opened | 208 | Shumyachi 110/35/10 | 10+10 | 1.52 | 6.32 | 4.3 | 120 | 2.02 | 0 | 10.5 | 8.48 | 8.48 | opened
| Nom. capacity MV, МVА | 10+10 | 2.72 | 2.72 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.94 | 3.66 | 3.66 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.08 | 0.64 | 120 | 1.44 | 0 | 10.5 | 9.06 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.58 | 2.66 | 0.64 | 120 | 2.02 | 0 | 10.5 | 8.48
209 | Ershichi 110/35/10 | 10+10 | 2.25 | 0.62 | 120 | 1.63 | 0 | 10.5 | 8.87 | 8.87 | opened | 209 | Ershichi 110/35/10 | 10+10 | 0.65 | 2.9 | 0.75 | 120 | 2.15 | 0 | 10.5 | 8.35 | 8.35 | opened
| Nom. capacity MV, МVА | 10+10 | 0.4 | 0.4 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 0.53 | 0.53 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.85 | 0.22 | 120 | 1.63 | 0 | 10.5 | 8.87 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.52 | 2.37 | 0.22 | 120 | 2.15 | 0 | 10.5 | 8.35
210 | Rukhan 35/10 | 2,5+2,5 | 0.45 | 0 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened | 210 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.45 | 0 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
211 | Vyazma 1 110/35/10 | 40+40 | 42.21 | 11.83 | 120 | 30.38 | 0 | 42 | 11.62 | 11.62 | opened | 211 | Vyazma 1 110/35/10 | 40+40 | 17.5 | 59.71 | 15.76 | 120 | 43.95 | 0 | 42 | -1.95 | -1.95 | closed
| Nom. capacity MV, МVА | 40+40 | 25.68 | 11.27 | 121 | 14.41 | 0 | 42 | 27.59 |  |  |  | Nom. capacity MV, МVА | 40+40 | 8.93 | 34.61 | 15.2 |  | 19.41 | 0 | 42 | 22.59
| Nom. capacity LV, МVА | 40+40 | 16.53 | 0.56 | 122 | 15.97 | 0 | 42 | 26.03 |  |  |  | Nom. capacity LV, МVА | 40+40 | 8.57 | 25.1 | 0.56 | 120 | 24.54 | 0 | 42 | 17.46
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.99 | 0 | 120 | 2.99 | 0 | 6.615 | 3.625 | 3.625 | opened | 212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 1.62 | 4.61 | 0 | 120 | 4.61 | 0 | 6.615 | 2.005 | 2.005 | opened
213 | Khmelita 35/10 | 1,6+2,5 | 0.49 | 0.11 | 120 | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened | 213 | Khmelita 35/10 | 1,6+2,5 | 0.03 | 0.52 | 0.11 | 120 | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened
214 | Isakovo 35/10 | 2,5+4 | 0.76 | 0.3 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened | 214 | Isakovo 35/10 | 2,5+4 | 0 | 0.76 | 0.3 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
215 | Rizskoe 35/10 | 2,5+2,5 | 0.54 | 0.01 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened | 215 | Rizskoe 35/10 | 2,5+2,5 | 0.22 | 0.76 | 0.01 | 120 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened
216 | Beryozka 35/10 | 4+4 | 0.98 | 0 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 216 | Beryozka 35/10 | 4+4 | 0.25 | 1.23 | 0 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened
217 | Shimanovo 35/10 | 1,8+4 | 0.49 | 0.32 | 120 | 0.17 | 0 | 1.89 | 1.72 | 1.72 | opened | 217 | Shimanovo 35/10 | 1,8+4 | 0.08 | 0.57 | 0.32 | 120 | 0.25 | 0 | 1.89 | 1.64 | 1.64 | opened
218 | Kaydakovo 35/10 | 4+4 | 1.1 | 0.2 | 120 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened | 218 | Kaydakovo 35/10 | 4+4 | 0.13 | 1.23 | 0.2 | 120 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | opened
219 | Flour mill 35/10 | 10+10 | 6.82 | 0.13 | 120 | 6.69 | 0 | 10.5 | 3.81 | 3.81 | opened | 219 | Flour mill 35/10 | 10+10 | 5.85 | 12.67 | 0.13 | 120 | 12.54 | 0 | 10.5 | -2.04 | -2.04 | closed
220 | Kikino 35/10 | 2,5+2,5 | 0.58 | 0.41 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 220 | Kikino 35/10 | 2,5+2,5 | 0.21 | 0.79 | 0.41 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
221 | Vyazma 2 110/10 | 16+16 | 15.42 | 0 | 120 | 15.42 | 0 | 16.8 | 1.38 | 1.38 | opened | 221 | Vyazma 2 110/10 | 16+16 | 4.04 | 19.46 | 0 | 120 | 19.46 | 0 | 16.8 | -2.66 | -2.66 | closed
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.59 | 1.18 | 120 | 1.41 | 0 | 6.615 | 5.205 | 5.205 | opened | 222 | Tumanovo 110/35/10 | 6,3+6,3 | 0.28 | 2.87 | 1.18 | 120 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.84 | 0.84 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.84 | 0.84 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.75 | 0.34 | 120 | 1.41 | 0 | 6.615 | 5.205 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.28 | 2.03 | 0.34 | 120 | 1.69 | 0 | 6.615 | 4.925
223 | Rossiya 110/35/10 | 10+16 | 2.8 | 1.79 | 120 | 1.01 | 0 | 10.5 | 9.49 | 9.49 | opened | 223 | Rossiya 110/35/10 | 10+16 | 0.7 | 3.5 | 2.11 | 120 | 1.39 | 0 | 10.5 | 9.11 | 9.11 | opened
| Nom. capacity MV, МVА | 10+16 | 1.47 | 1.47 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.32 | 1.79 | 1.79 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.33 | 0.32 | 120 | 1.01 | 0 | 10.5 | 9.49 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.38 | 1.71 | 0.32 | 120 | 1.39 | 0 | 10.5 | 9.11
224 | Semlevo 35/10 | 2,5+4 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 224 | Semlevo 35/10 | 2,5+4 | 0.06 | 0.9 | 0 | 120 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | opened
225 | Artyomovo 35/10 | 2,5+2,5 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 225 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
226 | Gagarin 110/35/10 | 25+25 | 19.92 | 4.78 | 120 | 15.14 | 0 | 26.25 | 11.11 | 11.11 | opened | 226 | Gagarin 110/35/10 | 25+25 | 10.77 | 30.69 | 6.82 | 120 | 23.87 | 0 | 26.25 | 2.38 | 2.38 | opened
| Nom. capacity MV, МVА | 25+25 | 6.02 | 3.06 |  | 2.96 | 0 | 26.25 | 23.29 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.27 | 10.29 | 5.1 |  | 5.19 | 0 | 26.25 | 21.06
| Nom. capacity LV, МVА | 25+25 | 13.9 | 1.72 | 120 | 12.18 | 0 | 26.25 | 14.07 |  |  |  | Nom. capacity LV, МVА | 25+25 | 6.5 | 20.4 | 1.72 | 120 | 18.68 | 0 | 26.25 | 7.57
227 | Rodomanovo 35/10 | 4+4 | 0.76 | 1.18 | 120 | -0.42 | 0 | 4.2 | 4.62 | 4.62 | opened | 227 | Rodomanovo 35/10 | 4+4 | 0.9 | 1.66 | 1.18 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened
228 | Klushino 35/10 | 4+4 | 0.82 | 0.57 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 228 | Klushino 35/10 | 4+4 | 0.69 | 1.51 | 0.57 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | opened
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 229 | Ivino 35/10 | 1,6+1,6 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
230 | Karmanovo 35/10 | 4+4 | 3.84 | 0.21 | 120 | 3.63 | 0 | 4.2 | 0.57 | 0.57 | opened | 230 | Karmanovo 35/10 | 4+4 | 1.32 | 5.16 | 0.21 | 120 | 4.95 | 0 | 4.2 | -0.75 | -0.75 | closed
231 | Sverchkovo 35/10 | 2,5+2,5 | 1.46 | 0.75 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened | 231 | Sverchkovo 35/10 | 2,5+2,5 | 0.13 | 1.59 | 0.75 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
232 | Lesnaya 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened | 232 | Lesnaya 35/10 | 4+4 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
233 | Tesovo 35/10 | 1,6+2,5 | 0.67 | 0.48 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 233 | Tesovo 35/10 | 1,6+2,5 | 0.03 | 0.7 | 0.48 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
234 | Svetotekhnika 110/10 | 16+16 | 3.92 | 0.97 | 120 | 2.95 | 0 | 16.8 | 13.85 | 13.85 | opened | 234 | Svetotekhnika 110/10 | 16+16 | 3.8 | 7.72 | 0.97 | 120 | 6.75 | 0 | 16.8 | 10.05 | 10.05 | opened
235 | Mishino 110/35/10 | 10+10 | 3.98 | 2.2 | 120 | 1.78 | 0 | 10.5 | 8.72 | 8.72 | opened | 235 | Mishino 110/35/10 | 10+10 | 0.7 | 4.68 | 3.31 | 120 | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened
| Nom. capacity MV, МVА | 10+10 | 2.44 | 2.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.23 | 2.67 | 2.67 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.54 | 0.64 | 120 | 0.9 | 0 | 10.5 | 9.6 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.47 | 2.01 | 0.64 | 120 | 1.37 | 0 | 10.5 | 9.13
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.35 | 0.59 | 120 | 0.76 | 0 | 6.615 | 5.855 | 5.855 | opened | 236 | Nikolskoe 35/10 | 6,3+6,3 | 0.67 | 2.02 | 0.59 | 120 | 1.43 | 0 | 6.615 | 5.185 | 5.185 | opened
237 | Bekrino 35/10 | 2,5+2,5 | 0.55 | 0.09 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened | 237 | Bekrino 35/10 | 2,5+2,5 | 0 | 0.55 | 0.09 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
238 | Trubnaya 110/10 | 25+25 | 6.38 | 1.57 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | opened | 238 | Trubnaya 110/10 | 25+25 | 2.92 | 9.3 | 1.57 | 120 | 7.73 | 0 | 26.25 | 18.52 | 18.52 | opened
239 | Temkino 110/35/10 | 10+10 | 3.88 | 1.3 | 120 | 2.58 | 0 | 10.5 | 7.92 | 7.92 | opened | 239 | Temkino 110/35/10 | 10+10 | 2.65 | 6.53 | 2.48 | 120 | 4.05 | 0 | 10.5 | 6.45 | 6.45 | opened
| Nom. capacity MV, МVА | 10+10 | 1.05 | 1.05 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.18 | 2.23 | 2.23 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.83 | 0.25 | 120 | 2.58 | 0 | 10.5 | 7.92 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.47 | 4.3 | 0.25 | 120 | 4.05 | 0 | 10.5 | 6.45
240 | Narytka 35/10 | 2,5+2,5 | 0.15 | 0.05 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 240 | Narytka 35/10 | 2,5+2,5 | 0 | 0.15 | 0.05 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
241 | Novodugino 110/35/10 | 10+10 | 4.6 | 2.48 | 120 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened | 241 | Novodugino 110/35/10 | 10+10 | 0.79 | 5.39 | 3.03 | 120 | 2.36 | 0 | 10.5 | 8.14 | 8.14 | opened
| Nom. capacity MV, МVА | 10+10 | 2 | 2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.55 | 2.55 | 2.55 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.6 | 0.48 | 120 | 2.12 | 0 | 10.5 | 8.38 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 2.82 | 0.48 | 120 | 2.34 | 0 | 10.5 | 8.16
242 | Vysokoe 35/10 | 1,6+4 | 0.55 | 0.42 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 242 | Vysokoe 35/10 | 1,6+4 | 0.39 | 0.94 | 0.42 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
243 | Khotkovo 35/10 | 4+4 | 0.67 | 0.26 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 243 | Khotkovo 35/10 | 4+4 | 0 | 0.67 | 0.26 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened
244 | Dneprovsk 110/35/10 | 10+10 | 4.66 | 3.47 | 120 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened | 244 | Dneprovsk 110/35/10 | 10+10 | 1.2 | 5.86 | 4.67 | 120 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened
| Nom. capacity MV, МVА | 10+10 | 3.31 | 3.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.2 | 4.51 | 4.51 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.35 | 0.16 | 120 | 1.19 | 0 | 10.5 | 9.31 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 1.35 | 0.16 | 120 | 1.19 | 0 | 10.5 | 9.31
245 | Lipetsy 35/10 | 2,5+2,5 | 0.33 | 0.75 | 120 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | opened | 245 | Lipetsy 35/10 | 2,5+2,5 | 0.1 | 0.43 | 0.75 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.52 | 0.7 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened | 246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0 | 0.52 | 0.7 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened
247 | Sychevka 110/35/10 | 16+25 | 8.78 | 1.47 | 120 | 7.31 | 0 | 16.8 | 9.49 | 9.49 | opened | 247 | Sychevka 110/35/10 | 16+25 | 8.03 | 16.81 | 1.78 | 120 | 15.03 | 0 | 16.8 | 1.77 | 1.77 | opened
| Nom. capacity MV, МVА | 16+25 | 3.5 | 0.7 |  | 2.8 | 0 | 16.8 | 14 |  |  |  | Nom. capacity MV, МVА | 16+25 | 3.05 | 6.55 | 1.01 |  | 5.54 | 0 | 16.8 | 11.26
| Nom. capacfity LV, МVА | 16+25 | 5.28 | 0.77 | 120 | 4.51 | 0 | 16.8 | 12.29 |  |  |  | Nom. capacfity LV, МVА | 16+25 | 5.02 | 10.3 | 0.77 | 120 | 9.53 | 0 | 16.8 | 7.27
248 | Sutormino 35/10 | 1,8+4 | 0.56 | 0.06 | 120 | 0.5 | 0 | 1.89 | 1.39 | 1.39 | opened | 248 | Sutormino 35/10 | 1,8+4 | 0 | 0.56 | 0.06 | 120 | 0.5 | 0 | 1.89 | 1.39 | 1.39 | opened
249 | Karavaevo 35/10 | 4+4 | 1.14 | 0.29 | 120 | 0.85 | 0 | 4.2 | 3.35 | 3.35 | opened | 249 | Karavaevo 35/10 | 4+4 | 0.38 | 1.52 | 0.29 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened
250 | Lukino 35/10 | 4+1,6 | 0.73 | 0.51 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 250 | Lukino 35/10 | 4+1,6 | 0 | 0.73 | 0.51 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
251 | Subbotniki 110/10 | 6,3+6,3 | 0.66 | 0 | 120 | 0.66 | 0 | 6.615 | 5.955 | 5.955 | opened | 251 | Subbotniki 110/10 | 6,3+6,3 | 0.37 | 1.03 | 0 | 120 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | opened
252 | Ugra 110/10 | 6,3+6,3 | 2.82 | 0 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 252 | Ugra 110/10 | 6,3+6,3 | 0.27 | 3.09 | 0 | 120 | 3.09 | 0 | 6.615 | 3.525 | 3.525 | opened
253 | Znamenka 110/35/10 | 10+10 | 2.52 | 1.35 | 120 | 1.17 | 0 | 10.5 | 9.33 | 9.33 | opened | 253 | Znamenka 110/35/10 | 10+10 | 2.72 | 5.24 | 1.48 | 120 | 3.76 | 0 | 10.5 | 6.74 | 6.74 | opened
| Nom. capacity MV, МVА | 10+10 | 1.32 | 1.32 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 1.45 | 1.45 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.2 | 0.03 | 120 | 1.17 | 0 | 10.5 | 9.33 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.59 | 3.79 | 0.03 | 120 | 3.76 | 0 | 10.5 | 6.74
254 | Losmino 35/10 | 2,5+2,5 | 1.14 | 0.4 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened | 254 | Losmino 35/10 | 2,5+2,5 | 0 | 1.14 | 0.4 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.1 | 0.43 | 120 | 0.67 | 0 | 6.615 | 5.945 | 5.945 | opened | 255 | Vskhody 110/35/10 | 6,3+6,3 | 0.11 | 1.21 | 0.43 | 120 | 0.78 | 0 | 6.615 | 5.835 | 5.835 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.42 | 0.42 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.42 | 0.42 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.68 | 0.01 | 120 | 0.67 | 0 | 6.615 | 5.945 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.11 | 0.79 | 0.01 | 120 | 0.78 | 0 | 6.615 | 5.835
| Total: | 3150.6 | 566.25 | [8 empty] | 2: Total:; 3: 3150.6; 4: 254.66; 5: 820.91
| deficit | [8 empty] | -0.37 |  | 2: deficit; Мin. 12: -50.34
| proficit | [8 empty] | 1074.43 |  | 2: proficit; Мin. 12: 866.42

## Орел 3
table 1
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit/proficit of Main Substation, MVA |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kv Almazovo | 2.5 | 0.38 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.45 | 0.45 | opened | 1 | SS 35/10 kv Almazovo | 2.5 | 0.029 | 0.409 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.421 | 0.421 | opened
2 | SS 35/10 kv Voronets | 2.5 | 0.31 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.6 | 0.6 | opened | 2 | SS 35/10 kv Voronets | 2.5 | 0 | 0.31 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.6 | 0.6 | opened
3 | SS 35/10 kv Gostoml | 2.5 | 0.65 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.01 | 0.01 | opened | 3 | SS 35/10 kv Gostoml | 2.5 | 0.041 | 0.691 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.909 | 0.909 | opened
4 | SS 35/10 kv Gubkino | 3.2 | 0.47 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.09 | 1.09 | opened | 4 | SS 35/10 kv Gubkino | 3.2 | 0.038 | 0.508 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.052 | 1.052 | opened
5 | SS 35/10 kv Devyatino | 1.6 | 0.31 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.4 | 0.4 | opened | 5 | SS 35/10 kv Devyatino | 1.6 | 0.012 | 0.322 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.388 | 0.388 | opened
6 | SS 35/10 kv Kamenka | 2.5 | 0.76 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.84 | 0.84 | opened | 6 | SS 35/10 kv Kamenka | 2.5 | 0.025 | 0.785 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.815 | 0.815 | opened
7 | SS 35/10 kv Kozminskaya | 2.5 | 0.28 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.01 | 1.01 | opened | 7 | SS 35/10 kv Kozminskaya | 2.5 | 0.045 | 0.325 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.965 | 0.965 | opened
8 | SS 110/35/10 kv Maloarkhangelskaya | 10 | 5.93 | 6.14 | 60 | 0.21 | 0 | 6.14 | 0.21 | 0.21 | opened | 8 | SS 110/35/10 kv Maloarkhangelskaya | 10 | 3.139 | 9.099 | 6.14 | 60 | 6.14 | 0 | 6.14 | -2.959 | -2.959 | closed
| Nom. capacity MV, MVA | 10 | 2.66 | 1.94 | 60 | [7 empty] | Nom. capacity MV, MVA | 10 | 0.063 | 2.723 | 1.94 | 60 | 1.94 | 0 | 1.94 | -0.783
| Nom. capacity LV, MVA | 10 | 3.3 | 4.2 | 60 | 0.9 | 0 | 4.2 | 0.9 |  |  |  | Nom. capacity LV, MVA | 10 | 3.076 | 6.376 | 4.2 | 60 | 4.2 | 0 | 4.2 | -2.176
9 | SS 110/35/10 kv Novopolevo | 16 | 2.74 | 3.71 | 30 | 3.71 | 0 | 3.71 | 0.97 | -0.27 | closed | 9 | SS 110/35/10 kv Novopolevo | 16 | 0.505 | 3.265 | 3.71 | 30 | 3.71 | 0 | 3.71 | 0.445 | -0.623 | closed
| Nom. capacity MV, MVA | 16 | 1.38 | 2.6 | 30 | [7 empty] | Nom. capacity MV, MVA | 16 | 0.152 | 1.532 | 2.6 | 30 | 2.6 | 0 | 2.6 | 1.068
| Nom. capacity LV, MVA | 16 | 1.38 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.27 |  |  |  | Nom. capacity LV, MVA | 16 | 0.353 | 1.733 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.623
10 | SS 35/10 kv Nikolskaya | 2.5 | 0.6 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.73 | 0.73 | opened | 10 | SS 35/10 kv Nikolskaya | 2.5 | 0.04 | 0.64 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.69 | 0.69 | opened
11 | SS 35/10 kv Paramonovo | 1.8 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | opened | 11 | SS 35/10 kv Paramonovo | 1.8 | 0.059 | 0.209 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.271 | 0.271 | opened
12 | SS 35/10 kv Senkovo | 1.6 | 0.31 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.98 | 0.98 | opened | 12 | SS 35/10 kv Senkovo | 1.6 | 0.078 | 0.388 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.902 | 0.902 | opened
13 | SS 35/10 kv Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | opened | 13 | SS 35/10 kv Somovo | 2.5 | 0.004 | 0.344 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.616 | 0.616 | opened
14 | SS 110/35/10 kv Trosna | 16 | 2.53 | 4.16 | 45 | 4.16 | 0 | 4.16 | 1.63 | 0.72 | opened | 14 | SS 110/35/10 kv Trosna | 16 | 0.079 | 2.619 | 4.16 | 45 | 4.16 | 0 | 4.16 | 1.541 | 1.541 | opened
| Nom. capacity MV, MVA | 16 | 1.46 | 2.36 | 45 | [7 empty] | Nom. capacity MV, MVA | 16 | 0.007 | 1.467 | 2.36 | 45 | 2.36 | 0 | 2.36 | 0.893
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.072 | 1.152 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.648
15 | SS 35/10 kv Shablykino | 5.6 | 0.09 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.71 | 0.71 | opened | 15 | SS 35/10 kv Shablykino | 5.6 | 0.015 | 0.105 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.695 | 0.695 | opened
16 | SS 35/10 kv Yuryevo | 2.5 | 0.18 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.89 | 0.89 | opened | 16 | SS 35/10 kv Yuryevo | 2.5 | 0.047 | 0.227 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.843 | 0.843 | opened
17 | SS 110/35/10 kv Region V | 10 | 3.77 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.63 | 1.56 | opened | 17 | SS 110/35/10 kv Region V | 10 | 0.2 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 | 1.36 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | [8 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 3.84 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.56 |  |  |  | Nom. capacity LV, MVA | 10 | 0.2 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36
18 | SS 110/10 kv Pishchevaya | 6.3 | 2.57 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.695 | -0.695 | closed | 18 | SS 110/10 kv Pishchevaya | 6.3 | 2.353 | 4.923 | 1.875 | 60 | 1.875 | 0 | 1.875 | -3.048 | -3.048 | closed
19 | SS 110/10 kv Telchye | 3.2 | 1.65 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.19 | -0.19 | closed | 19 | SS 110/10 kv Telchye | 3.2 | 0.198 | 1.848 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.388 | -0.388 | closed
20 | SS 110/10 kv B.Chern | 2.5 | 0.31 | 1 | 120 | 1 | 0 | 1 | 0.69 | 0.69 | opened | 20 | SS 110/10 kv B.Chern | 2.5 | 0.006 | 0.316 | 1 | 120 | 1 | 0 | 1 | 0.684 | 0.684 | opened
21 | SS 35/10 kv Bashkatovo | 1.6 | 0.37 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.43 | 0.43 | opened | 21 | SS 35/10 kv Bashkatovo | 1.6 | 0.018 | 0.388 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.412 | 0.412 | opened
22 | SS 35/10 kv Vysokoe | 1.6 | 0.28 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.96 | 0.96 | opened | 22 | SS 35/10 kv Vysokoe | 1.6 | 0 | 0.28 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.96 | 0.96 | opened
23 | SS 35/10 kv Gladkoe | 2.5 | 0.43 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.03 | 1.03 | opened | 23 | SS 35/10 kv Gladkoe | 2.5 | 0.014 | 0.444 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.016 | 1.016 | opened
24 | SS 35/10 kv Lykovo | 2.5 | 0.82 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.42 | 0.42 | opened | 24 | SS 35/10 kv Lykovo | 2.5 | 0.06 | 0.88 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.36 | 0.36 | opened
25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened | 25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.3 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.38 | 0.38 | opened | 26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.026 | 0.326 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.354 | 0.354 | opened
27 | SS 35/10 kv Koptevo | 2.5 | 0.28 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.16 | 0.16 | opened | 27 | SS 35/10 kv Koptevo | 2.5 | 0 | 0.28 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.16 | 0.16 | opened
28 | SS 110/35/10/6 kv Meat processing factory | 10 | 1.57 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.56 | 0.32 | opened | 28 | SS 110/35/10/6 kv Meat processing factory | 10 | 0.012 | 1.822 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.308 | 0.308 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | [7 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.81 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.32 |  |  |  | Nom. capacity LV, MVA | 10 | 0.012 | 1.822 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.308
29 | SS 110/35/10 kv Shatilovo | 10 | 1.43 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.74 | -0.74 | closed | 29 | SS 110/35/10 kv Shatilovo | 10 | 0.005 | 1.485 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.795 | -0.795 | closed
| Nom. capacity MV, MVA | 10 | 0.53 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.37 |  |  |  | Nom. capacity MV, MVA | 10 | 0.011 | 0.541 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.381
| Nom. capacity LV, MVA | 10 | 0.91 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.38 |  |  |  | Nom. capacity LV, MVA | 10 | 0.034 | 0.944 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.414
30 | SS 110/35/10 kv Sovkhoznaya | 10 | 6.46 | 8.96 | 120 | 8.96 | 0 | 8.96 | 2.5 | 1.23 | opened | 30 | SS 110/35/10 kv Sovkhoznaya | 10 | 1.192 | 7.682 | 8.96 | 120 | 8.96 | 0 | 8.96 | 1.278 | 0.108 | opened
| Nom. capacity MV, MVA | 10 | 5.39 | 6.62 | 120 | 6.62 | 0 | 6.62 | 1.23 |  |  |  | Nom. capacity MV, MVA | 10 | 1.122 | 6.512 | 6.62 | 120 | 6.62 | 0 | 6.62 | 0.108
| Nom. capacity LV, MVA | 10 | 1.1 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.24 |  |  |  | Nom. capacity LV, MVA | 10 | 0.07 | 1.17 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.17
31 | SS 35/10 kv Danilovskaya | 1.6 | 0.45 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.09 | 0.09 | opened | 31 | SS 35/10 kv Danilovskaya | 1.6 | 0 | 0.45 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.09 | 0.09 | opened
32 | SS 35/10 kv Korseevo | 1.8 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | opened | 32 | SS 35/10 kv Korseevo | 1.8 | 0 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | opened
33 | SS 35/10 kv Lipovets | 2.5 | 0.82 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.57 | 0.57 | opened | 33 | SS 35/10 kv Lipovets | 2.5 | 0.007 | 0.827 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.563 | 0.563 | opened
34 | SS 35/10 kv Misaylovo | 1.6 | 0.47 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.13 | 1.13 | opened | 34 | SS 35/10 kv Misaylovo | 1.6 | 0.004 | 0.474 | 1.6 |  | 1.6 | 0 | 1.6 | 1.126 | 1.126 | opened
35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | opened | 35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.009 | 0.269 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.041 | 0.041 | opened
36 | SS 35/10 kv Pankovo | 1.8 | 0.53 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.07 | 1.07 | opened | 36 | SS 35/10 kv Pankovo | 1.8 | 0.011 | 0.541 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.059 | 1.059 | opened
37 | SS 35/10 kv Sudbishchi | 2.5 | 0.73 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.87 | 0.87 | opened | 38 | SS 35/10 kv Sudbishchi | 2.5 | 0.015 | 0.745 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.855 | 0.855 | opened
38 | SS 35/10 kv Tim | 1.6 | 0.71 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.89 | 0.89 | opened | 39 | SS 35/10 kv Tim | 1.6 | 0.013 | 0.723 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.877 | 0.877 | opened
39 | SS 35/10 kv Topki | 1 | 0.36 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.24 | 1.24 | opened | 40 | SS 35/10 kv Topki | 1 | 0.006 | 0.366 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.234 | 1.234 | opened
40 | SS 35/10 kv Yarishche | 2.5 | 0.4 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.2 | 1.2 | opened | 41 | SS 35/10 kv Yarishche | 2.5 | 0.039 | 0.439 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.161 | 1.161 | opened
41 | SS 110/10 kv Alshanskaya | 10+10 | 6.6 | 3.88 | 30 | 2.72 | 0 | 10.5 | 7.78 | 7.78 | opened | 42 | SS 110/10 kv Alshanskaya | 10+10 | 0.422 | 7.022 | 3.88 | 30 | 3.142 | 0 | 10.5 | 7.358 | 7.358 | opened
42 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | opened | 43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.034 | 0.434 | 0.93 | 90 | -0.496 | 0 | 2.625 | 3.121 | 3.121 | opened
43 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened | 44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.012 | 0.572 | 0 |  | 0.572 | 0 | 1.68 | 1.108 | 1.108 | opened
44 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.9 | 3.06 | 90 | -0.16 | 0 | 10.5 | 10.66 | 10.29 | opened | 45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 1.648 | 4.518 | 3.06 | 90 | 1.458 | 0 | 10.5 | 9.042 | 9.042 | opened
45 | Nom. capacity MV, MVA | 10+10 | 2.64 | 2.43 | 90 | 0.21 | 0 | 10.5 | 10.29 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.166 | 2.806 | 2.43 | 90 | 0.376 | 0 | 10.5 | 10.124
| Nom. capacity LV, MVA | 10+10 | 0.23 | 0.63 | 90 | -0.4 | 0 | 10.5 | 10.9 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.482 | 1.712 | 0.63 | 90 | 1.082 | 0 | 10.5 | 9.418
| SS 35/10 kv Baklanovo | 1,6+1,6 | 0.83 | 0.64 | 60 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.014 | 0.844 | 0.64 | 60 | 0.204 | 0 | 1.68 | 1.476 | 1.476 | opened
46 | SS 35/10 kv Biofactory | 6,3+6,3 | 2.88 | 2.05 | 90 | 0.83 | 0 | 6.615 | 5.785 | 5.785 | opened | 47 | SS 35/10 kv Biofactory | 6,3+6,3 | 0.396 | 3.276 | 2.05 | 90 | 1.226 | 0 | 6.615 | 5.389 | 5.389 | opened
47 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.85 | 1.46 | 30 | 2.39 | 0 | 2.625 | 0.235 | 0.235 | opened | 48 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 2.031 | 5.881 | 1.46 | 30 | 4.421 | 0 | 2.625 | -1.796 | -1.796 | closed
48 | SS 110/10 kv Vostochnaya | 15+15 | 14.87 | 5.87 | 120 | 9 | 0 | 15.75 | 6.75 | 6.75 | opened | 49 | SS 110/10 kv Vostochnaya | 15+15 | 0 | 14.87 | 5.87 | 120 | 9 |  | 15.75 | 6.75 | 6.75 | opened
49 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 3.64 | 0.45 | 60 | 3.19 | 0 | 10.5 | 7.31 | 7.31 | opened | 50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 0.136 | 3.766 | 0.45 | 60 | 3.316 | 0 | 10.5 | 7.184 | 7.184 | opened
50 | Nom. capacity MV, MVA | 10+10 | 0.31 | 0 | 0 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.012 | 0.322 | 0 |  | 0.322 | 0 | 10.5 | 10.178
| Nom. capacity LV, MVA | 10+10 | 3.32 | 0.45 | 60 | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.124 | 3.444 | 0.45 | 60 | 2.994 | 0 | 10.5 | 7.506
| SS 110/10 kv Zheleznodorozhnaya | 16+16 | 12.57 | 3.98 | 180 | 8.59 | 0 | 16.8 | 8.21 | 8.21 | opened | 51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 1.707 | 14.277 | 3.98 | 180 | 10.297 | 0 | 16.8 | 6.503 | 6.503 | opened
51 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 1.06 | 0.64 | 60 | 0.42 | 0 | 1.89 | 1.47 | 1.47 | opened | 52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 0.021 | 1.081 | 0.64 | 60 | 0.441 | 0 | 1.89 | 1.449 | 1.449 | opened
52 | SS 110/6 kv Zavodskaya | 40+25 | 16.07 | 4.39 | 150 | 11.68 | 0 | 26.25 | 14.57 | 14.57 | opened | 53 | SS 110/6 kv Zavodskaya | 40+25 | 0 | 16.07 | 4.39 | 150 | 11.68 | 0 | 26.25 | 14.57 | 14.57 | opened
53 | SS 110/6 kv Zapadnaya | 25+25 | 25.03 | 0 | 120 | 25.03 | 0 | 26.25 | 1.22 | 1.22 | opened | 54 | SS 110/6 kv Zapadnaya | 25+25 | 19.118 | 44.148 | 5.37 | 120 | 38.778 | 0 | 26.25 | -12.528 | -12.528 | closed
54 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 2.08 | 1.48 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 0.414 | 2.494 | 1.48 | 60 | 1.014 | 0 | 2.625 | 1.611 | 1.611 | opened
55 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 1.16 | 1.18 | 30 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened | 56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 0.053 | 1.213 | 1.18 | 30 | 0.033 | 0 | 1.68 | 1.647 | 1.647 | opened
56 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.28 | 1.44 | 90 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened | 57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.564 | 10.874 | 1.44 | 90 | 9.434 | 0 | 10.5 | 1.066 | 1.066 | opened
57 | Nom. capacity MV, MVA | 10+10 | 1.49 | 1 | 90 | 0.49 | 0 | 10.5 | 10.01 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.49 | 1 | 90 | 0.49 | 0 | 10.5 | 10.01
| Nom. capacity LV, MVA | 10+10 | 3.82 | 0.44 | 90 | 3.38 | 0 | 10.5 | 7.12 |  |  |  | Nom. capacity LV, MVA | 10+10 | 5.564 | 9.384 | 0.44 | 90 | 8.944 | 0 | 10.5 | 1.556
| SS 110/35/10 kv Kromskaya | 16+16 | 8.63 | 6.83 | 45 | 1.8 | 0 | 16.8 | 15 | 14.42 | opened | 58 | SS 110/35/10 kv Kromskaya | 16+16 | 6.409 | 15.619 | 6.83 | 45 | 8.789 | 0 | 16.8 | 8.011 | 8.011 | opened
58 | Nom. capacity MV, MVA | 16+16 | 5 | 5 | 45 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 6.02 | 11.02 | 5 | 45 | 6.02 | 0 | 16.8 | 10.78
| Nom. capacity LV, MVA | 16+16 | 4.21 | 1.83 | 45 | 2.38 | 0 | 16.8 | 14.42 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.389 | 4.599 | 1.83 | 45 | 2.769 | 0 | 16.8 | 14.031
| SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 1.16 | 0.95 | 30 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 0.007 | 1.167 | 0.95 | 30 | 0.217 | 0 | 2.625 | 2.408 | 2.408 | opened
59 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.83 | 0 | - | 0.83 | 0 | 1.68 | 0.85 | 0.85 | opened | 60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.005 | 0.835 | 0 |  | 0.835 | 0 | 1.68 | 0.845 | 0.845 | opened
60 | SS 35/10 kv Kutafino | 1,6+1,6 | 0.22 | 0.83 | 30 | -0.61 | 0 | 1.68 | 2.29 | 2.29 | opened | 61 | SS 35/10 kv Kutafino | 1,6+1,6 | 5.893 | 6.113 | 0.83 | 30 | 5.283 | 0 | 1.68 | -3.603 | -3.603 | closed
61 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.55 | 1.59 | 30 | -1.04 | 0 | 2.625 | 3.665 | 3.665 | opened | 62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.048 | 0.598 | 1.59 | 30 | -0.992 | 0 | 2.625 | 3.617 | 3.617 | opened
62 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.43 | 0.47 | 60 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened | 63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.006 | 0.436 | 0.47 | 60 | -0.034 | 0 | 1.05 | 1.084 | 1.084 | opened
63 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.42 | 0.99 | 90 | -0.57 | 0 | 1.89 | 2.46 | 2.46 | opened | 64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0 | 0.42 | 0.99 | 90 | -0.57 | 0 | 1.89 | 2.46 | 2.46 | opened
64 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.54 | 1.7 | 30 | -1.16 | 0 | 5.88 | 7.04 | 7.04 | opened | 65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.353 | 0.893 | 1.7 | 30 | -0.807 | 0 | 5.88 | 6.687 | 6.687 | opened
65 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 7.38 | 1.41 | 90 | 5.97 | 0 | 10.5 | 4.53 | 4.53 | opened | 66 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 1.181 | 8.571 | 1.41 | 90 | 7.161 | 0 | 10.5 | 3.339 | 3.339 | opened
66 | Nom. capacity MV, MVA | 10+10 | 1.3 | 0.86 | 90 | 0.44 | 0 | 10.5 | 10.06 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.092 | 1.392 | 0.86 | 90 | 0.532 | 0 | 10.5 | 9.968
| Nom. capacity LV, MVA | 10+10 | 6.09 | 0.55 | 90 | 5.54 | 0 | 10.5 | 4.96 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.089 | 7.179 | 0.55 | 90 | 6.629 | 0 | 10.5 | 3.871
| SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.58 | 1.63 | 45 | -1.05 | 0 | 2.625 | 3.675 | 3.675 | opened | 67 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.021 | 0.601 | 1.63 | 45 | -1.029 | 0 | 2.625 | 3.654 | 3.654 | opened
67 | SS 35/10 kv Novopetrovka | 2,5+1,6 | 0.45 | 0.73 | 60 | -0.28 | 0 | 1.68 | 1.96 | 1.96 | opened | 68 | SS 35/10 kv Novopetrovka | 2,5+1,6 | 0.039 | 0.489 | 0.73 | 60 | -0.241 | 0 | 1.68 | 1.921 | 1.921 | opened
68 | SS 35/10 kv Putimets | 2,5+2,5 | 0.82 | 1.53 | 90 | -0.71 | 0 | 2.625 | 3.335 | 3.335 | opened | 69 | SS 35/10 kv Putimets | 2,5+2,5 | 0.146 | 0.966 | 1.53 | 90 | -0.564 | 0 | 2.625 | 3.189 | 3.189 | opened
69 | SS 110/10 kv Pishchevaya | 40+25 | 6.16 | 2.22 | 60 | 3.94 | 0 | 26.25 | 22.31 | 22.31 | opened | 70 | SS 110/10 kv Pishchevaya | 40+25 | 0.146 | 6.306 | 2.22 | 60 | 4.086 | 0 | 26.25 | 22.164 | 22.164 | opened
70 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.49 | 0.65 | 90 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | opened | 71 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0 | 0.49 | 0.65 | 90 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | opened
71 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 3.17 | 1.98 | 45 | 1.19 | 0 | 10.5 | 9.31 | 9.21 | opened | 72 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 0.846 | 4.026 | 1.98 | 45 | 2.046 | 0 | 10.5 | 8.454 | 8.454 | opened
72 | Nom. capacity MV, MVA | 10+10 | 1.32 | 1.41 | 45 | -0.09 | 0 | 10.5 | 10.59 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.124 | 1.444 | 1.41 | 45 | 0.034 | 0 | 10.5 | 10.466
| Nom. capacity LV, MVA | 10+10 | 1.86 | 0.57 | 45 | 1.29 | 0 | 10.5 | 9.21 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.722 | 2.582 | 0.57 | 45 | 2.012 | 0 | 10.5 | 8.488
| SS 35/10 kv Streletskaya | 4+4 | 2.24 | 0.91 | 90 | 1.33 | 0 | 4.2 | 2.87 | 2.87 | opened | 73 | SS 35/10 kv Streletskaya | 4+4 | 0.087 | 2.327 | 0.91 | 90 | 1.417 | 0 | 4.2 | 2.783 | 2.783 | opened
73 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 29.48 | 3.86 | 180 | 25.62 | 0 | 68.25 | 42.63 | 19 | opened | 74 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 2.329 | 31.709 | 3.86 | 180 | 27.849 | 0 | 68.25 | 40.401 | 40.401 | opened
74 | Nom. capacity MV, MVA | 20+20 | 7.1 | 5.1 | 90 | 2 | 0 | 21 | 19 |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.577 | 7.677 | 5.1 | 90 | 2.577 | 0 | 21 | 18.423
| Nom. capacity LV, MVA | 20+20+25+40 | 22.28 | 3.86 | 180 | 18.42 | 0 | 68.25 | 49.83 |  |  |  | Nom. capacity LV, MVA | 20+20+25+40 | 1.752 | 24.032 | 3.86 | 180 | 20.172 | 0 | 68.25 | 48.078
| SS 35/10 kv Soskovskaya | 4+3,2 | 1.49 | 0.64 | 90 | 0.85 | 0 | 3.36 | 2.51 | 2.51 | opened | 75 | SS 35/10 kv Soskovskaya | 4+3,2 | 0.068 | 1.558 | 0.64 | 90 | 0.918 | 0 | 3.36 | 2.442 | 2.442 | opened
75 | SS 35/10 kv Trosna | 5,6+3,2 | 0.81 | 1.76 | 30 | -0.95 | 0 | 3.36 | 4.31 | 4.31 | opened | 76 | SS 35/10 kv Trosna | 5,6+3,2 | 0.024 | 0.834 | 1.76 | 30 | -0.926 | 0 | 3.36 | 4.286 | 4.286 | opened
76 | SS 110/10 kv Khimmash | 25+25 | 8.13 | 1.51 | 120 | 6.62 | 0 | 26.25 | 19.63 | 19.63 | opened | 77 | SS 110/10 kv Khimmash | 25+25 | 3.582 | 11.712 | 1.51 | 120 | 10.202 | 0 | 26.25 | 16.048 | 16.048 | opened
77 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 1.12 | 0 | - | 1.12 | 0 | 5.88 | 4.76 | 4.76 | opened | 78 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0 | 1.12 | 0 |  | 1.12 | 0 | 5.88 | 4.76 | 4.76 | opened
78 | SS 35/10 kv Khotynetskaya | 4+2,5 | 2.47 | 1.49 | 80 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened | 79 | SS 35/10 kv Khotynetskaya | 4+2,5 | 0.119 | 2.589 | 1.49 | 80 | 1.099 | 0 | 2.625 | 1.526 | 1.526 | opened
79 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.53 | 1.03 | 80 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened | 80 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.029 | 0.559 | 1.03 | 80 | -0.471 | 0 | 1.68 | 2.151 | 2.151 | opened
80 | SS 110/10/6 kv Tsentralnaya | 25+25 | 13.82 | 3.46 | 135 | 10.36 | 0 | 26.25 | 15.89 | 15.89 | opened | 81 | SS 110/10/6 kv Tsentralnaya | 25+25 | 0 | 13.82 | 3.46 | 135 | 10.36 | 0 | 26.25 | 15.89 | 15.89 | opened
81 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 2.37 | 1.36 | 30 | 1.01 | 0 | 6.615 | 5.605 | 5.605 | opened | 82 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 0.057 | 2.447 | 1.36 | 30 | 1.087 | 0 | 6.615 | 5.528 | 5.528 | opened
82 | Nom. capacity MV, MVA | 6,3+6,3 | 0.97 | 0.54 | 30 | 0.43 | 0 | 6.615 | 6.185 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.048 | 1.018 | 0.54 | 30 | 0.478 | 0 | 6.615 | 6.137
| Nom. capacity LV, MVA | 6,3+6,3 | 1.42 | 0.82 | 30 | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.009 | 1.429 | 0.82 | 30 | 0.609 | 0 | 6.615 | 6.006
| SS 110/35/10 kv Shakhovo | 10+10 | 2.51 | 2.55 | 120 | -0.04 | 0 | 10.5 | 10.54 | 10.07 | opened | 83 | SS 110/35/10 kv Shakhovo | 10+10 | 0.228 | 2.748 | 2.55 | 120 | 0.198 | 0 | 10.5 | 10.302 | 10.302 | opened
83 | Nom. capacity MV, MVA | 10+10 | 0.82 | 0.39 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.146 | 0.966 | 0.39 | 120 | 0.576 | 0 | 10.5 | 9.924
| Nom. capacity LV, MVA | 10+10 | 1.7 | 2.16 | 120 | -0.46 | 0 | 10.5 | 10.96 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.082 | 1.782 | 2.16 | 120 | -0.378 | 0 | 10.5 | 10.878
| SS 35/10 kv Shepino | 2,5+1,6 | 1.4 | 1.1 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 84 | SS 35/10 kv Shepino | 2,5+1,6 | 0.102 | 1.502 | 1.1 | 120 | 0.402 | 0 | 1.68 | 1.278 | 1.278 | opened
84 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 10.72 | 0.74 | 60 | 9.98 | 0 | 26.25 | 16.27 | 16.27 | opened | 85 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 1.176 | 11.896 | 0.74 | 60 | 11.156 | 0 | 26.25 | 15.094 | 15.094 | opened
85 | SS 110/10 kv Yuzhnaya | 10+10 | 9.07 | 1.05 | 90 | 8.02 | 0 | 10.5 | 2.48 | 2.48 | opened | 86 | SS 110/10 kv Yuzhnaya | 10+10 | 1.418 | 10.488 | 1.05 | 90 | 9.438 | 0 | 10.5 | 1.062 | 1.062 | opened
86 | SS 220/110/10 kv Mtsensk | 40+40 | 9.81 | 0 | - | 9.81 | 0 | 42 | 32.19 | 32.19 | opened | 87 | SS 220/110/10 kv Mtsensk | 40+40 | 0.486 | 10.296 | 0 |  | 10.296 | 0 | 42 | 31.704 | 31.704 | opened
87 | SS 110/35/10 kv Kommash | 10+16 | 10.51 | 4.65 | 90 | 5.86 | 0 | 10.5 | 4.64 | 4.64 | opened | 88 | SS 110/35/10 kv Kommash | 10+16 | 0.085 | 10.585 | 4.65 | 90 | 5.935 | 0 | 10.5 | 4.565 | 4.565 | opened
88 | Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.5 | 4.65 | 90 | 5.85 | 0 | 10.5 | 4.65 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.085 | 10.585 | 4.65 | 90 | 5.935 | 0 | 10.5 | 4.565
| SS 110/35/10 kv Novosergievka | 6,3+10 | 2.55 | 4.13 | 120 | -1.58 | 0 | 6.615 | 8.195 | 6.695 | opened | 89 | SS 110/35/10 kv Novosergievka | 6,3+10 | 0.108 | 2.668 | 4.13 | 120 | -1.462 | 0 | 6.615 | 8.077 | 8.077 | opened
89 | Nom. capacity MV, MVA | 6,3+10 | 2.32 | 2.4 | 120 | -0.08 | 0 | 6.615 | 6.695 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.108 | 2.428 | 2.4 | 120 | 0.028 | 0 | 6.615 | 6.587
| Nom. capacity LV, MVA | 6,3+10 | 0.24 | 1.73 | 120 | -1.49 | 0 | 6.615 | 8.105 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.24 | 1.73 | 120 | -1.49 | 0 | 6.615 | 8.105
| SS 110/10 kv 1 Voin | 6,3+6,3 | 2.33 | 1.83 | 120 | 0.5 | 0 | 6.615 | 6.115 | 6.115 | opened | 90 | SS 110/10 kv 1 Voin | 6,3+6,3 | 1.648 | 3.978 | 1.83 | 120 | 2.148 | 0 | 6.615 | 4.467 | 4.467 | opened
90 | SS 110/35/10 kv Zalegoshch | 10+16 | 5.94 | 3.95 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened | 91 | SS 110/35/10 kv Zalegoshch | 10+16 | 0.766 | 6.676 | 3.95 | 120 | 2.726 | 0 | 10.5 | 7.774 | 7.774 | opened
91 | Nom. capacity MV, MVA | 10+16 | 2.48 | 2.39 | 120 | 0.09 | 0 | 10.5 | 10.41 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.05 | 2.53 | 2.39 | 120 | 0.14 | 0 | 10.5 | 10.36
| Nom. capacity LV, MVA | 10+16 | 3.43 | 1.56 | 120 | 1.87 | 0 | 10.5 | 8.63 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.716 | 4.146 | 1.56 | 120 | 2.586 | 0 | 10.5 | 7.914
| SS 110/10 kv Kochety | 2,5+2,5 | 0.34 | 0.66 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened | 92 | SS 110/10 kv Kochety | 2,5+2,5 | 0.162 | 0.502 | 0.66 | 120 | -0.158 | 0 | 2.625 | 2.783 | 2.783 | opened
92 | SS 110/35/10 kv Bolkhov | 10+10 | 8.61 | 4.1 | 120 | 4.51 | 0 | 10.5 | 5.99 | 5.99 | opened | 93 | SS 110/35/10 kv Bolkhov | 10+10 | 0.422 | 9.032 | 4.1 | 120 | 4.932 | 0 | 10.5 | 5.568 | 5.568 | opened
93 | Nom. capacity MV, MVA | 10+10 | 3.01 | 2.45 | 120 | 0.56 | 0 | 10.5 | 9.94 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.384 | 3.394 | 2.45 | 120 | 0.944 | 0 | 10.5 | 9.556
| Nom. capacity LV, MVA | 10+10 | 5.6 | 1.65 | 120 | 3.95 | 0 | 10.5 | 6.55 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.038 | 5.638 | 1.65 | 120 | 3.988 | 0 | 10.5 | 6.512
| SS 110/35/10 kv Novosil | 10+10 | 4.69 | 2.98 | 120 | 1.71 | 0 | 10.5 | 8.79 | 8.79 | opened | 94 | SS 110/35/10 kv Novosil | 10+10 | 0.069 | 4.759 | 2.98 | 120 | 1.779 | 0 | 10.5 | 8.721 | 8.721 | opened
94 | Nom. capacity MV, MVA | 10+10 | 2.4 | 1.46 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.038 | 2.438 | 1.46 | 120 | 0.978 | 0 | 10.5 | 9.522
| Nom. capacity LV, MVA | 10+10 | 2.29 | 1.52 | 120 | 0.77 | 0 | 10.5 | 9.73 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.031 | 2.321 | 1.52 | 120 | 0.801 | 0 | 10.5 | 9.699
| SS 110/35/10 kv Znamenskaya | 10+10 | 2.2 | 1.78 | 120 | 0.42 | 0 | 10.5 | 10.08 | 10.08 | opened | 95 | SS 110/35/10 kv Znamenskaya | 10+10 | 0.052 | 2.252 | 1.78 | 120 | 0.472 | 0 | 10.5 | 10.028 | 10.028 | opened
95 | Nom. capacity MV, MVA | 10+10 | 0.49 | 0.34 | 120 | 0.15 | 0 | 10.5 | 10.35 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.49 | 0.34 | 120 | 0.15 | 0 | 10.5 | 10.35
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.052 | 1.762 | 1.44 | 120 | 0.322 | 0 | 10.5 | 10.178
| SS 35/10 kv Apalkovo | 1,8+1,8 | 0.43 | 0.48 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened | 96 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0.192 | 0.622 | 0.48 | 120 | 0.142 | 0 | 1.89 | 1.748 | 1.748 | opened
96 | SS 35/10 kv Podberyozovo | 4+1 | 0.26 | 0.59 | 120 | -0.33 | 0 | 1.05 | 1.38 | 1.38 | opened | 97 | SS 35/10 kv Podberyozovo | 4+1 | 0.016 | 0.276 | 0.59 | 120 | -0.314 | 0 | 1.05 | 1.364 | 1.364 | opened
97 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.51 | 0 |  | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened | 98 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.006 | 0.516 | 0 |  | 0.516 | 0 | 1.68 | 1.164 | 1.164 | opened
98 | SS 35/10 kv Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened | 99 | SS 35/10 kv Alyoshnya | 1+1 | 0.002 | 0.342 | 0.24 | 120 | 0.102 | 0 | 1.05 | 0.948 | 0.948 | opened
99 | SS 35/10 kv Lomovoe | 2,5+2,5 | 1 | 0 | - | 1 | 0 | 2.625 | 1.625 | 1.625 | opened | 100 | SS 35/10 kv Lomovoe | 2,5+2,5 | 0.023 | 1.023 | 0 |  | 1.023 | 0 | 2.625 | 1.602 | 1.602 | opened
100 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.91 | 0.63 | 120 | 0.28 |  | 2.625 | 2.345 | 2.345 | opened | 101 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.025 | 0.935 | 0.63 | 120 | 0.305 | 0 | 2.625 | 2.32 | 2.32 | opened
101 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | opened | 102 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | opened
102 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.32 | 0 | - | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened | 103 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0 | 0.32 | 0 |  | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
103 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 1.1 | 0.67 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 104 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.134 | 1.234 | 0.67 | 120 | 0.564 | 0 | 2.625 | 2.061 | 2.061 | opened
104 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 105 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.014 | 0.514 | 0.37 | 120 | 0.144 | 0 | 1.68 | 1.536 | 1.536 | opened
105 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.63 | 0.69 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened | 106 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.017 | 0.647 | 0.69 | 120 | -0.043 | 0 | 2.625 | 2.668 | 2.668 | opened
106 | SS 35/10 kv Odinok | 1,6+1,6 | 0.38 | 0 | - | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened | 107 | SS 35/10 kv Odinok | 1,6+1,6 | 0.021 | 0.401 | 0 |  | 0.401 | 0 | 1.68 | 1.279 | 1.279 | opened
107 | SS 35/10 kv Uzkoe | 1,6+1 | 0.21 | 0.25 | 120 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened | 108 | SS 35/10 kv Uzkoe | 1,6+1 | 0 | 0.21 | 0.25 | 120 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened
108 | SS 35/10 kv Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 109 | SS 35/10 kv Korsakovo | 2,5+4 | 0.054 | 0.814 | 0.69 | 120 | 0.124 | 0 | 2.625 | 2.501 | 2.501 | opened
109 | SS 35/10 kv Paramonovo | 4+2,5 | 0.88 | 0.76 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 110 | SS 35/10 kv Paramonovo | 4+2,5 | 0 | 0.88 | 0.76 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
110 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.22 | 0 | - | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 111 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.018 | 0.238 | 0 |  | 0.238 | 0 | 1.68 | 1.442 | 1.442 | opened
111 | SS 110/35/10 kv Verkhovye I | 16+10 | 8.57 | 3.65 | 120 | 4.92 | 0 | 10.5 | 5.58 | 5.58 | opened | 112 | SS 110/35/10 kv Verkhovye I | 16+10 | 0.161 | 8.791 | 3.65 | 120 | 5.141 | 0 | 10.5 | 5.359 | 5.359 | opened
112 | Nom. capacity MV, MVA | 16+10 | 3.01 | 2.05 | 120 | 0.96 | 0 | 10.5 | 9.54 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.025 | 3.035 | 2.05 | 120 | 0.985 | 0 | 10.5 | 9.515
| Nom. capacity LV, MVA | 16+10 | 5.62 | 1.6 | 120 | 4.02 | 0 | 10.5 | 6.48 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.136 | 5.756 | 1.6 | 120 | 4.156 | 0 | 10.5 | 6.344
| SS 110/35/10 kv Verkhovye II | 40+40 | 16.92 | 0.3 | - | 16.62 | 0 | 42 | 25.38 | 25.38 | opened | 113 | SS 110/35/10 kv Verkhovye II | 40+40 | 0.009 | 16.959 | 0.3 |  | 16.659 | 0 | 42 | 25.341 | 25.341 | opened
113 | Nom. capacity MV, MVA | 40+40 | 0.47 | 0.3 | - | 0.17 | 0 | 42 | 41.83 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.009 | 0.479 | 0.3 |  | 0.179 | 0 | 42 | 41.821
| Nom. capacity LV, MVA | 40+40 | 16.48 | 0 | - | 16.48 | 0 | 42 | 25.52 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 16.48 | 0 |  | 16.48 | 0 | 42 | 25.52
| SS 110/35/10 kv Dolgoe | 16+10 | 7.02 | 3.38 | 120 | 3.64 | 0 | 10.5 | 6.86 | 6.86 | opened | 114 | SS 110/35/10 kv Dolgoe | 16+10 | 0.02 | 7.05 | 3.38 | 120 | 3.67 | 0 | 10.5 | 6.83 | 6.83 | opened
114 | Nom. capacity MV, MVA | 16+10 | 2.67 | 2.38 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.013 | 2.683 | 2.38 | 120 | 0.303 | 0 | 10.5 | 10.197
| Nom. capacity LV, MVA | 16+10 | 4.36 | 1 | 120 | 3.36 | 0 | 10.5 | 7.14 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.007 | 4.367 | 1 | 120 | 3.367 | 0 | 10.5 | 7.133
| SS 110/35/10 kv Kolpny-110 | 10+16 | 5.8 | 2.79 | 120 | 3.01 | 0 | 10.5 | 7.49 | 7.49 | opened | 115 | SS 110/35/10 kv Kolpny-110 | 10+16 | 0.063 | 5.843 | 2.79 | 120 | 3.053 | 0 | 10.5 | 7.447 | 7.447 | opened
115 | Nom. capacity MV, MVA | 10+16 | 3.92 | 2.46 | 120 | 1.46 | 0 | 10.5 | 9.04 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.01 | 3.93 | 2.46 | 120 | 1.47 | 0 | 10.5 | 9.03
| Nom. capacity LV, MVA | 10+16 | 1.86 | 0.33 | 120 | 1.53 | 0 | 10.5 | 8.97 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.053 | 1.913 | 0.33 | 120 | 1.583 | 0 | 10.5 | 8.917
| SS 110/35/10 kv Kr. Zarya | 10+10 | 5.24 | 1.54 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | opened | 116 | SS 110/35/10 kv Kr. Zarya | 10+10 | 0.065 | 5.315 | 1.54 | 120 | 3.775 | 0 | 10.5 | 6.725 | 6.725 | opened
116 | Nom. capacity MV, MVA | 10+10 | 1.69 | 1.29 | 120 | 0.4 | 0 | 10.5 | 10.1 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.024 | 1.714 | 1.29 | 120 | 0.424 | 0 | 10.5 | 10.076
| Nom. capacity LV, MVA | 10+10 | 3.56 | 0.25 | 120 | 3.31 | 0 | 10.5 | 7.19 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.041 | 3.601 | 0.25 | 120 | 3.351 | 0 | 10.5 | 7.149
| SS 110/35/10 kv Pokrovskaya | 10+10 | 5.84 | 2.84 | 120 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened | 117 | SS 110/35/10 kv Pokrovskaya | 10+10 | 0.427 | 6.287 | 2.84 | 120 | 3.447 | 0 | 10.5 | 7.053 | 7.053 | opened
117 | Nom. capacity MV, MVA | 10+10 | 2.41 | 2.12 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.116 | 2.526 | 2.12 | 120 | 0.406 | 0 | 10.5 | 10.094
| Nom. capacity LV, MVA | 10+10 | 3.45 | 0.72 | 120 | 2.73 | 0 | 10.5 | 7.77 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.311 | 3.761 | 0.72 | 120 | 3.041 | 0 | 10.5 | 7.459
| SS 110/35/6 kv Cherkasskaya | 40+25 | 29.08 | 13.39 | 120 | 15.69 | 0 | 26.25 | 10.56 | 10.56 | opened | 118 | SS 110/35/6 kv Cherkasskaya | 40+25 | 2.477 | 31.707 | 13.39 | 120 | 18.317 | 0 | 26.25 | 7.933 | 7.933 | opened
118 | Nom. capacity MV, MVA | 40+25 | 13.36 | 10.84 | 120 | 2.52 | 0 | 26.25 | 23.73 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.453 | 15.813 | 10.84 | 120 | 4.973 | 0 | 26.25 | 21.277
| Nom. capacity LV, MVA | 40+25 | 15.87 | 2.55 | 120 | 13.32 | 0 | 26.25 | 12.93 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0.024 | 15.894 | 2.55 | 120 | 13.344 | 0 | 26.25 | 12.906
| SS 110/6 kv Plastmass | 16+16 | 10.73 | 0 | - | 10.73 | 0 | 16.8 | 6.07 | 6.07 | opened | 119 | SS 110/6 kv Plastmass | 16+16 | 0 | 10.73 | 0 |  | 10.73 | 0 | 16.8 | 6.07 | 6.07 | opened
119 | SS 110/10 kv PM | 10+10 | 5.07 | 0 | - | 5.07 | 0 | 10.5 | 5.43 | 5.43 | opened | 120 | SS 110/10 kv PM | 10+10 | 0 | 5.07 | 0 |  | 5.07 | 0 | 10.5 | 5.43 | 5.43 | opened
120 | SS 110/10 kv Rechitsa | 6,3+6,3 | 1.81 | 1.85 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened | 121 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.015 | 1.825 | 1.85 | 120 | -0.025 | 0 | 6.615 | 6.64 | 6.64 | opened
121 | SS 110/10 kv R.Brod | 5,6+10 | 1.69 | 0.29 | 120 | 1.4 | 0 | 5.88 | 4.48 | 4.48 | opened | 122 | SS 110/10 kv R.Brod | 5,6+10 | 0.559 | 2.249 | 0.29 | 120 | 1.959 | 0 | 5.88 | 3.921 | 3.921 | opened
122 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.61 | 0.13 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened | 123 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.035 | 0.645 | 0.13 | 120 | 0.515 | 0 | 1.68 | 1.165 | 1.165 | opened
123 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 1.6 | 0.65 | 120 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened | 124 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 0.052 | 1.652 | 0.65 | 120 | 1.002 | 0 | 2.625 | 1.623 | 1.623 | opened
124 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0.76 | 0.43 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 125 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0 | 0.76 | 0.43 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
125 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 1.1 | 0.56 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | opened | 126 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.027 | 1.127 | 0.56 | 120 | 0.567 | 0 | 1.68 | 1.113 | 1.113 | opened
126 | SS 35/10 kv Droskovo | 4+2,5 | 1.34 | 0 | - | 1.34 | 0 | 2.625 | 1.285 | 1.285 | opened | 127 | SS 35/10 kv Droskovo | 4+2,5 | 0.081 | 1.421 | 0 |  | 1.421 | 0 | 2.625 | 1.204 | 1.204 | opened
127 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 2.44 | 0.39 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | opened | 128 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 0 | 2.44 | 0.39 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | opened
128 | SS 35/10 kv Krutoe | 2,5+1,6 | 1.59 | 0.87 | 120 | 0.72 | 0 | 1.68 | 0.96 | 0.96 | opened | 129 | SS 35/10 kv Krutoe | 2,5+1,6 | 0.096 | 1.686 | 0.87 | 120 | 0.816 | 0 | 1.68 | 0.864 | 0.864 | opened
129 | SS 35/10 kv Mezentsevo | 4+6,3 | 3.15 | 1.11 | 80 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | opened | 130 | SS 35/10 kv Mezentsevo | 4+6,3 | 0.153 | 3.303 | 1.11 | 80 | 2.193 | 0 | 4.2 | 2.007 | 2.007 | opened
130 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.12 | 0 | - | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 131 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.008 | 0.128 | 0 |  | 0.128 | 0 | 1.68 | 1.552 | 1.552 | opened
131 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0.44 | 0.39 | - | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened | 132 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0 | 0.44 | 0.39 |  | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
132 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 1.85 | 0.54 | 80 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened | 133 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 0.069 | 1.919 | 0.54 | 80 | 1.379 | 0 | 2.625 | 1.246 | 1.246 | opened
133 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.47 | 1.67 | 120 | -1.2 | 0 | 3.36 | 4.56 | 4.56 | opened | 134 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.009 | 0.479 | 1.67 | 120 | -1.191 | 0 | 3.36 | 4.551 | 4.551 | opened
134 | SS 35/6 kv Pushkarskaya | 4+4 | 5.27 | 0 |  | 5.27 | 0 | 4.2 | -1.07 | -1.07 | closed | 135 | SS 35/6 kv Pushkarskaya | 4+4 | 0 | 5.27 | 0 |  | 5.27 | 0 | 4.2 | -1.07 | -1.07 | closed
135 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0.68 | 0.25 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 136 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0 | 0.68 | 0.25 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
136 | SS 35/10 kv Rosstani | 2,5+2,5 | 1.28 | 0.7 | 80 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 137 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.059 | 1.339 | 0.7 | 80 | 0.639 | 0 | 2.625 | 1.986 | 1.986 | opened
137 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.4 | 1.5 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 138 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.115 | 2.515 | 1.5 | 120 | 1.015 | 0 | 2.625 | 1.61 | 1.61 | opened
138 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.47 | 0.33 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 139 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.013 | 0.483 | 0.33 | 120 | 0.153 | 0 | 1.68 | 1.527 | 1.527 | opened
139 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0.24 | 0 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 140 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0 | 0.24 | 0 |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
140 | SS 35/10 kv SSK | 1,6+1 | 0.11 | 0 |  | 0.11 | 0 | 1.05 | 0.94 | 0.94 | opened | 37 | SS 35/10 kv SSK | 1,6+1 | 0 | 0.11 | 0 |  | 0.11 | 0 | 1.05 | 0.94 | 0.94 | opened
141 | SS 35/10 kv Urynok | 1,6+1,6 | 1.23 | 0.52 | 20 | 0.71 | 0 | 1.68 | 0.97 | 0.97 | opened | 141 | SS 35/10 kv Urynok | 1,6+1,6 | 0 | 1.23 | 0.52 | 20 | 0.71 | 0 | 1.68 | 0.97 | 0.97 | opened
142 | SS 35/10 kv Khomutovo | 4+4 | 2.54 | 0.31 | 80 | 2.23 | 0 | 4.2 | 1.97 | 1.97 | opened | 142 | SS 35/10 kv Khomutovo | 4+4 | 0.012 | 2.552 | 0.31 | 80 | 2.242 | 0 | 4.2 | 1.958 | 1.958 | opened
| Total: | [10 empty] | 2: Total:; 4: 102.372; 5: 748.402
| deficit | [8 empty] | -2.965 |  | 2: deficit; Мin. 12: -26.81
| proficit | [8 empty] | 541.995 |  | 2: proficit; Мin. 12: 525.014

## Курск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Additional capacity according to provided technical specifications | Expected load at main substation | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations | [11 empty] | One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.64 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.66 | 1.2 | opened | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.016 | 1.656 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.644 | 1.189 | opened
| Nom. capacity MV, MVA | 6.3 | 1.1 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.2 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.011 | 1.111 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.189
| Nom. capacity MV, MVA | 6.3 | 0.54 | 4 | 24 hours | 4 | 0 | 4 | 3.46 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.005 | 0.545 | 4 | 24 hours | 4 | 0 | 4 | 3.455
2 | SS 110/10 Beketovo | 1*6,3 | 0.39 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.76 | 1.76 | opened | 2 | SS 110/10 Beketovo | 1*6,3 |  | 0.39 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.76 | 1.76 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.84 | 6.7 | 24 hours | 6.7 | 0 | 6.7 | 3.86 | 0.16 | opened | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.181 | 3.021 | 6.7 | 24 hours | 6.7 | 0 | 6.7 | 3.679 | 0.012 | opened
| Nom. capacity MV, MVA | 6.3 | 0.5 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 0.533 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.667
| Nom. capacity LV, MVA | 6.3 | 2.34 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 0.16 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.148 | 2.488 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 0.012
4 | SS 110/10 Voskhod | 1*10 | 0.8 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.7 | 1.7 | opened | 4 | SS 110/10 Voskhod | 1*10,0 | 0.039 | 0.839 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.661 | 1.661 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.82 | 6 | 24 hours | 6 | 0 | 6 | 5.18 | 1.48 | opened | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0 | 0.82 | 6 | 24 hours | 6 | 0 | 6 | 5.18 | 1.48 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.82 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.48 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.82 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.48
6 | SS 110/35/10 Zhukovka | 1*10 | 1.1 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.06 | 0.49 | opened | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.016 | 1.116 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.044 | 0.49 | opened
| Nom. capacity MV, MVA | 10 | 0.93 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.57 |  |  |  | Nom. capacity MV, MVA | 10 | 0.016 | 0.946 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.554
| Nom. capacity LV, MVA | 10 | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49 |  |  |  | Nom. capacity LV, MVA | 10 |  | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | SS 110/10 Zabelye | 1*2,5 | 0.31 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.84 | 1.84 | opened | 7 | SS 110/10 Zabelye | 1*2,5 | 0.003 | 0.313 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.837 | 1.837 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened | 8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened
9 | SS 110/35/10 Lachinovo | 1*10 | 1.28 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.85 | 1 | opened | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.46 | 1.74 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.39 | 0.54 | opened
| Nom. capacity MV, MVA | 10 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85
| Nom. capacity LV, MVA | 10 | 0.53 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1 |  |  |  | Nom. capacity LV, MVA | 10 | 0.46 | 0.99 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.54
10 | SS 110/10 Malaya Loknya | 1*10 | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened | 10 | SS 110/10 Malaya Loknya | 1*10,0 |  | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened
11 | SS 110/35/10 Maritsa | 1*2,5 | 0.99 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.93 | 0.93 | opened | 11 | SS 110/35/10 Maritsa | 1*2,5 | 0.01 | 1 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.92 | 0.92 | opened
12 | SS 110/35/10 Raskhovets | 1*6,3 | 0.56 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.33 | 1.97 | opened | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.005 | 0.565 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.325 | 1.97 | opened
| Nom. capacity MV, MVA | 6.3 | 0.38 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.36 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.005 | 0.385 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.355
| Nom. capacity LV, MVA | 6.3 | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97
13 | SS 110/10 Semyonovskaya | 1*2,5 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.403 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.997 | 0.997 | opened
14 | SS 110/6 Teplichnaya | 1*16 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened | 14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.7 | 9.8 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | -3.16 | -3.16 | closed
15 | SS 110/35/10 Troitskaya | 1*10 | 3.01 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.49 | 0.79 | opened | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 0.745 | 3.755 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 3.745 | 0.776 | opened
| Nom. capacity MV, MVA | 10 | 2.7 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.7 |  |  |  | Nom. capacity MV, MVA | 10 | 0.731 | 3.431 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 2.969
| Nom. capacity LV, MVA | 10 | 0.31 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.79 |  |  |  | Nom. capacity LV, MVA | 10 | 0.014 | 0.324 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.776
16 | SS 35/10 Avtodor | 1*2,5 | 0.46 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.34 | 0.34 | opened | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.503 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.297 | 0.297 | opened
17 | SS 35/10 Agronom | 1*1,8 | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.195 | 0.895 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.065 | 0.065 | opened
18 | SS 35/10 Akimovka | 1*2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened | 18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1*2,5 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.015 | 0.295 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.135 | 1.135 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1*4 | 0.55 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.79 | 0.79 | opened | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.015 | 0.565 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.775 | 0.775 | opened
21 | SS 35/10 B. Gneushevo | 1*2,5 | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 |  | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened
22 | SS 35/10 B.Soldatskoe1 | 1*3,2 | 0.78 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 2.05 | 2.05 | opened | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.231 | 1.011 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.819 | 1.819 | opened
23 | SS 35/10 Banishchi | 1*1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.015 | 0.235 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.405 | 0.405 | opened
24 | SS 35/10 Baranovo | 1*4 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.0977 | 0.5577 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.8723 | 0.8723 | opened
25 | SS 35/10 Belgorodka | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.865 | 1.865 | opened
26 | SS 35/10 Belitsa | 1*4 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.262 | 0.862 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.898 | 0.898 | opened
27 | SS 35/10 Biryukovka | 1*1,6 | 0.6 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.07 | 0.07 | opened | 27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.6 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.07 | 0.07 | opened
28 | SS 35/10 Bobrovka | 1*1,6 | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened | 28 | SS 35/10 Bobrovka | 1 х 1,6 |  | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened
29 | SS 35/10 Bobrovo | 1*2,5 | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened | 29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened
30 | SS 35/10 Budki | 1*1 | 0.09 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.55 | 0.55 | opened | 30 | SS 35/10 Budki | 1 х 1,0 |  | 0.09 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.55 | 0.55 | opened
31 | SS 35/10 Bukreevka (CPS) | 1*1,8 | 0.59 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.01 | 1.01 | opened | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.033 | 0.623 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.977 | 0.977 | opened
32 | SS 35/10 Bukreevka (WPS) | 1*1,6 | 0.21 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.43 | 0.43 | opened | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.037 | 0.247 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.393 | 0.393 | opened
33 | SS 35/10 Burtsevka | 1*1,6 | 0.18 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.25 | 1.25 | opened | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.022 | 0.202 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.228 | 1.228 | opened
34 | SS 35/10 Bykovo | 1*4 | 0.89 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.54 | 0.54 | opened | 34 | SS 35/10 Bykovo | 1 х 4,0 | 0.205 | 1.095 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.335 | 0.335 | opened
35 | SS 35/10 V. Shchigor | 1*2,5 | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened | 35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened
36 | SS 35/10 Vanino | 1*2,5 | 0.36 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.44 | 0.44 | opened | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.058 | 0.418 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.382 | 0.382 | opened
37 | SS 35/10 Vasilyevka | 1*2,5 | 0.64 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.41 | 0.41 | opened | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.035 | 0.675 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.375 | 0.375 | opened
38 | SS 35/10 Water storage | 1*4 | 1.58 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 1.14 | 1.14 | opened | 38 | SS 35/10 Water storage | 1 х 4,0 | 3.536 | 5.116 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | -2.396 | -2.396 | closed
39 | SS 35/10 Volokonsk | 1*2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened | 39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1*2,5 | 0.65 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.25 | 0.25 | opened | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.664 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.236 | 0.236 | opened
41 | SS 35/10 Voronok | 1*4 | 0.86 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.24 | 1.24 | opened | 41 | SS 35/10 Voronok | 1 х 4,0 | 0.013 | 0.873 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.227 | 1.227 | opened
42 | SS 35/10 Vyazovoe | 1*2,5 | 0.66 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.49 | 1.49 | opened | 42 | SS 35/10 Vyazovoe | 1 х 2,5 |  | 0.66 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.49 | 1.49 | opened
43 | SS 35/10 Gakhovo | 1*2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.57 | 1.57 | opened
44 | SS 35/10 Generalshino | 1*2,5 | 0.25 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.01 | 0.26 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.24 | 1.24 | opened
45 | SS 35/10 Glazovo | 1*2,5 | 0.94 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.46 | 0.46 | opened | 45 | SS 35/10 Glazovo | 1 х 2,5 |  | 0.94 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.46 | 0.46 | opened
46 | SS 35/10 Glebovo | 1*2,5 | 0.49 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.91 | 0.91 | opened | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.003 | 0.493 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.907 | 0.907 | opened
47 | SS 35/10 Gordeevka | 1*1,6 | 0.12 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.58 | 0.58 | opened | 47 | SS 35/10 Gordeevka | 1 х 1,6 |  | 0.12 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.58 | 0.58 | opened
48 | SS 35/10 Gorodensk | 1*1,6 | 0.59 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.17 | 0.17 | opened | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.044 | 0.634 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.126 | 0.126 | opened
49 | SS 35/10 Goryainovo | 1*2,5 | 0.5 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.6 | 0.6 | opened | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.011 | 0.511 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.589 | 0.589 | opened
50 | SS 35/10 12th State stud farm | 1*2,5 | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened | 50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened
51 | SS 35/10 Grayvoronka | 1*2,5 | 0.5 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.93 | 0.93 | opened | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.042 | 0.542 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.888 | 0.888 | opened
52 | SS 35/10 Grinyovka | 1*2,5 | 0.28 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.57 | 2.57 | opened | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.005 | 0.285 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.565 | 2.565 | opened
53 | SS 35/10 Gustomoy | 1*1,6 | 0.21 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.73 | 0.73 | opened | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.006 | 0.216 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.724 | 0.724 | opened
54 | SS 35/10 Daryino | 1*2,5 | 0.4 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.4 | 1.4 | opened | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.032 | 0.432 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.368 | 1.368 | opened
55 | SS 35/10 Demyakino | 1*2,5 | 0.43 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.37 | 0.37 | opened | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.026 | 0.456 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.344 | 0.344 | opened
56 | SS 35/10 Efrosimovka | 1*1,8 | 0.38 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.69 | 0.69 | opened | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.025 | 0.405 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.665 | 0.665 | opened
57 | SS 35/10 Zhdanovo | 1*2,5 | 0.38 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.47 | 0.47 | opened | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.038 | 0.418 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.432 | 0.432 | opened
58 | SS 35/10 Zashchitnoe | 1*1,6 | 0.32 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.83 | 1.83 | opened | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.011 | 0.331 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.819 | 1.819 | opened
59 | SS 35/10 Zvannoe | 1*2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.043 | 0.643 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.197 | 0.197 | opened
60 | SS 35/10 Znamenka | 1*1,8 | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened | 60 | SS 35/10 Znamenka | 1 х 1,8 |  | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened
61 | SS 35/10 Iskra | 1*2,5 | 0.16 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.42 | 0.42 | opened | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.033 | 0.193 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.387 | 0.387 | opened
62 | SS 35/10 Kazanka | 1*4 | 0.33 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.47 | 0.47 | opened | 62 | SS 35/10 Kazanka | 1 х 4,0 |  | 0.33 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.47 | 0.47 | opened
63 | SS 35/10 Kalinovka (new) | 1*2,5 | 0.17 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.63 | 1.63 | opened | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.01 | 0.18 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.62 | 1.62 | opened
64 | SS 35/10 Karyzh | 1*1,6 | 0.18 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.46 | 0.46 | opened | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.01 | 0.19 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.45 | 0.45 | opened
65 | SS 35/10 Kitaevka | 1*1,6 | 0.26 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.48 | 0.48 | opened | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.202 | 0.462 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.278 | 0.278 | opened
66 | SS 35/10 Kobylki | 1*2,5 | 0.68 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.85 | 0.85 | opened | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.031 | 0.711 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.819 | 0.819 | opened
67 | SS 35/10 Kolontaevka | 1*2,5 | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened | 67 | SS 35/10 Kolontaevka | 1 х 2,5 |  | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened
68 | SS 35/10 Kondratovka | 1*1,8 | 0.55 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.87 | 0.87 | opened | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.022 | 0.572 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.848 | 0.848 | opened
69 | SS 35/10 Korovyakovka | 1*1,6 | 0.21 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.55 | 0.55 | opened | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.009 | 0.219 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.541 | 0.541 | opened
70 | SS 35/10 Lezhenki | 1*2,5 | 0.09 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.34 | 1.34 | opened | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.104 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.326 | 1.326 | opened
71 | SS 35/10 Leninskaya | 1*1,8 | 0.67 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.06 | 0.06 | opened | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.025 | 0.695 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.035 | 0.035 | opened
72 | SS 35/10 Lobazovka | 1*2,5 | 0.86 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.23 | 0.23 | opened | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.011 | 0.871 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.219 | 0.219 | opened
73 | SS 35/10 Lugovka | 1*1,6 | 0.54 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.75 | 0.75 | opened | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.035 | 0.575 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.715 | 0.715 | opened
74 | SS 35/10 Lyubava | 1*6,3 | 0.31 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.84 | 0.84 | opened | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0.008 | 0.318 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.832 | 0.832 | opened
75 | SS 35/10 Lyubimovka-1 | 1*3,2 | 0 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.96 | 0.96 | opened | 75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.041 | 0.041 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.919 | 0.919 | opened
76 | SS 35/10 M. Kamenets | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.051 | 0.651 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.449 | 0.449 | opened
77 | SS 35/10 М. Gneushevo | 1*4 | 0.7 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.58 | 0.58 | opened | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.005 | 0.705 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.575 | 0.575 | opened
78 | SS 35/10 М. Kryuki | 1*2,5 | 0.4 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.79 | 0.79 | opened | 78 | SS 35/10 М. Kryuki | 1 х 2,5 |  | 0.4 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.79 | 0.79 | opened
79 | SS 35/10 Markovo | 1*2,5 | 0.65 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.15 | 0.15 | opened | 79 | SS 35/10 Markovo | 1 х 2,5 | 0.001 | 0.651 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.149 | 0.149 | opened
80 | SS 35/10 Marmyzhi | 1*2,5 | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened | 80 | SS 35/10 Marmyzhi | 1 х 2,5 |  | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened
81 | SS 35/10 Melovoe | 1*4 | 0.99 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.16 | 1.16 | opened | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.013 | 1.003 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.147 | 1.147 | opened
82 | SS 35/10 Mokva | 1*4 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.033 | 0.533 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.617 | 1.617 | opened
83 | SS 35/10 Mokrusheno | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.026 | 0.626 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.474 | 0.474 | opened
84 | SS 35/10 Molotychi | 1*2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
85 | SS 35/10 Mochaki | 1*2,5 | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened | 85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened
86 | SS 35/10 N. Vladimirovka | 1*2,5 | 0.08 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.22 | 4.22 | opened | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.08 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.22 | 4.22 | opened
87 | SS 35/10 N. Gurovo | 1*4,0 | 0.73 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.42 | 1.42 | opened | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.008 | 0.738 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.412 | 1.412 | opened
88 | SS 35/10 Nadeyka | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.168 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.232 | 1.232 | opened
89 | SS 35/10 Niva | 1*2,5 | 0.4 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.16 | 1.16 | opened | 89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.415 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.145 | 1.145 | opened
90 | SS 35/10 Olgovka | 1*2,5 | 0.41 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.56 | 0.56 | opened | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0.005 | 0.415 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.555 | 0.555 | opened
91 | SS 35/10 Olkhovatka | 1*4 | 0.38 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.26 | 0.26 | opened | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.01 | 0.39 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.25 | 0.25 | opened
92 | SS 35/10 Orositelnaya | 1*4 | 0.93 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 2.04 | 2.04 | opened | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.71 | 1.64 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 1.33 | 1.33 | opened
93 | SS 35/10 Peny-2 | 1*2,5 | 0.6 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.72 | 1.72 | opened | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.41 | 1.01 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.31 | 1.31 | opened
94 | SS 35/10 Perestuplino (old) | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
95 | SS 35/10 Perestuplino (new) | 1*2,5 | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 |  | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened
96 | SS 35/10 Petrovo | 1*6,3 | 1 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.15 | 1.15 | opened | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0.099 | 1.099 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.051 | 1.051 | opened
97 | SS 35/10 Petrovskaya | 1*2,5 | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened | 97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened
98 | SS 35/10 Pokrovskoe | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.865 | 1.865 | opened
99 | SS 35/10 Prilepy | 1*1,6 | 0.53 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.62 | 1.62 | opened | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.539 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.611 | 1.611 | opened
100 | SS 35/10 Pristen | 1*4 | 2.3 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 1 | 1 | opened | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.03 | 2.33 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 0.97 | 0.97 | opened
101 | SS 35/10 R. Budy 35/10 | 1*4 | 0 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.74 | 0.74 | opened | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.012 | 0.012 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.728 | 0.728 | opened
102 | SS 35/10 Reut | 1*2,5 | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | opened | 102 | SS 35/10 Reut | 1 х 2,5 |  | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | opened
103 | SS 35/10 Rovenka | 1*1,6 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened | 103 | SS 35/10 Rovenka | 1 х 1,6 | 0.015 | 0.175 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.255 | 1.255 | opened
104 | SS 35/10 Rodina (NPC) | 1*2,5 | 0.17 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.53 | 0.53 | opened | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.033 | 0.203 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.497 | 0.497 | opened
105 | SS 35/10 Rodina (EPS) | 1*4 | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 |  | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened
106 | SS 35/10 Rubanshchina | 1*2,5 | 0.4 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.91 | 0.91 | opened | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.003 | 0.403 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.907 | 0.907 | opened
107 | SS 35/10 Rusanovo | 1*1,8 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.414 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.016 | 1.016 | opened
108 | SS 35/10 Ryshkovo | 1*2,5 | 0.56 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.38 | 0.38 | opened | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.038 | 0.598 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.342 | 0.342 | opened
109 | SS 35/10 Ryazanovo | 1*1,6 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened | 109 | SS 35/10 Ryazanovo | 1 х 1,6 |  | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened
110 | SS 35/10 Sazanovka | 1*2,5 | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened | 110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened
111 | SS 35/10 Sergievka | 1*2,5 | 0.4 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.3 | 2.3 | opened | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0.005 | 0.405 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.295 | 2.295 | opened
112 | SS 35/10 Sokolye | 1*2,5 | 0.3 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.13 | 1.13 | opened | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.051 | 0.351 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.079 | 1.079 | opened
113 | SS 35/10 Solntsevo | 1*2,5 | 0.9 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.86 | 0.86 | opened | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.075 | 0.975 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.785 | 0.785 | opened
114 | SS 35/10 Spasskoe | 1*1,6 | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened | 114 | SS 35/10 Spasskoe | 1 х 1,6 |  | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened
115 | SS 35/10 Sr. Olshanka | 1*2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.004 | 0.304 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.096 | 1.096 | opened
116 | SS 35/10 Streletskaya | 1*2,5 | 0.35 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.95 | 0.95 | opened | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.038 | 0.388 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.912 | 0.912 | opened
117 | SS 35/10 Subbotino | 1*2,5 | 0.6 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.74 | 0.74 | opened | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.005 | 0.605 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.735 | 0.735 | opened
118 | SS 35/10 Sukhaya | 1*1,6 | 0.44 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.27 | 0.27 | opened | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.002 | 0.442 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.268 | 0.268 | opened
119 | SS 35/10 Telmana | 1*2,5 | 0.3 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.85 | 0.85 | opened | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.009 | 0.309 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.841 | 0.841 | opened
120 | SS 35/10 Terebuzh | 1*2,5 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.007 | 0.467 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.963 | 0.963 | opened
121 | SS 35/10 Fateevka | 1*2,5 | 0.08 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.62 | 0.62 | opened | 121 | SS 35/10 Fateevka | 1 х 2,5 |  | 0.08 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.62 | 0.62 | opened
122 | SS 35/10 Fentisovo | 1*1,6 | 0.17 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.55 | 1.55 | opened | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.015 | 0.185 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.535 | 1.535 | opened
123 | SS 35/10 Chapaevskaya | 1*2,5 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.011 | 0.211 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.889 | 0.889 | opened
124 | SS 35/10 Chemerki | 1*1,6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
125 | SS 35/10 Chizhovka | 1*1,6 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.018 | 0.368 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.062 | 1.062 | opened
126 | SS 35/10 Shatilovka | 1*2,5 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.011 | 0.171 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.259 | 1.259 | opened
127 | SS 35/10 Sheptukhovka | 1*2,5 | 0.75 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.72 | 0.72 | opened | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.013 | 0.763 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.707 | 0.707 | opened
128 | SS 35/10 Shuklino | 1*2,5 | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened | 128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened
129 | SS 35/10 Elevator | 1*6,3 | 0.31 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.29 | 0.29 | opened | 129 | SS 35/10 Elevator | 1х6,3 |  | 0.31 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.29 | 0.29 | opened
130 | SS 35/10 Yankovo | 1*1,6 | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened | 130 | SS 35/10 Yankovo | 1 х 1,6 |  | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened
131 | SS 35/10 Yasenki | 1*2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened | 131 | SS 35/10 Yasenki | 1 х 2,5 | 0.038 | 0.518 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.632 | 1.632 | opened
Two- and more transformer substations | [11 empty] | Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened
2 | SS 110/10 ARZ | 6,3+10 | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | opened | 2 | SS 110/10 ARZ | 6,3+10,0 |  | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | opened
3 | SS 110/35/10 Atomgrad | 2*25 | 13.07 | 20.2 | 120 | -7.13 | 0 | 26.25 | 33.38 | 26.02 | opened | 3 | SS 110/35/10 Atomgrad | 2*25 | 0.157 | 13.227 | 20.2 | 120 | -6.973 | 0 | 26.25 | 33.223 | 25.961 | opened
| Nom. capacity MV, MVA | 25 | 3.24 | 10.6 | 120 | -7.36 | 0 | 26.25 | 33.61 |  |  |  | Nom. capacity MV, MVA | 25 | 0.098 | 3.338 | 10.6 | 120 | -7.262 | 0 | 26.25 | 33.512
| Nom. capacity lV, MVA | 25 | 9.83 | 9.6 | 120 | 0.23 | 0 | 26.25 | 26.02 |  |  |  | Nom. capacity lV, MVA | 25 | 0.059 | 9.889 | 9.6 | 120 | 0.289 | 0 | 26.25 | 25.961
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | opened | 4 | SS 110/10 B. Zhirovo | 2*6,3 |  | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | opened
5 | SS 110/35/10 Basovo | 5,6+10 | 1.19 | 6.19 | 15 | -5 | 0 | 5.88 | 10.88 | 5.38 | opened | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.012 | 1.202 | 6.19 | 15 | -4.988 | 0 | 5.88 | 10.868 | 5.379 | opened
| Nom. capacity MV, MVA | 5,6+10 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38 |  |  |  | Nom. capacity MV, MVA | 5,6+10,0 | 0.011 | 0.511 | 6 |  | -5.489 | 0 | 5.88 | 11.369
| Nom. capacity LV, MVA | 5,6+10 | 0.69 | 0.19 | 120 | 0.5 | 0 | 5.88 | 5.38 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.001 | 0.691 | 0.19 | 120 | 0.501 | 0 | 5.88 | 5.379
6 | SS 110/35/10 Belaya | 2*16 | 8.4 | 12 | 120 | -3.6 | 0 | 16.8 | 20.4 | 13.4 | opened | 6 | SS 110/35/10 Belaya | 2*16,0 | 1 | 9.4 | 12 | 120 | -2.6 | 0 | 16.8 | 19.4 | 12.68 | opened
| Nom. capacity MV, MVA | 16 | 3.4 | 0 |  | 3.4 | 0 | 16.8 | 13.4 |  |  |  | Nom. capacity MV, MVA | 16 | 0.72 | 4.12 | 0 |  | 4.12 | 0 | 16.8 | 12.68
| Nom. capacity LV, MVA | 16 | 5 | 12 | 120 | -7 | 0 | 16.8 | 23.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.28 | 5.28 | 12 | 120 | -6.72 | 0 | 16.8 | 23.52
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.2 | 1.3 | 120 | -0.1 | 0 | 6.62 | 6.72 | 6.02 | opened | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.036 | 1.236 | 1.3 | 120 | -0.064 | 0 | 6.62 | 6.684 | 6.016 | opened
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.62 | 6.02 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.004 | 0.604 |  |  | 0.604 | 0 | 6.62 | 6.016
| Nom. capacity LV, MVA | 6.3 | 0.6 | 1.3 | 120 | -0.7 | 0 | 6.62 | 7.32 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.032 | 0.632 | 1.3 | 120 | -0.668 | 0 | 6.62 | 7.288
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.31 | 1.17 | 45 | 1.14 | 0 | 2.63 | 1.49 | 1.49 | opened | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.044 | 2.354 | 1.17 | 45 | 1.184 | 0 | 2.63 | 1.446 | 1.446 | opened
9 | SS 110/35/6 Volokno | 40+2*40,5 | 37.58 | 16.8 | 0 | 20.78 | 0 | 84.53 | 63.75 | 61.28 | opened | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.525 | 39.105 | 16.8 | 0 | 22.305 | 0 | 84.53 | 62.225 | 61.202 | opened
| Nom. capacity MV, MVA | 40+2*40,5 | 14.33 | 16.8 | 0 | -2.47 | 0 | 84.53 | 87 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 1.447 | 15.777 | 16.8 | 0 | -1.023 | 0 | 84.53 | 85.553
| Nom. capacity MV, MVA | 40+2*40,5 | 23.25 | 0 | 0 | 23.25 | 0 | 84.53 | 61.28 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.078 | 23.328 | 0 | 0 | 23.328 | 0 | 84.53 | 61.202
10 | SS 110/10 Vysokaya* | 2*16 | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | closed* | 10 | SS 110/10 Vysokaya* | 2*16,0 |  | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | closed
11 | SS 110/35/10 Glushkovo | 2*10 | 8.7 | 8.04 | 120 | 0.66 | 0 | 10.5 | 9.84 | 8.44 | opened | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 0.581 | 9.281 | 8.04 | 120 | 1.241 | 0 | 10.5 | 9.259 | 8.4 | opened
| Nom. capacity MV, MVA | 10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 10.5 | 11.9 |  |  |  | Nom. capacity MV, MVA | 10 | 0.541 | 5.741 | 6.6 | 120 | -0.859 | 0 | 10.5 | 11.359
| Nom. capacity LV, MVA | 10 | 3.5 | 1.44 | 80 | 2.06 | 0 | 10.5 | 8.44 |  |  |  | Nom. capacity LV, MVA | 10 | 0.04 | 3.54 | 1.44 | 80 | 2.1 | 0 | 10.5 | 8.4
12 | SS 110/10 Gorodskaya | 2*25 | 10.4 | 0 | 0 | 10.4 | 0 | 26.25 | 15.85 | 15.85 | opened | 12 | SS 110/10 Gorodskaya | 2*25,0 | 4.53 | 14.93 | 0 | 0 | 14.93 | 0 | 26.25 | 11.32 | 11.32 | opened
13 | SS 110/35/10 Gorshechnoe | 10+16 | 9.41 | 6.52 | 120 | 2.89 | 0 | 10.5 | 7.61 | 7.61 | opened | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 0.653 | 10.063 | 6.52 | 120 | 3.543 | 0 | 10.5 | 6.957 | 6.957 | opened
| Nom. capacity MV, MVA | 10+16 | 6.13 | 6.06 |  | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 0.297 | 6.427 | 6.06 |  | 0.367 | 0 | 10.5 | 10.133
| Nom. capacity LV, MVA | 10+16 | 3.28 | 0.46 | 120 | 2.82 | 0 | 10.5 | 7.68 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.356 | 3.636 | 0.46 | 120 | 3.176 | 0 | 10.5 | 7.324
14 | SS 110/35/10 Dmitriev | 2*10 | 7.09 | 10.4 | 120 | -3.31 | 0 | 10.5 | 13.81 | 8.43 | opened | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 0.216 | 7.306 | 10.4 | 120 | -3.094 | 0 | 10.5 | 13.594 | 8.219 | opened
| Nom. capacity MV, MVA | 10 | 2.02 | 7.4 |  | -5.38 | 0 | 10.5 | 15.88 |  |  |  | Nom. capacity MV, MVA | 10 | 0.005 | 2.025 | 7.4 |  | -5.375 | 0 | 10.5 | 15.875
| Nom. capacity LV, MVA | 10 | 5.07 | 3 | 80 | 2.07 | 0 | 10.5 | 8.43 |  |  |  | Nom. capacity LV, MVA | 10 | 0.211 | 5.281 | 3 | 80 | 2.281 | 0 | 10.5 | 8.219
15 | SS 110/6 Dolgie Budy | 2*10 | 0.8 | 0.5 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.817 | 0.5 | 120 | 0.317 | 0 | 10.5 | 10.183 | 10.183 | opened
16 | SS 110/35/10 Zolotukhino | 2*25 | 6.76 | 23.57 | 80 | -16.81 | 0 | 26.25 | 43.06 | 25.59 | opened | 16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.277 | 7.037 | 23.57 | 80 | -16.533 | 0 | 26.25 | 42.783 | 25.371 | opened
| Nom. capacity MV, MVA | 25 | 2.8 | 18.8 |  | -16 | 0 | 26.25 | 42.25 |  |  |  | Nom. capacity MV, MVA | 25 | 0.058 | 2.858 | 18.8 |  | -15.942 | 0 | 26.25 | 42.192
| Nom. capacity LV, MVA | 25 | 3.96 | 3.3 | 120 | 0.66 | 0 | 26.25 | 25.59 |  |  |  | Nom. capacity LV, MVA | 25 | 0.219 | 4.179 | 3.3 | 120 | 0.879 | 0 | 26.25 | 25.371
17 | SS 110/35/10 Kamyshi | 2*6,3 | 8.59 | 5.45 | 20 | 3.14 | 0 | 6.62 | 3.48 | 3.07 | opened | 17 | SS 110/35/10 Kamyshi | 2*6,3 | 3.96 | 12.55 | 5.45 | 20 | 7.1 | 0 | 6.62 | -0.48 | -0.801 | closed
| Nom. capacity MV, MVA | 6.3 | 7 | 3.45 |  | 3.55 | 0 | 6.62 | 3.07 |  |  |  | Nom. capacity MV, MVA | 6.3 | 3.871 | 10.871 | 3.45 |  | 7.421 | 0 | 6.62 | -0.801
| Nom. capacity LV, MVA | 6.3 | 1.59 | 2 | 20 | -0.41 | 0 | 6.62 | 7.03 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.089 | 1.679 | 2 | 20 | -0.321 | 0 | 6.62 | 6.941
18 | SS 110/35/10 Kastornoe | 15+16 | 14.13 | 6.97 | 120 | 7.16 | 0 | 15.75 | 8.59 | 8.59 | opened | 18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.424 | 14.554 | 6.97 | 120 | 7.584 | 0 | 15.75 | 8.166 | 8.166 | opened
| Nom. capacity MV, MVA | 15+16 | 10.63 | 6.6 |  | 4.03 | 0 | 15.75 | 11.72 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.338 | 10.968 | 6.6 |  | 4.368 | 0 | 15.75 | 11.382
| Nom. capacity LV, MVA | 15+16 | 3.5 | 0.37 | 120 | 3.13 | 0 | 15.75 | 12.62 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.086 | 3.586 | 0.37 | 120 | 3.216 | 0 | 15.75 | 12.534
19 | SS 110/35/10 Kilikino | 2*16 | 2.53 | 6.9 | 120 | -4.37 | 0 | 16.8 | 21.17 | 18.51 | opened | 19 | SS 110/35/10 Kilikino | 2*16,0 | 0.052 | 2.582 | 6.9 | 120 | -4.318 | 0 | 16.8 | 21.118 | 18.51 | opened
| Nom. capacity MV, MVA | 16 | 2.34 | 5 |  | -2.66 | 0 | 16.8 | 19.46 |  |  |  | Nom. capacity MV, MVA | 16 | 0.052 | 2.392 | 5 |  | -2.608 | 0 | 16.8 | 19.408
| Nom. capacity LV, MVA | 16 | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | SS 110/35/6 Kirovskaya | 2*40 | 53.66 | 16.36 | 120 | 37.3 | 0 | 42 | 4.7 | 4.7 | opened | 20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.57 | 56.23 | 16.36 | 120 | 39.87 | 0 | 42 | 2.13 | 2.13 | opened
| Nom. capacity MV, MVA | 40 | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39 |  |  |  | Nom. capacity MV, MVA | 40 |  | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Nom. capacity LV, MVA | 40 | 26.99 | 3.3 | 120 | 23.69 | 0 | 42 | 18.31 |  |  |  | Nom. capacity LV, MVA | 40 | 2.57 | 29.56 | 3.3 | 120 | 26.26 | 0 | 42 | 15.74
21 | SS 110/35/10 Klyukva | 2*16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | opened | 21 | SS 110/35/10 Klyukva | 2*16,0 | 0.307 | 3.587 | 1.2 | 120 | 2.387 | 0 | 16.8 | 14.413 | 14.413 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16 |  | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.307 | 3.587 | 1.2 | 120 | 2.387 | 0 | 16.8 | 14.413
22 | SS 110/10 Kompressornaya | 2*40 | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened | 22 | SS 110/10 Kompressornaya | 2*40,0 |  | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened
23 | SS 110/35/10 Konyshevka | 10+16 | 9.06 | 8 | 120 | 1.06 | 0 | 10.5 | 9.44 | 9.44 | opened | 23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.032 | 10.092 | 8 | 120 | 2.092 | 0 | 10.5 | 8.408 | 8.408 | opened
| Nom. capacity MV, MVA | 10+16 | 6.94 | 5.9 |  | 1.04 | 0 | 10.5 | 9.46 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.077 | 7.017 | 5.9 |  | 1.117 | 0 | 10.5 | 9.383
| Nom. capacity LV, MVA | 10+16 | 2.12 | 2.1 |  | 0.02 | 0 | 10.5 | 10.48 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.955 | 3.075 | 2.1 |  | 0.975 | 0 | 10.5 | 9.525
24 | SS 110/10 Kotelnaya | 10+25 | 7.8 | 2.1 | 0 | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 24 | SS 110/10 Kotelnaya | 10,0+25,0 | 2.842 | 10.642 | 2.1 | 0 | 8.542 | 0 | 10.5 | 1.958 | 1.958 | opened
25 | SS 110/35/10 Kshen | 2*10 | 8.73 | 6.63 | 10 | 2.1 | 0 | 10.5 | 8.4 | 6.59 | opened | 25 | SS 110/35/10 Kshen | 2*10,0 | 1.816 | 10.546 | 6.63 | 10 | 3.916 | 0 | 10.5 | 6.584 | 5.177 | opened
| Nom. capacity MV, MVA | 10 | 4.25 | 6.06 |  | -1.81 | 0 | 10.5 | 12.31 |  |  |  | Nom. capacity MV, MVA | 10 | 0.403 | 4.653 | 6.06 |  | -1.407 | 0 | 10.5 | 11.907
| Nom. capacity LV, MVA | 10 | 4.48 | 0.57 | 120 | 3.91 | 0 | 10.5 | 6.59 |  |  |  | Nom. capacity LV, MVA | 10 | 1.413 | 5.893 | 0.57 | 120 | 5.323 | 0 | 10.5 | 5.177
26 | SS 110/6 Lesnaya | 2*40 | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | opened | 26 | SS 110/6 Lesnaya | 2*40,0 |  | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | opened
27 | SS 110/35/10 Lgov | 2*25 | 13.14 | 4 | 120 | 9.14 | 0 | 26.25 | 17.11 | 3.02 | opened | 27 | SS 110/35/10 Lgov | 2*25,0 | 0.294 | 13.434 | 4 | 120 | 9.434 | 0 | 26.25 | 16.816 | 2.726 | opened
| Nom. capacity MV, MVA | 25 | 1.66 |  |  | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. capacity MV, MVA | 25 | 0 | 1.66 |  |  | 1.66 | 0 | 10.5 | 8.84
| Nom. capacity LV, MVA | 25 | 11.48 | 4 | 120 | 7.48 | 0 | 10.5 | 3.02 |  |  |  | Nom. capacity LV, MVA | 25 | 0.294 | 11.774 | 4 | 120 | 7.774 | 0 | 10.5 | 2.726
28 | SS 110/35/10 Lukashevka | 2*16 | 8.27 | 10.6 | 120 | -2.33 | 0 | 16.8 | 19.13 | 17.03 | opened | 28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.057 | 8.327 | 10.6 | 120 | -2.273 | 0 | 16.8 | 19.073 | 16.973 | opened
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03 |  |  |  | Nom. capacity MV, MVA | 16 | 0.057 | 5.127 | 5.3 |  | -0.173 | 0 | 16.8 | 16.973
| Nom. capacity LV, MVA | 16 | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | SS 110/35/10 Lyubostan | 6,3+10 | 5.6 | 13.1 | 120 | -7.5 | 0 | 6.62 | 14.12 | 7.32 | opened | 29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.126 | 5.726 | 13.1 | 120 | -7.374 | 0 | 6.62 | 13.994 | 7.315 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5 | 11.8 |  | -6.8 | 0 | 6.62 | 13.42 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.121 | 5.121 | 11.8 |  | -6.679 | 0 | 6.62 | 13.299
| Nom. capacity LV, MVA | 6,3+10 | 0.6 | 1.3 |  | -0.7 | 0 | 6.62 | 7.32 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.005 | 0.605 | 1.3 |  | -0.695 | 0 | 6.62 | 7.315
30 | SS 110/35/6 Manturovo | 2*16 | 6.58 | 9.35 | 10 | -2.77 | 0 | 16.8 | 19.57 | 16.86 | opened | 30 | SS 110/35/6 Manturovo | 2*16,0 | 0.382 | 6.962 | 9.35 | 10 | -2.388 | 0 | 16.8 | 19.188 | 16.86 | opened
| Nom. capacity MV, MVA | 16 | 6.38 | 9.09 |  | -2.71 | 0 | 16.8 | 19.51 |  |  |  | Nom. capacity MV, MVA | 16 | 0.382 | 6.762 | 9.09 |  | -2.328 | 0 | 16.8 | 19.128
| Nom. capacity LV, MVA | 16 | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86
31 | SS 110/35/10 8th Marta | 6,3+10 | 7.07 | 9.6 | 120 | -2.53 | 0 | 6.62 | 9.15 | 7.41 | opened | 31 | SS 110/35/10 8th Marta | 6,3+10,0 | 0.492 | 7.562 | 9.6 | 120 | -2.038 | 0 | 6.62 | 8.658 | 6.924 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5.81 | 6.6 | 120 | -0.79 | 0 | 6.62 | 7.41 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.486 | 6.296 | 6.6 | 120 | -0.304 | 0 | 6.62 | 6.924
| Nom. capacity LV, MVA | 6,3+10 | 1.26 | 3 | 45 | -1.74 | 0 | 6.62 | 8.36 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.006 | 1.266 | 3 | 45 | -1.734 | 0 | 6.62 | 8.354
32 | SS 110/10 Martovskaya | 2*6,3 | 0.74 | 0.55 | 120 | 0.19 | 0 | 6.62 | 6.43 | 6.43 | opened | 32 | SS 110/10 Martovskaya | 2*6,3 | 0.288 | 1.028 | 0.55 | 120 | 0.478 | 0 | 6.62 | 6.142 | 6.142 | opened
33 | SS 110/35/10 Maryino | 10+25 | 6.15 | 8.11 | 120 | -1.96 | 0 | 10.5 | 12.46 | 11.27 | opened | 33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.087 | 6.237 | 8.11 | 120 | -1.873 | 0 | 10.5 | 12.373 | 11.26 | opened
| Nom. capacity MV, MVA | 10+25 | 3.71 | 4.9 |  | -1.19 | 0 | 10.5 | 11.69 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.077 | 3.787 | 4.9 |  | -1.113 | 0 | 10.5 | 11.613
| Nom. capacity LV, MVA | 10+25 | 2.44 | 3.21 |  | -0.77 | 0 | 10.5 | 11.27 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.01 | 2.45 | 3.21 |  | -0.76 | 0 | 10.5 | 11.26
34 | SS 110/35/10 Medvenka | 2*10 | 5.95 | 19.22 | 120 | -13.27 | 0 | 10.5 | 23.77 | 8.74 | opened | 34 | SS 110/35/10 Medvenka | 2*10,0 | 0.356 | 6.306 | 19.22 | 120 | -12.914 | 0 | 10.5 | 23.414 | 8.623 | opened
| Nom. capacity MV, MVA | 10 | 2.07 | 17.1 |  | -15.03 | 0 | 10.5 | 25.53 |  |  |  | Nom. capacity MV, MVA | 10 | 0.239 | 2.309 | 17.1 |  | -14.791 | 0 | 10.5 | 25.291
| Nom. capacity LV, MVA | 10 | 3.88 | 2.12 | 120 | 1.76 | 0 | 10.5 | 8.74 |  |  |  | Nom. capacity LV, MVA | 10 | 0.117 | 3.997 | 2.12 | 120 | 1.877 | 0 | 10.5 | 8.623
35 | SS 110/6 Neftyanaya | 2*10 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened | 35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened
36 | SS 110/35/10 Oboyan | 16 + 25 | 16.1 | 26.86 | 120 | -10.76 | 0 | 16.8 | 27.56 | 12.16 | opened | 36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 0.735 | 16.835 | 26.86 | 120 | -10.025 | 0 | 16.8 | 26.825 | 11.462 | opened
| Nom. capacity MV, MVA | 16 + 25 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.037 | 2.037 | 17.4 | 0 | -15.363 | 0 | 16.8 | 32.163
| Nom. capacity LV, MVA | 16 + 25 | 14.1 | 9.46 |  | 4.64 | 0 | 16.8 | 12.16 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.698 | 14.798 | 9.46 |  | 5.338 | 0 | 16.8 | 11.462
37 | SS 110/35/10 Oktyabrskaya | 2*16 | 8.62 | 15.5 | 120 | -6.88 | 0 | 16.8 | 23.68 | 14.72 | opened | 37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.204 | 8.824 | 15.5 | 120 | -6.676 | 0 | 16.8 | 23.476 | 14.599 | opened
| Nom. capacity MV, MVA | 16 | 5.54 | 14.5 |  | -8.96 | 0 | 16.8 | 25.76 |  |  |  | Nom. capacity MV, MVA | 16 | 0.083 | 5.623 | 14.5 |  | -8.877 | 0 | 16.8 | 25.677
| Nom. capacity LV, MVA | 16 | 3.08 | 1 | 120 | 2.08 | 0 | 16.8 | 14.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.121 | 3.201 | 1 | 120 | 2.201 | 0 | 16.8 | 14.599
38 | SS 110/35/10 Olkhovka | 2*6,3 | 1.92 | 6.31 | 120 | -4.39 | 0 | 6.62 | 11.01 | 7.71 | opened | 38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.052 | 1.972 | 6.31 | 120 | -4.338 | 0 | 6.62 | 10.958 | 7.691 | opened
| Nom. capacity MV, MVA | 6.3 | 1.7 | 5 | 120 | -3.3 | 0 | 6.62 | 9.92 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 1.733 | 5 | 120 | -3.267 | 0 | 6.62 | 9.887
| Nom. capacity LV, MVA | 6.3 | 0.22 | 1.31 | 120 | -1.09 | 0 | 6.62 | 7.71 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.019 | 0.239 | 1.31 | 120 | -1.071 | 0 | 6.62 | 7.691
39 | SS 110/10 Paniki | 2*2,5 | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | opened | 39 | SS 110/10 Paniki | 2 х 2,5 |  | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | opened
40 | SS 110/35/10 Peny | 2*16,0 | 9.63 | 6.9 | 120 | 2.73 | 0 | 16.8 | 14.07 | 14.07 | opened | 40 | SS 110/35/10 Peny | 2 х 16,0 | 0.124 | 9.754 | 6.9 | 120 | 2.854 | 0 | 16.8 | 13.946 | 13.946 | opened
| Nom. capacity MV, MVA | 16 | 4.37 | 3.5 |  | 0.87 | 0 | 16.8 | 15.93 |  |  |  | Nom. capacity MV, MVA | 16 | 0.104 | 4.474 | 3.5 |  | 0.974 | 0 | 16.8 | 15.826
| Nom. capacity LV, MVA | 16 | 5.26 | 3.4 | 120 | 1.86 | 0 | 16.8 | 14.94 |  |  |  | Nom. capacity LV, MVA | 16 | 0.02 | 5.28 | 3.4 | 120 | 1.88 | 0 | 16.8 | 14.92
41 | SS 110/35/10 Pribor | 2*25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened | 41 | SS 110/35/10 Pribor | 2 х 25,0 | 0 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 25 |  | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 |  |  |  | Nom. capacity LV, MVA | 25 |  | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | SS 110/10 Progress | 2*63 | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | opened | 42 | SS 110/10 Progress | 2 х 63,0 |  | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | opened
43 | SS 110/10 Poultry plant | 6,3+10 | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | opened | 43 | SS 110/10 Poultry plant | 6,3 + 10,0 |  | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | opened
44 | SS 110/35/10 R. Budy | 2*10,0 | 3.4 | 15.7 | 120 | -12.3 | 0 | 10.5 | 22.8 | 15.5 | opened | 44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.007 | 3.407 | 15.7 | 120 | -12.293 | 0 | 10.5 | 22.793 | 15.493 | opened
| Nom. capacity MV, MVA | 10 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.007 | 1.407 | 6.4 |  | -4.993 | 0 | 10.5 | 15.493
45 | SS 110/35/10 Razinkovo | 6,3+10 | 2.9 | 21.4 | 45 | -18.5 | 0 | 6.62 | 25.12 | 9.27 | opened | 45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 0.401 | 3.301 | 21.4 | 45 | -18.099 | 0 | 6.62 | 24.719 | 9.192 | opened
| Nom. capacity MV, MVA | 6,3+10 | 1.95 | 17.8 |  | -15.85 | 0 | 6.62 | 22.47 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 0.323 | 2.273 | 17.8 |  | -15.527 | 0 | 6.62 | 22.147
| Nom. capacity LV, MVA | 6,3+10 | 0.95 | 3.6 | 45 | -2.65 | 0 | 6.62 | 9.27 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.078 | 1.028 | 3.6 | 45 | -2.572 | 0 | 6.62 | 9.192
46 | SS 110/35/10 Rudnaya | 2*31,5 | 20.09 | 3.25 | 10 | 16.84 | 0 | 33.1 | 16.26 | 16.26 | opened | 46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.536 | 20.626 | 3.25 | 10 | 17.376 | 0 | 33.1 | 15.724 | 15.724 | opened
| Nom. capacity MV, MVA | 31.5 | 14.23 | 1.7 |  | 12.53 | 0 | 33.1 | 20.57 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.528 | 14.758 | 1.7 |  | 13.058 | 0 | 33.1 | 20.042
| Nom. capacity LV, MVA | 31.5 | 5.86 | 1.55 | 120 | 4.31 | 0 | 33.1 | 28.79 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.008 | 5.868 | 1.55 | 120 | 4.318 | 0 | 33.1 | 28.782
47 | SS 110/35/10 Rylsk | 16+25 | 18.95 | 11 | 120 | 7.95 | 0 | 16.8 | 8.85 | 8.85 | opened | 47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 0.704 | 19.654 | 11 | 120 | 8.654 | 0 | 16.8 | 8.146 | 8.146 | opened
| Nom. capacity MV, MVA | 16+25 | 12.9 | 7 |  | 5.9 | 0 | 16.8 | 10.9 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.646 | 13.546 | 7 |  | 6.546 | 0 | 16.8 | 10.254
| Nom. capacity LV, MVA | 16+25 | 6.05 | 4 | 120 | 2.05 | 0 | 16.8 | 14.75 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.058 | 6.108 | 4 | 120 | 2.108 | 0 | 16.8 | 14.692
48 | SS 110/10 Solovyinaya | 2*25 | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened | 48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened
49 | SS 110/10 STK | 2*10 | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | opened | 49 | SS 110/10 STK | 2 х 10,0 |  | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | opened
50 | SS 110/10 Studenok | 2*6,3 | 3.62 | 0.7 | 120 | 2.92 | 0 | 6.62 | 3.7 | 3.7 | opened | 50 | SS 110/10 Studenok | 2 х 6,3 | 0.053 | 3.673 | 0.7 | 120 | 2.973 | 0 | 6.62 | 3.647 | 3.647 | opened
51 | SS 110/35/10 Sudzha | 2*25 | 16.5 | 29 | 120 | -12.5 | 0 | 26.25 | 38.75 | 28.05 | opened | 51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.116 | 17.616 | 29 | 120 | -11.384 | 0 | 26.25 | 37.634 | 27.44 | opened
| Nom. capacity MV, MVA | 25 | 6.4 | 17.1 |  | -10.7 | 0 | 26.25 | 36.95 |  |  |  | Nom. capacity MV, MVA | 25 | 0.506 | 6.906 | 17.1 |  | -10.194 | 0 | 26.25 | 36.444
| Nom. capacity LV, MVA | 25 | 10.1 | 11.9 |  | -1.8 | 0 | 26.25 | 28.05 |  |  |  | Nom. capacity LV, MVA | 25 | 0.61 | 10.71 | 11.9 |  | -1.19 | 0 | 26.25 | 27.44
52 | SS 110/35/10 Schyotmash | 2*25 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | opened | 52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.439 | 20.039 | 0 | 0 | 20.039 | 0 | 26.25 | 6.211 | 6.211 | opened
| Nom. capacity MV, MVA | 25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 |  |  |  | Nom. capacity MV, MVA | 25 | 0.989 | 4.889 |  |  | 4.889 | 0 | 26.25 | 21.361
| Nom. capacity LV, MVA | 25 | 9.7 | 0 | 0 | 9.7 | 0 | 26.25 | 16.55 |  |  |  | Nom. capacity LV, MVA | 25 | 5.45 | 15.15 | 0 | 0 | 15.15 | 0 | 26.25 | 11.1
53 | SS 110/35/10 Tyotkino | 2*10 | 5.51 | 3.44 | 120 | 2.07 | 0 | 10.5 | 8.43 | 7.63 | opened | 53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.019 | 5.529 | 3.44 | 120 | 2.089 | 0 | 10.5 | 8.411 | 7.62 | opened
| Nom. capacity MV, MVA | 10 | 1.2 | 2 |  | -0.8 | 0 | 10.5 | 11.3 |  |  |  | Nom. capacity MV, MVA | 10 | 0.009 | 1.209 | 2 |  | -0.791 | 0 | 10.5 | 11.291
| Nom. capacity LV, MVA | 10 | 4.31 | 1.44 |  | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, MVA | 10 | 0.01 | 4.32 | 1.44 |  | 2.88 | 0 | 10.5 | 7.62
54 | SS 110/35/10 Tim | 6,3+16 | 5.7 | 9.59 | 120 | -3.89 | 0 | 6.62 | 10.51 | 5.02 | opened | 54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.394 | 6.094 | 9.59 | 120 | -3.496 | 0 | 6.62 | 10.116 | 4.939 | opened
| Nom. capacity MV, MVA | 6,3+16 | 3.6 | 9.09 |  | -5.49 | 0 | 6.62 | 12.11 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.313 | 3.913 | 9.09 |  | -5.177 | 0 | 6.62 | 11.797
| Nom. capacity LV, MVA | 6,3+16 | 2.1 | 0.5 | 120 | 1.6 | 0 | 6.62 | 5.02 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.081 | 2.181 | 0.5 | 120 | 1.681 | 0 | 6.62 | 4.939
55 | SS 110/35/10 Uyutnoe | 10+16 | 1.01 | 0.5 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.83 | opened | 55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.01 | 1.02 | 0.5 | 120 | 0.52 | 0 | 10.5 | 9.98 | 9.83 | opened
| Nom. capacity MV, MVA | 10+16 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83
| Nom. capacity LV, MVA | 10+16 | 0.34 | 0.5 | 120 | -0.16 | 0 | 10.5 | 10.66 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.01 | 0.35 | 0.5 | 120 | -0.15 | 0 | 10.5 | 10.65
56 | SS 110/35/10 Fatezh | 2*16 | 6.32 | 17.4 | 120 | -11.08 | 0 | 16.8 | 27.88 | 17.08 | opened | 56 | SS 110/35/10 Fatezh | 2 х 16,0 | 0.741 | 7.061 | 17.4 | 120 | -10.339 | 0 | 16.8 | 27.139 | 16.951 | opened
| Nom. capacity MV, MVA | 16 | 2 | 12.8 |  | -10.8 | 0 | 16.8 | 27.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.612 | 2.612 | 12.8 |  | -10.188 | 0 | 16.8 | 26.988
| Nom. capacity LV, MVA | 16 | 4.32 | 4.6 | 120 | -0.28 | 0 | 16.8 | 17.08 |  |  |  | Nom. capacity LV, MVA | 16 | 0.129 | 4.449 | 4.6 | 120 | -0.151 | 0 | 16.8 | 16.951
57 | SS 110/35/10 Fosforitnaya | 2*25 | 5.44 | 12.34 | 120 | -6.9 | 0 | 26.25 | 33.15 | 24.41 | opened | 57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.122 | 5.562 | 12.34 | 120 | -6.778 | 0 | 26.25 | 33.028 | 24.408 | opened
| Nom. capacity MV, MVA | 25 | 3.38 | 12.12 |  | -8.74 | 0 | 26.25 | 34.99 |  |  |  | Nom. capacity MV, MVA | 25 | 0.12 | 3.5 | 12.12 |  | -8.62 | 0 | 26.25 | 34.87
| Nom. capacity LV, MVA | 25 | 2.06 | 0.22 | 10 | 1.84 | 0 | 26.25 | 24.41 |  |  |  | Nom. capacity LV, MVA | 25 | 0.002 | 2.062 | 0.22 | 10 | 1.842 | 0 | 26.25 | 24.408
58 | SS 110/35/10 Khomutovka | 7,5+10 | 5.69 | 6.3 | 80 | -0.61 | 0 | 7.88 | 8.49 | 5.32 | opened | 58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.134 | 5.824 | 6.3 | 80 | -0.476 | 0 | 7.88 | 8.356 | 5.204 | opened
| Nom. capacity MV, MVA | 7,5+10 | 0.73 | 3.9 |  | -3.17 | 0 | 7.88 | 11.05 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.018 | 0.748 | 3.9 |  | -3.152 | 0 | 7.88 | 11.032
| Nom. capacity LV, MVA | 7,5+10 | 4.96 | 2.4 | 80 | 2.56 | 0 | 7.88 | 5.32 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.116 | 5.076 | 2.4 | 80 | 2.676 | 0 | 7.88 | 5.204
59 | SS 110/35/10 Cheremisinovo | 2*16 | 6.15 | 9.38 | 10 | -3.23 | 0 | 16.8 | 20.03 | 15.06 | opened | 59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.282 | 6.432 | 9.38 | 10 | -2.948 | 0 | 16.8 | 19.748 | 14.943 | opened
| Nom. capacity MV, MVA | 16 | 4.12 | 9.09 |  | -4.97 | 0 | 16.8 | 21.77 |  |  |  | Nom. capacity MV, MVA | 16 | 0.165 | 4.285 | 9.09 |  | -4.805 | 0 | 16.8 | 21.605
| Nom. capacity LV, MVA | 16 | 2.03 | 0.29 | 120 | 1.74 | 0 | 16.8 | 15.06 |  |  |  | Nom. capacity LV, MVA | 16 | 0.117 | 2.147 | 0.29 | 120 | 1.857 | 0 | 16.8 | 14.943
60 | SS 110/35/10 Cheremoshki | 2*6,3 | 3.34 | 8.25 | 120 | -4.91 | 0 | 6.62 | 11.53 | 7.09 | opened | 60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.064 | 3.404 | 8.25 | 120 | -4.846 | 0 | 6.62 | 11.466 | 7.085 | opened
| Nom. capacity MV, MVA | 6.3 | 2.56 | 7 |  | -4.44 | 0 | 6.62 | 11.06 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.059 | 2.619 | 7 |  | -4.381 | 0 | 6.62 | 11.001
| Nom. capacity LV, MVA | 6.3 | 0.78 | 1.25 | 129 | -0.47 | 0 | 6.62 | 7.09 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.005 | 0.785 | 1.25 | 129 | -0.465 | 0 | 6.62 | 7.085
61 | SS 110/35/10 Shumakovo | 2*10 | 4.4 | 13.73 | 120 | -9.33 | 0 | 10.5 | 19.83 | 12.03 | opened | 61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.268 | 4.668 | 13.73 | 120 | -9.062 | 0 | 10.5 | 19.562 | 11.967 | opened
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3 |  |  |  | Nom. capacity MV, MVA | 10 | 0.205 | 3.605 | 11.2 |  | -7.595 | 0 | 10.5 | 18.095
| Nom. capacity LV, MVA | 10 | 1 | 2.53 | 120 | -1.53 | 0 | 10.5 | 12.03 |  |  |  | Nom. capacity LV, MVA | 10 | 0.063 | 1.063 | 2.53 | 120 | -1.467 | 0 | 10.5 | 11.967
62 | SS 110/35/10 Shchigry | 2*25 | 11.28 | 12.9 | 120 | -1.62 | 0 | 26.5 | 28.12 | 21.55 | opened | 62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.51 | 11.79 | 12.9 | 120 | -1.11 | 0 | 26.5 | 27.61 | 21.366 | opened
| Nom. capacity MV, MVA | 25 | 5.55 | 12.12 |  | -6.57 | 0 | 26.5 | 33.07 |  |  |  | Nom. capacity MV, MVA | 25 | 0.326 | 5.876 | 12.12 |  | -6.244 | 0 | 26.5 | 32.744
| Nom. capacity LV, MVA | 25 | 5.73 | 0.78 | 120 | 4.95 | 0 | 26.5 | 21.55 |  |  |  | Nom. capacity LV, MVA | 25 | 0.184 | 5.914 | 0.78 | 120 | 5.134 | 0 | 26.5 | 21.366
63 | SS 110/35/10 Yastrebovka | 7,5+10 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.88 | 11.63 | 6.95 | opened | 63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.1977 | 2.7577 | 6.31 | 10 | -3.5523 | 0 | 7.88 | 11.4323 | 6.912 | opened
| Nom. capacity MV, MVA | 7,5+10 | 1.38 | 6.06 |  | -4.68 | 0 | 7.88 | 12.56 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.1597 | 1.5397 | 6.06 |  | -4.5203 | 0 | 7.88 | 12.4003
| Nom. capacity LV, MVA | 7,5+10 | 1.18 | 0.25 | 10 | 0.93 | 0 | 7.88 | 6.95 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.038 | 1.218 | 0.25 | 10 | 0.968 | 0 | 7.88 | 6.912
64 | SS 35/10 Amosovka | 2*2,5 | 0.31 | 0.2 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened | 64 | SS 35/10 Amosovka | 2 х 2,5 | 0.008 | 0.318 | 0.2 | 120 | 0.118 | 0 | 2.63 | 2.512 | 2.512 | opened
65 | SS 35/10 Afanasyevka (SPS) | 1,6+2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 |  | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
66 | SS 35/10 B.Soldatskoe 2 | 2*4 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 |  | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
67 | SS 35/10 B.Zmeinets | 2*1,6 | 0.23 | 1.43 | 120 | -1.2 | 0 | 1.68 | 2.88 | 2.88 | opened | 67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.01 | 0.24 | 1.43 | 120 | -1.19 | 0 | 1.68 | 2.87 | 2.87 | opened
68 | SS 35/10 Bezlesnaya | 2*4 | 1.19 | 6.1 | 0 | -4.91 | 0 | 4.2 | 9.11 | 9.11 | opened | 68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.246 | 1.436 | 6.1 | 0 | -4.664 | 0 | 4.2 | 8.864 | 8.864 | opened
69 | SS 35/10 Bereza | 1,0+2,5 | 0.49 | 0.15 | 120 | 0.34 | 0 | 1.05 | 0.71 | 0.71 | opened | 69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.016 | 0.506 | 0.15 | 120 | 0.356 | 0 | 1.05 | 0.694 | 0.694 | opened
70 | SS 35/10 Blagodat | 2,5+4 | 0.99 | 0.29 | 120 | 0.7 | 0 | 2.63 | 1.93 | 1.93 | opened | 70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.076 | 1.066 | 0.29 | 120 | 0.776 | 0 | 2.63 | 1.854 | 1.854 | opened
71 | SS 35/10 Bykanovo | 2*2,5 | 0.5 | 0.41 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened | 71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.029 | 0.529 | 0.41 | 120 | 0.119 | 0 | 2.63 | 2.511 | 2.511 | opened
72 | SS 35/10 V. Lyubazh | 4+10 | 1.17 | 0.4 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | opened | 72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.532 | 1.702 | 0.4 | 120 | 1.302 | 0 | 4.2 | 2.898 | 2.898 | opened
73 | SS 35/10 Vesyoloe | 2*1,6 | 0.8 | 0.22 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.453 | 1.253 | 0.22 | 120 | 1.033 | 0 | 1.68 | 0.647 | 0.647 | opened
74 | SS 35/10 Volobuevka | 2,5+4 | 0.57 | 0.46 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened | 74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.034 | 0.604 | 0.46 | 120 | 0.144 | 0 | 2.63 | 2.486 | 2.486 | opened
75 | SS 35/10 Voropaevo | 2*4 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened | 75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.021 | 0.891 | 0 | 0 | 0.891 | 0 | 4.2 | 3.309 | 3.309 | opened
76 | SS 35/10 Vostochnaya | 2*6,3 | 4.13 | 0.46 | 120 | 3.67 | 0 | 6.62 | 2.95 | 2.95 | opened | 76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.184 | 4.314 | 0.46 | 120 | 3.854 | 0 | 6.62 | 2.766 | 2.766 | opened
77 | SS 35/10 Vygornoe | 2*2,5 | 1.22 | 0.51 | 120 | 0.71 | 0 | 2.63 | 1.92 | 1.92 | opened | 77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.106 | 1.326 | 0.51 | 120 | 0.816 | 0 | 2.63 | 1.814 | 1.814 | opened
78 | SS 35/10 Gastomlya | 2*1,6 | 0.3 | 0.17 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.009 | 0.309 | 0.17 | 120 | 0.139 | 0 | 1.68 | 1.541 | 1.541 | opened
79 | SS 35/10 Gorodok | 2*4 | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened | 79 | SS 35/10 Gorodok | 2 х 4,0 |  | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened
80 | SS 35/10 Guevo | 2*2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.63 | 3.12 | 3.12 | opened | 80 | SS 35/10 Guevo | 2 х 2,5 | 0.04 | 1.24 | 1.69 | 20 | -0.45 | 0 | 2.63 | 3.08 | 3.08 | opened
81 | SS 35/10 Dolzhenkovo | 2*1,6 | 0.4 | 0.38 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened | 81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.442 | 0.38 | 120 | 0.062 | 0 | 1.68 | 1.618 | 1.618 | opened
82 | SS 35/6 Dukhovets | 2,5+4 | 3.33 | 3.5 | 0 | -0.17 | 0 | 2.63 | 2.8 | 2.8 | opened | 82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 3.445 | 3.5 | 0 | -0.055 | 0 | 2.63 | 2.685 | 2.685 | opened
83 | SS 35/10 Zhernovets | 2*2,5 | 0.4 | 0.26 | 120 | 0.14 | 0 | 2.63 | 2.49 | 2.49 | opened | 83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.405 | 0.26 | 120 | 0.145 | 0 | 2.63 | 2.485 | 2.485 | opened
84 | SS 35/6 Zapadnaya | 2*10 | 12.57 | 2.5 | 0 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | opened | 84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 12.58 | 2.5 | 0 | 10.08 | 0 | 10.5 | 0.42 | 0.42 | opened
85 | SS 35/10 Zolotukhinskaya KRS | 2*4 | 1.1 | 1.67 | 0 | -0.57 | 0 | 4.2 | 4.77 | 4.77 | opened | 85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.018 | 1.118 | 1.67 | 0 | -0.552 | 0 | 4.2 | 4.752 | 4.752 | opened
86 | SS 35/10 Zuevka | 1,6+2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened | 86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.085 | 0.985 | 0.93 | 45 | 0.055 | 0 | 1.68 | 1.625 | 1.625 | opened
87 | SS 35/10 Ivanino | 2*6,3 | 2.19 | 2.69 | 80 | -0.5 | 0 | 6.62 | 7.12 | 7.12 | opened | 87 | SS 35/10 Ivanino | 2 х 6,3 | 0.031 | 2.221 | 2.69 | 80 | -0.469 | 0 | 6.62 | 7.089 | 7.089 | opened
88 | SS 35/10 Kalinovka | 1,8+2,5 | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened | 88 | SS 35/10 Kalinovka | 1,8 + 2,5 |  | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened
89 | SS 35/10 Kirilovka | 2*1,6 | 0.29 | 0.52 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened | 89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.305 | 0.52 | 120 | -0.215 | 0 | 1.68 | 1.895 | 1.895 | opened
90 | SS 35/6 Kislinskaya | 2*10 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened | 90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 17.109 | 6.25 | 20 | 10.859 | 0 | 10.5 | -0.359 | -0.359 | closed
91 | SS 35/10 Fodder plant | 4+6,3 | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened | 91 | SS 35/10 Fodder plant | 4,0+6,3 |  | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
92 | SS 35/10 Mixed fodder plant | 2*6,3 | 3.31 | 0.21 | 120 | 3.1 | 0 | 6.62 | 3.52 | 3.52 | opened | 92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.083 | 3.393 | 0.21 | 120 | 3.183 | 0 | 6.62 | 3.437 | 3.437 | opened
93 | SS 35/10 Kommunalnaya | 3,2+4 | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened | 93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 |  | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened
94 | SS 35/10 Korenevo | 4+6,3 | 3.45 | 1.56 | 80 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened | 94 | SS 35/10 Korenevo | 4,0 + 6,3 | 0.403 | 3.853 | 1.56 | 80 | 2.293 | 0 | 4.2 | 1.907 | 1.907 | opened
95 | SS 35/10 Kremyanoe | 2,5+4 | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | opened | 95 | SS 35/10 Kremyanoe | 2,5 + 4,0 |  | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | opened
96 | SS 35/10 Krupets | 1,8+2,5 | 1.6 | 0.42 | 120 | 1.18 | 0 | 1.89 | 0.71 | 0.71 | opened | 96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.764 | 0.42 | 120 | 1.344 | 0 | 1.89 | 0.546 | 0.546 | opened
97 | SS 35/10 Kulbaki | 2*2,5 | 0.88 | 0.6 | 120 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened | 97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.003 | 0.883 | 0.6 | 120 | 0.283 | 0 | 2.63 | 2.347 | 2.347 | opened
98 | SS 35/10 Kultprosvet | 2*2,5 | 0.18 | 0.17 | 120 | 0.01 | 0 | 2.63 | 2.62 | 2.62 | opened | 98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.003 | 0.183 | 0.17 | 120 | 0.013 | 0 | 2.63 | 2.617 | 2.617 | opened
99 | SS 35/10 Kurchatov | 2*10 | 4.85 | 4.5 | 80 | 0.35 | 0 | 10.5 | 10.15 | 10.15 | opened | 99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 4.855 | 4.5 | 80 | 0.355 | 0 | 10.5 | 10.145 | 10.145 | opened
100 | SS 35/10 Kutok | 2*2,5 | 0.17 | 0.05 | 120 | 0.12 | 0 | 2.63 | 2.51 | 2.51 | opened | 100 | SS 35/10 Kutok | 2 х 2,5 | 0.005 | 0.175 | 0.05 | 120 | 0.125 | 0 | 2.63 | 2.505 | 2.505 | opened
101 | SS 35/10 Linets | 2*2,5 | 0.67 | 0.25 | 120 | 0.42 | 0 | 2.63 | 2.21 | 2.21 | opened | 101 | SS 35/10 Linets | 2 х 2,5 | 0.016 | 0.686 | 0.25 | 120 | 0.436 | 0 | 2.63 | 2.194 | 2.194 | opened
102 | SS 35/10 Luch | 2*6,3 | 2.83 | 0.23 | 120 | 2.6 | 0 | 6.62 | 4.02 | 4.02 | opened | 102 | SS 35/10 Luch | 2 х 6,3 | 0.303 | 3.133 | 0.23 | 120 | 2.903 | 0 | 6.62 | 3.717 | 3.717 | opened
103 | SS 35/10 Lyubimovka-2 | 2*4 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | opened | 103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.029 | 0.779 | 1.59 | 80 | -0.811 | 0 | 4.2 | 5.011 | 5.011 | opened
104 | SS 35/10 Matveevka | 2*2,5 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.63 | 2.04 | 2.04 | opened | 104 | SS 35/10 Matveevka | 2 х 2,5 | 0.02 | 0.69 | 0.08 | 120 | 0.61 | 0 | 2.63 | 2.02 | 2.02 | opened
105 | SS 35/10 Mayak | 2*2,5 | 0.41 | 0.3 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened | 105 | SS 35/10 Mayak | 2 х 2,5 | 0.006 | 0.416 | 0.3 | 120 | 0.116 | 0 | 2.63 | 2.514 | 2.514 | opened
106 | SS 35/10 Mikhailovka | 4+6,3 | 2.15 | 1.7 | 80 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened | 106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.14 | 2.29 | 1.7 | 80 | 0.59 | 0 | 4.2 | 3.61 | 3.61 | opened
107 | SS 35/10 Murynovka | 2*4 | 0.63 | 0.3 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | opened | 107 | SS 35/10 Murynovka | 2 х 4,0 | 0.178 | 0.808 | 0.3 | 120 | 0.508 | 0 | 4.2 | 3.692 | 3.692 | opened
108 | SS 35/10 N. Borki | 2*2,5 | 0.5 | 0.63 | 120 | -0.13 | 0 | 2.63 | 2.76 | 2.76 | opened | 108 | SS 35/10 N. Borki | 2 х 2,5 | 0.011 | 0.511 | 0.63 | 120 | -0.119 | 0 | 2.63 | 2.749 | 2.749 | opened
109 | SS 35/10 Nikolskaya | 1,6+1,8 | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened | 109 | SS 35/10 Nikolskaya | 1,6 + 1,8 |  | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
110 | SS 35/10 Novaya | 2*2,5 | 1.08 | 0.4 | 120 | 0.68 | 0 | 2.63 | 1.95 | 1.95 | opened | 110 | SS 35/10 Novaya | 2 х 2,5 | 0.246 | 1.326 | 0.4 | 120 | 0.926 | 0 | 2.63 | 1.704 | 1.704 | opened
111 | SS 35/10 Orekhovo | 2*2,5 | 0.73 | 0.19 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened | 111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.036 | 0.766 | 0.19 | 120 | 0.576 | 0 | 2.63 | 2.054 | 2.054 | opened
112 | SS 35/10 Orlovka | 2*2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.63 | 2.98 | 2.98 | opened | 112 | SS 35/10 Orlovka | 2 х 2,5 | 0.015 | 0.185 | 0.52 | 120 | -0.335 | 0 | 2.63 | 2.965 | 2.965 | opened
113 | SS 35/10 Osotskoe | 2*2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | opened | 113 | SS 35/10 Osotskoe | 2 х 2,5 |  | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | opened
114 | SS 35/10 Okhochevka | 4+6,3 | 1.27 | 0.74 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.172 | 1.442 | 0.74 | 120 | 0.702 | 0 | 4.2 | 3.498 | 3.498 | opened
115 | SS 35/10 Panino | 2*2,5 | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened | 115 | SS 35/10 Panino | 2 х 2,5 |  | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened
116 | SS 35/10 Pervoavgustovka | 2,5+3,2 | 0.74 | 0.52 | 120 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened | 116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.026 | 0.766 | 0.52 | 120 | 0.246 | 0 | 2.63 | 2.384 | 2.384 | opened
117 | SS 35/10 Petrinka | 2,5+4 | 1.1 | 0.3 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened | 117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.711 | 1.811 | 0.3 | 120 | 1.511 | 0 | 2.63 | 1.119 | 1.119 | opened
118 | SS 35/10 Platava | 2*2,5 | 1.07 | 0.26 | 120 | 0.81 | 0 | 2.63 | 1.82 | 1.82 | opened | 118 | SS 35/10 Platava | 2 х 2,5 | 0.012 | 1.082 | 0.26 | 120 | 0.822 | 0 | 2.63 | 1.808 | 1.808 | opened
119 | SS 35/10 Pogozhee | 2*1,6 | 0.23 | 0.46 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened | 119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.277 | 0.46 | 120 | -0.183 | 0 | 1.68 | 1.863 | 1.863 | opened
120 | SS 35/10 Porechnoe | 2*4 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | opened | 120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.005 | 0.505 | 1.16 | 120 | -0.655 | 0 | 4.2 | 4.855 | 4.855 | opened
121 | SS 35/10 Pochepnoe | 2*6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened | 121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened
122 | SS 35/10 Prigorodnoe | 2*2,5 | 0.52 | 0.3 | 80 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened | 122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.274 | 0.794 | 0.3 | 80 | 0.494 | 0 | 2.63 | 2.136 | 2.136 | opened
123 | SS 35/10 Pselets | 2*1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened | 123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened
124 | SS 35/10 Puzachi | 1,6+4 | 0.4 | 0.43 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened | 124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.014 | 0.414 | 0.43 | 120 | -0.016 | 0 | 1.68 | 1.696 | 1.696 | opened
125 | SS 35/10 Pushkarnoe | 2*2,5 | 0.8 | 0.32 | 120 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened | 125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.024 | 0.824 | 0.32 | 120 | 0.504 | 0 | 2.625 | 2.121 | 2.121 | opened
126 | SS 35/10 R.Kolodets | 2*2,5 | 0.6 | 0.44 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.337 | 0.937 | 0.44 | 120 | 0.497 | 0 | 2.625 | 2.128 | 2.128 | opened
127 | SS 35/10 Razvetye | 2*4 | 2.38 | 1.03 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 127 | SS 35/10 Razvetye | 2 х 4,0 | 0.388 | 2.768 | 1.03 | 120 | 1.738 | 0 | 4.2 | 2.462 | 2.462 | opened
128 | SS 35/10 V. Reutets | 2*4 | 0.28 | 0.11 | 120 | 0.17 | 0 | 4.2 | 4.03 | 4.03 | opened | 128 | SS 35/10 V. Reutets | 2 х 4,0 |  | 0.28 | 0.11 | 120 | 0.17 | 0 | 4.2 | 4.03 | 4.03 | opened
129 | SS 35/10 Rozhdestvenka | 2*1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.061 | 0.361 | 0.29 | 120 | 0.071 | 0 | 1.68 | 1.609 | 1.609 | opened
130 | SS 35/10 Rubilnik | 2*2,5 | 0.78 | 1.18 | 80 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | opened | 130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.045 | 0.825 | 1.18 | 80 | -0.355 | 0 | 2.625 | 2.98 | 2.98 | opened
131 | SS 35/10 Ryzhkovo | 2*1,6 | 0.23 | 0.08 | 20 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.007 | 0.237 | 0.08 | 20 | 0.157 | 0 | 1.68 | 1.523 | 1.523 | opened
132 | SS 35/10 Sapogovo | 2*2,5 | 1.57 | 0.6 | 20 | 0.97 | 0 | 2.63 | 1.66 | 1.66 | opened | 132 | SS 35/10 Sapogovo | 2 х 2,5 | 0.056 | 1.626 | 0.6 | 20 | 1.026 | 0 | 2.63 | 1.604 | 1.604 | opened
133 | SS 35/10 Svoboda-selskaya | 2*6,3 | 4.01 | 2.25 | 80 | 1.76 | 0 | 6.615 | 4.855 | 4.855 | opened | 133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.124 | 4.134 | 2.25 | 80 | 1.884 | 0 | 6.615 | 4.731 | 4.731 | opened
134 | SS 35/10 Selektsionnaya | 2*4 | 1.56 | 1.4 | 45 | 0.16 | 0 | 4.2 | 4.04 | 4.04 | opened | 134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.027 | 1.587 | 1.4 | 45 | 0.187 | 0 | 4.2 | 4.013 | 4.013 | opened
135 | SS 35/10 Semyonovka | 2*2,5 | 0.5 | 0 | - | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.042 | 0.542 | 0 | - | 0.542 | 0 | 2.625 | 2.083 | 2.083 | opened
136 | SS 35/10 Seed plant | 2*2,5 | 0.6 | 0.6 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened | 136 | SS 35/10 Seed plant | 2 х 2,5 | 0.04 | 0.64 | 0.6 | 120 | 0.04 | 0 | 2.63 | 2.59 | 2.59 | opened
137 | SS 35/10 Snagost | 2*4 | 1.26 | 0.05 | 10 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened | 137 | SS 35/10 Snagost | 2 х 4,0 | 0.03 | 1.29 | 0.05 | 10 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened
138 | SS 35/10 SOM | 1,6+4 | 1.56 | 0.08 | 10 | 1.48 | 0 | 1.68 | 0.2 | 0.2 | opened | 138 | SS 35/10 SOM | 1,6 + 4,0 | 0.056 | 1.616 | 0.08 | 10 | 1.536 | 0 | 1.68 | 0.144 | 0.144 | opened
139 | SS 35/10 Sosnovy Bor | 3,2+4 | 0.69 | 0.69 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.036 | 0.726 | 0.69 | 120 | 0.036 | 0 | 3.36 | 3.324 | 3.324 | opened
140 | SS 35/10 Stakanovo | 2*2,5 | 1.23 | 0.58 | 80 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened | 140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.027 | 1.257 | 0.58 | 80 | 0.677 | 0 | 2.625 | 1.948 | 1.948 | opened
141 | SS 35/10 Starkovo | 2*1,6 | 0.43 | 0.2 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | opened | 141 | SS 35/10 Starkovo | 2 х 1,6 |  | 0.43 | 0.2 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | opened
142 | CC 35/10 Starshee | 2*1,6 | 0.31 | 0.2 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened | 142 | CC 35/10 Starshee | 2 х 1,6 | 0.005 | 0.315 | 0.2 | 120 | 0.115 | 0 | 1.68 | 1.565 | 1.565 | opened
143 | SS 35/10 Teplitsy | 2*4 | 2.25 | 1.08 | 45 | 1.17 | 0 | 4.2 | 3.03 | 3.03 | opened | 143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.052 | 2.302 | 1.08 | 45 | 1.222 | 0 | 4.2 | 2.978 | 2.978 | opened
144 | SS 35/10 Turovka | 2*2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.63 | 2.43 | 2.43 | opened | 144 | SS 35/10 Turovka | 2 х 2,5 | 0.053 | 0.853 | 0.6 | 120 | 0.253 | 0 | 2.63 | 2.377 | 2.377 | opened
145 | SS 35/10 Uspenka | 2*2,5 | 1.19 | 1 | 80 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened | 145 | SS 35/10 Uspenka | 2 х 2,5 | 0.005 | 1.195 | 1 | 80 | 0.195 | 0 | 2.63 | 2.435 | 2.435 | opened
146 | SS 35/6 Tsentralnaya | 2*25 | 24.9 | 5 | 10 | 19.9 | 0 | 26.25 | 6.35 | 6.35 | opened | 146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0.005 | 24.905 | 5 | 10 | 19.905 | 0 | 26.25 | 6.345 | 6.345 | opened
147 | SS 35/10 Chermoshnoe | 2*2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened | 147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
148 | SS 35/10 Shatalovka | 2,5+4 | 0.31 | 0.21 | 80 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.031 | 0.341 | 0.21 | 80 | 0.131 | 0 | 2.625 | 2.494 | 2.494 | opened
149 | SS 35/10 Shipy | 2*2,5 | 0.2 | 0.3 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.212 | 0.3 | 120 | -0.088 | 0 | 2.625 | 2.713 | 2.713 | opened
150 | SS 35/10 Elevator | 4+6,3 | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | opened | 150 | SS 35/10 Elevator | 4,0 + 6,3 |  | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | opened
151 | SS 35/10 Yugo-Zapadnaya | 2*10 | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened | 151 | SS 35/10 Yugo-Zapadnaya | 1 х 10,0 |  | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened
152 | SS 35/10 Plant of reiтащксув-concrete products | 2*2,5 | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened | 152 | SS 35/10 Plant of reiтащксув-concrete products | 2 х 2,5 |  | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened
| TOTAL: | 3185.9 | 763.705 | 777.41 | [5 empty] | 1191.575 |  |  | TOTAL: | 3185.9 | 68.392 | 840.9814 | 784.31 | [5 empty] | 1155.925
| deficit | [8 empty] | -8.27 |  |  | deficit | [9 empty] | -14.986
| proficit | [8 empty] | 1183.31 |  |  | proficit | [9 empty] | 1140.939

## Липецк
table 1
No. | Object of main substation, voltage class | Current deficit | [9 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA |  | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
[5 empty] | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [12 empty] | 1: One-transformer substations
| SS 110/10kv Lev Tolstoy | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | closed |  | SS 110/10kv Lev Tolstoy | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | closed
| SS 110/10 kv Dvurechki | 6.3 |  | 2.03 | 0.1 | 70 | 1.93 | 0 | 0.1 | -1.93 | -1.93 | closed |  | SS 110/10 kv Dvurechki | 6.3 | 0.136 | 2.166 | 0.1 | 70 | 2.066 | 0 | 0.1 | -2.066 | -2.066 | closed
| SS 35/10 kv Vesyoloe | 2.5 |  | 0.070668 | 0.8 | 100 | -0.72933 | 0 | 0.8 | 0.72933 | 0.72933 | opened |  | SS 35/10 kv Vesyoloe | 2.5 | 0.015 | 0.085668 | 0.8 | 100 | -0.71433 | 0 | 0.8 | 0.71433 | 0.71433 | opened
| SS 35/10 kv Kr.Palna | 3.2 |  | 0.73 | 1.2 | 70 | -0.47 | 0 | 1.2 | 0.47 | 0.47 | opened |  | SS 35/10 kv Kr.Palna | 3.2 | 0.01 | 0.74 | 1.2 | 70 | -0.46 | 0 | 1.2 | 0.46 | 0.46 | opened
| SS 35/10 kv Kamenka | 2.5 |  | 0.93 | 1.5 | 60 | -0.57 | 0 | 1.5 | 0.57 | 0.57 | opened |  | SS 35/10 kv Kamenka | 2.5 |  | 0.93 | 1.5 | 60 | -0.57 | 0 | 1.5 | 0.57 | 0.57 | opened
| SS 35/10 kv Krasotynovka | 2.5 |  | 0.43 | 1.5 | 50 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened |  | SS 35/10 kv Krasotynovka | 2.5 |  | 0.43 | 1.5 | 50 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened
| SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed |  | SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed
| SS 35/10 kv Pankratovka | 2.5 |  | 0.63 | 1.2 | 90 | -0.57 | 0 | 1.2 | 0.57 | 0.57 | opened |  | SS 35/10 kv Pankratovka | 2.5 |  | 0.63 | 1.2 | 90 | -0.57 | 0 | 1.2 | 0.57 | 0.57 | opened
| SS 35/10 kv Preobrazhenye | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | closed |  | SS 35/10 kv Preobrazhenye | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | closed
| SS 35/10 kv Yakovlevo | 2.5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 0 | -0.9 | -0.9 | closed |  | SS 35/10 kv Yakovlevo | 2.5 | 0.01 | 0.91 | 0 | 0 | 0.91 | 0 | 0 | -0.91 | -0.91 | closed
| SS 110/10kv Terbunsky gonchar | 25 |  | without load | [8 empty] | 2: SS 110/10kv Terbunsky gonchar; 3: 25; 4: 15.135; 5: 15.135
| SS 35/10 kv Pervomayskaya | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | closed |  | SS 35/10 kv Pervomayskaya | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | closed
| SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.91 | 0.9 | 90 | 0.01 | 0 | 0.9 | -0.01 | -0.01 | closed |  | SS 35/10 kv Kamennaya Lubna | 2.5 | 0.015 | 0.925 | 0.9 | 90 | 0.025 | 0 | 0.9 | -0.025 | -0.025 | closed
| SS 35/10 kv Znamenka | 2.5 |  | 0.87 | 0.4 | 8 hours | 0.47 | 0 | 0.4 | -0.47 | -0.47 | closed |  | SS 35/10 kv Znamenka | 2.5 |  | 0.87 | 0.4 | 8 hours | 0.47 | 0 | 0.4 | -0.47 | -0.47 | closed
| SS 35/10 kv Pikovo | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | closed |  | SS 35/10 kv Pikovo | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | closed
| SS 35/10 kv Nikolskoe | 4 |  | 0.28 | 0.8 | 150 | -0.52 | 0 | 0.8 | 0.52 | 0.52 | opened |  | SS 35/10 kv Nikolskoe | 4 |  | 0.28 | 0.8 | 150 | -0.52 | 0 | 0.8 | 0.52 | 0.52 | opened
| SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed |  | SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed
| SS 35/6 kv Druzhba | 5.6 |  | Integrated distribution device of low voltage-6kv not ours | [7 empty] | opened | 2: SS 35/6 kv Druzhba; 3: 5.6; 5: 0
| SS 35/10 kv SOM | 1.6 |  | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | closed |  | SS 35/10 kv SOM | 1.6 |  | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | closed
| SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed |  | SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed
| SS 35/10 kv Sindyakino | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | opened |  | SS 35/10 kv Sindyakino | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | opened
| SS 35/10 kv Kurino | 2.5 |  | 0.5 | 0 | 0 | 0.5 | 0 | 0 | -0.5 | -0.5 | closed |  | SS 35/10 kv Kurino | 2.5 | 0.035 | 0.535 | 0 | 0 | 0.535 | 0 | 0 | -0.535 | -0.535 | closed
| SS 35/10 kv Novodubovoe | 2.5 |  | 0.88 | 0 | 0 | 0.88 | 0 | 0 | -0.88 | -0.88 | closed |  | SS 35/10 kv Novodubovoe | 2.5 | 0.022 | 0.902 | 0 | 0 | 0.902 | 0 | 0 | -0.902 | -0.902 | closed
| SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed |  | SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed
| SS 35/6 kv Karyer | 4 |  | without load | [8 empty] | 2: SS 35/6 kv Karyer; 3: 4; 5: 0
Two- and more transformer substations (for two voltage levels) | [12 empty] | 1: Two- and more transformer substations (for two voltage levels)
| SS 110/6 kv Agregatnaya | 16+16 | 32 | 15.14 | 0 | 0 | 15.14 | 0 | 16.8 | 1.66 | 1.66 | opened |  | SS 110/6 kv Agregatnaya | 16+16 | 0.404 | 15.544 | 0 | 0 | 15.544 | 0 | 16.8 | 1.256 | 1.256 | opened
| SS 110/6 kv Zapadnaya | 40+40 | 80 | 17.44 | 0 | 0 | 17.44 | 0 | 42 | 24.56 | 24.56 | opened |  | SS 110/6 kv Zapadnaya | 40+40 | 2.758 | 20.198 | 0 | 0 | 20.198 | 0 | 42 | 21.802 | 21.802 | opened
| SS 110/10 kv Kashary | 2,5+6,3 | 8.8 | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | opened |  | SS 110/10 kv Kashary | 2,5+6,3 |  | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | opened
| SS 110/6 kv Tabak | 16+16 | 32 | 9.48 | 3.2 | 20 | 6.28 | 0 | 16.8 | 10.52 | 10.52 | opened |  | SS 110/6 kv Tabak | 16+16 | 0.018 | 9.498 | 3.2 | 20 | 6.298 | 0 | 16.8 | 10.502 | 10.502 | opened
| SS 110/10 kv Lukoshkino | 10+2,5 | 12.5 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | opened |  | SS 110/10 kv Lukoshkino | 10+2,5 |  | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | opened
| SS 110/10kv Niva | 10+10 | 20 | 5.09 | 1 | 100 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened |  | SS 110/10kv Niva | 10+10 | 0.02 | 5.11 | 1 | 100 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | opened
| SS 110/10 kv Olkhovets | 2,5+2,5 | 5 | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened |  | SS 110/10 kv Olkhovets | 2,5+2,5 |  | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
| SS 110/10 kv Kuyman | 2,5+2,5 | 5 | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 |  |  | SS 110/10 kv Kuyman | 2,5+2,5 |  | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
| SS 110/10 kv Lutoshkino | 2,5+2,5 | 5 | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened |  | SS 110/10 kv Lutoshkino | 2,5+2,5 |  | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened
| SS 110/10 kv Krugloe | 2,5+2,5 | 5 | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened |  | SS 110/10 kv Krugloe | 2,5+2,5 |  | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
| SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 80 | 45.62 | 4.5 | 30 | 41.12 | 0 | 42 | 0.88 | 0.88 | * |  | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 11 | 56.62 | 4.5 | 30 | 52.12 | 0 | 42 | -10.12 | -10.12 | closed
| SS 110/6 kv Privokzalnaya | 20+20+25 | 65 | 49.71 | 1.38 | 30 | 48.33 | 0 | 42 | -6.33 | -6.33 | closed |  | SS 110/6 kv Privokzalnaya | 20+20+25 | 5.634 | 55.344 | 1.38 | 30 | 53.964 | 0 | 42 | -11.964 | -11.964 | closed
| SS 110/10/6 kv Yuzhnaya | 40+40 | 80 | 43.07 | 6 | 30 | 37.07 | 0 | 42 | 4.93 | 4.93 | * |  | SS 110/10/6 kv Yuzhnaya | 40+40 | 4.778 | 47.848 | 6 | 30 | 41.848 | 0 | 42 | 0.152 | 0.152 | *
| SS 110/6 kv Sitovka | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | * |  | SS 110/6 kv Sitovka | 10+10 |  | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
| SS 110/6 kv LTP | 6,3+10 | 16.3 | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | * |  | SS 110/6 kv LTP | 6,3+10 |  | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | *
| SS 110/6 kv KPD | 10+10 | 20 | 2.31 | 0 | 0 | 2.31 | 0 | 10.5 | 8.19 | 8.19 | * |  | SS 110/6 kv KPD | 10+10 | 1.78 | 4.09 | 0 | 0 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | *
| SS 110/10 kv Oktyabskaya | 40+40 | 80 | 19.12 | 4 | 30 | 15.12 | 0 | 42 | 26.88 | 26.88 | * |  | SS 110/10 kv Oktyabskaya | 40+40 | 12.092 | 31.212 | 4 | 30 | 27.212 | 0 | 42 | 14.788 | 14.788 | *
| SS 110/10 kv Universitetskaya | 40+40 |  | 0 | 0 | 0 | 0 | 0 | 42 | 42 | 42 | opened |  | SS 110/10 kv Universitetskaya | 40+40 | 42.205 | 42.205 | 0 | 0 | 42.205 | 0 | 42 | -0.205 | -0.205 | closed
| SS 110/6 kv Teplichnaya | 15+15 | 30 | 7.58 | 0 | 0 | 7.58 | 0 | 15.75 | 8.17 | 8.17 | * |  | SS 110/6 kv Teplichnaya | 15+15 | 0.209 | 7.789 | 0 | 0 | 7.789 | 0 | 15.75 | 7.961 | 7.961 | *
| SS 110/6 kv GPP-2 LTZ | 63+63 | 126 | 12.14 | 0 | 0 | 12.14 | 0 | 66.15 | 54.01 | 54.01 | * |  | SS 110/6 kv GPP-2 LTZ | 63+63 | 2.32 | 14.46 | 0 | 0 | 14.46 | 0 | 66.15 | 51.69 | 51.69 | *
| SS 35/10 kv Avangard | 4+4 | 8 | 1.1 | 1.2 | 110 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened |  | SS 35/10 kv Avangard | 4+4 | 0.008 | 1.108 | 1.2 | 110 | -0.092 | 0 | 4.2 | 4.292 | 4.292 | opened
| SS 35/10 kv Afanasysevo | 2,5+2,5 | 5 | 1.81 | 0 | 0 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | opened |  | SS 35/10 kv Afanasysevo | 2,5+2,5 | 0.038 | 1.848 | 0 | 0 | 1.848 | 0 | 2.625 | 0.777 | 0.777 | opened
| SS 35/10 kv Babarykino | 2,5+2,5 | 5 | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | opened |  | SS 35/10 kv Babarykino | 2,5+2,5 |  | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | opened
| SS 35/10 kv Avrora | 2,5+2,5 | 5 | 0.88 | 1.2 | 110 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened |  | SS 35/10 kv Avrora | 2,5+2,5 | 0.282 | 1.162 | 1.2 | 110 | -0.038 | 0 | 2.625 | 2.663 | 2.663 | opened
| SS 35/10 kv B.Boyovka | 2,5+2,5 | 5 | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened |  | SS 35/10 kv B.Boyovka | 2,5+2,5 |  | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened
| SS 35/10 kv Borki | 2,5+2,5 | 5 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | opened |  | SS 35/10 kv Borki | 2,5+2,5 |  | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | opened
| SS 35/6kv Vostochnaya | 10+16 | 26 | 8.72 | 4.8 | 20 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | opened |  | SS 35/6kv Vostochnaya | 10+16 | 2 | 10.72 | 4.8 | 20 | 5.92 | 0 | 10.5 | 4.58 | 4.58 | opened
| SS 35/10 kv Vasilyevka | 2,5+2,5 | 5 | 0.52 | 1.5 | 90 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | opened |  | SS 35/10 kv Vasilyevka | 2,5+2,5 |  | 0.52 | 1.5 | 90 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | opened
| SS 35/10 kv Voronets | 4+4 | 8 | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened |  | SS 35/10 kv Voronets | 4+4 |  | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened
| SS 35/6 kv Golikovo | 1,8+1,6 | 3.4 | 0.11 | 0 | 0 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened |  | SS 35/6 kv Golikovo | 1,8+1,6 |  | 0.11 | 0 | 0 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
| SS 35/10 kv Gatishche | 2,5+2,5 | 5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened |  | SS 35/10 kv Gatishche | 2,5+2,5 |  | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
| SS 35/10 kv Gnilusha | 6,3+6,3 | 12.6 | 1.36 | 1.2 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | opened |  | SS 35/10 kv Gnilusha | 6,3+6,3 | 0.601 | 1.961 | 1.2 | 120 | 0.761 | 0 | 6.615 | 5.854 | 5.854 | opened
| SS 35/10kv Gryzlovo | 2,5+2,5 | 5 | 0.54 | 0.8 | 110 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | opened |  | SS 35/10kv Gryzlovo | 2,5+2,5 |  | 0.54 | 0.8 | 110 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | opened
| SS 35/10 kv Zhernovnoe | 2,5+2,5 | 5 | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | opened |  | SS 35/10 kv Zhernovnoe | 2,5+2,5 |  | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | opened
| SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 4.8 | 2.35 | 0 | 0 | 2.35 | 0 | 1.68 | -0.67 | -0.67 | closed |  | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.008 | 2.358 | 0 | 0 | 2.358 | 0 | 1.68 | -0.678 | -0.678 | closed
| SS 35/10 kv Zakharovka | 2,5+2,5 | 5 | 0.42 | 0.8 | 60 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | opened |  | SS 35/10 kv Zakharovka | 2,5+2,5 |  | 0.42 | 0.8 | 60 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | opened
| SS 35/10 kv Kazaki | 4+4 | 8 | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | opened |  | SS 35/10 kv Kazaki | 4+4 |  | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | opened
| SS 35/10 kv Kolesovo | 6,3+6,3 | 12.6 | 1.38 | 1.5 | 90 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | opened |  | SS 35/10 kv Kolesovo | 6,3+6,3 | 0.322 | 1.702 | 1.5 | 90 | 0.202 | 0 | 6.615 | 6.413 | 6.413 | opened
| SS 35/10 kv Knyazevo | 2,5+2,5 | 5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened |  | SS 35/10 kv Knyazevo | 2,5+2,5 |  | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
| SS 35/10 kv Kirillovo | 2,5+2,5 | 5 | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | opened |  | SS 35/10 kv Kirillovo | 2,5+2,5 |  | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | opened
| SS 35/10 kv Ksizovo | 2,5+2,5 | 5 | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened |  | SS 35/10 kv Ksizovo | 2,5+2,5 |  | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
| SS 35/10 kv Lamskoe | 2,5+2,5 | 5 | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened |  | SS 35/10 kv Lamskoe | 2,5+2,5 |  | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened
| SS 35/10 kv Kazachye | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened |  | SS 35/10 kv Kazachye | 2,5+2,5 | 0.388 | 0.678 | 0 | 0 | 0.678 | 0 | 2.625 | 1.947 | 1.947 | opened
| SS 35/10 kv Lebyazhye | 2,5+1,6 | 4.1 | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened |  | SS 35/10 kv Lebyazhye | 2,5+1,6 |  | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened
| SS 35/10 kv Lomovets | 1,6+2,5 | 4.1 | 0.24 | 0 | 0 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened |  | SS 35/10 kv Lomovets | 1,6+2,5 |  | 0.24 | 0 | 0 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
| SS 35/10 kv Olshanets | 2,5+4 | 6.5 | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened |  | SS 35/10 kv Olshanets | 2,5+4 |  | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened
| SS 35/10 kv Ploskoe | 4+4 | 8 | 3.76 | 3 | 70 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened |  | SS 35/10 kv Ploskoe | 4+4 | 0.026 | 3.786 | 3 | 70 | 0.786 | 0 | 4.2 | 3.414 | 3.414 | opened
| SS 35/10 kv Stegalovka | 2,5+3,2 | 5.7 | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | opened |  | SS 35/10 kv Stegalovka | 2,5+3,2 |  | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | opened
| SS 35/10 kv Solidarnost | 4+4 | 8 | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened |  | SS 35/10 kv Solidarnost | 4+4 |  | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
| SS 35/10 kv Timiryazevo | 4+4 | 8 | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened |  | SS 35/10 kv Timiryazevo | 4+4 |  | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
| SS 35/10 kv Talitsa | 2,5+2,5 | 5 | 1.55 | 1.5 | 110 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened |  | SS 35/10 kv Talitsa | 2,5+2,5 | 0.007 | 1.557 | 1.5 | 110 | 0.057 | 0 | 2.625 | 2.568 | 2.568 | opened
| SS 35/10 kv the II Terbuny | 2,5+2,5 | 5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened |  | SS 35/10 kv the II Terbuny | 2,5+2,5 | 1.07 | 1.86 | 0 | 0 | 1.86 | 0 | 2.625 | 0.765 | 0.765 | opened
| SS 35/10 kv Tikhii Don | 4+4 | 8 | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | opened |  | SS 35/10 kv Tikhii Don | 4+4 |  | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | opened
| SS 35/10 kv Khitrovo | 6,3+6,3 | 12.6 | 0.36 | 0 | 0 | 0.36 | 0 | 6.615 | 6.255 | 6.255 | opened |  | SS 35/10 kv Khitrovo | 6,3+6,3 |  | 0.36 | 0 | 0 | 0.36 | 0 | 6.62 | 6.26 | 6.26 | opened
| SS 35/10 kv Chernava | 2,5+2,5 | 5 | 2.02 | 0 | 0 | 2.02 | 0 | 2.625 | 0.605 | 0.605 | opened |  | SS 35/10 kv Chernava | 2,5+2,5 | 0.015 | 2.035 | 0 | 0 | 2.035 | 0 | 2.625 | 0.59 | 0.59 | opened
| SS 35/10 kv Chernoles | 2,5+2,5 | 5 | 0.18 | 0 | 0 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened |  | SS 35/10 kv Chernoles | 2,5+2,5 | 0.007 | 0.187 | 0 | 0 | 0.187 | 0 | 2.625 | 2.438 | 2.438 | opened
| SS 35/6 kv SS No. 5 | 6,3+3,2 | 9.5 | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | opened |  | SS 35/6 kv SS No. 5 | 6,3+3,2 |  | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | opened
| SS 35/10 kv Krasnoe | 4+4 | 8 | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | opened |  | SS 35/10 kv Krasnoe | 4+4 |  | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | opened
| SS 35/10 kv Tyoploe | 2,5+2,5 | 5 | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened |  | SS 35/10 kv Tyoploe | 2,5+2,5 |  | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened
| SS 35/10 kv Dankov-selskaya | 6,3+4 | 10.3 | 5.61 | 2 | 120 | 3.61 | 0 | 4.2 | 0.59 | 0.59 | opened |  | SS 35/10 kv Dankov-selskaya | 6,3+4 | 0.61 | 6.22 | 2 | 120 | 4.22 | 0 | 4.2 | -0.02 | -0.02 | closed
| SS 35/10 kv Kolybelskaya | 2,5+2,5 | 5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | opened |  | SS 35/10 kv Kolybelskaya | 2,5+2,5 |  | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | opened
| SS 35/10 kv Topki | 2,5+2,5 | 5 | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened |  | SS 35/10 kv Topki | 2,5+2,5 |  | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
| SS 35/10 kv Agronom | 4+6,3 | 10.3 | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened |  | SS 35/10 kv Agronom | 4+6,3 |  | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened
| SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 5 | 2.14 | 0.5 | 60 | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened |  | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 0.021 | 2.161 | 0.5 | 60 | 1.661 | 0 | 2.625 | 0.964 | 0.964 | opened
| SS 35/10 kv Gagarino | 1,8+1,8 | 3.6 | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened |  | SS 35/10 kv Gagarino | 1,8+1,8 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened
| SS 35/10 kv Ranenburg | 1,6+1,6 | 3.2 | 1.95 | 0.5 | 60 | 1.45 | 0 | 1.68 | 0.23 | 0.23 | opened |  | SS 35/10 kv Ranenburg | 1,6+1,6 | 0.177 | 2.127 | 0.5 | 60 | 1.627 | 0 | 1.68 | 0.053 | 0.053 | opened
| SS 35/10 kv Sergievka | 2,5+2,5 | 5 | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened |  | SS 35/10 kv Sergievka | 2,5+2,5 |  | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
| SS 35/10 kv Drezgalovo | 1,6+1,6 | 3.2 | 0.37 | 0.5 | 60 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened |  | SS 35/10 kv Drezgalovo | 1,6+1,6 | 0.015 | 0.385 | 0.5 | 60 | -0.115 | 0 | 1.68 | 1.795 | 1.795 | opened
| SS 35/10 kv Dolgoe | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened |  | SS 35/10 kv Dolgoe | 2,5+2,5 |  | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
| SS 35/10 kv Voskresenovka | 1,6+1,6 | 3.2 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened |  | SS 35/10 kv Voskresenovka | 1,6+1,6 |  | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened
| SS 35/10 kv Saprykino | 1,6+2,5 | 4.1 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened |  | SS 35/10 kv Saprykino | 1,6+2,5 | 0.011 | 0.591 | 0 | 0 | 0.591 | 0 | 1.68 | 1.089 | 1.089 | opened
| SS 35/10 kv Nopolyanye | 2,5+2,5 | 5 | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened |  | SS 35/10 kv Nopolyanye | 2,5+2,5 |  | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
| SS 35/10 kv Vednoe | 2,5+2,5 | 5 | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened |  | SS 35/10 kv Vednoe | 2,5+2,5 |  | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened
| SS 35/10 kv Bigildino | 2,5+2,5 | 5 | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened |  | SS 35/10 kv Bigildino | 2,5+2,5 |  | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
| SS 35/10 kv Kultura | 2,5+2,5 | 5 | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened |  | SS 35/10 kv Kultura | 2,5+2,5 |  | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
| SS 35/10 kv Baryatino | 2,5+2,5 | 5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened |  | SS 35/10 kv Baryatino | 2,5+2,5 |  | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
| SS 35/10 kv B.Popovo | 2,5+2,5 | 5 | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened |  | SS 35/10 kv B.Popovo | 2,5+2,5 |  | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened
| SS 35/10 kv B. Izbishchi | 2,5+2,5 | 5 | 1.8 | 0.5 | 60 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened |  | SS 35/10 kv B. Izbishchi | 2,5+2,5 | 0.75 | 2.55 | 0.5 | 60 | 2.05 | 0 | 2.625 | 0.575 | 0.575 | opened
| SS 35/10 kv Polibino | 2,5+2,5 | 5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened |  | SS 35/10 kv Polibino | 2,5+2,5 |  | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
| SS 35/10 kv Dubrava | 2,5+2,5 | 5 | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened |  | SS 35/10 kv Dubrava | 2,5+2,5 |  | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened
| SS 35/10 kv Khrushchevo | 2,5+2,5 | 5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened |  | SS 35/10 kv Khrushchevo | 2,5+2,5 |  | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened
| SS 35/10 kv B. Verkh | 2,5+2,5 | 5 | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened |  | SS 35/10 kv B. Verkh | 2,5+2,5 |  | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
| SS 35/10 kv Golovinshchino | 2,5+2,5 | 5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened |  | SS 35/10 kv Golovinshchino | 2,5+2,5 |  | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened
| SS 35/10 kv Yablonevoe | 2,5+2,5 | 5 | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened |  | SS 35/10 kv Yablonevoe | 2,5+2,5 |  | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
| SS 35/10 kv Politovo | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened |  | SS 35/10 kv Politovo | 2,5+2,5 |  | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened
| SS 35/10 kv Complex | 4+4 | 8 | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | opened |  | SS 35/10 kv Complex | 4+4 |  | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | opened
| SS 35/10 kv No.1 | 4+4 | 8 | 3.38 | 0 | 0 | 3.38 | 0 | 4.2 | 0.82 | 0.82 | opened |  | SS 35/10 kv No.1 | 4+4 | 0.176 | 3.556 | 0 | 0 | 3.556 | 0 | 4.2 | 0.644 | 0.644 | opened
| SS 35/6 kv No. 2 | 1+1+1 | 3 | 3.49 | 0 | 0 | 3.49 | 0 | 1.05 | -2.44 | -2.44 | closed |  | SS 35/6 kv No. 2 | 1+1+1 | 0.234 | 3.724 | 0 | 0 | 3.724 | 0 | 1.05 | -2.674 | -2.674 | closed
| SS 35/10 kv No. 3 | 2,5+2,5 | 5 | 1.26 | 0.46 | 90 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | * |  | SS 35/10 kv No. 3 | 2,5+2,5 | 1.665 | 2.925 | 0.46 | 90 | 2.465 | 0 | 2.625 | 0.16 | 0.16 | *
| SS 35/6 kv No. 4 | 4+4 | 8 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | * |  | SS 35/6 kv No. 4 | 4+4 | 0.032 | 2.662 | 0 | 0 | 2.662 | 0 | 4.2 | 1.538 | 1.538 | *
| SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 11.9 | 4.5 | 0 | 0 | 4.5 | 0 | 5.88 | 1.38 | 1.38 | opened |  | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 0.456 | 4.956 | 0 | 0 | 4.956 | 0 | 5.88 | 0.924 | 0.924 | opened
| SS 35/10 kv Butyrki | 5,6+4 | 9.6 | 7.13 | 1.6 | 100 | 5.53 | 0 | 4.2 | -1.33 | -1.33 | closed |  | SS 35/10 kv Butyrki | 5,6+4 | 0.454 | 7.584 | 1.6 | 100 | 5.984 | 0 | 4.2 | -1.784 | -1.784 | closed
| SS 35/10 kv Yarlukovo | 3,2+4 | 7.2 | 3.4 | 1.5 | 80 | 1.9 | 0 | 3.36 | 1.46 | 1.46 | opened |  | SS 35/10 kv Yarlukovo | 3,2+4 | 0.212 | 3.612 | 1.5 | 80 | 2.112 | 0 | 3.36 | 1.248 | 1.248 | opened
| SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 3.2 | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened |  | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 |  | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened
| SS 35/10 kv Pravda | 4+2,5 | 6.5 | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | opened |  | SS 35/10 kv Pravda | 4+2,5 |  | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | opened
| SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 | 5 | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened |  | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 |  | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
| SS 35/10 kv Matyra | 4+3,2 | 7.2 | 4.68 | 0 | 0 | 4.68 | 0 | 3.36 | -1.32 | -1.32 | closed |  | SS 35/10 kv Matyra | 4+3,2 | 0.208 | 4.888 | 0 | 0 | 4.888 | 0 | 3.36 | -1.528 | -1.528 | closed
| SS 35/10 kv Vperyod | 4+4 | 8 | 0.88 | 0.32 | 80 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | opened |  | SS 35/10 kv Vperyod | 4+4 | 0.045 | 0.925 | 0.32 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | opened
| SS 35/10 kv Maley | 4+2,5 | 6.5 | 0.48 | 0.12 | 70 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened |  | SS 35/10 kv Maley | 4+2,5 | 0.016 | 0.496 | 0.12 | 70 | 0.376 | 0 | 2.625 | 2.249 | 2.249 | opened
| SS 35/10 kv SKhТ | 2,5+1,6 | 4.1 | 0.96 | 0.8 | 90 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened |  | SS 35/10 kv SKhТ | 2,5+1,6 | 0.695 | 1.655 | 0.8 | 90 | 0.855 | 0 | 1.68 | 0.825 | 0.825 | opened
| SS 35/10 kv Soshki | 4+4 | 8 | 0.8 | 0.2 | 80 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened |  | SS 35/10 kv Soshki | 4+4 | 0.005 | 0.805 | 0.2 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | opened
| SS 35/6 kv Tavolzhanka | 4+4 | 8 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened |  | SS 35/6 kv Tavolzhanka | 4+4 | 0.794 | 4.464 | 0 | 0 | 4.464 | 0 | 4.2 | -0.264 | -0.264 | closed
| SS 35/10 kv Trubetchino | 2,5+2,5 | 5 | 1.71 | 0 | 0 | 1.71 | 0 | 2.625 | 0.915 | 0.915 | * |  | SS 35/10 kv Trubetchino | 2,5+2,5 | 0.395 | 2.105 | 0 | 0 | 2.105 | 0 | 2.625 | 0.52 | 0.52 | opened
| SS 35/10 kv Ratchino | 2,5+2,5 | 5 | 1.11 | 0.12 | 70 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | * |  | SS 35/10 kv Ratchino | 2,5+2,5 | 0.125 | 1.235 | 0.12 | 70 | 1.115 | 0 | 2.625 | 1.51 | 1.51 | *
| SS 35/10 kv Kalikino | 3,2+3,2 | 6.4 | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | * |  | SS 35/10 kv Kalikino | 3,2+3,2 |  | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | *
| SS 35/10 kv Borisovka | 4+2,5 | 6.5 | 2.74 | 0 | 0 | 2.74 | 0 | 2.625 | -0.115 | -0.115 | closed |  | SS 35/10 kv Borisovka | 4+2,5 | 0.419 | 3.159 | 0 | 0 | 3.159 | 0 | 2.625 | -0.534 | -0.534 | closed
| SS 35/10 kv Vvedenka | 4+4 | 8 | 4 | 0.14 | 70 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | * |  | SS 35/10 kv Vvedenka | 4+4 | 1.369 | 5.369 | 0.14 | 70 | 5.229 | 0 | 4.2 | -1.029 | -1.029 | closed
| SS 35/10 kv Gryaznoe | 4+4 | 8 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | * |  | SS 35/10 kv Gryaznoe | 4+4 | 0.548 | 1.708 | 0 | 0 | 1.708 | 0 | 4.2 | 2.492 | 2.492 | *
| SS 35/10 kv Borino | 4+4 | 8 | 4.24 | 1.2 | 90 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | * |  | SS 35/10 kv Borino | 4+4 | 0.33 | 4.57 | 1.2 | 90 | 3.37 | 0 | 4.2 | 0.83 | 0.83 | *
| SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 5 | 1.6 | 1.88 | 100 (45) | -0.28 | 0 | 2.625 | 2.905 | 2.905 | * |  | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 3.085 | 4.685 | 1.88 | 100 (45) | 2.805 | 0 | 2.625 | -0.18 | -0.18 | closed
| SS 35/10 kv Troitskaya | 2,5+4 | 6.5 | 2.33 | 0.6 | 70 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | * |  | SS 35/10 kv Troitskaya | 2,5+4 | 0.026 | 2.356 | 0.6 | 70 | 1.756 | 0 | 2.625 | 0.869 | 0.869 | *
| SS 35/6 kv Veshalovka | 2,5+2,5 | 5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | * |  | SS 35/6 kv Veshalovka | 2,5+2,5 |  | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | *
| SS 35/10 kv Pruzhinki | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | * |  | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.015 | 0.615 | 0 | 0 | 0.615 | 0 | 2.625 | 2.01 | 2.01 | *
| SS 35/10 kv Stebaevo | 2,5+2,5 | 5 | 0.95 | 0.28 | 80 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | * |  | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.015 | 0.965 | 0.28 | 80 | 0.685 | 0 | 2.625 | 1.94 | 1.94 | *
| SS 35/10 kv Khleboprodukty | 6,3+6,3 | 12.6 | 3.52 | 0.6 | 100 | 2.92 | 0 | 6.615 | 3.695 | 3.695 | * |  | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 0.346 | 3.866 | 0.6 | 100 | 3.266 | 0 | 6.615 | 3.349 | 3.349 | *
| SS 35/10 kv Sentsovo | 10+10 | 20 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 | 5.3 | * |  | SS 35/10 kv Sentsovo | 10+10 | 1.815 | 7.015 | 0 | 0 | 7.015 | 0 | 10.5 | 3.485 | 3.485 | *
| SS 35/10 kv Meet processing factory | 6,3+6,3 | 12.6 | 4.46 | 1.6 | 110 | 2.86 | 0 | 6.62 | 3.76 | 3.76 | * |  | SS 35/10 kv Meet processing factory | 6,3+6,3 | 2.081 | 6.541 | 1.6 | 110 | 4.941 | 0 | 6.62 | 1.679 | 1.679 | *
| SS 35/6 kv Poultry plant | 4+4 | 8 | 1.93 | 0 | 0 | 1.93 | 0 | 4.2 | 2.27 | 2.27 | * |  | SS 35/6 kv Poultry plant | 4+4 | 0.087 | 2.017 | 0 | 0 | 2.017 | 0 | 4.2 | 2.183 | 2.183 | *
| SS 35/6 kv Water intake | 10+10 | 20 | 0.43 | 0 | 0 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | * |  | SS 35/6 kv Water intake | 10+10 | 0.034 | 0.464 | 0 | 0 | 0.464 | 0 | 10.5 | 10.036 | 10.036 | *
| SS 35/10 kv Petrovskaya | 2,5+4 | 6.5 | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened |  | SS 35/10 kv Petrovskaya | 2,5+4 |  | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
| SS 35/10 kv Lebedyanka | 2,5+2,5 | 5 | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened |  | SS 35/10 kv Lebedyanka | 2,5+2,5 |  | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
| SS 35/10 kv Novocherkutino | 4+4 | 8 | 0.97 | 1.02 | 100 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | opened |  | SS 35/10 kv Novocherkutino | 4+4 | 0.008 | 0.978 | 1.02 | 100 | -0.042 | 0 | 4.2 | 4.242 | 4.242 | opened
| SS 35/10 kv Ivanovka | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened |  | SS 35/10 kv Ivanovka | 2,5+2,5 | 0.05 | 1.11 | 0 | 0 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | opened
| SS 35/10 kv Poddubrovka | 2,5+2,5 | 5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | opened |  | SS 35/10 kv Poddubrovka | 2,5+2,5 | 0.037 | 1.007 | 0 | 0 | 1.007 | 0 | 2.625 | 1.618 | 1.618 | opened
| SS 35/10 kv Plavitsa | 1,6+1,6 | 3.2 | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened |  | SS 35/10 kv Plavitsa | 1,6+1,6 |  | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
| SS 35/10 kv Parshinovka | 1,6+2,5 | 4.1 | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened |  | SS 35/10 kv Parshinovka | 1,6+2,5 |  | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
| SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 7.2 | 2.2 | 1.28 | 100 | 0.92 | 0 | 3.36 | 2.44 | 2.44 | opened |  | SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 0.05 | 2.25 | 1.28 | 100 | 0.97 | 0 | 3.36 | 2.39 | 2.39 | opened
| SS 35/10 kv Demshinka | 2,5+2,5 | 5 | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened |  | SS 35/10 kv Demshinka | 2,5+2,5 |  | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened
| SS 35/10 kv Bereznyagovka | 1,6+1,6 | 3.2 | 0.62 | 0.46 | 80 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened |  | SS 35/10 kv Bereznyagovka | 1,6+1,6 | 0.011 | 0.631 | 0.46 | 80 | 0.171 | 0 | 1.68 | 1.509 | 1.509 | opened
| SS 35/10 kv Dmitrievka | 2,5+2,5 | 5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened |  | SS 35/10 kv Dmitrievka | 2,5+2,5 |  | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened
| SS 35/10 kv Pashkovo | 2,5+2,5 | 5 | 1.89 | 0 | 0 | 1.89 | 0 | 2.625 | 0.735 | 0.735 | opened |  | SS 35/10 kv Pashkovo | 2,5+2,5 | 0.02 | 1.91 | 0 | 0 | 1.91 | 0 | 2.625 | 0.715 | 0.715 | opened
| SS 35/10 kv Moskovka | 1,6+1,6 | 3.2 | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | opened |  | SS 35/10 kv Moskovka | 1,6+1,6 |  | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | opened
| SS 35/10 kv Bochinovka | 4+4 | 8 | 3.14 | 1.18 | 90 | 1.96 | 0 | 4.2 | 2.24 | 2.24 | opened |  | SS 35/10 kv Bochinovka | 4+4 | 0.028 | 3.168 | 1.18 | 90 | 1.988 | 0 | 4.2 | 2.212 | 2.212 | opened
| SS 35/10 kv Fyodorovka | 2,5+2,5 | 5 | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened |  | SS 35/10 kv Fyodorovka | 2,5+2,5 |  | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
| SS 35/10 kv Kulikovo | 2,5+2,5 | 5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened |  | SS 35/10 kv Kulikovo | 2,5+2,5 |  | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
| SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 5 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | * |  | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 1.261 | 2.501 | 0 | 0 | 2.501 | 0 | 2.625 | 0.124 | 0.124 | *
| SS 35/10 kv Dmitryashevka | 2,5+2,5 | 5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | * |  | SS 35/10 kv Dmitryashevka | 2,5+2,5 |  | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | *
| SS 35/10 kv Rechnaya | 4+4 | 8 | 1.57 | 1.06 | 100 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | * |  | SS 35/10 kv Rechnaya | 4+4 | 0.018 | 1.588 | 1.06 | 100 | 0.528 | 0 | 4.2 | 3.672 | 3.672 | *
| SS 35/10 kv Negachevka | 2,5+2,5 | 5 | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | * |  | SS 35/10 kv Negachevka | 2,5+2,5 |  | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | *
| SS 35/10 kv Karamyshevo | 10+10 | 20 | 0.56 | 0.1 | 70 | 0.46 | 0 | 10.5 | 10.04 | 10.04 | opened |  | SS 35/10 kv Karamyshevo | 10+10 | 0.036 | 0.596 | 0.1 | 70 | 0.496 | 0 | 10.5 | 10.004 | 10.004 | opened
| SS 35/10 kv Tyushevka | 1,6+1,6 | 3.2 | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | * |  | SS 35/10 kv Tyushevka | 1,6+1,6 |  | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | *
| SS 35/10 kv Sselki | 10+10 |  | 0 | [8 empty] | 2: SS 35/10 kv Sselki; 3: 10+10; 4: 4.752; 5: 4.752
Two- and more transformer substations (for three voltage levels) | [12 empty] | 1: Two- and more transformer substations (for three voltage levels)
| SS 110/35/10 kv Terbuny-110 | 10+10 | 20 | 9.26 | 3.5 |  | 5.76 | 0 | 10.5 | 4.74 | 4.71 | opened |  | SS 110/35/10 kv Terbuny-110 | 10+10 | 0.986 | 10.246 | 3.5 |  | 6.746 | 0 | 10.5 | 3.754 | 3.734 | opened
| Nom. Capacity MV, МVA | 10+10 |  | 3.47 | 3.5 | 30 | -0.03 | 0 | 10.5 | 10.53 |  |  |  | Nom. Capacity MV, МVA | 10+10 | 0.01 | 3.48 | 3.5 | 30 | -0.02 | 0 | 10.5 | 10.52
| Nom. capacity LV, МVA | 10+10 |  | 5.79 | 0 | 0 | 5.79 | 0 | 10.5 | 4.71 |  |  |  | Nom. capacity LV, МVA | 10+10 | 0.976 | 6.766 | 0 | 0 | 6.766 | 0 | 10.5 | 3.734
| SS 110/35/10 kv Dolgorukovo | 6,3+10 | 16.3 | 6.98 | 4 |  | 2.98 | 0 | 6.615 | 3.635 | 3.525 | opened |  | SS 110/35/10 kv Dolgorukovo | 6,3+10 | 0.015 | 6.995 | 4 |  | 2.995 | 0 | 6.615 | 3.62 | 3.525 | opened
| Nom. capacity MV, МVA | 6,3+10 |  | 3.89 | 4 | 45 | -0.11 | 0 | 6.615 | 6.725 |  |  |  | Nom. capacity MV, МVA | 6,3+10 | 0.015 | 3.905 | 4 | 45 | -0.095 | 0 | 6.615 | 6.71
| Nom. capacity LV, МVA | 6,3+10 |  | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525 |  |  |  | Nom. capacity LV, МVA | 6,3+10 | 0 | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525
| SS 110/35/10 kv Volovo | 10+10 | 20 | 2.07 | 0.89 |  | 1.18 | 0 | 10.5 | 9.32 | 9.32 | opened |  | SS 110/35/10 kv Volovo | 10+10 | 0.14 | 2.21 | 0.89 |  | 1.32 | 0 | 10.5 | 9.18 | 9.18 | opened
| Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 |  | 2.07 | 0.89 | 60 | 1.18 | 0 | 10.5 | 9.32 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.14 | 2.21 | 0.89 | 60 | 1.32 | 0 | 10.5 | 9.18
| SS 110/35/10 kv Izmalkovo | 10+10 | 20 | 5 | 1.2 |  | 3.8 | 0 | 10.5 | 6.7 | 6.7 | opened |  | SS 110/35/10 kv Izmalkovo | 10+10 | 2.545 | 7.545 | 1.2 |  | 6.345 | 0 | 10.5 | 4.155 | 4.155 | opened
| Nom. capacity MV, МVА | 10+10 |  | 2.82 | 1.2 | 30 | 1.62 | 0 | 10.5 | 8.88 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 2.82 | 1.2 | 30 | 1.62 | 0 | 10.5 | 8.88
| Nom. capacity LV, МVА | 10+10 |  | 2.18 | 0 | 0 | 2.18 | 0 | 10.5 | 8.32 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.545 | 4.725 | 0 | 0 | 4.725 | 0 | 10.5 | 5.775
| SS 110/35/10 kv Gorokhovskaya | 16+16 | 32 | 10.52 | 7.2 |  | 3.32 | 0 | 16.8 | 13.48 | 13.48 | opened |  | SS 110/35/10 kv Gorokhovskaya | 16+16 | 2.613 | 13.133 | 7.2 |  | 5.933 | 0 | 16.8 | 10.867 | 10.867 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.94 | 6 | 30 | 0.94 | 0 | 16.8 | 15.86 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.601 | 8.541 | 6 | 30 | 2.541 | 0 | 16.8 | 14.259
| Nom. capacity LV, МVА | 16+16 |  | 3.58 | 1.2 | 120 | 2.38 | 0 | 16.8 | 14.42 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.012 | 4.592 | 1.2 | 120 | 3.392 | 0 | 16.8 | 13.408
| SS 110/35/10 kv Donskaya | 10+10 | 20 | 7.1 | 4.89 |  | 2.21 | 0 | 10.5 | 8.29 | 8.25 | opened |  | SS 110/35/10 kv Donskaya | 10+10 | 0.022 | 7.122 | 4.89 |  | 2.232 | 0 | 10.5 | 8.268 | 8.243 | opened
| Nom. capacity MV, МVА | 10+10 |  | 3.96 | 4 | 30 | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.015 | 3.975 | 4 | 30 | -0.025 | 0 | 10.5 | 10.525
| Nom. capacity LV, МVА | 10+10 |  | 3.14 | 0.89 | 120 | 2.25 | 0 | 10.5 | 8.25 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.007 | 3.147 | 0.89 | 120 | 2.257 | 0 | 10.5 | 8.243
| SS 110/35/10 kv Lebedyan | 16+16 | 32 | 15.92 | 9 |  | 6.92 | 0 | 16.8 | 9.88 | 9.88 | opened |  | SS 110/35/10 kv Lebedyan | 16+16 | 0.636 | 16.556 | 9 |  | 7.556 | 0 | 16.8 | 9.244 | 9.244 | opened
| Nom. capacity MV, МVА | 16+16 |  | 7.2 | 6 | 60 | 1.2 | 0 | 16.8 | 15.6 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.021 | 7.221 | 6 | 60 | 1.221 | 0 | 16.8 | 15.579
| Nom. capacity LV, МVА | 16+16 |  | 8.72 | 3 | 120 | 5.72 | 0 | 16.8 | 11.08 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.615 | 9.335 | 3 | 120 | 6.335 | 0 | 16.8 | 10.465
| SS 110/35/10 kv Chaplygin-novaya | 16+16 | 32 | 7.58 | 4.5 |  | 3.08 | 0 | 16.8 | 13.72 | 13.72 | opened |  | SS 110/35/10 kv Chaplygin-novaya | 16+16 | 0.007 | 7.587 | 4.5 |  | 3.087 | 0 | 16.8 | 13.713 | 13.713 | opened
| Nom. capacity MV, МVА | 16+16 |  | 3.4 | 2.5 | 20 | 0.9 | 0 | 16.8 | 15.9 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 3.4 | 2.5 | 20 | 0.9 | 0 | 16.8 | 15.9
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 2 | 100 | 2.18 | 0 | 16.8 | 14.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.007 | 4.187 | 2 | 100 | 2.187 | 0 | 16.8 | 14.613
| SS 110/35/10 kv Kompressornaya | 16+16 | 32 | 4.81 | 3.2 |  | 1.61 | 0 | 16.8 | 15.19 | 15.19 | opened |  | SS 110/35/10 kv Kompressornaya | 16+16 | 0.177 | 4.987 | 3.2 |  | 1.787 | 0 | 16.8 | 15.013 | 15.013 | opened
| Nom. Capacity MV, МVА | 16+16 |  | 2.51 | 2.2 | 20 | 0.31 | 0 | 16.8 | 16.49 |  |  |  | Nom. Capacity MV, МVА | 16+16 | 0.177 | 2.687 | 2.2 | 20 | 0.487 | 0 | 16.8 | 16.313
| Nom. capacity LV, МVА | 16+16 |  | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0 | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5
| SS 110/35/10 kv Rossiya | 16+16 | 32 | 5.6 | 3.8 |  | 1.8 | 0 | 16.8 | 15 | 15 | opened |  | SS 110/35/10 kv Rossiya | 16+16 | 0.026 | 5.626 | 3.8 |  | 1.826 | 0 | 16.8 | 14.974 | 14.974 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.67 | 3 | 60 | 1.67 | 0 | 16.8 | 15.13 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.026 | 4.696 | 3 | 60 | 1.696 | 0 | 16.8 | 15.104
| Nom. capacity LV, МVА | 16+16 |  | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0 | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67
| SS 110/35/10 kv Beryozovka | 16+10 | 26 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | opened |  | SS 110/35/10 kv Beryozovka | 16+10 | 0 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | opened
| Nom. capacity MV, МVА | 16+10 |  | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13 |  |  |  | Nom. capacity MV, МVА | 16+10 | 0 | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13
| Nom. capacity LV, МVА | 16+10 |  | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0 | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29
| SS 110/35/10 kv Astapovo | 16+16 | 32 | 4.62 | 3 |  | 1.62 | 0 | 16.8 | 15.18 | 15.18 | opened |  | SS 110/35/10 kv Astapovo | 16+16 | 0.5 | 5.12 | 3 |  | 2.12 | 0 | 16.8 | 14.68 | 14.68 | opened
| Nom. capacity MV, МVА | 16+16 |  | 2.74 | 2 | 60 | 0.74 | 0 | 16.8 | 16.06 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 2.74 | 2 | 60 | 0.74 | 0 | 16.8 | 16.06
| Nom. capacity LV, МVА | 16+16 |  | 1.88 | 1 | 60 | 0.88 | 0 | 16.8 | 15.92 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.5 | 2.38 | 1 | 60 | 1.38 | 0 | 16.8 | 15.42
| SS 110/35/10 kv Khimicheskaya | 16+16 | 32 | 8.46 | 5.5 |  | 2.96 | 0 | 16.8 | 13.84 | 13.84 | opened |  | SS 110/35/10 kv Khimicheskaya | 16+16 | 0.625 | 9.085 | 5.5 |  | 3.585 | 0 | 16.8 | 13.215 | 13.215 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.34 | 4.5 | 60 | 1.84 | 0 | 16.8 | 14.96 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.61 | 6.95 | 4.5 | 60 | 2.45 | 0 | 16.8 | 14.35
| Nom. capacity LV, МVА | 16+16 |  | 2.12 | 1 | 60 | 1.12 | 0 | 16.8 | 15.68 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.015 | 2.135 | 1 | 60 | 1.135 | 0 | 16.8 | 15.665
| SS 110/35/6 kv Bugor | 15+15+25 | 55 | 36.17 | 0.5 |  | 35.67 | 1 | 31.5 | -5.17 | -5.17 | closed |  | SS 110/35/6 kv Bugor | 15+15+25 | 13.45 | 49.62 | 0.5 |  | 49.12 | 1 | 31.5 | -18.62 | -18.62 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.37 | 0 | 0 | 9.37 | 0 | 31.5 | 22.13 |  |  |  | Nom. capacity MV, МVА | 15+15+25 | 10.4 | 19.77 | 0 | 0 | 19.77 | 0 | 31.5 | 11.73
| Nom. capacity LV, МVА | 15+15+25 |  | 26.8 | 0.5 | 40 | 26.3 | 1 | 31.5 | 4.2 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 3.05 | 29.85 | 0.5 | 40 | 29.35 | 1 | 31.5 | 1.15
| SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 115 | 47.33 | 0 |  | 47.33 | 0 | 54.6 | 7.27 | -6.45 | closed |  | SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 2.6895 | 50.0195 | 0 |  | 50.0195 | 0 | 54.6 | 4.5805 | -9.0395 | closed
| Nom. capacity MV, МVА | 63+20 |  | 27.45 | 0 | 0 | 27.45 | 0 | 21 | -6.45 |  |  |  | Nom. capacity MV, МVА | 63+20 | 2.5895 | 30.0395 | 0 | 0 | 30.0395 | 0 | 21 | -9.0395
| Nom. capacity LV, МVА | 63+32+20 |  | 19.88 | 0 | 30 | 19.88 | 0 | 54.6 | 34.72 |  |  |  | Nom. capacity LV, МVА | 63+32+20 | 0.1 | 19.98 | 0 | 30 | 19.98 | 0 | 54.6 | 34.62
| SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 81.5 | 11.03 | 2.5 |  | 8.53 | 0 | 52.5 | 43.97 | -3.6 | closed |  | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 0.803 | 11.833 | 2.5 |  | 9.333 | 0 | 52.5 | 43.167 | -4.056 | closed
| Nom. capacity MV, МVА | 31.5 |  | 5.6 | 2 | 10 | 3.6 | 0 | 2 | -3.6 |  |  |  | Nom. capacity MV, МVА | 31.5 | 0.456 | 6.056 | 2 | 10 | 4.056 | 0 | 2 | -4.056
| Nom. capacity LV, МVА | 25+25+31,5 |  | 5.43 | 0.5 | 80 | 4.93 | 0 | 52.5 | 47.57 |  |  |  | Nom. capacity LV, МVА | 25+25+31,5 | 0.347 | 5.777 | 0.5 | 80 | 5.277 | 0 | 52.5 | 47.223
| SS 110/35/10 kv Usman | 16+16 | 32 | 15.28 | 6.5 |  | 8.78 | 0 | 16.8 | 8.02 | 7.93 | opened |  | SS 110/35/10 kv Usman | 16+16 | 0.232 | 15.512 | 6.5 |  | 9.012 | 0 | 16.8 | 7.788 | 7.746 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.91 | 5 | 20 | -0.09 | 0 | 16.8 | 16.89 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.048 | 4.958 | 5 | 20 | -0.042 | 0 | 16.8 | 16.842
| Nom. Capacity LV, МVА | 16+16 |  | 10.37 | 1.5 | 100 | 8.87 | 0 | 16.8 | 7.93 |  |  |  | Nom. Capacity LV, МVА | 16+16 | 0.184 | 10.554 | 1.5 | 100 | 9.054 | 0 | 16.8 | 7.746
| SS 110/35/10 kv Aksai | 10+10 | 20 | 8.32 | 1.12 |  | 7.2 | 0 | 10.5 | 3.3 | 3.3 | opened |  | SS 110/35/10 kv Aksai | 10+10 | 0.0435 | 8.3635 | 1.12 |  | 7.2435 | 0 | 10.5 | 3.2565 | 3.2565 | opened
| Nom. Capacity MV, МVА | 10+10 |  | 5.82 | 0.5 | 20 | 5.32 | 0 | 10.5 | 5.18 |  |  |  | Nom. Capacity MV, МVА | 10+10 | 0.0385 | 5.8585 | 0.5 | 20 | 5.3585 | 0 | 10.5 | 5.1415
| Nom. capacity LV, МVА | 10+10 |  | 2.5 | 0.62 | 80 | 1.88 | 0 | 10.5 | 8.62 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.005 | 2.505 | 0.62 | 80 | 1.885 | 0 | 10.5 | 8.615
| SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 12.6 | 4.91 | 3.34 |  | 1.57 | 0 | 6.615 | 5.045 | 5.045 | opened |  | SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 0.0475 | 4.9575 | 3.34 |  | 1.6175 | 0 | 6.615 | 4.9975 | 4.9975 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 3.55 | 3 | 10 | 0.55 | 0 | 6.615 | 6.065 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.0425 | 3.5925 | 3 | 10 | 0.5925 | 0 | 6.615 | 6.0225
| Nom. capacity LV, МVА | 6,3+6,3 |  | 1.36 | 0.34 | 80 | 1.02 | 0 | 6.615 | 5.595 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.005 | 1.365 | 0.34 | 80 | 1.025 | 0 | 6.615 | 5.59
| SS 110/35/10 kv Khvorostyanka | 10+16 | 26 | 12.41 | 6.72 |  | 5.69 | 0 | 10.5 | 4.81 | 4.81 | opened |  | SS 110/35/10 kv Khvorostyanka | 10+16 | 0.7935 | 13.2035 | 6.72 |  | 6.4835 | 0 | 10.5 | 4.0165 | 4.0165 | opened
| Nom. capacity MV, МVА | 10+16 |  | 9.32 | 6.5 | 20 | 2.82 | 0 | 10.5 | 7.68 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.7785 | 10.0985 | 6.5 | 20 | 3.5985 | 0 | 10.5 | 6.9015
| Nom. capacity LV, МVА | 10+16 |  | 3.09 | 0.22 | 80 | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.015 | 3.105 | 0.22 | 80 | 2.885 | 0 | 10.5 | 7.615
| SS 110/35/10 kv Dobrinka | 16+10 | 26 | 6.89 | 5.68 |  | 1.21 | 0 | 10.5 | 9.29 | 8.88 | opened |  | SS 110/35/10 kv Dobrinka | 16+10 | 0.154 | 7.044 | 5.68 |  | 1.364 | 0 | 10.5 | 9.136 | 8.776 | opened
| Nom. capacity СН, МВА | 16+10 |  | 3.59 | 4 | 80 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Nom. capacity СН, МВА | 16+10 | 0.05 | 3.64 | 4 | 80 | -0.36 | 0 | 10.5 | 10.86
| Nom. capacity LV, МVА | 16+10 |  | 3.3 | 1.68 | 100 | 1.62 | 0 | 10.5 | 8.88 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.104 | 3.404 | 1.68 | 100 | 1.724 | 0 | 10.5 | 8.776
| SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 12.6 | 1.39 | 0.4 |  | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened |  | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 0.01 | 1.4 | 0.4 |  | 1 | 0 | 6.615 | 5.615 | 5.615 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.77 | 0.4 | 90 | 0.37 | 0 | 6.615 | 6.245 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.01 | 0.78 | 0.4 | 90 | 0.38 | 0 | 6.615 | 6.235
| SS 110/35/10 kv Kazinka | 16+16 | 32 | 15.81 | 0 |  | 15.81 | 0 | 16.8 | 0.99 | 0.99 | opened |  | SS 110/35/10 kv Kazinka | 16+16 | 1.495 | 17.305 | 0 |  | 17.305 | 0 | 16.8 | -0.505 | -0.505 | closed
| Nom. capacity MV, МVА | 16+16 |  | 10.36 | 0 | 0 | 10.36 | 0 | 16.8 | 6.44 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.11 | 11.47 | 0 | 0 | 11.47 | 0 | 16.8 | 5.33
| Nom. capacity LV, МVА | 16+16 |  | 5.45 | 0 | 0 | 5.45 | 0 | 16.8 | 11.35 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.385 | 5.835 | 0 | 0 | 5.835 | 0 | 16.8 | 10.965
| SS 110/35/10 kv Dobroe | 16+16 | 32 | 11.4 | 3 |  | 8.4 | 0 | 16.8 | 8.4 | 8.4 | * |  | SS 110/35/10 kv Dobroe | 16+16 | 2.886 | 14.286 | 3 |  | 11.286 | 0 | 16.8 | 5.514 | 5.514 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.22 | 3 | 20 | 3.22 | 0 | 16.8 | 13.58 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.544 | 6.764 | 3 | 20 | 3.764 | 0 | 16.8 | 13.036
| Nom. capacity LV, МVА | 16+16 |  | 5.18 | 0 | 0 | 5.18 | 0 | 16.8 | 11.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 2.342 | 7.522 | 0 | 0 | 7.522 | 0 | 16.8 | 9.278
| SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 16.3 | 7.64 | 5 |  | 2.64 | 0 | 6.615 | 3.975 | 3.975 | * |  | SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 0.1605 | 7.8005 | 5 |  | 2.8005 | 0 | 6.615 | 3.8145 | 3.8145 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 5.4 | 5 | 10 | 0.4 | 0 | 6.615 | 6.215 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.0905 | 5.4905 | 5 | 10 | 0.4905 | 0 | 6.615 | 6.1245
| Nom. capacity LV, МVА | 10+6,3 |  | 2.24 | 0 | 0 | 2.24 | 0 | 6.615 | 4.375 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.07 | 2.31 | 0 | 0 | 2.31 | 0 | 6.615 | 4.305
| SS 110/35/6 kv Verbilovo | 10+6,3 | 16.3 | 3.96 | 0 |  | 3.96 | 0 | 6.62 | 2.66 | 2.66 | * |  | SS 110/35/6 kv Verbilovo | 10+6,3 | 0.636 | 4.596 | 0 |  | 4.596 | 0 | 6.62 | 2.024 | 2.024 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 2.76 | 0 | 0 | 2.76 | 0 | 6.62 | 3.86 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.563 | 3.323 | 0 | 0 | 3.323 | 0 | 6.62 | 3.297
| Nom. capacity LV, МVА | 10+6,3 |  | 1.2 | 0 | 0 | 1.2 | 0 | 6.62 | 5.42 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.073 | 1.273 | 0 | 0 | 1.273 | 0 | 6.62 | 5.347
| SS 110/35/10 kv Khlevnoe | 16+16 | 32 | 10.04 | 0 |  | 10.04 | 0 | 16.8 | 6.76 | 6.76 | * |  | SS 110/35/10 kv Khlevnoe | 16+16 | 4.038 | 14.078 | 0 |  | 14.078 | 0 | 16.8 | 2.722 | 2.722 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.336 | 7.196 | 0 | 0 | 7.196 | 0 | 16.8 | 9.604
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 0 | 0 | 4.18 | 0 | 16.8 | 12.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 2.702 | 6.882 | 0 | 0 | 6.882 | 0 | 16.8 | 9.918
| SS 110/35/10 kv Naberezhnoe | 6,3+10 | 16.3 | 2.46 | 4.5 |  | -2.04 | 0 | 6.62 | 8.66 | 5.45 | opened |  | SS 110/35/10 kv Naberezhnoe | 6,3+10 | 1.07 | 3.53 | 4.5 |  | -0.97 | 0 | 6.62 | 7.59 | 5.45 | opened
| Nom. capacity MV, МVА | 6,3+10 |  | 1.29 | 4.5 | 10 | -3.21 | 0 | 6.62 | 9.83 |  |  |  | Nom. capacity MV, МVА | 6,3+10 | 1.07 | 2.36 | 4.5 | 10 | -2.14 | 0 | 6.62 | 8.76
| Nom. capacity LV, МVА | 6,3+10 |  | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45 |  |  |  | Nom. capacity LV, МVА | 6,3+10 | 0 | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45
| SS 110/35/10 kv Chaplygin | 7,5+6,3 | 13.8 | 5.54 | 4.5 |  | 1.04 | 0 | 6.62 | 5.58 | 5.58 | opened |  | SS 110/35/10 kv Chaplygin | 7,5+6,3 | 0.005 | 5.545 | 4.5 |  | 1.045 | 0 | 6.62 | 5.575 | 5.575 | opened
| Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 7,5+6,3 |  | 5.54 | 4.5 | 30 | 1.04 | 0 | 6.62 | 5.58 |  |  |  | Nom. capacity LV, МVА | 7,5+6,3 | 0.005 | 5.545 | 4.5 | 30 | 1.045 | 0 | 6.62 | 5.575
| SS 110/35/10 kv Troekurovo | 10+6,3 | 16.3 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | opened |  | SS 110/35/10 kv Troekurovo | 10+6,3 | 0 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | opened
| Nom. capacity MV, МVА | 10+6,3 |  | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0 | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32
| Nom. capacity LV, МVА | 10+6,3 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0 | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67
| Total: | 2515.6 | 2515.6 | 731.9979 | [6 empty] | 680.7721 |  | 2: Total:; 3: 2522.5; 5: 890.9564; Мin. 12: 538.6086
| deficit | [9 empty] | -37.1994 |  | 2: deficit; Мin. 12: -73.0729
| proficit | [9 empty] | 446.8977 | taking into account * | 2: proficit; Мin. 12: 313.7232; Мin. 13: taking into account *
* Ограничение на присоединяемую мощность по режиму работы сети 110, 220 кВ (по данным Липецкого РДУ) | * Restriction to connected capacity according to working schedule of the grid of 110,220kv (according to data of Lipetsk Regional Dispatching Office)
Note on E31: Автор: нагрузка 1 МВт, введена в сентябре
Note on E174: Автор: введена в сентябре, потебители неподключены
Note on S31: Автор: нагрузка 1 МВт, введена в сентябре
Note on S174: Автор: введена в сентябре, потебители неподключены

## ярославль 3
[9 empty] | table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including redistribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including redistribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 0.35 | 0.837 | 24 hours | 0.837 | 0 | 0.837 | 0.487 | 0.487 | opened | 1 | SS 35/10 Matveevo | 1.6 | 0.004 | 0.354 | 0.837 | 24 hours | 0.837 | 0 | 0.837 | 0.483 | 0.483 | opened
2 | SS 35/10 Mikhailovskoe | 6.3 | 1.34 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.28 | 5.28 | opened | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.343 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.277 | 5.277 | opened
3 | SS 35/10 Shirinye | 2.5 | 2.56 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | -1.798 | -1.798 | closed | 3 | SS 35/10 Shirinye | 2.5 | 0.23 | 2.79 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | -2.028 | -2.028 | closed
4 | SS 110/10 Pokrov | 2.5 | 0.29 | 0.945 | 24 hours | 0.945 | 0 | 0.945 | 0.655 | 0.655 | opened | 4 | SS 110/10 Pokrov | 2.5 | 0 | 0.29 | 0.945 | 24 hours | 0.945 | 0 | 0.945 | 0.655 | 0.655 | opened
5 | SS 35/10 Obnora | 1.6 | 0.4 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.7 | 0.7 | opened | 5 | SS 35/10 Obnora | 1.6 | 0.01 | 0.41 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.69 | 0.69 | opened
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 11.1 |  |  | 11.1 | 0 | 10.5 | -0.6 | -0.6 | closed | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 14.5826 |  |  | 14.5826 | 0 | 10.5 | -4.0827 | -4.0827 | closed
| Nom. capacity MV, МVА | 10+10 | 8.84 |  |  | 8.84 | 0 | 10.5 | 1.66 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 12.082; Мin. 8: 12.082; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: -1.5819
| Nom. capacity LV, МVА | 10+10 | 2.26 |  |  | 2.26 | 0 | 10.5 | 8.24 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.2407 | 2.5007 |  |  | 2.5007 | 0 | 10.5 | 7.9993
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.49 |  |  | 1.49 | 0 | 1.68 | 0.19 | 0.19 | opened | 7 | SS 35/10 Ananyino | 1,6+1,6 | 0.229 | 1.719 |  |  | 1.719 | 0 | 1.68 | -0.039 | -0.039 | closed
8 | SS 110/10/10 Bragino | 40+40 | 35.09 | 1.937 | 120 | 33.153 | 0 | 42 | 8.847 | 8.847 | opened | 8 | SS 110/10/10 Bragino | 40+40 | 5.6276 | 40.7176 | 1.937 | 120 | 38.7806 | 0 | 42 | 3.2194 | 3.2194 | opened
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 2.85 | 0.843 | 120 | 2.007 | 0 | 4.2 | 2.193 | 2.193 | opened | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.455 | 3.305 | 0.843 | 120 | 2.462 | 0 | 4.2 | 1.738 | 1.738 | opened
10 | SS 35/10 Vatolino | 2,5+4,0 | 3.52 |  |  | 3.52 | 0 | 2.63 | -0.89 | -0.89 | closed | 10 | SS 35/10 Vatolino | 2,5+4,0 | 0.582 | 4.102 |  |  | 4.102 | 0 | 2.63 | -1.472 | -1.472 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 4.85 |  |  | 4.85 | 0 | 6.62 | 1.77 | 1.77 | opened | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.4041 | 5.2541 |  |  | 5.2541 | 0 | 6.62 | 1.3659 | 1.3659 | opened
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 2.28 |  |  | 2.28 | 0 | 4.2 | 1.92 | 1.92 | opened | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.1799 | 2.4599 |  |  | 2.4599 | 0 | 4.2 | 1.7401 | 1.7401 | opened
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.76 |  |  | 0.76 | 0 | 1.68 | 0.92 | 0.92 | opened | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.057 | 0.817 |  |  | 0.817 | 0 | 1.68 | 0.863 | 0.863 | opened
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.66 |  |  | 1.66 | 0 | 4.2 | 2.54 | 2.54 | opened | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.5939 | 3.2539 |  |  | 3.2539 | 0 | 4.2 | 0.9461 | 0.9461 | opened
15 | SS 35/10 Volna | 2,5+2,5 | 3.06 |  |  | 3.06 | 0 | 2.63 | -0.43 | -0.43 | closed | 15 | SS 35/10 Volna | 2,5+2,5 | 0.216 | 3.276 |  |  | 3.276 | 0 | 2.63 | -0.646 | -0.646 | closed
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 1.89 | 0.2 | 120 | 1.69 | 0 | 2.63 | 0.94 | 0.94 | opened | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.099 | 1.989 | 0.2 | 120 | 1.789 | 0 | 2.63 | 0.841 | 0.841 | opened
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.52 | 0.22 | 120 | 0.3 | 0 | 2.63 | 2.33 | 2.33 | opened | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.021 | 0.541 | 0.22 | 120 | 0.321 | 0 | 2.63 | 2.309 | 2.309 | opened
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 3.05 | 0.674 | 120 | 2.376 | 0 | 4.2 | 1.824 | 1.824 | opened | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.354 | 3.404 | 0.674 | 120 | 2.73 | 0 | 4.2 | 1.47 | 1.47 | opened
19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.91 | 1.02 | 120 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 1.7379 | 4.6479 | 1.02 | 120 | 3.6279 | 0 | 4.2 | 0.5721 | 0.5721 | opened
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 1.75 |  |  | 1.75 | 0 | 6.62 | 4.87 | 4.87 | opened | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 1.75 |  |  | 1.75 | 0 | 6.62 | 4.87 | 4.87 | opened
21 | SS 110/6 Depo | 16+16 | 8.33 |  |  | 8.33 | 0 | 16.8 | 8.47 | 8.47 | opened | 21 | SS 110/6 Depo | 16+16 | 9.6025 | 17.9325 |  |  | 17.9325 | 0 | 16.8 | -1.1325 | -1.1325 | closed
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.23 | 0.956 | 120 | 0.274 | 0 | 1.68 | 1.406 | 1.406 | opened | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.384 | 1.614 | 0.956 | 120 | 0.658 | 0 | 1.68 | 1.022 | 1.022 | opened
23 | SS 110/10 Druzhba | 16+16 | 6.33 | 0.16 | 120 | 6.17 | 0 | 16.8 | 10.63 | 10.63 | opened | 23 | SS 110/10 Druzhba | 16+16 | 0.2743 | 6.6043 | 0.16 | 120 | 6.4443 | 0 | 16.8 | 10.3557 | 10.3557 | opened
24 | SS 35/10 Dubki | 6,3+6,3 | 4.62 | 0.787 | 120 | 3.833 | 0 | 6.62 | 2.787 | 2.787 | opened | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.3435 | 4.9635 | 0.787 | 120 | 4.1765 | 0 | 6.62 | 2.4435 | 2.4435 | opened
25 | SS 35/10 Dybino | 2,5+2,5 | 1.22 |  |  | 1.22 | 0 | 2.63 | 1.41 | 1.41 | opened | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.339 | 1.559 |  |  | 1.559 | 0 | 2.63 | 1.071 | 1.071 | opened
26 | SS 35/6 Zavolzhskaya | 10+10 | 12.43 |  |  | 12.43 | 0 | 10.5 | -1.93 | -1.93 | closed | 26 | SS 35/6 Zavolzhskaya | 10+10 | 2.1892 | 14.6192 |  |  | 14.6192 | 0 | 10.5 | -4.1192 | -4.1192 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 38.2 |  |  | 38.2 | 0 | 42 | 3.8 | 3.8 | opened | 27 | SS 110/6/6 Institutskaya | 40+40 | 4.3884 | 42.5884 |  |  | 42.5884 | 0 | 42 | -0.58836 | -0.58836 | closed
28 | SS 35/10 Koza | 1,6+1,6 | 0.41 | 0.179 | 120 | 0.231 | 0 | 1.68 | 1.449 | 1.449 | opened | 28 | SS 35/10 Koza | 1,6+1,6 | 0.014 | 0.424 | 0.179 | 120 | 0.245 | 0 | 1.68 | 1.435 | 1.435 | opened
29 | SS 110/35/6 Konstatinovo | 20+20 | 13.99 | 0.1 | 120 | 13.89 | 0 | 21 | 7.11 | 7.11 | opened | 29 | SS 110/35/6 Konstatinovo | 20+20 |  | 14.782 | 0.1 | 120 | 14.682 | 0 | 21 | 6.318 | 6.318 | opened
| Nom. capacity MV, МVА | 20+20 | 9.73 |  |  | 9.73 | 0 | 21 | 11.27 |  |  | 2: Nom. capacity MV, МVА; 3: 20+20; 5: 10.417; Мin. 8: 10.417; Мin. 9: 0; Мin. 10: 21; Мin. 11: 10.583
| Nom. capacity LV, МVА | 20+20 | 4.26 | 0.1 | 120 | 4.16 | 0 | 21 | 16.84 |  |  |  | Nom. capacity LV, МVА | 20+20 | 0.105 | 4.365 | 0.1 | 120 | 4.265 | 0 | 21 | 16.735
30 | SS 35/10 Kurba | 2,5+2,5 | 2.58 | 1.71 | 120 | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.064 | 2.644 | 1.71 | 120 | 0.934 | 0 | 2.63 | 1.696 | 1.696 | opened
31 | SS 35/10 Lesnye Polyany | 10+10 | 6.92 | 0.48 | 120 | 6.44 | 0 | 10.5 | 4.06 | 4.06 | opened | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.0135 | 7.9335 | 0.48 | 120 | 7.4535 | 0 | 10.5 | 3.0465 | 3.0465 | opened
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 7.16 | 3.69 | 120 | 3.47 | 0 | 6.62 | 3.15 | 3.15 | opened | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 2.3235 | 9.4835 | 3.69 | 120 | 5.7935 | 0 | 6.62 | 0.8265 | 0.8265 | opened
33 | SS 35/10 Nekrasovo | 10+10 | 9.86 |  |  | 9.86 | 0 | 10.5 | 0.64 | 0.64 | opened | 33 | SS 35/10 Nekrasovo | 10+10 | 1.2484 | 11.1084 |  |  | 11.1084 | 0 | 10.5 | -0.60837 | -0.60837 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 1.049 | 0.38 | 120 | 0.669 | 0 | 2.63 | 1.961 | 1.961 | opened | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.035 | 1.084 | 0.38 | 120 | 0.704 | 0 | 2.63 | 1.926 | 1.926 | opened
35 | SS 110/35/6 Oil refinary plant | 25+25 | 16.28 |  |  | 16.28 | 0 | 26.25 | 9.97 | 9.97 | opened | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 23.6841 |  |  | 23.6841 | 0 | 26.25 | 2.5659 | 2.5659 | opened
| Nom. capacity MV, МVА | 25+25 | 8.4 |  |  | 8.4 | 0 | 26.25 | 17.85 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 8.8041; Мin. 8: 8.8041; Мin. 9: 0; Мin. 10: 26.25; Мin. 11: 17.4459
| Nom. capacity LV, МVА | 25+25 | 7.88 |  |  | 7.88 | 0 | 26.25 | 18.37 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7 | 14.88 |  |  | 14.88 | 0 | 26.25 | 11.37
36 | SS 110/6/6 Orion | 40+40 | 14.32 |  |  | 14.32 | 0 | 42 | 27.68 | 27.68 | opened | 36 | SS 110/6/6 Orion | 40+40 | 1.5346 | 15.8546 |  |  | 15.8546 | 0 | 42 | 26.1454 | 26.1454 | opened
37 | SS 110/35/6 Pavlovskaya | 20+25 | 21.5 |  |  | 21.5 | 0 | 21 | -0.5 | -0.5 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 21.8644 |  |  | 21.8644 | 0 | 21 | -0.8644 | -0.8644 | closed
| Nom. capacity MV, МVА | 20+25 | 7.1 |  |  | 7.1 | 0 | 21 | 13.9 |  |  | 2: Nom. capacity MV, МVА; 3: 20+25; 5: 7.277; Мin. 8: 7.277; Мin. 9: 0; Мin. 10: 21; Мin. 11: 13.723
| Nom. capaity LV, МVА | 20+25 | 14.4 |  |  | 14.4 | 0 | 21 | 6.6 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.1874 | 14.5874 |  |  | 14.5874 | 0 | 21 | 6.4126
38 | SS 110/10 Pereval | 16+16 | 8.6 |  |  | 8.6 | 0 | 16.8 | 8.2 | 8.2 | opened | 38 | SS 110/10 Pereval | 16+16 | 8.8616 | 17.4616 |  |  | 17.4616 | 0 | 16.8 | -0.66158 | -0.66158 | closed
39 | SS 110/6/6 Perekop | 25+25 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74 | 12.74 | opened | 39 | SS 110/6/6 Perekop | 25+25 | 3.2276 | 16.7376 |  |  | 16.7376 | 0 | 26.25 | 9.5124 | 9.5124 | opened
40 | SS 110/6/6 Poligraf | 40+40 | 40.327 |  |  | 40.327 | 0 | 42 | 1.673 | 1.673 | opened | 40 | SS 110/6/6 Poligraf | 40+40 | 5.0724 | 45.3994 |  |  | 45.3994 | 0 | 42 | -3.3994 | -3.3994 | closed
41 | SS 110/35/10 Prechistoe | 10+10 | 5.37 | 0.213 | 120 | 5.157 | 0 | 10.5 | 5.343 | 5.343 | opened | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 5.743 | 0.213 | 120 | 5.53 | 0 | 10.5 | 4.97 | 4.97 | opened
| Nom. capacity MV, МVА | 10+10 | 1.79 |  |  | 1.79 | 0 | 10.5 | 8.71 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 1.8989; Мin. 8: 1.8989; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 8.6011
| Nom. capacity LV, МVА | 10+10 | 3.58 | 0.213 | 120 | 3.367 | 0 | 10.5 | 7.133 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.264 | 3.844 | 0.213 | 120 | 3.631 | 0 | 10.5 | 6.869
42 | SS 35/10 Preventorium | 2,5+2,5 | 0.61 | 0.316 | 120 | 0.294 | 0 | 2.63 | 2.336 | 2.336 | opened | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.9913 | 3.6013 | 0.316 | 120 | 3.2853 | 0 | 2.63 | -0.6553 | -0.6553 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.12 | 0.044 | 120 | 0.076 | 0 | 2.63 | 2.554 | 2.554 | opened | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0 | 0.12 | 0.044 | 120 | 0.076 | 0 | 2.63 | 2.554 | 2.554 | opened
44 | SS 110/6/6 Severnaya | 63+63 | 39.51 |  |  | 39.51 | 0 | 66.15 | 26.64 | 26.64 | opened | 44 | SS 110/6/6 Severnaya | 63+63 | 14.8047 | 54.3147 |  |  | 54.3147 | 0 | 66.15 | 11.8353 | 11.8353 | opened
45 | SS 35/10 Sereda | 2,5+2,5 | 1.36 | 0.108 | 120 | 1.252 | 0 | 2.63 | 1.378 | 1.378 | opened | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.1175 | 1.4775 | 0.108 | 120 | 1.3695 | 0 | 2.63 | 1.2605 | 1.2605 | opened
46 | SS 110/6 Tormoznaya | 16+16 | 16.63 |  |  | 16.63 | 0 | 16.8 | 0.17 | 0.17 | opened | 46 | SS 110/6 Tormoznaya | 16+16 | 0.603 | 17.233 |  |  | 17.233 | 0 | 16.8 | -0.433 | -0.433 | closed
47 | SS 110/6 Petrol station pump | 16+16 | 4.52 |  |  | 4.52 | 0 | 16.8 | 12.28 | 12.28 | opened | 47 | SS 110/6 Petrol station pump | 16+16 | 0.6 | 5.12 |  |  | 5.12 | 0 | 16.8 | 11.68 | 11.68 | opened
48 | SS 35/10 Troitsa | 2,5+2,5 | 0.5 | 0.108 | 120 | 0.392 | 0 | 2.63 | 2.238 | 2.238 | opened | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.005 | 0.505 | 0.108 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | opened
49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.61 | 0.01 | 120 | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.09 | 0.7 | 0.01 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | opened
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 7.54 |  |  | 7.54 | 0 | 6.62 | -0.92 | -0.92 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.096 | 7.636 |  |  | 7.636 | 0 | 6.62 | -1.016 | -1.016 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.78 |  |  | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.056 | 0.836 |  |  | 0.836 | 0 | 2.63 | 1.794 | 1.794 | opened
52 | SS 35/10 Urozhay | 4,0+4,0 | 3.2 | 0.825 | 120 | 2.375 | 0 | 4.2 | 1.825 | 1.825 | opened | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.577 | 3.777 | 0.825 | 120 | 2.952 | 0 | 4.2 | 1.248 | 1.248 | opened
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.75 | 0.134 | 120 | 0.31 | 0 | 3.36 | 3.05 | 2.054 | opened | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 1.442 | 0.134 | 120 | 1.308 | 0 | 3.36 | 2.052 | 2.052 | opened
| Nom. capacity MV, МVА | 6.3 | 2.31 | [8 empty] | 2: Nom. capacity MV, МVА; 3: 6.3
| Nom. capacity LV, МVА | 6.3 | 1.44 | 0.134 | 120 | 1.306 | 0 | 3.36 | 2.054 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.002 | 1.442 | 0.134 | 120 | 1.308 | 0 | 3.36 | 2.052
54 | SS 110/10 Chayka | 25+25 | 22.04 |  |  | 22.04 | 0 | 26.25 | 4.21 | 4.21 | opened | 54 | SS 110/10 Chayka | 25+25 | 3.2336 | 25.2736 |  |  | 25.2736 | 0 | 26.25 | 0.97639 | 0.97639 | opened
55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.78 | 0.19 | 120 | 1.59 | 0 | 2.63 | 1.04 | 1.04 | opened | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 0.294 | 2.074 | 0.19 | 120 | 1.884 | 0 | 2.63 | 0.746 | 0.746 | opened
56 | SS 35/10 Shchedrino | 4,0+4,0 | 2.19 |  |  | 2.19 | 0 | 4.2 | 2.01 | 2.01 | opened | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.509 | 2.699 |  |  | 2.699 | 0 | 4.2 | 1.501 | 1.501 | opened
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 32.63 |  |  | 32.63 | 0 | 42 | 9.37 | 9.37 | opened | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 6.8018 | 39.4318 |  |  | 39.4318 | 0 | 42 | 2.5682 | 2.5682 | opened
58 | SS 110/10/6 Yartsevo | 25+25 | 10.32 |  |  | 10.32 | 0 | 26.25 | 15.93 | 15.93 | opened | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.453 | 10.773 |  |  | 10.773 | 0 | 26.25 | 15.477 | 15.477 | opened
59 | SS 110/10 Altynovo | 6,3+6,3 | 3.512 |  |  | 3.512 | 0 | 6.62 | 3.108 | 3.108 | opened | 59 | SS 110/10 Altynovo | 6,3+6,3 | 0.2525 | 3.7645 |  |  | 3.7645 | 0 | 6.62 | 2.8555 | 2.8555 | opened
60 | SS 110/35/10 Borisogleb | 10+16 | 7.938 |  |  | 7.938 | 0 | 10.5 | 2.562 | 2.562 | opened | 60 | SS 110/35/10 Borisogleb | 10+16 |  | 8.8987 |  |  | 8.8987 | 0 | 10.5 | 1.6013 | 1.6013 | opened
| Nom. capacity MV, МVА | 10+16 | 2.72 |  |  | 2.72 | 0 | 10.5 | 7.78 |  |  | 2: Nom. capacity MV, МVА; 3: 10+16; 5: 2.9985; Мin. 8: 2.9985; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 7.5015
| Nom. capacity LV, МVА | 10+16 | 5.218 |  |  | 5.218 | 0 | 10.5 | 5.282 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.6822 | 5.9002 |  |  | 5.9002 | 0 | 10.5 | 4.5998
61 | SS 110/35/10 Vasilkovo | 10+10 | 2.78 | 0.472 | 120 | 2.308 | 0 | 10.5 | 8.192 | 8.192 | opened | 61 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.127 | 0.472 | 120 | 2.655 | 0 | 10.5 | 7.845 | 7.845 | opened
| Nom. capacity MV, МVА | 10+10 | 1.732 |  |  | 1.732 | 0 | 10.5 | 8.768 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 2.059; Мin. 8: 2.059; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 8.441
| Nom. capacity LV, МVА | 10+10 | 1.048 | 0.472 | 120 | 0.576 | 0 | 10.5 | 9.924 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.02 | 1.068 | 0.472 | 120 | 0.596 | 0 | 10.5 | 9.904
62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.28 | 0.07 | 120 | 0.21 | 0 | 6.62 | 6.41 | 6.41 | opened | 62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0 | 0.28 | 0.07 | 120 | 0.21 | 0 | 6.62 | 6.41 | 6.41 | opened
63 | SS 110/6 Gavrilov Yam | 16+16 | 13.286 |  |  | 13.286 | 0 | 16.8 | 3.514 | 3.514 | opened | 63 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 13.286 |  |  | 13.286 | 0 | 16.8 | 3.514 | 3.514 | opened
64 | SS 110/6 Kinoplyonka | 6,3+10 | 6.814 |  |  | 6.814 | 0 | 6.62 | -0.194 | -0.194 | closed | 64 | SS 110/6 Kinoplyonka | 6,3+10 | 2.941 | 9.755 |  |  | 9.755 | 0 | 6.62 | -3.135 | -3.135 | closed
65 | SS 110/35/10 Klimatino | 6,3+6,3 | 1.257 |  |  | 1.257 | 0 | 6.62 | 5.363 | 5.363 | opened | 65 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.288 |  |  | 1.288 | 0 | 6.62 | 5.332 | 5.332 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.313 |  |  | 0.313 | 0 | 6.62 | 6.307 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 0.313; Мin. 8: 0.313; Мin. 9: 0; Мin. 10: 6.62; Мin. 11: 6.307
| Nom. capacity LV, МVА | 6,3+6,3 | 0.944 |  |  | 0.944 | 0 | 6.62 | 5.676 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.031 | 0.975 |  |  | 0.975 | 0 | 6.62 | 5.645
66 | SS 110/35/10 Nila | 6,3+6,3 | 11.107 | 0.45 | 120 | 10.657 | 0 | 6.62 | -4.037 | -4.037 | closed | 66 | SS 110/35/10 Nila | 6,3+6,3 |  | 20.3387 | 0.45 | 120 | 19.8887 | 0 | 6.62 | -13.2687 | -13.2687 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 8.33 |  |  | 8.33 | 0 | 6.62 | -1.71 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 11.1497; Мin. 8: 11.1497; Мin. 9: 0; Мin. 10: 6.62; Мin. 11: -4.5297
| Nom. capacity LV, МVА | 6,3+6,3 | 2.777 | 0.45 | 120 | 2.327 | 0 | 6.62 | 4.293 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 6.412 | 9.189 | 0.45 | 120 | 8.739 | 0 | 6.62 | -2.119
67 | SS 110/35/6 Pereslavl | 25+25 | 26.546 |  |  | 26.546 | 0 | 26.25 | -0.296 | -0.296 | closed | 67 | SS 110/35/6 Pereslavl | 25+25 |  | 34.449 |  |  | 34.449 | 0 | 26.25 | -8.199 | -8.199 | closed
| Nom. capacity MV, МVА | 25+25 | 11.941 |  |  | 11.941 | 0 | 26.25 | 14.309 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 19.062; Мin. 8: 19.062; Мin. 9: 0; Мin. 10: 26.25; Мin. 11: 7.188
| Nom. capacity LV, МVА | 25+25 | 14.605 |  |  | 14.605 | 0 | 26.25 | 11.645 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.782 | 15.387 |  |  | 15.387 | 0 | 26.25 | 10.863
68 | SS 110/10 Ploski | 2,5+2,5 | 1.778 |  |  | 1.778 | 0 | 2.63 | 0.852 | 0.852 | opened | 68 | SS 110/10 Ploski | 2,5+2,5 | 0.2625 | 2.0405 |  |  | 2.0405 | 0 | 2.63 | 0.5895 | 0.5895 | opened
69 | SS 110/35/10 Rostov | 25+20 | 21.343 |  |  | 21.343 | 0 | 21 | -0.343 | -0.343 | closed | 69 | SS 110/35/10 Rostov | 25+20 |  | 23.6 |  |  | 23.6 | 0 | 21 | -2.6 | -2.6 | closed
| Nom. capacity MV, МVА | 25+20 | 1.894 |  |  | 1.894 | 0 | 21 | 19.106 |  |  | 2: Nom. capacity MV, МVА; 3: 25+20; 5: 2.254; Мin. 8: 2.254; Мin. 9: 0; Мin. 10: 21; Мin. 11: 18.746
| Nom. Capacity LV, МVА | 25+20 | 19.449 |  |  | 19.449 | 0 | 21 | 1.551 |  |  |  | Nom. Capacity LV, МVА | 25+20 | 1.897 | 21.346 |  |  | 21.346 | 0 | 21 | -0.346
70 | SS 110/35/10 Technical school | 6,3+6,3 | 8.359 |  |  | 8.359 | 0 | 6.62 | -1.739 | -1.739 | closed | 70 | SS 110/35/10 Technical school | 6,3+6,3 |  | 11.8547 |  |  | 11.8547 | 0 | 6.62 | -5.2348 | -5.2348 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 4.041 |  |  | 4.041 | 0 | 6.62 | 2.579 |  |  | 2: Nom. capacity MV, МVА; 3: 6,3+6,3; 5: 5.4688; Мin. 8: 5.4688; Мin. 9: 0; Мin. 10: 6.62; Мin. 11: 1.1513
| Nom. capacity LV, МVА | 6,3+6,3 | 4.318 |  |  | 4.318 | 0 | 6.62 | 2.302 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.068 | 6.386 |  |  | 6.386 | 0 | 6.62 | 0.234
71 | SS 110/35/10 Uglich | 25+25 | 24.206 |  |  | 24.206 | 0 | 26.25 | 2.044 | 2.044 | opened | 71 | SS 110/35/10 Uglich | 25+25 |  | 26.2015 |  |  | 26.2015 | 0 | 26.25 | 0.0485 | 0.0485 | opened
| Nom. capacidty MV, МVА | 25+25 | 18.6 |  |  | 18.6 | 0 | 26.25 | 7.65 |  |  | 2: Nom. capacidty MV, МVА; 3: 25+25; 5: 18.7405; Мin. 8: 18.7405; Мin. 9: 0; Мin. 10: 26.25; Мin. 11: 7.5095
| Nom. capacity LV, МVА | 25+25 | 5.606 |  |  | 5.606 | 0 | 26.25 | 20.644 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.855 | 7.461 |  |  | 7.461 | 0 | 26.25 | 18.789
72 | SS 110/10 Ustye | 10+10 | 4.915 | 0.32 | 120 | 4.595 | 0 | 10.5 | 5.905 | 5.905 | opened | 72 | SS 110/10 Ustye | 10+10 | 0.266 | 5.181 | 0.32 | 120 | 4.861 | 0 | 10.5 | 5.639 | 5.639 | opened
73 | SS 110/10 Shurskol | 10+10 | 1.976 | 1.18 | 120 | 0.796 | 0 | 10.5 | 9.704 | 9.704 | opened | 73 | SS 110/10 Shurskol | 10+10 | 0.135 | 2.111 | 1.18 | 120 | 0.931 | 0 | 10.5 | 9.569 | 9.569 | opened
74 | SS 110/10 Yur.Sloboda | 10+10 | 9.319 | 0.173 | 120 | 9.146 | 0 | 10.5 | 1.354 | 1.354 | opened | 74 | SS 110/10 Yur.Sloboda | 10+10 | 0.7095 | 10.0285 | 0.173 | 120 | 9.8555 | 0 | 10.5 | 0.6445 | 0.6445 | opened
75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.47 |  |  | 0.47 | 0 | 2.63 | 2.16 | 2.16 | opened | 75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.035 | 0.505 |  |  | 0.505 | 0 | 2.63 | 2.125 | 2.125 | opened
76 | SS 35/6 Batki | 1,6+1,6 | 1.548 |  |  | 1.548 | 0 | 1.68 | 0.132 | 0.132 | opened | 76 | SS 35/6 Batki | 1,6+1,6 | 0.0858 | 1.6338 |  |  | 1.6338 | 0 | 1.68 | 0.0462 | 0.0462 | opened
77 | SS 35/10 Beregovaya | 1.6 | 0.25 | 1.71 | 24 hours | 1.71 | 0 | 1.71 | 1.46 | 1.46 | opened | 77 | SS 35/10 Beregovaya | 1.6 | 0.005 | 0.255 | 1.71 | 24 hours | 1.71 | 0 | 1.71 | 1.455 | 1.455 | opened
78 | SS 35/10 Berendeevo | 2,5+2,5 | 1.428 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | -0.628 | -0.628 | closed | 78 | SS 35/10 Berendeevo | 2,5+2,5 | 0.354 | 1.782 | 0.8 |  | 0.8 | 0 | 0.8 | -0.982 | -0.982 | closed
79 | SS 35/10 Vorzha | 1,8+1,8 | 0.524 | 0.454 | 120 | 0.07 | 0 | 1.89 | 1.82 | 1.82 | opened | 79 | SS 35/10 Vorzha | 1,8+1,8 | 0.277 | 0.801 | 0.454 | 120 | 0.347 | 0 | 1.89 | 1.543 | 1.543 | opened
80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.09 | 0.182 | 120 | 0.908 | 0 | 1.68 | 0.772 | 0.772 | opened | 80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.057 | 1.147 | 0.182 | 120 | 0.965 | 0 | 1.68 | 0.715 | 0.715 | opened
81 | SS 35/10 Glebovo | 2,5+2,5 | 2.049 |  |  | 2.049 | 0 | 2.63 | 0.581 | 0.581 | opened | 81 | SS 35/10 Glebovo | 2,5+2,5 | 1.3286 | 3.3776 |  |  | 3.3776 | 0 | 2.63 | -0.7476 | -0.7476 | closed
82 | SS 35/10 Gorki | 2,5+2,5 | 1.021 |  |  | 1.021 | 0 | 2.63 | 1.609 | 1.609 | opened | 82 | SS 35/10 Gorki | 2,5+2,5 | 0.1515 | 1.1725 |  |  | 1.1725 | 0 | 2.63 | 1.4575 | 1.4575 | opened
83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.165 |  |  | 1.165 | 0 | 1.68 | 0.515 | 0.515 | opened | 83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.037 | 1.202 |  |  | 1.202 | 0 | 1.68 | 0.478 | 0.478 | opened
84 | SS 35/10 Zaozerye | 2,5+1,6 | 1.199 |  |  | 1.199 | 0 | 1.68 | 0.481 | 0.481 | opened | 84 | SS 35/10 Zaozerye | 2,5+1,6 | 0.076 | 1.275 |  |  | 1.275 | 0 | 1.68 | 0.405 | 0.405 | opened
85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 1.511 |  |  | 1.511 | 0 | 2.63 | 1.119 | 1.119 | opened | 85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0485 | 1.5595 |  |  | 1.5595 | 0 | 2.63 | 1.0705 | 1.0705 | opened
86 | SS 35/10 Kibernetik | 6,3+6,3 | 1.835 |  |  | 1.835 | 0 | 6.62 | 4.785 | 4.785 | opened | 86 | SS 35/10 Kibernetik | 6,3+6,3 | 3.0195 | 4.8545 |  |  | 4.8545 | 0 | 6.62 | 1.7655 | 1.7655 | opened
87 | SS 35/10 Klementyevo | 2.5 | 0.342 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.418 | 0.418 | opened | 87 | SS 35/10 Klementyevo | 2.5 | 0.016 | 0.358 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.402 | 0.402 | opened
88 | SS 35/10 Krasnoe | 4,0+4,0 | 1.74 | 0.81 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | opened | 88 | SS 35/10 Krasnoe | 4,0+4,0 | 0.91 | 2.65 | 0.81 | 120 | 1.84 | 0 | 4.2 | 2.36 | 2.36 | opened
89 | SS 35/10 Kulakovo | 2,5+2,5 | 1.675 |  |  | 1.675 | 0 | 2.63 | 0.955 | 0.955 | opened | 89 | SS 35/10 Kulakovo | 2,5+2,5 | 0.206 | 1.881 |  |  | 1.881 | 0 | 2.63 | 0.749 | 0.749 | opened
90 | SS 35/6 Kupan | 2,5+2,5 | 2.398 |  |  | 2.398 | 0 | 2.63 | 0.232 | 0.232 | opened | 90 | SS 35/6 Kupan | 2,5+2,5 | 1.0837 | 3.4817 |  |  | 3.4817 | 0 | 2.63 | -0.85174 | -0.85174 | closed
91 | SS 35/10 Markovo | 2,5+2,5 | 1.224 | 0.36 | 120 | 0.864 | 0 | 2.63 | 1.766 | 1.766 | opened | 91 | SS 35/10 Markovo | 2,5+2,5 | 0.357 | 1.581 | 0.36 | 120 | 1.221 | 0 | 2.63 | 1.409 | 1.409 | opened
92 | SS 35/10 Nagorye | 4,0+4,0 | 3.343 |  |  | 3.343 | 0 | 4.2 | 0.857 | 0.857 | opened | 92 | SS 35/10 Nagorye | 4,0+4,0 | 0.437 | 3.78 |  |  | 3.78 | 0 | 4.2 | 0.42 | 0.42 | opened
93 | SS 35/10 Porechye | 6,3+6,3 | 1.911 | 0.036 | 120 | 1.875 | 0 | 6.62 | 4.745 | 4.745 | opened | 93 | SS 35/10 Porechye | 6,3+6,3 | 0.09 | 2.001 | 0.036 | 120 | 1.965 | 0 | 6.62 | 4.655 | 4.655 | opened
94 | SS 35/10 Pruzhinino | 2,5+2,5 | 1.254 |  |  | 1.254 | 0 | 2.63 | 1.376 | 1.376 | opened | 94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.1735 | 1.4275 |  |  | 1.4275 | 0 | 2.63 | 1.2025 | 1.2025 | opened
95 | SS 35/10 Ramenye | 2,5+2,5 | 0.839 | 0.087 | 120 | 0.752 | 0 | 2.63 | 1.878 | 1.878 | opened | 95 | SS 35/10 Ramenye | 2,5+2,5 | 0.016 | 0.855 | 0.087 | 120 | 0.768 | 0 | 2.63 | 1.862 | 1.862 | opened
96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 1.853 |  |  | 1.853 | 0 | 1.68 | -0.173 | -0.173 | closed | 96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 0.101 | 1.954 |  |  | 1.954 | 0 | 1.68 | -0.274 | -0.274 | closed
97 | SS 35/10 Saraevo | 1+1,6 | 1.291 |  |  | 1.291 | 0 | 1.05 | -0.241 | -0.241 | closed | 97 | SS 35/10 Saraevo | 1+1,6 | 0.697 | 1.988 |  |  | 1.988 | 0 | 1.05 | -0.938 | -0.938 | closed
98 | SS 35/10 Selifontovo | 2,5+2,5 | 1.399 | 0.182 | 120 | 1.217 | 0 | 2.63 | 1.413 | 1.413 | opened | 98 | SS 35/10 Selifontovo | 2,5+2,5 | 0.232 | 1.631 | 0.182 | 120 | 1.449 | 0 | 2.63 | 1.181 | 1.181 | opened
99 | SS 35/10 Semibratovo | 4,0+4,0 | 1.206 | 0.25 | 120 | 0.956 | 0 | 4.2 | 3.244 | 3.244 | opened | 99 | SS 35/10 Semibratovo | 4,0+4,0 | 0 | 1.206 | 0.25 | 120 | 0.956 | 0 | 2.63 | 1.674 | 1.674 | opened
100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.252 |  |  | 1.252 | 0 | 1.68 | 0.428 | 0.428 | opened | 100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.2921 | 1.5441 |  |  | 1.5441 | 0 | 1.68 | 0.1359 | 0.1359 | opened
101 | SS 35/10 Solomidino | 2.5 | 0.612 | 1.18 | 24 hours | 1.18 | 0 | 1.18 | 0.568 | 0.568 | opened | 101 | SS 35/10 Solomidino | 2.5 | 1.5586 | 2.1706 | 1.18 | 24 hours | 1.18 | 0 | 1.18 | -0.9906 | -0.9906 | closed
102 | SS 35/10 Stavotino | 4,0+4,0 | 1.336 | 0.445 | 120 | 0.891 | 0 | 4.2 | 3.309 | 3.309 | opened | 102 | SS 35/10 Stavotino | 4,0+4,0 | 0.8235 | 2.1595 | 0.445 | 120 | 1.7145 | 0 | 4.2 | 2.4855 | 2.4855 | opened
103 | SS 35/10 Urusovo | 2,5+2,5 | 0.529 | 0.053 | 120 | 0.476 | 0 | 2.63 | 2.154 | 2.154 | opened | 103 | SS 35/10 Urusovo | 2,5+2,5 | 0.003 | 0.532 | 0.053 | 120 | 0.479 | 0 | 2.63 | 2.151 | 2.151 | opened
104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.522 |  |  | 0.522 | 0 | 2.63 | 2.108 | 2.108 | opened | 104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.77 | 1.292 |  |  | 1.292 | 0 | 2.63 | 1.338 | 1.338 | opened
105 | SS 35/10 Choporovo | 2,5+2,5 | 0.532 |  |  | 0.532 | 0 | 2.63 | 2.098 | 2.098 | opened | 105 | SS 35/10 Choporovo | 2,5+2,5 | 0.015 | 0.547 |  |  | 0.547 | 0 | 2.63 | 2.083 | 2.083 | opened
106 | SS 35/10 Shchurovo | 2,5+2,5 | 1.07 | 0.27 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened | 106 | SS 35/10 Shchurovo | 2,5+2,5 | 0.022 | 1.092 | 0.27 | 120 | 0.822 | 0 | 2.63 | 1.808 | 1.808 | opened
107 | SS 35/10 Neksans | 10+10 | 1.619 |  |  | 1.619 | 0 | 10.5 | 8.881 | 8.881 | opened | 107 | SS 35/10 Neksans | 10+10 | 0 | 1.619 |  |  | 1.619 | 0 | 10.5 | 8.881 | 8.881 | opened
108 | SS 35/6 Pribrezhnaya | 10+10 | 13.006 |  |  | 13.006 | 0 | 10.5 | -2.506 | -2.506 | closed | 108 | SS 35/6 Pribrezhnaya | 10+10 | 0 | 13.006 |  |  | 13.006 | 0 | 10.5 | -2.506 | -2.506 | closed
109 | SS 110/10 Product pipeline | 6,3+6,3 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened | 109 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened
110 | SS 110/10 Nekouz | 6,3+6,3 | 2.82 | 0.084 | 120 | 2.736 | 0 | 6.62 | 3.884 | 3.884 | opened | 110 | SS 110/10 Nekouz | 6,3+6,3 | 0.026 | 2.846 | 0.084 | 120 | 2.762 | 0 | 6.62 | 3.858 | 3.858 | opened
111 | SS 110/6 Yuzhnaya | 25+25 | 19.89 |  |  | 19.89 | 0 | 26.25 | 6.36 | 6.36 | opened | 111 | SS 110/6 Yuzhnaya | 25+25 | 0.18826 | 20.0783 |  |  | 20.0783 | 0 | 26.25 | 6.1717 | 6.1717 | opened
112 | SS 110/10 Optika | 10+10 | 4.97 | 1.18 | 120 | 3.79 | 0 | 10.5 | 6.71 | 6.71 | opened | 112 | SS 110/10 Optika | 10+10 | 0.333 | 5.303 | 1.18 | 120 | 4.123 | 0 | 10.5 | 6.377 | 6.377 | opened
113 | SS 110/6 Poligrafmash | 16+16 | 8.54 |  |  | 8.54 | 0 | 16.8 | 8.26 | 8.26 | opened | 113 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 8.6 |  |  | 8.6 | 0 | 16.8 | 8.2 | 8.2 | opened
114 | SS 110/6/6 Zapadnaya | 63+63 | 56.01 |  |  | 56.01 | 0 | 66.15 | 10.14 | 10.14 | opened | 114 | SS 110/6/6 Zapadnaya | 63+63 | 1.339 | 57.349 |  |  | 57.349 | 0 | 66.15 | 8.801 | 8.801 | opened
115 | SS 110/35/6 Volzhskaya | 40+40 | 8.3 |  |  | 8.3 | 0 | 42 | 33.7 | 33.7 | opened | 115 | SS 110/35/6 Volzhskaya | 40+40 |  | 8.333 |  |  | 8.333 | 0 | 42 | 33.667 | 33.667 | opened
| Nom. capacity MV, МVА | 40+40 | [9 empty] | 2: Nom. capacity MV, МVА; 3: 40+40
| Nom. capacity LV, МVА | 40+40 | 8.3 |  |  | 7.9 | 0 | 42 | 34.1 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.033 | 8.333 |  |  | 8.333 | 0 | 42 | 33.667
116 | SS 110/35/6 Levoberezhnaya | 16+16 | 14.456 |  |  | 14.456 | 0 | 16.8 | 2.344 | 2.344 | opened | 116 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.271 |  |  | 15.271 | 0 | 16.8 | 1.529 | 1.529 | opened
| Nom. capacity MV, МVА | 16+16 | 9.321 |  |  | 9.321 | 0 | 16.8 | 7.479 |  |  | 2: Nom. capacity MV, МVА; 3: 16+16; 5: 9.857; Мin. 8: 9.857; Мin. 9: 0; Мin. 10: 16.8; Мin. 11: 6.943
| Nom. capacity LV, МVА | 16+16 | 5.135 |  |  | 5.135 | 0 | 16.8 | 11.665 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.279 | 5.414 |  |  | 5.414 | 0 | 16.8 | 11.386
117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 2.2 |  |  | 2.2 | 0 | 7.88 | 5.68 | 5.68 | opened | 117 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 2.205 |  |  | 2.205 | 0 | 7.88 | 5.675 | 5.675 | opened
| Nom. capacity MV, МVА | 7,5+7,5 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43 |  |  | 2: Nom. capacity MV, МVА; 3: 7,5+7,5; 5: 1.45; Мin. 8: 1.45; Мin. 9: 0; Мin. 10: 7.88; Мin. 11: 6.43
| Nom. capacity LV, МVА | 7,5+7,5 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0.005 | 0.755 |  |  | 0.755 | 0 | 7.88 | 7.125
118 | SS 110/6 Dock yard | 10+10 | 4.43 |  |  | 4.43 | 0 | 10.5 | 6.07 | 6.07 | opened | 118 | SS 110/6 Dock yard | 10+10 | 0.056 | 4.486 |  |  | 4.486 | 0 | 10.5 | 6.014 | 6.014 | opened
119 | SS 110/6 Selekhovo | 6,3+6,3 | 4.27 |  |  | 4.27 | 0 | 6.62 | 2.35 | 2.35 | opened | 119 | SS 110/6 Selekhovo | 6,3+6,3 | 0.079 | 4.349 |  |  | 4.349 | 0 | 6.62 | 2.271 | 2.271 | opened
120 | SS 35/6 Kamenniki | 4,0+4,0 | 1.74 |  |  | 1.74 | 0 | 4.2 | 2.46 | 2.46 | opened | 120 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 1.889 |  |  | 1.889 | 0 | 4.2 | 2.311 | 2.311 | opened
121 | SS 35/10 Shashkovo | 1,6+1,6 | 1.03 | 0.532 | 120 | 0.498 | 0 | 1.68 | 1.182 | 1.182 | opened | 121 | SS 35/10 Shashkovo | 1,6+1,6 | 0.231 | 1.261 | 0.532 | 120 | 0.729 | 0 | 1.68 | 0.951 | 0.951 | opened
122 | SS 110/6 Veretye | 25+25 | 19.05 |  |  | 19.05 | 0 | 26.25 | 7.2 | 7.2 | opened | 122 | SS 110/6 Veretye | 25+25 | 1.722 | 20.772 |  |  | 20.772 | 0 | 26.25 | 5.478 | 5.478 | opened
123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.53 | 0.83 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 0.781 | 3.311 | 0.83 | 120 | 2.481 | 0 | 4.2 | 1.719 | 1.719 | opened
124 | SS 35/10 Arefino | 2,5+2,5 | 0.95 | 0.361 | 120 | 0.589 | 0 | 2.63 | 2.041 | 2.041 | opened | 124 | SS 35/10 Arefino | 2,5+2,5 | 0.106 | 1.056 | 0.361 | 120 | 0.695 | 0 | 2.63 | 1.935 | 1.935 | opened
125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.81 |  |  | 0.81 | 0 | 1.68 | 0.87 | 0.87 | opened | 125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.03 | 0.84 |  |  | 0.84 | 0 | 1.68 | 0.84 | 0.84 | opened
126 | SS 35/10 Pokrov | 1,6+1,6 | 0.71 | 0.34 | 120 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | opened | 126 | SS 35/10 Pokrov | 1,6+1,6 | 0 | 0.71 | 0.34 | 120 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | opened
127 | SS 35/10 Anikovo | 2,5+2,5 | 1.13 | 0.29 | 120 | 0.84 | 0 | 2.63 | 1.79 | 1.79 | opened | 127 | SS 35/10 Anikovo | 2,5+2,5 | 0.02 | 1.15 | 0.29 | 120 | 0.86 | 0 | 2.63 | 1.77 | 1.77 | opened
128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.05 |  |  | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened | 128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.307 | 0.357 |  |  | 0.357 | 0 | 2.63 | 2.273 | 2.273 | opened
129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 5.2 |  |  | 5.2 | 0 | 6.62 | 1.42 | 1.42 | opened | 129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.2235 | 5.4235 |  |  | 5.4235 | 0 | 6.62 | 1.1965 | 1.1965 | opened
130 | SS 35/10 Breytovo | 4,0+4,0 | 4.21 |  |  | 4.21 | 0 | 4.2 | -0.01 | -0.01 | closed | 130 | SS 35/10 Breytovo | 4,0+4,0 | 1.062 | 5.272 |  |  | 5.272 | 0 | 4.2 | -1.072 | -1.072 | closed
131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.83 | 0.27 | 120 | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened | 131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.023 | 0.853 | 0.27 | 120 | 0.583 | 0 | 1.68 | 1.097 | 1.097 | opened
132 | SS 35/10 Znamovo | 2,5+2,5 | 0.82 | 0.82 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened | 132 | SS 35/10 Znamovo | 2,5+2,5 | 0 | 0.82 | 0.82 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened
133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened | 133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened
134 | SS 35/10 Zapolye | 2,5+2,5 | 0.45 |  |  | 0.45 | 0 | 2.63 | 2.18 | 2.18 | opened | 134 | SS 35/10 Zapolye | 2,5+2,5 | 0.0905 | 0.5405 |  |  | 0.5405 | 0 | 2.63 | 2.0895 | 2.0895 | opened
135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.43 | 0.843 | 120 | 0.587 | 0 | 1.68 | 1.093 | 1.093 | opened | 135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.12 | 1.55 | 0.843 | 120 | 0.707 | 0 | 1.68 | 0.973 | 0.973 | opened
136 | SS 35/10 Latskoe | 1,6+2,5 | 0.24 | 0.053 | 120 | 0.187 | 0 | 1.68 | 1.493 | 1.493 | opened | 136 | SS 35/10 Latskoe | 1,6+2,5 | 0.01045 | 0.25045 | 0.053 | 120 | 0.19745 | 0 | 1.68 | 1.4826 | 1.4826 | opened
137 | SS 35/10 Borok | 2,5+4,0 | 1.73 | 0.572 | 120 | 1.158 | 0 | 2.63 | 1.472 | 1.472 | opened | 137 | SS 35/10 Borok | 2,5+4,0 | 0.13675 | 1.8667 | 0.572 | 120 | 1.2948 | 0 | 2.63 | 1.3353 | 1.3353 | opened
138 | SS 35/10 Myshkin | 6,3+6,3 | 4.31 | 0.386 | 120 | 3.924 | 0 | 6.62 | 2.696 | 2.696 | opened | 138 | SS 35/10 Myshkin | 6,3+6,3 | 0.638 | 4.948 | 0.386 | 120 | 4.562 | 0 | 6.62 | 2.058 | 2.058 | opened
139 | SS 110/10 Volga | 6,3+5,6 | 1.85 |  |  | 1.85 | 0 | 5.88 | 4.03 | 4.03 | opened | 139 | SS 110/10 Volga | 6,3+5,6 | 0 | 1.85 |  |  | 1.85 | 0 | 5.88 | 4.03 | 4.03 | opened
140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 2 | 0.309 | 120 | 1.691 | 0 | 2.63 | 0.939 | 0.939 | opened | 140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.195 | 2.195 | 0.309 | 120 | 1.886 | 0 | 2.63 | 0.744 | 0.744 | opened
141 | SS 110/35/6 Vostochnaya | 25+25 | 19.27 |  |  | 19.27 | 0 | 26.25 | 6.98 | 6.98 | opened | 141 | SS 110/35/6 Vostochnaya | 25+25 |  | 20.006 |  |  | 20.006 | 0 | 26.25 | 6.244 | 6.244 | opened
| Nom. capacity MV, МVА | 25+25 | 3.688 |  |  | 3.688 | 0 | 26.25 | 22.562 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 4.364; Мin. 8: 4.364; Мin. 9: 0; Мin. 10: 26.25; Мin. 11: 21.886
| Nom. capacity LV, МVА | 25+25 | 15.582 |  |  | 15.582 | 0 | 26.25 | 10.668 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.06 | 15.642 |  |  | 15.642 | 0 | 26.25 | 10.608
142 | SS 110/35/10 Zalesye | 10+10 | 9.362 | 1.13 | 120 | 8.232 | 0 | 10.5 | 2.268 | 2.268 | opened | 142 | SS 110/35/10 Zalesye | 10+10 |  | 9.412 | 1.13 | 120 | 8.282 | 0 | 10.5 | 2.218 | 2.218 | opened
| Nom. capacity MV, МVА | 10+10 | 2.187 |  |  | 2.187 | 0 | 10.5 | 8.313 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 2.187; Мin. 8: 2.187; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 8.313
| Nom. capacity LV, МVА | 10+10 | 7.175 | 1.13 | 120 | 6.045 | 0 | 10.5 | 4.455 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.05 | 7.225 | 1.13 | 120 | 6.095 | 0 | 10.5 | 4.405
143 | SS 110/10 Lugovaya | 6,3+6,3 | 2.93 |  |  | 2.93 | 0 | 6.62 | 3.69 | 3.69 | opened | 143 | SS 110/10 Lugovaya | 6,3+6,3 | 0.058 | 2.988 |  |  | 2.988 | 0 | 6.62 | 3.632 | 3.632 | opened
144 | SS 110/35/10 Lom | 10+10 | 8.743 | 1.54 | 120 | 7.203 | 0 | 10.5 | 3.297 | 3.297 | opened | 144 | SS 110/35/10 Lom | 10+10 |  | 9.6719 | 1.54 | 120 | 8.1319 | 0 | 10.5 | 2.3681 | 2.3681 | opened
| Nom. capacity MV, МVА | 10+10 | 6.877 |  |  | 6.877 | 0 | 10.5 | 3.623 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 7.5155; Мin. 8: 7.5155; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 2.9845
| Nom. capacity LV, МVА | 10+10 | 1.866 | 1.54 | 120 | 0.326 | 0 | 10.5 | 10.174 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.2904 | 2.1564 | 1.54 | 120 | 0.6164 | 0 | 10.5 | 9.8836
145 | SS 35/10 Varegovo | 2,5+1,6 | 0.88 |  |  | 0.88 | 0 | 1.68 | 0.8 | 0.8 | opened | 145 | SS 35/10 Varegovo | 2,5+1,6 | 0.108 | 0.988 |  |  | 0.988 | 0 | 1.68 | 0.692 | 0.692 | opened
146 | SS 110/35/10 Shestikhino | 10+10 | 8.57 | 0.306 | 120 | 8.264 | 0 | 10.5 | 2.236 | 2.236 | opened | 146 | SS 110/35/10 Shestikhino | 10+10 |  | 9.9533 | 0.306 | 120 | 9.6472 | 0 | 10.5 | 0.85275 | 0.85275 | opened
| Nom. capacity MV, МVА | 10+10 | 7.809 |  |  | 7.809 | 0 | 10.5 | 2.691 |  |  | 2: Nom. capacity MV, МVА; 3: 10+10; 5: 9.0582; Мin. 8: 9.0582; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 1.4418
| Nom. capacity LV, МVА | 10+10 | 0.761 | 0.306 | 120 | 0.455 | 0 | 10.5 | 10.045 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.134 | 0.895 | 0.306 | 120 | 0.589 | 0 | 10.5 | 9.911
147 | SS 110/35/10 Kryukovo | 6.3 | 2.327 | 0.87 | 24 hours | 1.457 | 0 | 6.62 | 5.163 | 4.543 | opened | 147 | SS 110/35/10 Kryukovo | 6.3 |  | 2.646 | 0.87 | 24 hours | 1.776 | 0 | 6.62 | 4.844 | 4.224 | opened
| Nom. capacidty MV, МVА | 6.3 | 2.077 |  |  | 2.077 | 0 | 6.62 | 4.543 |  |  | 2: Nom. capacidty MV, МVА; 3: 6.3; 5: 2.396; Мin. 8: 2.396; Мin. 9: 0; Мin. 10: 6.62; Мin. 11: 4.224
| Nom. capacity LV, МVА | 6.3 | 0.25 | 0.87 | 24 hours | -0.62 | 0 | 6.62 | 7.24 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.25 | 0.87 | 24 hours | -0.62 | 0 | 6.62 | 7.24
148 | SS 35/10 Beloe | 2.5 | 0.74 | 1.58 | 24 hours | 1.58 | 0 | 1.58 | 0.84 | 0.84 | opened | 148 | SS 35/10 Beloe | 2.5 | 0 | 0.74 | 1.58 | 24 hours | 1.58 | 0 | 1.58 | 0.84 | 0.84 | opened
149 | SS 110/35/10 Glebovo | 10 | 6.473 | 0.654 | 24 hours | 5.819 | 0 | 10.5 | 4.681 | 4.681 | opened | 149 | SS 110/35/10 Glebovo | 10 |  | 7.9935 | 0.654 | 24 hours | 7.3395 | 0 | 10.5 | 3.1605 | 3.1605 | opened
| Nom. capacity MV, МVА | 10 | 3.485 |  |  | 3.485 | 0 | 10.5 | 7.015 |  |  | 2: Nom. capacity MV, МVА; 3: 10; 5: 3.9955; Мin. 8: 3.9955; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 6.5045
| Nom. capacity LV, МVА | 10 | 2.988 | 0.654 | 24 hours | 2.334 | 0 | 10.5 | 8.166 |  |  |  | Nom. capacity LV, МVА | 10 | 1.01 | 3.998 | 0.654 | 24 hours | 3.344 | 0 | 10.5 | 7.156
150 | SS 35/10 Ermakovo | 1.6 | 1.02 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | -0.15 | -0.15 | closed | 150 | SS 35/10 Ermakovo | 1.6 | 0.047 | 1.067 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | -0.197 | -0.197 | closed
151 | SS 35/10 Milyushino | 1.6 | 0.78 | 1.053 | 24 hours | 1.053 | 0 | 1.053 | 0.273 | 0.273 | opened | 151 | SS 35/10 Milyushino | 1.6 | 0.151 | 0.931 | 1.053 | 24 hours | 1.053 | 0 | 1.053 | 0.122 | 0.122 | opened
152 | SS 35/10 Sutka | 2.5 | 0.68 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.19 | 0.19 | opened | 152 | SS 35/10 Sutka | 2.5 | 0.022 | 0.702 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.168 | 0.168 | opened
153 | SS 35/10 Sit | 1.6 | 0.55 | 0.55 | 24 hours | 0.55 | 0 | 0.55 | 0 | 0 | opened | 153 | SS 35/10 Sit | 1.6 | 0.2223 | 0.7723 | 0.55 | 24 hours | 0.55 | 0 | 0.55 | -0.2223 | -0.2223 | closed
154 | SS 35/10 Gorelovo | 1.6 | 0.67 | 0.78 | 24 hours | 0.78 | 0 | 0.78 | 0.11 | 0.11 | opened | 154 | SS 35/10 Gorelovo | 1.6 | 0.251 | 0.921 | 0.78 | 24 hours | 0.78 | 0 | 0.78 | -0.141 | -0.141 | closed
155 | SS 35/6 Pishchalkino | 1.6 | 0.89 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.79 | 0.79 | opened | 155 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.89 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.79 | 0.79 | opened
156 | SS 35/6 Varegovo | 1.6 | 0.258 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.422 | 1.422 | opened | 156 | SS 35/6 Varegovo | 1.6 | 0 | 0.258 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.422 | 1.422 | opened
| Total: | 2618.6 | 907.904 | [8 empty] | 2: Total:; 3: 2618.6; 5: 1060.6059
| deficit | [8 empty] | 17.385 |  | 2: deficit; Мin. 12: -57.0281
| proficit | [8 empty] | 511.476 |  | 2: proficit; Мin. 12: 389.9747
E.V. Turapin