## Смоленскэнерго
[9 empty] | table 1 | [11 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Current deficit/ proficit, MVA |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main substation, MVA | Expected dificit / proficit, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.24 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.46 | 0.46 | opened | 1 | Gerchiki 35/10 | 2.5 | 0.4 | 0.64 | 0.7 | 24 hours | -0.06 | 0 | 0.7 | 0.06 | 0.06 | opened
2 | Verkhovye 35/10 | 4 | 0.59 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.77 | 0.77 | opened | 2 | Verkhovye 35/10 | 4 | 0 | 0.59 | 1.36 | 24 hours | -0.77 | 0 | 1.36 | 0.77 | 0.77 | opened
3 | Neykovo 35/10 | 2.5 | 0.14 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.59 | 1.59 | opened | 3 | Neykovo 35/10 | 2.5 | 0 | 0.14 | 1.73 | 24 hours | -1.59 | 0 | 1.73 | 1.59 | 1.59 | opened
4 | Merlino 110/35/10 | 6.3 | 0.34 | 0.34 | 24 hours | 0.34 | 0 | 0.34 | 0 | 0 | opened | 4 | Merlino 110/35/10 | 6.3 | 0 | 0.34 | 0.34 | 24 hours | 0 | 0 | 0.34 | 0 | 0 | opened
| Nom. capacity MV, МVА | 6.3 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0 | 0.1 | 0.1 | 24 hours | 0 | 0 | 0.1 | 0
| Nom. capacity LV, МVА | 6.3 | 0.24 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.24 | 0.24 | 24 hours | 0 | 0 | 0.24 | 0
5 | Belyaevo 35/10 | 1.6 | 0.3 | 2.11 | 24 hours | 2.11 | 0 | 2.11 | 1.81 | 1.81 | opened | 5 | Belyaevo 35/10 | 1.6 | 0 | 0.3 | 2.11 | 24 hours | -1.81 | 0 | 2.11 | 1.81 | 1.81 | opened
6 | Zaozerye 35/10 | 1.6 | 0.17 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.68 | 0.68 | opened | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.17 | 0.85 | 24 hours | -0.68 | 0 | 0.85 | 0.68 | 0.68 | opened
7 | Selezni 35/10 | 2.5 | 0.37 | 2.21 | 24 hours | 2.21 | 0 | 2.21 | 1.84 | 1.84 | opened | 7 | Selezni 35/10 | 2.5 | 0 | 0.37 | 2.21 | 24 hours | -1.84 | 0 | 2.21 | 1.84 | 1.84 | opened
8 | Logovo 110/10 | 6.3 | 0.4 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.96 | 0.96 | opened | 8 | Logovo 110/10 | 6.3 | 0 | 0.4 | 1.36 | 24 hours | -0.96 | 0 | 1.36 | 0.96 | 0.96 | opened
9 | Dubrovka 35/10 | 2.5 | 0.24 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 1.12 | 1.12 | opened | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.34 | 1.36 | 24 hours | -1.02 | 0 | 1.36 | 1.02 | 1.02 | opened
10 | Svistovichi 35/10 | 2.5 | 0.28 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.57 | 0.57 | opened | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.28 | 0.85 | 24 hours | -0.57 | 0 | 0.85 | 0.57 | 0.57 | opened
11 | Elsha 35/10 | 1.6 | 0.09 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.76 | 0.76 | opened | 11 | Elsha 35/10 | 1.6 | 0 | 0.09 | 0.85 | 24 hours | -0.76 | 0 | 0.85 | 0.76 | 0.76 | opened
12 | Sapsho 35/10 | 4 | 0.88 | 2.12 | 24 hours | 2.12 | 0 | 2.12 | 1.24 | 1.24 | opened | 12 | Sapsho 35/10 | 4 | 0.18 | 1.06 | 2.12 | 24 hours | -1.06 | 0 | 2.12 | 1.06 | 1.06 | opened
13 | Divo 110/10 | 2.5 | 0.6 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.25 | 0.25 | opened | 13 | Divo 110/10 | 2.5 | 0.14 | 0.74 | 0.85 | 24 hours | -0.11 | 0 | 0.85 | 0.11 | 0.11 | opened
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 24 hours | 1.02 | 0 | 1.02 | 0.57 | 0.57 | opened | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.45 | 1.02 | 24 hours | -0.57 | 0 | 1.02 | 0.57 | 0.57 | opened
15 | Zamoshye 35/10 | 2.5 | 0.07 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.61 | 0.61 | opened | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.07 | 0.68 | 24 hours | -0.61 | 0 | 0.68 | 0.61 | 0.61 | opened
16 | Loino 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 16 | Loino 35/10 | 2.5 | 0 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
17 | Rokot 35/10 | 2.5 | 0.29 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.01 | 1.01 | opened | 17 | Rokot 35/10 | 2.5 | 0 | 0.29 | 1.3 | 24 hours | -1.01 | 0 | 1.3 | 1.01 | 1.01 | opened
18 | Nikontsy 35/10 | 2.5 | 0.15 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.7 | 0.7 | opened | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.15 | 0.85 | 24 hours | -0.7 | 0 | 0.85 | 0.7 | 0.7 | opened
19 | Batishchevo 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.09 | 1.73 | 24 hours | -1.64 | 0 | 1.73 | 1.64 | 1.64 | opened
20 | Vasino 35/10 | 2.5 | 0.31 | 0 | 24 hours | 0 | 0 | 0 | -0.31 | -0.31 | closed | 20 | Vasino 35/10 | 2.5 | 0 | 0.31 | 0 | 24 hours | 0.31 | 0 | 0 | -0.31 | -0.31 | closed
21 | Bulgakovo 35/10 | 2.5 | 0.26 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.47 | 1.47 | opened | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.26 | 1.73 | 24 hours | -1.47 | 0 | 1.73 | 1.47 | 1.47 | opened
22 | Spas-Ugly 35/10 | 1.6 | 0.16 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.52 | 0.52 | opened | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.16 | 0.68 | 24 hours | -0.52 | 0 | 0.68 | 0.52 | 0.52 | opened
23 | Tretyakovo 35/10 | 4 | 0.25 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.3 | 2.3 | opened | 23 | Tretyakovo 35/10 | 4 | 0 | 0.25 | 2.55 | 24 hours | -2.3 | 0 | 2.55 | 2.3 | 2.3 | opened
24 | Velisto 35/10 | 2.5 | 0.09 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.21 | 1.21 | opened | 24 | Velisto 35/10 | 2.5 | 0 | 0.09 | 1.3 | 24 hours | -1.21 | 0 | 1.3 | 1.21 | 1.21 | opened
25 | Baturino 35/10 | 1.6 | 0.1 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.75 | 0.75 | opened | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.28 | 0.85 | 24 hours | -0.57 | 0 | 0.85 | 0.57 | 0.57 | opened
26 | Pechatniki 35/10 | 2.5 | 0.34 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.12 | 3.12 | opened | 26 | Pechatniki 35/10 | 2.5 | 0 | 0.34 | 3.46 | 24 hours | -3.12 | 0 | 3.46 | 3.12 | 3.12 | opened
27 | Garistovo 35/10 | 1.6 | 0.18 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.67 | 0.67 | opened | 27 | Garistovo 35/10 | 1.6 | 0 | 0.18 | 0.85 | 24 hours | -0.67 | 0 | 0.85 | 0.67 | 0.67 | opened
28 | Bezzaboty 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.09 | 1.73 | 24 hours | -1.64 | 0 | 1.73 | 1.64 | 1.64 | opened
29 | Vysokoe 35/10 | 2.5 | 0.2 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.35 | 2.35 | opened | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.2 | 2.55 | 24 hours | -2.35 | 0 | 2.55 | 2.35 | 2.35 | opened
30 | Zaytsevo 35/10 | 1.6 | 0.35 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.5 | 0.5 | opened | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.35 | 0.85 | 24 hours | -0.5 | 0 | 0.85 | 0.5 | 0.5 | opened
31 | Saveevo 35/10 | 2.5 | 0.46 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.39 | 0.39 | opened | 31 | Saveevo 35/10 | 2.5 | 0 | 0.46 | 0.85 | 24 hours | -0.39 | 0 | 0.85 | 0.39 | 0.39 | opened
32 | Gorenovo 35/10 | 1.6 | 0.26 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.29 | 2.29 | opened | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.26 | 2.55 | 24 hours | -2.29 | 0 | 2.55 | 2.29 | 2.29 | opened
33 | Shpunty 35/10 | 2.5 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 33 | Shpunty 35/10 | 2.5 | 0.42 | 0.65 | 0.85 | 24 hours | -0.2 | 0 | 0.85 | 0.2 | 0.2 | opened
34 | Kadino 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 34 | Kadino 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
35 | Стегримово 35/10 | 2.5 | 0.08 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.81 | 2.81 | opened | 35 | Стегримово 35/10 | 2.5 | 0 | 0.08 | 2.89 | 24 hours | -2.81 | 0 | 2.89 | 2.81 | 2.81 | opened
36 | Zhukovo 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
37 | Mikshino 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 37 | Mikshino 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
38 | Petrovichi 35/10 | 2.5 | 0.18 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.37 | 2.37 | opened | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.18 | 2.55 | 24 hours | -2.37 | 0 | 2.55 | 2.37 | 2.37 | opened
39 | Mikulichi 35/10 | 2.5 | 0.51 | 4.59 | 24 hours | 4.59 | 0 | 4.59 | 4.08 | 4.08 | opened | 39 | Mikulichi 35/10 | 2.5 | 0.07 | 0.58 | 4.59 | 24 hours | -4.01 | 0 | 4.59 | 4.01 | 4.01 | opened
40 | Nedeykovichi 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
41 | Posyolki 110/35/10 | 6.3 | 0.71 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.23 | 0.23 | opened | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.71 | 0.94 | 24 hours | -0.23 | 0 | 0.94 | 0.23 | 0.23 | opened
42 | Kuzmichi 35/10 | 2.5 | 0.34 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.39 | 1.39 | opened | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.34 | 1.73 | 24 hours | -1.39 | 0 | 1.73 | 1.39 | 1.39 | opened
43 | Maksheevo 110/10 | 6.3 | 0.41 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.14 | 2.14 | opened | 43 | Maksheevo 110/10 | 6.3 | 0 | 0.41 | 2.55 | 24 hours | -2.14 | 0 | 2.55 | 2.14 | 2.14 | opened
44 | Putkovo 35/10 | 1.8 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 44 | Putkovo 35/10 | 1.8 | 0.06 | 0.29 | 0.85 | 24 hours | -0.56 | 0 | 0.85 | 0.56 | 0.56 | opened
45 | Uspenskoe 35/10 | 2.5 | 0.49 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.06 | 2.06 | opened | 45 | Uspenskoe 35/10 | 2.5 | 0 | 0.49 | 2.55 | 24 hours | -2.06 | 0 | 2.55 | 2.06 | 2.06 | opened
46 | Kalpita 35/10 | 1.6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 46 | Kalpita 35/10 | 1.6 | 0 | 0.06 | 0.85 | 24 hours | -0.79 | 0 | 0.85 | 0.79 | 0.79 | opened
47 | Kasnya 110/10 | 2.5 | 0.32 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.14 | 3.14 | opened | 47 | Kasnya 110/10 | 2.5 | 0 | 0.32 | 3.46 | 24 hours | -3.14 | 0 | 3.46 | 3.14 | 3.14 | opened
48 | Akatovo 35/10 | 1.6 | 1.01 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 1.88 | 1.88 | opened | 48 | Akatovo 35/10 | 1.6 | 1.2 | 2.21 | 2.89 | 24 hours | -0.68 | 0 | 2.89 | 0.68 | 0.68 | opened
49 | Gorki 35/10 | 1.6 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 49 | Gorki 35/10 | 1.6 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.06 | 0.06 | opened | 50 | Druzhba 35/10 | 2.5 | 0 | 0.79 | 0.85 | 24 hours | -0.06 | 0 | 0.85 | 0.06 | 0.06 | opened
51 | NS-21 110/10 | 16 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened
52 | NS-22 110/35/10 | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0 | 0 | opened | 52 | NS-22 110/35/10 | 25 | 1.32 | 3.41 | 3.41 | 24 hours | 0 | 0 | 3.41 | 0 | 0 | opened
| Nom. capacity MV, МVА | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 1.32 | 3.41 | 3.41 | 24 hours | 0 | 0 | 3.41 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.47 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.99 | 2.99 | opened | 53 | Shuyskoe 35/10 | 2.5 | 0.05 | 0.52 | 3.46 | 24 hours | -2.94 | 0 | 3.46 | 2.94 | 2.94 | opened
54 | Torbeevo 110/10 | 6.3 | 0.35 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.54 | 2.54 | opened | 54 | Torbeevo 110/10 | 6.3 | 0.08 | 0.43 | 2.89 | 24 hours | -2.46 | 0 | 2.89 | 2.46 | 2.46 | opened
55 | Leuzdovo 35/10 | 1 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 55 | Leuzdovo 35/10 | 1 | 0.3 | 0.42 | 0.68 | 24 hours | -0.26 | 0 | 0.68 | 0.26 | 0.26 | opened
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.56 | 1.56 | opened | 56 | Maltsevo 35/10 | 2.5 | 0.01 | 0.18 | 1.73 | 24 hours | -1.55 | 0 | 1.73 | 1.55 | 1.55 | opened
57 | Avrora 35/10 | 2.5 | 0.09 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.59 | 0.59 | opened | 57 | Avrora 35/10 | 2.5 | 2.77 | 2.86 | 0.68 | 24 hours | 2.18 | 0 | 0.68 | -2.18 | -2.18 | closed
58 | Bekhteevo 35/10 | 2.5 | 0.08 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.6 | 0.6 | opened | 58 | Bekhteevo 35/10 | 2.5 | 0.07 | 0.15 | 0.68 | 24 hours | -0.53 | 0 | 0.68 | 0.53 | 0.53 | opened
59 | Sereda 35/10 | 2.5 | 0.38 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.3 | 0.3 | opened | 59 | Sereda 35/10 | 2.5 | 0 | 0.38 | 0.68 | 24 hours | -0.3 | 0 | 0.68 | 0.3 | 0.3 | opened
60 | Mikhali 35/10 | 2.5 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 60 | Mikhali 35/10 | 2.5 | 0 | 0.06 | 0.85 | 24 hours | -0.79 | 0 | 0.85 | 0.79 | 0.79 | opened
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 24 hours | 0 | 0 | 0 | -0.06 | -0.06 | closed | 61 | Mytishino 35/10 | 1.6 | 0 | 0.06 | 0 | 24 hours | 0.06 | 0 | 0 | -0.06 | -0.06 | closed
62 | Zakharyevskoe 35/10 | 1.6 | 0.19 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.66 | 0.66 | opened | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.19 | 0.85 | 24 hours | -0.66 | 0 | 0.85 | 0.66 | 0.66 | opened
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 63 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 24 hours | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
64 | Baskakovka 35/10 | 4 | 0.21 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.52 | 1.52 | opened | 64 | Baskakovka 35/10 | 4 | 0 | 0.21 | 1.73 | 24 hours | -1.52 | 0 | 1.73 | 1.52 | 1.52 | opened
65 | Ekimtsevo 110/10 | 2.5 | 0.36 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.37 | 1.37 | opened | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0.36 | 1.73 | 24 hours | -1.37 | 0 | 1.73 | 1.37 | 1.37 | opened
Two-transformer substations | [11 empty] | 1: Two-transformer substations
66 | Smolensk 1 (FPC) 110/35/6 | 40+40 | 41.67 | 5.68 | 120 | 35.99 | 0 | 42 | 6.01 | 6.01 | opened | 66 | Smolensk 1 (FPC) 110/35/6 | 40+40 | 17.23 | 58.9 | 13.28 | 120 | 45.62 | 0 | 42 | -3.62 | -3.62 | closed
| Nom. capavity MV, МVА | 40+40 | 4.9 | 3.76 |  | 1.14 | 0 | 42 | 40.86 |  |  |  | Nom. capavity MV, МVА | 40+40 | 6.46 | 11.36 | 11.36 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 36.77 | 1.92 | 120 | 34.85 | 0 | 42 | 7.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 10.77 | 47.54 | 1.92 | 120 | 45.62 | 0 | 42 | -3.62
67 | Water intake 35/6 | 4+4 | 2.93 | 1.2 | 120 | 1.73 | 0 | 4.2 | 2.47 | 2.47 | opened | 67 | Water intake 35/6 | 4+4 | 2.4 | 5.33 | 1.2 | 120 | 4.13 | 0 | 4.2 | 0.07 | 0.07 | opened
68 | Tychinino 35/10 | 4+4 | 1.1 | 0.91 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened | 68 | Tychinino 35/10 | 4+4 | 0.13 | 1.23 | 0.91 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | opened
69 | Ryabtsevo 35/10 | 4+4 | 2.4 | 0 | 120 | 2.4 | 0 | 4.2 | 1.8 | 1.8 | opened | 69 | Ryabtsevo 35/10 | 4+4 | 2.72 | 5.12 | 0 | 120 | 5.12 | 0 | 4.2 | -0.92 | -0.92 | closed
70 | Smolensk 2 110/6 | 40+40 | 16.21 | 6.41 | 120 | 9.8 | 0 | 42 | 32.2 | 32.2 | opened | 70 | Smolensk 2 110/6 | 40+40 | 2.53 | 18.74 | 6.41 | 120 | 12.33 | 0 | 42 | 29.67 | 29.67 | opened
71 | Vostochnaya 110/6 | 25+16 | 5.71 | 0 | 120 | 5.71 | 0 | 16.8 | 11.09 | 11.09 | opened | 71 | Vostochnaya 110/6 | 25+16 | 4.7 | 10.41 | 0 | 120 | 10.41 | 0 | 16.8 | 6.39 | 6.39 | opened
72 | Diffuzion 110/6 | 25+25 | 14.69 | 1.06 | 120 | 13.63 | 0 | 26.25 | 12.62 | 12.62 | opened | 72 | Diffuzion 110/6 | 25+25 | 18.8 | 33.49 | 1.06 | 120 | 32.43 | 0 | 26.25 | -6.18 | -6.18 | closed
73 | Zavodskaya 110/35/10 | 16+16 | 17.31 | 17.07 | 120 | 0.24 | 0 | 16.8 | 16.56 | 13.12 | opened | 73 | Zavodskaya 110/35/10 | 16+16 | 15.89 | 33.2 | 25.02 | 120 | 8.18 | 0 | 16.8 | 8.62 | 8.62 | opened
| Nom. capacity MV, МVА | 16+16 | 15.1 | 11.42 |  | 3.68 | 0 | 16.8 | 13.12 |  |  |  | Nom. capacity MV, МVА | 16+16 | 4.27 | 19.37 | 19.37 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.21 | 5.65 | 120 | -3.44 | 0 | 16.8 | 20.24 |  |  |  | Nom. capacity LV, МVА | 16+16 | 11.62 | 13.83 | 5.65 | 120 | 8.18 | 0 | 16.8 | 8.62
74 | Yasennaya 35/6 | 10+10 | 8.98 | 0 | 120 | 8.98 | 0 | 10.5 | 1.52 | 1.52 | opened | 74 | Yasennaya 35/6 | 10+10 | 1.29 | 10.27 | 0 | 120 | 10.27 | 0 | 10.5 | 0.23 | 0.23 | opened
75 | Gnezodovo 35/6 | 7,5+7,5 | 4.32 | 0.42 | 120 | 3.9 | 0 | 7.875 | 3.975 | 3.975 | opened | 75 | Gnezodovo 35/6 | 7,5+7,5 | 3.05 | 7.37 | 0.42 | 120 | 6.95 | 0 | 7.875 | 0.925 | 0.925 | opened
76 | Zapadnaya 110/6 | 25+16 | 13.58 | 0.63 | 120 | 12.95 | 0 | 16.8 | 3.85 | 3.85 | opened | 76 | Zapadnaya 110/6 | 25+16 | 8.5 | 22.08 | 0.63 | 120 | 21.45 | 0 | 16.8 | -4.65 | -4.65 | closed
77 | Katyn 2 110/35/10 | 10+16 | 4.58 | 2.59 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened | 77 | Katyn 2 110/35/10 | 10+16 | 9.4 | 13.98 | 7.08 | 120 | 6.9 | 0 | 10.5 | 3.6 | 3.6 | opened
| Nom. capacity MV, МVА | 10+16 | 2.59 | 2.59 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 4.49 | 7.08 | 7.08 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.99 | 0 | 120 | 1.99 | 0 | 10.5 | 8.51 |  |  |  | Nom. capacity LV, МVА | 10+16 | 4.91 | 6.9 | 0 | 120 | 6.9 | 0 | 10.5 | 3.6
78 | Katyn 1 35/10 | 4+4 | 1.57 | 0.05 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | opened | 78 | Katyn 1 35/10 | 4+4 | 1.65 | 3.22 | 0.05 | 120 | 3.17 | 0 | 4.2 | 1.03 | 1.03 | opened
79 | Lubnya 35/10 | 4+4 | 1.33 | 0.13 | 120 | 1.2 | 0 | 4.2 | 3 | 3 | opened | 79 | Lubnya 35/10 | 4+4 | 2.11 | 3.44 | 0.13 | 120 | 3.31 | 0 | 4.2 | 0.89 | 0.89 | opened
80 | Kozino 110/35/10 | 10+10 | 8.41 | 6.51 | 120 | 1.9 | 0 | 10.5 | 8.6 | 8.6 | opened | 80 | Kozino 110/35/10 | 10+10 | 12.01 | 20.42 | 1.03 | 120 | 19.39 | 0 | 10.5 | -8.89 | -8.89 | closed
| Nom. capacity MV, МVА | 10+10 | 6.5 | 6.5 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 8.93 | 15.43 | 1.02 |  | 14.41 | 0 | 10.5 | -3.91
| Nom. capacity LV, МVА | 10+10 | 1.91 | 0.01 | 120 | 1.9 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity LV, МVА | 10+10 | 3.08 | 4.99 | 0.01 | 120 | 4.98 | 0 | 10.5 | 5.52
81 | Odintsovo 35/10 | 6,3+6,3 | 4.55 | 2.15 | 120 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened | 81 | Odintsovo 35/10 | 6,3+6,3 | 7.02 | 11.57 | 2.15 | 120 | 9.42 | 0 | 6.615 | -2.805 | -2.805 | closed
82 | Trudilovo 35/10 | 2,5+2,5 | 1.29 | 0.08 | 120 | 1.21 | 0 | 2.625 | 1.415 | 1.415 | opened | 82 | Trudilovo 35/10 | 2,5+2,5 | 0.78 | 2.07 | 0.08 | 120 | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened
83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 |  | 0 | 0 | 42 | 42 | 42 | opened | 83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 | 0 |  | 0 | 0 | 42 | 42 | 42 | opened
84 | Pronino 110/35/6 | 10+10 | 6.24 | 4.67 | 120 | 1.57 | 0 | 10.5 | 8.93 | 8.93 | opened | 84 | Pronino 110/35/6 | 10+10 | 3.52 | 9.76 | 7.24 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | opened
| Nom. capacity MV, МVА | 10+10 | 3.48 | 3.48 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.57 | 6.05 | 6.05 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.76 | 1.19 | 120 | 1.57 | 0 | 10.5 | 8.93 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.95 | 3.71 | 1.19 | 120 | 2.52 | 0 | 10.5 | 7.98
85 | Olsha 35/10 | 2,5+2,5 | 0.92 | 0 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 85 | Olsha 35/10 | 2,5+2,5 | 2.01 | 2.93 | 0 | 120 | 2.93 | 0 | 2.625 | -0.305 | -0.305 | closed
86 | Krasny bor 35/6 | 4+4 | 2.58 | 0 | 120 | 2.58 | 0 | 4.2 | 1.62 | 1.62 | opened | 86 | Krasny bor 35/6 | 4+4 | 0.54 | 3.12 | 0 | 120 | 3.12 | 0 | 4.2 | 1.08 | 1.08 | opened
87 | Severnaya 110/35/6 | 25+25 | 17.69 | 6.13 | 120 | 11.56 | 0 | 26.25 | 14.69 | 14.69 | opened | 87 | Severnaya 110/35/6 | 25+25 | 15.5 | 33.19 | 15.22 | 120 | 17.97 | 0 | 26.25 | 8.28 | 8.28 | opened
| Nom. capacity MV, МVА | 25+25 | 3.54 | 3.54 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 12.63 | 12.63 | 12.63 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 14.15 | 2.59 | 120 | 11.56 | 0 | 26.25 | 14.69 |  |  |  | Nom. capacity LV, МVА | 25+25 | 2.87 | 17.02 | 2.59 | 120 | 14.43 | 0 | 26.25 | 11.82
88 | Peсhersk 35/6 | 4+4 | 2.59 | 0.34 | 120 | 2.25 | 0 | 4.2 | 1.95 | 1.95 | opened | 88 | Peсhersk 35/6 | 4+4 | 11.06 | 13.65 | 0.34 | 120 | 13.31 | 0 | 4.2 | -9.11 | -9.11 | closed
89 | Kolodnya 35/6 | 6,3+4 | 2.56 | 0 | 120 | 2.56 | 0 | 4.2 | 1.64 | 1.64 | opened | 89 | Kolodnya 35/6 | 6,3+4 | 1.01 | 3.57 | 0 | 120 | 3.57 | 0 | 4.2 | 0.63 | 0.63 | opened
90 | Tsentralnaya 110/10/6 | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18 | 11.18 | opened | 90 | Tsentralnaya 110/10/6 | 25+25 | 2.96 | 23.79 | 7.66 | 120 | 16.13 | 0 | 26.25 | 10.12 | 10.12 | opened
| Nom. capacity MV, МVА | 25+25 | 0 | 0 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 1.9 | 1.9 | 1.9 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.06 | 21.89 | 5.76 | 120 | 16.13 | 0 | 26.25 | 10.12
91 | Chernushki 110/10/6 | 25+25 | 18.02 | 2.12 | 120 | 15.9 | 0 | 26.25 | 10.35 | 10.35 | opened | 91 | Chernushki 110/10/6 | 25+25 | 10.5 | 28.52 | 2.12 | 120 | 26.4 | 0 | 26.25 | -0.15 | -0.15 | closed
| Nom. capacity MV, МVА | 25+25 | 6.43 | 0 |  | 6.43 | 0 | 26.25 | 19.82 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.92 | 12.35 | 0 |  | 12.35 | 0 | 26.25 | 13.9
| Nom. Capacity LV, МVА | 25+25 | 11.59 | 2.12 | 120 | 9.47 | 0 | 26.25 | 16.78 |  |  |  | Nom. Capacity LV, МVА | 25+25 | 4.58 | 16.17 | 2.12 | 120 | 14.05 | 0 | 26.25 | 12.2
92 | Yuzhnaya 110/35/6 | 40+40 | 32.46 | 7.03 | 120 | 25.43 | 0 | 42 | 16.57 | 16.57 | opened | 92 | Yuzhnaya 110/35/6 | 40+40 | 21.51 | 53.97 | 9.97 | 120 | 44 | 0 | 42 | -2 | -2 | closed
| Nom. capacity MV, МVА | 40+40 | 1.31 | 1.31 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, МVА | 40+40 | 2.94 | 4.25 | 4.25 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 31.15 | 5.72 | 120 | 25.43 | 0 | 42 | 16.57 |  |  |  | Nom. capacity LV, МVА | 40+40 | 18.57 | 49.72 | 5.72 | 120 | 44 | 0 | 42 | -2
93 | Karyernaya 110/35/6 | 16+16 | 4.43 | 2.39 | 120 | 2.04 | 0 | 16.8 | 14.76 | 14.76 | opened | 93 | Karyernaya 110/35/6 | 16+16 | 5.25 | 9.68 | 5.34 | 120 | 4.34 | 0 | 16.8 | 12.46 | 12.46 | opened
| Nom. capacity MV, МВА | 16+16 | 2.39 | 2.39 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МВА | 16+16 | 2.95 | 5.34 | 5.34 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.04 | 0 | 120 | 2.04 | 0 | 16.8 | 14.76 |  |  |  | Nom. capacity LV, МVА | 16+16 | 2.3 | 4.34 | 0 | 120 | 4.34 | 0 | 16.8 | 12.46
94 | Koshchino 35/10 | 4+4 | 0.87 | 0.11 | 120 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened | 94 | Koshchino 35/10 | 4+4 | 0.15 | 1.02 | 0.11 | 120 | 0.91 | 0 | 4.2 | 3.29 | 3.29 | opened
95 | Kommunar 35/10 | 2,5+2,5 | 0.67 | 0.03 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened | 95 | Kommunar 35/10 | 2,5+2,5 | 0.05 | 0.72 | 0.03 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened
96 | Kasplya 110/35/10 | 10+10 | 3.4 | 3.07 | 120 | 0.33 | 0 | 10.5 | 10.17 | 10.17 | opened | 96 | Kasplya 110/35/10 | 10+10 | 5.01 | 8.41 | 7.83 | 120 | 0.58 | 0 | 10.5 | 9.92 | 9.92 | opened
| Nom. capacity MV, МVА | 10+10 | 2.21 | 2.21 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.76 | 6.97 | 6.97 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.19 | 0.86 | 120 | 0.33 | 0 | 10.5 | 10.17 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.25 | 1.44 | 0.86 | 120 | 0.58 | 0 | 10.5 | 9.92
97 | Apolye 35/10 | 2,5+2,5 | 0.79 | 0.17 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 97 | Apolye 35/10 | 2,5+2,5 | 0.02 | 0.81 | 0.17 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
98 | Zhukovskaya 35/10 | 4+4 | 1.84 | 0.19 | 120 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | opened | 98 | Zhukovskaya 35/10 | 4+4 | 3.39 | 5.23 | 0.19 | 120 | 5.04 | 0 | 4.2 | -0.84 | -0.84 | closed
99 | Mazaltsevo 110/35/10 | 10+10 | 2.59 | 2.16 | 120 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | opened | 99 | Mazaltsevo 110/35/10 | 10+10 | 14.45 | 17.04 | 16.59 | 120 | 0.45 | 0 | 10.5 | 10.05 | 10.05 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 14.43 | 16.33 | 16.33 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.69 | 0.26 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.02 | 0.71 | 0.26 | 120 | 0.45 | 0 | 10.5 | 10.05
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 100 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
101 | Krasny 110/35/10 | 10+10 | 4.22 | 2.26 | 120 | 1.96 | 0 | 10.5 | 8.54 | 8.54 | opened | 101 | Krasny 110/35/10 | 10+10 | 3.37 | 7.59 | 3.43 | 120 | 4.16 | 0 | 10.5 | 6.34 | 6.34 | opened
| Nom. capacity MV, МVА | 10+10 | 1.8 | 1.8 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.17 | 2.97 | 2.97 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.42 | 0.46 | 120 | 1.96 | 0 | 10.5 | 8.54 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.2 | 4.62 | 0.46 | 120 | 4.16 | 0 | 10.5 | 6.34
102 | Voloelovo 35/10 | 2,5+2,5 | 0.04 | 0.01 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 102 | Voloelovo 35/10 | 2,5+2,5 | 0 | 0.04 | 0.01 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened | 103 | Kryukovo 35/10 | 2,5+2,5 | 0.4 | 0.52 | 0.26 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened
104 | Miganovo 35/10 | 2,5+2,5 | 1.18 | 0.49 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened | 104 | Miganovo 35/10 | 2,5+2,5 | 1.25 | 2.43 | 0.49 | 120 | 1.94 | 0 | 2.625 | 0.685 | 0.685 | opened
105 | Velizh 110/35/10 | 10+10 | 5.77 | 2.05 | 120 | 3.72 | 0 | 10.5 | 6.78 | 6.78 | opened | 105 | Velizh 110/35/10 | 10+10 | 1.75 | 7.52 | 2.16 | 120 | 5.36 | 0 | 10.5 | 5.14 | 5.14 | opened
| Nom. capacity MV, МVА | 10+10 | 1.38 | 1.38 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.11 | 1.49 | 1.49 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.39 | 0.67 | 120 | 3.72 | 0 | 10.5 | 6.78 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.64 | 6.03 | 0.67 | 120 | 5.36 | 0 | 10.5 | 5.14
106 | Chepli 35/10 | 2,5+2,5 | 0.4 | 0.09 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 106 | Chepli 35/10 | 2,5+2,5 | 0 | 0.4 | 0.09 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
107 | Demidov 110/35/10 | 10+16 | 5.52 | 1.14 | 120 | 4.38 | 0 | 10.5 | 6.12 | 6.12 | opened | 107 | Demidov 110/35/10 | 10+16 | 1.6 | 7.12 | 1.38 | 120 | 5.74 | 0 | 10.5 | 4.76 | 4.76 | opened
| Nom. capacity MV, МVА | 10+16 | 0.96 | 0.96 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.24 | 1.2 | 1.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.56 | 0.18 | 120 | 4.38 | 0 | 10.5 | 6.12 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.36 | 5.92 | 0.18 | 120 | 5.74 | 0 | 10.5 | 4.76
108 | Staroe selo 35/10 | 2,5+2,5 | 0.34 | 0.17 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 108 | Staroe selo 35/10 | 2,5+2,5 | 0 | 0.34 | 0.17 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
109 | Zakrutye 35/10 | 2,5+2,5 | 0.13 | 0 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 109 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.13 | 0 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
110 | Zaborye 35/10 | 1,6+2,5 | 0.34 | 0.21 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 110 | Zaborye 35/10 | 1,6+2,5 | 0 | 0.34 | 0.21 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
111 | Mikhailovskoe 110/35/10 | 10+10 | 1.07 | 0.73 | 120 | 0.34 | 0 | 10.5 | 10.16 | 10.16 | opened | 111 | Mikhailovskoe 110/35/10 | 10+10 | 0.6 | 1.67 | 0.91 | 120 | 0.76 | 0 | 10.5 | 9.74 | 9.74 | opened
| Nom. capacity MV, МVА | 10+10 | 0.31 | 0.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.18 | 0.49 | 0.49 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.76 | 0.42 | 120 | 0.34 | 0 | 10.5 | 10.16 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.32 | 1.08 | 0.42 | 120 | 0.66 | 0 | 10.5 | 9.84
112 | Kardymovo 110/35/10 | 10+16 | 5.69 | 3.2 | 120 | 2.49 | 0 | 10.5 | 8.01 | 8.01 | opened | 112 | Kardymovo 110/35/10 | 10+16 | 7.43 | 13.12 | 5.36 | 120 | 7.76 | 0 | 10.5 | 2.74 | 2.74 | opened
| Nom. capacity MV, МVА | 10+16 | 2.58 | 2.58 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 2.16 | 4.74 | 4.74 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.11 | 0.62 | 120 | 1.49 | 0 | 10.5 | 9.01 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.27 | 7.38 | 0.62 | 120 | 6.76 | 0 | 10.5 | 3.74
113 | Sinkovo 35/6 | 4+2,5 | 0.44 | 0.16 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 113 | Sinkovo 35/6 | 4+2,5 | 0.05 | 0.49 | 0.16 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
114 | Kamenka 35/10 | 2,5+2,5 | 1.4 | 0.42 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened | 114 | Kamenka 35/10 | 2,5+2,5 | 0.94 | 2.34 | 0.42 | 120 | 1.92 | 0 | 2.625 | 0.705 | 0.705 | opened
115 | Solovyevo 35/10 | 4+4 | 0.28 | 0.04 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 115 | Solovyevo 35/10 | 4+4 | 0.13 | 0.41 | 0.04 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened
116 | Rudnya (FPC) 110/35/10 | 10+16 | 8.33 | 1.87 | 120 | 6.46 | 0 | 10.5 | 4.04 | 4.04 | opened | 116 | Rudnya (FPC) 110/35/10 | 10+16 | 2.8 | 11.13 | 2.94 | 120 | 8.19 | 0 | 10.5 | 2.31 | 2.31 | opened
| Nom. capacity MV, МVА | 10+16 | 0.94 | 0.94 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 1.07 | 2.01 | 2.01 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.39 | 0.93 | 120 | 6.46 | 0 | 10.5 | 4.04 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.73 | 9.12 | 0.93 | 120 | 8.19 | 0 | 10.5 | 2.31
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.2 | 0.75 | 120 | -0.55 | 0 | 2.625 | 3.175 | 3.175 | opened | 117 | Zhichitsy 35/10 | 2,5+2,5 | 0 | 0.2 | 0.75 | 120 | -0.55 | 0 | 2.625 | 3.175 | 3.175 | opened
118 | Mikulino 35/10 | 6,3+6,3 | 0.88 | 1.1 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.835 | opened | 118 | Mikulino 35/10 | 6,3+6,3 | 0.18 | 1.06 | 1.1 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.52 | 0.74 | 120 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | opened | 119 | Lyubavichi 35/10 | 2,5+2,5 | 0.42 | 0.94 | 0.74 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
120 | Kazimirovo 35/10 | 4+4 | 0.12 | 0.02 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened | 120 | Kazimirovo 35/10 | 4+4 | 0.03 | 0.15 | 0.02 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | opened
121 | Golynki 110/35/6 | 25+25 | 4.58 | 2.91 | 120 | 1.67 | 0 | 26.25 | 24.58 | 24.58 | opened | 121 | Golynki 110/35/6 | 25+25 | 5.39 | 9.97 | 8.24 | 120 | 1.73 | 0 | 26.25 | 24.52 | 24.52 | opened
| Nom. Capacity MV, МVА | 25+25 | 2.75 | 2.75 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, МVА | 25+25 | 5.33 | 8.08 | 8.08 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.83 | 0.16 | 120 | 1.67 | 0 | 26.25 | 24.58 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.06 | 1.89 | 0.16 | 120 | 1.73 | 0 | 26.25 | 24.52
122 | Belei 35/10 | 2,5+2,5 | 1.61 | 0.75 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | opened | 122 | Belei 35/10 | 2,5+2,5 | 4.77 | 6.38 | 0.75 | 120 | 5.63 | 0 | 2.625 | -3.005 | -3.005 | closed
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.15 | 1.45 | 120 | 1.7 | 0 | 6.615 | 4.915 | 4.915 | opened | 123 | Ponizovye 110/35/10 | 6,3+6,3 | 0.18 | 3.33 | 1.45 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.39 | 1.39 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 1.39 | 1.39 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.76 | 0.06 | 120 | 1.7 | 0 | 6.615 | 4.915 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.18 | 1.94 | 0.06 | 120 | 1.88 | 0 | 6.615 | 4.735
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 124 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
125 | Safonovo 110/6 | 15+20 | 9.25 | 0.06 | 120 | 9.19 | 0 | 15.75 | 6.56 | 6.56 | opened | 125 | Safonovo 110/6 | 15+20 | 5.42 | 14.67 | 0.06 | 120 | 14.61 | 0 | 15.75 | 1.14 | 1.14 | opened
126 | Gornaya 110/35/6 | 25+25 | 11.7 | 11.58 | 120 | 0.12 | 0 | 26.25 | 26.13 | 26.13 | opened | 126 | Gornaya 110/35/6 | 25+25 | 5.05 | 16.75 | 16.47 | 120 | 0.28 | 0 | 26.25 | 25.97 | 25.97 | opened
| Nom. capacity MV, МVА | 25+25 | 6.91 | 6.91 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.89 | 11.8 | 11.8 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 4.79 | 4.67 | 120 | 0.12 | 0 | 26.25 | 26.13 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.16 | 4.95 | 4.67 | 120 | 0.28 | 0 | 26.25 | 25.97
127 | Water intake 35/6 | 6,3+4 | 1.68 | 0.69 | 120 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | opened | 127 | Water intake 35/6 | 6,3+4 | 1.53 | 3.21 | 0.69 | 120 | 2.52 | 0 | 4.2 | 1.68 | 1.68 | opened
128 | Vadino 35/10 | 4+4 | 1.23 | 0 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened | 128 | Vadino 35/10 | 4+4 | 1.91 | 3.14 | 0 | 120 | 3.14 | 0 | 4.2 | 1.06 | 1.06 | opened
129 | ZSSK 35/6 | 4+4 | 1.61 | 0.75 | 120 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 129 | ZSSK 35/6 | 4+4 | 1.03 | 2.64 | 0.75 | 120 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened
130 | Yanovo 35/10 | 4+6,3 | 0.27 | 0.05 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | opened | 130 | Yanovo 35/10 | 4+6,3 | 0 | 0.27 | 0.05 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | opened
131 | Kapyrevshchina 35/10 | 4+4 | 1.26 | 0.22 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened | 131 | Kapyrevshchina 35/10 | 4+4 | 0 | 1.26 | 0.22 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened
132 | Miropolye 35/10 | 2,5+2,5 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened | 132 | Miropolye 35/10 | 2,5+2,5 | 0 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 3.34 | 1.34 | 120 | 2 | 0 | 5.88 | 3.88 | 1.88 | opened | 133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.83 | 5.17 | 2.62 | 120 | 2.55 | 0 | 5.88 | 3.33 | 3.33 | opened
| Nom. capacity MV, МVА | 5,6+6,3 | 0.91 | 0.91 |  | 0 | 1 | 5.88 | 4.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 1.28 | 2.19 | 2.19 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.43 | 0.43 | 120 | 2 | 2 | 5.88 | 1.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.55 | 2.98 | 0.43 | 120 | 2.55 | 0 | 5.88 | 3.33
134 | Alferovo 35/10 | 2,5+2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened | 134 | Alferovo 35/10 | 2,5+2,5 | 0.4 | 0.59 | 0.2 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
135 | Kasulino 35/10 | 2,5+2,5 | 0.15 | 0 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened | 135 | Kasulino 35/10 | 2,5+2,5 | 0.52 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | opened
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.28 | 0.15 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.35 | 0.63 | 0.15 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened
137 | Glinka 110/35/10 | 10+6,3 | 2 | 0.44 | 120 | 1.56 | 0 | 6.615 | 5.055 | 3.055 | opened | 137 | Glinka 110/35/10 | 10+6,3 | 0.95 | 2.95 | 0.62 | 120 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.33 | 0.33 |  | 0 | 1 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.18 | 0.51 | 0.51 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.67 | 0.11 | 120 | 1.56 | 2 | 6.615 | 3.055 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.77 | 2.44 | 0.11 | 120 | 2.33 | 0 | 6.615 | 4.285
138 | Dobromino 35/10 | 2,5+2,5 | 0.24 | 0 | 120 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | opened | 138 | Dobromino 35/10 | 2,5+2,5 | 0.14 | 0.38 | 0 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
139 | Bely kholm 35/10 | 1,6+1,6 | 0.09 | 0 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 139 | Bely kholm 35/10 | 1,6+1,6 | 0.04 | 0.13 | 0 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
140 | Dukhovshchina 110/35/10 | 10+10 | 3.26 | 1.89 | 120 | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened | 140 | Dukhovshchina 110/35/10 | 10+10 | 1.67 | 4.93 | 2.94 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened
| Nom. capacity MV, МVА | 10+10 | 1.63 | 1.63 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.05 | 2.68 | 2.68 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.63 | 0.26 | 120 | 1.37 | 0 | 10.5 | 9.13 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.62 | 2.25 | 0.26 | 120 | 1.99 | 0 | 10.5 | 8.51
141 | Zimets 35/10 | 4+4 | 0.3 | 0.06 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 141 | Zimets 35/10 | 4+4 | 0 | 0.3 | 0.06 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened
142 | Beresnevo 35/10 | 1,6+1,6 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 142 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
143 | Prechistoe 110/35/10 | 6,3+6,3 | 1.92 | 0.14 | 120 | 1.78 | 0 | 6.615 | 4.835 | 4.835 | opened | 143 | Prechistoe 110/35/10 | 6,3+6,3 | 0.36 | 2.28 | 0.14 | 120 | 2.14 | 0 | 6.615 | 4.475 | 4.475 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.34 | 0 |  | 1.34 | 0 | 6.615 | 5.275 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 1.7 | 0 |  | 1.7 | 0 | 6.615 | 4.915
| Nom. capacity LV, МVА | 6,3+6,3 | 0.58 | 0.14 | 120 | 0.44 | 0 | 6.615 | 6.175 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.58 | 0.14 | 120 | 0.44 | 0 | 6.615 | 6.175
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 144 | Vorontsovo 35/10 | 2,5+2,5 | 0 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
145 | Ozyorny 35/10 | 6,3+6,3 | 1.32 | 0.01 | 120 | 1.31 | 0 | 6.615 | 5.305 | 5.305 | opened | 145 | Ozyorny 35/10 | 6,3+6,3 | 0.34 | 1.66 | 0.01 | 120 | 1.65 | 0 | 6.615 | 4.965 | 4.965 | opened
146 | Igorevskaya 110/10 | 10+10 | 4.94 | 0 | 120 | 4.94 | 0 | 10.5 | 5.56 | 5.56 | opened | 146 | Igorevskaya 110/10 | 10+10 | 0.6 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35 | 9.35 | opened
147 | Kanyutino 110/35/10 | 5,6+6,3 | 2.78 | 1.68 | 120 | 1.1 | 0 | 5.88 | 4.78 | 4.78 | opened | 147 | Kanyutino 110/35/10 | 5,6+6,3 | 0.79 | 3.57 | 3.4 | 120 | 0.17 | 0 | 5.88 | 5.71 | 5.71 | opened
| Nom. capacity LV, МVА | 5,6+6,3 | 2.4 | 2.4 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.79 | 3.19 | 3.19 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.38 | 0.21 | 120 | 0.17 | 0 | 5.88 | 5.71 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.38 | 0.21 | 120 | 0.17 | 0 | 5.88 | 5.71
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.21 | 0.25 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened | 148 | Bogolyubovo 35/10 | 2,5+2,5 | 0 | 1.21 | 0.25 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
149 | Kholm-Zhirki 35/10 | 2,5+4 | 1.8 | 0.4 | 120 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | opened | 149 | Kholm-Zhirki 35/10 | 2,5+4 | 0.6 | 2.4 | 0.4 | 120 | 2 | 0 | 2.625 | 0.625 | 0.625 | opened
150 | Dorogobuzh 1 110/35/10 | 16+16 | 6.74 | 2.85 | 120 | 3.89 | 0 | 16.8 | 12.91 | 12.91 | opened | 150 | Dorogobuzh 1 110/35/10 | 16+16 | 1.48 | 8.22 | 3 | 120 | 5.22 | 0 | 16.8 | 11.58 | 11.58 | opened
| Nom. capacity MV, МVА | 16+16 | 2.33 | 2.33 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.15 | 2.48 | 2.48 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.41 | 0.52 | 120 | 3.89 | 0 | 16.8 | 12.91 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.33 | 5.74 | 0.52 | 120 | 5.22 | 0 | 16.8 | 11.58
151 | Kaskovo 35/10 | 1,6+4 | 0.78 | 0.09 | 120 | 0.69 | 0 | 1.68 | 0.99 | 0.99 | opened | 151 | Kaskovo 35/10 | 1,6+4 | 0 | 0.78 | 0.09 | 120 | 0.69 | 0 | 1.68 | 0.99 | 0.99 | opened
152 | Usvyatye 35/10 | 2,5+4 | 0.89 | 0 | 120 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened | 152 | Usvyatye 35/10 | 2,5+4 | 0 | 0.89 | 0 | 120 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened
153 | Ushakovo 35/10 | 1,6+2,5 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 153 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.16 | 0.04 | 120 | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened | 155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.16 | 0.04 | 120 | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened
156 | Elnya 110/35/10 | 16+16 | 7.26 | 3.03 | 120 | 4.23 | 0 | 16.8 | 12.57 | 12.57 | opened | 156 | Elnya 110/35/10 | 16+16 | 0.61 | 7.87 | 3.24 | 120 | 4.63 | 0 | 16.8 | 12.17 | 12.17 | opened
| Nom. capacity MV, МVА | 16+16 | 2.49 | 2.49 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.21 | 2.7 | 2.7 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.77 | 0.54 | 10 | 4.23 | 0 | 16.8 | 12.57 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.4 | 5.17 | 0.54 | 120 | 4.63 | 0 | 16.8 | 12.17
157 | Pavlovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 157 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
158 | Sharapovo 35/10 | 4+4 | 0.9 | 1 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened | 158 | Sharapovo 35/10 | 4+4 | 0 | 0.9 | 1 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
159 | Korobets 35/10 | 2,5+2,5 | 1.05 | 0.17 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 159 | Korobets 35/10 | 2,5+2,5 | 0 | 1.05 | 0.17 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
160 | Baltutino 35/10 | 2,5+2,5 | 0.53 | 0 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened | 160 | Baltutino 35/10 | 2,5+2,5 | 0.15 | 0.68 | 0 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | opened
161 | Lapino 110/35/10 | 5,6+5,6 | 1.15 | 0.79 | 120 | 0.36 | 0 | 5.88 | 5.52 | 5.52 | opened | 161 | Lapino 110/35/10 | 5,6+5,6 | 0.09 | 1.24 | 0.88 | 120 | 0.36 | 0 | 5.88 | 5.52 | 5.52 | opened
| Nom. capacity MV, МVА | 5,6+5,6 | 0.79 | 0.79 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0.09 | 0.88 | 0.88 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.36 | 0 | 120 | 0.36 | 0 | 5.88 | 5.52 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 5.88 | 5.52
162 | Mutishche 35/10 | 1,6+2,5 | 0.28 | 0.08 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 162 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.28 | 0.08 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
163 | Suetovo 110/35/10 | 6,3+6,3 | 1.91 | 1.56 | 120 | 0.35 | 0 | 6.615 | 6.265 | 6.265 | opened | 163 | Suetovo 110/35/10 | 6,3+6,3 | 1.32 | 3.23 | 2.64 | 120 | 0.59 | 0 | 6.615 | 6.025 | 6.025 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.98 | 0.98 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1.08 | 2.06 | 2.06 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.93 | 0.58 | 120 | 0.35 | 0 | 6.615 | 6.265 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.17 | 0.58 | 120 | 0.59 | 0 | 6.615 | 6.025
164 | Pushkino 35/10 | 2,5+2,5 | 0.56 | 0.04 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 164 | Pushkino 35/10 | 2,5+2,5 | 1.08 | 1.64 | 0.04 | 120 | 1.6 | 0 | 2.625 | 1.025 | 1.025 | opened
165 | Yartsevo 1 110/10 | 40+40 | 13.57 | 5.34 | 120 | 8.23 | 0 | 42 | 33.77 | 33.77 | opened | 165 | Yartsevo 1 110/10 | 40+40 | 6.59 | 20.16 | 5.34 | 120 | 14.82 | 0 | 42 | 27.18 | 27.18 | opened
166 | Yartsevo 2 110/10 | 16+16 | 10.61 | 0.75 | 120 | 9.86 | 0 | 16.8 | 6.94 | 6.94 | opened | 166 | Yartsevo 2 110/10 | 16+16 | 6.6 | 17.21 | 0.75 | 120 | 16.46 | 0 | 16.8 | 0.34 | 0.34 | opened
167 | Saprykino 110/35/10 | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105 | 6.105 | opened | 167 | Saprykino 110/35/10 | 6,3+6,3 | 0.14 | 1.05 | 0.4 | 120 | 0.65 | 0 | 6.615 | 5.965 | 5.965 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.14 | 1.05 | 0.4 | 120 | 0.65 | 0 | 6.615 | 5.965
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.19 | 0 | 120 | 2.19 | 0 | 6.615 | 4.425 | 4.425 | opened | 168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.97 | 3.16 | 0 | 120 | 3.16 | 0 | 6.615 | 3.455 | 3.455 | opened
169 | Egoryevo 35/10 | 6,3+6,3 | 4.65 | 0 | 120 | 4.65 | 0 | 6.615 | 1.965 | 1.965 | opened | 169 | Egoryevo 35/10 | 6,3+6,3 | 0.14 | 4.79 | 0 | 120 | 4.79 | 0 | 6.615 | 1.825 | 1.825 | opened
170 | Shalomino 35/10 | 1,6+2,5 | 0.59 | 0.13 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened | 170 | Shalomino 35/10 | 1,6+2,5 | 0.17 | 0.76 | 0.13 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened
171 | Roslavl 110/35/6 | 25+40 | 26.59 | 1.4 | 120 | 25.19 | 0 | 26.25 | 1.06 | 1.06 | opened | 171 | Roslavl 110/35/6 | 25+40 | 1.93 | 28.52 | 1.4 | 120 | 27.12 | 0 | 26.25 | -0.87 | -0.87 | closed
| Nom. capacity MV, МVА | 25+40 | 11.79 | 1.4 |  | 10.39 | 0 | 26.25 | 15.86 |  |  |  | Nom. capacity MV, МVА | 25+40 | 0.75 | 12.54 | 1.4 |  | 11.14 | 0 | 26.25 | 15.11
| Nom. сapacity LV, МVА | 25+40 | 14.8 | 0 | 120 | 14.8 | 0 | 26.25 | 11.45 |  |  |  | Nom. сapacity LV, МVА | 25+40 | 1.18 | 15.98 | 0 | 120 | 15.98 | 0 | 26.25 | 10.27
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.88 | 0 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | opened | 172 | Meet processing plant 35/6 | 6,3+6,3 | 0.11 | 1.99 | 0 | 120 | 1.99 | 0 | 6.615 | 4.625 | 4.625 | opened
173 | Perenka 35/10 | 4+4 | 0.36 | 0 | 120 | 0.36 | 0 | 4.2 | 3.84 | 3.84 | opened | 173 | Perenka 35/10 | 4+4 | 0.01 | 0.37 | 0 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened
174 | Khoroshevo 35/10 | 2,5+4 | 1.19 | 0 | 120 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened | 174 | Khoroshevo 35/10 | 2,5+4 | 0.08 | 1.27 | 0 | 120 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened
175 | Lipovka 35/10 | 2,5+2,5 | 0.52 | 0 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 175 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.52 | 0 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
176 | Kirilly 35/10 | 2,5+2,5 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 176 | Kirilly 35/10 | 2,5+2,5 | 0.52 | 1.33 | 0 | 120 | 1.33 | 0 | 2.625 | 1.295 | 1.295 | opened
177 | Desnogorsk 110/35/10 | 25+25 | 17.92 | 3.15 | 120 | 14.77 | 0 | 26.25 | 11.48 | 11.48 | opened | 177 | Desnogorsk 110/35/10 | 25+25 | 0.63 | 18.55 | 3.16 | 120 | 15.39 | 0 | 26.25 | 10.86 | 10.86 | opened
| Nom. capacity MV, МVА | 25+25 | 3.15 | 3.15 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0.62 | 3.77 | 3.16 |  | 0.61 | 0 | 26.25 | 25.64
| Nom. capacidty LV, МVА | 25+25 | 14.77 | 0 | 120 | 14.77 | 0 | 26.25 | 11.48 |  |  |  | Nom. capacidty LV, МVА | 25+25 | 0.01 | 14.78 | 0 | 120 | 14.78 | 0 | 26.25 | 11.47
178 | Ekimovichi 35/10 | 4+4 | 2.31 | 0.24 | 120 | 2.07 | 0 | 4.2 | 2.13 | 2.13 | opened | 178 | Ekimovichi 35/10 | 4+4 | 0.07 | 2.38 | 0.24 | 120 | 2.14 | 0 | 4.2 | 2.06 | 2.06 | opened
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.18 | 0.07 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 179 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.18 | 0.07 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
180 | Kokhany 35/10 | 1,6+1,6 | 0.33 | 0.09 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 180 | Kokhany 35/10 | 1,6+1,6 | 0.09 | 0.42 | 0.09 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
181 | Koski 35/10 | 4+4 | 0.49 | 0 | 120 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | opened | 181 | Koski 35/10 | 4+4 | 0.01 | 0.5 | 0 | 120 | 0.5 | 0 | 4.2 | 3.7 | 3.7 | opened
182 | Industrialnaya 110/35/6 | 16+16 | 4.43 | 0.7 | 120 | 3.73 | 0 | 16.8 | 13.07 | 4.565 | opened | 182 | Industrialnaya 110/35/6 | 16+16 | 1.42 | 5.85 | 0.7 | 120 | 5.15 | 0 | 16.8 | 11.65 | 5.565 | opened
| Nom. capacity MV, МVА | 16,3+5,3 | 0.7 | 0.7 |  | 0 | 1 | 5.565 | 4.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0 | 0.7 | 0.7 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 3.73 | 0 | 120 | 3.73 | 2 | 11.235 | 5.505 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 1.42 | 5.15 | 0 | 120 | 5.15 | 0 | 11.235 | 6.085
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.88 | 0 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 183 | Astapkovichi 35/10 | 2,5+2,5 | 0 | 0.88 | 0 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.11 | 0.72 | 120 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | opened | 184 | Barsuki 110/35/10 | 6,3+6,3 | 0.28 | 1.39 | 1 | 120 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.72 | 0.72 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.28 | 1 | 1 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.39 | 0 | 120 | 0.39 | 0 | 6.615 | 6.225 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.39 | 0 | 120 | 0.39 | 0 | 6.615 | 6.225
185 | Bogdanovo 35/10 | 4+4 | 0.54 | 0 | 120 | 0.54 | 0 | 4.2 | 3.66 | 3.66 | opened | 185 | Bogdanovo 35/10 | 4+4 | 0.28 | 0.82 | 0 | 120 | 0.82 | 0 | 4.2 | 3.38 | 3.38 | opened
186 | Prigorye 110/35/10 | 10+2,5 | 0.89 | 0.48 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened | 186 | Prigorye 110/35/10 | 10+2,5 | 0.12 | 1.01 | 0.6 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened
| Nom. capacity MV, МVА | 10+2,5 | 0.48 | 0.48 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0.12 | 0.6 | 0.6 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.41 | 0 | 120 | 0.41 | 0 | 2.625 | 2.215 |  |  |  | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 2.625 | 2.215
187 | Bekhovo 35/10 | 2,5+2,5 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened | 187 | Bekhovo 35/10 | 2,5+2,5 | 0.12 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
188 | Pochinok 110/35/10 | 10+16 | 8.99 | 3.63 | 120 | 5.36 | 0 | 10.5 | 5.14 | 5.14 | opened | 188 | Pochinok 110/35/10 | 10+16 | 1.38 | 10.37 | 4.14 | 120 | 6.23 | 0 | 10.5 | 4.27 | 4.27 | opened
| Nom. capacidty MV, МVА | 10+16 | 3.55 | 3.55 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacidty MV, МVА | 10+16 | 0.51 | 4.06 | 4.06 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.44 | 0.08 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.87 | 6.31 | 0.08 | 120 | 6.23 | 0 | 10.5 | 4.27
189 | Divinskaya 35/10 | 4+4 | 1.23 | 0.17 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | opened | 189 | Divinskaya 35/10 | 4+4 | 0.04 | 1.27 | 0.17 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened
190 | Shatalovo 35/10 | 2,5+2,5 | 1.75 | 0 | 120 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | opened | 190 | Shatalovo 35/10 | 2,5+2,5 | 0 | 1.75 | 0 | 120 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | opened
191 | Panskaya 35/10 | 6,3+6,3 | 1.48 | 0 | 120 | 1.48 | 0 | 6.615 | 5.135 | 5.135 | opened | 191 | Panskaya 35/10 | 6,3+6,3 | 0.51 | 1.99 | 0 | 120 | 1.99 | 0 | 6.615 | 4.625 | 4.625 | opened
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.28 | 1.44 | 120 | 1.84 | 0 | 6.615 | 4.775 | 4.775 | opened | 192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.14 | 6.42 | 2.05 | 120 | 4.37 | 0 | 6.615 | 2.245 | 2.245 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.99 | 0.99 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.61 | 1.6 | 1.6 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.29 | 0.45 | 120 | 1.84 | 0 | 6.615 | 4.775 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.53 | 4.82 | 0.45 | 120 | 4.37 | 0 | 6.615 | 2.245
193 | Belik 35/10 | 2,5+2,5 | 0.22 | 0.33 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened | 193 | Belik 35/10 | 2,5+2,5 | 0 | 0.22 | 0.33 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened
194 | Pervomayskaya 35/10 | 4+4 | 1.4 | 0 | 120 | 1.4 | 0 | 4.2 | 2.8 | 2.8 | opened | 194 | Pervomayskaya 35/10 | 4+4 | 0.54 | 1.94 | 0 | 120 | 1.94 | 0 | 4.2 | 2.26 | 2.26 | opened
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.84 | 2.07 | 120 | -0.23 | 0 | 6.615 | 6.845 | 6.255 | opened | 195 | Vaskovo 110/35/10 | 6,3+6,3 | 0.04 | 1.88 | 1.52 | 120 | 0.36 | 0 | 6.615 | 6.255 | 6.255 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.27 | 1.27 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.04 | 1.31 | 1.31 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.57 | 0.21 | 120 | 0.36 | 0 | 6.615 | 6.255 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.57 | 0.21 | 120 | 0.36 | 0 | 6.615 | 6.255
196 | Strigino 35/10 | 2,5+2,5 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 196 | Strigino 35/10 | 2,5+2,5 | 0 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
197 | Komintern 35/10 | 2,5+2,5 | 0.58 | 0 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 197 | Komintern 35/10 | 2,5+2,5 | 0 | 0.58 | 0 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
198 | Monastyrshchina 110/35/10 | 10+10 | 4.37 | 1.9 | 120 | 2.47 | 0 | 10.5 | 8.03 | 8.03 | opened | 198 | Monastyrshchina 110/35/10 | 10+10 | 0.2 | 4.57 | 1.97 | 120 | 2.6 | 0 | 10.5 | 7.9 | 7.9 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.07 | 1.97 | 1.97 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.47 | 0 | 120 | 2.47 | 0 | 10.5 | 8.03 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.13 | 2.6 | 0 | 120 | 2.6 | 0 | 10.5 | 7.9
199 | N.Mikhailov 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened | 199 | N.Mikhailov 35/10 | 4+4 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
200 | Tatarsk 35/10 | 3,2+4 | 0.81 | 0 | 120 | 0.81 | 0 | 3.36 | 2.55 | 2.55 | opened | 200 | Tatarsk 35/10 | 3,2+4 | 0.02 | 0.83 | 0 | 120 | 0.83 | 0 | 3.36 | 2.53 | 2.53 | opened
201 | Turki 35/10 | 1,6+1,6 | 0.34 | 0 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened | 201 | Turki 35/10 | 1,6+1,6 | 0 | 0.34 | 0 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened
202 | Sozh 35/10 | 4+4 | 0.52 | 0 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | opened | 202 | Sozh 35/10 | 4+4 | 0.02 | 0.54 | 0 | 120 | 0.54 | 0 | 4.2 | 3.66 | 3.66 | opened
203 | Khislavichi 110/35/10 | 16+16 | 4.11 | 1.61 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | opened | 203 | Khislavichi 110/35/10 | 16+16 | 0.49 | 4.6 | 1.81 | 120 | 2.79 | 0 | 16.8 | 14.01 | 14.01 | opened
| Nom. capacity MV, МVА | 16+16 | 1.43 | 1.43 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.2 | 1.63 | 1.63 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.68 | 0.18 | 120 | 2.5 | 0 | 16.8 | 14.3 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.29 | 2.97 | 0.18 | 120 | 2.79 | 0 | 16.8 | 14.01
204 | Gorodishche 35/10 | 1,8+2,5 | 0.82 | 0 | 120 | 0.82 | 0 | 1.89 | 1.07 | 1.07 | opened | 204 | Gorodishche 35/10 | 1,8+2,5 | 0 | 0.82 | 0 | 120 | 0.82 | 0 | 1.89 | 1.07 | 1.07 | opened
205 | Komarovka 35/10 | 4+4 | 0.32 | 0.02 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 205 | Komarovka 35/10 | 4+4 | 0 | 0.32 | 0.02 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
206 | Cherepovo 35/10 | 2,5+2,5 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened | 206 | Cherepovo 35/10 | 2,5+2,5 | 0.05 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
207 | Studenets 35/10 | 1,6+2,5 | 0.34 | 0.01 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened | 207 | Studenets 35/10 | 1,6+2,5 | 0.15 | 0.49 | 0.01 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened
208 | Shumyachi 110/35/10 | 10+10 | 4.8 | 3.36 | 120 | 1.44 | 0 | 10.5 | 9.06 | 9.06 | opened | 208 | Shumyachi 110/35/10 | 10+10 | 1.02 | 5.82 | 4.04 | 120 | 1.78 | 0 | 10.5 | 8.72 | 8.72 | opened
| Nom. capacity MV, МVА | 10+10 | 2.72 | 2.72 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.68 | 3.4 | 3.4 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.08 | 0.64 | 120 | 1.44 | 0 | 10.5 | 9.06 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.34 | 2.42 | 0.64 | 120 | 1.78 | 0 | 10.5 | 8.72
209 | Ershichi 110/35/10 | 10+10 | 2.25 | 0.62 | 120 | 1.63 | 0 | 10.5 | 8.87 | 8.87 | opened | 209 | Ershichi 110/35/10 | 10+10 | 0.39 | 2.64 | 0.62 | 120 | 2.02 | 0 | 10.5 | 8.48 | 8.48 | opened
| Nom. capacity MV, МVА | 10+10 | 0.4 | 0.4 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.4 | 0.4 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.85 | 0.22 | 120 | 1.63 | 0 | 10.5 | 8.87 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.39 | 2.24 | 0.22 | 120 | 2.02 | 0 | 10.5 | 8.48
210 | Rukhan 35/10 | 2,5+2,5 | 0.45 | 0 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened | 210 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.45 | 0 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
211 | Vyazma 1 110/35/10 | 40+40 | 42.21 | 11.83 | 120 | 30.38 | 0 | 42 | 11.62 | 11.62 | opened | 211 | Vyazma 1 110/35/10 | 40+40 | 19.66 | 61.87 | 15.76 | 120 | 46.11 | 0 | 42 | -4.11 | -4.11 | closed
| Nom. capacity MV, МVА | 40+40 | 25.68 | 11.27 | 121 | 14.41 | 0 | 42 | 27.59 |  |  |  | Nom. capacity MV, МVА | 40+40 | 11.09 | 36.77 | 15.2 |  | 21.57 | 0 | 42 | 20.43
| Nom. capacity LV, МVА | 40+40 | 16.53 | 0.56 | 122 | 15.97 | 0 | 42 | 26.03 |  |  |  | Nom. capacity LV, МVА | 40+40 | 8.57 | 25.1 | 0.56 | 120 | 24.54 | 0 | 42 | 17.46
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.99 | 0 | 120 | 2.99 | 0 | 6.615 | 3.625 | 3.625 | opened | 212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 1.62 | 4.61 | 0 | 120 | 4.61 | 0 | 6.615 | 2.005 | 2.005 | opened
213 | Khmelita 35/10 | 1,6+2,5 | 0.49 | 0.11 | 120 | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened | 213 | Khmelita 35/10 | 1,6+2,5 | 0.3 | 0.79 | 0.11 | 120 | 0.68 | 0 | 1.68 | 1 | 1 | opened
214 | Isakovo 35/10 | 2,5+4 | 0.76 | 0.3 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened | 214 | Isakovo 35/10 | 2,5+4 | 0 | 0.76 | 0.3 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
215 | Rizskoe 35/10 | 2,5+2,5 | 0.54 | 0.01 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened | 215 | Rizskoe 35/10 | 2,5+2,5 | 0.22 | 0.76 | 0.01 | 120 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened
216 | Beryozka 35/10 | 4+4 | 0.98 | 0 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 216 | Beryozka 35/10 | 4+4 | 0.25 | 1.23 | 0 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened
217 | Shimanovo 35/10 | 1,8+4 | 0.49 | 0.32 | 120 | 0.17 | 0 | 1.89 | 1.72 | 1.72 | opened | 217 | Shimanovo 35/10 | 1,8+4 | 0.08 | 0.57 | 0.32 | 120 | 0.25 | 0 | 1.89 | 1.64 | 1.64 | opened
218 | Kaydakovo 35/10 | 4+4 | 1.21 | 0.2 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened | 218 | Kaydakovo 35/10 | 4+4 | 0.13 | 1.34 | 0.2 | 120 | 1.14 | 0 | 4.2 | 3.06 | 3.06 | opened
219 | Flour mill 35/10 | 10+10 | 6.82 | 0.13 | 120 | 6.69 | 0 | 10.5 | 3.81 | 3.81 | opened | 219 | Flour mill 35/10 | 10+10 | 6.66 | 13.48 | 0.13 | 120 | 13.35 | 0 | 10.5 | -2.85 | -2.85 | closed
220 | Kikino 35/10 | 2,5+2,5 | 0.58 | 0.41 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 220 | Kikino 35/10 | 2,5+2,5 | 0.83 | 1.41 | 0.41 | 120 | 1 | 0 | 2.625 | 1.625 | 1.625 | opened
221 | Vyazma 2 110/10 | 16+16 | 15.42 | 0 | 120 | 15.42 | 0 | 16.8 | 1.38 | 1.38 | opened | 221 | Vyazma 2 110/10 | 16+16 | 4.75 | 20.17 | 0 | 120 | 20.17 | 0 | 16.8 | -3.37 | -3.37 | closed
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.59 | 1.18 | 120 | 1.41 | 0 | 6.615 | 5.205 | 5.205 | opened | 222 | Tumanovo 110/35/10 | 6,3+6,3 | 0.5 | 3.09 | 1.34 | 120 | 1.75 | 0 | 6.615 | 4.865 | 4.865 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.84 | 0.84 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.16 | 1 | 1 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.75 | 0.34 | 120 | 1.41 | 0 | 6.615 | 5.205 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.34 | 2.09 | 0.34 | 120 | 1.75 | 0 | 6.615 | 4.865
223 | Rossiya 110/35/10 | 10+16 | 2.8 | 1.79 | 120 | 1.01 | 0 | 10.5 | 9.49 | 9.49 | opened | 223 | Rossiya 110/35/10 | 10+16 | 0.19 | 2.99 | 1.97 | 120 | 1.02 | 0 | 10.5 | 9.48 | 9.48 | opened
| Nom. capacity MV, МVА | 10+16 | 1.47 | 1.47 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.18 | 1.65 | 1.65 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.33 | 0.32 | 120 | 1.01 | 0 | 10.5 | 9.49 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.01 | 1.34 | 0.32 | 120 | 1.02 | 0 | 10.5 | 9.48
224 | Semlevo 35/10 | 2,5+4 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 224 | Semlevo 35/10 | 2,5+4 | 0.71 | 1.55 | 0 | 120 | 1.55 | 0 | 2.625 | 1.075 | 1.075 | opened
225 | Artyomovo 35/10 | 2,5+2,5 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 225 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
226 | Gagarin 110/35/10 | 25+25 | 19.92 | 4.78 | 120 | 15.14 | 0 | 26.25 | 11.11 | 11.11 | opened | 226 | Gagarin 110/35/10 | 25+25 | 13.11 | 33.03 | 6.82 | 120 | 26.21 | 0 | 26.25 | 0.04 | 0.04 | opened
| Nom. capacity MV, МVА | 25+25 | 6.02 | 3.06 |  | 2.96 | 0 | 26.25 | 23.29 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.47 | 11.49 | 5.1 |  | 6.39 | 0 | 26.25 | 19.86
| Nom. capacity LV, МVА | 25+25 | 13.9 | 1.72 | 120 | 12.18 | 0 | 26.25 | 14.07 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.64 | 21.54 | 1.72 | 120 | 19.82 | 0 | 26.25 | 6.43
227 | Rodomanovo 35/10 | 4+4 | 0.97 | 1.18 | 120 | -0.21 | 0 | 4.2 | 4.41 | 4.41 | opened | 227 | Rodomanovo 35/10 | 4+4 | 2.41 | 3.38 | 1.18 | 120 | 2.2 | 0 | 4.2 | 2 | 2 | opened
228 | Klushino 35/10 | 4+4 | 0.82 | 0.57 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 228 | Klushino 35/10 | 4+4 | 0.69 | 1.51 | 0.57 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | opened
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 229 | Ivino 35/10 | 1,6+1,6 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
230 | Karmanovo 35/10 | 4+4 | 3.84 | 0.21 | 120 | 3.63 | 0 | 4.2 | 0.57 | 0.57 | opened | 230 | Karmanovo 35/10 | 4+4 | 1.32 | 5.16 | 0.21 | 120 | 4.95 | 0 | 4.2 | -0.75 | -0.75 | closed
231 | Sverchkovo 35/10 | 2,5+2,5 | 1.46 | 0.75 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened | 231 | Sverchkovo 35/10 | 2,5+2,5 | 0.2 | 1.66 | 0.75 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | opened
232 | Lesnaya 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened | 232 | Lesnaya 35/10 | 4+4 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
233 | Tesovo 35/10 | 1,6+2,5 | 0.67 | 0.48 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 233 | Tesovo 35/10 | 1,6+2,5 | 0.03 | 0.7 | 0.48 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
234 | Svetotekhnika 110/10 | 16+16 | 3.92 | 0.97 | 120 | 2.95 | 0 | 16.8 | 13.85 | 13.85 | opened | 234 | Svetotekhnika 110/10 | 16+16 | 3.8 | 7.72 | 0.97 | 120 | 6.75 | 0 | 16.8 | 10.05 | 10.05 | opened
235 | Mishino 110/35/10 | 10+10 | 3.98 | 2.2 | 120 | 1.78 | 0 | 10.5 | 8.72 | 8.72 | opened | 235 | Mishino 110/35/10 | 10+10 | 0.9 | 4.88 | 3.48 | 120 | 1.4 | 0 | 10.5 | 9.1 | 9.1 | opened
| Nom. capacity MV, МVА | 10+10 | 2.44 | 2.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.4 | 2.84 | 2.84 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.54 | 0.64 | 120 | 0.9 | 0 | 10.5 | 9.6 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.5 | 2.04 | 0.64 | 120 | 1.4 | 0 | 10.5 | 9.1
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.35 | 0.59 | 120 | 0.76 | 0 | 6.615 | 5.855 | 5.855 | opened | 236 | Nikolskoe 35/10 | 6,3+6,3 | 0.2 | 1.55 | 0.59 | 120 | 0.96 | 0 | 6.615 | 5.655 | 5.655 | opened
237 | Bekrino 35/10 | 2,5+2,5 | 0.55 | 0.09 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened | 237 | Bekrino 35/10 | 2,5+2,5 | 0 | 0.55 | 0.09 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
238 | Trubnaya 110/10 | 25+25 | 6.38 | 1.57 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | opened | 238 | Trubnaya 110/10 | 25+25 | 4.36 | 10.74 | 1.57 | 120 | 9.17 | 0 | 26.25 | 17.08 | 17.08 | opened
239 | Temkino 110/35/10 | 10+10 | 3.88 | 1.3 | 120 | 2.58 | 0 | 10.5 | 7.92 | 7.92 | opened | 239 | Temkino 110/35/10 | 10+10 | 2.65 | 6.53 | 2.48 | 120 | 4.05 | 0 | 10.5 | 6.45 | 6.45 | opened
| Nom. capacity MV, МVА | 10+10 | 1.05 | 1.05 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.18 | 2.23 | 2.23 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.83 | 0.25 | 120 | 2.58 | 0 | 10.5 | 7.92 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.47 | 4.3 | 0.25 | 120 | 4.05 | 0 | 10.5 | 6.45
240 | Narytka 35/10 | 2,5+2,5 | 0.15 | 0.05 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 240 | Narytka 35/10 | 2,5+2,5 | 0 | 0.15 | 0.05 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
241 | Novodugino 110/35/10 | 10+10 | 4.6 | 2.48 | 120 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened | 241 | Novodugino 110/35/10 | 10+10 | 1.47 | 6.07 | 3.73 | 120 | 2.34 | 0 | 10.5 | 8.16 | 8.16 | opened
| Nom. capacity MV, МVА | 10+10 | 2 | 2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.25 | 3.25 | 3.25 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.6 | 0.48 | 120 | 2.12 | 0 | 10.5 | 8.38 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 2.82 | 0.48 | 120 | 2.34 | 0 | 10.5 | 8.16
242 | Vysokoe 35/10 | 1,6+4 | 0.55 | 0.42 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 242 | Vysokoe 35/10 | 1,6+4 | 0.85 | 1.4 | 0.42 | 120 | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened
243 | Khotkovo 35/10 | 4+4 | 0.67 | 0.26 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 243 | Khotkovo 35/10 | 4+4 | 0 | 0.67 | 0.26 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened
244 | Dneprovsk 110/35/10 | 10+10 | 4.66 | 3.47 | 120 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened | 244 | Dneprovsk 110/35/10 | 10+10 | 1.41 | 6.07 | 4.78 | 120 | 1.29 | 0 | 10.5 | 9.21 | 9.21 | opened
| Nom. capacity MV, МVА | 10+10 | 3.31 | 3.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.31 | 4.62 | 4.62 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.35 | 0.16 | 120 | 1.19 | 0 | 10.5 | 9.31 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.1 | 1.45 | 0.16 | 120 | 1.29 | 0 | 10.5 | 9.21
245 | Lipetsy 35/10 | 2,5+2,5 | 0.33 | 0.75 | 120 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | opened | 245 | Lipetsy 35/10 | 2,5+2,5 | 0.42 | 0.75 | 0.75 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.52 | 0.7 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened | 246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0 | 0.52 | 0.7 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened
247 | Sychevka 110/35/10 | 16+25 | 8.78 | 1.47 | 120 | 7.31 | 0 | 16.8 | 9.49 | 9.49 | opened | 247 | Sychevka 110/35/10 | 16+25 | 8.03 | 16.81 | 1.78 | 120 | 15.03 | 0 | 16.8 | 1.77 | 1.77 | opened
| Nom. capacity MV, МVА | 16+25 | 3.5 | 0.7 |  | 2.8 | 0 | 16.8 | 14 |  |  |  | Nom. capacity MV, МVА | 16+25 | 3.05 | 6.55 | 1.01 |  | 5.54 | 0 | 16.8 | 11.26
| Nom. capacfity LV, МVА | 16+25 | 5.28 | 0.77 | 120 | 4.51 | 0 | 16.8 | 12.29 |  |  |  | Nom. capacfity LV, МVА | 16+25 | 5.02 | 10.3 | 0.77 | 120 | 9.53 | 0 | 16.8 | 7.27
248 | Sutormino 35/10 | 1,8+4 | 0.56 | 0.06 | 120 | 0.5 | 0 | 1.89 | 1.39 | 1.39 | opened | 248 | Sutormino 35/10 | 1,8+4 | 0 | 0.56 | 0.06 | 120 | 0.5 | 0 | 1.89 | 1.39 | 1.39 | opened
249 | Karavaevo 35/10 | 4+4 | 1.14 | 0.29 | 120 | 0.85 | 0 | 4.2 | 3.35 | 3.35 | opened | 249 | Karavaevo 35/10 | 4+4 | 0.38 | 1.52 | 0.29 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened
250 | Lukino 35/10 | 4+1,6 | 0.73 | 0.51 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 250 | Lukino 35/10 | 4+1,6 | 0 | 0.73 | 0.51 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
251 | Subbotniki 110/10 | 6,3+6,3 | 0.66 | 0 | 120 | 0.66 | 0 | 6.615 | 5.955 | 5.955 | opened | 251 | Subbotniki 110/10 | 6,3+6,3 | 0.37 | 1.03 | 0 | 120 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | opened
252 | Ugra 110/10 | 6,3+6,3 | 2.82 | 0 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 252 | Ugra 110/10 | 6,3+6,3 | 0.4 | 3.22 | 0 | 120 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened
253 | Znamenka 110/35/10 | 10+10 | 2.52 | 1.35 | 120 | 1.17 | 0 | 10.5 | 9.33 | 9.33 | opened | 253 | Znamenka 110/35/10 | 10+10 | 2.72 | 5.24 | 1.48 | 120 | 3.76 | 0 | 10.5 | 6.74 | 6.74 | opened
| Nom. capacity MV, МVА | 10+10 | 1.32 | 1.32 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 1.45 | 1.45 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.2 | 0.03 | 120 | 1.17 | 0 | 10.5 | 9.33 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.59 | 3.79 | 0.03 | 120 | 3.76 | 0 | 10.5 | 6.74
254 | Losmino 35/10 | 2,5+2,5 | 1.14 | 0.4 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened | 254 | Losmino 35/10 | 2,5+2,5 | 0 | 1.14 | 0.4 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.1 | 0.43 | 120 | 0.67 | 0 | 6.615 | 5.945 | 5.945 | opened | 255 | Vskhody 110/35/10 | 6,3+6,3 | 0.11 | 1.21 | 0.43 | 120 | 0.78 | 0 | 6.615 | 5.835 | 5.835 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.42 | 0.42 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.42 | 0.42 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.68 | 0.01 | 120 | 0.67 | 0 | 6.615 | 5.945 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.11 | 0.79 | 0.01 | 120 | 0.78 | 0 | 6.615 | 5.835
| Total: | 3150.6 | 566.25 | [8 empty] | 2: Total:; 3: 3150.6; 4: 254.66; 5: 820.91
| deficit | [8 empty] | -0.37 |  | 2: deficit; Мin. 12: -56.975
| proficit | [8 empty] | 1072.28 |  | 2: proficit; Мin. 12: 848.815