## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 321403 | Belgorodenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 12257114.03 | 0 | 0 | 0 | 0 | 11559846.74 | 485844.4 | 211422.89 | 0
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 10852839.99; Group6: 10331929.65; Group7: 413107.23; Group8: 107803.11
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 0
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 527521.96; Group6: 527521.96
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 868856.78; Group6: 700395.13; Group7: 66439.2; Group8: 102022.45
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 7895.3; Group7: 6297.97; Group8: 1597.33
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 979708.71 | 0 | 0 | 0 | 0 | 838745.72 | 140751.64 | 211.35 | 0
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 703763.35; Group6: 699140.99; Group7: 4411.01; Group8: 211.35
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 0
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 1029.89; Group6: 1029.89
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 274915.47; Group6: 138574.84; Group7: 136340.63
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1464542.48 | 4796158.04 | 2931170.81
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 4840113.95 | 0 | 0 | 0 | 0 | 0 | 1464542.48 | 3375571.47 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 1427872.42 | 0 | 0 | 0 | 0 | 0 | 0 | 1420586.57 | 7285.85
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 2923884.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2923884.96
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 4840113.95 | 1427872.42 | 2923884.96 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 1464542.48; Group6: 1464542.48; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 4796158.04; Group6: 3375571.47; Group7: 1420586.57; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 2931170.81 | 0 | 0 | 0 | 0 | 0 | 7285.85 | 2923884.96 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 11277405.32 | 0 | 0 | 0 | 0 | 10721101.02 | 1809635.24 | 5007369.58 | 2931170.81
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | Group1: 10376189.24; Group6: 5683230.75; Group7: 285351.12; Group8: 1822245.95; Group9: 2585361.42
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 1174275.78 | 0 | 0 | 0 | 0 | 0 | 80822.9 | 712667.65 | 380785.23
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 621662.12 | 0 | 0 | 0 | 0 | 0 | 80822.9 | 540839.22 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 171828.43 | 0 | 0 | 0 | 0 | 0 | 0 | 171828.43
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 380785.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380785.23
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 11347.23; Group9: 11347.23
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 901216.08 | 0 | 0 | 0 | 0 | 197756.32 | 96411.7 | 261238.67 | 345809.39
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 7.99 | 0 | 0 | 0 | 0 | 1.84 | 5.33 | 5.22 | 11.8
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 834335.06 | 0 | 0 | 0 | 0 | 197756.33 | 96411.69 | 261238.67 | 278928.37
8.1 | conditional permanent losses, thousand kWh | 81 | 159836.24 | 0 | 0 | 0 | 0 | 36502.15 | 21633.74 | 79258.25 | 22442.1
8.2 | losses under load, thousand kWh | 82 | 628846.76 | 0 | 0 | 0 | 0 | 137810.95 | 70497.64 | 170490.29 | 250047.88
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 45652.06 | 0 | 0 | 0 | 0 | 23443.23 | 4280.31 | 11490.13 | 6438.39
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 7.4 | 0 | 0 | 0 | 0 | 1.84 | 5.33 | 5.22 | 9.52
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 7.65
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 7.51
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10721101.02 | 0 | 1809635.24 | 0 | 5007369.58 | 0 | 2931170.81 | 0 | 11277405.32 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36502.15 | 0.34 | 21633.74 | 1.2 | 79258.25 | 1.58 | 22442.1 | 0.77 | 159836.24 | 1.42
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 19971.7 | 0.19 | 11042.5 | 0.61 | 58899.81 | 1.18 |  | 0 | 89914.01 | 0.8
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 2807.09 | 0.03 |  | 0 |  | 0 |  | 0 | 2807.09 | 0.02
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 3181.65 | 0.03 | 2636.36 | 0.15 | 8839.14 | 0.18 |  | 0 | 14657.15 | 0.13
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 2009.3 | 0.04 |  | 0 | 2009.3 | 0.02
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 422.4 | 0 | 200 | 0.01 | 586.14 | 0.01 | 487.85 | 0.02 | 1696.39 | 0.02
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 1958 | 0.02 | 1994.4 | 0.11 | 7166.1 | 0.14 |  | 0 | 11118.5 | 0.1
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 21954.25 | 0.75 | 21954.25 | 0.19
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 583 | 0.01 | 366 | 0.02 | 162.5 | 0 |  | 0 | 1111.5 | 0.01
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 159 | 0 | 55.42 | 0 | 20.2 | 0 |  | 0 | 234.62 | 0
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 11.22 | 0 | 2.3 | 0 | 0.09 | 0 |  | 0 | 13.61 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 30.36 | 0 | 5.76 | 0 |  | 0 |  | 0 | 36.12 | 0
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 50.08 | 0 |  | 0 | 50.08 | 0
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 7377.73 | 0.07 | 5331 | 0.29 | 1524.89 | 0.03 |  | 0 | 14233.62 | 0.13
2.15 | Electricity consumption for melting ice | 4215 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137810.95 | 1.29 | 70497.64 | 3.9 | 170490.29 | 3.4 | 250047.88 | 8.53 | 628846.76 | 5.58
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 11993.56 | 0.11 | 8376.64 | 0.46 | 20105.57 | 0.4 |  | 0 | 40475.77 | 0.36
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 125817.39 | 1.17 | 62121 | 3.43 | 150384.72 | 3 | 250047.88 | 0 | 588370.99 | 5.22
3.3 | Losses under load in current limiting reactors | 4303 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174313.1 | 1.63 | 92131.38 | 5.09 | 249748.54 | 4.99 | 272489.98 | 9.3 | 788683 | 6.99
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 23443.23 | 0.22 | 4280.31 | 0.24 | 11490.13 | 0.23 | 6438.39 | 0.22 | 45652.06 | 0.4
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197756.33 | 1.84 | 96411.69 | 5.33 | 261238.67 | 5.22 | 278928.37 | 9.52 | 834335.06 | 7.4
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | Group1: Victor Ivanovich Filatov; Group2: Deputy General Director of IDGC of Centre - Belgorodenergo division director; Group3: 304577; Group4: Filatov@mrsk-1.ru
| Responsible for completing the template | 412 | Group1: Alexander Vladimirovich Zhivtsov; Group2: Head of Forecasting electric energy and power balance and loss analysis Department; Group3: 581779; Group4: Zhivtsov_AV@mrsk-1.ru
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | Group1: IDGC of Centre - Belgorodenergo division
| Postal address | 422 | Group1: 308000 Belgorod, Preobrazhenskaya street 42
| Code of the reporting organization per Russian Business and Organization Classification | 423 | Group1: 75720657
| Activity code per Russian National Classifier of Economic Activities | 424 | Group1: 74.15
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | Group1: 45286565000
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | Group1: 41002
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | Group1: 47
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | Group1: 16
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | Group1: 14401000000
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16