## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 340903 | Bryanskenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 5319383.17 | 0 | 0 | 0 | 0 | 4774455.55 | 152858.8 | 391764.91 | 303.91
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 36744.4; Group6: 36744.4
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 4855532.15; Group6: 4481860.98; Group7: 64267.42; Group8: 309289.7; Group9: 114.05
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 97684.45; Group6: 97519.93; Group7: 164.52
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 329422.17; Group6: 158330.24; Group7: 88426.86; Group8: 82475.21; Group9: 189.86
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 0
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 1343175.38 | 0 | 0 | 0 | 0 | 1336637.65 | 6077.91 | 459.82 | 0
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 1.32; Group6: 1.32
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 788432.49; Group6: 786924.33; Group7: 1048.34; Group8: 459.82
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 305901.3; Group6: 300872.17; Group7: 5029.13
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 248840.27; Group6: 248839.83; Group7: 0.44
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 603196.68 | 2740444.67 | 392981.25
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 2653374.09 | 0 | 0 | 0 | 0 | 0 | 603196.68 | 2050177.41 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 690267.26 | 0 | 0 | 0 | 0 | 0 | 0 | 690267.26 | 0
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 392981.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392981.25
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 2653374.09 | 690267.26 | 392981.25 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 603196.68; Group6: 603196.68; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 2740444.67; Group6: 2050177.41; Group7: 690267.26; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 392981.25 | 0 | 0 | 0 | 0 | 0 |  | 392981.25 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 3976207.79 | 0 | 0 | 0 | 0 | 3437817.9 | 749977.57 | 3131749.76 | 393285.16
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | Group1: 3741820.8; Group6: 729445.17; Group7: 46359.11; Group8: 2665014.1; Group9: 301002.42
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 2313085.3 | 0 | 0 | 0 | 0 | 0 | 0 | 2297124.62 | 15960.68
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 1835402.07 | 0 | 0 | 0 | 0 | 0 |  | 1835402.07 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 461722.55 | 0 | 0 | 0 | 0 | 0 | 0 | 461722.55
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 15960.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15960.68
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 7233.45; Group8: 7215.94; Group9: 17.51
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 234386.99 | 0 | 0 | 0 | 0 | 54998.64 | 13351.2 | 73754.41 | 92282.74
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 5.89 | 0 | 0 | 0 | 0 | 1.6 | 1.78 | 2.36 | 23.46
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 199656.99 | 0 | 0 | 0 | 0 | 106681.16 | 26134.95 | 43995.53 | 22845.35
8.1 | conditional permanent losses, thousand kWh | 81 | 93267.08 | 0 | 0 | 0 | 0 | 42442.58 | 14923.25 | 30710.36 | 5190.89
8.2 | losses under load, thousand kWh | 82 | 99852.05 | 0 | 0 | 0 | 0 | 60423.44 | 10822.94 | 12465.55 | 16140.12
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 6537.86 | 0 | 0 | 0 | 0 | 3815.14 | 388.76 | 819.62 | 1514.34
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 5.02 | 0 | 0 | 0 | 0 | 3.1 | 3.48 | 1.4 | 5.81
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 5.46
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 6.15
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3437817.9 | 0 | 749977.57 | 0 | 3131749.76 | 0 | 393285.16 | 0 | 3976207.79 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42442.58 | 1.23 | 14923.25 | 1.99 | 30710.36 | 0.98 | 5190.89 | 1.32 | 93267.08 | 2.35
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 23558.82 | 0.69 | 9221.84 | 1.23 | 21606.9 | 0.69 |  | 0 | 54387.56 | 1.37
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 1436 | 0.04 |  | 0 |  | 0 |  | 0 | 1436 | 0.04
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 4595.22 | 0.13 | 2395.51 | 0.32 | 6724.38 | 0.21 |  | 0 | 13715.11 | 0.34
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 68.33 | 0 |  | 0 | 68.33 | 0
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 354.17 | 0.01 | 85.22 | 0.01 | 353.14 | 0.01 | 276.26 | 0.07 | 1068.79 | 0.03
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 1936 | 0.06 | 766.86 | 0.1 | 533.35 | 0.02 |  | 0 | 3236.21 | 0.08
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 4914.63 | 1.25 | 4914.63 | 0.12
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 695.37 | 0.02 | 240.71 | 0.03 |  | 0 |  | 0 | 936.08 | 0.02
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 187.81 | 0.01 | 62.17 | 0.01 | 16.77 | 0 |  | 0 | 266.75 | 0.01
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 11.43 | 0 | 4.72 | 0 | 0.43 | 0 |  | 0 | 16.58 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 34.52 | 0 | 1.78 | 0 |  | 0 |  | 0 | 36.3 | 0
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 | 4215.33 | 0.12 | 282.56 | 0.04 |  | 0 |  | 0 | 4497.89 | 0.11
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 5417.91 | 0.16 | 1861.88 | 0.25 | 1407.06 | 0.04 |  | 0 | 8686.85 | 0.22
2.15 | Electricity consumption for melting ice | 4215 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60423.44 | 1.76 | 10822.94 | 1.44 | 12465.55 | 0.4 | 16140.12 | 4.1 | 99852.05 | 2.51
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 6756.82 | 0.2 | 2538.16 | 0.34 | 997.42 | 0.03 |  | 0 | 10292.4 | 0.26
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 53616.8 | 1.56 | 8284.78 | 1.1 | 11468.13 | 0.37 | 16140.12 | 0 | 89509.83 | 2.25
3.3 | Losses under load in current limiting reactors | 4303 |  | 0 |  | 0 |  | 0 |  | 0 | 49.82 | 0 |  | 0 |  | 0 |  | 0 | 49.82 | 0
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102866.02 | 2.99 | 25746.19 | 3.43 | 43175.91 | 1.38 | 21331.01 | 5.42 | 193119.13 | 4.86
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 3815.14 | 0.11 | 388.76 | 0.05 | 819.62 | 0.03 | 1514.34 | 0.39 | 6537.86 | 0.16
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106681.16 | 3.1 | 26134.95 | 3.48 | 43995.53 | 1.4 | 22845.35 | 5.81 | 199656.99 | 5.02
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | Group1: Burenok N.V.; Group2: Division director
| Responsible for completing the template | 412 | Group1: Chernysheva L.V.; Group2: leading specialist; Group3: 67-20-77; Group4: Chernyshova.LV@mrsk-1.ru
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | bar: Group1
| Postal address | 422 | bar: Group1
| Code of the reporting organization per Russian Business and Organization Classification | 423 | bar: Group1
| Activity code per Russian National Classifier of Economic Activities | 424 | bar: Group1
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | bar: Group1
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | bar: Group1
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | bar: Group1
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | bar: Group1
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | bar: Group1
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16