## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 321103 | Kurskenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 7216532.94 | 0 | 0 | 0 | 0 | 6861642.89 | 182818.43 | 172071.62 | 0
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 6149752.58; Group6: 6054318.22; Group7: 23976.47; Group8: 71457.89
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 52416.67; Group6: 52416.67
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 6667.15; Group6: 6667.03; Group7: 0.12
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 996136.1; Group6: 742246.66; Group7: 153275.71; Group8: 100613.73
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 11560.44; Group6: 5994.31; Group7: 5566.13
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 1573832.96 | 0 | 0 | 0 | 0 | 1536592.05 | 9989.74 | 26887.4 | 363.77
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 363212.43; Group6: 362639.54; Group7: 0.34; Group8: 208.78; Group9: 363.77
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 25495.14; Group6: 25495.14
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 752049.38; Group6: 751711.2; Group7: 338.18
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 433076.01; Group6: 396746.17; Group7: 9651.22; Group8: 26678.62
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 947051.61 | 2466195.99 | 676719.15
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 2527601.9 | 0 | 0 | 0 | 0 | 0 | 947051.61 | 1580550.29 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 885645.7 | 0 | 0 | 0 | 0 | 0 | 0 | 885645.7 | 0
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 676719.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 676719.15
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 2527601.9 | 885645.7 | 676719.15 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 947051.61; Group6: 947051.61; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 2466195.99; Group6: 1580550.29; Group7: 885645.7; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 676719.15 | 0 | 0 | 0 | 0 | 0 |  | 676719.15 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 5642699.98 | 0 | 0 | 0 | 0 | 5325050.84 | 1119880.3 | 2611380.21 | 676355.38
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | Group1: 5149774.19; Group6: 2634109.93; Group7: 154027.97; Group8: 1819098.18; Group9: 542538.11
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 1593650.03 | 0 | 0 | 0 | 0 | 0 | 70049.8 | 1498599.2 | 25001.03
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 1216608.6 | 0 | 0 | 0 | 0 | 0 | 70049.8 | 1146558.8 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 352040.4 | 0 | 0 | 0 | 0 | 0 | 0 | 352040.4
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 25001.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25001.03
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 13645.14; Group9: 13645.14
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 492925.79 | 0 | 0 | 0 | 0 | 163339.01 | 80206.63 | 115562.88 | 133817.27
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 8.74 | 0 | 0 | 0 | 0 | 3.07 | 7.16 | 4.43 | 19.79
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 476962.68 | 0 | 0 | 0 | 0 | 247649.59 | 42739.18 | 95867.37 | 90706.54
8.1 | conditional permanent losses, thousand kWh | 81 | 150593.39 | 0 | 0 | 0 | 0 | 48158.33 | 24469.35 | 68694.15 | 9271.56
8.2 | losses under load, thousand kWh | 82 | 293118.38 | 0 | 0 | 0 | 0 | 180968.15 | 16692.83 | 22692.92 | 72764.48
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 33250.91 | 0 | 0 | 0 | 0 | 18523.11 | 1577 | 4480.3 | 8670.5
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 8.45 | 0 | 0 | 0 | 0 | 4.65 | 3.82 | 3.67 | 13.41
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 8.53
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 8.53
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5325050.84 | 0 | 1119880.3 | 0 | 2611380.21 | 0 | 676355.38 | 0 | 5642699.98 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48158.33 | 0.9 | 24469.35 | 2.18 | 68694.15 | 2.63 | 9271.56 | 1.37 | 150593.39 | 2.67
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 30210 | 0.57 | 14476.3 | 1.29 | 46184.6 | 1.77 |  | 0 | 90870.9 | 1.61
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 1013.01 | 0.02 |  | 0 |  | 0 |  | 0 | 1013.01 | 0.02
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 3321.8 | 0.06 | 2522.1 | 0.23 | 5800 | 0.22 |  | 0 | 11643.9 | 0.21
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 110.4 | 0 |  | 0 | 110.4 | 0
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 1215.46 | 0.02 | 901.58 | 0.08 | 1005.63 | 0.04 | 1096.59 | 0.16 | 4219.26 | 0.07
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 3325.31 | 0.06 | 1856.45 | 0.17 | 973.08 | 0.04 |  | 0 | 6154.84 | 0.11
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 | 21.03 | 0 | 49.8 | 0 | 150.98 | 0.01 | 8174.97 | 1.21 | 8396.78 | 0.15
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 902.7 | 0.02 | 588.1 | 0.05 | 12701.2 | 0.49 |  | 0 | 14192 | 0.25
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 310.11 | 0.01 | 111.74 | 0.01 | 641.43 | 0.02 |  | 0 | 1063.28 | 0.02
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 2.61 | 0 | 0.09 | 0 | 0.03 | 0 |  | 0 | 2.73 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 70.5 | 0 | 6.99 | 0 |  | 0 |  | 0 | 77.49 | 0
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 | 294.8 | 0.01 |  | 0 | 759.5 | 0.03 |  | 0 | 1054.3 | 0.02
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 7435.5 | 0.14 | 3953.4 | 0.35 | 367.3 | 0.01 |  | 0 | 11756.2 | 0.21
2.15 | Electricity consumption for melting ice | 4215 |  | 0 |  | 0 |  | 0 |  | 0 | 35.5 | 0 | 2.8 | 0 |  | 0 |  | 0 | 38.3 | 0
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180968.15 | 3.4 | 16692.83 | 1.49 | 22692.92 | 0.87 | 72764.48 | 10.76 | 293118.38 | 5.19
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 7347 | 0.14 | 3340.33 | 0.3 | 2218.88 | 0.08 |  | 0 | 12906.21 | 0.23
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 173527 | 3.26 | 13352.5 | 1.19 | 20474.04 | 0.78 | 72764.48 | 0 | 280118.02 | 4.96
3.3 | Losses under load in current limiting reactors | 4303 |  | 0 |  | 0 |  | 0 |  | 0 | 94.15 | 0 |  | 0 |  | 0 |  | 0 | 94.15 | 0
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229126.48 | 4.3 | 41162.18 | 3.68 | 91387.07 | 3.5 | 82036.04 | 12.13 | 443711.77 | 7.86
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 18523.11 | 0.35 | 1577 | 0.14 | 4480.3 | 0.17 | 8670.5 | 1.28 | 33250.91 | 0.59
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247649.59 | 4.65 | 42739.18 | 3.82 | 95867.37 | 3.67 | 90706.54 | 13.41 | 476962.68 | 8.45
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | Group1: A.V. Pilyugin; Group2: Deputy General Director of IDGC of Centre - Kurskenergo division director; Group3: [4712]55-73-59; Group4: pilyugin.av@mrsk-1.ru
| Responsible for completing the template | 412 | Group1: A.V. Pozdnyakov; Group2: Head of Forecasting electric energy and power balance and loss analysis Department; Group3: [4712]55-73-89; Group4: pozdnyakov.alv@mrsk-1.ru
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | Group1: IDGC of Centre - Kurskenergo division
| Postal address | 422 | Group1: 305029, Kursk, K. Marx street 27
| Code of the reporting organization per Russian Business and Organization Classification | 423 | Group1: 00104610
| Activity code per Russian National Classifier of Economic Activities | 424 | Group1: 40.12.
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | Group1: 38401365000
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | Group1: 49014
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | Group1: 90
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | Group1: 16
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | bar: Group1
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16