## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 311203 | Lipetsenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 9540814.99 | 0 | 0 | 0 | 514119.11 | 8308897.65 | 416782.88 | 301015.35 | 0
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 1.25; Group8: 1.25
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 7716669.69; Group5: 514119.11; Group6: 6595516.6; Group7: 388807.21; Group8: 218226.77
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 23314.44; Group6: 166.85; Group7: 22955.99; Group8: 191.6
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 1794595.03; Group6: 1713214.2; Group7: 1.37; Group8: 81379.46
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 6234.58; Group7: 5018.31; Group8: 1216.27
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 2128527.02 | 0 | 0 | 0 | 0 | 2108020.44 | 9440.38 | 11066.2 | 0
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 862.62; Group7: 178.04; Group8: 684.58
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 1970194.91; Group6: 1959771.96; Group7: 9262.34; Group8: 1160.61
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 15132.76; Group6: 5911.75; Group8: 9221.01
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 142336.73; Group6: 142336.73
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1002164.15 | 3107285.25 | 807244.47
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 3004641.33 | 0 | 0 | 0 | 0 | 0 | 1002164.15 | 2002477.18 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 1104808.07 | 0 | 0 | 0 | 0 | 0 | 0 | 1104808.07 | 0
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 807244.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807244.47
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 3004641.33 | 1104808.07 | 807244.47 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 1002164.15; Group6: 1002164.15; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 3107285.25; Group6: 2002477.18; Group7: 1104808.07; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 807244.47 | 0 | 0 | 0 | 0 | 0 |  | 807244.47 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 7412287.97 | 0 | 0 | 0 | 514119.11 | 6200877.21 | 1409506.65 | 3397234.4 | 807244.47
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | 6736988.71 |  |  |  | 514119.11 | 2970970.55 | 181832.42 | 2404894.18 | 665172.45
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 2224699.81 | 0 | 0 | 0 | 0 | 0 | 177072.33 | 1996354.33 | 51273.15
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 1989013.17 | 0 | 0 | 0 | 0 | 0 | 177072.33 | 1811940.84 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 184647.09 | 0 | 0 | 0 | 0 | 0 | 0 | 184413.49 | 233.6
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 51039.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51039.55
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 17192.13; Group9: 17192.13
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 675299.26 | 0 | 0 | 0 | 0 | 225265.33 | 122866.16 | 185095.75 | 142072.02
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 9.11 | 0 | 0 | 0 | 0 | 3.63 | 8.72 | 5.45 | 17.6
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 675299.26 | 0 | 0 | 0 | 0 | 225265.33 | 122866.17 | 185095.75 | 142072.01
8.1 | conditional permanent losses, thousand kWh | 81 | 124615.4 | 0 | 0 | 0 | 0 | 32654.9 | 23641.84 | 60640.13 | 7678.53
8.2 | losses under load, thousand kWh | 82 | 452800.75 | 0 | 0 | 0 | 0 | 148991.85 | 78317.34 | 97849.86 | 127641.7
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 97883.11 | 0 | 0 | 0 | 0 | 43618.58 | 20906.99 | 26605.76 | 6751.78
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 9.11 | 0 | 0 | 0 | 0 | 3.63 | 8.72 | 5.45 | 17.6
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 9.48
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 8.86
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 514119.11 | 0 | 6200877.21 | 0 | 1409506.65 | 0 | 3397234.4 | 0 | 807244.47 | 0 | 7412287.97 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32654.9 | 0.53 | 23641.84 | 1.68 | 60640.13 | 1.78 | 7678.53 | 0.95 | 124615.4 | 1.68
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 21734.28 | 0.35 | 17956.67 | 1.27 | 47619.05 | 1.4 |  | 0 | 87310 | 1.18
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 2195.69 | 0.04 |  | 0 |  | 0 |  | 0 | 2195.69 | 0.03
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 3528.85 | 0.06 | 2581.62 | 0.18 | 5959.6 | 0.18 |  | 0 | 12070.07 | 0.16
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 54.9 | 0 |  | 0 | 54.9 | 0
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 370.64 | 0.01 | 260.56 | 0.02 | 2321.66 | 0.07 | 3130.87 | 0.39 | 6083.73 | 0.08
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 503.44 | 0.01 | 332.28 | 0.02 | 1767.05 | 0.05 | 2164.5 | 0.27 | 4767.27 | 0.06
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1748.66 | 0.22 | 1748.66 | 0.02
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 631.51 | 0.01 | 435.96 | 0.03 | 559.33 | 0.02 |  | 0 | 1626.8 | 0.02
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 277.67 | 0 | 27.74 | 0 | 681.76 | 0.02 |  | 0 | 987.17 | 0.01
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 16.53 | 0 | 3.28 | 0 | 13.46 | 0 |  | 0 | 33.27 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 82.75 | 0 | 77.33 | 0.01 | 315.03 | 0.01 |  | 0 | 475.11 | 0.01
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 | 21.24 | 0 | 21.24 | 0 | 21.24 | 0 |  | 0 | 63.72 | 0
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 3292.3 | 0.05 | 1945.16 | 0.14 | 1327.05 | 0.04 | 634.5 | 0.08 | 7199.01 | 0.1
2.15 | Electricity consumption for melting ice | 4215 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148991.85 | 2.4 | 78317.34 | 5.56 | 97849.86 | 2.88 | 127641.7 | 15.81 | 452800.75 | 6.11
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 44617.32 | 0.72 | 16938.49 | 1.2 | 16892.46 | 0.5 |  | 0 | 78448.27 | 1.06
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 104374.53 | 1.68 | 61378.85 | 4.35 | 80361.83 | 2.37 | 127641.7 | 0 | 373756.91 | 5.04
3.3 | Losses under load in current limiting reactors | 4303 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 595.57 | 0.02 |  | 0 | 595.57 | 0.01
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181646.75 | 2.93 | 101959.18 | 7.23 | 158489.99 | 4.67 | 135320.23 | 16.76 | 577416.15 | 7.79
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 43618.58 | 0.7 | 20906.99 | 1.48 | 26605.76 | 0.78 | 6751.78 | 0.84 | 97883.11 | 1.32
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225265.33 | 3.63 | 122866.17 | 8.72 | 185095.75 | 5.45 | 142072.01 | 17.6 | 675299.26 | 9.11
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | Group1: A.N. Konanykhin; Group2: Deputy General Director of IDGC of Centre - Lipetskenergo division director; Group3: [4742] 22-83-60
| Responsible for completing the template | 412 | Group1: N.I. Vetrova; Group2: Head of Forecasting electric energy and power balance and loss analysis Department; Group3: [4742] 22-82-60; Group4: vetrova.ni@mrsk-1.ru
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | Group1: IDGC of Centre - Lipetskenergo division
| Postal address | 422 | Group1: 398001 Lipetsk, 50 years of NLMK 33
| Code of the reporting organization per Russian Business and Organization Classification | 423 | bar: Group1
| Activity code per Russian National Classifier of Economic Activities | 424 | bar: Group1
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | bar: Group1
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | bar: Group1
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | bar: Group1
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | bar: Group1
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | bar: Group1
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16