## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 311003 | Orelenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 4249527.02 | 0 | 0 | 0 | 0 | 4077116.27 | 14598.12 | 157433.59 | 379.04
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 62097.09; Group6: 62097.09
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 2654515.86; Group6: 2527837.4; Group7: 7590.58; Group8: 119087.88
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 453791.68; Group6: 448439.55; Group7: 5352.13
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 1079122.39; Group6: 1038742.23; Group7: 1655.41; Group8: 38345.71; Group9: 379.04
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 0
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 1884924.42 | 0 | 0 | 0 | 0 | 1869345.56 | 14506.57 | 1072.29 | 0
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 0
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 1293562.66; Group6: 1292492.74; Group8: 1069.92
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 562032.25; Group6: 558380.24; Group7: 3652.01
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 29329.51; Group6: 18472.58; Group7: 10854.56; Group8: 2.37
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 418251.77 | 1678688.48 | 380581.54
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 1698614.2 | 0 | 0 | 0 | 0 | 0 | 418251.77 | 1280362.43 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 398326.05 | 0 | 0 | 0 | 0 | 0 | 0 | 398326.05 | 0
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 380581.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380581.54
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 1698614.2 | 398326.05 | 380581.54 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 418251.77; Group6: 418251.77; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 1678688.48; Group6: 1280362.43; Group7: 398326.05; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 380581.54 | 0 | 0 | 0 | 0 | 0 |  | 380581.54 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 2364602.6 | 0 | 0 | 0 | 0 | 2207770.71 | 418343.32 | 1835049.78 | 380960.58
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | Group1: 2054024.37; Group6: 360678.62; Group7: 2835.78; Group8: 1370859.59; Group9: 319650.38
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 540991.5 | 0 | 0 | 0 | 0 | 0 | 0 | 484758.76 | 56232.74
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 454471.28 | 0 | 0 | 0 | 0 | 0 |  | 454471.28 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 86520.22 | 0 | 0 | 0 | 0 | 0 | 0 | 30287.48 | 56232.74
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 4260.77; Group8: 982.06; Group9: 3278.71
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 310578.23 | 0 | 0 | 0 | 0 | 148477.89 | 17181.49 | 83608.65 | 61310.2
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 13.13 | 0 | 0 | 0 | 0 | 6.73 | 4.11 | 4.56 | 16.09
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 288229.68 | 0 | 0 | 0 | 0 | 148477.89 | 17181.49 | 83608.65 | 38961.65
8.1 | conditional permanent losses, thousand kWh | 81 | 78592.34 | 0 | 0 | 0 | 0 | 31321 | 12664.56 | 30801.99 | 3804.79
8.2 | losses under load, thousand kWh | 82 | 191737.12 | 0 | 0 | 0 | 0 | 109161.97 | 3002 | 45973.15 | 33600
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 17900.22 | 0 | 0 | 0 | 0 | 7994.92 | 1514.93 | 6833.51 | 1556.86
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 12.19 | 0 | 0 | 0 | 0 | 6.73 | 4.11 | 4.56 | 10.23
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 11.59; Гр6: 6.02; Гр7: 4.84; Гр8: 4.48; Гр9: 8.06
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 11.59; Гр6: 6.02; Гр7: 4.84; Гр8: 4.48; Гр9: 8.06
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2207770.71 | 0 | 418343.32 | 0 | 1835049.78 | 0 | 380960.58 | 0 | 2364602.6 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31321 | 1.42 | 12664.56 | 3.03 | 30801.99 | 1.68 | 3804.79 | 1 | 78592.34 | 3.32
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 22018 | 1 | 8279 | 1.98 | 24000.67 | 1.31 |  | 0 | 54297.67 | 2.3
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 1686 | 0.08 |  | 0 |  | 0 |  | 0 | 1686 | 0.07
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 2837.32 | 0.13 | 2008.5 | 0.48 | 6552.68 | 0.36 |  | 0 | 11398.5 | 0.48
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 4.37 | 0 | 60.71 | 0 |  | 0 | 65.08 | 0
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 167.98 | 0.01 | 110.46 | 0.03 | 8.16 | 0 |  | 0 | 286.6 | 0.01
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 831.34 | 0.04 | 613.32 | 0.15 | 12.55 | 0 |  | 0 | 1457.21 | 0.06
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 | 7.7 | 0 | 12.35 | 0 | 0.12 | 0 | 3804.79 | 1 | 3824.96 | 0.16
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 547.2 | 0.02 | 269.7 | 0.06 | 3.93 | 0 |  | 0 | 820.83 | 0.03
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 64.32 | 0 | 20.94 | 0.01 | 119.32 | 0.01 |  | 0 | 204.58 | 0.01
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 0.76 | 0 | 0.15 | 0 |  | 0 |  | 0 | 0.91 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 25.74 | 0 | 1.62 | 0 |  | 0 |  | 0 | 27.36 | 0
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 | 121.94 | 0.01 |  | 0 |  | 0 |  | 0 | 121.94 | 0.01
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 3012.7 | 0.14 | 1344.15 | 0.32 | 43.85 | 0 |  | 0 | 4400.7 | 0.19
2.15 | Electricity consumption for melting ice | 4215 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109161.97 | 4.94 | 3002 | 0.72 | 45973.15 | 2.51 | 33600 | 8.82 | 191737.12 | 8.11
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 2696 | 0.12 | 682 | 0.16 | 6096.2 | 0.33 |  | 0 | 9474.2 | 0.4
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 106320.74 | 4.82 | 2320 | 0.55 | 39871.45 | 2.17 | 33600 | 0 | 182112.19 | 7.7
3.3 | Losses under load in current limiting reactors | 4303 |  | 0 |  | 0 |  | 0 |  | 0 | 145.23 | 0.01 |  | 0 | 5.5 | 0 |  | 0 | 150.73 | 0.01
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140482.97 | 6.36 | 15666.56 | 3.74 | 76775.14 | 4.18 | 37404.79 | 9.82 | 270329.46 | 11.43
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 7994.92 | 0.36 | 1514.93 | 0.36 | 6833.51 | 0.37 | 1556.86 | 0.41 | 17900.22 | 0.76
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148477.89 | 6.73 | 17181.49 | 4.11 | 83608.65 | 4.56 | 38961.65 | 10.23 | 288229.68 | 12.19
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | bar: Group1 to Group4
| Responsible for completing the template | 412 | bar: Group1 to Group4
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | bar: Group1
| Postal address | 422 | bar: Group1
| Code of the reporting organization per Russian Business and Organization Classification | 423 | bar: Group1
| Activity code per Russian National Classifier of Economic Activities | 424 | bar: Group1
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | bar: Group1
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | bar: Group1
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | bar: Group1
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | bar: Group1
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | bar: Group1
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16