## Sheet1
Template 10092 The balance of power at voltage levels and the structure of losses in regional grid companies
| Reporting date | December 2010
| Site | 311503 | Tambovenergo division
Section 1. The structure of the balance of power at voltage levels
Item # | Indicator | Page code | Total | 750 kV | 500 kV | 330 kV | 220 kV | 150-110 kV | 27,5-60 kV | 1-20 kV | 0,4 kV
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9
1 | Electrical energy injected into the grid, total, thousand kWh | 1 | 3553418.56 | 0 | 0 | 0 | 0 | 2698069.8 | 222304.02 | 632661.67 | 383.07
1.1 | Injected into the grid of Federal Grid Company, thousand kWh | 11 | Group1: 2619429.91; Group6: 1936408.99; Group7: 208907.49; Group8: 473910.73; Group9: 202.7
1.2 | Injected into the grid of Interregional Grid Companies, thousand kWh | 12 | Group1: 0
1.3 | Injected into the grid of Adjacent Grid Companies, thousand kWh | 13 | Group1: 10210.01; Group6: 10210.01
1.4 | Injected into the grid of Generating Companies, thousand kWh | 14 | Group1: 920705.58; Group6: 751450.8; Group7: 10323.47; Group8: 158750.94; Group9: 180.37
1.5 | Injected into the grid of isolated generating plants, thousand kWh | 15 | Group1: 3073.06; Group7: 3073.06
2 | Electrical energy delivery from the grid, total, thousand kWh | 2 | 486643.61 | 0 | 0 | 0 | 0 | 484131.61 | 76.82 | 2435.18 | 0
2.1 | Delivery to the grid of Federal Grid Company, thousand kWh | 21 | Group1: 236535.22; Group6: 234110.89; Group8: 2424.33
2.2 | Delivery to the grid of Interregional Grid Companies, thousand kWh | 22 | Group1: 91467.71; Group6: 91467.71
2.3 | Delivery to the grid of Adjacent Grid Companies, thousand kWh | 23 | Group1: 0
2.4 | Delivery to the grid of Generating Companies, thousand kWh | 24 | Group1: 158640.68; Group6: 158553.01; Group7: 76.82; Group8: 10.85
3 | Electrical energy Injected into from the grid of adjacent voltage, total, thousand kWh | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 914231.44 | 1743852.44 | 520957.82
3.1 | Injected into the grid of 750 kV, thousand kWh | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | Injected into the grid of 500 kV, thousand kWh | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | Injected into the grid of 330 kV, thousand kWh | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Injected into the grid of 220 kV, thousand kWh | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | Injected into the grid of 110 kV, thousand kWh | 35 | 1938415.47 | 0 | 0 | 0 | 0 | 0 | 914231.44 | 1024184.03 | 0
3.6 | Injected into the grid of 27,5-60 kV, thousand kWh | 36 | 719668.41 | 0 | 0 | 0 | 0 | 0 | 0 | 719668.41 | 0
3.7 | Injected into the grid of 1-20 kV, thousand kWh | 37 | 520957.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520957.82
4 | Delivery of electrical energy to the grid of adjacent voltage, total, thousand kWh | 4 | 0 | 0 | 0 | 0 | 0 | 1938415.47 | 719668.41 | 520957.82 | 0
4.1 | Delivery to the grid of 500 kV, thousand kWh | 41 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Delivery to the grid of 330 kV, thousand kWh | 42 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Delivery to the grid of 220 kV, thousand kWh | 43 | Group1: 0; Group5: 0; Group7: 0; Group8: 0; Group9: 0
4.4 | Delivery to the grid of 110 kV, thousand kWh | 44 | Group1: 0; Group6: 0; Group7: 0; Group8: 0; Group9: 0
4.5 | Delivery to the grid of 27,5-60 kV, thousand kWh | 45 | Group1: 914231.44; Group6: 914231.44; Group7: 0; Group8: 0; Group9: 0
4.6 | Delivery to the grid of 1-20 kV, thousand kWh | 46 | Group1: 1743852.44; Group6: 1024184.03; Group7: 719668.41; Group8: 0; Group9: 0
4.7 | Delivery to the grid of 0,4 kV, thousand kWh | 47 | 520957.82 | 0 | 0 | 0 | 0 | 0 |  | 520957.82 | 0
5 | Electrical energy supply to the grid, thousand kWh | 5 | 3066774.95 | 0 | 0 | 0 | 0 | 2213938.19 | 1136458.64 | 2374078.93 | 521340.89
6 | Volume (amount) of transferred (consumed) electricity, total, thousand kWh | 6 | Group1: 2825809.73; Group6: 207238.63; Group7: 380054.04; Group8: 1789694.08; Group9: 448822.98
6.1 | Volume (amount) of transferred (consumed) electricity to customers directly connected to the buses of substations, thousand kWh | 61 | 1639184.8 | 0 | 0 | 0 | 0 | 0 | 244587.9 | 1389555.82 | 5041.08
6.1.1 | primary voltage level of HV substations, thousand kWh | 611 | 1483674.7 | 0 | 0 | 0 | 0 | 0 | 244587.9 | 1239086.8 | 0
6.1.2 | primary voltage level of MV1 substations, thousand kWh | 612 | 150469.02 | 0 | 0 | 0 | 0 | 0 | 0 | 150469.02
6.1.3 | primary voltage level of MV11 substations, thousand kWh | 613 | 5041.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5041.08
6.2 | consumption due to production (including economic) needs, thousand kWh | 62 | Group1: 8557.01; Group8: 6891.89; Group9: 1665.12
7 | Actual (reporting) losses of electricity in the grid, thousand kWh | 7 | 240965.22 | 0 | 0 | 0 | 0 | 68284.09 | 36736.19 | 63427.03 | 72517.91
7.1 | The ratio of actual (reporting) losses of electricity as a percentage of electricity supply to the grid, % | 71 | 7.86 | 0 | 0 | 0 | 0 | 3.08 | 3.23 | 2.67 | 13.91
8 | Technical losses of electrical energy, total, thousand kWh | 8 | 240965.22 | 0 | 0 | 0 | 0 | 68284.09 | 36736.19 | 63427.03 | 72517.91
8.1 | conditional permanent losses, thousand kWh | 81 | 100013.3 | 0 | 0 | 0 | 0 | 34987.74 | 18894.48 | 39909.34 | 6221.74
8.2 | losses under load, thousand kWh | 82 | 129649.6 | 0 | 0 | 0 | 0 | 29137.85 | 14766.95 | 20923.55 | 64821.25
8.3 | losses due to allowed accuracy of metering devices, thousand kWh | 83 | 11302.32 | 0 | 0 | 0 | 0 | 4158.5 | 3074.76 | 2594.14 | 1474.92
8.4 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, % | 84 | 7.86 | 0 | 0 | 0 | 0 | 3.08 | 3.23 | 2.67 | 13.91
Раздел Норматив
Номер статьи. | Наименование | Код стр. | Всего | 750 кВ | 500 кВ | 330 кВ | 220 кВ | 150-110 кВ | 27,5-60 кВ | 1-20 кВ | 0,4 кВ
|  |  | Гр1 | Гр2 | Гр3 | Гр4 | Гр5 | Гр6 | Гр7 | Гр8 | Гр9
8.5 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, approved by the Ministry of Energy of the Russian Federation, % | 85 | Гр1: 7.84; Гр6: 3.72; Гр7: 3.61; Гр8: 2.38; Гр9: 12.49
8.6 | The ratio of technological losses of electricity as a percentage of electricity supply to the grid, adopted by the regulator, % | 86 | Гр1: 7.98; Гр6: 2.94; Гр7: 4.8; Гр8: 6.03; Гр9: 12.91
Section 2. The structure of technical losses of electricity
Item # | Name of the structural components | Page code | 750 kV, thousand kWh | 750 kV, % | 500 kV, thousand kWh | 500 kV, % | 350 kV, thousand kWh | 350 kV, % | 220 kV, thousand kWh | 220 kV, % | 150 - 110 kV, thousand kWh | 150 - 110 kV, % | 27,5 - 60 kV, thousand kWh | 27,5 - 60 kV, % | 1 - 20 kV, thousand kWh | 1 - 20 kV, % | 0,4 kV, thousand kWh | 0,4 kV, % | total, thousand kWh | total, %
|  |  | Group1 | Group2 | Group3 | Group4 | Group5 | Group6 | Group7 | Group8 | Group9 | Group10 | Group11 | Group12 | Group13 | Group14 | Group15 | Group16 | Group17 | Group18
1 | Electrical energy supplied to the grid | 4100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2213938.19 | 0 | 1136458.64 | 0 | 2374078.93 | 0 | 521340.89 | 0 | 3066774.95 | 0
2 | conditional permanent losses of electrical energy | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34987.74 | 1.58 | 18894.48 | 1.66 | 39909.34 | 1.68 | 6221.74 | 1.19 | 100013.3 | 3.26
2.1 | Loss on idling transformers | 4201 |  | 0 |  | 0 |  | 0 |  | 0 | 21400.19 | 0.97 | 11036.87 | 0.97 | 34021.56 | 1.43 |  | 0 | 66458.62 | 2.17
2.2 | Loss on corona discharge in overhead lines | 4202 |  | 0 |  | 0 |  | 0 |  | 0 | 2000.6 | 0.09 |  | 0 |  | 0 |  | 0 | 2000.6 | 0.07
2.3 | Surface-leakage current in overhead lines | 4203 |  | 0 |  | 0 |  | 0 |  | 0 | 4136.6 | 0.19 | 3139.39 | 0.28 | 5271.99 | 0.22 |  | 0 | 12547.98 | 0.41
2.4 | Insulation losses in cable lines | 4204 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 77.52 | 0 |  | 0 | 77.52 | 0
2.5 | Measuring current transformer losses | 4205 |  | 0 |  | 0 |  | 0 |  | 0 | 425.27 | 0.02 | 265.86 | 0.02 | 33.16 | 0 | 68.94 | 0.01 | 793.23 | 0.03
2.6 | Measuring voltage transformer losses | 4206 |  | 0 |  | 0 |  | 0 |  | 0 | 732.57 | 0.03 | 705 | 0.06 | 14.22 | 0 |  | 0 | 1451.79 | 0.05
2.7 | Losses in directly connected meters | 4207 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0.25 | 0 | 6152.8 | 1.18 | 6153.05 | 0.2
2.8 | Losses in shunt reactors | 4208 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
2.9 | Losses in the connecting wires and busbars of substations | 4209 |  | 0 |  | 0 |  | 0 |  | 0 | 736.95 | 0.03 | 568.18 | 0.05 |  | 0 |  | 0 | 1305.13 | 0.04
2.10 | Losses in valve-type arresters | 4210 |  | 0 |  | 0 |  | 0 |  | 0 | 91.96 | 0 | 36.94 | 0 | 118.36 | 0 |  | 0 | 247.26 | 0.01
2.11 | Losses in surge arresters | 4211 |  | 0 |  | 0 |  | 0 |  | 0 | 3.33 | 0 |  | 0 | 0.12 | 0 |  | 0 | 3.45 | 0
2.12 | Losses in HF communication connected devices | 4212 |  | 0 |  | 0 |  | 0 |  | 0 | 39.25 | 0 | 293.37 | 0.03 |  | 0 |  | 0 | 332.62 | 0.01
2.13 | Losses in compensating devices | 4213 |  | 0 |  | 0 |  | 0 |  | 0 | 1407.88 | 0.06 |  | 0 | 200 | 0.01 |  | 0 | 1607.88 | 0.05
2.14 | Electrical energy utility consumption | 4214 |  | 0 |  | 0 |  | 0 |  | 0 | 3516.06 | 0.16 | 2215.17 | 0.19 |  | 0 |  | 0 | 5731.23 | 0.19
2.15 | Electricity consumption for melting ice | 4215 |  | 0 |  | 0 |  | 0 |  | 0 | 497.08 | 0.02 | 633.7 | 0.06 | 172.16 | 0.01 |  | 0 | 1302.94 | 0.04
3 | Losses of electrical energy under load | 4300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29137.85 | 1.32 | 14766.95 | 1.3 | 20923.55 | 0.88 | 64821.25 | 12.43 | 129649.6 | 4.23
3.1 | Losses under load in transformers | 4301 |  | 0 |  | 0 |  | 0 |  | 0 | 5722 | 0.26 | 2756.41 | 0.24 | 2135.13 | 0.09 |  | 0 | 10613.54 | 0.35
3.2 | Losses under load in power lines | 4302 |  | 0 |  | 0 |  | 0 |  | 0 | 23387.34 | 1.06 | 12010.54 | 1.06 | 18788.42 | 0.79 | 64821.25 | 0 | 119007.55 | 3.88
3.3 | Losses under load in current limiting reactors | 4303 |  | 0 |  | 0 |  | 0 |  | 0 | 28.51 | 0 |  | 0 |  | 0 |  | 0 | 28.51 | 0
3.4 | Losses under load in busbars | 4304 | Group2: 0; Group4: 0; Group6: 0; Group8: 0; Group10: 0; Group12: 0; Group14: 0; Group16: 0; Group17: 0; Group18: 0
4 | Technical losses of eklectrical energy | 4400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64125.59 | 2.9 | 33661.43 | 2.96 | 60832.89 | 2.56 | 71042.99 | 13.63 | 229662.9 | 7.49
5 | Losses of electrical energy due to allowed accuracy of metering devices | 4500 |  | 0 |  | 0 |  | 0 |  | 0 | 4158.5 | 0.19 | 3074.76 | 0.27 | 2594.14 | 0.11 | 1474.92 | 0.28 | 11302.32 | 0.37
6 | Technological losses of electrical energy | 4600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68284.09 | 3.08 | 36736.19 | 3.23 | 63427.03 | 2.67 | 72517.91 | 13.91 | 240965.22 | 7.86
Section Contact Information
| Item | Page code | Group1: Name; Group2: Title; Group3: Contact telephone; Group4: E-mail
|  |  | Group1 | Group2 | Group3 | Group4
| Head of an organization | 411 | Group1: V.A. Syschikov; Group2: Deputy General Director of IDGC of Centre - Tambovenergo division director; Group3: [4752]56-96-85; Group4: eremina.oi@mrsk-1.ru
| Responsible for completing the template | 412 | Group1: I.P. Polyakov; Group2: Head of Forecasting electric energy and power balance and loss analysis Department; Group3: [4752]578-227; Group4: polyakov.ip@mrsk-1.ru
Section Code links
| Item | Page code | Group1: Value
Group1
| Name of reporting organization | 421 | Group1: IDGC of Centre - Tambovenergo division
| Postal address | 422 | Group1: 392680, Tambov, Morshanskoye shosse 23
| Code of the reporting organization per Russian Business and Organization Classification | 423 | Group1: 81990183
| Activity code per Russian National Classifier of Economic Activities | 424 | Group1: 40.10.2
| Territory code per All-Russian Classifier of Political Subdivisions | 425 | Group1: 68401368000
| Code of ministry (department), authority per National Classifier of Government Entities and Administration | 426 | Group1: 41002
| Code of the legal form per All-Russia Classifier of Forms of Ownership Code | 427 | Group1: 90
| Ownership code per All-Russia Classifier of Forms of Ownership | 428 | Group1: 16
| Area code for services per All-Russian Classifier of Political Subdivisions | 429 | Group1: 68401368000
<< 15.02.2011 >>
Plugin version from 26.01.2010 11:49:54
| Version IS_Client - 4.11.3 | 4.11.3
| Version АРМ - 26.01.2010 12.18.16 | 26.01.2010 12.18.16