## Липецк
table 1
No. | Object of main substation, voltage class | Current deficit | [9 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA |  | Summary total capacity of central substation following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of Main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load calculated in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [12 empty] | 1: One-transformer substations
| SS 110/10kv Lev Tolstoy | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | closed |  | SS 110/10kv Lev Tolstoy | 10 | 0.028 | 2.658 | 1.6 | 30 | 1.058 | 0 | 1.6 | -1.058 | -1.058 | closed
| SS 110/10 kv Dvurechki | 6.3 |  | 2.03 | 0.1 | 70 | 1.93 | 0 | 0.1 | -1.93 | -1.93 | closed |  | SS 110/10 kv Dvurechki | 6.3 | 0.178 | 2.208 | 0.1 | 70 | 2.108 | 0 | 0.1 | -2.108 | -2.108 | closed
| SS 35/10 kv Vesyoloe | 2.5 |  | 0.16 | 0.8 | 100 | -0.64 | 0 | 0.8 | 0.64 | 0.64 | opened |  | SS 35/10 kv Vesyoloe | 2.5 | 0.015 | 0.175 | 0.8 | 100 | -0.625 | 0 | 0.8 | 0.625 | 0.625 | opened
| SS 35/10 kv Kr.Palna | 3.2 |  | 0.73 | 1.2 | 70 | -0.47 | 0 | 1.2 | 0.47 | 0.47 | opened |  | SS 35/10 kv Kr.Palna | 3.2 | 0.023 | 0.753 | 1.2 | 70 | -0.447 | 0 | 1.2 | 0.447 | 0.447 | opened
| SS 35/10 kv Kamenka | 2.5 |  | 0.93 | 1.5 | 60 | -0.57 | 0 | 1.5 | 0.57 | 0.57 | opened |  | SS 35/10 kv Kamenka | 2.5 | 0.183 | 1.113 | 1.5 | 60 | -0.387 | 0 | 1.5 | 0.387 | 0.387 | opened
| SS 35/10 kv Krasotynovka | 2.5 |  | 0.43 | 1.5 | 50 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened |  | SS 35/10 kv Krasotynovka | 2.5 |  | 0.43 | 1.5 | 50 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened
| SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed |  | SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed
| SS 35/10 kv Pankratovka | 2.5 |  | 0.63 | 1.2 | 90 | -0.57 | 0 | 1.2 | 0.57 | 0.57 | opened |  | SS 35/10 kv Pankratovka | 2.5 |  | 0.63 | 1.2 | 90 | -0.57 | 0 | 1.2 | 0.57 | 0.57 | opened
| SS 35/10 kv Preobrazhenye | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | closed |  | SS 35/10 kv Preobrazhenye | 2.5 | 0.03 | 0.49 | 0 | 0 | 0.49 | 0 | 0 | -0.49 | -0.49 | closed
| SS 35/10 kv Yakovlevo | 2.5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 0 | -0.9 | -0.9 | closed |  | SS 35/10 kv Yakovlevo | 2.5 | 0.526 | 1.426 | 0 | 0 | 1.426 | 0 | 0 | -1.426 | -1.426 | closed
| SS 110/10kv Terbunsky gonchar | 25 |  | without load | [8 empty] | 2: SS 110/10kv Terbunsky gonchar; 3: 25; 4: 9.95; 5: 9.95
| SS 35/10 kv Pervomayskaya | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | closed |  | SS 35/10 kv Pervomayskaya | 2.5 | 0.008 | 0.858 | 0.3 | 60 | 0.558 | 0 | 0.3 | -0.558 | -0.558 | closed
| SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.91 | 0.9 | 90 | 0.01 | 0 | 0.9 | -0.01 | -0.01 | closed |  | SS 35/10 kv Kamennaya Lubna | 2.5 | 0.06 | 0.97 | 0.9 | 90 | 0.07 | 0 | 0.9 | -0.07 | -0.07 | closed
| SS 35/10 kv Znamenka | 2.5 |  | 0.87 | 0.4 | 8 hours | 0.47 | 0 | 0.4 | -0.47 | -0.47 | closed |  | SS 35/10 kv Znamenka | 2.5 | 0.02 | 0.89 | 0.4 | 8 hours | 0.49 | 0 | 0.4 | -0.49 | -0.49 | closed
| SS 35/10 kv Pikovo | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | closed |  | SS 35/10 kv Pikovo | 2.5 | 0.008 | 0.598 | 0.5 | 60 | 0.098 | 0 | 0.5 | -0.098 | -0.098 | closed
| SS 35/10 kv Nikolskoe | 4 |  | 0.28 | 0.8 | 150 | -0.52 | 0 | 0.8 | 0.52 | 0.52 | opened |  | SS 35/10 kv Nikolskoe | 4 | 0.01 | 0.29 | 0.8 | 150 | -0.51 | 0 | 0.8 | 0.51 | 0.51 | opened
| SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed |  | SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed
| SS 35/6 kv Druzhba | 5.6 |  | Integrated distribution device of low voltage-6kv not ours | [7 empty] | opened | 2: SS 35/6 kv Druzhba; 3: 5.6; 5: 0
| SS 35/10 kv SOM | 1.6 |  | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | closed |  | SS 35/10 kv SOM | 1.6 |  | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | closed
| SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed |  | SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed
| SS 35/10 kv Sindyakino | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | opened |  | SS 35/10 kv Sindyakino | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | opened
| SS 35/10 kv Kurino | 2.5 |  | 0.53 | 0 | 0 | 0.53 | 0 | 0 | -0.53 | -0.53 | closed |  | SS 35/10 kv Kurino | 2.5 | 0.053 | 0.583 | 0 | 0 | 0.583 | 0 | 0 | -0.583 | -0.583 | closed
| SS 35/10 kv Novodubovoe | 2.5 |  | 0.88 | 0 | 0 | 0.88 | 0 | 0 | -0.88 | -0.88 | closed |  | SS 35/10 kv Novodubovoe | 2.5 | 0.031 | 0.911 | 0 | 0 | 0.911 | 0 | 0 | -0.911 | -0.911 | closed
| SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed |  | SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed
| SS 35/6 kv Karyer | 4 |  | without load | [8 empty] | 2: SS 35/6 kv Karyer; 3: 4; 5: 0
Two- and more transformer substations (for two voltage levels) | [12 empty] | 1: Two- and more transformer substations (for two voltage levels)
| SS 110/6 kv Agregatnaya | 16+16 | 32 | 15.14 | 0 | 0 | 15.14 | 0 | 16.8 | 1.66 | 1.66 | opened |  | SS 110/6 kv Agregatnaya | 16+16 | 0.564 | 15.704 | 0 | 0 | 15.704 | 0 | 16.8 | 1.096 | 1.096 | opened
| SS 110/6 kv Zapadnaya | 40+40 | 80 | 17.44 | 0 | 0 | 17.44 | 0 | 42 | 24.56 | 24.56 | opened |  | SS 110/6 kv Zapadnaya | 40+40 | 4.27 | 21.71 | 0 | 0 | 21.71 | 0 | 42 | 20.29 | 20.29 | opened
| SS 110/10 kv Kashary | 2,5+6,3 | 8.8 | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | opened |  | SS 110/10 kv Kashary | 2,5+6,3 | 0.054 | 1.594 | 2.3 | 100 | -0.706 | 0 | 2.625 | 3.331 | 3.331 | opened
| SS 110/6 kv Tabak | 16+16 | 32 | 9.48 | 3.2 | 20 | 6.28 | 0 | 16.8 | 10.52 | 10.52 | opened |  | SS 110/6 kv Tabak | 16+16 | 0.225 | 9.705 | 3.2 | 20 | 6.505 | 0 | 16.8 | 10.295 | 10.295 | opened
| SS 110/10 kv Lukoshkino | 10+2,5 | 12.5 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | opened |  | SS 110/10 kv Lukoshkino | 10+2,5 | 0.014 | 1.084 | 0 | 0 | 1.084 | 0 | 2.625 | 1.541 | 1.541 | opened
| SS 110/10kv Niva | 10+10 | 20 | 5.09 | 1 | 100 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened |  | SS 110/10kv Niva | 10+10 | 0.05 | 5.14 | 1 | 100 | 4.14 | 0 | 10.5 | 6.36 | 6.36 | opened
| SS 110/10 kv Olkhovets | 2,5+2,5 | 5 | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened |  | SS 110/10 kv Olkhovets | 2,5+2,5 | 0.015 | 1.735 | 0.8 | 100 | 0.935 | 0 | 2.625 | 1.69 | 1.69 | opened
| SS 110/10 kv Kuyman | 2,5+2,5 | 5 | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | * |  | SS 110/10 kv Kuyman | 2,5+2,5 | 0.01 | 1.11 | 1 | 100 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
| SS 110/10 kv Lutoshkino | 2,5+2,5 | 5 | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened |  | SS 110/10 kv Lutoshkino | 2,5+2,5 |  | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened
| SS 110/10 kv Krugloe | 2,5+2,5 | 5 | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened |  | SS 110/10 kv Krugloe | 2,5+2,5 |  | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
| SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 80 | 45.62 | 4.5 | 30 | 41.12 | 0 | 42 | 0.88 | 0.88 | * |  | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 12.733 | 58.353 | 4.5 | 30 | 53.853 | 0 | 42 | -11.853 | -11.853 | closed
| SS 110/6 kv Privokzalnaya | 20+20+25 | 65 | 49.71 | 1.38 | 30 | 48.33 | 0 | 42 | -6.33 | -6.33 | closed |  | SS 110/6 kv Privokzalnaya | 20+20+25 | 0.978 | 50.688 | 1.38 | 30 | 49.308 | 0 | 42 | -7.308 | -7.308 | closed
| SS 110/10/6 kv Yuzhnaya | 40+40 | 80 | 43.07 | 6 | 30 | 37.07 | 0 | 42 | 4.93 | 4.93 | * |  | SS 110/10/6 kv Yuzhnaya | 40+40 | 4.577 | 47.647 | 6 | 30 | 41.647 | 0 | 42 | 0.353 | 0.353 | *
| SS 110/6 kv Sitovka | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | * |  | SS 110/6 kv Sitovka | 10+10 |  | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
| SS 110/6 kv LTP | 6,3+10 | 16.3 | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | * |  | SS 110/6 kv LTP | 6,3+10 |  | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | *
| SS 110/6 kv KPD | 10+10 | 20 | 2.31 | 0 | 0 | 2.31 | 0 | 10.5 | 8.19 | 8.19 | * |  | SS 110/6 kv KPD | 10+10 | 3 | 5.31 | 0 | 0 | 5.31 | 0 | 10.5 | 5.19 | 5.19 | *
| SS 110/10 kv Oktyabskaya | 40+40 | 80 | 19.12 | 4 | 30 | 15.12 | 0 | 42 | 26.88 | 26.88 | * |  | SS 110/10 kv Oktyabskaya | 40+40 | 12.089 | 31.209 | 4 | 30 | 27.209 | 0 | 42 | 14.791 | 14.791 | *
| SS 110/10 kv Universitetskaya | 40+40 |  | 0 | 0 | 0 | 0 | 0 | 42 | 42 | 42 | opened |  | SS 110/10 kv Universitetskaya | 40+40 | 40.95 | 40.95 | 0 | 0 | 40.95 | 0 | 42 | 1.05 | 1.05 | closed
| SS 110/6 kv Teplichnaya | 15+15 | 30 | 7.58 | 0 | 0 | 7.58 | 0 | 15.75 | 8.17 | 8.17 | * |  | SS 110/6 kv Teplichnaya | 15+15 | 0.014 | 7.594 | 0 | 0 | 7.594 | 0 | 15.75 | 8.156 | 8.156 | *
| SS 110/6 kv Trubnaya-2 | 25+25 | 50 | 2.4 | 0 | 0 | 2.4 | 0 | 26.25 | 23.85 | 23.85 | * |  | SS 110/6 kv Trubnaya-2 | 25+25 | 0.245 | 2.645 | 0 | 0 | 2.645 | 0 | 26.25 | 23.605 | 23.605 | *
| SS 110/6 kv GPP-2 LTZ | 63+63 | 126 | 12.14 | 0 | 0 | 12.14 | 0 | 66.15 | 54.01 | 54.01 | * |  | SS 110/6 kv GPP-2 LTZ | 63+63 | 1.6 | 13.74 | 0 | 0 | 13.74 | 0 | 66.15 | 52.41 | 52.41 | *
| SS 35/10 kv Avangard | 4+4 | 8 | 1.1 | 1.2 | 110 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened |  | SS 35/10 kv Avangard | 4+4 | 0.078 | 1.178 | 1.2 | 110 | -0.022 | 0 | 4.2 | 4.222 | 4.222 | opened
| SS 35/10 kv Afanasysevo | 2,5+2,5 | 5 | 1.81 | 0 | 0 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | opened |  | SS 35/10 kv Afanasysevo | 2,5+2,5 | 0.053 | 1.863 | 0 | 0 | 1.863 | 0 | 2.625 | 0.762 | 0.762 | opened
| SS 35/10 kv Babarykino | 2,5+2,5 | 5 | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | opened |  | SS 35/10 kv Babarykino | 2,5+2,5 | 0.01 | 1.08 | 1.4 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened
| SS 35/10 kv Avrora | 2,5+2,5 | 5 | 0.88 | 1.2 | 110 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened |  | SS 35/10 kv Avrora | 2,5+2,5 | 0.504 | 1.384 | 1.2 | 110 | 0.184 | 0 | 2.625 | 2.441 | 2.441 | opened
| SS 35/10 kv B.Boyovka | 2,5+2,5 | 5 | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened |  | SS 35/10 kv B.Boyovka | 2,5+2,5 |  | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened
| SS 35/10 kv Borki | 2,5+2,5 | 5 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | opened |  | SS 35/10 kv Borki | 2,5+2,5 |  | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | opened
| SS 35/6kv Vostochnaya | 10+16 | 26 | 8.72 | 4.8 | 20 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | opened |  | SS 35/6kv Vostochnaya | 10+16 | 2.058 | 10.778 | 4.8 | 20 | 5.978 | 0 | 10.5 | 4.522 | 4.522 | opened
| SS 35/10 kv Vasilyevka | 2,5+2,5 | 5 | 1.05 | 1.5 | 90 | -0.45 | 0 | 2.625 | 3.075 | 3.075 | opened |  | SS 35/10 kv Vasilyevka | 2,5+2,5 |  | 1.05 | 1.5 | 90 | -0.45 | 0 | 2.625 | 3.075 | 3.075 | opened
| SS 35/10 kv Voronets | 4+4 | 8 | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened |  | SS 35/10 kv Voronets | 4+4 | 0.022 | 2.172 | 1.2 | 110 | 0.972 | 0 | 4.2 | 3.228 | 3.228 | opened
| SS 35/6 kv Golikovo | 1,8+1,6 | 3.4 | 0.21 | 0 | 0 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened |  | SS 35/6 kv Golikovo | 1,8+1,6 |  | 0.21 | 0 | 0 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
| SS 35/10 kv Gatishche | 2,5+2,5 | 5 | 0.96 | 0 | 0 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened |  | SS 35/10 kv Gatishche | 2,5+2,5 |  | 0.96 | 0 | 0 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
| SS 35/10 kv Gnilusha | 6,3+6,3 | 12.6 | 1.57 | 1.2 | 120 | 0.37 | 0 | 6.615 | 6.245 | 6.245 | opened |  | SS 35/10 kv Gnilusha | 6,3+6,3 | 0.606 | 2.176 | 1.2 | 120 | 0.976 | 0 | 6.615 | 5.639 | 5.639 | opened
| SS 35/10kv Gryzlovo | 2,5+2,5 | 5 | 1.03 | 0.8 | 110 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened |  | SS 35/10kv Gryzlovo | 2,5+2,5 | 0.025 | 1.055 | 0.8 | 110 | 0.255 | 0 | 2.625 | 2.37 | 2.37 | opened
| SS 35/10 kv Zhernovnoe | 2,5+2,5 | 5 | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | opened |  | SS 35/10 kv Zhernovnoe | 2,5+2,5 | 0.352 | 0.972 | 1.5 | 100 | -0.528 | 0 | 2.625 | 3.153 | 3.153 | opened
| SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 4.8 | 2.35 | 0 | 0 | 2.35 | 0 | 1.68 | -0.67 | -0.67 | closed |  | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.27 | 2.62 | 0 | 0 | 2.62 | 0 | 1.68 | -0.94 | -0.94 | closed
| SS 35/10 kv Zakharovka | 2,5+2,5 | 5 | 0.89 | 0.8 | 60 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened |  | SS 35/10 kv Zakharovka | 2,5+2,5 |  | 0.89 | 0.8 | 60 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
| SS 35/10 kv Kazaki | 4+4 | 8 | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | opened |  | SS 35/10 kv Kazaki | 4+4 | 0.008 | 2.848 | 0 | 0 | 2.848 | 0 | 4.2 | 1.352 | 1.352 | opened
| SS 35/10 kv Kolesovo | 6,3+6,3 | 12.6 | 1.38 | 1.5 | 90 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | opened |  | SS 35/10 kv Kolesovo | 6,3+6,3 | 0.419 | 1.799 | 1.5 | 90 | 0.299 | 0 | 6.615 | 6.316 | 6.316 | opened
| SS 35/10 kv Knyazevo | 2,5+2,5 | 5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened |  | SS 35/10 kv Knyazevo | 2,5+2,5 |  | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
| SS 35/10 kv Kirillovo | 2,5+2,5 | 5 | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | opened |  | SS 35/10 kv Kirillovo | 2,5+2,5 |  | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | opened
| SS 35/10 kv Ksizovo | 2,5+2,5 | 5 | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened |  | SS 35/10 kv Ksizovo | 2,5+2,5 |  | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
| SS 35/10 kv Lamskoe | 2,5+2,5 | 5 | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened |  | SS 35/10 kv Lamskoe | 2,5+2,5 | 0.022 | 2.002 | 1.2 | 100 | 0.802 | 0 | 2.625 | 1.823 | 1.823 | opened
| SS 35/10 kv Kazachye | 2,5+2,5 | 5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened |  | SS 35/10 kv Kazachye | 2,5+2,5 | 0.403 | 0.853 | 0 | 0 | 0.853 | 0 | 2.625 | 1.772 | 1.772 | opened
| SS 35/10 kv Lebyazhye | 2,5+1,6 | 4.1 | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened |  | SS 35/10 kv Lebyazhye | 2,5+1,6 |  | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened
| SS 35/10 kv Lomovets | 1,6+2,5 | 4.1 | 0.27 | 0 | 0 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened |  | SS 35/10 kv Lomovets | 1,6+2,5 | 0.005 | 0.275 | 0 | 0 | 0.275 | 0 | 1.68 | 1.405 | 1.405 | opened
| SS 35/10 kv Olshanets | 2,5+4 | 6.5 | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened |  | SS 35/10 kv Olshanets | 2,5+4 |  | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened
| SS 35/10 kv Ploskoe | 4+4 | 8 | 3.76 | 3 | 70 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened |  | SS 35/10 kv Ploskoe | 4+4 | 1.205 | 4.965 | 3 | 70 | 1.965 | 0 | 4.2 | 2.235 | 2.235 | opened
| SS 35/10 kv Stegalovka | 2,5+3,2 | 5.7 | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | opened |  | SS 35/10 kv Stegalovka | 2,5+3,2 |  | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | opened
| SS 35/10 kv Solidarnost | 4+4 | 8 | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened |  | SS 35/10 kv Solidarnost | 4+4 | 0.026 | 1.326 | 1.2 | 70 | 0.126 | 0 | 4.2 | 4.074 | 4.074 | opened
| SS 35/10 kv Timiryazevo | 4+4 | 8 | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened |  | SS 35/10 kv Timiryazevo | 4+4 | 0.015 | 0.935 | 0.8 | 45 | 0.135 | 0 | 4.2 | 4.065 | 4.065 | opened
| SS 35/10 kv Talitsa | 2,5+2,5 | 5 | 1.55 | 1.5 | 110 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened |  | SS 35/10 kv Talitsa | 2,5+2,5 | 0.326 | 1.876 | 1.5 | 110 | 0.376 | 0 | 2.625 | 2.249 | 2.249 | opened
| SS 35/10 kv the II Terbuny | 2,5+2,5 | 5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened |  | SS 35/10 kv the II Terbuny | 2,5+2,5 | 1.07 | 1.86 | 0 | 0 | 1.86 | 0 | 2.625 | 0.765 | 0.765 | opened
| SS 35/10 kv Tikhii Don | 4+4 | 8 | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | opened |  | SS 35/10 kv Tikhii Don | 4+4 | 0.024 | 0.474 | 0.8 | 50 | -0.326 | 0 | 4.2 | 4.526 | 4.526 | opened
| SS 35/10 kv Khitrovo | 6,3+6,3 | 12.6 | 0.42 | 0 | 0 | 0.42 | 0 | 6.615 | 6.195 | 6.195 | opened |  | SS 35/10 kv Khitrovo | 6,3+6,3 | 0.014 | 0.434 | 0 | 0 | 0.434 | 0 | 6.62 | 6.186 | 6.186 | opened
| SS 35/10 kv Chernava | 2,5+2,5 | 5 | 2.02 | 0 | 0 | 2.02 | 0 | 2.625 | 0.605 | 0.605 | opened |  | SS 35/10 kv Chernava | 2,5+2,5 | 0.018 | 2.038 | 0 | 0 | 2.038 | 0 | 2.625 | 0.587 | 0.587 | opened
| SS 35/10 kv Chernoles | 2,5+2,5 | 5 | 0.18 | 0 | 0 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened |  | SS 35/10 kv Chernoles | 2,5+2,5 | 0.007 | 0.187 | 0 | 0 | 0.187 | 0 | 2.625 | 2.438 | 2.438 | opened
| SS 35/6 kv SS No. 5 | 6,3+3,2 | 9.5 | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | opened |  | SS 35/6 kv SS No. 5 | 6,3+3,2 |  | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | opened
| SS 35/10 kv Krasnoe | 4+4 | 8 | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | opened |  | SS 35/10 kv Krasnoe | 4+4 | 0.054 | 3.564 | 1 | 120 | 2.564 | 0 | 4.2 | 1.636 | 1.636 | opened
| SS 35/10 kv Tyoploe | 2,5+2,5 | 5 | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened |  | SS 35/10 kv Tyoploe | 2,5+2,5 |  | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened
| SS 35/10 kv Dankov-selskaya | 6,3+4 | 10.3 | 5.61 | 2 | 120 | 3.61 | 0 | 4.2 | 0.59 | 0.59 | opened |  | SS 35/10 kv Dankov-selskaya | 6,3+4 | 0.71 | 6.32 | 2 | 120 | 4.32 | 0 | 4.2 | -0.12 | -0.12 | closed
| SS 35/10 kv Kolybelskaya | 2,5+2,5 | 5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | opened |  | SS 35/10 kv Kolybelskaya | 2,5+2,5 | 0.023 | 1.153 | 0 | 0 | 1.153 | 0 | 2.625 | 1.472 | 1.472 | opened
| SS 35/10 kv Topki | 2,5+2,5 | 5 | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened |  | SS 35/10 kv Topki | 2,5+2,5 | 0.76 | 1.28 | 0.5 | 60 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened
| SS 35/10 kv Agronom | 4+6,3 | 10.3 | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened |  | SS 35/10 kv Agronom | 4+6,3 | 0.028 | 2.048 | 1 | 120 | 1.048 | 0 | 4.2 | 3.152 | 3.152 | opened
| SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 5 | 2.14 | 0.5 | 60 | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened |  | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 0.916 | 3.056 | 0.5 | 60 | 2.556 | 0 | 2.625 | 0.069 | 0.069 | opened
| SS 35/10 kv Gagarino | 1,8+1,8 | 3.6 | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened |  | SS 35/10 kv Gagarino | 1,8+1,8 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened
| SS 35/10 kv Ranenburg | 1,6+1,6 | 3.2 | 1.95 | 0.5 | 60 | 1.45 | 0 | 1.68 | 0.23 | 0.23 | opened |  | SS 35/10 kv Ranenburg | 1,6+1,6 | 0.194 | 2.144 | 0.5 | 60 | 1.644 | 0 | 1.68 | 0.036 | 0.036 | opened
| SS 35/10 kv Sergievka | 2,5+2,5 | 5 | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened |  | SS 35/10 kv Sergievka | 2,5+2,5 |  | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
| SS 35/10 kv Drezgalovo | 1,6+1,6 | 3.2 | 0.37 | 0.5 | 60 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened |  | SS 35/10 kv Drezgalovo | 1,6+1,6 |  | 0.37 | 0.5 | 60 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened
| SS 35/10 kv Dolgoe | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened |  | SS 35/10 kv Dolgoe | 2,5+2,5 |  | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
| SS 35/10 kv Voskresenovka | 1,6+1,6 | 3.2 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened |  | SS 35/10 kv Voskresenovka | 1,6+1,6 | 0.01 | 0.68 | 0 | 0 | 0.68 | 0 | 1.68 | 1 | 1 | opened
| SS 35/10 kv Saprykino | 1,6+2,5 | 4.1 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened |  | SS 35/10 kv Saprykino | 1,6+2,5 | 0.03 | 0.61 | 0 | 0 | 0.61 | 0 | 1.68 | 1.07 | 1.07 | opened
| SS 35/10 kv Nopolyanye | 2,5+2,5 | 5 | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened |  | SS 35/10 kv Nopolyanye | 2,5+2,5 |  | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
| SS 35/10 kv Vednoe | 2,5+2,5 | 5 | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened |  | SS 35/10 kv Vednoe | 2,5+2,5 | 0.009 | 1.159 | 0.5 | 180 | 0.659 | 0 | 2.625 | 1.966 | 1.966 | opened
| SS 35/10 kv Bigildino | 2,5+2,5 | 5 | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened |  | SS 35/10 kv Bigildino | 2,5+2,5 |  | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
| SS 35/10 kv Kultura | 2,5+2,5 | 5 | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened |  | SS 35/10 kv Kultura | 2,5+2,5 | 0.029 | 1.129 | 0.5 | 60 | 0.629 | 0 | 2.625 | 1.996 | 1.996 | opened
| SS 35/10 kv Boryatino | 2,5+2,5 | 5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened |  | SS 35/10 kv Boryatino | 2,5+2,5 |  | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
| SS 35/10 kv B.Popovo | 2,5+2,5 | 5 | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened |  | SS 35/10 kv B.Popovo | 2,5+2,5 | 0.022 | 1.832 | 0.5 | 60 | 1.332 | 0 | 2.625 | 1.293 | 1.293 | opened
| SS 35/10 kv B. Izbishchi | 2,5+2,5 | 5 | 1.8 | 0.5 | 60 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened |  | SS 35/10 kv B. Izbishchi | 2,5+2,5 | 0.755 | 2.555 | 0.5 | 60 | 2.055 | 0 | 2.625 | 0.57 | 0.57 | opened
| SS 35/10 kv Polibino | 2,5+2,5 | 5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened |  | SS 35/10 kv Polibino | 2,5+2,5 |  | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
| SS 35/10 kv Dubrava | 2,5+2,5 | 5 | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened |  | SS 35/10 kv Dubrava | 2,5+2,5 |  | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened
| SS 35/10 kv Khrushchevo | 2,5+2,5 | 5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened |  | SS 35/10 kv Khrushchevo | 2,5+2,5 |  | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened
| SS 35/10 kv B. Verkh | 2,5+2,5 | 5 | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened |  | SS 35/10 kv B. Verkh | 2,5+2,5 | 0.015 | 1.025 | 0.5 | 120 | 0.525 | 0 | 2.625 | 2.1 | 2.1 | opened
| SS 35/10 kv Golovinshchino | 2,5+2,5 | 5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened |  | SS 35/10 kv Golovinshchino | 2,5+2,5 | 0.015 | 0.565 | 0 | 0 | 0.565 | 0 | 2.625 | 2.06 | 2.06 | opened
| SS 35/10 kv Yablonevoe | 2,5+2,5 | 5 | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened |  | SS 35/10 kv Yablonevoe | 2,5+2,5 | 0.04 | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
| SS 35/10 kv Politovo | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened |  | SS 35/10 kv Politovo | 2,5+2,5 |  | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened
| SS 35/10 kv Complex | 4+4 | 8 | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | opened |  | SS 35/10 kv Complex | 4+4 |  | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | opened
| SS 35/10 kv No.1 | 4+4 | 8 | 3.38 | 0 | 0 | 3.38 | 0 | 4.2 | 0.82 | 0.82 | opened |  | SS 35/10 kv No.1 | 4+4 | 0.676 | 4.056 | 0 | 0 | 4.056 | 0 | 4.2 | 0.144 | 0.144 | opened
| SS 35/6 kv No. 2 | 1+1+1 | 3 | 3.49 | 0 | 0 | 3.49 | 0 | 1.05 | -2.44 | -2.44 | closed |  | SS 35/6 kv No. 2 | 1+1+1 | 0.334 | 3.824 | 0 | 0 | 3.824 | 0 | 1.05 | -2.774 | -2.774 | closed
| SS 35/10 kv No. 3 | 2,5+2,5 | 5 | 1.26 | 0.46 | 90 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | * |  | SS 35/10 kv No. 3 | 2,5+2,5 | 1.712 | 2.972 | 0.46 | 90 | 2.512 | 0 | 2.625 | 0.113 | 0.113 | *
| SS 35/6 kv No. 4 | 4+4 | 8 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | * |  | SS 35/6 kv No. 4 | 4+4 | 0.157 | 2.787 | 0 | 0 | 2.787 | 0 | 4.2 | 1.413 | 1.413 | *
| SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 11.9 | 4.5 | 0 | 0 | 4.5 | 0 | 5.88 | 1.38 | 1.38 | opened |  | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 0.752 | 5.252 | 0 | 0 | 5.252 | 0 | 5.88 | 0.628 | 0.628 | opened
| SS 35/10 kv Butyrki | 5,6+4 | 9.6 | 7.13 | 0 | 0 | 7.13 | 0 | 4.2 | -2.93 | -2.93 | closed |  | SS 35/10 kv Butyrki | 5,6+4 | -1.094 | 6.036 | 0 | 0 | 6.036 | 0 | 4.2 | -1.836 | -1.836 | closed
| SS 35/10 kv Yarlukovo | 3,2+4 | 7.2 | 3.4 | 1.5 | 80 | 1.9 | 0 | 3.36 | 1.46 | 1.46 | opened |  | SS 35/10 kv Yarlukovo | 3,2+4 | 0.357 | 3.757 | 1.5 | 80 | 2.257 | 0 | 3.36 | 1.103 | 1.103 | opened
| SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 3.2 | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened |  | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 |  | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened
| SS 35/10 kv Pravda | 4+2,5 | 6.5 | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | opened |  | SS 35/10 kv Pravda | 4+2,5 |  | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | opened
| SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 | 5 | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened |  | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 |  | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
| SS 35/10 kv Matyra | 4+3,2 | 7.2 | 4.68 | 0 | 0 | 4.68 | 0 | 3.36 | -1.32 | -1.32 | closed |  | SS 35/10 kv Matyra | 4+3,2 | 0.208 | 4.888 | 0 | 0 | 4.888 | 0 | 3.36 | -1.528 | -1.528 | closed
| SS 35/10 kv Vperyod | 4+4 | 8 | 0.88 | 0.32 | 80 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | opened |  | SS 35/10 kv Vperyod | 4+4 | 0.045 | 0.925 | 0.32 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | opened
| SS 35/10 kv Maley | 4+2,5 | 6.5 | 0.48 | 0.12 | 70 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened |  | SS 35/10 kv Maley | 4+2,5 |  | 0.48 | 0.12 | 70 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
| SS 35/10 kv SKhТ | 2,5+1,6 | 4.1 | 0.96 | 0 | 0 | 0.96 | 0 | 1.68 | 0.72 | 0.72 | opened |  | SS 35/10 kv SKhТ | 2,5+1,6 | 0.695 | 1.655 | 0 | 0 | 1.655 | 0 | 1.68 | 0.025 | 0.025 | opened
| SS 35/10 kv Soshki | 4+4 | 8 | 0.8 | 0.2 | 80 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened |  | SS 35/10 kv Soshki | 4+4 | 0.005 | 0.805 | 0.2 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | opened
| SS 35/6 kv Tavolzhanka | 4+4 | 8 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened |  | SS 35/6 kv Tavolzhanka | 4+4 | 0.916 | 4.586 | 0 | 0 | 4.586 | 0 | 4.2 | -0.386 | -0.386 | closed
| SS 35/10 kv Trubetchino | 2,5+2,5 | 5 | 1.71 | 0 | 0 | 1.71 | 0 | 2.625 | 0.915 | 0.915 | * |  | SS 35/10 kv Trubetchino | 2,5+2,5 | 0.39 | 2.1 | 0 | 0 | 2.1 | 0 | 2.625 | 0.525 | 0.525 | opened
| SS 35/10 kv Ratchino | 2,5+2,5 | 5 | 1.11 | 0.12 | 70 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | * |  | SS 35/10 kv Ratchino | 2,5+2,5 | 0.01 | 1.12 | 0.12 | 70 | 1 | 0 | 2.625 | 1.625 | 1.625 | *
| SS 35/10 kv Kalikino | 3,2+3,2 | 6.4 | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | * |  | SS 35/10 kv Kalikino | 3,2+3,2 | 0.005 | 1.945 | 0.42 | 80 | 1.525 | 0 | 3.36 | 1.835 | 1.835 | *
| SS 35/10 kv Borisovka | 4+2,5 | 6.5 | 2.74 | 0 | 0 | 2.74 | 0 | 2.625 | -0.115 | -0.115 | closed |  | SS 35/10 kv Borisovka | 4+2,5 | 0.717 | 3.457 | 0 | 0 | 3.457 | 0 | 2.625 | -0.832 | -0.832 | closed
| SS 35/10 kv Vvedenka | 4+4 | 8 | 4 | 0.14 | 70 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | * |  | SS 35/10 kv Vvedenka | 4+4 | 1.418 | 5.418 | 0.14 | 70 | 5.278 | 0 | 4.2 | -1.078 | -1.078 | closed
| SS 35/10 kv Gryaznoe | 4+4 | 8 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | * |  | SS 35/10 kv Gryaznoe | 4+4 | 0.585 | 1.745 | 0 | 0 | 1.745 | 0 | 4.2 | 2.455 | 2.455 | *
| SS 35/10 kv Borino | 4+4 | 8 | 4.24 | 1.2 | 90 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | * |  | SS 35/10 kv Borino | 4+4 | 0.1 | 4.34 | 1.2 | 90 | 3.14 | 0 | 4.2 | 1.06 | 1.06 | *
| SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 5 | 1.6 | 1.88 | 100 (45) | -0.28 | 0 | 2.625 | 2.905 | 2.905 | * |  | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 0.942 | 2.542 | 1.88 | 100 (45) | 0.662 | 0 | 2.625 | 1.963 | 1.963 | opened
| SS 35/10 kv Troitskaya | 2,5+4 | 6.5 | 2.33 | 0.6 | 70 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | * |  | SS 35/10 kv Troitskaya | 2,5+4 | 0.423 | 2.753 | 0.6 | 70 | 2.153 | 0 | 2.625 | 0.472 | 0.472 | *
| SS 35/6 kv Veshalovka | 2,5+2,5 | 5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | * |  | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.028 | 0.898 | 0 | 0 | 0.898 | 0 | 2.625 | 1.727 | 1.727 | *
| SS 35/10 kv Pruzhinki | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | * |  | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.015 | 0.615 | 0 | 0 | 0.615 | 0 | 2.625 | 2.01 | 2.01 | *
| SS 35/10 kv Stebaevo | 2,5+2,5 | 5 | 0.95 | 0.28 | 80 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | * |  | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.04 | 0.99 | 0.28 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | *
| SS 35/10 kv Khleboprodukty | 6,3+6,3 | 12.6 | 3.76 | 0.6 | 100 | 3.16 | 0 | 6.615 | 3.455 | 3.455 | * |  | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 0.35 | 4.11 | 0.6 | 100 | 3.51 | 0 | 6.615 | 3.105 | 3.105 | *
| SS 35/10 kv Sentsovo | 10+10 | 20 | 7.28 | 0 | 0 | 7.28 | 0 | 10.5 | 3.22 | 3.22 | * |  | SS 35/10 kv Sentsovo | 10+10 | 1.8 | 9.08 | 0 | 0 | 9.08 | 0 | 10.5 | 1.42 | 1.42 | *
| SS 35/10 kv Meet processing plant | 6,3+6,3 | 12.6 | 4.63 | 1.6 | 110 | 3.03 | 0 | 6.62 | 3.59 | 3.59 | * |  | SS 35/10 kv Meet processing plant | 6,3+6,3 | 2.143 | 6.773 | 1.6 | 110 | 5.173 | 0 | 6.62 | 1.447 | 1.447 | *
| SS 35/6 kv Poultry plant | 4+4 | 8 | 1.93 | 0 | 0 | 1.93 | 0 | 4.2 | 2.27 | 2.27 | * |  | SS 35/6 kv Poultry plant | 4+4 | 0.007 | 1.937 | 0 | 0 | 1.937 | 0 | 4.2 | 2.263 | 2.263 | *
| SS 35/6 kv Water intake | 10+10 | 20 | 1 | 0 | 0 | 1 | 0 | 10.5 | 9.5 | 9.5 | * |  | SS 35/6 kv Water intake | 10+10 | 0.069 | 1.069 | 0 | 0 | 1.069 | 0 | 10.5 | 9.431 | 9.431 | *
| SS 35/10 kv Petrovskaya | 2,5+4 | 6.5 | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened |  | SS 35/10 kv Petrovskaya | 2,5+4 |  | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
| SS 35/10 kv Lebedyanka | 2,5+2,5 | 5 | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened |  | SS 35/10 kv Lebedyanka | 2,5+2,5 |  | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
| SS 35/10 kv Novocherkutino | 4+4 | 8 | 0.97 | 1.02 | 100 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | opened |  | SS 35/10 kv Novocherkutino | 4+4 | 0.008 | 0.978 | 1.02 | 100 | -0.042 | 0 | 4.2 | 4.242 | 4.242 | opened
| SS 35/10 kv Ivanovka | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened |  | SS 35/10 kv Ivanovka | 2,5+2,5 | 0.05 | 1.11 | 0 | 0 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | opened
| SS 35/10 kv Poddubrovka | 2,5+2,5 | 5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | opened |  | SS 35/10 kv Poddubrovka | 2,5+2,5 | 0.037 | 1.007 | 0 | 0 | 1.007 | 0 | 2.625 | 1.618 | 1.618 | opened
| SS 35/10 kv Plavitsa | 1,6+1,6 | 3.2 | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened |  | SS 35/10 kv Plavitsa | 1,6+1,6 |  | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
| SS 35/10 kv Parshinovka | 1,6+2,5 | 4.1 | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened |  | SS 35/10 kv Parshinovka | 1,6+2,5 |  | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
| SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 7.2 | 2.2 | 1.28 | 100 | 0.92 | 0 | 3.36 | 2.44 | 2.44 | opened |  | SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 0.03 | 2.23 | 1.28 | 100 | 0.95 | 0 | 3.36 | 2.41 | 2.41 | opened
| SS 35/10 kv Demshinka | 2,5+2,5 | 5 | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened |  | SS 35/10 kv Demshinka | 2,5+2,5 | 0.014 | 0.284 | 0 | 0 | 0.284 | 0 | 2.625 | 2.341 | 2.341 | opened
| SS 35/10 kv Bereznyagovka | 1,6+1,6 | 3.2 | 0.62 | 0.46 | 80 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened |  | SS 35/10 kv Bereznyagovka | 1,6+1,6 | 0.015 | 0.635 | 0.46 | 80 | 0.175 | 0 | 1.68 | 1.505 | 1.505 | opened
| SS 35/10 kv Dmitrievka | 2,5+2,5 | 5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened |  | SS 35/10 kv Dmitrievka | 2,5+2,5 |  | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened
| SS 35/10 kv Pashkovo | 2,5+2,5 | 5 | 1.89 | 0 | 0 | 1.89 | 0 | 2.625 | 0.735 | 0.735 | opened |  | SS 35/10 kv Pashkovo | 2,5+2,5 | 0.026 | 1.916 | 0 | 0 | 1.916 | 0 | 2.625 | 0.709 | 0.709 | opened
| SS 35/10 kv Moskovka | 1,6+1,6 | 3.2 | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | opened |  | SS 35/10 kv Moskovka | 1,6+1,6 | 0.016 | 0.786 | 0 | 0 | 0.786 | 0 | 1.68 | 0.894 | 0.894 | opened
| SS 35/10 kv Bochinovka | 4+4 | 8 | 3.14 | 1.18 | 90 | 1.96 | 0 | 4.2 | 2.24 | 2.24 | opened |  | SS 35/10 kv Bochinovka | 4+4 | 0.608 | 3.748 | 1.18 | 90 | 2.568 | 0 | 4.2 | 1.632 | 1.632 | opened
| SS 35/10 kv Fyodorovka | 2,5+2,5 | 5 | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened |  | SS 35/10 kv Fyodorovka | 2,5+2,5 |  | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
| SS 35/10 kv Kulikovo | 2,5+2,5 | 5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened |  | SS 35/10 kv Kulikovo | 2,5+2,5 |  | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
| SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 5 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | * |  | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 1.276 | 2.516 | 0 | 0 | 2.516 | 0 | 2.625 | 0.109 | 0.109 | *
| SS 35/10 kv Dmitryashevka | 2,5+2,5 | 5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | * |  | SS 35/10 kv Dmitryashevka | 2,5+2,5 |  | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | *
| SS 35/10 kv Rechnaya | 4+4 | 8 | 1.57 | 1.06 | 100 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | * |  | SS 35/10 kv Rechnaya | 4+4 | 0.017 | 1.587 | 1.06 | 100 | 0.527 | 0 | 4.2 | 3.673 | 3.673 | *
| SS 35/10 kv Negachevka | 2,5+2,5 | 5 | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | * |  | SS 35/10 kv Negachevka | 2,5+2,5 |  | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | *
| SS 35/10 kv Karamyshevo | 10+10 | 20 | 0.67 | 0.1 | 70 | 0.57 | 0 | 10.5 | 9.93 | 9.93 | opened |  | SS 35/10 kv Karamyshevo | 10+10 | 0.051 | 0.721 | 0.1 | 70 | 0.621 | 0 | 10.5 | 9.879 | 9.879 | opened
| SS 35/10 kv Tyushevka | 1,6+1,6 | 3.2 | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | * |  | SS 35/10 kv Tyushevka | 1,6+1,6 | 0.007 | 0.967 | 0.1 | 70 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | *
| SS 35/10 kv Sselki | 10+10 |  | 0.1 | 0 | 0 | 0.1 | 0 | 10.5 | 10.4 | 10.4 | opened |  | SS 35/10 kv Sselki | 10+10 | 6.153 | 6.253 | 0 | 0 | 6.253 | 0 | 10.5 | 4.247 | 4.247 | opened
Two- and more transformer substations (for three voltage levels) | [12 empty] | 1: Two- and more transformer substations (for three voltage levels)
| SS 110/35/10 kv Terbuny-110 | 10+10 | 20 | 9.26 | 3.5 |  | 5.76 | 0 | 10.5 | 4.74 | 4.71 | opened |  | SS 110/35/10 kv Terbuny-110 | 10+10 | 1.978 | 11.238 | 3.5 |  | 7.738 | 0 | 10.5 | 2.762 | 2.762 | opened
| Nom. Capacity MV, МVA | 10+10 |  | 3.47 | 3.5 | 30 | -0.03 | 0 | 10.5 | 10.53 |  |  |  | Nom. Capacity MV, МVA | 10+10 | 0.526 | 3.996 | 3.5 | 30 | 0.496 | 0 | 10.5 | 10.004
| Nom. capacity LV, МVA | 10+10 |  | 5.79 | 0 | 0 | 5.79 | 0 | 10.5 | 4.71 |  |  |  | Nom. capacity LV, МVA | 10+10 | 1.452 | 7.242 | 0 | 0 | 7.242 | 0 | 10.5 | 3.258
| SS 110/35/10 kv Dolgorukovo | 6,3+10 | 16.3 | 6.98 | 4 |  | 2.98 | 0 | 6.615 | 3.635 | 3.525 | opened |  | SS 110/35/10 kv Dolgorukovo | 6,3+10 | 0.494 | 7.474 | 4 |  | 3.474 | 0 | 6.615 | 3.141 | 3.141 | opened
| Nom. capacity MV, МVA | 6,3+10 |  | 3.89 | 4 | 45 | -0.11 | 0 | 6.615 | 6.725 |  |  |  | Nom. capacity MV, МVA | 6,3+10 | 0.412 | 4.302 | 4 | 45 | 0.302 | 0 | 6.615 | 6.313
| Nom. capacity LV, МVA | 6,3+10 |  | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525 |  |  |  | Nom. capacity LV, МVA | 6,3+10 | 0.082 | 3.172 | 0 | 0 | 3.172 | 0 | 6.615 | 3.443
| SS 110/35/10 kv Volovo | 10+10 | 20 | 2.07 | 0.89 |  | 1.18 | 0 | 10.5 | 9.32 | 9.32 | opened |  | SS 110/35/10 kv Volovo | 10+10 | 0.157 | 2.227 | 0.89 |  | 1.337 | 0 | 10.5 | 9.163 | 9.163 | opened
| Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 |  | 2.07 | 0.89 | 60 | 1.18 | 0 | 10.5 | 9.32 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.157 | 2.227 | 0.89 | 60 | 1.337 | 0 | 10.5 | 9.163
| SS 110/35/10 kv Izmalkovo | 10+10 | 20 | 6.22 | 1.2 |  | 5.02 | 0 | 10.5 | 5.48 | 5.48 | opened |  | SS 110/35/10 kv Izmalkovo | 10+10 | 2.581 | 8.801 | 1.2 |  | 7.601 | 0 | 10.5 | 2.899 | 2.899 | opened
| Nom. capacity MV, МVА | 10+10 |  | 2.37 | 1.2 | 30 | 1.17 | 0 | 10.5 | 9.33 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.03 | 2.4 | 1.2 | 30 | 1.2 | 0 | 10.5 | 9.3
| Nom. capacity LV, МVА | 10+10 |  | 3.85 | 0 | 0 | 3.85 | 0 | 10.5 | 6.65 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.551 | 6.401 | 0 | 0 | 6.401 | 0 | 10.5 | 4.099
| SS 110/35/10 kv Gorokhovskaya | 16+16 | 32 | 10.52 | 7.2 |  | 3.32 | 0 | 16.8 | 13.48 | 13.48 | opened |  | SS 110/35/10 kv Gorokhovskaya | 16+16 | 3.575 | 14.095 | 7.2 |  | 6.895 | 0 | 16.8 | 9.905 | 9.905 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.94 | 6 | 30 | 0.94 | 0 | 16.8 | 15.86 |  |  |  | Nom. capacity MV, МVА | 16+16 | 2.202 | 9.142 | 6 | 30 | 3.142 | 0 | 16.8 | 13.658
| Nom. capacity LV, МVА | 16+16 |  | 3.58 | 1.2 | 120 | 2.38 | 0 | 16.8 | 14.42 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.373 | 4.953 | 1.2 | 120 | 3.753 | 0 | 16.8 | 13.047
| SS 110/35/10 kv Donskaya | 10+10 | 20 | 7.18 | 4.89 |  | 2.29 | 0 | 10.5 | 8.21 | 8.11 | opened |  | SS 110/35/10 kv Donskaya | 10+10 | 2.629 | 9.809 | 4.89 |  | 4.919 | 0 | 10.5 | 5.581 | 5.581 | opened
| Nom. capacity MV, МVА | 10+10 |  | 3.9 | 4 | 30 | -0.1 | 0 | 10.5 | 10.6 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.584 | 6.484 | 4 | 30 | 2.484 | 0 | 10.5 | 8.016
| Nom. capacity LV, МVА | 10+10 |  | 3.28 | 0.89 | 120 | 2.39 | 0 | 10.5 | 8.11 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.045 | 3.325 | 0.89 | 120 | 2.435 | 0 | 10.5 | 8.065
| SS 110/35/10 kv Lebedyan | 16+16 | 32 | 15.92 | 9 |  | 6.92 | 0 | 16.8 | 9.88 | 9.88 | opened |  | SS 110/35/10 kv Lebedyan | 16+16 | 1.2 | 17.12 | 9 |  | 8.12 | 0 | 16.8 | 8.68 | 8.68 | opened
| Nom. capacity MV, МVА | 16+16 |  | 7.2 | 6 | 60 | 1.2 | 0 | 16.8 | 15.6 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.981 | 8.181 | 6 | 60 | 2.181 | 0 | 16.8 | 14.619
| Nom. capacity LV, МVА | 16+16 |  | 8.72 | 3 | 120 | 5.72 | 0 | 16.8 | 11.08 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.219 | 8.939 | 3 | 120 | 5.939 | 0 | 16.8 | 10.861
| SS 110/35/10 kv Chaplygin-novaya | 16+16 | 32 | 7.58 | 4.5 |  | 3.08 | 0 | 16.8 | 13.72 | 13.72 | opened |  | SS 110/35/10 kv Chaplygin-novaya | 16+16 | 0.85 | 8.43 | 4.5 |  | 3.93 | 0 | 16.8 | 12.87 | 12.87 | opened
| Nom. capacity MV, МVА | 16+16 |  | 3.4 | 2.5 | 20 | 0.9 | 0 | 16.8 | 15.9 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.768 | 4.168 | 2.5 | 20 | 1.668 | 0 | 16.8 | 15.132
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 2 | 100 | 2.18 | 0 | 16.8 | 14.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.082 | 4.262 | 2 | 100 | 2.262 | 0 | 16.8 | 14.538
| SS 110/35/10 kv Kompressornaya | 16+16 | 32 | 4.81 | 3.2 |  | 1.61 | 0 | 16.8 | 15.19 | 15.19 | opened |  | SS 110/35/10 kv Kompressornaya | 16+16 | 0.2755 | 5.0855 | 3.2 |  | 1.8855 | 0 | 16.8 | 14.9145 | 14.9145 | opened
| Nom. Capacity MV, МVА | 16+16 |  | 2.51 | 2.2 | 20 | 0.31 | 0 | 16.8 | 16.49 |  |  |  | Nom. Capacity MV, МVА | 16+16 | 0.2315 | 2.7415 | 2.2 | 20 | 0.5415 | 0 | 16.8 | 16.2585
| Nom. capacity LV, МVА | 16+16 |  | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.044 | 2.344 | 1 | 60 | 1.344 | 0 | 16.8 | 15.456
| SS 110/35/10 kv Rossiya | 16+16 | 32 | 5.6 | 3.8 |  | 1.8 | 0 | 16.8 | 15 | 15 | opened |  | SS 110/35/10 kv Rossiya | 16+16 | 0.124 | 5.724 | 3.8 |  | 1.924 | 0 | 16.8 | 14.876 | 14.876 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.67 | 3 | 60 | 1.67 | 0 | 16.8 | 15.13 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.124 | 4.794 | 3 | 60 | 1.794 | 0 | 16.8 | 15.006
| Nom. capacity LV, МVА | 16+16 |  | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0 | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67
| SS 110/35/10 kv Beryozovka | 16+10 | 26 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | opened |  | SS 110/35/10 kv Beryozovka | 16+10 | 0 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | opened
| Nom. capacity MV, МVА | 16+10 |  | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13 |  |  |  | Nom. capacity MV, МVА | 16+10 | 0 | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13
| Nom. capacity LV, МVА | 16+10 |  | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0 | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29
| SS 110/35/10 kv Astapovo | 16+16 | 32 | 4.62 | 3 |  | 1.62 | 0 | 16.8 | 15.18 | 15.18 | opened |  | SS 110/35/10 kv Astapovo | 16+16 | 0.05 | 4.67 | 3 |  | 1.67 | 0 | 16.8 | 15.13 | 15.13 | opened
| Nom. capacity MV, МVА | 16+16 |  | 2.74 | 2 | 60 | 0.74 | 0 | 16.8 | 16.06 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.035 | 2.775 | 2 | 60 | 0.775 | 0 | 16.8 | 16.025
| Nom. capacity LV, МVА | 16+16 |  | 1.88 | 1 | 60 | 0.88 | 0 | 16.8 | 15.92 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.015 | 1.895 | 1 | 60 | 0.895 | 0 | 16.8 | 15.905
| SS 110/35/10 kv Khimicheskaya | 16+16 | 32 | 8.46 | 5.5 |  | 2.96 | 0 | 16.8 | 13.84 | 13.84 | opened |  | SS 110/35/10 kv Khimicheskaya | 16+16 | 0.85 | 9.31 | 5.5 |  | 3.81 | 0 | 16.8 | 12.99 | 12.99 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.34 | 4.5 | 60 | 1.84 | 0 | 16.8 | 14.96 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.72 | 7.06 | 4.5 | 60 | 2.56 | 0 | 16.8 | 14.24
| Nom. capacity LV, МVА | 16+16 |  | 2.12 | 1 | 60 | 1.12 | 0 | 16.8 | 15.68 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.13 | 2.25 | 1 | 60 | 1.25 | 0 | 16.8 | 15.55
| SS 110/35/6 kv Bugor | 15+15+25 | 55 | 36.17 | 0.5 |  | 35.67 | 1 | 31.5 | -5.17 | -5.17 | closed |  | SS 110/35/6 kv Bugor | 15+15+25 | 11.583 | 47.753 | 0.5 |  | 47.253 | 1 | 31.5 | -16.753 | -16.753 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.37 | 0 | 0 | 9.37 | 0 | 31.5 | 22.13 |  |  |  | Nom. capacity MV, МVА | 15+15+25 | 10.4 | 19.77 | 0 | 0 | 19.77 | 0 | 31.5 | 11.73
| Nom. capacity LV, МVА | 15+15+25 |  | 26.8 | 0.5 | 40 | 26.3 | 1 | 31.5 | 4.2 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 1.183 | 27.983 | 0.5 | 40 | 27.483 | 1 | 31.5 | 3.017
| SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 115 | 47.33 | 0 |  | 47.33 | 0 | 54.6 | 7.27 | -6.45 | closed |  | SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 1.3705 | 48.7005 | 0 |  | 48.7005 | 0 | 54.6 | 5.8995 | -7.5705 | closed
| Nom. capacity MV, МVА | 63+20 |  | 27.45 | 0 | 0 | 27.45 | 0 | 21 | -6.45 |  |  |  | Nom. capacity MV, МVА | 63+20 | 1.1205 | 28.5705 | 0 | 0 | 28.5705 | 0 | 21 | -7.5705
| Nom. capacity LV, МVА | 63+32+20 |  | 19.88 | 0 | 30 | 19.88 | 0 | 54.6 | 34.72 |  |  |  | Nom. capacity LV, МVА | 63+32+20 | 0.25 | 20.13 | 0 | 30 | 20.13 | 0 | 54.6 | 34.47
| SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 81.5 | 11.03 | 2.5 |  | 8.53 | 0 | 52.5 | 43.97 | -3.6 | closed |  | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 1.551 | 12.581 | 2.5 |  | 10.081 | 0 | 52.5 | 42.419 | -4.352 | closed
| Nom. capacity MV, МVА | 31.5 |  | 5.6 | 2 | 10 | 3.6 | 0 | 2 | -3.6 |  |  |  | Nom. capacity MV, МVА | 31.5 | 0.752 | 6.352 | 2 | 10 | 4.352 | 0 | 2 | -4.352
| Nom. capacity LV, МVА | 25+25 |  | 5.43 | 0.5 | 80 | 4.93 | 0 | 26.25 | 21.32 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.799 | 6.229 | 0.5 | 80 | 5.729 | 0 | 26.25 | 20.521
| SS 110/35/10 kv Usman | 16+16 | 32 | 15.28 | 6.5 |  | 8.78 | 0 | 16.8 | 8.02 | 7.93 | opened |  | SS 110/35/10 kv Usman | 16+16 | 1.444 | 16.724 | 6.5 |  | 10.224 | 0 | 16.8 | 6.576 | 6.576 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.91 | 5 | 20 | -0.09 | 0 | 16.8 | 16.89 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.634 | 5.544 | 5 | 20 | 0.544 | 0 | 16.8 | 16.256
| Nom. Capacity LV, МVА | 16+16 |  | 10.37 | 1.5 | 100 | 8.87 | 0 | 16.8 | 7.93 |  |  |  | Nom. Capacity LV, МVА | 16+16 | 0.81 | 11.18 | 1.5 | 100 | 9.68 | 0 | 16.8 | 7.12
| SS 110/35/10 kv Aksai | 10+10 | 20 | 8.32 | 1.12 |  | 7.2 | 0 | 10.5 | 3.3 | 3.3 | opened |  | SS 110/35/10 kv Aksai | 10+10 | 0.0585 | 8.3785 | 1.12 |  | 7.2585 | 0 | 10.5 | 3.2415 | 3.2415 | opened
| Nom. Capacity MV, МVА | 10+10 |  | 5.82 | 0.5 | 20 | 5.32 | 0 | 10.5 | 5.18 |  |  |  | Nom. Capacity MV, МVА | 10+10 | 0.0535 | 5.8735 | 0.5 | 20 | 5.3735 | 0 | 10.5 | 5.1265
| Nom. capacity LV, МVА | 10+10 |  | 2.5 | 0.62 | 80 | 1.88 | 0 | 10.5 | 8.62 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.005 | 2.505 | 0.62 | 80 | 1.885 | 0 | 10.5 | 8.615
| SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 12.6 | 4.91 | 3.34 |  | 1.57 | 0 | 6.615 | 5.045 | 5.045 | opened |  | SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 0.0655 | 4.9755 | 3.34 |  | 1.6355 | 0 | 6.615 | 4.9795 | 4.9795 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 3.55 | 3 | 10 | 0.55 | 0 | 6.615 | 6.065 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.0605 | 3.6105 | 3 | 10 | 0.6105 | 0 | 6.615 | 6.0045
| Nom. capacity LV, МVА | 6,3+6,3 |  | 1.36 | 0.34 | 80 | 1.02 | 0 | 6.615 | 5.595 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.005 | 1.365 | 0.34 | 80 | 1.025 | 0 | 6.615 | 5.59
| SS 110/35/10 kv Khvorostyanka | 10+16 | 26 | 12.41 | 6.72 |  | 5.69 | 0 | 10.5 | 4.81 | 4.81 | opened |  | SS 110/35/10 kv Khvorostyanka | 10+16 | 0.7965 | 13.2065 | 6.72 |  | 6.4865 | 0 | 10.5 | 4.0135 | 4.0135 | opened
| Nom. capacity MV, МVА | 10+16 |  | 9.32 | 6.5 | 20 | 2.82 | 0 | 10.5 | 7.68 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.7805 | 10.1005 | 6.5 | 20 | 3.6005 | 0 | 10.5 | 6.8995
| Nom. capacity LV, МVА | 10+16 |  | 3.09 | 0.22 | 80 | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.016 | 3.106 | 0.22 | 80 | 2.886 | 0 | 10.5 | 7.614
| SS 110/35/10 kv Dobrinka | 16+10 | 26 | 6.89 | 5.68 |  | 1.21 | 0 | 10.5 | 9.29 | 8.88 | opened |  | SS 110/35/10 kv Dobrinka | 16+10 | 0.094 | 6.984 | 5.68 |  | 1.304 | 0 | 10.5 | 9.196 | 8.816 | opened
| Nom. capacity СН, МВА | 16+10 |  | 3.59 | 4 | 80 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Nom. capacity СН, МВА | 16+10 | 0.03 | 3.62 | 4 | 80 | -0.38 | 0 | 10.5 | 10.88
| Nom. capacity LV, МVА | 16+10 |  | 3.3 | 1.68 | 100 | 1.62 | 0 | 10.5 | 8.88 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.064 | 3.364 | 1.68 | 100 | 1.684 | 0 | 10.5 | 8.816
| SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 12.6 | 1.39 | 0.4 |  | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened |  | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 0.014 | 1.404 | 0.4 |  | 1.004 | 0 | 6.615 | 5.611 | 5.611 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.014 | 0.634 | 0 | 0 | 0.634 | 0 | 6.615 | 5.981
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.77 | 0.4 | 90 | 0.37 | 0 | 6.615 | 6.245 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.77 | 0.4 | 90 | 0.37 | 0 | 6.615 | 6.245
| SS 110/35/10 kv Kazinka | 16+16 | 32 | 15.81 | 0 |  | 15.81 | 0 | 16.8 | 0.99 | 0.99 | opened |  | SS 110/35/10 kv Kazinka | 16+16 | 2.438 | 18.248 | 0 |  | 18.248 | 0 | 16.8 | -1.448 | -1.448 | closed
| Nom. capacity MV, МVА | 16+16 |  | 10.36 | 0 | 0 | 10.36 | 0 | 16.8 | 6.44 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.611 | 11.971 | 0 | 0 | 11.971 | 0 | 16.8 | 4.829
| Nom. capacity LV, МVА | 16+16 |  | 5.45 | 0 | 0 | 5.45 | 0 | 16.8 | 11.35 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.827 | 6.277 | 0 | 0 | 6.277 | 0 | 16.8 | 10.523
| SS 110/35/10 kv Dobroe | 16+16 | 32 | 11.4 | 3 |  | 8.4 | 0 | 16.8 | 8.4 | 8.4 | * |  | SS 110/35/10 kv Dobroe | 16+16 | 1.144 | 12.544 | 3 |  | 9.544 | 0 | 16.8 | 7.256 | 7.256 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.22 | 3 | 20 | 3.22 | 0 | 16.8 | 13.58 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.732 | 6.952 | 3 | 20 | 3.952 | 0 | 16.8 | 12.848
| Nom. capacity LV, МVА | 16+16 |  | 5.18 | 0 | 0 | 5.18 | 0 | 16.8 | 11.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.412 | 5.592 | 0 | 0 | 5.592 | 0 | 16.8 | 11.208
| SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 16.3 | 7.64 | 5 |  | 2.64 | 0 | 6.615 | 3.975 | 3.975 | * |  | SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 0.3305 | 7.9705 | 5 |  | 2.9705 | 0 | 6.615 | 3.6445 | 3.6445 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 5.4 | 5 | 10 | 0.4 | 0 | 6.615 | 6.215 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.2105 | 5.6105 | 5 | 10 | 0.6105 | 0 | 6.615 | 6.0045
| Nom. capacity LV, МVА | 10+6,3 |  | 2.24 | 0 | 0 | 2.24 | 0 | 6.615 | 4.375 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.12 | 2.36 | 0 | 0 | 2.36 | 0 | 6.615 | 4.255
| SS 110/35/6 kv Verbilovo | 10+6,3 | 16.3 | 3.96 | 0 |  | 3.96 | 0 | 6.62 | 2.66 | 2.66 | * |  | SS 110/35/6 kv Verbilovo | 10+6,3 | 0.698 | 4.658 | 0 |  | 4.658 | 0 | 6.62 | 1.962 | 1.962 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 2.76 | 0 | 0 | 2.76 | 0 | 6.62 | 3.86 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.625 | 3.385 | 0 | 0 | 3.385 | 0 | 6.62 | 3.235
| Nom. capacity LV, МVА | 10+6,3 |  | 1.2 | 0 | 0 | 1.2 | 0 | 6.62 | 5.42 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.073 | 1.273 | 0 | 0 | 1.273 | 0 | 6.62 | 5.347
| SS 110/35/10 kv Khlevnoe | 16+16 | 32 | 10.04 | 0 |  | 10.04 | 0 | 16.8 | 6.76 | 6.76 | * |  | SS 110/35/10 kv Khlevnoe | 16+16 | 4.93 | 14.97 | 0 |  | 14.97 | 0 | 16.8 | 1.83 | 1.83 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.377 | 7.237 | 0 | 0 | 7.237 | 0 | 16.8 | 9.563
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 0 | 0 | 4.18 | 0 | 16.8 | 12.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 3.553 | 7.733 | 0 | 0 | 7.733 | 0 | 16.8 | 9.067
| SS 110/35/10 kv Naberezhnoe | 6,3+10 | 16.3 | 2.46 | 4.5 |  | -2.04 | 0 | 6.62 | 8.66 | 5.45 | opened |  | SS 110/35/10 kv Naberezhnoe | 6,3+10 | 1.085 | 3.545 | 4.5 |  | -0.955 | 0 | 6.62 | 7.575 | 5.435 | opened
| Nom. capacity MV, МVА | 6,3+10 |  | 1.29 | 4.5 | 10 | -3.21 | 0 | 6.62 | 9.83 |  |  |  | Nom. capacity MV, МVА | 6,3+10 | 1.07 | 2.36 | 4.5 | 10 | -2.14 | 0 | 6.62 | 8.76
| Nom. capacity LV, МVА | 6,3+10 |  | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45 |  |  |  | Nom. capacity LV, МVА | 6,3+10 | 0.015 | 1.185 | 0 | 0 | 1.185 | 0 | 6.62 | 5.435
| SS 110/35/10 kv Chaplygin | 7,5+6,3 | 13.8 | 5.54 | 4.5 |  | 1.04 | 0 | 6.62 | 5.58 | 5.58 | opened |  | SS 110/35/10 kv Chaplygin | 7,5+6,3 | 0.057 | 5.597 | 4.5 |  | 1.097 | 0 | 6.62 | 5.523 | 5.523 | opened
| Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 7,5+6,3 |  | 5.54 | 4.5 | 30 | 1.04 | 0 | 6.62 | 5.58 |  |  |  | Nom. capacity LV, МVА | 7,5+6,3 | 0.057 | 5.597 | 4.5 | 30 | 1.097 | 0 | 6.62 | 5.523
| SS 110/35/10 kv Troekurovo | 10+6,3 | 16.3 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | opened |  | SS 110/35/10 kv Troekurovo | 10+6,3 | 0.0045 | 1.7545 | 0.5 |  | 1.2545 | 0 | 6.62 | 5.3655 | 5.3155 | opened
| Nom. capacity MV, МVА | 10+6,3 |  | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.0045 | 1.3045 | 0 | 0 | 1.3045 | 0 | 6.62 | 5.3155
| Nom. capacity LV, МVА | 10+6,3 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0 | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67
| Total: | 2565.6 | 2565.6 | 741.5472 | [6 empty] | 705.4128 |  | 2: Total:; 3: 2565.6; 5: 903.5957; Min 12: 549.6453
| deficit | [9 empty] | -38.8294 |  | 2: deficit; Min 12: -66.2919
| proficit | [9 empty] | 472.9684 | taking into account * | 2: proficit; Min 12: 334.4299; Min 13: taking into account *
* Restriction to connected capacity according to working schedule of the grid of 110,220kv (according to data of Lipetsk Regional Dispatching Office)
Note on S31: krutko_eg: нагрузка 1 МВт, введена в сентябре

## Текущий дефицит
List of indoor main substations of IDGC of Centre or Winter loads 2009. (current capacity deficit).
No. | Object of main substation, voltage class | Current deficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA |  | Суммарная полная мощность ЦП по результатам замеров максимума нагрузки Sмах , МВА | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Permissible load calculated in n-1 mode, MVA | Deficit /proficit of main substation, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
| SS 110/10kv Lev Tolstoy | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | closed
| SS 110/10 kv Dvurechki | 6.3 |  | 2.03 | 0.1 | 70 | 1.93 | 0 | 0.1 | -1.93 | -1.93 | closed
| SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed
| SS 35/10 kv Preobrazhenye | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | closed
| SS 35/10 kv Yakovlevo | 2.5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 0 | -0.9 | -0.9 | closed
| SS 110/10kv Terbunsky gonchar | 25 |  | 4: без нагрузки
| SS 35/10 kv Pervomayskaya | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | closed
| SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.91 | 0.9 | 90 | 0.01 | 0 | 0.9 | -0.01 | -0.01 | closed
| SS 35/10 kv Znamenka | 2.5 |  | 0.87 | 0.4 | 8 часов | 0.47 | 0 | 0.4 | -0.47 | -0.47 | closed
| SS 35/10 kv Pikovo | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | closed
| SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed
| SS 35/10 kv SOM | 1.6 |  | 0.1 |  |  | 0.1 | 0 | 0 | -0.1 | -0.1 | closed
| SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed
| SS 35/10 kv Novodubovoe | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0 | -0.88 | -0.88 | closed
| SS 35/10 kv Kurino | 2.5 |  | 0.53 | 0 | 0 | 0.53 | 0 | 0 | -0.53 | -0.53 | closed
| SS 35/10 kv Berezovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed
| SS 35/6 kv Karyer | 4 |  | 4: без нагрузки
Two- and more transformer substations (for two voltage levels)
| SS 110/10 kv Kuyman | 2,5+2,5 | 5 | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | *
| SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 80 | 45.62 | 4.5 | 30 | 41.12 | 0 | 42 | 0.88 | 0.88 | *
| SS 110/6 kv Privokzalnaya | 20+20+25 | 65 | 49.71 | 1.38 | 30 | 48.33 | 0 | 42 | -6.33 | -6.33 | closed
| SS 110/10/6 kv Yuzhnaya | 40+40 | 80 | 43.07 | 6 | 30 | 37.07 | 0 | 42 | 4.93 | 4.93 | *
| SS 110/6 kv Sitovka | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
| SS 110/6 kv LTP | 6,3+10 | 16.3 | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | *
| SS 110/6 kv KPD | 10+10 | 20 | 2.31 | 0 | 0 | 2.31 | 0 | 10.5 | 8.19 | 8.19 | *
| SS 110/10 kv Oktyabskaya | 40+40 | 80 | 19.12 | 4 | 30 | 15.12 | 0 | 42 | 26.88 | 26.88 | *
| SS 110/6 kv Teplichnaya | 15+15 | 30 | 7.58 | 0 | 0 | 7.58 | 0 | 15.75 | 8.17 | 8.17 | *
| SS 110/6 kv GPP-2 LTZ | 63+63 | 126 | 12.14 | 0 | 0 | 12.14 | 0 | 66.15 | 54.01 | 54.01 | *
| SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 4.8 | 2.35 | 0 | 0 | 2.35 | 0 | 1.68 | -0.67 | -0.67 | closed
| SS 35/6 kv No. 2 | 1+1+1 | 3 | 3.49 | 0 | 0 | 3.49 | 0 | 1.05 | -2.44 | -2.44 | closed
| SS 35/10 kv No. 3 | 2,5+2,5 | 5 | 1.26 | 0.46 | 90 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | *
| SS 35/6 kv No. 4 | 4+4 | 8 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | *
| SS 35/10 kv Butyrki | 5,6+4 | 9.6 | 7.13 | 0 | 0 | 7.13 | 0 | 4.2 | -2.93 | -2.93 | closed
| SS 35/10 kv Matyra | 4+3,2 | 7.2 | 4.68 | 0 | 0 | 4.68 | 0 | 3.36 | -1.32 | -1.32 | closed
| SS 35/10 kv Trubetchino | 2,5+2,5 | 5 | 1.71 | 0 | 0 | 1.71 | 0 | 2.625 | 0.915 | 0.915 | *
| SS 35/10 kv Ratchino | 2,5+2,5 | 5 | 1.11 | 0.12 | 70 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | *
| SS 35/10 kv Kalikino | 3,2+3,2 | 6.4 | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | *
| SS 35/10 kv Borisovka | 4+2,5 | 6.5 | 2.74 | 0 | 0 | 2.74 | 0 | 2.625 | -0.115 | -0.115 | closed
| SS 35/10 kv Vvedenka | 4+4 | 8 | 4 | 0.14 | 70 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | *
| SS 35/10 kv Gryaznoe | 4+4 | 8 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | *
| SS 35/10 kv Borino | 4+4 | 8 | 4.24 | 1.2 | 90 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | *
| SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 5 | 1.6 | 1.88 | 100 (45) | -0.28 | 0 | 2.625 | 2.905 | 2.905 | *
| SS 35/10 kv Troitskaya | 2,5+4 | 6.5 | 2.33 | 0.6 | 70 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | *
| SS 35/6 kv Veshalovka | 2,5+2,5 | 5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | *
| SS 35/10 kv Pruzhinki | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | *
| SS 35/10 kv Stebaevo | 2,5+2,5 | 5 | 0.95 | 0.28 | 80 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | *
| SS 35/10 kv Khleboprodukty | 6,3+6,3 | 12.6 | 3.76 | 0.6 | 100 | 3.16 | 0 | 6.615 | 3.455 | 3.455 | *
| SS 35/10 kv Sentsovo | 10+10 | 20 | 7.28 | 0 | 0 | 7.28 | 0 | 10.5 | 3.22 | 3.22 | *
| SS 35/10 kv Meet processing factory | 6,3+6,3 | 12.6 | 4.63 | 1.6 | 110 | 3.03 | 0 | 6.62 | 3.59 | 3.59 | *
| SS 35/6 kv Poultry plant | 4+4 | 8 | 1.93 | 0 | 0 | 1.93 | 0 | 4.2 | 2.27 | 2.27 | *
| SS 35/6 kv Water intake | 10+10 | 20 | 1 | 0 | 0 | 1 | 0 | 10.5 | 9.5 | 9.5 | *
| SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 5 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | *
| SS 35/10 kv Dmitryashevka | 2,5+2,5 | 5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | *
| SS 35/10 kv Rechnaya | 4+4 | 8 | 1.57 | 1.06 | 100 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | *
| SS 35/10 kv Negachevka | 2,5+2,5 | 5 | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | *
| SS 35/10 kv Tyushevka | 1,6+1,6 | 3.2 | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | *
| SS 35/10 kv Sselki | 10+10 |  | 4: 0
Two- and more transformer substations (for three voltage levels)
| SS 110/35/6 kv Bugor | 15+15+25 | 55 | 36.17 | 0.5 |  | 35.67 | 1 | 31.5 | -5.17 | -5.17 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.37 | 0 | 0 | 9.37 | 0 | 31.5 | 22.13
| Nom. capacity LV, МVА | 15+15+25 |  | 26.8 | 0.5 | 40 | 26.3 | 1 | 31.5 | 4.2
| SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 115 | 47.33 | 0 |  | 47.33 | 0 | 54.6 | 7.27 | -6.45 | closed
| Nom. capacity MV, МVА | 63+20 |  | 27.45 | 0 | 0 | 27.45 | 0 | 21 | -6.45
| Nom. capacity LV, МVА | 63+32+20 |  | 19.88 | 0 | 30 | 19.88 | 0 | 54.6 | 34.72
| SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 81.5 | 11.03 | 2.5 |  | 8.53 | 0 | 52.5 | 43.97 | -3.6 | closed
| Nom. capacity MV, МVА | 31.5 |  | 5.6 | 2 | 10 | 3.6 | 0 | 2 | -3.6
| Nom. capacity LV, МVА | 25+25 |  | 5.43 | 0.5 | 80 | 4.93 | 0 | 26.25 | 21.32
| SS 110/35/10 kv Dobroe | 16+16 | 32 | 11.4 | 3 |  | 8.4 | 0 | 16.8 | 8.4 | 8.4 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.22 | 3 | 20 | 3.22 | 0 | 16.8 | 13.58
| Nom. capacity LV, МVА | 16+16 |  | 5.18 | 0 | 0 | 5.18 | 0 | 16.8 | 11.62
| SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 16.3 | 7.64 | 5 |  | 2.64 | 0 | 6.615 | 3.975 | 3.975 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 5.4 | 5 | 10 | 0.4 | 0 | 6.615 | 6.215
| Nom. capacity LV, МVА | 10+6,3 |  | 2.24 | 0 | 0 | 2.24 | 0 | 6.615 | 4.375
| SS 110/35/6 kv Verbilovo | 10+6,3 | 16.3 | 3.96 | 0 |  | 3.96 | 0 | 6.62 | 2.66 | 2.66 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 2.76 | 0 | 0 | 2.76 | 0 | 6.62 | 3.86
| Nom. capacity LV, МVА | 10+6,3 |  | 1.2 | 0 | 0 | 1.2 | 0 | 6.62 | 5.42
| SS 110/35/10 kv Khlevnoe | 16+16 | 32 | 10.04 | 0 |  | 10.04 | 0 | 16.8 | 6.76 | 6.76 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 0 | 0 | 4.18 | 0 | 16.8 | 12.62
| deficit |  |  | Мин. 11: -38.8294
* Restriction to connected capacity according to working schedule of the grid of 110,220kv (according to data of Lipetsk Regional Dispatching Office)
Note on E25: krutko_eg: нагрузка 1 МВт, введена в сентябре
Note on E65: krutko_eg: введена в сентябре, потебители неподключены

## Перспективный дефицит
Приложение 2
Форма расчёта пропускной способности Центров питания филиала ОАО "МРСК Центра" Липецкэнерго по итогам зимнего замера максимума нагрузки 2009 г. | [12 empty] | List of indoor main substations of the division of IDGC of Centre-"Lipetskenergo" for expected loads taking into account of new capacities on technological connection (expected deficit).
таблица 1
№п/п | Наименование объекта центра питания, класс напряжения | Текущий дефицит | [9 empty] | Примечание | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Установленная мощность трансформаторов Sуст. с указанием их количества, шт/ МВА |  | Суммарная полная мощность ЦП по результатам замеров максимума нагрузки Sмах , МВА | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Дефицит/профицит ЦП, МВА |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Permissible load calculated in n-1 mode, MVA | Deficit /proficit of main substation, MVA
[5 empty] | МВА | Мин. | [11 empty] | МВА | Мин.
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Однотрансформаторные ПС | [12 empty] | 1: One-transformer substations
| ПС 110/10кВ Лев Толстой | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | закрыт |  | SS 110/10kv Lev Tolstoy | 10 | 0.028 | 2.658 | 1.6 | 30 | 1.058 | 0 | 1.6 | -1.058 | -1.058 | closed
| ПС 110/10 кВ Двуречки | 6.3 |  | 2.03 | 0.1 | 70 | 1.93 | 0 | 0.1 | -1.93 | -1.93 | закрыт |  | SS 110/10 kv Dvurechki | 6.3 | 0.178 | 2.208 | 0.1 | 70 | 2.108 | 0 | 0.1 | -2.108 | -2.108 | closed
| ПС 35/10 кВ Озёрки | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | закрыт |  | SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed
| ПС 35/10 кВ Преображенье | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | закрыт |  | SS 35/10 kv Preobrazhenye | 2.5 | 0.03 | 0.49 | 0 | 0 | 0.49 | 0 | 0 | -0.49 | -0.49 | closed
| ПС 35/10 кВ Яковлево | 2.5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 0 | -0.9 | -0.9 | закрыт |  | SS 35/10 kv Yakovlevo | 2.5 | 0.526 | 1.426 | 0 | 0 | 1.426 | 0 | 0 | -1.426 | -1.426 | closed
| ПС 110/10кВ Тербунский гончар | 25 |  | без нагрузки | [8 empty] | 2: SS 110/10kv Terbunsky gonchar; 3: 25; 4: 9.95; 5: 9.95
| ПС 35/10 кВ Первомайская | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | закрыт |  | SS 35/10 kv Pervomayskaya | 2.5 | 0.008 | 0.858 | 0.3 | 60 | 0.558 | 0 | 0.3 | -0.558 | -0.558 | closed
| ПС 35/10 кВ Каменная Лубна | 2.5 |  | 0.91 | 0.9 | 90 | 0.01 | 0 | 0.9 | -0.01 | -0.01 | закрыт |  | SS 35/10 kv Kamennaya Lubna | 2.5 | 0.06 | 0.97 | 0.9 | 90 | 0.07 | 0 | 0.9 | -0.07 | -0.07 | closed
| ПС 35/10 кВ Знаменка | 2.5 |  | 0.87 | 0.4 | 8 часов | 0.47 | 0 | 0.4 | -0.47 | -0.47 | закрыт |  | SS 35/10 kv Znamenka | 2.5 | 0.02 | 0.89 | 0.4 | 8 часов | 0.49 | 0 | 0.4 | -0.49 | -0.49 | closed
| ПС 35/10 кВ Пиково | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | закрыт |  | SS 35/10 kv Pikovo | 2.5 | 0.008 | 0.598 | 0.5 | 60 | 0.098 | 0 | 0.5 | -0.098 | -0.098 | closed
| ПС 35/10 кВ Песковатка | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | закрыт |  | SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed
| ПС 35/6 кВ Дружба | 5.6 |  | КРУНН-6кВ не наши | [7 empty] | открыт | 2: ПС 35/6 кВ Дружба; 3: 5.6; 5: 0
| ПС 35/10 кВ СОМ | 1.6 |  | 0.1 |  |  | 0.1 | 0 | 0 | -0.1 | -0.1 | закрыт | 2: SS 35/10 kv SOM; 3: 1.6; 5: 0.1; Мин. 10: 0; Мин. 11: -0.1; Мин. 12: -0.1; Мин. 13: closed
| ПС 35/6 кВ Новониколаевка | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | закрыт |  | SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed
| ПС 35/10 кВ Синдякино | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | закрыт |  | ПС 35/10 кВ Синдякино | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | открыт
| ПС 35/10 кВ Курино | 2.5 |  | 0.5 | 0 | 0 | 0.5 | 0 | 0 | -0.5 | -0.5 | закрыт |  | SS 35/10 kv Kurino | 2.5 | 0.053 | 0.583 | 0 | 0 | 0.583 | 0 | 0 | -0.583 | -0.583 | closed
| ПС 35/10 кВ Новодубовое | 2.5 |  | 0.88 | 0 | 0 | 0.88 | 0 | 0 | -0.88 | -0.88 | открыт |  | SS 35/10 kv Novodubovoe | 2.5 | 0.031 | 0.911 | 0 | 0 | 0.911 | 0 | 0 | -0.911 | -0.911 | closed
| ПС 35/10 кВ Березовка | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | закрыт |  | SS 35/10 kv Berezovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed
| ПС 35/6 кВ Карьер | 4 |  | без нагрузки | [8 empty] | 2: SS 35/6 kv Karyer; 3: 4; 5: 0
Двух- и более трансформаторные ПС (на два уровня напряжения) | [12 empty] | 1: Two- and more transformer substations (for two voltage levels)
| ПС 110/6 кВ Агрегатная | 16+16 | 32 | 15.14 | 0 | 0 | 15.14 | 0 | 16.8 | 1.66 | 1.66 | открыт |  | ПС 110/6 кВ Агрегатная | 16+16 | 0.404 | 15.544 | 0 | 0 | 15.544 | 0 | 16.8 | 1.256 | 1.256 | открыт
| ПС 110/6 кВ Западная | 40+40 | 80 | 17.44 | 0 | 0 | 17.44 | 0 | 42 | 24.56 | 24.56 | открыт |  | ПС 110/6 кВ Западная | 40+40 | 2.758 | 20.198 | 0 | 0 | 20.198 | 0 | 42 | 21.802 | 21.802 | открыт
| ПС 110/10 кВ Кашары | 2,5+6,3 | 8.8 | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | открыт |  | ПС 110/10 кВ Кашары | 2,5+6,3 |  | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | открыт
| ПС 110/6 кВ Табак | 16+16 | 32 | 9.48 | 3.2 | 20 | 6.28 | 0 | 16.8 | 10.52 | 10.52 | открыт |  | ПС 110/6 кВ Табак | 16+16 | 0.018 | 9.498 | 3.2 | 20 | 6.298 | 0 | 16.8 | 10.502 | 10.502 | открыт
| ПС 110/10 кВ Лукошкино | 10+2,5 | 12.5 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | открыт |  | ПС 110/10 кВ Лукошкино | 10+2,5 |  | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | открыт
| ПС 110/10кВ Нива | 10+10 | 20 | 5.09 | 1 | 100 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | открыт |  | ПС 110/10кВ Нива | 10+10 | 0.02 | 5.11 | 1 | 100 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | открыт
| ПС 110/10 кВ Ольховец | 2,5+2,5 | 5 | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | открыт |  | ПС 110/10 кВ Ольховец | 2,5+2,5 |  | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | открыт
| ПС 110/10 кВ Куймань | 2,5+2,5 | 5 | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | * |  | ПС 110/10 кВ Куймань | 2,5+2,5 |  | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | открыт
| ПС 110/10 кВ Лутошкино | 2,5+2,5 | 5 | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | открыт |  | ПС 110/10 кВ Лутошкино | 2,5+2,5 |  | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | открыт
| ПС 110/10 кВ Круглое | 2,5+2,5 | 5 | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | открыт |  | ПС 110/10 кВ Круглое | 2,5+2,5 |  | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | открыт
| ПС 110/10/6 кВ Юго-Западная | 40+40 | 80 | 45.62 | 4.5 | 30 | 41.12 | 0 | 42 | 0.88 | 0.88 | * |  | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 12.733 | 58.353 | 4.5 | 30 | 53.853 | 0 | 42 | -11.853 | -11.853 | closed
| ПС 110/6 кВ Привокзальная | 20+20+25 | 65 | 49.71 | 1.38 | 30 | 48.33 | 0 | 42 | -6.33 | -6.33 | закрыт |  | SS 110/6 kv Privokzalnaya | 20+20+25 | 0.978 | 50.688 | 1.38 | 30 | 49.308 | 0 | 42 | -7.308 | -7.308 | closed
| ПС 110/10/6 кВ Южная | 40+40 | 80 | 43.07 | 6 | 30 | 37.07 | 0 | 42 | 4.93 | 4.93 | * |  | SS 110/10/6 kv Yuzhnaya | 40+40 | 4.577 | 47.647 | 6 | 30 | 41.647 | 0 | 42 | 0.353 | 0.353 | *
| ПС 110/6 кВ Ситовка | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | * |  | SS 110/6 kv Sitovka | 10+10 |  | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
| ПС 110/6 кВ ЛТП | 6,3+10 | 16.3 | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | * |  | SS 110/6 kv LTP | 6,3+10 |  | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | *
| ПС 110/6 кВ КПД | 10+10 | 20 | 2.31 | 0 | 0 | 2.31 | 0 | 10.5 | 8.19 | 8.19 | * |  | SS 110/6 kv KPD | 10+10 | 3 | 5.31 | 0 | 0 | 5.31 | 0 | 10.5 | 5.19 | 5.19 | *
| ПС 110/10 кВ Октябрьская | 40+40 | 80 | 19.12 | 4 | 30 | 15.12 | 0 | 42 | 26.88 | 26.88 | * |  | SS 110/10 kv Oktyabskaya | 40+40 | 12.089 | 31.209 | 4 | 30 | 27.209 | 0 | 42 | 14.791 | 14.791 | *
| ПС 110/10 кВ Университетская | 40+40 |  | 0 | 0 | 0 | 0 | 0 | 42 | 42 | 42 | открыт |  | SS 110/10 kv Universitetskaya | 40+40 | 40.95 | 40.95 | 0 | 0 | 40.95 | 0 | 42 | 1.05 | 1.05 | closed
| ПС 110/6 кВ Тепличная | 15+15 | 30 | 7.58 | 0 | 0 | 7.58 | 0 | 15.75 | 8.17 | 8.17 | * |  | SS 110/6 kv Teplichnaya | 15+15 | 0.014 | 7.594 | 0 | 0 | 7.594 | 0 | 15.75 | 8.156 | 8.156 | *
| ПС 110/6 кВ ГПП-2 ЛТЗ | 63+63 | 126 | 12.14 | 0 | 0 | 12.14 | 0 | 66.15 | 54.01 | 54.01 | * |  | SS 110/6 kv GPP-2 LTZ | 63+63 | 1.6 | 13.74 | 0 | 0 | 13.74 | 0 | 66.15 | 52.41 | 52.41 | *
| ПС 35/10 кВ Авангард | 4+4 | 8 | 1.1 | 1.2 | 110 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | открыт |  | ПС 35/10 кВ Авангард | 4+4 | 0.008 | 1.108 | 1.2 | 110 | -0.092 | 0 | 4.2 | 4.292 | 4.292 | открыт
| ПС 35/10 кВ Афанасьево | 2,5+2,5 | 5 | 1.81 | 0 | 0 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | открыт |  | ПС 35/10 кВ Афанасьево | 2,5+2,5 | 0.038 | 1.848 | 0 | 0 | 1.848 | 0 | 2.625 | 0.777 | 0.777 | открыт
| ПС 35/10 кВ Бабарыкино | 2,5+2,5 | 5 | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | открыт |  | ПС 35/10 кВ Бабарыкино | 2,5+2,5 |  | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | открыт
| ПС 35/10 кВ Аврора | 2,5+2,5 | 5 | 0.88 | 1.2 | 110 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | открыт |  | ПС 35/10 кВ Аврора | 2,5+2,5 | 0.282 | 1.162 | 1.2 | 110 | -0.038 | 0 | 2.625 | 2.663 | 2.663 | открыт
| ПС 35/10 кВ Б.Боёвка | 2,5+2,5 | 5 | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | открыт |  | ПС 35/10 кВ Б.Боёвка | 2,5+2,5 |  | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | открыт
| ПС 35/10 кВ Борки | 2,5+2,5 | 5 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | открыт |  | ПС 35/10 кВ Борки | 2,5+2,5 |  | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | открыт
| ПС 35/6кВ Восточная | 10+16 | 26 | 8.72 | 4.8 | 20 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | открыт |  | ПС 35/6кВ Восточная | 10+16 | 2 | 10.72 | 4.8 | 20 | 5.92 | 0 | 10.5 | 4.58 | 4.58 | открыт
| ПС 35/10 кВ Васильевка | 2,5+2,5 | 5 | 0.52 | 1.5 | 90 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | открыт |  | ПС 35/10 кВ Васильевка | 2,5+2,5 |  | 0.52 | 1.5 | 90 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | открыт
| ПС 35/10 кВ Воронец | 4+4 | 8 | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | открыт |  | ПС 35/10 кВ Воронец | 4+4 |  | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | открыт
| ПС 35/6 кВ Голиково | 1,8+1,6 | 3.4 | 0.11 | 0 | 0 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | открыт |  | ПС 35/6 кВ Голиково | 1,8+1,6 |  | 0.11 | 0 | 0 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | открыт
| ПС 35/10 кВ Гатище | 2,5+2,5 | 5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | открыт |  | ПС 35/10 кВ Гатище | 2,5+2,5 |  | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | открыт
| ПС 35/10 кВ Гнилуша | 6,3+6,3 | 12.6 | 1.36 | 1.2 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | открыт |  | ПС 35/10 кВ Гнилуша | 6,3+6,3 | 0.601 | 1.961 | 1.2 | 120 | 0.761 | 0 | 6.615 | 5.854 | 5.854 | открыт
| ПС 35/10кВ Грызлово | 2,5+2,5 | 5 | 0.54 | 0.8 | 110 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | открыт |  | ПС 35/10кВ Грызлово | 2,5+2,5 |  | 0.54 | 0.8 | 110 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | открыт
| ПС 35/10 кВ Жерновное | 2,5+2,5 | 5 | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | открыт |  | ПС 35/10 кВ Жерновное | 2,5+2,5 |  | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | открыт
| ПС 35/10 кВ Задонск-сельск. | 3,2+1,6 | 4.8 | 2.35 | 0 | 0 | 2.35 | 0 | 1.68 | -0.67 | -0.67 | закрыт |  | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.27 | 2.62 | 0 | 0 | 2.62 | 0 | 1.68 | -0.94 | -0.94 | closed
| ПС 35/10 кВ Захаровка | 2,5+2,5 | 5 | 0.42 | 0.8 | 60 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.42 | 0.8 | 60 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | открыт
| ПС 35/10 кВ Казаки | 4+4 | 8 | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | открыт |  | SS 35/10 kv No. 3 | 4+4 |  | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | открыт
| ПС 35/10 кВ Колесово | 6,3+6,3 | 12.6 | 1.38 | 1.5 | 90 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | открыт |  | SS 35/6 kv No. 4 | 6,3+6,3 | 0.322 | 1.702 | 1.5 | 90 | 0.202 | 0 | 6.615 | 6.413 | 6.413 | открыт
| ПС 35/10 кВ Князево | 2,5+2,5 | 5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | открыт
| ПС 35/10 кВ Кириллово | 2,5+2,5 | 5 | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | открыт
| ПС 35/10 кВ Ксизово | 2,5+2,5 | 5 | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | открыт
| ПС 35/10 кВ Ламское | 2,5+2,5 | 5 | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | открыт |  | SS 35/6 kv No. 4 | 2,5+2,5 |  | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | открыт
| ПС 35/10 кВ Казачье | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 | 0.388 | 0.678 | 0 | 0 | 0.678 | 0 | 2.625 | 1.947 | 1.947 | открыт
| ПС 35/10 кВ Лебяжье | 2,5+1,6 | 4.1 | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | открыт |  | SS 35/6 kv No. 2 | 2,5+1,6 |  | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | открыт
| ПС 35/10 кВ Ломовец | 1,6+2,5 | 4.1 | 0.24 | 0 | 0 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | открыт |  | SS 35/10 kv No. 3 | 1,6+2,5 |  | 0.24 | 0 | 0 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | открыт
| ПС 35/10 кВ Ольшанец | 2,5+4 | 6.5 | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | открыт |  | SS 35/6 kv No. 4 | 2,5+4 |  | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | открыт
| ПС 35/10 кВ Плоское | 4+4 | 8 | 3.76 | 3 | 70 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 4+4 | 0.026 | 3.786 | 3 | 70 | 0.786 | 0 | 4.2 | 3.414 | 3.414 | открыт
| ПС 35/10 кВ Стегаловка | 2,5+3,2 | 5.7 | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | открыт |  | SS 35/6 kv No. 2 | 2,5+3,2 |  | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | открыт
| ПС 35/10 кВ Солидарность | 4+4 | 8 | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | открыт |  | SS 35/10 kv No. 3 | 4+4 |  | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | открыт
| ПС 35/10 кВ Тимирязево | 4+4 | 8 | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | открыт |  | SS 35/6 kv No. 4 | 4+4 |  | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | открыт
| ПС 35/10 кВ Талица | 2,5+2,5 | 5 | 1.55 | 1.5 | 110 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 | 0.007 | 1.557 | 1.5 | 110 | 0.057 | 0 | 2.625 | 2.568 | 2.568 | открыт
| ПС 35/10 кВ II-е Тербуны | 2,5+2,5 | 5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 | 1.07 | 1.86 | 0 | 0 | 1.86 | 0 | 2.625 | 0.765 | 0.765 | открыт
| ПС 35/10 кВ Тихий Дон | 4+4 | 8 | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | открыт |  | SS 35/10 kv No. 3 | 4+4 |  | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | открыт
| ПС 35/10 кВ Хитрово | 6,3+6,3 | 12.6 | 0.36 | 0 | 0 | 0.36 | 0 | 6.615 | 6.255 | 6.255 | открыт |  | SS 35/6 kv No. 4 | 6,3+6,3 |  | 0.36 | 0 | 0 | 0.36 | 0 | 6.62 | 6.26 | 6.26 | открыт
| ПС 35/10 кВ Чернава | 2,5+2,5 | 5 | 2.02 | 0 | 0 | 2.02 | 0 | 2.625 | 0.605 | 0.605 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 | 0.015 | 2.035 | 0 | 0 | 2.035 | 0 | 2.625 | 0.59 | 0.59 | открыт
| ПС 35/10 кВ Чернолес | 2,5+2,5 | 5 | 0.18 | 0 | 0 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 | 0.007 | 0.187 | 0 | 0 | 0.187 | 0 | 2.625 | 2.438 | 2.438 | открыт
| ПС 35/6 кВ ПС № 5 | 6,3+3,2 | 9.5 | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | открыт |  | SS 35/10 kv No. 3 | 6,3+3,2 |  | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | открыт
| ПС 35/10 кВ Kрасное | 4+4 | 8 | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | открыт |  | SS 35/6 kv No. 4 | 4+4 |  | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | открыт
| ПС 35/10 кВ Теплое | 2,5+2,5 | 5 | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | открыт
| ПС 35/10 кВ Данков-сельская | 6,3+4 | 10.3 | 5.61 | 2 | 120 | 3.61 | 0 | 4.2 | 0.59 | 0.59 | открыт |  | SS 35/6 kv No. 2 | 6,3+6,3 | 0.61 | 6.22 | 2 | 120 | 4.22 | 0 | 6.615 | 2.395 | 2.395 | открыт
| ПС 35/10 кВ Колыбельская | 2,5+2,5 | 5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | открыт
| ПС 35/10 кВ Топки | 2,5+2,5 | 5 | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | открыт |  | SS 35/6 kv No. 4 | 2,5+2,5 |  | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | открыт
| ПС 35/10 кВ Агроном | 4+6,3 | 10.3 | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 4+6,3 |  | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | открыт
| ПС 35/10 кВ Троекурово-совхозная | 2,5+2,5 | 5 | 2.14 | 0.5 | 60 | 1.64 | 0 | 2.625 | 0.985 | 0.985 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 | 0.021 | 2.161 | 0.5 | 60 | 1.661 | 0 | 2.625 | 0.964 | 0.964 | открыт
| ПС 35/10 кВ Гагарино | 1,8+1,8 | 3.6 | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | открыт |  | SS 35/10 kv No. 3 | 1,8+1,8 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | открыт
| ПС 35/10 кВ Раненбург | 1,6+1,6 | 3.2 | 1.95 | 0.5 | 60 | 1.45 | 0 | 1.68 | 0.23 | 0.23 | открыт |  | SS 35/6 kv No. 4 | 1,6+1,6 | 0.177 | 2.127 | 0.5 | 60 | 1.627 | 0 | 1.68 | 0.053 | 0.053 | открыт
| ПС 35/10 кВ Сергиевка | 2,5+2,5 | 5 | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | открыт
| ПС 35/10 кВ Дрезгалово | 1,6+1,6 | 3.2 | 0.37 | 0.5 | 60 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | открыт |  | SS 35/6 kv No. 2 | 1,6+1,6 | 0.015 | 0.385 | 0.5 | 60 | -0.115 | 0 | 1.68 | 1.795 | 1.795 | открыт
| ПС 35/10 кВ Долгое | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | открыт
| ПС 35/10 кВ Воскресеновка | 1,6+1,6 | 3.2 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | открыт |  | SS 35/6 kv No. 4 | 1,6+1,6 |  | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | открыт
| ПС 35/10 кВ Сапрыкино | 1,6+2,5 | 4.1 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 1,6+2,5 | 0.011 | 0.591 | 0 | 0 | 0.591 | 0 | 1.68 | 1.089 | 1.089 | открыт
| ПС 35/10 кВ Новополянье | 2,5+2,5 | 5 | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | открыт
| ПС 35/10 кВ Ведное | 2,5+2,5 | 5 | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | открыт
| ПС 35/10 кВ Бигильдино | 2,5+2,5 | 5 | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | открыт |  | SS 35/6 kv No. 4 | 2,5+2,5 |  | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | открыт
| ПС 35/10 кВ Культура | 2,5+2,5 | 5 | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | открыт
| ПС 35/10 кВ Борятино | 2,5+2,5 | 5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | открыт
| ПС 35/10 кВ Б.Попово | 2,5+2,5 | 5 | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | открыт
| ПС 35/10 кВ Б. Избищи | 2,5+2,5 | 5 | 1.8 | 0.5 | 60 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | открыт |  | SS 35/6 kv No. 4 | 2,5+2,5 | 0.75 | 2.55 | 0.5 | 60 | 2.05 | 0 | 2.625 | 0.575 | 0.575 | открыт
| ПС 35/10 кВ Полибино | 2,5+2,5 | 5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | открыт
| ПС 35/10 кВ Дубрава | 2,5+2,5 | 5 | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | открыт
| ПС 35/10 кВ Хрущево | 2,5+2,5 | 5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | открыт
| ПС 35/10 кВ Б. Верх | 2,5+2,5 | 5 | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | открыт |  | SS 35/6 kv No. 4 | 2,5+2,5 |  | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | открыт
| ПС 35/10 кВ Головинщино | 2,5+2,5 | 5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 2,5+2,5 |  | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | открыт
| ПС 35/10 кВ Яблонево | 2,5+2,5 | 5 | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | открыт |  | SS 35/6 kv No. 2 | 2,5+2,5 |  | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | открыт
| ПС 35/10 кВ Политово | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | открыт |  | SS 35/10 kv No. 3 | 2,5+2,5 |  | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | открыт
| ПС 35/10 кВ Комплекс | 4+4 | 8 | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | открыт |  | SS 35/6 kv No. 4 | 4+4 |  | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | открыт
| ПС 35/10 кВ № 1 | 4+4 | 8 | 3.38 | 0 | 0 | 3.38 | 0 | 4.2 | 0.82 | 0.82 | открыт |  | SS 35/10 kv Zadonsk-selsk. | 4+4 | 0.176 | 3.556 | 0 | 0 | 3.556 | 0 | 4.2 | 0.644 | 0.644 | открыт
| ПС 35/6 кВ № 2 | 1+1+1 | 3 | 3.49 | 0 | 0 | 3.49 | 0 | 1.05 | -2.44 | -2.44 | закрыт |  | SS 35/6 kv No. 2 | 1+1+1 | 0.334 | 3.824 | 0 | 0 | 3.824 | 0 | 1.05 | -2.774 | -2.774 | closed
| ПС 35/10 кВ № 3 | 2,5+2,5 | 5 | 1.26 | 0.46 | 90 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | * |  | SS 35/10 kv No. 3 | 2,5+2,5 | 1.712 | 2.972 | 0.46 | 90 | 2.512 | 0 | 2.625 | 0.113 | 0.113 | *
| ПС 35/6 кВ № 4 | 4+4 | 8 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | * |  | SS 35/6 kv No. 4 | 4+4 | 0.157 | 2.787 | 0 | 0 | 2.787 | 0 | 4.2 | 1.413 | 1.413 | *
| ПС 35/6 кВ Грязи-город | 6,3+5,6 | 11.9 | 4.5 | 0 | 0 | 4.5 | 0 | 5.88 | 1.38 | 1.38 | открыт |  | ПС 35/6 кВ Грязи-город | 6,3+5,6 | 0.456 | 4.956 | 0 | 0 | 4.956 | 0 | 5.88 | 0.924 | 0.924 | открыт
| ПС 35/10 кВ Бутырки | 5,6+4 | 9.6 | 7.13 | 1.6 | 100 | 5.53 | 0 | 4.2 | -1.33 | -1.33 | закрыт |  | SS 35/10 kv Butyrki | 5,6+4 | -1.094 | 6.036 | 0 | 0 | 6.036 | 0 | 4.2 | -1.836 | -1.836 | closed
| ПС 35/10 кВ Ярлуково | 3,2+4 | 7.2 | 3.4 | 1.5 | 80 | 1.9 | 0 | 3.36 | 1.46 | 1.46 | открыт |  | SS 35/10 kv Matyra | 3,2+4 | 0.212 | 3.612 | 1.5 | 80 | 2.112 | 0 | 3.36 | 1.248 | 1.248 | открыт
| ПС 35/10 кВ Княжья Байгора | 1,6+1,6 | 3.2 | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | открыт |  | SS 35/10 kv Butyrki | 1,6+1,6 |  | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | открыт
| ПС 35/10 кВ Правда | 4+2,5 | 6.5 | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | открыт |  | SS 35/10 kv Matyra | 4+2,5 |  | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | открыт
| ПС 35/10 кВ Красная Дубрава | 2,5+2,5 | 5 | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | открыт |  | SS 35/10 kv Butyrki | 2,5+2,5 |  | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | открыт
| ПС 35/10 кВ Матыра | 4+3,2 | 7.2 | 4.68 | 0 | 0 | 4.68 | 0 | 3.36 | -1.32 | -1.32 | закрыт |  | SS 35/10 kv Matyra | 4+3,2 | 0.208 | 4.888 | 0 | 0 | 4.888 | 0 | 3.36 | -1.528 | -1.528 | closed
| ПС 35/10 кВ Вперед | 4+4 | 8 | 0.88 | 0.32 | 80 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | открыт |  | ПС 35/10 кВ Вперед | 4+4 | 0.045 | 0.925 | 0.32 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | открыт
| ПС 35/10 кВ Малей | 4+2,5 | 6.5 | 0.48 | 0.12 | 70 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | открыт |  | ПС 35/10 кВ Малей | 4+2,5 | 0.016 | 0.496 | 0.12 | 70 | 0.376 | 0 | 2.625 | 2.249 | 2.249 | открыт
| ПС 35/10 кВ СХТ | 2,5+1,6 | 4.1 | 0.96 | 0.8 | 90 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | открыт |  | SS 35/10 kv SKhT | 2,5+1,6 | 0.695 | 1.655 | 0 | 0 | 1.655 | 0 | 1.68 | 0.025 | 0.025 | closed
| ПС 35/10 кВ Сошки | 4+4 | 8 | 0.8 | 0.2 | 80 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | открыт |  | ПС 35/10 кВ Сошки | 4+4 | 0.005 | 0.805 | 0.2 | 80 | 0.605 | 0 | 4.2 | 3.595 | 3.595 | открыт
| ПС 35/6 кВ Таволжанка | 4+4 | 8 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | открыт |  | SS 35/6 kv Tavolzhanka | 4+4 | 0.916 | 4.586 | 0 | 0 | 4.586 | 0 | 4.2 | -0.386 | -0.386 | closed
| ПС 35/10 кВ Трубетчино | 2,5+2,5 | 5 | 1.71 | 0 | 0 | 1.71 | 0 | 2.625 | 0.915 | 0.915 | * |  | ПС 35/10 кВ Трубетчино | 2,5+2,5 | 0.395 | 2.105 | 0 | 0 | 2.105 | 0 | 2.625 | 0.52 | 0.52 | открыт
| ПС 35/10 кВ Ратчино | 2,5+2,5 | 5 | 1.11 | 0.12 | 70 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | * |  | SS 35/10 kv Ratchino | 2,5+2,5 | 0.01 | 1.12 | 0.12 | 70 | 1 | 0 | 2.625 | 1.625 | 1.625 | *
| ПС 35/10 кВ Каликино | 3,2+3,2 | 6.4 | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | * |  | SS 35/10 kv Kalikino | 3,2+3,2 | 0.005 | 1.945 | 0.42 | 80 | 1.525 | 0 | 3.36 | 1.835 | 1.835 | *
| ПС 35/10 кВ Борисовка | 4+2,5 | 6.5 | 2.74 | 0 | 0 | 2.74 | 0 | 2.625 | -0.115 | -0.115 | закрыт |  | SS 35/10 kv Borisovka | 4+2,5 | 0.717 | 3.457 | 0 | 0 | 3.457 | 0 | 2.625 | -0.832 | -0.832 | closed
| ПС 35/10 кВ Введенка | 4+4 | 8 | 4 | 0.14 | 70 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | * |  | SS 35/10 kv Vvedenka | 4+4 | 1.418 | 5.418 | 0.14 | 70 | 5.278 | 0 | 4.2 | -1.078 | -1.078 | closed
| ПС 35/10 кВ Грязное | 4+4 | 8 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | * |  | SS 35/10 kv Gryaznoe | 4+4 | 0.585 | 1.745 | 0 | 0 | 1.745 | 0 | 4.2 | 2.455 | 2.455 | *
| ПС 35/10 кВ Борино | 4+4 | 8 | 4.24 | 1.2 | 90 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | * |  | SS 35/10 kv Borino | 6,3+6,3 | 0.1 | 4.34 | 1.2 | 90 | 3.14 | 0 | 6.615 | 3.475 | 3.475 | *
| ПС 35/10 кВ Частая Дубрава | 2,5+2,5 | 5 | 1.6 | 1.88 | 100 (45) | -0.28 | 0 | 2.625 | 2.905 | 2.905 | * |  | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 0.942 | 2.542 | 1.88 | 100 (45) | 0.662 | 0 | 2.625 | 1.963 | 1.963 | closed
| ПС 35/10 кВ Троицкая | 2,5+4 | 6.5 | 2.33 | 0.6 | 70 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | * |  | SS 35/10 kv Troitskaya | 2,5+4 | 0.423 | 2.753 | 0.6 | 70 | 2.153 | 0 | 2.625 | 0.472 | 0.472 | *
| ПС 35/6 кВ Вешаловка | 2,5+2,5 | 5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | * |  | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.028 | 0.898 | 0 | 0 | 0.898 | 0 | 2.625 | 1.727 | 1.727 | *
| ПС 35/10 кВ Пружинки | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | * |  | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.015 | 0.615 | 0 | 0 | 0.615 | 0 | 2.625 | 2.01 | 2.01 | *
| ПС 35/10 кВ Стебаево | 2,5+2,5 | 5 | 0.95 | 0.28 | 80 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | * |  | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.04 | 0.99 | 0.28 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | *
| ПС 35/10 кВ Хлебопродукты | 6,3+6,3 | 12.6 | 3.52 | 0.6 | 100 | 2.92 | 0 | 6.615 | 3.695 | 3.695 | * |  | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 0.35 | 4.11 | 0.6 | 100 | 3.51 | 0 | 6.615 | 3.105 | 3.105 | *
| ПС 35/10 кВ Сенцово | 10+10 | 20 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 | 5.3 | * |  | SS 35/10 kv Sentsovo | 10+10 | 1.8 | 9.08 | 0 | 0 | 9.08 | 0 | 10.5 | 1.42 | 1.42 | *
| ПС 35/10 кВ Мясокомбинат | 6,3+6,3 | 12.6 | 4.46 | 1.6 | 110 | 2.86 | 0 | 6.62 | 3.76 | 3.76 | * |  | SS 35/10 kv Meet processing factory | 6,3+6,3 | 2.143 | 6.773 | 1.6 | 110 | 5.173 | 0 | 6.62 | 1.447 | 1.447 | *
| ПС 35/6 кВ Птицефабрика | 4+4 | 8 | 1.93 | 0 | 0 | 1.93 | 0 | 4.2 | 2.27 | 2.27 | * |  | SS 35/6 kv Poultry plant | 4+4 | 0.007 | 1.937 | 0 | 0 | 1.937 | 0 | 4.2 | 2.263 | 2.263 | *
| ПС 35/6 кВ Водозабор | 10+10 | 20 | 0.43 | 0 | 0 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | * |  | SS 35/6 kv Water intake | 10+10 | 0.069 | 1.069 | 0 | 0 | 1.069 | 0 | 10.5 | 9.431 | 9.431 | *
| ПС 35/10 кВ Петровская | 2,5+4 | 6.5 | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | открыт |  | ПС 35/10 кВ Петровская | 2,5+4 |  | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | открыт
| ПС 35/10 кВ Лебедянка | 2,5+2,5 | 5 | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | открыт |  | ПС 35/10 кВ Лебедянка | 2,5+2,5 |  | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | открыт
| ПС 35/10 кВ Новочеркутино | 4+4 | 8 | 0.97 | 1.02 | 100 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | открыт |  | ПС 35/10 кВ Новочеркутино | 4+4 | 0.008 | 0.978 | 1.02 | 100 | -0.042 | 0 | 4.2 | 4.242 | 4.242 | открыт
| ПС 35/10 кВ Ивановка | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | открыт |  | ПС 35/10 кВ Ивановка | 2,5+2,5 | 0.05 | 1.11 | 0 | 0 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | открыт
| ПС 35/10 кВ Поддубровка | 2,5+2,5 | 5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | открыт |  | ПС 35/10 кВ Поддубровка | 2,5+2,5 | 0.037 | 1.007 | 0 | 0 | 1.007 | 0 | 2.625 | 1.618 | 1.618 | открыт
| ПС 35/10 кВ Плавица | 1,6+1,6 | 3.2 | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | открыт |  | ПС 35/10 кВ Плавица | 1,6+1,6 |  | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | открыт
| ПС 35/10 кВ Паршиновка | 1,6+2,5 | 4.1 | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | открыт |  | ПС 35/10 кВ Паршиновка | 1,6+2,5 |  | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | открыт
| ПС 35/10 кВ Талицкий Чамлык | 3,2+4 | 7.2 | 2.2 | 1.28 | 100 | 0.92 | 0 | 3.36 | 2.44 | 2.44 | открыт |  | ПС 35/10 кВ Талицкий Чамлык | 3,2+4 | 0.05 | 2.25 | 1.28 | 100 | 0.97 | 0 | 3.36 | 2.39 | 2.39 | открыт
| ПС 35/10 кВ Демшинка | 2,5+2,5 | 5 | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | открыт |  | ПС 35/10 кВ Демшинка | 2,5+2,5 |  | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | открыт
| ПС 35/10 кВ Березняговка | 1,6+1,6 | 3.2 | 0.62 | 0.46 | 80 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | открыт |  | ПС 35/10 кВ Березняговка | 1,6+1,6 | 0.011 | 0.631 | 0.46 | 80 | 0.171 | 0 | 1.68 | 1.509 | 1.509 | открыт
| ПС 35/10 кВ Дмитриевка | 2,5+2,5 | 5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | открыт |  | ПС 35/10 кВ Дмитриевка | 2,5+2,5 |  | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | открыт
| ПС 35/10 кВ Пашково | 2,5+2,5 | 5 | 1.89 | 0 | 0 | 1.89 | 0 | 2.625 | 0.735 | 0.735 | открыт |  | ПС 35/10 кВ Пашково | 2,5+2,5 | 0.02 | 1.91 | 0 | 0 | 1.91 | 0 | 2.625 | 0.715 | 0.715 | открыт
| ПС 35/10 кВ Московка | 1,6+1,6 | 3.2 | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | открыт |  | ПС 35/10 кВ Московка | 1,6+1,6 |  | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | открыт
| ПС 35/10 кВ Бочиновка | 4+4 | 8 | 3.14 | 1.18 | 90 | 1.96 | 0 | 4.2 | 2.24 | 2.24 | открыт |  | ПС 35/10 кВ Бочиновка | 4+4 | 0.028 | 3.168 | 1.18 | 90 | 1.988 | 0 | 4.2 | 2.212 | 2.212 | открыт
| ПС 35/10 кВ Федоровка | 2,5+2,5 | 5 | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | открыт |  | ПС 35/10 кВ Федоровка | 2,5+2,5 |  | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | открыт
| ПС 35/10 кВ Куликово | 2,5+2,5 | 5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | открыт |  | ПС 35/10 кВ Куликово | 2,5+2,5 |  | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | открыт
| ПС 35/10 кВ Конь-Колодезь | 2,5+2,5 | 5 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | * |  | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 1.276 | 2.516 | 0 | 0 | 2.516 | 0 | 2.625 | 0.109 | 0.109 | *
| ПС 35/10 кВ Дмитряшевка | 2,5+2,5 | 5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | * |  | SS 35/10 kv Dmitryashevka | 2,5+2,5 |  | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | *
| ПС 35/10 кВ Речная | 4+4 | 8 | 1.57 | 1.06 | 100 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | * |  | SS 35/10 kv Rechnaya | 4+4 | 0.017 | 1.587 | 1.06 | 100 | 0.527 | 0 | 4.2 | 3.673 | 3.673 | *
| ПС 35/10 кВ Негачевка | 2,5+2,5 | 5 | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | * |  | SS 35/10 kv Negachevka | 2,5+2,5 |  | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | *
| ПС 35/10 кВ Карамышево | 10+10 | 20 | 0.56 | 0.1 | 70 | 0.46 | 0 | 10.5 | 10.04 | 10.04 | открыт |  | ПС 35/10 кВ Карамышево | 10+10 | 0.036 | 0.596 | 0.1 | 70 | 0.496 | 0 | 10.5 | 10.004 | 10.004 | открыт
| ПС 35/10 кВ Тюшевка | 1,6+1,6 | 3.2 | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | * |  | SS 35/10 kv Tyushevka | 1,6+1,6 | 0.007 | 0.967 | 0.1 | 70 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | *
| ПС 35/10 кВ Сселки | 10+10 |  | 0 | [8 empty] | 2: SS 35/10 kv Sselki; 3: 10+10; 4: 6.153; 5: 6.153
Двух- и более трансформаторные ПС (на три уровня напряжения) | [12 empty] | 1: Two- and more transformer substations (for three voltage levels)
| ПС 110/35/10 кВ Тербуны-110 | 10+10 | 20 | 9.26 | 3.5 |  | 5.76 | 0 | 10.5 | 4.74 | 4.71 | открыт |  | ПС 110/35/10 кВ Тербуны-110 | 10+10 | 1.502 | 10.762 | 3.5 |  | 7.262 | 0 | 10.5 | 3.238 | 3.238 | открыт
| Ном. Мощность СН, МВА | 10+10 |  | 3.47 | 3.5 | 30 | -0.03 | 0 | 10.5 | 10.53 |  |  |  | Ном. Мощность СН, МВА | 10+10 | 0.526 | 3.996 | 3.5 | 30 | 0.496 | 0 | 10.5 | 10.004
| Ном. мощность НН, МВА | 10+10 |  | 5.79 | 0 | 0 | 5.79 | 0 | 10.5 | 4.71 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.976 | 6.766 | 0 | 0 | 6.766 | 0 | 10.5 | 3.734
| ПС 110/35/10 кВ Долгоруково | 6,3+10 | 16.3 | 6.98 | 4 |  | 2.98 | 0 | 6.615 | 3.635 | 3.525 | открыт |  | ПС 110/35/10 кВ Долгоруково | 6,3+10 | #REF! | #REF! | 4 |  | #REF! | 0 | 6.615 | #REF! | #REF! | открыт
| Ном. Мощность СН, МВА | 6,3+10 |  | 3.89 | 4 | 45 | -0.11 | 0 | 6.615 | 6.725 |  |  |  | Ном. Мощность СН, МВА | 6,3+10 | #REF! | #REF! | 4 | 45 | #REF! | 0 | 6.615 | #REF!
| Ном. мощность НН, МВА | 6,3+10 |  | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525 |  |  |  | Ном. мощность НН, МВА | 6,3+10 | 0 | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525
| ПС 110/35/10 кВ Волово | 10+10 | 20 | 2.07 | 0.89 |  | 1.18 | 0 | 10.5 | 9.32 | 9.32 | открыт |  | ПС 110/35/10 кВ Волово | 10+10 | 0.14 | 2.21 | 0.89 |  | 1.32 | 0 | 10.5 | 9.18 | 9.18 | открыт
| Ном. Мощность СН, МВА | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5
| Ном. мощность НН, МВА | 10+10 |  | 2.07 | 0.89 | 60 | 1.18 | 0 | 10.5 | 9.32 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.14 | 2.21 | 0.89 | 60 | 1.32 | 0 | 10.5 | 9.18
| ПС 110/35/10 кВ Измалково | 10+10 | 20 | 5 | 1.2 |  | 3.8 | 0 | 10.5 | 6.7 | 6.7 | открыт |  | ПС 110/35/10 кВ Измалково | 10+10 | #REF! | #REF! | 1.2 |  | #REF! | 0 | 10.5 | #REF! | #REF! | открыт
| Ном. Мощность СН, МВА | 10+10 |  | 2.82 | 1.2 | 30 | 1.62 | 0 | 10.5 | 8.88 |  |  |  | Ном. Мощность СН, МВА | 10+10 | #REF! | #REF! | 1.2 | 30 | #REF! | 0 | 10.5 | #REF!
| Ном. мощность НН, МВА | 10+10 |  | 2.18 | 0 | 0 | 2.18 | 0 | 10.5 | 8.32 |  |  |  | Ном. мощность НН, МВА | 10+10 | 2.545 | 4.725 | 0 | 0 | 4.725 | 0 | 10.5 | 5.775
| ПС 110/35/10 кВ Гороховская | 16+16 | 32 | 10.52 | 7.2 |  | 3.32 | 0 | 16.8 | 13.48 | 13.48 | открыт |  | ПС 110/35/10 кВ Гороховская | 16+16 | 2.875 | 13.395 | 7.2 |  | 6.195 | 0 | 16.8 | 10.605 | 10.605 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 6.94 | 6 | 30 | 0.94 | 0 | 16.8 | 15.86 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 1.863 | 8.803 | 6 | 30 | 2.803 | 0 | 16.8 | 13.997
| Ном. мощность НН, МВА | 16+16 |  | 3.58 | 1.2 | 120 | 2.38 | 0 | 16.8 | 14.42 |  |  |  | Ном. мощность НН, МВА | 16+16 | 1.012 | 4.592 | 1.2 | 120 | 3.392 | 0 | 16.8 | 13.408
| ПС 110/35/10 кВ Донская | 10+10 | 20 | 7.1 | 4.89 |  | 2.21 | 0 | 10.5 | 8.29 | 8.25 | открыт |  | ПС 110/35/10 кВ Донская | 10+10 | 0.067 | 7.167 | 4.89 |  | 2.277 | 0 | 10.5 | 8.223 | 8.223 | открыт
| Ном. Мощность СН, МВА | 10+10 |  | 3.96 | 4 | 30 | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Ном. Мощность СН, МВА | 10+10 | 0.06 | 4.02 | 4 | 30 | 0.02 | 0 | 10.5 | 10.48
| Ном. мощность НН, МВА | 10+10 |  | 3.14 | 0.89 | 120 | 2.25 | 0 | 10.5 | 8.25 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.007 | 3.147 | 0.89 | 120 | 2.257 | 0 | 10.5 | 8.243
| ПС 110/35/10 кВ Лебедянь | 16+16 | 32 | 15.92 | 9 |  | 6.92 | 0 | 16.8 | 9.88 | 9.88 | открыт |  | ПС 110/35/10 кВ Лебедянь | 16+16 | 0.636 | 16.556 | 9 |  | 7.556 | 0 | 16.8 | 9.244 | 9.244 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 7.2 | 6 | 60 | 1.2 | 0 | 16.8 | 15.6 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.021 | 7.221 | 6 | 60 | 1.221 | 0 | 16.8 | 15.579
| Ном. мощность НН, МВА | 16+16 |  | 8.72 | 3 | 120 | 5.72 | 0 | 16.8 | 11.08 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.615 | 9.335 | 3 | 120 | 6.335 | 0 | 16.8 | 10.465
| ПС 110/35/10 кВ Чаплыгин-новая | 16+16 | 32 | 7.58 | 4.5 |  | 3.08 | 0 | 16.8 | 13.72 | 13.72 | открыт |  | ПС 110/35/10 кВ Чаплыгин-новая | 16+16 | 0.015 | 7.595 | 4.5 |  | 3.095 | 0 | 16.8 | 13.705 | 13.705 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 3.4 | 2.5 | 20 | 0.9 | 0 | 16.8 | 15.9 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.008 | 3.408 | 2.5 | 20 | 0.908 | 0 | 16.8 | 15.892
| Ном. мощность НН, МВА | 16+16 |  | 4.18 | 2 | 100 | 2.18 | 0 | 16.8 | 14.62 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.007 | 4.187 | 2 | 100 | 2.187 | 0 | 16.8 | 14.613
| ПС 110/35/10 кВ Компрессорная | 16+16 | 32 | 4.81 | 3.2 |  | 1.61 | 0 | 16.8 | 15.19 | 15.19 | открыт |  | ПС 110/35/10 кВ Компрессорная | 16+16 | #REF! | #REF! | 3.2 |  | #REF! | 0 | 16.8 | #REF! | #REF! | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 2.51 | 2.2 | 20 | 0.31 | 0 | 16.8 | 16.49 |  |  |  | Ном. Мощность СН, МВА | 16+16 | #REF! | #REF! | 2.2 | 20 | #REF! | 0 | 16.8 | #REF!
| Ном. мощность НН, МВА | 16+16 |  | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0 | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5
| ПС 110/35/10 кВ Россия | 16+16 | 32 | 5.6 | 3.8 |  | 1.8 | 0 | 16.8 | 15 | 15 | открыт |  | ПС 110/35/10 кВ Россия | 16+16 | 0.026 | 5.626 | 3.8 |  | 1.826 | 0 | 16.8 | 14.974 | 14.974 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 4.67 | 3 | 60 | 1.67 | 0 | 16.8 | 15.13 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.026 | 4.696 | 3 | 60 | 1.696 | 0 | 16.8 | 15.104
| Ном. мощность НН, МВА | 16+16 |  | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0 | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67
| ПС 110/35/10 кВ Березовка | 16+10 | 26 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | открыт |  | ПС 110/35/10 кВ Березовка | 16+10 | 0 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | открыт
| Ном. Мощность СН, МВА | 16+10 |  | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13 |  |  |  | Ном. Мощность СН, МВА | 16+10 | 0 | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13
| Ном. мощность НН, МВА | 16+10 |  | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29 |  |  |  | Ном. мощность НН, МВА | 16+10 | 0 | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29
| ПС 110/35/10 кВ Астапово | 16+16 | 32 | 4.62 | 3 |  | 1.62 | 0 | 16.8 | 15.18 | 15.18 | открыт |  | ПС 110/35/10 кВ Астапово | 16+16 | 0.52 | 5.14 | 3 |  | 2.14 | 0 | 16.8 | 14.66 | 14.66 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 2.74 | 2 | 60 | 0.74 | 0 | 16.8 | 16.06 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.02 | 2.76 | 2 | 60 | 0.76 | 0 | 16.8 | 16.04
| Ном. мощность НН, МВА | 16+16 |  | 1.88 | 1 | 60 | 0.88 | 0 | 16.8 | 15.92 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.5 | 2.38 | 1 | 60 | 1.38 | 0 | 16.8 | 15.42
| ПС 110/35/10 кВ Химическая | 16+16 | 32 | 8.46 | 5.5 |  | 2.96 | 0 | 16.8 | 13.84 | 13.84 | открыт |  | ПС 110/35/10 кВ Химическая | 16+16 | 0.625 | 9.085 | 5.5 |  | 3.585 | 0 | 16.8 | 13.215 | 13.215 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 6.34 | 4.5 | 60 | 1.84 | 0 | 16.8 | 14.96 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.61 | 6.95 | 4.5 | 60 | 2.45 | 0 | 16.8 | 14.35
| Ном. мощность НН, МВА | 16+16 |  | 2.12 | 1 | 60 | 1.12 | 0 | 16.8 | 15.68 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.015 | 2.135 | 1 | 60 | 1.135 | 0 | 16.8 | 15.665
| ПС 110/35/6 кВ Бугор | 15+15+25 | 55 | 36.17 | 0.5 |  | 35.67 | 1 | 31.5 | -5.17 | -5.17 | закрыт |  | SS 110/35/6 kv Bugor | 15+15+25 | 11.583 | 47.753 | 0.5 |  | 47.253 | 1 | 31.5 | -16.753 | -16.753 | closed
| Ном. Мощность СН, МВА | 15+15+25 |  | 9.37 | 0 | 0 | 9.37 | 0 | 31.5 | 22.13 |  |  |  | Nom. capacity MV, МVА | 15+15+25 | 10.4 | 19.77 | 0 | 0 | 19.77 | 0 | 31.5 | 11.73
| Ном. мощность НН, МВА | 15+15+25 |  | 26.8 | 0.5 | 40 | 26.3 | 1 | 31.5 | 4.2 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 1.183 | 27.983 | 0.5 | 40 | 27.483 | 1 | 31.5 | 3.017
| ПС 110/35/6 кВ Цементная | 63+32+20 | 115 | 47.33 | 0 |  | 47.33 | 0 | 54.6 | 7.27 | -6.45 | закрыт |  | SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 1.3755 | 48.7055 | 0 |  | 48.7055 | 0 | 54.6 | 5.8945 | -7.5755 | closed
| Ном. Мощность СН, МВА | 63+20 |  | 27.45 | 0 | 0 | 27.45 | 0 | 21 | -6.45 |  |  |  | Nom. capacity MV, МVА | 63+20 | 1.1255 | 28.5755 | 0 | 0 | 28.5755 | 0 | 21 | -7.5755
| Ном. мощность НН, МВА | 63+32+20 |  | 19.88 | 0 | 30 | 19.88 | 0 | 54.6 | 34.72 |  |  |  | Nom. capacity LV, МVА | 63+32+20 | 0.25 | 20.13 | 0 | 30 | 20.13 | 0 | 54.6 | 34.47
| ПС 110/35/10/60 кВ Гидрооборудование | 25+25+31,5 | 81.5 | 11.03 | 2.5 |  | 8.53 | 0 | 52.5 | 43.97 | -3.6 | закрыт |  | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 1.551 | 12.581 | 2.5 |  | 10.081 | 0 | 52.5 | 42.419 | -4.352 | closed
| Ном. Мощность СН, МВА | 31.5 |  | 5.6 | 2 | 10 | 3.6 | 0 | 2 | -3.6 |  |  |  | Nom. capacity MV, МVА | 31.5 | 0.752 | 6.352 | 2 | 10 | 4.352 | 0 | 2 | -4.352
| Ном. мощность НН, МВА | 25+25+31,5 |  | 5.43 | 0.5 | 80 | 4.93 | 0 | 52.5 | 47.57 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.799 | 6.229 | 0.5 | 80 | 5.729 | 0 | 26.25 | 20.521
| ПС 110/35/10 кВ Усмань | 16+16 | 32 | 15.28 | 6.5 |  | 8.78 | 0 | 16.8 | 8.02 | 7.93 | открыт |  | ПС 110/35/10 кВ Усмань | 16+16 | 0.232 | 15.512 | 6.5 |  | 9.012 | 0 | 16.8 | 7.788 | 7.746 | открыт
| Ном. Мощность СН, МВА | 16+16 |  | 4.91 | 5 | 20 | -0.09 | 0 | 16.8 | 16.89 |  |  |  | Ном. Мощность СН, МВА | 16+16 | 0.048 | 4.958 | 5 | 20 | -0.042 | 0 | 16.8 | 16.842
| Ном. мощность НН, МВА | 16+16 |  | 10.37 | 1.5 | 100 | 8.87 | 0 | 16.8 | 7.93 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.184 | 10.554 | 1.5 | 100 | 9.054 | 0 | 16.8 | 7.746
| ПС 110/35/10 кВ Аксай | 10+10 | 20 | 8.32 | 1.12 |  | 7.2 | 0 | 10.5 | 3.3 | 3.3 | открыт |  | ПС 110/35/10 кВ Аксай | 10+10 | 0.0435 | 8.3635 | 1.12 |  | 7.2435 | 0 | 10.5 | 3.2565 | 3.2565 | открыт
| Ном. Мощность СН, МВА | 10+10 |  | 5.82 | 0.5 | 20 | 5.32 | 0 | 10.5 | 5.18 |  |  |  | Ном. Мощность СН, МВА | 10+10 | 0.0385 | 5.8585 | 0.5 | 20 | 5.3585 | 0 | 10.5 | 5.1415
| Ном. мощность НН, МВА | 10+10 |  | 2.5 | 0.62 | 80 | 1.88 | 0 | 10.5 | 8.62 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.005 | 2.505 | 0.62 | 80 | 1.885 | 0 | 10.5 | 8.615
| ПС 110/35/10 кВ Никольская | 6,3+6,3 | 12.6 | 4.91 | 3.34 |  | 1.57 | 0 | 6.615 | 5.045 | 5.045 | открыт |  | ПС 110/35/10 кВ Никольская | 6,3+6,3 | 0.0475 | 4.9575 | 3.34 |  | 1.6175 | 0 | 6.615 | 4.9975 | 4.9975 | открыт
| Ном. Мощность СН, МВА | 6,3+6,3 |  | 3.55 | 3 | 10 | 0.55 | 0 | 6.615 | 6.065 |  |  |  | Ном. Мощность СН, МВА | 6,3+6,3 | 0.0425 | 3.5925 | 3 | 10 | 0.5925 | 0 | 6.615 | 6.0225
| Ном. мощность НН, МВА | 6,3+6,3 |  | 1.36 | 0.34 | 80 | 1.02 | 0 | 6.615 | 5.595 |  |  |  | Ном. мощность НН, МВА | 6,3+6,3 | 0.005 | 1.365 | 0.34 | 80 | 1.025 | 0 | 6.615 | 5.59
| ПС 110/35/10 кВ Хворостянка | 10+16 | 26 | 12.41 | 6.72 |  | 5.69 | 0 | 10.5 | 4.81 | 4.81 | открыт |  | ПС 110/35/10 кВ Хворостянка | 10+16 | 0.7935 | 13.2035 | 6.72 |  | 6.4835 | 0 | 10.5 | 4.0165 | 4.0165 | открыт
| Ном. Мощность СН, МВА | 10+16 |  | 9.32 | 6.5 | 20 | 2.82 | 0 | 10.5 | 7.68 |  |  |  | Ном. Мощность СН, МВА | 10+16 | 0.7785 | 10.0985 | 6.5 | 20 | 3.5985 | 0 | 10.5 | 6.9015
| Ном. мощность НН, МВА | 10+16 |  | 3.09 | 0.22 | 80 | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Ном. мощность НН, МВА | 10+16 | 0.015 | 3.105 | 0.22 | 80 | 2.885 | 0 | 10.5 | 7.615
| ПС 110/35/10 кВ Добринка | 16+10 | 26 | 6.89 | 5.68 |  | 1.21 | 0 | 10.5 | 9.29 | 8.88 | открыт |  | ПС 110/35/10 кВ Добринка | 16+10 | 0.154 | 7.044 | 5.68 |  | 1.364 | 0 | 10.5 | 9.136 | 8.776 | открыт
| Ном. Мощность СН, МВА | 16+10 |  | 3.59 | 4 | 80 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Ном. Мощность СН, МВА | 16+10 | 0.05 | 3.64 | 4 | 80 | -0.36 | 0 | 10.5 | 10.86
| Ном. мощность НН, МВА | 16+10 |  | 3.3 | 1.68 | 100 | 1.62 | 0 | 10.5 | 8.88 |  |  |  | Ном. мощность НН, МВА | 16+10 | 0.104 | 3.404 | 1.68 | 100 | 1.724 | 0 | 10.5 | 8.776
| ПС 110/35/10 кВ Верхняя Матренка | 6,3+6,3 | 12.6 | 1.39 | 0.4 |  | 0.99 | 0 | 6.615 | 5.625 | 5.625 | открыт |  | ПС 110/35/10 кВ Верхняя Матренка | 6,3+6,3 | 0.01 | 1.4 | 0.4 |  | 1 | 0 | 6.615 | 5.615 | 5.615 | открыт
| Ном. Мощность СН, МВА | 6,3+6,3 |  | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995 |  |  |  | Ном. Мощность СН, МВА | 6,3+6,3 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995
| Ном. мощность НН, МВА | 6,3+6,3 |  | 0.77 | 0.4 | 90 | 0.37 | 0 | 6.615 | 6.245 |  |  |  | Ном. мощность НН, МВА | 6,3+6,3 | 0.01 | 0.78 | 0.4 | 90 | 0.38 | 0 | 6.615 | 6.235
| ПС 110/35/10 кВ Казинка | 16+16 | 32 | 15.81 | 0 |  | 15.81 | 0 | 16.8 | 0.99 | 0.99 | открыт |  | SS 110/35/10 kv Kazinka | 16+16 | 2.438 | 18.248 | 0 |  | 18.248 | 0 | 16.8 | -1.448 | -1.448 | closed
| Ном. Мощность СН, МВА | 16+16 |  | 10.36 | 0 | 0 | 10.36 | 0 | 16.8 | 6.44 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.611 | 11.971 | 0 | 0 | 11.971 | 0 | 16.8 | 4.829
| Ном. мощность НН, МВА | 16+16 |  | 5.45 | 0 | 0 | 5.45 | 0 | 16.8 | 11.35 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.827 | 6.277 | 0 | 0 | 6.277 | 0 | 16.8 | 10.523
| ПС 110/35/10 кВ Доброе | 16+16 | 32 | 11.4 | 3 |  | 8.4 | 0 | 16.8 | 8.4 | 8.4 | * |  | SS 110/35/10 kv Dobroe | 16+16 | 1.139 | 12.539 | 3 |  | 9.539 | 0 | 16.8 | 7.261 | 7.261 | *
| Ном. Мощность СН, МВА | 16+16 |  | 6.22 | 3 | 20 | 3.22 | 0 | 16.8 | 13.58 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.732 | 6.952 | 3 | 20 | 3.952 | 0 | 16.8 | 12.848
| Ном. мощность НН, МВА | 16+16 |  | 5.18 | 0 | 0 | 5.18 | 0 | 16.8 | 11.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.407 | 5.587 | 0 | 0 | 5.587 | 0 | 16.8 | 11.213
| ПС 110/35/6 кВ Новая Деревня | 10+6,3 | 16.3 | 7.64 | 5 |  | 2.64 | 0 | 6.615 | 3.975 | 3.975 | * |  | SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 0.3255 | 7.9655 | 5 |  | 2.9655 | 0 | 6.615 | 3.6495 | 3.6495 | *
| Ном. Мощность СН, МВА | 10+6,3 |  | 5.4 | 5 | 10 | 0.4 | 0 | 6.615 | 6.215 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.2105 | 5.6105 | 5 | 10 | 0.6105 | 0 | 6.615 | 6.0045
| Ном. мощность НН, МВА | 10+6,3 |  | 2.24 | 0 | 0 | 2.24 | 0 | 6.615 | 4.375 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.115 | 2.355 | 0 | 0 | 2.355 | 0 | 6.615 | 4.26
| ПС 110/35/6 кВ Вербилово | 10+6,3 | 16.3 | 3.96 | 0 |  | 3.96 | 0 | 6.62 | 2.66 | 2.66 | * |  | SS 110/35/6 kv Verbilovo | 10+6,3 | 0.698 | 4.658 | 0 |  | 4.658 | 0 | 6.62 | 1.962 | 1.962 | *
| Ном. Мощность СН, МВА | 10+6,3 |  | 2.76 | 0 | 0 | 2.76 | 0 | 6.62 | 3.86 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.625 | 3.385 | 0 | 0 | 3.385 | 0 | 6.62 | 3.235
| Ном. мощность НН, МВА | 10+6,3 |  | 1.2 | 0 | 0 | 1.2 | 0 | 6.62 | 5.42 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.073 | 1.273 | 0 | 0 | 1.273 | 0 | 6.62 | 5.347
| ПС 110/35/10 кВ Хлевное | 16+16 | 32 | 10.04 | 0 |  | 10.04 | 0 | 16.8 | 6.76 | 6.76 | * |  | SS 110/35/10 kv Khlevnoe | 16+16 | 4.93 | 14.97 | 0 |  | 14.97 | 0 | 16.8 | 1.83 | 1.83 | *
| Ном. Мощность СН, МВА | 16+16 |  | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.377 | 7.237 | 0 | 0 | 7.237 | 0 | 16.8 | 9.563
| Ном. мощность НН, МВА | 16+16 |  | 4.18 | 0 | 0 | 4.18 | 0 | 16.8 | 12.62 |  |  |  | Nom. capacity LV, МVА | 16+16 | 3.553 | 7.733 | 0 | 0 | 7.733 | 0 | 16.8 | 9.067
| ПС 110/35/10 кВ Набережное | 6,3+10 | 16.3 | 2.46 | 4.5 |  | -2.04 | 0 | 6.62 | 8.66 | 5.45 | открыт |  | ПС 110/35/10 кВ Набережное | 6,3+10 | 1.07 | 3.53 | 4.5 |  | -0.97 | 0 | 6.62 | 7.59 | 5.45 | открыт
| Ном. Мощность СН, МВА | 6,3+10 |  | 1.29 | 4.5 | 10 | -3.21 | 0 | 6.62 | 9.83 |  |  |  | Ном. Мощность СН, МВА | 6,3+10 | 1.07 | 2.36 | 4.5 | 10 | -2.14 | 0 | 6.62 | 8.76
| Ном. мощность НН, МВА | 6,3+10 |  | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45 |  |  |  | Ном. мощность НН, МВА | 6,3+10 | 0 | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45
| ПС 110/35/10 кВ Чаплыгин | 7,5+6,3 | 13.8 | 5.54 | 4.5 |  | 1.04 | 0 | 6.62 | 5.58 | 5.58 | открыт |  | ПС 110/35/10 кВ Чаплыгин | 7,5+6,3 | 0.005 | 5.545 | 4.5 |  | 1.045 | 0 | 6.62 | 5.575 | 5.575 | открыт
| Ном. Мощность СН, МВА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62 |  |  |  | Ном. Мощность СН, МВА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62
| Ном. мощность НН, МВА | 7,5+6,3 |  | 5.54 | 4.5 | 30 | 1.04 | 0 | 6.62 | 5.58 |  |  |  | Ном. мощность НН, МВА | 7,5+6,3 | 0.005 | 5.545 | 4.5 | 30 | 1.045 | 0 | 6.62 | 5.575
| ПС 110/35/10 кВ Троекурово | 10+6,3 | 16.3 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | открыт |  | ПС 110/35/10 кВ Троекурово | 10+6,3 | 0 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | открыт
| Ном. Мощность СН, МВА | 10+6,3 |  | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32 |  |  |  | Ном. Мощность СН, МВА | 10+6,3 | 0 | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32
| Ном. мощность НН, МВА | 10+6,3 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67 |  |  |  | Ном. мощность НН, МВА | 10+6,3 | 0 | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67
| дефицит | [9 empty] | -37.1994 |  | 2: deficit; Мин. 12: -66.3569
* Ограничение на присоединяемую мощность по режиму работы сети 110, 220 кВ (по данным Липецкого РДУ)
Note on E27: krutko_eg: нагрузка 1 МВт, введена в сентябре
Note on E170: krutko_eg: введена в сентябре, потебители неподключены
Note on S27: krutko_eg: нагрузка 1 МВт, введена в сентябре
Note on S170: krutko_eg: введена в сентябре, потебители неподключены