## ЦП Текущий дефицит, табл.1
table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA
|  |  | MVA | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.81 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.49 | 1.08 | open
| Nom. capacity MV, MVA | 6.3 | 1.22 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.08
| Nom. capacity MV, MVA | 6.3 | 0.59 | 4 | 1 day and night | 4 | 0 | 4 | 3.41
2 | SS 110/10 Beketovo | 1*6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | open
3 | SS 110/35/10 Besedino | 1*6,3 | 3.34 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.46 | 0.52 | open
| Nom. capacity MV, MVA | 6.3 | 0.56 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.94
| Nom. capacity LV, MVA | 6.3 | 2.78 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.52
4 | SS 110/10 Voskhod | 1*10,0 | 0.6 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.9 | 1.9 | open
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.91 | 6 | 1 day and night | 6 | 0 | 6 | 5.09 | 1.39 | open
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.91 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.39
6 | SS 110/35/10 Zhukovka | 1*10,0 | 1.22 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.94 | 0.47 | open
| Nom. capacity MV, MVA | 10 | 1.03 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.47
| Nom. capacity LV, MVA | 10 | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47
7 | SS 110/10 Zabelye | 1*2,5 | 0.3 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.85 | 1.85 | open
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | open
9 | SS 110/35/10 Lachinovo | 1*10,0 | 1.4 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.73 | 1.13 | open
| Nom. capacity MV, MVA | 10 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6
| Nom. capacity LV, MVA | 10 | 0.4 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 1.13
10 | SS 110/10 Malaya Loknya | 1*10,0 | 1.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.2 | 0.2 | open
11 | SS 110/35/10 Maritsa | 1*2,5 | 1.65 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.27 | 0.27 | open
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.55 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.34 | 2.04 | open
| Nom. capacity MV, MVA | 6.3 | 0.44 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.3
| Nom. capacity LV, MVA | 6.3 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.03 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.37 | 1.37 | open
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 6.46 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | 0.18 | 0.18 | open
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.43 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 5.07 | 0.64 | open
| Nom. capacity MV, MVA | 10 | 1.97 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 4.43
| Nom. capacity LV, MVA | 10 | 0.46 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.64
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.53 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.27 | 0.27 | open
17 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.45 | 0.45 | open
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | open
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.24 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.19 | 1.19 | open
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.56 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.78 | 0.78 | open
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.79 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.17 | 0.17 | open
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.76 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.07 | 2.07 | open
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.36 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.28 | 0.28 | open
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.46 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.97 | 0.97 | open
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.28 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.87 | 1.87 | open
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.5 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.26 | 1.26 | open
27 | SS 35/10 Biryukovka | 1х1,6 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.26 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.41 | 0.41 | open
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
30 | SS 35/10 Budki | 1 х 1,0 | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | open
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.66 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.94 | 0.94 | open
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.22 | 1 | 1 day and night | 1 | 0 | 1 | 0.78 | 0.78 | open
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | open
34 | SS 35/10 Bykovo | 1 х 4,0 | 0.89 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.54 | 0.54 | open
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | open
36 | SS 35/10 Vanino | 1 х 2,5 | 0.24 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.56 | 0.56 | open
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.6 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.45 | 0.45 | open
38 | SS 35/10 Water storage | 1 х 4,0 | 1.76 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | 0.96 | 0.96 | open
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | open
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.72 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.18 | 0.18 | open
41 | SS 35/10 Voronok | 1 х 4,0 | 0.82 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.28 | 1.28 | open
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.45 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.7 | 1.7 | open
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.59 | 1.59 | open
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.21 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.29 | 1.29 | open
45 | SS 35/10 Glazovo | 1 х 2,5 | 1.26 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.24 | 0.24 | open
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.53 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.87 | 0.87 | open
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.3 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.4 | 0.4 | open
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.57 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.19 | 0.19 | open
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.5 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.6 | 0.6 | open
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | open
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.96 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.47 | 0.47 | open
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.61 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.24 | 2.24 | open
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.26 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.68 | 0.68 | open
54 | SS 35/10 Daryino | 1 х 2,5 | 0.4 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4 | 1.4 | open
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.61 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.19 | 0.19 | open
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.33 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.74 | 0.74 | open
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.3 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.55 | 0.55 | open
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.36 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.79 | 1.79 | open
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.49 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.35 | 0.35 | open
60 | SS 35/10 Znamenka | 1 х 1,8 | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | open
61 | SS 35/10 Iskra | 1 х 2,5 | 0.2 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.38 | 0.38 | open
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.41 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.39 | 0.39 | open
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.13 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.67 | 1.67 | open
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.31 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33 | 0.33 | open
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.28 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.46 | 0.46 | open
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.64 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.89 | 0.89 | open
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | open
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.55 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.87 | 0.87 | open
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.55 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.21 | 0.21 | open
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | open
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.64 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.19 | 0.19 | open
72 | SS 35/10 Lobazovka | 1 х 2,5 | 1.06 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.03 | 0.03 | open
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.58 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.71 | 0.71 | open
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.32 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.83 | 0.83 | open
75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.96 | 0.96 | open
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | open
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.76 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.52 | 0.52 | open
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.3 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.89 | 0.89 | open
79 | SS 35/10 Markovo | 1 х 2,5 | 0.68 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.12 | 0.12 | open
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.23 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.1 | 1.1 | open
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.99 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.16 | 1.16 | open
82 | SS 35/10 Mokva | 1 х 4,0 | 0.56 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.59 | 1.59 | open
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | open
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | open
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | open
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | open
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 1.1 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.05 | 1.05 | open
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.04 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.36 | 1.36 | open
89 | SS 35/10 Niva | 1 х 2,5 | 0.4 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.16 | 1.16 | open
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.5 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.47 | 0.47 | open
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.49 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.15 | 0.15 | open
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 1.46 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 1.51 | 1.51 | open
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.6 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.72 | 1.72 | open
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | open
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | open
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | open
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.19 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.96 | 1.96 | open
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.35 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8 | 1.8 | open
100 | SS 35/10 Pristen | 1 х 4,0 | 2.2 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.1 | 1.1 | open
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.74 | 0.74 | open
102 | SS 35/10 Reut | 1 х 2,5 | 0.44 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.66 | 0.66 | open
103 | SS 35/10 Rovenka | 1 х 1,6 | 1.16 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.44 | 0.44 | open
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.18 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.52 | 0.52 | open
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.38 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.92 | 1.92 | open
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.4 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.91 | 0.91 | open
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.19 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.24 | 1.24 | open
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.42 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.52 | 0.52 | open
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.53 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.62 | 0.62 | open
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | open
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.3 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.4 | 2.4 | open
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | open
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.81 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.95 | 0.95 | open
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.28 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.82 | 0.82 | open
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.35 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.95 | 0.95 | open
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.6 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.74 | 0.74 | open
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.54 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.17 | 0.17 | open
119 | SS 35/10 Telmana | 1 х 2,5 | 0.41 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.74 | 0.74 | open
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | open
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.07 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.63 | 0.63 | open
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.18 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.54 | 1.54 | open
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.34 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.76 | 0.76 | open
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | open
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | open
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.16 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.27 | 1.27 | open
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.58 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.89 | 0.89 | open
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | open
129 | SS 35/10 Elevator | 1х6,3 | 0.21 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.39 | 0.39 | open
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.24 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.4 | 0.4 | open
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.67 | 1.67 | open
Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | open
2 | SS 110/10 ARZ | 6,3+10,0 | 1.78 | 0.9 | 45 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | open
3 | SS 110/35/10 Atomgrad | 2*25 | 11.72 | 20.2 | 120 | -8.48 | 0 | 26.25 | 34.73 | 27.68 | open
| Nom. capacity MV, MVA | 25 | 3.55 | 10.6 | 120 | -7.05 | 0 | 26.25 | 33.3
| Nom. capacity lV, MVA | 25 | 8.17 | 9.6 | 120 | -1.43 | 0 | 26.25 | 27.68
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.83 | 0.6 | 120 | 0.23 | 0 | 6.615 | 6.385 | 6.385 | open
5 | SS 110/35/10 Basovo | 5,6+10,0 | 1.32 | 6.19 | 15 | -4.87 | 0 | 5.88 | 10.75 | 5.34 | open
| Nom. capacity MV, MVA | 5,6+10,0 | 0.59 | 6 |  | -5.41 | 0 | 5.88 | 11.29
| Nom. capacity LV, MVA | 5,6+10,0 | 0.73 | 0.19 | 120 | 0.54 | 0 | 5.88 | 5.34
6 | SS 110/35/10 Belaya | 2*16,0 | 7.1 | 12 | 120 | -4.9 | 0 | 16.8 | 21.7 | 13.6 | open
| Nom. capacity MV, MVA | 16 | 3.2 | 0 |  | 3.2 | 0 | 16.8 | 13.6
| Nom. capacity LV, MVA | 16 | 3.9 | 12 | 120 | -8.1 | 0 | 16.8 | 24.9
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.6 | 1.3 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.015 | open
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015
| Nom. capacity LV, MVA | 6.3 | 1 | 1.3 | 120 | -0.3 | 0 | 6.615 | 6.915
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.57 | 1.17 | 45 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | open
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 41.48 | 16.8 | 0 | 24.68 | 0 | 84.525 | 59.845 | 58.045 | open
| Nom. capacity MV, MVA | 40,0+2*40,5 | 15 | 16.8 | 0 | -1.8 | 0 | 84.525 | 86.325
| Nom. capacity MV, MVA | 40,0+2*40,5 | 26.48 | 0 | 0 | 26.48 | 0 | 84.525 | 58.045
10 | SS 110/10 Vysokaya* | 2*16,0 | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | closed
11 | SS 110/35/10 Glushkovo | 2*10,0 | 6.23 | 8.04 | 120 | -1.81 | 0 | 10.5 | 12.31 | 8.67 | open
| Nom. capacity MV, MVA | 10 | 2.96 | 6.6 | 120 | -3.64 | 0 | 10.5 | 14.14
| Nom. capacity LV, MVA | 10 | 3.27 | 1.44 | 80 | 1.83 | 0 | 10.5 | 8.67
12 | SS 110/10 Gorodskaya | 2*25,0 | 12.72 | 0 | 0 | 12.72 | 0 | 26.25 | 13.53 | 13.53 | open
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 8 | 6.52 | 120 | 1.48 | 0 | 10.5 | 9.02 | 7.61 | open
| Nom. capacity MV, MVA | 10+16,0 | 4.65 | 6.06 |  | -1.41 | 0 | 10.5 | 11.91
| Nom. capacity LV, MVA | 10+16,0 | 3.35 | 0.46 | 120 | 2.89 | 0 | 10.5 | 7.61
14 | SS 110/35/10 Dmitriev | 2*10,0 | 5.94 | 10.4 | 120 | -4.46 | 0 | 10.5 | 14.96 | 9.97 | open
| Nom. capacity MV, MVA | 10 | 2.41 | 7.4 |  | -4.99 | 0 | 10.5 | 15.49
| Nom. capacity LV, MVA | 10 | 3.53 | 3 | 80 | 0.53 | 0 | 10.5 | 9.97
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.9 | 0.5 | 120 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | open
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 7.52 | 22.1 | 80 | -14.58 | 0 | 26.25 | 40.83 | 25.21 | open
| Nom. capacity MV, MVA | 25 | 3.18 | 18.8 |  | -15.62 | 0 | 26.25 | 41.87
| Nom. capacity LV, MVA | 25 | 4.34 | 3.3 | 120 | 1.04 | 0 | 26.25 | 25.21
17 | SS 110/35/10 Kamyshi | 2*6,3 | 12.08 | 5.45 | 20 | 6.63 | 0 | 6.615 | -0.015 | -0.305 | closed
| Nom. capacity MV, MVA | 6.3 | 10.37 | 3.45 |  | 6.92 | 0 | 6.615 | -0.305
| Nom. capacity LV, MVA | 6.3 | 1.71 | 2 | 20 | -0.29 | 0 | 6.615 | 6.905
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 12.92 | 6.97 | 120 | 5.95 | 0 | 15.75 | 9.8 | 9.8 | open
| Nom. capacity MV, MVA | 15,0+16,0 | 9.88 | 6.6 |  | 3.28 | 0 | 15.75 | 12.47
| Nom. capacity LV, MVA | 15,0+16,0 | 3.04 | 0.37 | 120 | 2.67 | 0 | 15.75 | 13.08
19 | SS 110/35/10 Kilikino | 2*16,0 | 2.41 | 4.5 | 120 | -2.09 | 0 | 16.8 | 18.89 | 17.15 | open
| Nom. capacity MV, MVA | 16 | 2.25 | 2.6 |  | -0.35 | 0 | 16.8 | 17.15
| Nom. capacity LV, MVA | 16 | 0.16 | 1.9 | 120 | -1.74 | 0 | 16.8 | 18.54
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 52.37 | 16.36 | 120 | 36.01 | 0 | 42 | 5.99 | 5.99 | open
| Nom. capacity MV, MVA | 40 | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73
| Nom. capacity LV, MVA | 40 | 24.03 | 3.3 | 120 | 20.73 | 0 | 42 | 21.27
21 | SS 110/35/10 Klyukva | 2*16,0 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | open
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3
22 | SS 110/10 Kompressornaya | 2*40,0 | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | open
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 10.28 | 8 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.18 | open
| Nom. capacity MV, MVA | 10,0+16,0 | 8.22 | 5.9 |  | 2.32 | 0 | 10.5 | 8.18
| Nom. capacity LV, MVA | 10,0+16,0 | 2.06 | 2.1 |  | -0.04 | 0 | 10.5 | 10.54
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 10.27 | 4.1 | 0 | 6.17 | 0 | 10.5 | 4.33 | 4.33 | open
25 | SS 110/35/10 Kshen | 2*10,0 | 9.69 | 6.63 | 10 | 3.06 | 0 | 10.5 | 7.44 | 5.94 | open
| Nom. capacity MV, MVA | 10 | 4.56 | 6.06 |  | -1.5 | 0 | 10.5 | 12
| Nom. capacity LV, MVA | 10 | 5.13 | 0.57 | 120 | 4.56 | 0 | 10.5 | 5.94
26 | SS 110/6 Lesnaya | 2*40,0 | 2.34 | 0 | 0 | 2.34 | 0 | 42 | 39.66 | 39.66 | open
27 | SS 110/35/10 Lgov | 2*25,0 | 13.76 | 4 | 120 | 9.76 | 0 | 26.25 | 16.49 | 16.49 | open
| Nom. capacity MV, MVA | 25 | 2.07 |  |  | 2.07 | 0 | 26.25 | 24.18
| Nom. capacity LV, MVA | 25 | 11.69 | 4 | 120 | 7.69 | 0 | 26.25 | 18.56
28 | SS 110/35/10 Lukashevka | 2*16,0 | 8.83 | 10.6 | 120 | -1.77 | 0 | 16.8 | 18.57 | 17.03 | open
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03
| Nom. capacity LV, MVA | 16 | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 5.9 | 13.1 | 120 | -7.2 | 0 | 6.615 | 13.815 | 6.715 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 4.7 | 11.8 |  | -7.1 | 0 | 6.615 | 13.715
| Nom. capacity LV, MVA | 6,3+10,0 | 1.2 | 1.3 |  | -0.1 | 0 | 6.615 | 6.715
30 | SS 110/35/6 Manturovo | 2*16,0 | 7.38 | 9.35 | 10 | -1.97 | 0 | 16.8 | 18.77 | 16.89 | open
| Nom. capacity MV, MVA | 16 | 7.21 | 9.09 |  | -1.88 | 0 | 16.8 | 18.68
| Nom. capacity LV, MVA | 16 | 0.17 | 0.26 | 120 | -0.09 | 0 | 16.8 | 16.89
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 5.81 | 9.6 | 120 | -3.79 | 0 | 6.615 | 10.405 | 8.025 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 5.19 | 6.6 | 120 | -1.41 | 0 | 6.615 | 8.025
| Nom. capacity LV, MVA | 6,3+10,0 | 0.62 | 3 | 45 | -2.38 | 0 | 6.615 | 8.995
32 | SS 110/10 Martovskaya | 2*6,3 | 0.61 | 0.55 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | open
33 | SS 110/35/10 Maryino | 10,0+25,0 | 6.09 | 8.11 | 120 | -2.02 | 0 | 10.5 | 12.52 | 11.41 | open
| Nom. capacity MV, MVA | 10,0+25,0 | 3.79 | 4.9 |  | -1.11 | 0 | 10.5 | 11.61
| Nom. capacity LV, MVA | 10,0+25,0 | 2.3 | 3.21 |  | -0.91 | 0 | 10.5 | 11.41
34 | SS 110/35/10 Medvenka | 2*10,0 | 7.29 | 19.22 | 120 | -11.93 | 0 | 10.5 | 22.43 | 8.31 | open
| Nom. capacity MV, MVA | 10 | 2.98 | 17.1 |  | -14.12 | 0 | 10.5 | 24.62
| Nom. capacity LV, MVA | 10 | 4.31 | 2.12 | 120 | 2.19 | 0 | 10.5 | 8.31
35 | SS 110/6 Neftyanaya | 2*10,0 | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | open
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 16.25 | 26.86 | 120 | -10.61 | 0 | 16.8 | 27.41 | 12.01 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2
| Nom. capacity LV, MVA | 16,0 + 25,0 | 14.25 | 9.46 |  | 4.79 | 0 | 16.8 | 12.01
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 11.36 | 15.5 | 120 | -4.14 | 0 | 16.8 | 20.94 | 14.38 | open
| Nom. capacity MV, MVA | 16 | 7.93 | 14.5 |  | -6.57 | 0 | 16.8 | 23.37
| Nom. capacity LV, MVA | 16 | 3.42 | 1 | 120 | 2.42 | 0 | 16.8 | 14.38
38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 1.76 | 6.31 | 120 | -4.55 | 0 | 6.615 | 11.165 | 7.415 | open
| Nom. capacity MV, MVA | 6.3 | 1.25 | 5 | 120 | -3.75 | 0 | 6.615 | 10.365
| Nom. capacity LV, MVA | 6.3 | 0.51 | 1.31 | 120 | -0.8 | 0 | 6.615 | 7.415
39 | SS 110/10 Paniki | 2 х 2,5 | 0.88 | 0.1 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open
40 | SS 110/35/10 Peny | 2 х 16,0 | 5.83 | 6.9 | 120 | -1.07 | 0 | 16.8 | 17.87 | 17.3 | open
| Nom. capacity MV, MVA | 16 | 3 | 3.5 |  | -0.5 | 0 | 16.8 | 17.3
| Nom. capacity LV, MVA | 16 | 2.83 | 3.4 | 120 | -0.57 | 0 | 16.8 | 17.37
41 | SS 110/35/10 Pribor | 2 х 25,0 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | open
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56
42 | SS 110/10 Progress | 2 х 63,0 | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | open
43 | SS 110/10 Poultry plant | 6,3 + 10,0 | 6.58 | 0 | 0 | 6.58 | 0 | 6.615 | 0.035 | 0.035 | open
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 3.2 | 15.7 | 120 | -12.5 | 0 | 10.5 | 23 | 15.5 | open
| Nom. capacity MV, MVA | 10 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.8 | 21.4 | 45 | -18.6 | 0 | 6.615 | 25.215 | 9.195 | open
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.78 | 17.8 |  | -16.02 | 0 | 6.615 | 22.635
| Nom. capacity LV, MVA | 6,3 + 10,0 | 1.02 | 3.6 | 45 | -2.58 | 0 | 6.615 | 9.195
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 19.35 | 3.25 | 10 | 16.1 | 0 | 33.075 | 16.975 | 16.975 | open
| Nom. capacity MV, MVA | 31.5 | 13 | 1.7 |  | 11.3 | 0 | 33.075 | 21.775
| Nom. capacity LV, MVA | 31.5 | 6.35 | 1.55 | 120 | 4.8 | 0 | 33.075 | 28.275
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 15.28 | 11 | 120 | 4.28 | 0 | 16.8 | 12.52 | 12.52 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 8.41 | 7 |  | 1.41 | 0 | 16.8 | 15.39
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.87 | 4 | 120 | 2.87 | 0 | 16.8 | 13.93
48 | SS 110/10 Solovyinaya | 2 х 25,0 | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | open
49 | SS 110/10 STK | 2 х 10,0 | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 | 9.28 | open
50 | SS 110/10 Studenok | 2 х 6,3 | 2.08 | 0.7 | 120 | 1.38 | 0 | 6.615 | 5.235 | 5.235 | open
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 15.6 | 29 | 120 | -13.4 | 0 | 26.25 | 39.65 | 27.95 | open
| Nom. capacity MV, MVA | 25 | 5.4 | 17.1 |  | -11.7 | 0 | 26.25 | 37.95
| Nom. capacity LV, MVA | 25 | 10.2 | 11.9 |  | -1.7 | 0 | 26.25 | 27.95
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | open
| Nom. capacity MV, MVA | 25 | 3.67 |  |  | 3.67 | 0 | 26.25 | 22.58
| Nom. capacity LV, MVA | 25 | 9.93 | 0 | 0 | 9.93 | 0 | 26.25 | 16.32
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 3.87 | 3.44 | 120 | 0.43 | 0 | 10.5 | 10.07 | 8.57 | open
| Nom. capacity MV, MVA | 10 | 0.5 | 2 |  | -1.5 | 0 | 10.5 | 12
| Nom. capacity LV, MVA | 10 | 3.37 | 1.44 |  | 1.93 | 0 | 10.5 | 8.57
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 4.72 | 9.59 | 120 | -4.87 | 0 | 6.615 | 11.485 | 6.525 | open
| Nom. capacity MV, MVA | 6,3 + 16,0 | 4.13 | 9.09 |  | -4.96 | 0 | 6.615 | 11.575
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.59 | 0.5 | 120 | 0.09 | 0 | 6.615 | 6.525
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.63 | 0.5 | 120 | 0.13 | 0 | 10.5 | 10.37 | 10.04 | open
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.46 |  |  | 0.46 | 0 | 10.5 | 10.04
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.17 | 0.5 | 120 | -0.33 | 0 | 10.5 | 10.83
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 6.29 | 17.4 | 120 | -11.11 | 0 | 16.8 | 27.91 | 16.96 | open
| Nom. capacity MV, MVA | 16 | 1.85 | 12.8 |  | -10.95 | 0 | 16.8 | 27.75
| Nom. capacity LV, MVA | 16 | 4.44 | 4.6 | 120 | -0.16 | 0 | 16.8 | 16.96
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 4.33 | 12.34 | 120 | -8.01 | 0 | 26.25 | 34.26 | 25.08 | open
| Nom. capacity MV, MVA | 25 | 2.94 | 12.12 |  | -9.18 | 0 | 26.25 | 35.43
| Nom. capacity LV, MVA | 25 | 1.39 | 0.22 | 10 | 1.17 | 0 | 26.25 | 25.08
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 3.15 | 6.3 | 80 | -3.15 | 0 | 7.875 | 11.025 | 7.985 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.86 | 3.9 |  | -3.04 | 0 | 7.875 | 10.915
| Nom. capacity LV, MVA | 7,5 + 10,0 | 2.29 | 2.4 | 80 | -0.11 | 0 | 7.875 | 7.985
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 3.24 | 9.38 | 10 | -6.14 | 0 | 16.8 | 22.94 | 16.01 | open
| Nom. capacity MV, MVA | 16 | 2.16 | 9.09 |  | -6.93 | 0 | 16.8 | 23.73
| Nom. capacity LV, MVA | 16 | 1.08 | 0.29 | 120 | 0.79 | 0 | 16.8 | 16.01
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 2.7 | 8.25 | 120 | -5.55 | 0 | 6.615 | 12.165 | 7.025 | open
| Nom. capacity MV, MVA | 6.3 | 1.86 | 7 |  | -5.14 | 0 | 6.615 | 11.755
| Nom. capacity LV, MVA | 6.3 | 0.84 | 1.25 | 129 | -0.41 | 0 | 6.615 | 7.025
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 4.6 | 13.73 | 120 | -9.13 | 0 | 10.5 | 19.63 | 11.83 | open
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3
| Nom. capacity LV, MVA | 10 | 1.2 | 2.53 | 120 | -1.33 | 0 | 10.5 | 11.83
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 10.49 | 12.9 | 120 | -2.41 | 0 | 26.25 | 28.66 | 21.53 | open
| Nom. capacity MV, MVA | 25 | 4.99 | 12.12 |  | -7.13 | 0 | 26.25 | 33.38
| Nom. capacity LV, MVA | 25 | 5.5 | 0.78 | 120 | 4.72 | 0 | 26.25 | 21.53
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.875 | 11.625 | 6.83 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.26 | 6.06 |  | -4.8 | 0 | 7.88 | 12.68
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.3 | 0.25 | 10 | 1.05 | 0 | 7.88 | 6.83
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.45 | 0.37 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.2 | 1.43 | 120 | -1.23 | 0 | 1.68 | 2.91 | 2.91 | open
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.47 | 6.1 | 0 | -5.63 | 0 | 4.2 | 9.83 | 9.83 | open
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.08 | 0.15 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 1.05 | 0.29 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | open
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 1.37 | 0.4 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | open
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.55 | 0.22 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | open
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.4 | 0.46 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.4 | 0 | 0 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 2.37 | 0.46 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | open
77 | SS 35/10 Vygornoe | 2 х 2,5 | 1.38 | 0.51 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | open
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.44 | 0.17 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | open
79 | SS 35/10 Gorodok | 2 х 4,0 | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | open
80 | SS 35/10 Guevo | 2 х 2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.625 | 3.115 | 3.115 | open
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.2 | 0.38 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | open
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 3.44 | 3.5 | 0 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.86 | 0.26 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 10.39 | 2.5 | 0 | 7.89 | 0 | 10.5 | 2.61 | 2.61 | open
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.98 | 1.67 | 0 | -0.69 | 0 | 4.2 | 4.89 | 4.89 | open
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open
87 | SS 35/10 Ivanino | 2 х 6,3 | 2.29 | 2.69 | 80 | -0.4 | 0 | 6.615 | 7.015 | 7.015 | open
88 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 1.89 | 1.99 | 1.99 | open
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.33 | 0.52 | 120 | -0.19 | 0 | 1.68 | 1.87 | 1.87 | open
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 9.78 | 6.25 | 20 | 3.53 | 0 | 10.5 | 6.97 | 6.97 | open
91 | SS 35/10 Mixed fodder plant | 4,0+6,3 | 0.49 | 0 | 0 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | open
92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 3.1 | 0.21 | 120 | 2.89 | 0 | 6.615 | 3.725 | 3.725 | open
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 2.19 | 1.14 | 80 | 1.05 | 0 | 3.36 | 2.31 | 2.31 | open
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 4.35 | 1.56 | 80 | 2.79 | 0 | 4.2 | 1.41 | 1.41 | open
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.62 | 0.24 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
96 | SS 35/10 Krupets | 1,8 + 2,5 | 1.5 | 0.42 | 120 | 1.08 | 0 | 1.89 | 0.81 | 0.81 | open
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.7 | 0.6 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.14 | 0.17 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | open
99 | SS 35/10 Kurchatov | 2 х 10,0 | 4.52 | 4.5 | 80 | 0.02 | 0 | 10.5 | 10.48 | 10.48 | open
100 | SS 35/10 Kutok | 2 х 2,5 | 0.08 | 0.05 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open
101 | SS 35/10 Linets | 2 х 2,5 | 0.23 | 0.25 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
102 | SS 35/10 Luch | 2 х 6,3 | 3.03 | 0.23 | 120 | 2.8 | 0 | 6.615 | 3.815 | 3.815 | open
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | open
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.65 | 0.08 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | open
105 | SS 35/10 Mayak | 2 х 2,5 | 0.5 | 0.3 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 1.27 | 1.7 | 80 | -0.43 | 0 | 4.2 | 4.63 | 4.63 | open
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.87 | 0.3 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | open
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.51 | 0.63 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.4 | 0.03 | 80 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open
110 | SS 35/10 Novaya | 2 х 2,5 | 1.2 | 0.4 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | open
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.56 | 0.19 | 120 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | open
112 | SS 35/10 Orlovka | 2 х 2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.625 | 2.975 | 2.975 | open
113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.18 | 0.2 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.26 | 0.74 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | open
115 | SS 35/10 Panino | 2 х 2,5 | 0.28 | 0.11 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.62 | 0.52 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.61 | 0.3 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | open
118 | SS 35/10 Platava | 2 х 2,5 | 1.38 | 0.26 | 120 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | open
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.19 | 0.46 | 120 | -0.27 | 0 | 1.68 | 1.95 | 1.95 | open
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | open
121 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | open
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 1.39 | 0.3 | 80 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | open
123 | SS 35/10 Pselets | 2 х 1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.39 | 0.43 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.77 | 0.32 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | open
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.38 | 0.44 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open
127 | SS 35/10 Razvetye | 2 х 4,0 | 1.91 | 1.03 | 120 | 0.88 | 0 | 4.2 | 3.32 | 3.32 | open
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.74 | 0.11 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | open
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.28 | 0.29 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | open
130 | SS 35/10 Rubilnik | 2 х 2,5 | 1.25 | 1.18 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.28 | 0.08 | 20 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | open
132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.39 | 0.6 | 20 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | open
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 4.41 | 2.25 | 80 | 2.16 | 0 | 6.615 | 4.455 | 4.455 | open
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.09 | 1.4 | 45 | 0.69 | 0 | 4.2 | 3.51 | 3.51 | open
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.4 | 0 | - | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.51 | 0.6 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open
137 | SS 35/10 Snagost | 2 х 4,0 | 1.31 | 0.05 | 10 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | open
138 | SS 35/10 SOM | 1,6 + 4,0 | 1.03 | 0.08 | 10 | 0.95 | 0 | 1.68 | 0.73 | 0.73 | open
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.77 | 0.69 | 120 | 0.08 | 0 | 3.36 | 3.28 | 3.28 | open
140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.65 | 0.58 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.2 | 0.2 | 80 | 0 | 0 | 1.68 | 1.68 | 1.68 | open
142 | CC 35/10 Starshee | 2 х 1,6 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | open
143 | SS 35/10 Teplitsy | 2 х 4,0 | 2.02 | 1.08 | 45 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | open
144 | SS 35/10 Turovka | 2 х 2,5 | 0.44 | 0.6 | 120 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | open
145 | SS 35/10 Uspenka | 2 х 2,5 | 1.11 | 1 | 80 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open
146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 22.44 | 5 |  | 17.44 | 0 | 26.25 | 8.81 | 8.81 | open
147 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | open
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.38 | 0.21 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
149 | SS 35/10 Shipy | 2 х 2,5 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | open
150 | SS 35/10 Elevator | 4,0 + 6,3 | 1.53 | 0.6 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | open
151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.43 | 4.7 | 80 | 3.73 | 0 | 10.5 | 6.77 | 6.77 | open
152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 2.46 | 3.9 | 120 | -1.44 | 0 | 2.625 | 4.065 | 4.065 | open
| TOTAL: | 3185.9 | 761.961 | 777.99 | [5 empty] | 1221.894
| deficit | [8 empty] | -7.475
| proficit | [8 empty] | 1214.414

## ЦП Ожидаемый дефицит, табл.2
table 2
No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
[5 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.018 | 1.828 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.472 | 1.069 | open
| Nom. capacity MV, MVA | 6.3 | 0.011 | 1.231 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.069
| Nom. capacity MV, MVA | 6.3 | 0.007 | 0.597 | 4 | 1 day and night | 4 | 0 | 4 | 3.403
2 | SS 110/10 Beketovo | 1*6,3 | 2.461 | 2.791 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -0.641 | -0.641 | closed
3 | SS 110/35/10 Besedino | 1*6,3 | 0.033 | 3.373 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.427 | 0.52 | open
| Nom. capacity MV, MVA | 6.3 | 0.033 | 0.593 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.907
| Nom. capacity LV, MVA | 6.3 |  | 2.78 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.52
4 | SS 110/10 Voskhod | 1*10,0 | 0.061 | 0.661 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.839 | 1.839 | open
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.037 | 0.947 | 6 | 1 day and night | 6 | 0 | 6 | 5.053 | 1.353 | open
| Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.037 | 0.947 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.353
6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.091 | 1.311 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.849 | 0.47 | open
| Nom. capacity MV, MVA | 10 | 0.091 | 1.121 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.379
| Nom. capacity LV, MVA | 10 |  | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47
7 | SS 110/10 Zabelye | 1*2,5 | 0.028 | 0.328 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.822 | 1.822 | open
8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | open
9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.49 | 1.89 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.24 | 0.64 | open
| Nom. capacity MV, MVA | 10 | 0 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6
| Nom. capacity LV, MVA | 10 | 0.49 | 0.89 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.64
10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.014 | 1.214 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.186 | 0.186 | open
11 | SS 110/35/10 Maritsa | 1*6,3 | 0.025 | 1.675 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.245 | 0.245 | open
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.019 | 0.569 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.321 | 2.04 | open
| Nom. capacity MV, MVA | 6.3 | 0.019 | 0.459 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.281
| Nom. capacity LV, MVA | 6.3 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.033 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.367 | 1.367 | open
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.7 | 12.16 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | -5.52 | -5.52 | closed
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 1.638 | 4.068 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 3.432 | 0.601 | open
| Nom. capacity MV, MVA | 10 | 1.599 | 3.569 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 2.831
| Nom. capacity LV, MVA | 10 | 0.039 | 0.499 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.601
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.573 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.227 | 0.227 | open
17 | SS 35/10 Agronom | 1 х 1,8 | 0.195 | 0.695 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.255 | 0.255 | open
18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | open
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.015 | 0.255 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.175 | 1.175 | open
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.037 | 0.597 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.743 | 0.743 | open
21 | SS 35/10 B. Gneushevo | 1 х 2,5 |  | 0.79 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.17 | 0.17 | open
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.246 | 1.006 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 1.824 | 1.824 | open
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.02 | 0.38 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.26 | 0.26 | open
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.135 | 0.595 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.835 | 0.835 | open
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.015 | 0.295 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.855 | 1.855 | open
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.274 | 0.774 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.986 | 0.986 | open
27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
28 | SS 35/10 Bobrovka | 1 х 1,6 |  | 0.26 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.41 | 0.41 | open
29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
30 | SS 35/10 Budki | 1 х 1,0 |  | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | open
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.037 | 0.697 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.903 | 0.903 | open
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.045 | 0.265 | 1 | 1 day and night | 1 | 0 | 1 | 0.735 | 0.735 | open
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.04 | 0.32 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.11 | 1.11 | open
34 | SS 35/10 Bykovo | 1 х 4,0 | 3.813 | 4.703 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | -3.273 | -3.273 | closed
35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | open
36 | SS 35/10 Vanino | 1 х 2,5 | 0.068 | 0.308 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.492 | 0.492 | open
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.035 | 0.635 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.415 | 0.415 | open
38 | SS 35/10 Water storage | 1 х 4,0 | 3.545 | 5.305 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | -2.585 | -2.585 | closed
39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | open
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.734 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.166 | 0.166 | open
41 | SS 35/10 Voronok | 1 х 4,0 | 0.013 | 0.833 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.267 | 1.267 | open
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.032 | 0.482 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.668 | 1.668 | open
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.57 | 1.57 | open
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.01 | 0.22 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.28 | 1.28 | open
45 | SS 35/10 Glazovo | 1 х 2,5 | 0.02 | 1.28 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.22 | 0.22 | open
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.018 | 0.548 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.852 | 0.852 | open
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.07 | 0.37 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.33 | 0.33 | open
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.044 | 0.614 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.146 | 0.146 | open
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.025 | 0.525 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.575 | 0.575 | open
50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | open
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.042 | 1.002 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.428 | 0.428 | open
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.019 | 0.629 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.221 | 2.221 | open
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.009 | 0.269 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.671 | 0.671 | open
54 | SS 35/10 Daryino | 1 х 2,5 | 0.038 | 0.438 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.362 | 1.362 | open
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.05 | 0.66 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.14 | 0.14 | open
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.03 | 0.36 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.71 | 0.71 | open
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.045 | 0.345 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.505 | 0.505 | open
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.011 | 0.371 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.779 | 1.779 | open
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.043 | 0.533 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.307 | 0.307 | open
60 | SS 35/10 Znamenka | 1 х 1,8 |  | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | open
61 | SS 35/10 Iskra | 1 х 2,5 | 0.048 | 0.248 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.332 | 0.332 | open
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.009 | 0.419 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.381 | 0.381 | open
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.06 | 0.19 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.61 | 1.61 | open
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.01 | 0.32 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.32 | 0.32 | open
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.257 | 0.537 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.203 | 0.203 | open
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.031 | 0.671 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.859 | 0.859 | open
67 | SS 35/10 Kolontaevka | 1 х 2,5 |  | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | open
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.024 | 0.574 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.846 | 0.846 | open
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.017 | 0.567 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.193 | 0.193 | open
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.264 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.166 | 1.166 | open
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.035 | 0.675 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.155 | 0.155 | open
72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.011 | 1.071 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.019 | 0.019 | open
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.035 | 0.615 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.675 | 0.675 | open
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.017 | 0.337 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.813 | 0.813 | open
75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.041 | 0.041 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.919 | 0.919 | open
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.059 | 0.659 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.441 | 0.441 | open
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.015 | 0.775 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.505 | 0.505 | open
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.01 | 0.31 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.88 | 0.88 | open
79 | SS 35/10 Markovo | 1 х 2,5 | 0.01 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | open
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.015 | 0.245 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.085 | 1.085 | open
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.013 | 1.003 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.147 | 1.147 | open
82 | SS 35/10 Mokva | 1 х 4,0 | 0.057 | 0.617 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.533 | 1.533 | open
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.033 | 0.633 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.467 | 0.467 | open
84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | open
85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | open
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | open
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.014 | 1.114 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.036 | 1.036 | open
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.048 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.352 | 1.352 | open
89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.415 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.145 | 1.145 | open
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.13 | 0.63 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.34 | 0.34 | open
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.08 | 0.57 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.07 | 0.07 | open
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.952 | 2.412 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0.558 | 0.558 | open
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.42 | 1.02 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.3 | 1.3 | open
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | open
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 |  | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.158 | 0.488 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.662 | 1.662 | open
97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | open
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.015 | 0.205 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.945 | 1.945 | open
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.359 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.791 | 1.791 | open
100 | SS 35/10 Pristen | 1 х 4,0 | 0.097 | 2.297 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.003 | 1.003 | open
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.018 | 0.018 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.722 | 0.722 | open
102 | SS 35/10 Reut | 1 х 2,5 | 0.916 | 1.356 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | -0.256 | -0.256 | closed
103 | SS 35/10 Rovenka | 1 х 1,6 | 1.385 | 2.545 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | -0.945 | -0.945 | closed
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.033 | 0.213 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.487 | 0.487 | open
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 |  | 0.38 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.92 | 1.92 | open
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.018 | 0.418 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.892 | 0.892 | open
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.214 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.216 | 1.216 | open
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.044 | 0.464 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.476 | 0.476 | open
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.023 | 0.553 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.597 | 0.597 | open
110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | open
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.009 | 0.309 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.391 | 2.391 | open
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.058 | 0.308 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.122 | 1.122 | open
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.09 | 0.9 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.86 | 0.86 | open
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.003 | 0.283 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.817 | 0.817 | open
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.008 | 0.208 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.192 | 1.192 | open
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.038 | 0.388 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.912 | 0.912 | open
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.015 | 0.615 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.725 | 0.725 | open
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.009 | 0.549 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.161 | 0.161 | open
119 | SS 35/10 Telmana | 1 х 2,5 | 0.025 | 0.435 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.715 | 0.715 | open
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.035 | 0.395 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.035 | 1.035 | open
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.008 | 0.078 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.622 | 0.622 | open
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.025 | 0.205 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.515 | 1.515 | open
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.017 | 0.357 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.743 | 0.743 | open
124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | open
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.033 | 0.393 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.037 | 1.037 | open
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.019 | 0.179 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.251 | 1.251 | open
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.023 | 0.603 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.867 | 0.867 | open
128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | open
129 | SS 35/10 Elevator | 1х6,3 | 0.02 | 0.23 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.37 | 0.37 | open
130 | SS 35/10 Yankovo | 1 х 1,6 |  | 0.24 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.4 | 0.4 | open
131 | SS 35/10 Yasenki | 1 х 2,5 | 3.49 | 3.97 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -1.82 | -1.82 | closed
Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | open
2 | SS 110/10 ARZ | 6,3+10,0 |  | 1.78 | 0.9 | 45 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | open
3 | SS 110/35/10 Atomgrad | 2*25 | 0.327 | 12.047 | 20.2 | 120 | -8.153 | 0 | 26.25 | 34.403 | 27.593 | open
| Nom. capacity MV, MVA | 25 | 0.24 | 3.79 | 10.6 | 120 | -6.81 | 0 | 26.25 | 33.06
| Nom. capacity lV, MVA | 25 | 0.087 | 8.257 | 9.6 | 120 | -1.343 | 0 | 26.25 | 27.593
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.015 | 0.845 | 0.6 | 120 | 0.245 | 0 | 6.615 | 6.37 | 6.37 | open
5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.023 | 1.343 | 6.19 | 15 | -4.847 | 0 | 5.88 | 10.727 | 5.328 | open
| Nom. capacity MV, MVA | 5,6+10,0 | 0.011 | 0.601 | 6 |  | -5.399 | 0 | 5.88 | 11.279
| Nom. capacity LV, MVA | 5,6+10,0 | 0.012 | 0.742 | 0.19 | 120 | 0.552 | 0 | 5.88 | 5.328
6 | SS 110/35/10 Belaya | 2*16,0 | 1.174 | 8.274 | 12 | 120 | -3.726 | 0 | 16.8 | 20.526 | 12.849 | open
| Nom. capacity MV, MVA | 16 | 0.751 | 3.951 | 0 |  | 3.951 | 0 | 16.8 | 12.849
| Nom. capacity LV, MVA | 16 | 0.423 | 4.323 | 12 | 120 | -7.677 | 0 | 16.8 | 24.477
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.041 | 1.641 | 1.3 | 120 | 0.341 | 0 | 6.615 | 6.274 | 6.011 | open
| Nom. capacity MV, MVA | 6.3 | 0.004 | 0.604 |  |  | 0.604 | 0 | 6.615 | 6.011
| Nom. capacity LV, MVA | 6.3 | 0.037 | 1.037 | 1.3 | 120 | -0.263 | 0 | 6.615 | 6.878
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.05 | 2.62 | 1.17 | 45 | 1.45 | 0 | 2.625 | 1.175 | 1.175 | open
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.566 | 43.046 | 16.8 | 0 | 26.246 | 0 | 84.525 | 58.279 | 57.961 | open
| Nom. capacity MV, MVA | 40,0+2*40,5 | 1.482 | 16.482 | 16.8 | 0 | -0.318 | 0 | 84.525 | 84.843
| Nom. capacity MV, MVA | 40,0+2*40,5 | 0.084 | 26.564 | 0 | 0 | 26.564 | 0 | 84.525 | 57.961
10 | SS 110/10 Vysokaya* | 2*16,0 |  | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | closed
11 | SS 110/35/10 Glushkovo | 2*10,0 | 1.5325 | 7.7625 | 8.04 | 120 | -0.2775 | 0 | 10.5 | 10.7775 | 8.6645 | open
| Nom. capacity MV, MVA | 10 | 1.527 | 4.487 | 6.6 | 120 | -2.113 | 0 | 10.5 | 12.613
| Nom. capacity LV, MVA | 10 | 0.0055 | 3.2755 | 1.44 | 80 | 1.8355 | 0 | 10.5 | 8.6645
12 | SS 110/10 Gorodskaya | 2*25,0 | 4.53 | 17.25 | 0 | 0 | 17.25 | 0 | 26.25 | 9 | 9 | open
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 11.704 | 19.704 | 6.52 | 120 | 13.184 | 0 | 10.5 | -2.684 | -2.684 | closed
| Nom. capacity MV, MVA | 10+16,0 | 11.275 | 15.925 | 6.06 |  | 9.865 | 0 | 10.5 | 0.635
| Nom. capacity LV, MVA | 10+16,0 | 0.429 | 3.779 | 0.46 | 120 | 3.319 | 0 | 10.5 | 7.181
14 | SS 110/35/10 Dmitriev | 2*10,0 | 0.267 | 6.207 | 10.4 | 120 | -4.193 | 0 | 10.5 | 14.693 | 9.727 | open
| Nom. capacity MV, MVA | 10 | 0.024 | 2.434 | 7.4 |  | -4.966 | 0 | 10.5 | 15.466
| Nom. capacity LV, MVA | 10 | 0.243 | 3.773 | 3 | 80 | 0.773 | 0 | 10.5 | 9.727
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.917 | 0.5 | 120 | 0.417 | 0 | 10.5 | 10.083 | 10.083 | open
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.33 | 7.85 | 22.1 | 80 | -14.25 | 0 | 26.25 | 40.5 | 24.978 | open
| Nom. capacity MV, MVA | 25 | 0.098 | 3.278 | 18.8 |  | -15.522 | 0 | 26.25 | 41.772
| Nom. capacity LV, MVA | 25 | 0.232 | 4.572 | 3.3 | 120 | 1.272 | 0 | 26.25 | 24.978
17 | SS 110/35/10 Kamyshi | 2*6,3 | 4.129 | 16.209 | 5.45 | 20 | 10.759 | 0 | 6.615 | -4.144 | -4.345 | closed
| Nom. capacity MV, MVA | 6.3 | 4.04 | 14.41 | 3.45 |  | 10.96 | 0 | 6.615 | -4.345
| Nom. capacity LV, MVA | 6.3 | 0.089 | 1.799 | 2 | 20 | -0.201 | 0 | 6.615 | 6.816
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.46 | 13.38 | 6.97 | 120 | 6.41 | 0 | 15.75 | 9.34 | 9.34 | open
| Nom. capacity MV, MVA | 15,0+16,0 | 0.362 | 10.242 | 6.6 |  | 3.642 | 0 | 15.75 | 12.108
| Nom. capacity LV, MVA | 15,0+16,0 | 0.098 | 3.138 | 0.37 | 120 | 2.768 | 0 | 15.75 | 12.982
19 | SS 110/35/10 Kilikino | 2*16,0 | 0.0948 | 2.5048 | 4.5 | 120 | -1.9952 | 0 | 16.8 | 18.7952 | 17.0552 | open
| Nom. capacity MV, MVA | 16 | 0.0948 | 2.3448 | 2.6 |  | -0.2552 | 0 | 16.8 | 17.0552
| Nom. capacity LV, MVA | 16 |  | 0.16 | 1.9 | 120 | -1.74 | 0 | 16.8 | 18.54
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.67 | 55.04 | 16.36 | 120 | 38.68 | 0 | 42 | 3.32 | 3.32 | open
| Nom. capacity MV, MVA | 40 |  | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73
| Nom. capacity LV, MVA | 40 | 2.67 | 26.7 | 3.3 | 120 | 23.4 | 0 | 42 | 18.6
21 | SS 110/35/10 Klyukva | 2*16,0 | 0.421 | 4.121 | 1.2 | 120 | 2.921 | 0 | 16.8 | 13.879 | 13.879 | open
| Nom. capacity MV, MVA | 16 |  | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 0.421 | 4.121 | 1.2 | 120 | 2.921 | 0 | 16.8 | 13.879
22 | SS 110/10 Kompressornaya | 2*40,0 |  | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | open
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.1 | 11.38 | 8 | 120 | 3.38 | 0 | 10.5 | 7.12 | 7.12 | open
| Nom. capacity MV, MVA | 10,0+16,0 | 0.111 | 8.331 | 5.9 |  | 2.431 | 0 | 10.5 | 8.069
| Nom. capacity LV, MVA | 10,0+16,0 | 0.989 | 3.049 | 2.1 |  | 0.949 | 0 | 10.5 | 9.551
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 3.621 | 13.891 | 4.1 | 0 | 9.791 | 0 | 10.5 | 0.709 | 0.709 | open
25 | SS 110/35/10 Kshen | 2*10,0 | 1.998 | 11.688 | 6.63 | 10 | 5.058 | 0 | 10.5 | 5.442 | 4.458 | open
| Nom. capacity MV, MVA | 10 | 0.516 | 5.076 | 6.06 |  | -0.984 | 0 | 10.5 | 11.484
| Nom. capacity LV, MVA | 10 | 1.482 | 6.612 | 0.57 | 120 | 6.042 | 0 | 10.5 | 4.458
26 | SS 110/6 Lesnaya | 2*40,0 | 0.9 | 3.24 | 0 | 0 | 3.24 | 0 | 42 | 38.76 | 38.76 | open
27 | SS 110/35/10 Lgov | 2*25,0 | 0.375 | 14.135 | 4 | 120 | 10.135 | 0 | 26.25 | 16.115 | 16.115 | open
| Nom. capacity MV, MVA | 25 | 0 | 2.07 |  |  | 2.07 | 0 | 26.25 | 24.18
| Nom. capacity LV, MVA | 25 | 0.375 | 12.065 | 4 | 120 | 8.065 | 0 | 26.25 | 18.185
28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.1 | 8.93 | 10.6 | 120 | -1.67 | 0 | 16.8 | 18.47 | 16.93 | open
| Nom. capacity MV, MVA | 16 | 0.1 | 5.17 | 5.3 |  | -0.13 | 0 | 16.8 | 16.93
| Nom. capacity LV, MVA | 16 |  | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.138 | 6.038 | 13.1 | 120 | -7.062 | 0 | 6.615 | 13.677 | 6.706 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 0.129 | 4.829 | 11.8 |  | -6.971 | 0 | 6.615 | 13.586
| Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 1.209 | 1.3 |  | -0.091 | 0 | 6.615 | 6.706
30 | SS 110/35/6 Manturovo | 2*16,0 | 0.45 | 7.83 | 9.35 | 10 | -1.52 | 0 | 16.8 | 18.32 | 16.865 | open
| Nom. capacity MV, MVA | 16 | 0.425 | 7.635 | 9.09 |  | -1.455 | 0 | 16.8 | 18.255
| Nom. capacity LV, MVA | 16 | 0.025 | 0.195 | 0.26 | 120 | -0.065 | 0 | 16.8 | 16.865
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 4.93 | 10.74 | 9.6 | 120 | 1.14 | 0 | 6.615 | 5.475 | 3.104 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 4.921 | 10.111 | 6.6 | 120 | 3.511 | 0 | 6.615 | 3.104
| Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 0.629 | 3 | 45 | -2.371 | 0 | 6.615 | 8.986
32 | SS 110/10 Martovskaya | 2*6,3 | 0.324 | 0.934 | 0.55 | 120 | 0.384 | 0 | 6.615 | 6.231 | 6.231 | open
33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.109 | 6.199 | 8.11 | 120 | -1.911 | 0 | 10.5 | 12.411 | 11.39 | open
| Nom. capacity MV, MVA | 10,0+25,0 | 0.089 | 3.879 | 4.9 |  | -1.021 | 0 | 10.5 | 11.521
| Nom. capacity LV, MVA | 10,0+25,0 | 0.02 | 2.32 | 3.21 |  | -0.89 | 0 | 10.5 | 11.39
34 | SS 110/35/10 Medvenka | 2*10,0 | 0.487 | 7.777 | 19.22 | 120 | -11.443 | 0 | 10.5 | 21.943 | 8.134 | open
| Nom. capacity MV, MVA | 10 | 0.311 | 3.291 | 17.1 |  | -13.809 | 0 | 10.5 | 24.309
| Nom. capacity LV, MVA | 10 | 0.176 | 4.486 | 2.12 | 120 | 2.366 | 0 | 10.5 | 8.134
35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | open
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 1.099 | 17.349 | 26.86 | 120 | -9.511 | 0 | 16.8 | 26.311 | 10.972 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 0.061 | 2.061 | 17.4 | 0 | -15.339 | 0 | 16.8 | 32.139
| Nom. capacity LV, MVA | 16,0 + 25,0 | 1.038 | 15.288 | 9.46 |  | 5.828 | 0 | 16.8 | 10.972
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.442 | 11.802 | 15.5 | 120 | -3.698 | 0 | 16.8 | 20.498 | 14.047 | open
| Nom. capacity MV, MVA | 16 | 0.109 | 8.039 | 14.5 |  | -6.461 | 0 | 16.8 | 23.261
| Nom. capacity LV, MVA | 16 | 0.333 | 3.753 | 1 | 120 | 2.753 | 0 | 16.8 | 14.047
38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.052 | 1.812 | 6.31 | 120 | -4.498 | 0 | 6.615 | 11.113 | 7.396 | open
| Nom. capacity MV, MVA | 6.3 | 0.033 | 1.283 | 5 | 120 | -3.717 | 0 | 6.615 | 10.332
| Nom. capacity LV, MVA | 6.3 | 0.019 | 0.529 | 1.31 | 120 | -0.781 | 0 | 6.615 | 7.396
39 | SS 110/10 Paniki | 2 х 2,5 |  | 0.88 | 0.1 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open
40 | SS 110/35/10 Peny | 2 х 16,0 | 0.179 | 6.009 | 6.9 | 120 | -0.891 | 0 | 16.8 | 17.691 | 17.141 | open
| Nom. capacity MV, MVA | 16 | 0.159 | 3.159 | 3.5 |  | -0.341 | 0 | 16.8 | 17.141
| Nom. capacity LV, MVA | 16 | 0.02 | 2.85 | 3.4 | 120 | -0.55 | 0 | 16.8 | 17.35
41 | SS 110/35/10 Pribor | 2 х 25,0 | 0 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | open
| Nom. capacity MV, MVA | 25 |  | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 |  | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56
42 | SS 110/10 Progress | 2 х 63,0 |  | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | open
43 | SS 110/10 Poultry plant | 6,3 + 10,0 |  | 6.58 | 0 | 0 | 6.58 | 0 | 6.615 | 0.035 | 0.035 | open
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.007 | 3.207 | 15.7 | 120 | -12.493 | 0 | 10.5 | 22.993 | 15.493 | open
| Nom. capacity MV, MVA | 10 | 0 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 0.007 | 1.407 | 6.4 |  | -4.993 | 0 | 10.5 | 15.493
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 1.515 | 4.315 | 21.4 | 45 | -17.085 | 0 | 6.615 | 23.7 | 9.097 | open
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.417 | 3.197 | 17.8 |  | -14.603 | 0 | 6.615 | 21.218
| Nom. capacity LV, MVA | 6,3 + 10,0 | 0.098 | 1.118 | 3.6 | 45 | -2.482 | 0 | 6.615 | 9.097
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.59 | 19.94 | 3.25 | 10 | 16.69 | 0 | 33.075 | 16.385 | 16.385 | open
| Nom. capacity MV, MVA | 31.5 | 0.572 | 13.572 | 1.7 |  | 11.872 | 0 | 33.075 | 21.203
| Nom. capacity LV, MVA | 31.5 | 0.018 | 6.368 | 1.55 | 120 | 4.818 | 0 | 33.075 | 28.257
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 4.247 | 19.527 | 11 | 120 | 8.527 | 0 | 16.8 | 8.273 | 8.273 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 4.189 | 12.599 | 7 |  | 5.599 | 0 | 16.8 | 11.201
| Nom. capacity LV, MVA | 16,0 + 25,0 | 0.058 | 6.928 | 4 | 120 | 2.928 | 0 | 16.8 | 13.872
48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | open
49 | SS 110/10 STK | 2 х 10,0 |  | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 | 9.28 | open
50 | SS 110/10 Studenok | 2 х 6,3 | 0.134 | 2.214 | 0.7 | 120 | 1.514 | 0 | 6.615 | 5.101 | 5.101 | open
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.394 | 16.994 | 29 | 120 | -12.006 | 0 | 26.25 | 38.256 | 27.055 | open
| Nom. capacity MV, MVA | 25 | 0.499 | 5.899 | 17.1 |  | -11.201 | 0 | 26.25 | 37.451
| Nom. capacity LV, MVA | 25 | 0.895 | 11.095 | 11.9 |  | -0.805 | 0 | 26.25 | 27.055
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.661 | 20.261 | 0 | 0 | 20.261 | 0 | 26.25 | 5.989 | 5.989 | open
| Nom. capacity MV, MVA | 25 | 1.161 | 4.831 |  |  | 4.831 | 0 | 26.25 | 21.419
| Nom. capacity LV, MVA | 25 | 5.5 | 15.43 | 0 | 0 | 15.43 | 0 | 26.25 | 10.82
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.059 | 3.929 | 3.44 | 120 | 0.489 | 0 | 10.5 | 10.011 | 8.528 | open
| Nom. capacity MV, MVA | 10 | 0.017 | 0.517 | 2 |  | -1.483 | 0 | 10.5 | 11.983
| Nom. capacity LV, MVA | 10 | 0.042 | 3.412 | 1.44 |  | 1.972 | 0 | 10.5 | 8.528
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.482 | 5.202 | 9.59 | 120 | -4.388 | 0 | 6.615 | 11.003 | 6.412 | open
| Nom. capacity MV, MVA | 6,3 + 16,0 | 0.369 | 4.499 | 9.09 |  | -4.591 | 0 | 6.615 | 11.206
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.113 | 0.703 | 0.5 | 120 | 0.203 | 0 | 6.615 | 6.412
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.038 | 0.668 | 0.5 | 120 | 0.168 | 0 | 10.5 | 10.332 | 10.032 | open
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.008 | 0.468 |  |  | 0.468 | 0 | 10.5 | 10.032
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.03 | 0.2 | 0.5 | 120 | -0.3 | 0 | 10.5 | 10.8
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 2.883 | 9.173 | 17.4 | 120 | -8.227 | 0 | 16.8 | 25.027 | 16.427 | open
| Nom. capacity MV, MVA | 16 | 2.35 | 4.2 | 12.8 |  | -8.6 | 0 | 16.8 | 25.4
| Nom. capacity LV, MVA | 16 | 0.533 | 4.973 | 4.6 | 120 | 0.373 | 0 | 16.8 | 16.427
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.354 | 4.684 | 12.34 | 120 | -7.656 | 0 | 26.25 | 33.906 | 25.03 | open
| Nom. capacity MV, MVA | 25 | 0.304 | 3.244 | 12.12 |  | -8.876 | 0 | 26.25 | 35.126
| Nom. capacity LV, MVA | 25 | 0.05 | 1.44 | 0.22 | 10 | 1.22 | 0 | 26.25 | 25.03
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.151 | 3.301 | 6.3 | 80 | -2.999 | 0 | 7.875 | 10.874 | 7.861 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.027 | 0.887 | 3.9 |  | -3.013 | 0 | 7.875 | 10.888
| Nom. capacity LV, MVA | 7,5 + 10,0 | 0.124 | 2.414 | 2.4 | 80 | 0.014 | 0 | 7.875 | 7.861
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.46 | 3.7 | 9.38 | 10 | -5.68 | 0 | 16.8 | 22.48 | 15.756 | open
| Nom. capacity MV, MVA | 16 | 0.206 | 2.366 | 9.09 |  | -6.724 | 0 | 16.8 | 23.524
| Nom. capacity LV, MVA | 16 | 0.254 | 1.334 | 0.29 | 120 | 1.044 | 0 | 16.8 | 15.756
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.072 | 2.772 | 8.25 | 120 | -5.478 | 0 | 6.615 | 12.093 | 7.02 | open
| Nom. capacity MV, MVA | 6.3 | 0.067 | 1.927 | 7 |  | -5.073 | 0 | 6.615 | 11.688
| Nom. capacity LV, MVA | 6.3 | 0.005 | 0.845 | 1.25 | 129 | -0.405 | 0 | 6.615 | 7.02
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.283 | 4.883 | 13.73 | 120 | -8.847 | 0 | 10.5 | 19.347 | 11.738 | open
| Nom. capacity MV, MVA | 10 | 0.283 | 3.683 | 11.2 |  | -7.517 | 0 | 10.5 | 18.017
| Nom. capacity LV, MVA | 10 | 0.092 | 1.292 | 2.53 | 120 | -1.238 | 0 | 10.5 | 11.738
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.582 | 11.072 | 12.9 | 120 | -1.828 | 0 | 26.25 | 28.078 | 21.321 | open
| Nom. capacity MV, MVA | 25 | 0.373 | 5.363 | 12.12 |  | -6.757 | 0 | 26.25 | 33.007
| Nom. capacity LV, MVA | 25 | 0.209 | 5.709 | 0.78 | 120 | 4.929 | 0 | 26.25 | 21.321
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.305 | 2.865 | 6.31 | 10 | -3.445 | 0 | 7.875 | 11.32 | 6.765 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.24 | 1.5 | 6.06 |  | -4.56 | 0 | 7.88 | 12.44
| Nom. capacity LV, MVA | 7,5 + 10,0 | 0.065 | 1.365 | 0.25 | 10 | 1.115 | 0 | 7.88 | 6.765
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.008 | 0.368 | 0.2 | 120 | 0.168 | 0 | 2.625 | 2.457 | 2.457 | open
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.023 | 0.473 | 0.37 | 120 | 0.103 | 0 | 1.68 | 1.577 | 1.577 | open
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 |  | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.062 | 0.262 | 1.43 | 120 | -1.168 | 0 | 1.68 | 2.848 | 2.848 | open
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.432 | 0.902 | 6.1 | 0 | -5.198 | 0 | 4.2 | 9.398 | 9.398 | open
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.0188 | 0.0988 | 0.15 | 120 | -0.0512 | 0 | 1.05 | 1.1012 | 1.1012 | open
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.076 | 1.126 | 0.29 | 120 | 0.836 | 0 | 2.625 | 1.789 | 1.789 | open
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.079 | 0.479 | 0.41 | 120 | 0.069 | 0 | 2.625 | 2.556 | 2.556 | open
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.55 | 1.92 | 0.4 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | open
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.462 | 1.012 | 0.22 | 120 | 0.792 | 0 | 1.68 | 0.888 | 0.888 | open
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.044 | 0.444 | 0.46 | 120 | -0.016 | 0 | 2.625 | 2.641 | 2.641 | open
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.025 | 0.425 | 0 | 0 | 0.425 | 0 | 4.2 | 3.775 | 3.775 | open
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.274 | 2.644 | 0.46 | 120 | 2.184 | 0 | 6.615 | 4.431 | 4.431 | open
77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.15 | 1.53 | 0.51 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | open
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.009 | 0.449 | 0.17 | 120 | 0.279 | 0 | 1.68 | 1.401 | 1.401 | open
79 | SS 35/10 Gorodok | 2 х 4,0 |  | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | open
80 | SS 35/10 Guevo | 2 х 2,5 | 0.024 | 1.224 | 1.69 | 20 | -0.466 | 0 | 2.625 | 3.091 | 3.091 | open
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.242 | 0.38 | 120 | -0.138 | 0 | 1.68 | 1.818 | 1.818 | open
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 3.555 | 3.5 | 0 | 0.055 | 0 | 2.625 | 2.57 | 2.57 | open
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.865 | 0.26 | 120 | 0.605 | 0 | 2.625 | 2.02 | 2.02 | open
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 10.4 | 2.5 | 0 | 7.9 | 0 | 10.5 | 2.6 | 2.6 | open
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.625 | 1.605 | 1.67 | 0 | -0.065 | 0 | 4.2 | 4.265 | 4.265 | open
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.159 | 1.059 | 0.93 | 45 | 0.129 | 0 | 1.68 | 1.551 | 1.551 | open
87 | SS 35/10 Ivanino | 2 х 6,3 | 0.09 | 2.38 | 2.69 | 80 | -0.31 | 0 | 6.615 | 6.925 | 6.925 | open
88 | SS 35/10 Kalinovka | 1,8 + 2,5 |  | 0.4 | 0.5 | 120 | -0.1 | 0 | 1.89 | 1.99 | 1.99 | open
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.345 | 0.52 | 120 | -0.175 | 0 | 1.68 | 1.855 | 1.855 | open
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 10.189 | 6.25 | 20 | 3.939 | 0 | 10.5 | 6.561 | 6.561 | open
91 | SS 35/10 Mixed fodder plant | 4,0+6,3 |  | 0.49 | 0 | 0 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | open
92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.083 | 3.183 | 0.21 | 120 | 2.973 | 0 | 6.615 | 3.642 | 3.642 | open
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 0.5 | 2.69 | 1.14 | 80 | 1.55 | 0 | 3.36 | 1.81 | 1.81 | open
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 2.77 | 7.12 | 1.56 | 80 | 5.56 | 0 | 4.2 | -1.36 | -1.36 | closed
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 |  | 0.62 | 0.24 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.664 | 0.42 | 120 | 1.244 | 0 | 1.89 | 0.646 | 0.646 | open
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.967 | 1.667 | 0.6 | 120 | 1.067 | 0 | 2.625 | 1.558 | 1.558 | open
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.003 | 0.143 | 0.17 | 120 | -0.027 | 0 | 2.625 | 2.652 | 2.652 | open
99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 4.525 | 4.5 | 80 | 0.025 | 0 | 10.5 | 10.475 | 10.475 | open
100 | SS 35/10 Kutok | 2 х 2,5 | 0.009 | 0.089 | 0.05 | 120 | 0.039 | 0 | 2.625 | 2.586 | 2.586 | open
101 | SS 35/10 Linets | 2 х 2,5 | 1.11 | 1.34 | 0.25 | 120 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | open
102 | SS 35/10 Luch | 2 х 6,3 | 0.336 | 3.366 | 0.23 | 120 | 3.136 | 0 | 6.615 | 3.479 | 3.479 | open
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.029 | 0.779 | 1.59 | 80 | -0.811 | 0 | 4.2 | 5.011 | 5.011 | open
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.02 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open
105 | SS 35/10 Mayak | 2 х 2,5 | 0.016 | 0.516 | 0.3 | 120 | 0.216 | 0 | 2.625 | 2.409 | 2.409 | open
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.18 | 1.45 | 1.7 | 80 | -0.25 | 0 | 4.2 | 4.45 | 4.45 | open
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.2 | 1.07 | 0.3 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | open
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.02 | 0.53 | 0.63 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 |  | 0.4 | 0.03 | 80 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open
110 | SS 35/10 Novaya | 2 х 2,5 | 0.262 | 1.462 | 0.4 | 120 | 1.062 | 0 | 2.625 | 1.563 | 1.563 | open
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.051 | 0.611 | 0.19 | 120 | 0.421 | 0 | 2.625 | 2.204 | 2.204 | open
112 | SS 35/10 Orlovka | 2 х 2,5 | 2.574 | 2.744 | 0.52 | 120 | 2.224 | 0 | 2.625 | 0.401 | 0.401 | open
113 | SS 35/10 Osotskoe | 2 х 2,5 |  | 0.18 | 0.2 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.212 | 1.472 | 0.74 | 120 | 0.732 | 0 | 4.2 | 3.468 | 3.468 | open
115 | SS 35/10 Panino | 2 х 2,5 | 0.02 | 0.3 | 0.11 | 80 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | open
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.066 | 0.686 | 0.52 | 120 | 0.166 | 0 | 2.625 | 2.459 | 2.459 | open
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.716 | 2.326 | 0.3 | 120 | 2.026 | 0 | 2.625 | 0.599 | 0.599 | open
118 | SS 35/10 Platava | 2 х 2,5 | 0.014 | 1.394 | 0.26 | 120 | 1.134 | 0 | 2.625 | 1.491 | 1.491 | open
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.237 | 0.46 | 120 | -0.223 | 0 | 1.68 | 1.903 | 1.903 | open
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.008 | 0.508 | 1.16 | 120 | -0.652 | 0 | 4.2 | 4.852 | 4.852 | open
121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | open
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.274 | 1.664 | 0.3 | 80 | 1.364 | 0 | 2.625 | 1.261 | 1.261 | open
123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.05 | 0.44 | 0.43 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.195 | 0.965 | 0.32 | 120 | 0.645 | 0 | 2.625 | 1.98 | 1.98 | open
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.583 | 0.963 | 0.44 | 120 | 0.523 | 0 | 2.625 | 2.102 | 2.102 | open
127 | SS 35/10 Razvetye | 2 х 4,0 | 0.421 | 2.331 | 1.03 | 120 | 1.301 | 0 | 4.2 | 2.899 | 2.899 | open
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.025 | 0.765 | 0.11 | 120 | 0.655 | 0 | 4.2 | 3.545 | 3.545 | open
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.076 | 0.356 | 0.29 | 120 | 0.066 | 0 | 1.68 | 1.614 | 1.614 | open
130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.058 | 1.308 | 1.18 | 80 | 0.128 | 0 | 2.625 | 2.497 | 2.497 | open
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.009 | 0.289 | 0.08 | 20 | 0.209 | 0 | 1.68 | 1.471 | 1.471 | open
132 | SS 35/10 Sapogovo | 2 х 2,5 | 0.361 | 1.751 | 0.6 | 20 | 1.151 | 0 | 2.625 | 1.474 | 1.474 | open
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.311 | 4.721 | 2.25 | 80 | 2.471 | 0 | 6.615 | 4.144 | 4.144 | open
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.038 | 2.128 | 1.4 | 45 | 0.728 | 0 | 4.2 | 3.472 | 3.472 | open
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.074 | 0.474 | 0 | - | 0.474 | 0 | 2.625 | 2.151 | 2.151 | open
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.079 | 0.589 | 0.6 | 120 | -0.011 | 0 | 2.625 | 2.636 | 2.636 | open
137 | SS 35/10 Snagost | 2 х 4,0 | 0.073 | 1.383 | 0.05 | 10 | 1.333 | 0 | 4.2 | 2.867 | 2.867 | open
138 | SS 35/10 SOM | 1,6 + 4,0 | 0.091 | 1.121 | 0.08 | 10 | 1.041 | 0 | 1.68 | 0.639 | 0.639 | open
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.12 | 0.89 | 0.69 | 120 | 0.2 | 0 | 3.36 | 3.16 | 3.16 | open
140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.075 | 0.725 | 0.58 | 80 | 0.145 | 0 | 2.625 | 2.48 | 2.48 | open
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.009 | 0.209 | 0.2 | 80 | 0.009 | 0 | 1.68 | 1.671 | 1.671 | open
142 | CC 35/10 Starshee | 2 х 1,6 | 0.014 | 0.254 | 0.2 | 120 | 0.054 | 0 | 1.68 | 1.626 | 1.626 | open
143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.11 | 2.13 | 1.08 | 45 | 1.05 | 0 | 4.2 | 3.15 | 3.15 | open
144 | SS 35/10 Turovka | 2 х 2,5 | 0.065 | 0.505 | 0.6 | 120 | -0.095 | 0 | 2.625 | 2.72 | 2.72 | open
145 | SS 35/10 Uspenka | 2 х 2,5 | 0.049 | 1.159 | 1 | 80 | 0.159 | 0 | 2.625 | 2.466 | 2.466 | open
146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0.005 | 22.445 | 5 |  | 17.445 | 0 | 26.25 | 8.805 | 8.805 | open
147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | open
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.085 | 0.465 | 0.21 | 80 | 0.255 | 0 | 2.625 | 2.37 | 2.37 | open
149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.112 | 0.3 | 120 | -0.188 | 0 | 2.625 | 2.813 | 2.813 | open
150 | SS 35/10 Elevator | 4,0 + 6,3 | 0.015 | 1.545 | 0.6 | 120 | 0.945 | 0 | 4.2 | 3.255 | 3.255 | open
151 | SS 35/10 Yugo-Zapadnaya | 1 х 10,0 | 2.35 | 10.78 | 4.7 | 80 | 6.08 | 0 | 10.5 | 4.42 | 4.42 | open
152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 0.053 | 2.513 | 3.9 | 120 | -1.387 | 0 | 2.625 | 4.012 | 4.012 | open
| TOTAL: | 3185.9 | 114.4801 | 876.4411 | 783.88 | [5 empty] | 1168.5789
| deficit | [9 empty] | -30.599
| proficit | [9 empty] | 1137.9799

## табл.1+табл.2
[9 empty] | table 1 | [12 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.81 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.49 | 1.08 | open | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.018 | 1.828 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.472 | 1.069 | open
| Nom. capacity MV, MVA | 6.3 | 1.22 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.08 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.011 | 1.231 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.069
| Nom. capacity MV, MVA | 6.3 | 0.59 | 4 | 1 day and night | 4 | 0 | 4 | 3.41 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.007 | 0.597 | 4 | 1 day and night | 4 | 0 | 4 | 3.403
2 | SS 110/10 Beketovo | 1*6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | open | 2 | SS 110/10 Beketovo | 1*6,3 | 2.461 | 2.791 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -0.641 | -0.641 | closed
3 | SS 110/35/10 Besedino | 1*6,3 | 3.34 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.46 | 0.52 | open | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.033 | 3.373 | 6.8 | 1 day and night | 6.8 | 0 | 6.8 | 3.427 | 0.52 | open
| Nom. capacity MV, MVA | 6.3 | 0.56 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.94 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 0.593 | 3.5 | 1 day and night | 3.5 | 0 | 3.5 | 2.907
| Nom. capacity LV, MVA | 6.3 | 2.78 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.52 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 2.78 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 0.52
4 | SS 110/10 Voskhod | 1*10,0 | 0.6 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.9 | 1.9 | open | 4 | SS 110/10 Voskhod | 1*10,0 | 0.061 | 0.661 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.839 | 1.839 | open
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.91 | 6 | 1 day and night | 6 | 0 | 6 | 5.09 | 1.39 | open | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.037 | 0.947 | 6 | 1 day and night | 6 | 0 | 6 | 5.053 | 1.353 | open
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 1 day and night | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.91 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.39 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.037 | 0.947 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.353
6 | SS 110/35/10 Zhukovka | 1*10,0 | 1.22 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.94 | 0.47 | open | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.091 | 1.311 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.849 | 0.47 | open
| Nom. capacity MV, MVA | 10 | 1.03 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.47 |  |  |  | Nom. capacity MV, MVA | 10 | 0.091 | 1.121 | 4.5 | 1 day and night | 4.5 | 0 | 4.5 | 3.379
| Nom. capacity LV, MVA | 10 | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47 |  |  |  | Nom. capacity LV, MVA | 10 |  | 0.19 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.47
7 | SS 110/10 Zabelye | 1*2,5 | 0.3 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.85 | 1.85 | open | 7 | SS 110/10 Zabelye | 1*2,5 | 0.028 | 0.328 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.822 | 1.822 | open
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | open | 8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.4 | 0.45 | 1 day and night | 0.45 | 0 | 0.45 | 0.05 | 0.05 | open
9 | SS 110/35/10 Lachinovo | 1*10,0 | 1.4 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.73 | 1.13 | open | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.49 | 1.89 | 5.13 | 1 day and night | 5.13 | 0 | 5.13 | 3.24 | 0.64 | open
| Nom. capacity MV, MVA | 10 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1 | 3.6 | 1 day and night | 3.6 | 0 | 3.6 | 2.6
| Nom. capacity LV, MVA | 10 | 0.4 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 1.13 |  |  |  | Nom. capacity LV, MVA | 10 | 0.49 | 0.89 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.64
10 | SS 110/10 Malaya Loknya | 1*10,0 | 1.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.2 | 0.2 | open | 10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.014 | 1.214 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.186 | 0.186 | open
11 | SS 110/35/10 Maritsa | 1*2,5 | 1.65 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.27 | 0.27 | open | 11 | SS 110/35/10 Maritsa | 1*6,3 | 0.025 | 1.675 | 1.92 | 1 day and night | 1.92 | 0 | 1.92 | 0.245 | 0.245 | open
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.55 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.34 | 2.04 | open | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.019 | 0.569 | 5.89 | 1 day and night | 5.89 | 0 | 5.89 | 5.321 | 2.04 | open
| Nom. capacity MV, MVA | 6.3 | 0.44 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.3 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.019 | 0.459 | 3.74 | 1 day and night | 3.74 | 0 | 3.74 | 3.281
| Nom. capacity LV, MVA | 6.3 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.03 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.37 | 1.37 | open | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.033 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.367 | 1.367 | open
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 6.46 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | 0.18 | 0.18 | open | 14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.7 | 12.16 | 6.64 | 1 day and night | 6.64 | 0 | 6.64 | -5.52 | -5.52 | closed
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.43 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 5.07 | 0.64 | open | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 1.638 | 4.068 | 7.5 | 1 day and night | 7.5 | 0 | 7.5 | 3.432 | 0.601 | open
| Nom. capacity MV, MVA | 10 | 1.97 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 4.43 |  |  |  | Nom. capacity MV, MVA | 10 | 1.599 | 3.569 | 6.4 | 1 day and night | 6.4 | 0 | 6.4 | 2.831
| Nom. capacity LV, MVA | 10 | 0.46 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.64 |  |  |  | Nom. capacity LV, MVA | 10 | 0.039 | 0.499 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.601
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.53 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.27 | 0.27 | open | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.573 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.227 | 0.227 | open
17 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.45 | 0.45 | open | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.195 | 0.695 | 0.95 | 1 day and night | 0.95 | 0 | 0.95 | 0.255 | 0.255 | open
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | open | 18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.23 | 0.68 | 1 day and night | 0.68 | 0 | 0.68 | 0.45 | 0.45 | open
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.24 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.19 | 1.19 | open | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.015 | 0.255 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.175 | 1.175 | open
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.56 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.78 | 0.78 | open | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.037 | 0.597 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.743 | 0.743 | open
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.79 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.17 | 0.17 | open | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 |  | 0.79 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.17 | 0.17 | open
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.76 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 2.07 | 2.07 | open | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.246 | 1.006 | 2.83 | 1 day and night | 2.83 | 0 | 2.83 | 1.824 | 1.824 | open
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.36 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.28 | 0.28 | open | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.02 | 0.38 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.26 | 0.26 | open
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.46 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.97 | 0.97 | open | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.135 | 0.595 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.835 | 0.835 | open
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.28 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.87 | 1.87 | open | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.015 | 0.295 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.855 | 1.855 | open
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.5 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 1.26 | 1.26 | open | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.274 | 0.774 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.986 | 0.986 | open
27 | SS 35/10 Biryukovka | 1х1,6 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open | 27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.26 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.41 | 0.41 | open | 28 | SS 35/10 Bobrovka | 1 х 1,6 |  | 0.26 | 0.67 | 1 day and night | 0.67 | 0 | 0.67 | 0.41 | 0.41 | open
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open | 29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.4 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.36 | 0.36 | open
30 | SS 35/10 Budki | 1 х 1,0 | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | open | 30 | SS 35/10 Budki | 1 х 1,0 |  | 0.14 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.6 | 0.6 | open
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.66 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.94 | 0.94 | open | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.037 | 0.697 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.903 | 0.903 | open
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.22 | 1 | 1 day and night | 1 | 0 | 1 | 0.78 | 0.78 | open | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.045 | 0.265 | 1 | 1 day and night | 1 | 0 | 1 | 0.735 | 0.735 | open
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.28 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.15 | 1.15 | open | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.04 | 0.32 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.11 | 1.11 | open
34 | SS 35/10 Bykovo | 1 х 4,0 | 0.89 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.54 | 0.54 | open | 34 | SS 35/10 Bykovo | 1 х 4,0 | 3.813 | 4.703 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | -3.273 | -3.273 | closed
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | open | 35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.11 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 2.04 | 2.04 | open
36 | SS 35/10 Vanino | 1 х 2,5 | 0.24 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.56 | 0.56 | open | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.068 | 0.308 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.492 | 0.492 | open
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.6 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.45 | 0.45 | open | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.035 | 0.635 | 1.05 | 1 day and night | 1.05 | 0 | 1.05 | 0.415 | 0.415 | open
38 | SS 35/10 Water storage | 1 х 4,0 | 1.76 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | 0.96 | 0.96 | open | 38 | SS 35/10 Water storage | 1 х 4,0 | 3.545 | 5.305 | 2.72 | 1 day and night | 2.72 | 0 | 2.72 | -2.585 | -2.585 | closed
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | open | 39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.8 | 0.8 | open
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.72 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.18 | 0.18 | open | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.734 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.166 | 0.166 | open
41 | SS 35/10 Voronok | 1 х 4,0 | 0.82 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.28 | 1.28 | open | 41 | SS 35/10 Voronok | 1 х 4,0 | 0.013 | 0.833 | 2.1 | 1 day and night | 2.1 | 0 | 2.1 | 1.267 | 1.267 | open
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.45 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.7 | 1.7 | open | 42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.032 | 0.482 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.668 | 1.668 | open
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.59 | 1.59 | open | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.57 | 1.57 | open
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.21 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.29 | 1.29 | open | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.01 | 0.22 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 1.28 | 1.28 | open
45 | SS 35/10 Glazovo | 1 х 2,5 | 1.26 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.24 | 0.24 | open | 45 | SS 35/10 Glazovo | 1 х 2,5 | 0.02 | 1.28 | 1.5 | 1 day and night | 1.5 | 0 | 1.5 | 0.22 | 0.22 | open
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.53 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.87 | 0.87 | open | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.018 | 0.548 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 0.852 | 0.852 | open
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.3 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.4 | 0.4 | open | 47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.07 | 0.37 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.33 | 0.33 | open
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.57 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.19 | 0.19 | open | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.044 | 0.614 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.146 | 0.146 | open
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.5 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.6 | 0.6 | open | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.025 | 0.525 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.575 | 0.575 | open
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | open | 50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.85 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.58 | 0.58 | open
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.96 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.47 | 0.47 | open | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.042 | 1.002 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 0.428 | 0.428 | open
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.61 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.24 | 2.24 | open | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.019 | 0.629 | 2.85 | 1 day and night | 2.85 | 0 | 2.85 | 2.221 | 2.221 | open
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.26 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.68 | 0.68 | open | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.009 | 0.269 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.671 | 0.671 | open
54 | SS 35/10 Daryino | 1 х 2,5 | 0.4 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.4 | 1.4 | open | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.038 | 0.438 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.362 | 1.362 | open
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.61 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.19 | 0.19 | open | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.05 | 0.66 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.14 | 0.14 | open
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.33 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.74 | 0.74 | open | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.03 | 0.36 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 0.71 | 0.71 | open
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.3 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.55 | 0.55 | open | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.045 | 0.345 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.505 | 0.505 | open
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.36 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.79 | 1.79 | open | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.011 | 0.371 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.779 | 1.779 | open
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.49 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.35 | 0.35 | open | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.043 | 0.533 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.307 | 0.307 | open
60 | SS 35/10 Znamenka | 1 х 1,8 | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | open | 60 | SS 35/10 Znamenka | 1 х 1,8 |  | 1.01 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.14 | 1.14 | open
61 | SS 35/10 Iskra | 1 х 2,5 | 0.2 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.38 | 0.38 | open | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.048 | 0.248 | 0.58 | 1 day and night | 0.58 | 0 | 0.58 | 0.332 | 0.332 | open
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.41 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.39 | 0.39 | open | 62 | SS 35/10 Kazanka | 1 х 4,0 | 0.009 | 0.419 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.381 | 0.381 | open
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.13 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.67 | 1.67 | open | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.06 | 0.19 | 1.8 | 1 day and night | 1.8 | 0 | 1.8 | 1.61 | 1.61 | open
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.31 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.33 | 0.33 | open | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.01 | 0.32 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.32 | 0.32 | open
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.28 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.46 | 0.46 | open | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.257 | 0.537 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.203 | 0.203 | open
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.64 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.89 | 0.89 | open | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.031 | 0.671 | 1.53 | 1 day and night | 1.53 | 0 | 1.53 | 0.859 | 0.859 | open
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | open | 67 | SS 35/10 Kolontaevka | 1 х 2,5 |  | 0.55 | 0.84 | 1 day and night | 0.84 | 0 | 0.84 | 0.29 | 0.29 | open
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.55 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.87 | 0.87 | open | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.024 | 0.574 | 1.42 | 1 day and night | 1.42 | 0 | 1.42 | 0.846 | 0.846 | open
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.55 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.21 | 0.21 | open | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.017 | 0.567 | 0.76 | 1 day and night | 0.76 | 0 | 0.76 | 0.193 | 0.193 | open
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | open | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.264 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.166 | 1.166 | open
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.64 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.19 | 0.19 | open | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.035 | 0.675 | 0.83 | 1 day and night | 0.83 | 0 | 0.83 | 0.155 | 0.155 | open
72 | SS 35/10 Lobazovka | 1 х 2,5 | 1.06 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.03 | 0.03 | open | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.011 | 1.071 | 1.09 | 1 day and night | 1.09 | 0 | 1.09 | 0.019 | 0.019 | open
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.58 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.71 | 0.71 | open | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.035 | 0.615 | 1.29 | 1 day and night | 1.29 | 0 | 1.29 | 0.675 | 0.675 | open
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.32 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.83 | 0.83 | open | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0.017 | 0.337 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.813 | 0.813 | open
75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.96 | 0.96 | open | 75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.041 | 0.041 | 0.96 | 1 day and night | 0.96 | 0 | 0.96 | 0.919 | 0.919 | open
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | open | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.059 | 0.659 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.441 | 0.441 | open
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.76 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.52 | 0.52 | open | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.015 | 0.775 | 1.28 | 1 day and night | 1.28 | 0 | 1.28 | 0.505 | 0.505 | open
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.3 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.89 | 0.89 | open | 78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.01 | 0.31 | 1.19 | 1 day and night | 1.19 | 0 | 1.19 | 0.88 | 0.88 | open
79 | SS 35/10 Markovo | 1 х 2,5 | 0.68 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.12 | 0.12 | open | 79 | SS 35/10 Markovo | 1 х 2,5 | 0.01 | 0.69 | 0.8 | 1 day and night | 0.8 | 0 | 0.8 | 0.11 | 0.11 | open
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.23 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.1 | 1.1 | open | 80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.015 | 0.245 | 1.33 | 1 day and night | 1.33 | 0 | 1.33 | 1.085 | 1.085 | open
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.99 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.16 | 1.16 | open | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.013 | 1.003 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.147 | 1.147 | open
82 | SS 35/10 Mokva | 1 х 4,0 | 0.56 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.59 | 1.59 | open | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.057 | 0.617 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.533 | 1.533 | open
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.6 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.5 | 0.5 | open | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.033 | 0.633 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.467 | 0.467 | open
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | open | 84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.42 | 0.9 | 1 day and night | 0.9 | 0 | 0.9 | 0.48 | 0.48 | open
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | open | 85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.001 | 1.07 | 1 day and night | 1.07 | 0 | 1.07 | 1.069 | 1.069 | open
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | open | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.08 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | 4.22 | 4.22 | open
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 1.1 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.05 | 1.05 | open | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.014 | 1.114 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.036 | 1.036 | open
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.04 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.36 | 1.36 | open | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.048 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.352 | 1.352 | open
89 | SS 35/10 Niva | 1 х 2,5 | 0.4 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.16 | 1.16 | open | 89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.415 | 1.56 | 1 day and night | 1.56 | 0 | 1.56 | 1.145 | 1.145 | open
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.5 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.47 | 0.47 | open | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0.13 | 0.63 | 0.97 | 1 day and night | 0.97 | 0 | 0.97 | 0.34 | 0.34 | open
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.49 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.15 | 0.15 | open | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.08 | 0.57 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.07 | 0.07 | open
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 1.46 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 1.51 | 1.51 | open | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.952 | 2.412 | 2.97 | 1 day and night | 2.97 | 0 | 2.97 | 0.558 | 0.558 | open
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.6 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.72 | 1.72 | open | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.42 | 1.02 | 2.32 | 1 day and night | 2.32 | 0 | 2.32 | 1.3 | 1.3 | open
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | open | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.15 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.25 | 1.25 | open
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 |  | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.33 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.82 | 1.82 | open | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0.158 | 0.488 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.662 | 1.662 | open
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | open | 97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.04 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.7 | 0.7 | open
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.19 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.96 | 1.96 | open | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.015 | 0.205 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.945 | 1.945 | open
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.35 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.8 | 1.8 | open | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.359 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.791 | 1.791 | open
100 | SS 35/10 Pristen | 1 х 4,0 | 2.2 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.1 | 1.1 | open | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.097 | 2.297 | 3.3 | 1 day and night | 3.3 | 0 | 3.3 | 1.003 | 1.003 | open
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.74 | 0.74 | open | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.018 | 0.018 | 0.74 | 1 day and night | 0.74 | 0 | 0.74 | 0.722 | 0.722 | open
102 | SS 35/10 Reut | 1 х 2,5 | 0.44 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.66 | 0.66 | open | 102 | SS 35/10 Reut | 1 х 2,5 | 0.916 | 1.356 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | -0.256 | -0.256 | closed
103 | SS 35/10 Rovenka | 1 х 1,6 | 1.16 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.44 | 0.44 | open | 103 | SS 35/10 Rovenka | 1 х 1,6 | 1.385 | 2.545 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | -0.945 | -0.945 | closed
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.18 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.52 | 0.52 | open | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.033 | 0.213 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.487 | 0.487 | open
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.38 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.92 | 1.92 | open | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 |  | 0.38 | 2.3 | 1 day and night | 2.3 | 0 | 2.3 | 1.92 | 1.92 | open
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.4 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.91 | 0.91 | open | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.018 | 0.418 | 1.31 | 1 day and night | 1.31 | 0 | 1.31 | 0.892 | 0.892 | open
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.19 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.24 | 1.24 | open | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.214 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.216 | 1.216 | open
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.42 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.52 | 0.52 | open | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.044 | 0.464 | 0.94 | 1 day and night | 0.94 | 0 | 0.94 | 0.476 | 0.476 | open
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.53 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.62 | 0.62 | open | 109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.023 | 0.553 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.597 | 0.597 | open
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | open | 110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.3 | 1.25 | 1 day and night | 1.25 | 0 | 1.25 | 0.95 | 0.95 | open
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.3 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.4 | 2.4 | open | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0.009 | 0.309 | 2.7 | 1 day and night | 2.7 | 0 | 2.7 | 2.391 | 2.391 | open
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.25 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.18 | 1.18 | open | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.058 | 0.308 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.122 | 1.122 | open
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.81 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.95 | 0.95 | open | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.09 | 0.9 | 1.76 | 1 day and night | 1.76 | 0 | 1.76 | 0.86 | 0.86 | open
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.28 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.82 | 0.82 | open | 114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.003 | 0.283 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.817 | 0.817 | open
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.2 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.2 | 1.2 | open | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.008 | 0.208 | 1.4 | 1 day and night | 1.4 | 0 | 1.4 | 1.192 | 1.192 | open
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.35 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.95 | 0.95 | open | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.038 | 0.388 | 1.3 | 1 day and night | 1.3 | 0 | 1.3 | 0.912 | 0.912 | open
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.6 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.74 | 0.74 | open | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.015 | 0.615 | 1.34 | 1 day and night | 1.34 | 0 | 1.34 | 0.725 | 0.725 | open
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.54 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.17 | 0.17 | open | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.009 | 0.549 | 0.71 | 1 day and night | 0.71 | 0 | 0.71 | 0.161 | 0.161 | open
119 | SS 35/10 Telmana | 1 х 2,5 | 0.41 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.74 | 0.74 | open | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.025 | 0.435 | 1.15 | 1 day and night | 1.15 | 0 | 1.15 | 0.715 | 0.715 | open
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | open | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.035 | 0.395 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.035 | 1.035 | open
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.07 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.63 | 0.63 | open | 121 | SS 35/10 Fateevka | 1 х 2,5 | 0.008 | 0.078 | 0.7 | 1 day and night | 0.7 | 0 | 0.7 | 0.622 | 0.622 | open
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.18 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.54 | 1.54 | open | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.025 | 0.205 | 1.72 | 1 day and night | 1.72 | 0 | 1.72 | 1.515 | 1.515 | open
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.34 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.76 | 0.76 | open | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.017 | 0.357 | 1.1 | 1 day and night | 1.1 | 0 | 1.1 | 0.743 | 0.743 | open
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | open | 124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.07 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.78 | 0.78 | open
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.36 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.07 | 1.07 | open | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.033 | 0.393 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.037 | 1.037 | open
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.16 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.27 | 1.27 | open | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.019 | 0.179 | 1.43 | 1 day and night | 1.43 | 0 | 1.43 | 1.251 | 1.251 | open
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.58 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.89 | 0.89 | open | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.023 | 0.603 | 1.47 | 1 day and night | 1.47 | 0 | 1.47 | 0.867 | 0.867 | open
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | open | 128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.18 | 0.85 | 1 day and night | 0.85 | 0 | 0.85 | 0.67 | 0.67 | open
129 | SS 35/10 Elevator | 1х6,3 | 0.21 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.39 | 0.39 | open | 129 | SS 35/10 Elevator | 1х6,3 | 0.02 | 0.23 | 0.6 | 1 day and night | 0.6 | 0 | 0.6 | 0.37 | 0.37 | open
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.24 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.4 | 0.4 | open | 130 | SS 35/10 Yankovo | 1 х 1,6 |  | 0.24 | 0.64 | 1 day and night | 0.64 | 0 | 0.64 | 0.4 | 0.4 | open
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | 1.67 | 1.67 | open | 131 | SS 35/10 Yasenki | 1 х 2,5 | 3.49 | 3.97 | 2.15 | 1 day and night | 2.15 | 0 | 2.15 | -1.82 | -1.82 | closed
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | open | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 7.88 | 0 | 0 | 7.88 | 0 | 26.25 | 18.37 | 18.37 | open
2 | SS 110/10 ARZ | 6,3+10,0 | 1.78 | 0.9 | 45 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | open | 2 | SS 110/10 ARZ | 6,3+10,0 |  | 1.78 | 0.9 | 45 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | open
3 | SS 110/35/10 Atomgrad | 2*25 | 11.72 | 20.2 | 120 | -8.48 | 0 | 26.25 | 34.73 | 27.68 | open | 3 | SS 110/35/10 Atomgrad | 2*25 | 0.327 | 12.047 | 20.2 | 120 | -8.153 | 0 | 26.25 | 34.403 | 27.593 | open
| Nom. capacity MV, MVA | 25 | 3.55 | 10.6 | 120 | -7.05 | 0 | 26.25 | 33.3 |  |  |  | Nom. capacity MV, MVA | 25 | 0.24 | 3.79 | 10.6 | 120 | -6.81 | 0 | 26.25 | 33.06
| Nom. capacity lV, MVA | 25 | 8.17 | 9.6 | 120 | -1.43 | 0 | 26.25 | 27.68 |  |  |  | Nom. capacity lV, MVA | 25 | 0.087 | 8.257 | 9.6 | 120 | -1.343 | 0 | 26.25 | 27.593
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.83 | 0.6 | 120 | 0.23 | 0 | 6.615 | 6.385 | 6.385 | open | 4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.015 | 0.845 | 0.6 | 120 | 0.245 | 0 | 6.615 | 6.37 | 6.37 | open
5 | SS 110/35/10 Basovo | 5,6+10,0 | 1.32 | 6.19 | 15 | -4.87 | 0 | 5.88 | 10.75 | 5.34 | open | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.023 | 1.343 | 6.19 | 15 | -4.847 | 0 | 5.88 | 10.727 | 5.328 | open
| Nom. capacity MV, MVA | 5,6+10,0 | 0.59 | 6 |  | -5.41 | 0 | 5.88 | 11.29 |  |  |  | Nom. capacity MV, MVA | 5,6+10,0 | 0.011 | 0.601 | 6 |  | -5.399 | 0 | 5.88 | 11.279
| Nom. capacity LV, MVA | 5,6+10,0 | 0.73 | 0.19 | 120 | 0.54 | 0 | 5.88 | 5.34 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.012 | 0.742 | 0.19 | 120 | 0.552 | 0 | 5.88 | 5.328
6 | SS 110/35/10 Belaya | 2*16,0 | 7.1 | 12 | 120 | -4.9 | 0 | 16.8 | 21.7 | 13.6 | open | 6 | SS 110/35/10 Belaya | 2*16,0 | 1.174 | 8.274 | 12 | 120 | -3.726 | 0 | 16.8 | 20.526 | 12.849 | open
| Nom. capacity MV, MVA | 16 | 3.2 | 0 |  | 3.2 | 0 | 16.8 | 13.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.751 | 3.951 | 0 |  | 3.951 | 0 | 16.8 | 12.849
| Nom. capacity LV, MVA | 16 | 3.9 | 12 | 120 | -8.1 | 0 | 16.8 | 24.9 |  |  |  | Nom. capacity LV, MVA | 16 | 0.423 | 4.323 | 12 | 120 | -7.677 | 0 | 16.8 | 24.477
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.6 | 1.3 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.015 | open | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.041 | 1.641 | 1.3 | 120 | 0.341 | 0 | 6.615 | 6.274 | 6.011 | open
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.004 | 0.604 |  |  | 0.604 | 0 | 6.615 | 6.011
| Nom. capacity LV, MVA | 6.3 | 1 | 1.3 | 120 | -0.3 | 0 | 6.615 | 6.915 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.037 | 1.037 | 1.3 | 120 | -0.263 | 0 | 6.615 | 6.878
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.57 | 1.17 | 45 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | open | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.05 | 2.62 | 1.17 | 45 | 1.45 | 0 | 2.625 | 1.175 | 1.175 | open
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 41.48 | 16.8 | 0 | 24.68 | 0 | 84.525 | 59.845 | 58.045 | open | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.566 | 43.046 | 16.8 | 0 | 26.246 | 0 | 84.525 | 58.279 | 57.961 | open
| Nom. capacity MV, MVA | 40,0+2*40,5 | 15 | 16.8 | 0 | -1.8 | 0 | 84.525 | 86.325 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 1.482 | 16.482 | 16.8 | 0 | -0.318 | 0 | 84.525 | 84.843
| Nom. capacity MV, MVA | 40,0+2*40,5 | 26.48 | 0 | 0 | 26.48 | 0 | 84.525 | 58.045 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.084 | 26.564 | 0 | 0 | 26.564 | 0 | 84.525 | 57.961
10 | SS 110/10 Vysokaya* | 2*16,0 | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | closed | 10 | SS 110/10 Vysokaya* | 2*16,0 |  | 27.17 | 3.2 | 15 | 23.97 | 0 | 16.8 | -7.17 | -7.17 | closed
11 | SS 110/35/10 Glushkovo | 2*10,0 | 6.23 | 8.04 | 120 | -1.81 | 0 | 10.5 | 12.31 | 8.67 | open | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 1.5325 | 7.7625 | 8.04 | 120 | -0.2775 | 0 | 10.5 | 10.7775 | 8.6645 | open
| Nom. capacity MV, MVA | 10 | 2.96 | 6.6 | 120 | -3.64 | 0 | 10.5 | 14.14 |  |  |  | Nom. capacity MV, MVA | 10 | 1.527 | 4.487 | 6.6 | 120 | -2.113 | 0 | 10.5 | 12.613
| Nom. capacity LV, MVA | 10 | 3.27 | 1.44 | 80 | 1.83 | 0 | 10.5 | 8.67 |  |  |  | Nom. capacity LV, MVA | 10 | 0.0055 | 3.2755 | 1.44 | 80 | 1.8355 | 0 | 10.5 | 8.6645
12 | SS 110/10 Gorodskaya | 2*25,0 | 12.72 | 0 | 0 | 12.72 | 0 | 26.25 | 13.53 | 13.53 | open | 12 | SS 110/10 Gorodskaya | 2*25,0 | 4.53 | 17.25 | 0 | 0 | 17.25 | 0 | 26.25 | 9 | 9 | open
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 8 | 6.52 | 120 | 1.48 | 0 | 10.5 | 9.02 | 7.61 | open | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 11.704 | 19.704 | 6.52 | 120 | 13.184 | 0 | 10.5 | -2.684 | -2.684 | closed
| Nom. capacity MV, MVA | 10+16,0 | 4.65 | 6.06 |  | -1.41 | 0 | 10.5 | 11.91 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 11.275 | 15.925 | 6.06 |  | 9.865 | 0 | 10.5 | 0.635
| Nom. capacity LV, MVA | 10+16,0 | 3.35 | 0.46 | 120 | 2.89 | 0 | 10.5 | 7.61 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.429 | 3.779 | 0.46 | 120 | 3.319 | 0 | 10.5 | 7.181
14 | SS 110/35/10 Dmitriev | 2*10,0 | 5.94 | 10.4 | 120 | -4.46 | 0 | 10.5 | 14.96 | 9.97 | open | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 0.267 | 6.207 | 10.4 | 120 | -4.193 | 0 | 10.5 | 14.693 | 9.727 | open
| Nom. capacity MV, MVA | 10 | 2.41 | 7.4 |  | -4.99 | 0 | 10.5 | 15.49 |  |  |  | Nom. capacity MV, MVA | 10 | 0.024 | 2.434 | 7.4 |  | -4.966 | 0 | 10.5 | 15.466
| Nom. capacity LV, MVA | 10 | 3.53 | 3 | 80 | 0.53 | 0 | 10.5 | 9.97 |  |  |  | Nom. capacity LV, MVA | 10 | 0.243 | 3.773 | 3 | 80 | 0.773 | 0 | 10.5 | 9.727
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.9 | 0.5 | 120 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | open | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.917 | 0.5 | 120 | 0.417 | 0 | 10.5 | 10.083 | 10.083 | open
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 7.52 | 22.1 | 80 | -14.58 | 0 | 26.25 | 40.83 | 25.21 | open | 16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.33 | 7.85 | 22.1 | 80 | -14.25 | 0 | 26.25 | 40.5 | 24.978 | open
| Nom. capacity MV, MVA | 25 | 3.18 | 18.8 |  | -15.62 | 0 | 26.25 | 41.87 |  |  |  | Nom. capacity MV, MVA | 25 | 0.098 | 3.278 | 18.8 |  | -15.522 | 0 | 26.25 | 41.772
| Nom. capacity LV, MVA | 25 | 4.34 | 3.3 | 120 | 1.04 | 0 | 26.25 | 25.21 |  |  |  | Nom. capacity LV, MVA | 25 | 0.232 | 4.572 | 3.3 | 120 | 1.272 | 0 | 26.25 | 24.978
17 | SS 110/35/10 Kamyshi | 2*6,3 | 12.08 | 5.45 | 20 | 6.63 | 0 | 6.615 | -0.015 | -0.305 | closed | 17 | SS 110/35/10 Kamyshi | 2*6,3 | 4.129 | 16.209 | 5.45 | 20 | 10.759 | 0 | 6.615 | -4.144 | -4.345 | closed
| Nom. capacity MV, MVA | 6.3 | 10.37 | 3.45 |  | 6.92 | 0 | 6.615 | -0.305 |  |  |  | Nom. capacity MV, MVA | 6.3 | 4.04 | 14.41 | 3.45 |  | 10.96 | 0 | 6.615 | -4.345
| Nom. capacity LV, MVA | 6.3 | 1.71 | 2 | 20 | -0.29 | 0 | 6.615 | 6.905 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.089 | 1.799 | 2 | 20 | -0.201 | 0 | 6.615 | 6.816
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 12.92 | 6.97 | 120 | 5.95 | 0 | 15.75 | 9.8 | 9.8 | open | 18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.46 | 13.38 | 6.97 | 120 | 6.41 | 0 | 15.75 | 9.34 | 9.34 | open
| Nom. capacity MV, MVA | 15,0+16,0 | 9.88 | 6.6 |  | 3.28 | 0 | 15.75 | 12.47 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.362 | 10.242 | 6.6 |  | 3.642 | 0 | 15.75 | 12.108
| Nom. capacity LV, MVA | 15,0+16,0 | 3.04 | 0.37 | 120 | 2.67 | 0 | 15.75 | 13.08 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.098 | 3.138 | 0.37 | 120 | 2.768 | 0 | 15.75 | 12.982
19 | SS 110/35/10 Kilikino | 2*16,0 | 2.41 | 4.5 | 120 | -2.09 | 0 | 16.8 | 18.89 | 17.15 | open | 19 | SS 110/35/10 Kilikino | 2*16,0 | 0.0948 | 2.5048 | 4.5 | 120 | -1.9952 | 0 | 16.8 | 18.7952 | 17.0552 | open
| Nom. capacity MV, MVA | 16 | 2.25 | 2.6 |  | -0.35 | 0 | 16.8 | 17.15 |  |  |  | Nom. capacity MV, MVA | 16 | 0.0948 | 2.3448 | 2.6 |  | -0.2552 | 0 | 16.8 | 17.0552
| Nom. capacity LV, MVA | 16 | 0.16 | 1.9 | 120 | -1.74 | 0 | 16.8 | 18.54 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.16 | 1.9 | 120 | -1.74 | 0 | 16.8 | 18.54
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 52.37 | 16.36 | 120 | 36.01 | 0 | 42 | 5.99 | 5.99 | open | 20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.67 | 55.04 | 16.36 | 120 | 38.68 | 0 | 42 | 3.32 | 3.32 | open
| Nom. capacity MV, MVA | 40 | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73 |  |  |  | Nom. capacity MV, MVA | 40 |  | 28.33 | 13.06 | 120 | 15.27 | 0 | 42 | 26.73
| Nom. capacity LV, MVA | 40 | 24.03 | 3.3 | 120 | 20.73 | 0 | 42 | 21.27 |  |  |  | Nom. capacity LV, MVA | 40 | 2.67 | 26.7 | 3.3 | 120 | 23.4 | 0 | 42 | 18.6
21 | SS 110/35/10 Klyukva | 2*16,0 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | open | 21 | SS 110/35/10 Klyukva | 2*16,0 | 0.421 | 4.121 | 1.2 | 120 | 2.921 | 0 | 16.8 | 13.879 | 13.879 | open
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  | 2: Nom. capacity MV, MVA; 3: 16; 5: 0; Min 8: 0; Min 9: 0; Min 10: 16.8; Min 11: 16.8
| Nom. capacity LV, MVA | 16 | 3.7 | 1.2 | 120 | 2.5 | 0 | 16.8 | 14.3 |  |  |  | Nom. capacity LV, MVA | 16 | 0.421 | 4.121 | 1.2 | 120 | 2.921 | 0 | 16.8 | 13.879
22 | SS 110/10 Kompressornaya | 2*40,0 | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | open | 22 | SS 110/10 Kompressornaya | 2*40,0 |  | 6.37 | 0 | 0 | 6.37 | 0 | 42 | 35.63 | 35.63 | open
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 10.28 | 8 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.18 | open | 23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.1 | 11.38 | 8 | 120 | 3.38 | 0 | 10.5 | 7.12 | 7.12 | open
| Nom. capacity MV, MVA | 10,0+16,0 | 8.22 | 5.9 |  | 2.32 | 0 | 10.5 | 8.18 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.111 | 8.331 | 5.9 |  | 2.431 | 0 | 10.5 | 8.069
| Nom. capacity LV, MVA | 10,0+16,0 | 2.06 | 2.1 |  | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.989 | 3.049 | 2.1 |  | 0.949 | 0 | 10.5 | 9.551
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 10.27 | 4.1 | 0 | 6.17 | 0 | 10.5 | 4.33 | 4.33 | open | 24 | SS 110/10 Kotelnaya | 10,0+25,0 | 3.621 | 13.891 | 4.1 | 0 | 9.791 | 0 | 10.5 | 0.709 | 0.709 | open
25 | SS 110/35/10 Kshen | 2*10,0 | 9.69 | 6.63 | 10 | 3.06 | 0 | 10.5 | 7.44 | 5.94 | open | 25 | SS 110/35/10 Kshen | 2*10,0 | 1.998 | 11.688 | 6.63 | 10 | 5.058 | 0 | 10.5 | 5.442 | 4.458 | open
| Nom. capacity MV, MVA | 10 | 4.56 | 6.06 |  | -1.5 | 0 | 10.5 | 12 |  |  |  | Nom. capacity MV, MVA | 10 | 0.516 | 5.076 | 6.06 |  | -0.984 | 0 | 10.5 | 11.484
| Nom. capacity LV, MVA | 10 | 5.13 | 0.57 | 120 | 4.56 | 0 | 10.5 | 5.94 |  |  |  | Nom. capacity LV, MVA | 10 | 1.482 | 6.612 | 0.57 | 120 | 6.042 | 0 | 10.5 | 4.458
26 | SS 110/6 Lesnaya | 2*40,0 | 2.34 | 0 | 0 | 2.34 | 0 | 42 | 39.66 | 39.66 | open | 26 | SS 110/6 Lesnaya | 2*40,0 | 0.9 | 3.24 | 0 | 0 | 3.24 | 0 | 42 | 38.76 | 38.76 | open
27 | SS 110/35/10 Lgov | 2*25,0 | 13.76 | 4 | 120 | 9.76 | 0 | 26.25 | 16.49 | 16.49 | open | 27 | SS 110/35/10 Lgov | 2*25,0 | 0.375 | 14.135 | 4 | 120 | 10.135 | 0 | 26.25 | 16.115 | 16.115 | open
| Nom. capacity MV, MVA | 25 | 2.07 |  |  | 2.07 | 0 | 26.25 | 24.18 |  |  |  | Nom. capacity MV, MVA | 25 | 0 | 2.07 |  |  | 2.07 | 0 | 26.25 | 24.18
| Nom. capacity LV, MVA | 25 | 11.69 | 4 | 120 | 7.69 | 0 | 26.25 | 18.56 |  |  |  | Nom. capacity LV, MVA | 25 | 0.375 | 12.065 | 4 | 120 | 8.065 | 0 | 26.25 | 18.185
28 | SS 110/35/10 Lukashevka | 2*16,0 | 8.83 | 10.6 | 120 | -1.77 | 0 | 16.8 | 18.57 | 17.03 | open | 28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.1 | 8.93 | 10.6 | 120 | -1.67 | 0 | 16.8 | 18.47 | 16.93 | open
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03 |  |  |  | Nom. capacity MV, MVA | 16 | 0.1 | 5.17 | 5.3 |  | -0.13 | 0 | 16.8 | 16.93
| Nom. capacity LV, MVA | 16 | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.76 | 5.3 | 120 | -1.54 | 0 | 16.8 | 18.34
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 5.9 | 13.1 | 120 | -7.2 | 0 | 6.615 | 13.815 | 6.715 | open | 29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.138 | 6.038 | 13.1 | 120 | -7.062 | 0 | 6.615 | 13.677 | 6.706 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 4.7 | 11.8 |  | -7.1 | 0 | 6.615 | 13.715 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.129 | 4.829 | 11.8 |  | -6.971 | 0 | 6.615 | 13.586
| Nom. capacity LV, MVA | 6,3+10,0 | 1.2 | 1.3 |  | -0.1 | 0 | 6.615 | 6.715 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 1.209 | 1.3 |  | -0.091 | 0 | 6.615 | 6.706
30 | SS 110/35/6 Manturovo | 2*16,0 | 7.38 | 9.35 | 10 | -1.97 | 0 | 16.8 | 18.77 | 16.89 | open | 30 | SS 110/35/6 Manturovo | 2*16,0 | 0.45 | 7.83 | 9.35 | 10 | -1.52 | 0 | 16.8 | 18.32 | 16.865 | open
| Nom. capacity MV, MVA | 16 | 7.21 | 9.09 |  | -1.88 | 0 | 16.8 | 18.68 |  |  |  | Nom. capacity MV, MVA | 16 | 0.425 | 7.635 | 9.09 |  | -1.455 | 0 | 16.8 | 18.255
| Nom. capacity LV, MVA | 16 | 0.17 | 0.26 | 120 | -0.09 | 0 | 16.8 | 16.89 |  |  |  | Nom. capacity LV, MVA | 16 | 0.025 | 0.195 | 0.26 | 120 | -0.065 | 0 | 16.8 | 16.865
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 5.81 | 9.6 | 120 | -3.79 | 0 | 6.615 | 10.405 | 8.025 | open | 31 | SS 110/35/10 8th Marta | 6,3+10,0 | 4.93 | 10.74 | 9.6 | 120 | 1.14 | 0 | 6.615 | 5.475 | 3.104 | open
| Nom. capacity MV, MVA | 6,3+10,0 | 5.19 | 6.6 | 120 | -1.41 | 0 | 6.615 | 8.025 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 4.921 | 10.111 | 6.6 | 120 | 3.511 | 0 | 6.615 | 3.104
| Nom. capacity LV, MVA | 6,3+10,0 | 0.62 | 3 | 45 | -2.38 | 0 | 6.615 | 8.995 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 0.629 | 3 | 45 | -2.371 | 0 | 6.615 | 8.986
32 | SS 110/10 Martovskaya | 2*6,3 | 0.61 | 0.55 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | open | 32 | SS 110/10 Martovskaya | 2*6,3 | 0.324 | 0.934 | 0.55 | 120 | 0.384 | 0 | 6.615 | 6.231 | 6.231 | open
33 | SS 110/35/10 Maryino | 10,0+25,0 | 6.09 | 8.11 | 120 | -2.02 | 0 | 10.5 | 12.52 | 11.41 | open | 33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.109 | 6.199 | 8.11 | 120 | -1.911 | 0 | 10.5 | 12.411 | 11.39 | open
| Nom. capacity MV, MVA | 10,0+25,0 | 3.79 | 4.9 |  | -1.11 | 0 | 10.5 | 11.61 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.089 | 3.879 | 4.9 |  | -1.021 | 0 | 10.5 | 11.521
| Nom. capacity LV, MVA | 10,0+25,0 | 2.3 | 3.21 |  | -0.91 | 0 | 10.5 | 11.41 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.02 | 2.32 | 3.21 |  | -0.89 | 0 | 10.5 | 11.39
34 | SS 110/35/10 Medvenka | 2*10,0 | 7.29 | 19.22 | 120 | -11.93 | 0 | 10.5 | 22.43 | 8.31 | open | 34 | SS 110/35/10 Medvenka | 2*10,0 | 0.487 | 7.777 | 19.22 | 120 | -11.443 | 0 | 10.5 | 21.943 | 8.134 | open
| Nom. capacity MV, MVA | 10 | 2.98 | 17.1 |  | -14.12 | 0 | 10.5 | 24.62 |  |  |  | Nom. capacity MV, MVA | 10 | 0.311 | 3.291 | 17.1 |  | -13.809 | 0 | 10.5 | 24.309
| Nom. capacity LV, MVA | 10 | 4.31 | 2.12 | 120 | 2.19 | 0 | 10.5 | 8.31 |  |  |  | Nom. capacity LV, MVA | 10 | 0.176 | 4.486 | 2.12 | 120 | 2.366 | 0 | 10.5 | 8.134
35 | SS 110/6 Neftyanaya | 2*10,0 | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | open | 35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.11 |  |  | 0.11 | 0 | 10.5 | 10.39 | 10.39 | open
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 16.25 | 26.86 | 120 | -10.61 | 0 | 16.8 | 27.41 | 12.01 | open | 36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 1.099 | 17.349 | 26.86 | 120 | -9.511 | 0 | 16.8 | 26.311 | 10.972 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.061 | 2.061 | 17.4 | 0 | -15.339 | 0 | 16.8 | 32.139
| Nom. capacity LV, MVA | 16,0 + 25,0 | 14.25 | 9.46 |  | 4.79 | 0 | 16.8 | 12.01 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 1.038 | 15.288 | 9.46 |  | 5.828 | 0 | 16.8 | 10.972
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 11.36 | 15.5 | 120 | -4.14 | 0 | 16.8 | 20.94 | 14.38 | open | 37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.442 | 11.802 | 15.5 | 120 | -3.698 | 0 | 16.8 | 20.498 | 14.047 | open
| Nom. capacity MV, MVA | 16 | 7.93 | 14.5 |  | -6.57 | 0 | 16.8 | 23.37 |  |  |  | Nom. capacity MV, MVA | 16 | 0.109 | 8.039 | 14.5 |  | -6.461 | 0 | 16.8 | 23.261
| Nom. capacity LV, MVA | 16 | 3.42 | 1 | 120 | 2.42 | 0 | 16.8 | 14.38 |  |  |  | Nom. capacity LV, MVA | 16 | 0.333 | 3.753 | 1 | 120 | 2.753 | 0 | 16.8 | 14.047
38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 1.76 | 6.31 | 120 | -4.55 | 0 | 6.615 | 11.165 | 7.415 | open | 38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.052 | 1.812 | 6.31 | 120 | -4.498 | 0 | 6.615 | 11.113 | 7.396 | open
| Nom. capacity MV, MVA | 6.3 | 1.25 | 5 | 120 | -3.75 | 0 | 6.615 | 10.365 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 1.283 | 5 | 120 | -3.717 | 0 | 6.615 | 10.332
| Nom. capacity LV, MVA | 6.3 | 0.51 | 1.31 | 120 | -0.8 | 0 | 6.615 | 7.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.019 | 0.529 | 1.31 | 120 | -0.781 | 0 | 6.615 | 7.396
39 | SS 110/10 Paniki | 2 х 2,5 | 0.88 | 0.1 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open | 39 | SS 110/10 Paniki | 2 х 2,5 |  | 0.88 | 0.1 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open
40 | SS 110/35/10 Peny | 2 х 16,0 | 5.83 | 6.9 | 120 | -1.07 | 0 | 16.8 | 17.87 | 17.3 | open | 40 | SS 110/35/10 Peny | 2 х 16,0 | 0.179 | 6.009 | 6.9 | 120 | -0.891 | 0 | 16.8 | 17.691 | 17.141 | open
| Nom. capacity MV, MVA | 16 | 3 | 3.5 |  | -0.5 | 0 | 16.8 | 17.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.159 | 3.159 | 3.5 |  | -0.341 | 0 | 16.8 | 17.141
| Nom. capacity LV, MVA | 16 | 2.83 | 3.4 | 120 | -0.57 | 0 | 16.8 | 17.37 |  |  |  | Nom. capacity LV, MVA | 16 | 0.02 | 2.85 | 3.4 | 120 | -0.55 | 0 | 16.8 | 17.35
41 | SS 110/35/10 Pribor | 2 х 25,0 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | open | 41 | SS 110/35/10 Pribor | 2 х 25,0 | 0 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | open
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  | 2: Nom. capacity MV, MVA; 3: 25; 5: 0; Min 8: 0; Min 9: 0; Min 10: 26.25; Min 11: 26.25
| Nom. capacity LV, MVA | 25 | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56 |  |  |  | Nom. capacity LV, MVA | 25 |  | 29.19 | 6.5 | 0 | 22.69 | 0 | 26.25 | 3.56
42 | SS 110/10 Progress | 2 х 63,0 | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | open | 42 | SS 110/10 Progress | 2 х 63,0 |  | 26.67 | 0 | 0 | 26.67 | 0 | 66.15 | 39.48 | 39.48 | open
43 | SS 110/10 Poultry plant | 6,3 + 10,0 | 6.58 | 0 | 0 | 6.58 | 0 | 6.615 | 0.035 | 0.035 | open | 43 | SS 110/10 Poultry plant | 6,3 + 10,0 |  | 6.58 | 0 | 0 | 6.58 | 0 | 6.615 | 0.035 | 0.035 | open
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 3.2 | 15.7 | 120 | -12.5 | 0 | 10.5 | 23 | 15.5 | open | 44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.007 | 3.207 | 15.7 | 120 | -12.493 | 0 | 10.5 | 22.993 | 15.493 | open
| Nom. capacity MV, MVA | 10 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 1.8 | 9.3 |  | -7.5 | 0 | 10.5 | 18
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.007 | 1.407 | 6.4 |  | -4.993 | 0 | 10.5 | 15.493
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.8 | 21.4 | 45 | -18.6 | 0 | 6.615 | 25.215 | 9.195 | open | 45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 1.515 | 4.315 | 21.4 | 45 | -17.085 | 0 | 6.615 | 23.7 | 9.097 | open
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.78 | 17.8 |  | -16.02 | 0 | 6.615 | 22.635 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 1.417 | 3.197 | 17.8 |  | -14.603 | 0 | 6.615 | 21.218
| Nom. capacity LV, MVA | 6,3 + 10,0 | 1.02 | 3.6 | 45 | -2.58 | 0 | 6.615 | 9.195 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.098 | 1.118 | 3.6 | 45 | -2.482 | 0 | 6.615 | 9.097
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 19.35 | 3.25 | 10 | 16.1 | 0 | 33.075 | 16.975 | 16.975 | open | 46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.59 | 19.94 | 3.25 | 10 | 16.69 | 0 | 33.075 | 16.385 | 16.385 | open
| Nom. capacity MV, MVA | 31.5 | 13 | 1.7 |  | 11.3 | 0 | 33.075 | 21.775 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.572 | 13.572 | 1.7 |  | 11.872 | 0 | 33.075 | 21.203
| Nom. capacity LV, MVA | 31.5 | 6.35 | 1.55 | 120 | 4.8 | 0 | 33.075 | 28.275 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.018 | 6.368 | 1.55 | 120 | 4.818 | 0 | 33.075 | 28.257
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 15.28 | 11 | 120 | 4.28 | 0 | 16.8 | 12.52 | 12.52 | open | 47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 4.247 | 19.527 | 11 | 120 | 8.527 | 0 | 16.8 | 8.273 | 8.273 | open
| Nom. capacity MV, MVA | 16,0 + 25,0 | 8.41 | 7 |  | 1.41 | 0 | 16.8 | 15.39 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 4.189 | 12.599 | 7 |  | 5.599 | 0 | 16.8 | 11.201
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.87 | 4 | 120 | 2.87 | 0 | 16.8 | 13.93 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.058 | 6.928 | 4 | 120 | 2.928 | 0 | 16.8 | 13.872
48 | SS 110/10 Solovyinaya | 2 х 25,0 | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | open | 48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 6.38 | 0 | 0 | 6.38 | 0 | 26.25 | 19.87 | 19.87 | open
49 | SS 110/10 STK | 2 х 10,0 | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 | 9.28 | open | 49 | SS 110/10 STK | 2 х 10,0 |  | 1.22 | 0 | 0 | 1.22 | 0 | 10.5 | 9.28 | 9.28 | open
50 | SS 110/10 Studenok | 2 х 6,3 | 2.08 | 0.7 | 120 | 1.38 | 0 | 6.615 | 5.235 | 5.235 | open | 50 | SS 110/10 Studenok | 2 х 6,3 | 0.134 | 2.214 | 0.7 | 120 | 1.514 | 0 | 6.615 | 5.101 | 5.101 | open
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 15.6 | 29 | 120 | -13.4 | 0 | 26.25 | 39.65 | 27.95 | open | 51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.394 | 16.994 | 29 | 120 | -12.006 | 0 | 26.25 | 38.256 | 27.055 | open
| Nom. capacity MV, MVA | 25 | 5.4 | 17.1 |  | -11.7 | 0 | 26.25 | 37.95 |  |  |  | Nom. capacity MV, MVA | 25 | 0.499 | 5.899 | 17.1 |  | -11.201 | 0 | 26.25 | 37.451
| Nom. capacity LV, MVA | 25 | 10.2 | 11.9 |  | -1.7 | 0 | 26.25 | 27.95 |  |  |  | Nom. capacity LV, MVA | 25 | 0.895 | 11.095 | 11.9 |  | -0.805 | 0 | 26.25 | 27.055
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | open | 52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.661 | 20.261 | 0 | 0 | 20.261 | 0 | 26.25 | 5.989 | 5.989 | open
| Nom. capacity MV, MVA | 25 | 3.67 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, MVA | 25 | 1.161 | 4.831 |  |  | 4.831 | 0 | 26.25 | 21.419
| Nom. capacity LV, MVA | 25 | 9.93 | 0 | 0 | 9.93 | 0 | 26.25 | 16.32 |  |  |  | Nom. capacity LV, MVA | 25 | 5.5 | 15.43 | 0 | 0 | 15.43 | 0 | 26.25 | 10.82
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 3.87 | 3.44 | 120 | 0.43 | 0 | 10.5 | 10.07 | 8.57 | open | 53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.059 | 3.929 | 3.44 | 120 | 0.489 | 0 | 10.5 | 10.011 | 8.528 | open
| Nom. capacity MV, MVA | 10 | 0.5 | 2 |  | -1.5 | 0 | 10.5 | 12 |  |  |  | Nom. capacity MV, MVA | 10 | 0.017 | 0.517 | 2 |  | -1.483 | 0 | 10.5 | 11.983
| Nom. capacity LV, MVA | 10 | 3.37 | 1.44 |  | 1.93 | 0 | 10.5 | 8.57 |  |  |  | Nom. capacity LV, MVA | 10 | 0.042 | 3.412 | 1.44 |  | 1.972 | 0 | 10.5 | 8.528
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 4.72 | 9.59 | 120 | -4.87 | 0 | 6.615 | 11.485 | 6.525 | open | 54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.482 | 5.202 | 9.59 | 120 | -4.388 | 0 | 6.615 | 11.003 | 6.412 | open
| Nom. capacity MV, MVA | 6,3 + 16,0 | 4.13 | 9.09 |  | -4.96 | 0 | 6.615 | 11.575 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.369 | 4.499 | 9.09 |  | -4.591 | 0 | 6.615 | 11.206
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.59 | 0.5 | 120 | 0.09 | 0 | 6.615 | 6.525 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.113 | 0.703 | 0.5 | 120 | 0.203 | 0 | 6.615 | 6.412
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.63 | 0.5 | 120 | 0.13 | 0 | 10.5 | 10.37 | 10.04 | open | 55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.038 | 0.668 | 0.5 | 120 | 0.168 | 0 | 10.5 | 10.332 | 10.032 | open
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.46 |  |  | 0.46 | 0 | 10.5 | 10.04 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0.008 | 0.468 |  |  | 0.468 | 0 | 10.5 | 10.032
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.17 | 0.5 | 120 | -0.33 | 0 | 10.5 | 10.83 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.03 | 0.2 | 0.5 | 120 | -0.3 | 0 | 10.5 | 10.8
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 6.29 | 17.4 | 120 | -11.11 | 0 | 16.8 | 27.91 | 16.96 | open | 56 | SS 110/35/10 Fatezh | 2 х 16,0 | 2.883 | 9.173 | 17.4 | 120 | -8.227 | 0 | 16.8 | 25.027 | 16.427 | open
| Nom. capacity MV, MVA | 16 | 1.85 | 12.8 |  | -10.95 | 0 | 16.8 | 27.75 |  |  |  | Nom. capacity MV, MVA | 16 | 2.35 | 4.2 | 12.8 |  | -8.6 | 0 | 16.8 | 25.4
| Nom. capacity LV, MVA | 16 | 4.44 | 4.6 | 120 | -0.16 | 0 | 16.8 | 16.96 |  |  |  | Nom. capacity LV, MVA | 16 | 0.533 | 4.973 | 4.6 | 120 | 0.373 | 0 | 16.8 | 16.427
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 4.33 | 12.34 | 120 | -8.01 | 0 | 26.25 | 34.26 | 25.08 | open | 57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.354 | 4.684 | 12.34 | 120 | -7.656 | 0 | 26.25 | 33.906 | 25.03 | open
| Nom. capacity MV, MVA | 25 | 2.94 | 12.12 |  | -9.18 | 0 | 26.25 | 35.43 |  |  |  | Nom. capacity MV, MVA | 25 | 0.304 | 3.244 | 12.12 |  | -8.876 | 0 | 26.25 | 35.126
| Nom. capacity LV, MVA | 25 | 1.39 | 0.22 | 10 | 1.17 | 0 | 26.25 | 25.08 |  |  |  | Nom. capacity LV, MVA | 25 | 0.05 | 1.44 | 0.22 | 10 | 1.22 | 0 | 26.25 | 25.03
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 3.15 | 6.3 | 80 | -3.15 | 0 | 7.875 | 11.025 | 7.985 | open | 58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.151 | 3.301 | 6.3 | 80 | -2.999 | 0 | 7.875 | 10.874 | 7.861 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.86 | 3.9 |  | -3.04 | 0 | 7.875 | 10.915 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.027 | 0.887 | 3.9 |  | -3.013 | 0 | 7.875 | 10.888
| Nom. capacity LV, MVA | 7,5 + 10,0 | 2.29 | 2.4 | 80 | -0.11 | 0 | 7.875 | 7.985 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.124 | 2.414 | 2.4 | 80 | 0.014 | 0 | 7.875 | 7.861
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 3.24 | 9.38 | 10 | -6.14 | 0 | 16.8 | 22.94 | 16.01 | open | 59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.46 | 3.7 | 9.38 | 10 | -5.68 | 0 | 16.8 | 22.48 | 15.756 | open
| Nom. capacity MV, MVA | 16 | 2.16 | 9.09 |  | -6.93 | 0 | 16.8 | 23.73 |  |  |  | Nom. capacity MV, MVA | 16 | 0.206 | 2.366 | 9.09 |  | -6.724 | 0 | 16.8 | 23.524
| Nom. capacity LV, MVA | 16 | 1.08 | 0.29 | 120 | 0.79 | 0 | 16.8 | 16.01 |  |  |  | Nom. capacity LV, MVA | 16 | 0.254 | 1.334 | 0.29 | 120 | 1.044 | 0 | 16.8 | 15.756
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 2.7 | 8.25 | 120 | -5.55 | 0 | 6.615 | 12.165 | 7.025 | open | 60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.072 | 2.772 | 8.25 | 120 | -5.478 | 0 | 6.615 | 12.093 | 7.02 | open
| Nom. capacity MV, MVA | 6.3 | 1.86 | 7 |  | -5.14 | 0 | 6.615 | 11.755 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.067 | 1.927 | 7 |  | -5.073 | 0 | 6.615 | 11.688
| Nom. capacity LV, MVA | 6.3 | 0.84 | 1.25 | 129 | -0.41 | 0 | 6.615 | 7.025 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.005 | 0.845 | 1.25 | 129 | -0.405 | 0 | 6.615 | 7.02
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 4.6 | 13.73 | 120 | -9.13 | 0 | 10.5 | 19.63 | 11.83 | open | 61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.283 | 4.883 | 13.73 | 120 | -8.847 | 0 | 10.5 | 19.347 | 11.738 | open
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3 |  |  |  | Nom. capacity MV, MVA | 10 | 0.283 | 3.683 | 11.2 |  | -7.517 | 0 | 10.5 | 18.017
| Nom. capacity LV, MVA | 10 | 1.2 | 2.53 | 120 | -1.33 | 0 | 10.5 | 11.83 |  |  |  | Nom. capacity LV, MVA | 10 | 0.092 | 1.292 | 2.53 | 120 | -1.238 | 0 | 10.5 | 11.738
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 10.49 | 12.9 | 120 | -2.41 | 0 | 26.25 | 28.66 | 21.53 | open | 62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.582 | 11.072 | 12.9 | 120 | -1.828 | 0 | 26.25 | 28.078 | 21.321 | open
| Nom. capacity MV, MVA | 25 | 4.99 | 12.12 |  | -7.13 | 0 | 26.25 | 33.38 |  |  |  | Nom. capacity MV, MVA | 25 | 0.373 | 5.363 | 12.12 |  | -6.757 | 0 | 26.25 | 33.007
| Nom. capacity LV, MVA | 25 | 5.5 | 0.78 | 120 | 4.72 | 0 | 26.25 | 21.53 |  |  |  | Nom. capacity LV, MVA | 25 | 0.209 | 5.709 | 0.78 | 120 | 4.929 | 0 | 26.25 | 21.321
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.875 | 11.625 | 6.83 | open | 63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.305 | 2.865 | 6.31 | 10 | -3.445 | 0 | 7.875 | 11.32 | 6.765 | open
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.26 | 6.06 |  | -4.8 | 0 | 7.88 | 12.68 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.24 | 1.5 | 6.06 |  | -4.56 | 0 | 7.88 | 12.44
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.3 | 0.25 | 10 | 1.05 | 0 | 7.88 | 6.83 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.065 | 1.365 | 0.25 | 10 | 1.115 | 0 | 7.88 | 6.765
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 64 | SS 35/10 Amosovka | 2 х 2,5 | 0.008 | 0.368 | 0.2 | 120 | 0.168 | 0 | 2.625 | 2.457 | 2.457 | open
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.45 | 0.37 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open | 65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.023 | 0.473 | 0.37 | 120 | 0.103 | 0 | 1.68 | 1.577 | 1.577 | open
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open | 66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 |  | 1.22 | 1.1 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | open
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.2 | 1.43 | 120 | -1.23 | 0 | 1.68 | 2.91 | 2.91 | open | 67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.062 | 0.262 | 1.43 | 120 | -1.168 | 0 | 1.68 | 2.848 | 2.848 | open
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.47 | 6.1 | 0 | -5.63 | 0 | 4.2 | 9.83 | 9.83 | open | 68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.432 | 0.902 | 6.1 | 0 | -5.198 | 0 | 4.2 | 9.398 | 9.398 | open
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.08 | 0.15 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open | 69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.0188 | 0.0988 | 0.15 | 120 | -0.0512 | 0 | 1.05 | 1.1012 | 1.1012 | open
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 1.05 | 0.29 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | open | 70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.076 | 1.126 | 0.29 | 120 | 0.836 | 0 | 2.625 | 1.789 | 1.789 | open
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.4 | 0.41 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.079 | 0.479 | 0.41 | 120 | 0.069 | 0 | 2.625 | 2.556 | 2.556 | open
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 1.37 | 0.4 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | open | 72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.55 | 1.92 | 0.4 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | open
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.55 | 0.22 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | open | 73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.462 | 1.012 | 0.22 | 120 | 0.792 | 0 | 1.68 | 0.888 | 0.888 | open
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.4 | 0.46 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open | 74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.044 | 0.444 | 0.46 | 120 | -0.016 | 0 | 2.625 | 2.641 | 2.641 | open
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.4 | 0 | 0 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open | 75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.025 | 0.425 | 0 | 0 | 0.425 | 0 | 4.2 | 3.775 | 3.775 | open
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 2.37 | 0.46 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | open | 76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.274 | 2.644 | 0.46 | 120 | 2.184 | 0 | 6.615 | 4.431 | 4.431 | open
77 | SS 35/10 Vygornoe | 2 х 2,5 | 1.38 | 0.51 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | open | 77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.15 | 1.53 | 0.51 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | open
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.44 | 0.17 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | open | 78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.009 | 0.449 | 0.17 | 120 | 0.279 | 0 | 1.68 | 1.401 | 1.401 | open
79 | SS 35/10 Gorodok | 2 х 4,0 | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | open | 79 | SS 35/10 Gorodok | 2 х 4,0 |  | 2.33 | 0.7 | 45 | 1.63 | 0 | 4.2 | 2.57 | 2.57 | open
80 | SS 35/10 Guevo | 2 х 2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.625 | 3.115 | 3.115 | open | 80 | SS 35/10 Guevo | 2 х 2,5 | 0.024 | 1.224 | 1.69 | 20 | -0.466 | 0 | 2.625 | 3.091 | 3.091 | open
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.2 | 0.38 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | open | 81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.242 | 0.38 | 120 | -0.138 | 0 | 1.68 | 1.818 | 1.818 | open
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 3.44 | 3.5 | 0 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open | 82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 3.555 | 3.5 | 0 | 0.055 | 0 | 2.625 | 2.57 | 2.57 | open
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.86 | 0.26 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open | 83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.865 | 0.26 | 120 | 0.605 | 0 | 2.625 | 2.02 | 2.02 | open
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 10.39 | 2.5 | 0 | 7.89 | 0 | 10.5 | 2.61 | 2.61 | open | 84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 10.4 | 2.5 | 0 | 7.9 | 0 | 10.5 | 2.6 | 2.6 | open
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.98 | 1.67 | 0 | -0.69 | 0 | 4.2 | 4.89 | 4.89 | open | 85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.625 | 1.605 | 1.67 | 0 | -0.065 | 0 | 4.2 | 4.265 | 4.265 | open
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open | 86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.159 | 1.059 | 0.93 | 45 | 0.129 | 0 | 1.68 | 1.551 | 1.551 | open
87 | SS 35/10 Ivanino | 2 х 6,3 | 2.29 | 2.69 | 80 | -0.4 | 0 | 6.615 | 7.015 | 7.015 | open | 87 | SS 35/10 Ivanino | 2 х 6,3 | 0.09 | 2.38 | 2.69 | 80 | -0.31 | 0 | 6.615 | 6.925 | 6.925 | open
88 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 1.89 | 1.99 | 1.99 | open | 88 | SS 35/10 Kalinovka | 1,8 + 2,5 |  | 0.4 | 0.5 | 120 | -0.1 | 0 | 1.89 | 1.99 | 1.99 | open
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.33 | 0.52 | 120 | -0.19 | 0 | 1.68 | 1.87 | 1.87 | open | 89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.345 | 0.52 | 120 | -0.175 | 0 | 1.68 | 1.855 | 1.855 | open
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 9.78 | 6.25 | 20 | 3.53 | 0 | 10.5 | 6.97 | 6.97 | open | 90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 10.189 | 6.25 | 20 | 3.939 | 0 | 10.5 | 6.561 | 6.561 | open
91 | SS 35/10 Mixed fodder plant | 4,0+6,3 | 0.49 | 0 | 0 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | open | 91 | SS 35/10 Mixed fodder plant | 4,0+6,3 |  | 0.49 | 0 | 0 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | open
92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 3.1 | 0.21 | 120 | 2.89 | 0 | 6.615 | 3.725 | 3.725 | open | 92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.083 | 3.183 | 0.21 | 120 | 2.973 | 0 | 6.615 | 3.642 | 3.642 | open
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 2.19 | 1.14 | 80 | 1.05 | 0 | 3.36 | 2.31 | 2.31 | open | 93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 0.5 | 2.69 | 1.14 | 80 | 1.55 | 0 | 3.36 | 1.81 | 1.81 | open
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 4.35 | 1.56 | 80 | 2.79 | 0 | 4.2 | 1.41 | 1.41 | open | 94 | SS 35/10 Korenevo | 4,0 + 6,3 | 2.77 | 7.12 | 1.56 | 80 | 5.56 | 0 | 4.2 | -1.36 | -1.36 | closed
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.62 | 0.24 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open | 95 | SS 35/10 Kremyanoe | 2,5 + 4,0 |  | 0.62 | 0.24 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
96 | SS 35/10 Krupets | 1,8 + 2,5 | 1.5 | 0.42 | 120 | 1.08 | 0 | 1.89 | 0.81 | 0.81 | open | 96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.664 | 0.42 | 120 | 1.244 | 0 | 1.89 | 0.646 | 0.646 | open
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.7 | 0.6 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open | 97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.967 | 1.667 | 0.6 | 120 | 1.067 | 0 | 2.625 | 1.558 | 1.558 | open
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.14 | 0.17 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | open | 98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.003 | 0.143 | 0.17 | 120 | -0.027 | 0 | 2.625 | 2.652 | 2.652 | open
99 | SS 35/10 Kurchatov | 2 х 10,0 | 4.52 | 4.5 | 80 | 0.02 | 0 | 10.5 | 10.48 | 10.48 | open | 99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 4.525 | 4.5 | 80 | 0.025 | 0 | 10.5 | 10.475 | 10.475 | open
100 | SS 35/10 Kutok | 2 х 2,5 | 0.08 | 0.05 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | open | 100 | SS 35/10 Kutok | 2 х 2,5 | 0.009 | 0.089 | 0.05 | 120 | 0.039 | 0 | 2.625 | 2.586 | 2.586 | open
101 | SS 35/10 Linets | 2 х 2,5 | 0.23 | 0.25 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open | 101 | SS 35/10 Linets | 2 х 2,5 | 1.11 | 1.34 | 0.25 | 120 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | open
102 | SS 35/10 Luch | 2 х 6,3 | 3.03 | 0.23 | 120 | 2.8 | 0 | 6.615 | 3.815 | 3.815 | open | 102 | SS 35/10 Luch | 2 х 6,3 | 0.336 | 3.366 | 0.23 | 120 | 3.136 | 0 | 6.615 | 3.479 | 3.479 | open
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | open | 103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.029 | 0.779 | 1.59 | 80 | -0.811 | 0 | 4.2 | 5.011 | 5.011 | open
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.65 | 0.08 | 120 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | open | 104 | SS 35/10 Matveevka | 2 х 2,5 | 0.02 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open
105 | SS 35/10 Mayak | 2 х 2,5 | 0.5 | 0.3 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 105 | SS 35/10 Mayak | 2 х 2,5 | 0.016 | 0.516 | 0.3 | 120 | 0.216 | 0 | 2.625 | 2.409 | 2.409 | open
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 1.27 | 1.7 | 80 | -0.43 | 0 | 4.2 | 4.63 | 4.63 | open | 106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.18 | 1.45 | 1.7 | 80 | -0.25 | 0 | 4.2 | 4.45 | 4.45 | open
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.87 | 0.3 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | open | 107 | SS 35/10 Murynovka | 2 х 4,0 | 0.2 | 1.07 | 0.3 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | open
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.51 | 0.63 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open | 108 | SS 35/10 N. Borki | 2 х 2,5 | 0.02 | 0.53 | 0.63 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | open
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.4 | 0.03 | 80 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open | 109 | SS 35/10 Nikolskaya | 1,6 + 1,8 |  | 0.4 | 0.03 | 80 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open
110 | SS 35/10 Novaya | 2 х 2,5 | 1.2 | 0.4 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | open | 110 | SS 35/10 Novaya | 2 х 2,5 | 0.262 | 1.462 | 0.4 | 120 | 1.062 | 0 | 2.625 | 1.563 | 1.563 | open
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.56 | 0.19 | 120 | 0.37 | 0 | 2.625 | 2.255 | 2.255 | open | 111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.051 | 0.611 | 0.19 | 120 | 0.421 | 0 | 2.625 | 2.204 | 2.204 | open
112 | SS 35/10 Orlovka | 2 х 2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.625 | 2.975 | 2.975 | open | 112 | SS 35/10 Orlovka | 2 х 2,5 | 2.574 | 2.744 | 0.52 | 120 | 2.224 | 0 | 2.625 | 0.401 | 0.401 | open
113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.18 | 0.2 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open | 113 | SS 35/10 Osotskoe | 2 х 2,5 |  | 0.18 | 0.2 | 120 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | open
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.26 | 0.74 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | open | 114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.212 | 1.472 | 0.74 | 120 | 0.732 | 0 | 4.2 | 3.468 | 3.468 | open
115 | SS 35/10 Panino | 2 х 2,5 | 0.28 | 0.11 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 115 | SS 35/10 Panino | 2 х 2,5 | 0.02 | 0.3 | 0.11 | 80 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | open
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.62 | 0.52 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | open | 116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.066 | 0.686 | 0.52 | 120 | 0.166 | 0 | 2.625 | 2.459 | 2.459 | open
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.61 | 0.3 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | open | 117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.716 | 2.326 | 0.3 | 120 | 2.026 | 0 | 2.625 | 0.599 | 0.599 | open
118 | SS 35/10 Platava | 2 х 2,5 | 1.38 | 0.26 | 120 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | open | 118 | SS 35/10 Platava | 2 х 2,5 | 0.014 | 1.394 | 0.26 | 120 | 1.134 | 0 | 2.625 | 1.491 | 1.491 | open
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.19 | 0.46 | 120 | -0.27 | 0 | 1.68 | 1.95 | 1.95 | open | 119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.237 | 0.46 | 120 | -0.223 | 0 | 1.68 | 1.903 | 1.903 | open
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | open | 120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.008 | 0.508 | 1.16 | 120 | -0.652 | 0 | 4.2 | 4.852 | 4.852 | open
121 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | open | 121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.03 | 0.08 | 120 | -0.05 | 0 | 6.615 | 6.665 | 6.665 | open
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 1.39 | 0.3 | 80 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | open | 122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.274 | 1.664 | 0.3 | 80 | 1.364 | 0 | 2.625 | 1.261 | 1.261 | open
123 | SS 35/10 Pselets | 2 х 1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open | 123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.39 | 0.43 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open | 124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.05 | 0.44 | 0.43 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.77 | 0.32 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | open | 125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.195 | 0.965 | 0.32 | 120 | 0.645 | 0 | 2.625 | 1.98 | 1.98 | open
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.38 | 0.44 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | open | 126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.583 | 0.963 | 0.44 | 120 | 0.523 | 0 | 2.625 | 2.102 | 2.102 | open
127 | SS 35/10 Razvetye | 2 х 4,0 | 1.91 | 1.03 | 120 | 0.88 | 0 | 4.2 | 3.32 | 3.32 | open | 127 | SS 35/10 Razvetye | 2 х 4,0 | 0.421 | 2.331 | 1.03 | 120 | 1.301 | 0 | 4.2 | 2.899 | 2.899 | open
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.74 | 0.11 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | open | 128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.025 | 0.765 | 0.11 | 120 | 0.655 | 0 | 4.2 | 3.545 | 3.545 | open
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.28 | 0.29 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | open | 129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.076 | 0.356 | 0.29 | 120 | 0.066 | 0 | 1.68 | 1.614 | 1.614 | open
130 | SS 35/10 Rubilnik | 2 х 2,5 | 1.25 | 1.18 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.058 | 1.308 | 1.18 | 80 | 0.128 | 0 | 2.625 | 2.497 | 2.497 | open
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.28 | 0.08 | 20 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | open | 131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.009 | 0.289 | 0.08 | 20 | 0.209 | 0 | 1.68 | 1.471 | 1.471 | open
132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.39 | 0.6 | 20 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | open | 132 | SS 35/10 Sapogovo | 2 х 2,5 | 0.361 | 1.751 | 0.6 | 20 | 1.151 | 0 | 2.625 | 1.474 | 1.474 | open
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 4.41 | 2.25 | 80 | 2.16 | 0 | 6.615 | 4.455 | 4.455 | open | 133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.311 | 4.721 | 2.25 | 80 | 2.471 | 0 | 6.615 | 4.144 | 4.144 | open
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.09 | 1.4 | 45 | 0.69 | 0 | 4.2 | 3.51 | 3.51 | open | 134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.038 | 2.128 | 1.4 | 45 | 0.728 | 0 | 4.2 | 3.472 | 3.472 | open
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.4 | 0 | - | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open | 135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.074 | 0.474 | 0 | - | 0.474 | 0 | 2.625 | 2.151 | 2.151 | open
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.51 | 0.6 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 136 | SS 35/10 Seed plant | 2 х 2,5 | 0.079 | 0.589 | 0.6 | 120 | -0.011 | 0 | 2.625 | 2.636 | 2.636 | open
137 | SS 35/10 Snagost | 2 х 4,0 | 1.31 | 0.05 | 10 | 1.26 | 0 | 4.2 | 2.94 | 2.94 | open | 137 | SS 35/10 Snagost | 2 х 4,0 | 0.073 | 1.383 | 0.05 | 10 | 1.333 | 0 | 4.2 | 2.867 | 2.867 | open
138 | SS 35/10 SOM | 1,6 + 4,0 | 1.03 | 0.08 | 10 | 0.95 | 0 | 1.68 | 0.73 | 0.73 | open | 138 | SS 35/10 SOM | 1,6 + 4,0 | 0.091 | 1.121 | 0.08 | 10 | 1.041 | 0 | 1.68 | 0.639 | 0.639 | open
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.77 | 0.69 | 120 | 0.08 | 0 | 3.36 | 3.28 | 3.28 | open | 139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.12 | 0.89 | 0.69 | 120 | 0.2 | 0 | 3.36 | 3.16 | 3.16 | open
140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.65 | 0.58 | 80 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.075 | 0.725 | 0.58 | 80 | 0.145 | 0 | 2.625 | 2.48 | 2.48 | open
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.2 | 0.2 | 80 | 0 | 0 | 1.68 | 1.68 | 1.68 | open | 141 | SS 35/10 Starkovo | 2 х 1,6 | 0.009 | 0.209 | 0.2 | 80 | 0.009 | 0 | 1.68 | 1.671 | 1.671 | open
142 | CC 35/10 Starshee | 2 х 1,6 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | open | 142 | CC 35/10 Starshee | 2 х 1,6 | 0.014 | 0.254 | 0.2 | 120 | 0.054 | 0 | 1.68 | 1.626 | 1.626 | open
143 | SS 35/10 Teplitsy | 2 х 4,0 | 2.02 | 1.08 | 45 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | open | 143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.11 | 2.13 | 1.08 | 45 | 1.05 | 0 | 4.2 | 3.15 | 3.15 | open
144 | SS 35/10 Turovka | 2 х 2,5 | 0.44 | 0.6 | 120 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | open | 144 | SS 35/10 Turovka | 2 х 2,5 | 0.065 | 0.505 | 0.6 | 120 | -0.095 | 0 | 2.625 | 2.72 | 2.72 | open
145 | SS 35/10 Uspenka | 2 х 2,5 | 1.11 | 1 | 80 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open | 145 | SS 35/10 Uspenka | 2 х 2,5 | 0.049 | 1.159 | 1 | 80 | 0.159 | 0 | 2.625 | 2.466 | 2.466 | open
146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 22.44 | 5 |  | 17.44 | 0 | 26.25 | 8.81 | 8.81 | open | 146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0.005 | 22.445 | 5 |  | 17.445 | 0 | 26.25 | 8.805 | 8.805 | open
147 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | open | 147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.2 | 0.5 | 120 | -0.3 | 0 | 2.625 | 2.925 | 2.925 | open
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.38 | 0.21 | 80 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.085 | 0.465 | 0.21 | 80 | 0.255 | 0 | 2.625 | 2.37 | 2.37 | open
149 | SS 35/10 Shipy | 2 х 2,5 | 0.1 | 0.3 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | open | 149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.112 | 0.3 | 120 | -0.188 | 0 | 2.625 | 2.813 | 2.813 | open
150 | SS 35/10 Elevator | 4,0 + 6,3 | 1.53 | 0.6 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | open | 150 | SS 35/10 Elevator | 4,0 + 6,3 | 0.015 | 1.545 | 0.6 | 120 | 0.945 | 0 | 4.2 | 3.255 | 3.255 | open
151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.43 | 4.7 | 80 | 3.73 | 0 | 10.5 | 6.77 | 6.77 | open | 151 | SS 35/10 Yugo-Zapadnaya | 1 х 10,0 | 2.35 | 10.78 | 4.7 | 80 | 6.08 | 0 | 10.5 | 4.42 | 4.42 | open
152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 2.46 | 3.9 | 120 | -1.44 | 0 | 2.625 | 4.065 | 4.065 | open | 152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 0.053 | 2.513 | 3.9 | 120 | -1.387 | 0 | 2.625 | 4.012 | 4.012 | open
| TOTAL: | 3185.9 | 761.961 | 777.99 | [5 empty] | 1221.894 |  | 2: TOTAL:; 3: 3185.9; 4: 114.4801; 5: 876.0431; MVA 6: 783.88; Min 12: 1168.5789
| deficit | [8 empty] | -7.475 |  | 2: deficit; Min 12: -30.599
| proficit | [8 empty] | 1214.414 |  | 2: proficit; Min 12: 1137.9799

## свод-текущий дефицит
The list of closed supply centers of IDGC of Centre - Kurskenergo division (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA
Kurskenergo
1. | SS 110/10 Vysokaya* | 2*16 | -7.17
2. | SS 110/35/10 Kamyshi | 2*6,3 | -0.305
Total current deficit (winter 2010) |  |  | -7.475

## свод-ожидаемый дефицит
The list of closed supply centers of IDGC of Centre - Kurskenergo division with expected load taking into account new connections and other development of the electical networks (expected deficit of capacity) for January 2011.
No. | Name of supply center, voltage class |  | Expected deficit, MVA
Kurskenergo
1. | SS 110/10 Beketovo* | 1 х 6,3 | -0.641
2. | SS 110/6 Teplichnaya* | 1 х 16,0 | -5.52
3. | SS 35/10 kV Bykovo* | 1 х 4,0 | -3.273
4. | SS 35/10 Water storage* | 1 х 4,0 | -2.585
5. | SS 35/10 Reut | 1 х 2,5 | -0.256
6. | SS 35/10 Rovenka | 1 х 1,6 | -0.945
7. | SS 35/10 Yasenki* | 1 х 2,5 | -1.82
8. | SS 110/10 Vysokaya* | 2 х 16,0 | -7.17
9. | SS 110/35/10 Gorshechnoe | 10+16,0 | -2.684
10. | SS 110/35/10 Kamyshi* | 2 х 6,3 | -4.345
11. | SS 35/10 Korenevo | 4,0 + 6,3 | -1.36
Total expected deficit (winter 2011) |  |  | -30.599