## Тверь
table 1 | [21 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | Load percent against the nominal capacity, % | №п/п | Наименование объекта центра питания, класс напряжения | Expected deficit/proficit | [9 empty] | Note | Load percent against the nominal capacity, % | Production division
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of main substation following the results of measurements of load maximal Sмах , MVA | Total capacity, re-distributed according to operating rules MVA for the period time |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA | [5 empty] | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | MVA | Min. | [12 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
1 | SS Alekseykovo 35/10 kv | 1.6 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 |  | 11.9048 | 1 | SS Alekseykovo 35/10 kv | 1.6 | 0 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 |  | 11.9048 | Bezhetskie Power networks
2 | SS Belyznitsy 35/10 kv | 2.5 | 0.7 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 0.8 | 0.8 |  | 26.6667 | 2 | SS Belyznitsy 35/10 kv | 2.5 | 0 | 0.7 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 0.8 | 0.8 |  | 26.6667 | Bezhetskie Power networks
3 | SS Borisovskoe 35/10 kv | 1 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 9.5238 | 3 | SS Borisovskoe 35/10 kv | 1 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 9.5238 | Bezhetskie Power networks
4 | SS Vysokusha 35/10 kv | 2.5 | 0.1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.2 | 1.2 |  | 3.8095 | 4 | SS Vysokusha 35/10 kv | 2.5 | 0 | 0.1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.2 | 1.2 |  | 3.8095 | Bezhetskie Power networks
5 | SS Hotel 35/10 kv | 1.6 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 |  | 11.9048 | 5 | SS Hotel 35/10 kv | 1.6 | 0 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 |  | 11.9048 | Bezhetskie Power networks
6 | SS Grigorovo 35/10 kv | 2.5 | 0.1 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.8 | 0.8 |  | 3.8095 | 6 | SS Grigorovo 35/10 kv | 2.5 | 0.015 | 0.115 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.785 | 0.785 |  | 4.381 | Bezhetskie Power networks
7 | SS Deledino 35/10 kv | 4 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  | 4.7619 | 7 | SS Deledino 35/10 kv | 4 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 |  | 4.7619 | Bezhetskie Power networks
8 | SS Zaramenye 35/10 kv | 1.6 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 |  | 23.8095 | 8 | SS Zaramenye 35/10 kv | 1.6 | 0 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 |  | 23.8095 | Bezhetskie Power networks
9 | SS Zoby 35/10 kv | 4 | 0.1 | 3 | 24 hours | 3 | 0 | 3 | 2.9 | 2.9 |  | 2.381 | 9 | SS Zoby 35/10 kv | 4 | 0 | 0.1 | 3 | 24 hours | 3 | 0 | 3 | 2.9 | 2.9 |  | 2.381 | Bezhetskie Power networks
10 | SS Koy 35/10 kv | 1.6 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 |  | 5.9524 | 10 | SS Koy 35/10 kv | 1.6 | 0.03 | 0.13 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.57 | 0.57 |  | 7.7381 | Bezhetskie Power networks
11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.1 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1.1 | 1.1 |  | 5.9524 | 11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.125 | 0.225 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.975 | 0.975 |  | 13.3929 | Bezhetskie Power networks
12 | SS Litvinovo 35/10 kv | 4 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 4.7619 | 12 | SS Litvinovo 35/10 kv | 4 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 4.7619 | Bezhetskie Power networks
13 | SS Loshchemlya 35/10 kv | 2.5 | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 |  | 22.8571 | 13 | SS Loshchemlya 35/10 kv | 2.5 | 0.015 | 0.615 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.185 | 0.185 |  | 23.4286 | Bezhetskie Power networks
14 | SS Lyubegoshchi 35/10 kv | 1.8 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 |  | 21.164 | 14 | SS Lyubegoshchi 35/10 kv | 1.8 | 0 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 |  | 21.164 | Bezhetskie Power networks
15 | SS Martynovo 35/10 kv | 1.6 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  | 11.9048 | 15 | SS Martynovo 35/10 kv | 1.6 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  | 11.9048 | Bezhetskie Power networks
16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 |  | 3.8095 | 16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 |  | 3.8095 | Bezhetskie Power networks
17 | SS Morozovo 35/10 kv | 2.5 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 7.619 | 17 | SS Morozovo 35/10 kv | 2.5 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 7.619 | Bezhetskie Power networks
18 | SS Popovka 35/10 kv | 1 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 |  | 9.5238 | 18 | SS Popovka 35/10 kv | 1 | 0 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 |  | 9.5238 | Bezhetskie Power networks
19 | SS Romantsevo 35/10 kv | 4 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 |  | 4.7619 | 19 | SS Romantsevo 35/10 kv | 4 | 0.026875 | 0.22687 | 1 | 24 hours | 1 | 0 | 1 | 0.77312 | 0.77312 |  | 5.4018 | Bezhetskie Power networks
20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0.6 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.3 | 0.3 |  | 22.8571 | 20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0 | 0.6 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.3 | 0.3 |  | 22.8571 | Bezhetskie Power networks
21 | SS Sukromny 35/10 kv | 1.6 | 0.5 | 1.7 | 24 hours | 1.7 | 0 | 1.7 | 1.2 | 1.2 |  | 29.7619 | 21 | SS Sukromny 35/10 kv | 1.6 | 0 | 0.5 | 1.7 | 24 hours | 1.7 | 0 | 1.7 | 1.2 | 1.2 |  | 29.7619 | Bezhetskie Power networks
22 | SS tebleshi 35/10 kv | 2.5 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 | 1.6 |  | 7.619 | 22 | SS tebleshi 35/10 kv | 2.5 | 0 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 | 1.6 |  | 7.619 | Bezhetskie Power networks
23 | SS Trestna 35/10 kv | 2.5 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  | 7.619 | 23 | SS Trestna 35/10 kv | 2.5 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 |  | 7.619 | Bezhetskie Power networks
24 | SS Fralyovo 35/10 kv | 4 | 0.8 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1 | 1 |  | 19.0476 | 24 | SS Fralyovo 35/10 kv | 4 | 0 | 0.8 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1 | 1 |  | 19.0476 | Bezhetskie Power networks
25 | SS Chamerovo 35/10 kv | 1.8 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6 | 0.6 |  | 42.328 | 25 | SS Chamerovo 35/10 kv | 1.8 | 0.33625 | 1.1362 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.26375 | 0.26375 |  | 60.119 | Bezhetskie Power networks
26 | SS Akhmatovo 110/10 kv | 2.5 | 0.4 | 1 | 24 hours | 1 | 0 | 1 | 0.6 | 0.6 |  | 15.2381 | 26 | SS Akhmatovo 110/10 kv | 2.5 | 0 | 0.4 | 1 | 24 hours | 1 | 0 | 1 | 0.6 | 0.6 |  | 15.2381 | Bezhetskie Power networks
27 | SS Kladovo 110/10 kv | 6.3 | 1 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 0.8 | 0.8 |  | 15.1172 | 27 | SS Kladovo 110/10 kv | 6.3 | 0 | 1 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 0.8 | 0.8 |  | 15.1172 | Bezhetskie Power networks
28 | SS Laptikha 110/10 kv | 2.5 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | 0.7 |  | 19.0476 | 28 | SS Laptikha 110/10 kv | 2.5 | 0 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | 0.7 |  | 19.0476 | Bezhetskie Power networks
29 | SS Malyshevo 110/10 kv | 2.5 | 0.8 | 1 | 24 hours | 1 | 0 | 1 | 0.2 | 0.2 |  | 30.4762 | 29 | SS Malyshevo 110/10 kv | 2.5 | 0.04425 | 0.84425 | 1 | 24 hours | 1 | 0 | 1 | 0.15575 | 0.15575 |  | 32.1619 | Bezhetskie Power networks
30 | SS Start 10/10 kv | 16 | 1.6 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0 | 0 |  | 9.5238 | 30 | SS Start 10/10 kv | 16 | 0.0375 | 1.6375 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | -0.0375 | -0.0375 | MS is closed | 9.747 | Bezhetskie Power networks
31 | SS Rassvet 110/35 kv | 10 | 4.5 | 5 | 24 hours | 5 | 0 | 5 | 0.5 | 0.5 |  | 42.8571 | 31 | SS Rassvet 110/35 kv | 10 | 0.505 | 5.005 | 5 | 24 hours | 5 | 0 | 5 | -0.005 | -0.005 | MS is closed | 47.6667 | Bezhetskie Power networks
32 | SS Ivanovo 110/35/10 kv | 6.3 | 1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.3 | -0.8 | MS is closed | 15.1172 | 32 | SS Ivanovo 110/35/10 kv | 6.3 | 0.33625 | 1.3362 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | -0.03625 | -1.1362 | MS is closed | 20.2003 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 6.3 | 0.8 | 0 | 24 hours | 0 | 0 | 0 | -0.8 |  |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.33625 | 1.1362 | 0 | 24 hours | 0 | 0 | 0 | -1.1362
| Nom. capacity LV, MVA | 6.3 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 |  |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1
33 | SS Kesma 110/35/10 kv | 6.3 | 1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.4 | -0.2 | MS is closed | 15.1172 | 33 | SS Kesma 110/35/10 kv | 6.3 | 0 | 1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.4 | -0.2 | MS is closed | 15.1172 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 6.3 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2 |  |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2
| Nom. capacity LV, MVA | 6.3 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6 |  |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6
34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0.4 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.8 | -0.2 | MS is closed | 6.8027 | 34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0 | 0.4 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.8 | -0.2 | MS is closed | 6.8027 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 5.6 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2 |  |  |  |  | Nom. capacity MV, MVA | 5.6 | 0 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2
| Nom. capacity LV, MVA | 5.6 | 0.2 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1 |  |  |  |  | Nom. capacity LV, MVA | 5.6 | 0 | 0.2 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1
35 | SS Topalki 110/35/10 kv | 6.3 | 2.1 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 1.6 | 0 |  | 31.746 | 35 | SS Topalki 110/35/10 kv | 6.3 | 0.075 | 2.175 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 1.525 | -0.075 | MS is closed | 32.8798 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 6.3 | 1.9 | 1.9 | 24 hours | 1.9 | 0 | 1.9 | 0 |  |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.075 | 1.975 | 1.9 | 24 hours | 1.9 | 0 | 1.9 | -0.075
| Nom. capacity LV, MVA | 6.3 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 |  |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6
36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0.1 | 1 | 24 hours | -0.9 | 0 | 1.05 | 1.95 | 1.95 |  | 9.5238 | 36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0 | 0.1 | 1 | 24 hours | -0.9 | 0 | 1.05 | 1.95 | 1.95 |  | 9.5238 | Bezhetskie Power networks
37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 1.8 | 1.4 | 24 hours | 0.4 | 0 | 1.68 | 1.28 | 1.28 |  | 107.1429 | 37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 0.075 | 1.875 | 1.4 | 24 hours | 0.475 | 0 | 1.68 | 1.205 | 1.205 |  | 111.6071 | Bezhetskie Power networks
38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 4.3 | 1.9 | 24 hours | 2.4 | 0 | 4.2 | 1.8 | 1.8 |  | 102.381 | 38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 0.02 | 4.32 | 1.9 | 24 hours | 2.42 | 0 | 4.2 | 1.78 | 1.78 |  | 102.8571 | Bezhetskie Power networks
39 | SS Molokovo 35/10 kv | 2,5+4,0 | 1.2 | 1.5 | 24 hours | -0.3 | 0 | 2.63 | 2.93 | 2.93 |  | 45.6274 | 39 | SS Molokovo 35/10 kv | 2,5+4,0 | 0 | 1.2 | 1.5 | 24 hours | -0.3 | 0 | 2.63 | 2.93 | 2.93 |  | 45.6274 | Bezhetskie Power networks
40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 |  | 11.4068 | 40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 |  | 11.4068 | Bezhetskie Power networks
41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 1.2 | 1.4 | 24 hours | -0.2 | 0 | 1.68 | 1.88 | 1.88 |  | 71.4286 | 41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 0.162 | 1.362 | 1.4 | 24 hours | -0.038 | 0 | 1.68 | 1.718 | 1.718 |  | 81.0714 | Bezhetskie Power networks
42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 3.8 | 1.4 | 24 hours | 2.4 | 0 | 3.4 | 1 | 1 |  | 111.7647 | 42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 0.475 | 4.275 | 1.4 | 24 hours | 2.875 | 0 | 3.4 | 0.525 | 0.525 |  | 125.7353 | Bezhetskie Power networks
43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0.4 | 0.8 | 24 hours | -0.4 | 0 | 1.68 | 2.08 | 2.08 |  | 23.8095 | 43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0 | 0.4 | 0.8 | 24 hours | -0.4 | 0 | 1.68 | 2.08 | 2.08 |  | 23.8095 | Bezhetskie Power networks
44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0.9 | 1.8 | 24 hours | -0.9 | 0 | 6.62 | 7.52 | 7.52 |  | 13.5952 | 44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0.027 | 0.927 | 1.8 | 24 hours | -0.873 | 0 | 6.62 | 7.493 | 7.493 |  | 14.003 | Bezhetskie Power networks
45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 4.2 | 0 |  | 4.2 | 0 | 6.62 | 2.42 | 2.42 |  | 63.4441 | 45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 0.058 | 4.258 | 0 |  | 4.258 | 0 | 6.62 | 2.362 | 2.362 |  | 64.3202 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.62 | 6.62 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.015 | 0.015 | 0 |  | 0.015 | 0 | 6.62 | 6.605
| Nom. capacity LV, MVA | 6,3+6,3 | 4.2 | 0 |  | 4.2 | 0 | 6.62 | 2.42 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.043 | 4.243 | 0 |  | 4.243 | 0 | 6.62 | 2.377
46 | SS DVP 110/35/10 kv | 25,0+25,0 | 11.7 | 2.5 | 24 hours | 9.2 | 0 | 26.3 | 17.1 | 17.1 |  | 44.4867 | 46 | SS DVP 110/35/10 kv | 25,0+25,0 | 0 | 11.7 | 2.5 | 24 hours | 9.2 | 0 | 26.3 | 17.1 | 17.1 |  | 44.4867 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 25,0+25,0 | 4.6 | 2.5 | 24 hours | 2.1 | 0 | 26.3 | 24.2 |  |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0 | 4.6 | 2.5 | 24 hours | 2.1 | 0 | 26.3 | 24.2
| Nom. capacity LV, MVA | 25,0+25,0 | 7.1 | 0 |  | 7.1 | 0 | 26.3 | 19.2 |  |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0 | 7.1 | 0 |  | 7.1 | 0 | 26.3 | 19.2
47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 5.4 | 2 | 24 hours | 3.4 | 0 | 10.5 | 7.1 | 5.3 |  | 51.4286 | 47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 0 | 5.4 | 2 | 24 hours | 3.4 | 0 | 10.5 | 7.1 | 5.3 |  | 51.4286 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 10,0+10,0 | 0.2 | 2 | 24 hours | -1.8 | 0 | 10.5 | 12.3 |  |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.2 | 2 | 24 hours | -1.8 | 0 | 10.5 | 12.3
| Nom. capacity LV, MVA | 10,0+10,0 | 5.2 | 0 |  | 5.2 | 0 | 10.5 | 5.3 |  |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 5.2 | 0 |  | 5.2 | 0 | 10.5 | 5.3
48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 2.4 | 2.2 | 24 hours | 0.2 | 0 | 6.62 | 6.42 | 6.42 |  | 36.2538 | 48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 0 | 2.4 | 2.2 | 24 hours | 0.2 | 0 | 6.62 | 6.42 | 6.42 |  | 36.2538 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 6,3+6,3 | 2.2 | 2.2 | 24 hours | 0 | 0 | 6.62 | 6.62 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 2.2 | 2.2 | 24 hours | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, MVA | 6,3+6,3 | 0.2 | 0 |  | 0.2 | 0 | 6.62 | 6.42 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.2 | 0 |  | 0.2 | 0 | 6.62 | 6.42
49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 5.4 | 7.5 | 24 hours | -2.1 | 0 | 10.5 | 12.6 | 9.9 |  | 51.4286 | 49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 0.125 | 5.525 | 7.5 | 24 hours | -1.975 | 0 | 10.5 | 12.475 | 9.9 |  | 52.619 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 10,0+10,0 | 3.3 | 6 | 24 hours | -2.7 | 0 | 10.5 | 13.2 |  |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0.125 | 3.425 | 6 | 24 hours | -2.575 | 0 | 10.5 | 13.075
| Nom. capacity LV, MVA | 10,0+10,0 | 2.1 | 1.5 | 24 hours | 0.6 | 0 | 10.5 | 9.9 |  |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 2.1 | 1.5 | 24 hours | 0.6 | 0 | 10.5 | 9.9
50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 17.1 | 5 | 24 hours | 12.1 | 0 | 26.3 | 14.2 | 14.2 |  | 65.019 | 50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 0.064375 | 17.1644 | 5 | 24 hours | 12.1644 | 0 | 26.3 | 14.1356 | 14.1356 |  | 65.2638 | Bezhetskie Power networks
| Nom. capacity MV, MVA | 25,0+25,0 | 5.9 | 5 | 24 hours | 0.9 | 0 | 26.3 | 25.4 |  |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0.026875 | 5.9269 | 5 | 24 hours | 0.92688 | 0 | 26.3 | 25.3731
| Nom. capacity LV, MVA | 25,0+25,0 | 11.2 | 0 |  | 11.2 | 0 | 26.3 | 15.1 |  |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0.0375 | 11.2375 | 0 |  | 11.2375 | 0 | 26.3 | 15.0625
51 | SS Belsky Karyer 35/6 kv | 4 | 0.08 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.07 | -0.07 | MS is closed | 1.9048 | 51 | SS Belsky Karyer 35/6 kv | 4 | 0 | 0.08 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.07 | -0.07 | MS is closed | 1.9048 | Vyshnevolotskie Power networks
52 | SS Dubrovka 35/10 kv | 1.6 | 0.17 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0.07 | 0.07 |  | 10.119 | 52 | SS Dubrovka 35/10 kv | 1.6 | 0 | 0.17 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0.07 | 0.07 |  | 10.119 | Vyshnevolotskie Power networks
53 | SS Zhilotkovo 35/10 kv | 1.8 | 0.19 | 0 |  | 0 | 0 | 0 | -0.19 | -0.19 | MS is closed | 10.0529 | 53 | SS Zhilotkovo 35/10 kv | 1.8 | 0 | 0.19 | 0 |  | 0 | 0 | 0 | -0.19 | -0.19 | MS is closed | 10.0529 | Vyshnevolotskie Power networks
54 | SS Kopachevo 35/10 kv | 1.6 | 0.47 | 0.47 | 24 hours | 0.47 | 0 | 0.47 | 0 | 0 |  | 27.9762 | 54 | SS Kopachevo 35/10 kv | 1.6 | 0 | 0.47 | 0.47 | 24 hours | 0.47 | 0 | 0.47 | 0 | 0 |  | 27.9762 | Vyshnevolotskie Power networks
55 | SS Kuznetsovo 35/10 kv | 1.6 | 0.51 | 0.51 | 24 hours | 0.51 | 0 | 0.51 | 0 | 0 |  | 30.3571 | 55 | SS Kuznetsovo 35/10 kv | 1.6 | 0 | 0.51 | 0.51 | 24 hours | 0.51 | 0 | 0.51 | 0 | 0 |  | 30.3571 | Vyshnevolotskie Power networks
56 | SS Luzhnikovo 35/10 kv | 2.5 | 0.102 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | -0.002 | -0.002 | MS is closed | 3.8857 | 56 | SS Luzhnikovo 35/10 kv | 2.5 | 0 | 0.102 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | -0.002 | -0.002 | MS is closed | 3.8857 | Vyshnevolotskie Power networks
57 | SS Nasakino 35/10 kv | 0.56 | 0.05 | 0 |  | 0 | 0 | 0 | -0.05 | -0.05 | MS is closed | 8.5034 | 57 | SS Nasakino 35/10 kv | 0.56 | 0 | 0.05 | 0 |  | 0 | 0 | 0 | -0.05 | -0.05 | MS is closed | 8.5034 | Vyshnevolotskie Power networks
58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 1.32 | 1.32 | 24 hours | 1.32 | 0 | 1.32 | 0 | 0 |  | 5.0286 | 58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 0 | 1.32 | 1.32 | 24 hours | 1.32 | 0 | 1.32 | 0 | 0 |  | 5.0286 | Vyshnevolotskie Power networks
59 | SS Porozhki 35/10 kv | 1 | 0.43 | 0.43 | 24 hours | 0.43 | 0 | 0.43 | 0 | 0 |  | 40.9524 | 59 | SS Porozhki 35/10 kv | 1 | 0.04905 | 0.47905 | 0.43 | 24 hours | 0.43 | 0 | 0.43 | -0.04905 | -0.04905 | MS is closed | 45.6238 | Vyshnevolotskie Power networks
60 | SS Kh.B.K. 35/6 kv | 4 | 2.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -1.8 | -1.8 | MS is closed | 64.2857 | 60 | SS Kh.B.K. 35/6 kv | 4 | 0 | 2.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -1.8 | -1.8 | MS is closed | 64.2857 | Vyshnevolotskie Power networks
61 | SS no.5 35/6 kv | 1.0+1.6 | 0.65 | 0 |  | 0.65 | 0 | 1.05 | 0.4 | 0.4 |  | 61.9048 | 61 | SS no.5 35/6 kv | 1.0+1.6 | 0 | 0.65 | 0 |  | 0.65 | 0 | 1.05 | 0.4 | 0.4 |  | 61.9048 | Vyshnevolotskie Power networks
62 | SS 9-е Yanvarya 35/10 kv | 6,3+10 | 3.04 | 0 |  | 3.04 | 0 | 6.62 | 3.58 | 3.58 |  | 45.9215 | 62 | SS 9-е Yanvarya 35/10 kv | 6,3+10 | 0 | 3.04 | 0 |  | 3.04 | 0 | 6.62 | 3.58 | 3.58 |  | 45.9215 | Vyshnevolotskie Power networks
63 | SS AKU 35/6 kv | 3,2+4 | 0.752 | 0.2 | 120 | 0.552 | 0 | 3.36 | 2.808 | 2.808 |  | 22.381 | 63 | SS AKU 35/6 kv | 3,2+4 | 0 | 0.752 | 0.2 | 120 | 0.552 | 0 | 3.36 | 2.608 | 2.608 |  | 22.381 | Vyshnevolotskie Power networks
64 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0.05 | 0 |  | 0.05 | 0 | 1.05 | 1 | 1 |  | 4.7619 | 64 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0 | 0.05 | 0 |  | 0.05 | 0 | 1.05 | 1 | 1 |  | 4.7619 | Vyshnevolotskie Power networks
65 | SS B-4 110/6 kv | 10+10 | 3.968 | 0 |  | 3.968 | 0 | 10.5 | 6.532 | 6.532 |  | 37.7905 | 65 | SS B-4 110/6 kv | 10+10 | 0 | 3.968 | 0 |  | 3.968 | 0 | 10.5 | 6.532 | 6.532 |  | 37.7905 | Vyshnevolotskie Power networks
66 | SS Borisovo 35/6 kv | 3.2+3.2 | 2.67 | 0 |  | 2.67 | 0 | 3.36 | 0.69 | 0.69 |  | 79.4643 | 66 | SS Borisovo 35/6 kv | 3.2+3.2 | 0 | 2.67 | 0 |  | 2.67 | 0 | 3.36 | 0.69 | 0.69 |  | 79.4643 | Vyshnevolotskie Power networks
67 | SS Borovno 35/10 kv | 2.5+2.5 | 0.58 | 0.2 | 120 | 0.38 | 0 | 2.63 | 2.25 | 2.25 |  | 22.0532 | 67 | SS Borovno 35/10 kv | 2.5+2.5 | 0 | 0.58 | 0.2 | 120 | 0.38 | 0 | 2.63 | 2.25 | 2.25 |  | 22.0532 | Vyshnevolotskie Power networks
68 | SS Bushevets 110/10 kv | 6.3+6.3 | 0.51 | 0 |  | 0.51 | 0 | 6.62 | 6.11 | 6.11 |  | 7.7039 | 68 | SS Bushevets 110/10 kv | 6.3+6.3 | 0 | 0.51 | 0 |  | 0.51 | 0 | 6.62 | 6.11 | 6.11 |  | 7.7039 | Vyshnevolotskie Power networks
69 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 3.7 | 0 |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 |  | 55.8912 | 69 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 0 | 3.7 | 0 |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 |  | 55.8912 | Vyshnevolotskie Power networks
70 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0.425 | 0 |  | 0.425 | 0 | 1.68 | 1.255 | 1.255 |  | 25.2976 | 70 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0.1 | 0.525 | 0 |  | 0.525 | 0 | 1.68 | 1.155 | 1.155 |  | 31.25 | Vyshnevolotskie Power networks
71 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0.663 | 0.4 | 120 | 0.263 | 0 | 1.68 | 1.417 | 1.417 |  | 39.4643 | 71 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0.075 | 0.738 | 0.4 | 120 | 0.338 | 0 | 1.68 | 1.342 | 1.342 |  | 43.9286 | Vyshnevolotskie Power networks
72 | SS Gorodok 35/10 kv | 1.6+1.6 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 |  | 17.2024 | 72 | SS Gorodok 35/10 kv | 1.6+1.6 | 2.6515 | 2.9405 | 0 |  | 2.9405 | 0 | 1.68 | -1.2605 | -1.2605 | MS is closed | 175.0298 | Vyshnevolotskie Power networks
73 | SS DOZ 35/10 kv | 4+4 | 6.205 | 0 |  | 6.205 | 0 | 4.2 | -2.005 | -2.005 | MS is closed | 147.7381 | 73 | SS DOZ 35/10 kv | 4+4 | 0 | 6.205 | 0 |  | 6.205 | 0 | 4.2 | -2.005 | -2.005 | MS is closed | 147.7381 | Vyshnevolotskie Power networks
74 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.48 | 0 |  | 0.48 | 0 | 1.68 | 1.2 | 1.2 |  | 28.5714 | 74 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.02 | 0.5 | 0 |  | 0.5 | 0 | 1.68 | 1.18 | 1.18 |  | 29.7619 | Vyshnevolotskie Power networks
75 | SS Esenovichi 35/10 kv | 1.8+2.5 | 0.969 | 0 |  | 0.969 | 0 | 1.89 | 0.921 | 0.921 |  | 51.2698 | 75 | SS Esenovichi 35/10 kv | 1.8+2.5 | 0 | 0.969 | 0 |  | 0.969 | 0 | 1.89 | 0.921 | 0.921 |  | 51.2698 | Vyshnevolotskie Power networks
76 | SS CG 35/10 kv | 6.3+6.3 | 0.204 | 0 |  | 0.204 | 0 | 6.62 | 6.416 | 6.416 |  | 3.0816 | 76 | SS CG 35/10 kv | 6.3+6.3 | 0 | 0.204 | 0 |  | 0.204 | 0 | 6.62 | 6.416 | 6.416 |  | 3.0816 | Vyshnevolotskie Power networks
77 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0.59 | 0.2 | 120 | 0.39 | 0 | 6.62 | 6.23 | 6.23 |  | 8.9124 | 77 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0 | 0.59 | 0.2 | 120 | 0.39 | 0 | 6.62 | 6.23 | 6.23 |  | 8.9124 | Vyshnevolotskie Power networks
78 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0.66 | 0.2 | 120 | 0.46 | 0 | 2.63 | 2.17 | 2.17 |  | 25.0951 | 78 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0 | 0.66 | 0.2 | 120 | 0.46 | 0 | 2.63 | 2.17 | 2.17 |  | 25.0951 | Vyshnevolotskie Power networks
79 | SS Kozlovo 35/10 kv | 1.8+4 | 0.68 | 0 |  | 0.68 | 0 | 1.89 | 1.21 | 1.21 |  | 35.9788 | 79 | SS Kozlovo 35/10 kv | 1.8+4 | 0 | 0.68 | 0 |  | 0.68 | 0 | 1.89 | 1.21 | 1.21 |  | 35.9788 | Vyshnevolotskie Power networks
80 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 |  | 24.4048 | 80 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 |  | 24.4048 | Vyshnevolotskie Power networks
81 | SS Krasny May 35/6 kv | 10+10 | 2.25 | 0 |  | 2.25 | 0 | 10.5 | 8.25 | 8.25 |  | 21.4286 | 81 | SS Krasny May 35/6 kv | 10+10 | 0.025 | 2.275 | 0 |  | 2.275 | 0 | 10.5 | 8.225 | 8.225 |  | 21.6667 | Vyshnevolotskie Power networks
82 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 1.96 | 0.2 | 120 | 1.76 | 0 | 3.36 | 1.6 | 1.6 |  | 58.3333 | 82 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 0 | 1.96 | 0.2 | 120 | 1.76 | 0 | 3.36 | 1.6 | 1.6 |  | 58.3333 | Vyshnevolotskie Power networks
83 | SS Lukino 35/10 kv | 2.5+1.6 | 0.22 | 0 |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 |  | 13.0952 | 83 | SS Lukino 35/10 kv | 2.5+1.6 | 0 | 0.22 | 0 |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 |  | 13.0952 | Vyshnevolotskie Power networks
84 | SS Makarovo 35/6 kv | 4+4 | 0.85 | 0.1 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 |  | 20.2381 | 84 | SS Makarovo 35/6 kv | 4+4 | 0 | 0.85 | 0.1 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 |  | 20.2381 | Vyshnevolotskie Power networks
85 | SS Mankhino 110/10 kv | 2.5+2.5 | 0.26 | 0 |  | 0.26 | 0 | 2.63 | 2.37 | 2.37 |  | 9.8859 | 85 | SS Mankhino 110/10 kv | 2.5+2.5 | 0 | 0.26 | 0 |  | 0.26 | 0 | 2.63 | 2.37 | 2.37 |  | 9.8859 | Vyshnevolotskie Power networks
86 | SS Moldino 35/10 kv | 1+1 | 0.85 | 0.2 | 120 | 0.65 | 0 | 1.05 | 0.4 | 0.4 |  | 80.9524 | 86 | SS Moldino 35/10 kv | 1+1 | 0.025 | 0.875 | 0.2 | 120 | 0.675 | 0 | 1.05 | 0.375 | 0.375 |  | 83.3333 | Vyshnevolotskie Power networks
87 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0.697 | 0.5 | 120 | 0.197 | 0 | 1.05 | 0.853 | 0.853 |  | 66.381 | 87 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0.0358 | 0.7328 | 0.5 | 120 | 0.2328 | 0 | 1.05 | 0.8172 | 0.8172 |  | 69.7905 | Vyshnevolotskie Power networks
88 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 |  | 24.4048 | 88 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 |  | 24.4048 | Vyshnevolotskie Power networks
89 | SS OEZ 35/6 kv | 2.5+5.6 | 1.6 | 1.25 | 120 | 0.35 | 0 | 2.63 | 2.28 | 2.28 |  | 60.8365 | 89 | SS OEZ 35/6 kv | 2.5+5.6 | 0 | 1.6 | 1.25 | 120 | 0.35 | 0 | 2.63 | 2.28 | 2.28 |  | 60.8365 | Vyshnevolotskie Power networks
90 | SS Plotichno 35/10 kv | 1.8+1.6 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 |  | 17.2024 | 90 | SS Plotichno 35/10 kv | 1.8+1.6 | 0 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 |  | 17.2024 | Vyshnevolotskie Power networks
91 | SS Popovo 35/10 kv | 1+1 | 0.66 | 0 |  | 0.66 | 0 | 1.05 | 0.39 | 0.39 |  | 62.8571 | 91 | SS Popovo 35/10 kv | 1+1 | 0 | 0.66 | 0 |  | 0.66 | 0 | 1.05 | 0.39 | 0.39 |  | 62.8571 | Vyshnevolotskie Power networks
92 | SS Proletary 35/10 kv | 2.5+2.5 | 2.13 | 0.7 | 120 | 1.43 | 0 | 2.63 | 1.2 | 1.2 |  | 80.9886 | 92 | SS Proletary 35/10 kv | 2.5+2.5 | 0.155 | 2.285 | 0.7 | 120 | 1.585 | 0 | 2.63 | 1.045 | 1.045 |  | 86.8821 | Vyshnevolotskie Power networks
93 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0.34 | 0 |  | 0.34 | 0 | 2.63 | 2.29 | 2.29 |  | 12.9278 | 93 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0.015 | 0.355 | 0 |  | 0.355 | 0 | 2.63 | 2.275 | 2.275 |  | 13.4981 | Vyshnevolotskie Power networks
94 | SS Ryad 35/10 kv | 2.5+2.5 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.63 | 2.4 | 2.4 |  | 16.3498 | 94 | SS Ryad 35/10 kv | 2.5+2.5 | 0 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.63 | 2.4 | 2.4 |  | 16.3498 | Vyshnevolotskie Power networks
95 | Ss Seglino 35/10 kv | 1.6+1.6 | 0.68 | 0 |  | 0.68 | 0 | 1.68 | 1 | 1 |  | 40.4762 | 95 | Ss Seglino 35/10 kv | 1.6+1.6 | 0 | 0.68 | 0 |  | 0.68 | 0 | 1.68 | 1 | 1 |  | 40.4762 | Vyshnevolotskie Power networks
96 | SS Soroki 35/10 kv | 2.5+2.5 | 0.595 | 0 |  | 0.595 | 0 | 2.63 | 2.035 | 2.035 |  | 22.6236 | 96 | SS Soroki 35/10 kv | 2.5+2.5 | 0 | 0.595 | 0 |  | 0.595 | 0 | 2.63 | 2.035 | 2.035 |  | 22.6236 | Vyshnevolotskie Power networks
97 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0.7 | 0.4 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 |  | 41.6667 | 97 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0 | 0.7 | 0.4 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 |  | 41.6667 | Vyshnevolotskie Power networks
98 | SS Timkovo 35/10 kv | 1.6+1.6 | 1.003 | 0 |  | 1.003 | 0 | 1.68 | 0.677 | 0.677 |  | 59.7024 | 98 | SS Timkovo 35/10 kv | 1.6+1.6 | 0.10125 | 1.1042 | 0 |  | 1.1042 | 0 | 1.68 | 0.57575 | 0.57575 |  | 65.7292 | Vyshnevolotskie Power networks
99 | SS Firovo 35/10 kv | 2.5+2.5 | 1.785 | 1.35 | 120 | 0.435 | 0 | 2.63 | 2.195 | 2.195 |  | 67.8707 | 99 | SS Firovo 35/10 kv | 2.5+2.5 | 0 | 1.785 | 1.35 | 120 | 0.435 | 0 | 2.63 | 2.195 | 2.195 |  | 67.8707 | Vyshnevolotskie Power networks
100 | SS Yubileynaya 35/6 kv | 7.5+10 | 4.8 | 0.9 | 120 | 3.9 | 0 | 8.17 | 4.27 | 4.27 |  | 58.7515 | 100 | SS Yubileynaya 35/6 kv | 7.5+10 | 0.375 | 5.175 | 0.9 | 120 | 4.275 | 0 | 8.17 | 3.895 | 3.895 |  | 63.3415 | Vyshnevolotskie Power networks
101 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0.204 | 0.17 | 120 | 0.034 | 0 | 2.63 | 2.596 | 2.596 |  | 7.7567 | 101 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0 | 0.204 | 0.17 | 120 | 0.034 | 0 | 2.63 | 2.596 | 2.596 |  | 7.7567 | Vyshnevolotskie Power networks
102 | SS Brusovo 110/35/10 kv | 10+10 | 2.58 | 3.9 | 120 | -1.32 | 0 | 10.5 | 11.82 | 10.5 |  | 24.5714 | 102 | SS Brusovo 110/35/10 kv | 10+10 | 0.314 | 2.894 | 3.9 | 120 | -1.006 | 0 | 10.5 | 11.506 | 10.5 |  | 27.5619 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 10+10 | 2.1 | 2.1 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.1 | 2.1 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 0.48 | 1.8 | 120 | -1.32 | 0 | 10.5 | 11.82 |  |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.314 | 0.794 | 1.8 | 120 | -1.006 | 0 | 10.5 | 11.506
103 | SS Vypozovo 110/35/6 kv | 10+10 | 5.4 | 6.88 | 120 | -1.48 | 0 | 10.5 | 11.98 | 10.5 |  | 51.4286 | 103 | SS Vypozovo 110/35/6 kv | 10+10 | 0 | 5.4 | 6.88 | 120 | -1.48 | 0 | 10.5 | 11.98 | 10.5 |  | 51.4286 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 10+10 | 3.18 | 3.18 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 3.18 | 3.18 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 2.22 | 3.7 | 120 | -1.48 | 0 | 10.5 | 11.98 |  |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.22 | 3.7 | 120 | -1.48 | 0 | 10.5 | 11.98
104 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 28.7 | 19.6 | 120 | 9.1 | 0 | 42 | 32.9 | 30 |  | 68.3333 | 104 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 0.6125 | 29.3125 | 19.6 | 120 | 9.7125 | 0 | 42 | 32.2875 | 29.425 |  | 69.7917 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 40+40 | 22.8 | 10.8 | 120 | 12 | 0 | 42 | 30 |  |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.575 | 23.375 | 10.8 | 120 | 12.575 | 0 | 42 | 29.425
| Nom. capacity LV, MVA | 40+40 | 5.9 | 8.8 | 120 | -2.9 | 0 | 42 | 44.9 |  |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.0375 | 5.9375 | 8.8 | 120 | -2.8625 | 0 | 42 | 44.8625
105 | SS Kasharovo 110/35/10-6 kv | 25+20 | 11.99 | 11.5 | 120 | 0.49 | 0 | 21 | 20.51 | 20.51 |  | 57.0952 | 105 | SS Kasharovo 110/35/10-6 kv | 25+20 | 0.03125 | 12.0213 | 11.5 | 120 | 0.52125 | 0 | 21 | 20.4788 | 20.4788 |  | 57.244 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 25+20 | 7.2 | 7.2 | 120 | 0 | 0 | 21 | 21 |  |  |  |  | Nom. capacity MV, MVA | 25+20 | 0 | 7.2 | 7.2 | 120 | 0 | 0 | 21 | 21
| Nom. capacity LV, MVA | 25+20 | 4.79 | 4.3 | 120 | 0.49 | 0 | 21 | 20.51 |  |  |  |  | Nom. capacity LV, MVA | 25+20 | 0.03125 | 4.8213 | 4.3 | 120 | 0.52125 | 0 | 21 | 20.4788
106 | SS Spirovo 110/35/10 kv | 16+16 | 3.32 | 1.2 | 120 | 2.12 | 0 | 16.8 | 14.68 | 14.68 |  | 19.7619 | 106 | SS Spirovo 110/35/10 kv | 16+16 | 2.6515 | 5.9715 | 1.2 | 120 | 4.7715 | 0 | 16.8 | 12.0285 | 12.0285 |  | 35.5446 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 16+16 | 0.6 | 0.6 |  | 0 | 0 | 16.8 | 16.8 |  |  |  |  | Nom. capacity MV, MVA | 16+16 | 2.6515 | 3.2515 | 0.6 |  | 2.6515 | 0 | 16.8 | 14.1485
| Nom. capacity LV, MVA | 16+16 | 2.72 | 0.6 | 120 | 2.12 | 0 | 16.8 | 14.68 |  |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 2.72 | 0.6 | 120 | 2.12 | 0 | 16.8 | 14.68
107 | SS Trud 110/35/10 kv | 16+16 | 4.11 | 4.02 | 120 | 0.09 | 0 | 16.8 | 16.71 | 16.71 |  | 24.4643 | 107 | SS Trud 110/35/10 kv | 16+16 | 0.015 | 4.125 | 4.02 | 120 | 0.105 | 0 | 16.8 | 16.695 | 16.695 |  | 24.5536 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 16+16 | 4.02 | 4.02 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.015 | 4.035 | 4.02 | 120 | 0.015 | 0 | 16.8 | 16.785
| Nom. capacity LV, MVA | 16+16 | 0.09 | 0 |  | 0.09 | 0 | 16.8 | 16.71 |  |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 0.09 | 0 |  | 0.09 | 0 | 16.8 | 16.71
108 | SS Udomlya 110/35/10 kv | 25+25 | 9.06 | 11.16 | 120 | -2.1 | 0 | 26.25 | 28.35 | 26.25 |  | 34.5143 | 108 | SS Udomlya 110/35/10 kv | 25+25 | 9.423 | 18.483 | 11.16 | 120 | 7.3231 | 0 | 26.25 | 18.927 | 18.927 |  | 70.4116 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 25+25 | 3.96 | 3.96 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. capacity MV, MVA | 25+25 | 4.603 | 8.5631 | 3.96 | 120 | 4.603 | 0 | 26.25 | 21.647
| Nom. capacity LV, MVA | 25+25 | 5.1 | 7.2 | 120 | -2.1 | 0 | 26.25 | 28.35 |  |  |  |  | Nom. capacity LV, MVA | 25+25 | 4.82 | 9.92 | 7.2 | 120 | 2.72 | 0 | 26.25 | 23.53
109 | SS Kholokholenka 110/35/10 kv | 6.3+6.3 | 3.35 | 2.16 | 120 | 1.19 | 0 | 6.62 | 5.43 | 5.43 |  | 50.6042 | 109 | SS Kholokholenka 110/35/10 kv | 6.3+6.3 | 3.6 | 6.95 | 2.16 | 120 | 4.79 | 0 | 6.62 | 1.83 | 1.83 |  | 104.9849 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 6,3+6,3 | 2.16 | 2.16 | 120 | 0 | 0 | 6.62 | 6.62 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.1 | 2.26 | 2.16 | 120 | 0.1 | 0 | 6.62 | 6.52
| Nom. capacity LV, MVA | 6,3+6,3 | 1.19 | 0 |  | 1.19 | 0 | 6.62 | 5.43 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 3.5 | 4.69 | 0 |  | 4.69 | 0 | 6.62 | 1.93
110 | SS Leontyevo 110/35/10 kv | 25+25 | 2.969 | 2.88 | 120 | 0.089 | 0 | 26.25 | 26.161 | 26.161 |  | 11.3105 | 110 | SS Leontyevo 110/35/10 kv | 6.3+6.4 | 0.025 | 2.994 | -6.48 | 120 | 9.474 | 0 | 6.62 | -2.854 | -2.854 | MS is closed | 45.2266 | Vyshnevolotskie Power networks
| Nom. capacity MV, MVA | 25+25 | 2.88 | 2.88 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.025 | 2.905 | -2.16 | 120 | 5.065 | 0 | 6.62 | 1.555
| Nom. capacity LV, MVA | 25+25 | 0.089 | 0 |  | 0.089 | 0 | 26.25 | 26.161 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.089 | -4.32 |  | 4.409 | 0 | 6.62 | 2.211
111 | 35/6 kv Mikrorayonnaya | 6.3 | 2.2689 | 2.2689 | 24 hours | 2.2689 | 0 | 2.2689 | 0 | 0 |  | 34.2992 | 111 | 35/6 kv Mikrorayonnaya | 6.3 | 0 | 2.2689 | 2.2689 | 24 hours | 2.2689 | 0 | 2.2689 | 0 | 0 |  | 34.2992 | Kimrskie Power networks
112 | 35/10 kv Barykovo | 2,5 +2,5 | 0.94458 | 0 |  | 0.94458 | 0 | 2.625 | 1.6804 | 1.6804 |  | 35.984 | 112 | 35/10 kv Barykovo | 2,5 +2,5 | 0.1495 | 1.0941 | 0 |  | 1.0941 | 0 | 2.625 | 1.5309 | 1.5309 |  | 41.6792 | Kimrskie Power networks
113 | 35/10 kv B.Gorodok | 5,6 +6,3 | 3.5074 | 0 |  | 3.5074 | 0 | 5.88 | 2.3726 | 2.3726 |  | 59.6497 | 113 | 35/10 kv B.Gorodok | 5,6+6,3 | 2.5875 | 6.0949 | 0 |  | 6.0949 | 0 | 5.88 | -0.2149 | -0.2149 | MS is closed | 103.6548 | Kimrskie Power networks
114 | 35/10 kv Vega | 2,5 +2,5 | 0.7266 | 0 |  | 0.7266 | 0 | 2.625 | 1.8984 | 1.8984 |  | 27.68 | 114 | 35/10 kv Vega | 2,5 +2,5 | 0.23125 | 0.95785 | 0 |  | 0.95785 | 0 | 2.625 | 1.6671 | 1.6671 |  | 36.4895 | Kimrskie Power networks
115 | 35/10 kv Volga | 6,3+6,3 | 4.2324 | 0 |  | 4.2324 | 0 | 6.615 | 2.3826 | 2.3826 |  | 63.9825 | 115 | 35/10 kv Volga | 6,3+6,3 | 0.29 | 4.5224 | 0 |  | 4.5224 | 0 | 6.615 | 2.0926 | 2.0926 |  | 68.3665 | Kimrskie Power networks
116 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 1.9245 | 0 |  | 1.9245 | 0 | 2.625 | 0.70055 | 0.70055 |  | 73.3125 | 116 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 0.1368 | 2.0613 | 0 |  | 2.0613 | 0 | 2.625 | 0.56375 | 0.56375 |  | 78.5239 | Kimrskie Power networks
117 | 35/10 kv Kalyazin | 6,3 +6,3 | 7.1478 | 0 |  | 7.1478 | 0 | 6.615 | -0.53284 | -0.53284 | MS is closed | 108.0551 | 117 | 35/10 kv Kalyazin | 6,3 +6,3 | 1.9275 | 9.0753 | 0 |  | 9.0753 | 0 | 6.615 | -2.4603 | -2.4603 | MS is closed | 137.1934 | Kimrskie Power networks
118 | 35/10 kv Kimry | 16,0+16,0 | 8.1169 | 0 |  | 8.1169 | 0 | 16.8 | 8.6831 | 8.6831 |  | 48.3149 | 118 | 35/10 kv Kimry | 16,0+16,0 | 0.053 | 8.1699 | 0 |  | 8.1699 | 0 | 16.8 | 8.6301 | 8.6301 |  | 48.6304 | Kimrskie Power networks
119 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0.85376 | 0 |  | 0.85376 | 0 | 2.625 | 1.7712 | 1.7712 |  | 32.524 | 119 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0.018 | 0.87175 | 0 |  | 0.87175 | 0 | 2.625 | 1.7532 | 1.7532 |  | 33.2097 | Kimrskie Power networks
120 | 35/10 kv Kurortnaya | 4,0 +4,0 | 1.4532 | 0 |  | 1.4532 | 0 | 4.2 | 2.7468 | 2.7468 |  | 34.6 | 120 | 35/10 kv Kurortnaya | 4,0 +4,0 | 0.37625 | 1.8295 | 0 |  | 1.8295 | 0 | 4.2 | 2.3706 | 2.3706 |  | 43.5583 | Kimrskie Power networks
121 | 35/10 kv Mayak | 6,3 +6,3 | 3.4695 | 0 |  | 3.4695 | 0 | 6.615 | 3.1455 | 3.1455 |  | 52.4492 | 121 | 35/10 kv Mayak | 6,3 +6,3 | 1.9045 | 5.374 | 0 |  | 5.374 | 0 | 6.615 | 1.241 | 1.241 |  | 81.2398 | Kimrskie Power networks
122 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 2.2706 | 0 |  | 2.2706 | 0 | 4.2 | 1.9294 | 1.9294 |  | 54.0625 | 122 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 0.1135 | 2.3841 | 0 |  | 2.3841 | 0 | 4.2 | 1.8159 | 1.8159 |  | 56.7649 | Kimrskie Power networks
123 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0.52177 | 0 |  | 0.52177 | 0 | 1.89 | 1.3682 | 1.3682 |  | 27.6068 | 123 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0 | 0.52177 | 0 |  | 0.52177 | 0 | 1.89 | 1.3682 | 1.3682 |  | 27.6068 | Kimrskie Power networks
124 | 35/10 kv Neklyudovo | 1,6 +1,6 | 1.1807 | 0 |  | 1.1807 | 0 | 1.68 | 0.49928 | 0.49928 |  | 70.2812 | 124 | 35/10 kv Neklyudovo | 1,6 +1,6 | 0.143 | 1.3237 | 0 |  | 1.3237 | 0 | 1.68 | 0.35628 | 0.35628 |  | 78.7932 | Kimrskie Power networks
125 | 35/10 kv Nerl | 4,0 +2,5 | 1.3987 | 0 |  | 1.3987 | 0 | 2.625 | 1.2263 | 1.2263 |  | 53.284 | 125 | 35/10 kv Nerl | 4,0 +2,5 | 0.38275 | 1.7815 | 0 |  | 1.7815 | 0 | 2.625 | 0.84354 | 0.84354 |  | 67.865 | Kimrskie Power networks
126 | 35/10 kv Plutkovo | 2,5 +2,5 | 0.89009 | 0 |  | 0.89009 | 0 | 2.625 | 1.7349 | 1.7349 |  | 33.908 | 126 | 35/10 kv Plutkovo | 2,5 +2,5 | 0.2995 | 1.1896 | 0 |  | 1.1896 | 0 | 2.625 | 1.4354 | 1.4354 |  | 45.3175 | Kimrskie Power networks
127 | 35/10 kv Savtsino | 2,5 +2,5 | 0.23615 | 0 |  | 0.23615 | 0 | 2.625 | 2.3889 | 2.3889 |  | 8.9961 | 127 | 35/10 kv Savtsino | 2,5 +2,5 | 0 | 0.23615 | 0 |  | 0.23615 | 0 | 2.625 | 2.3889 | 2.3889 |  | 8.9961 | Kimrskie Power networks
128 | 35/10 kv Sotskoe | 1,6 +2,5 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 |  | 27.0312 | 128 | 35/10 kv Sotskoe | 1,6 +2,5 | 0 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 |  | 27.0312 | Kimrskie Power networks
129 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0.19981 | 0 |  | 0.19981 | 0 | 2.625 | 2.4252 | 2.4252 |  | 7.612 | 129 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0 | 0.19981 | 0 |  | 0.19981 | 0 | 2.625 | 2.4252 | 2.4252 |  | 7.612 | Kimrskie Power networks
130 | 35/10 kv Ulanovo | 1,6 +1,6 | 1.2055 | 0 |  | 1.2055 | 0 | 1.68 | 0.47454 | 0.47454 |  | 71.7538 | 130 | 35/10 kv Ulanovo | 1,6 +1,6 | 0.034 | 1.2395 | 0 |  | 1.2395 | 0 | 1.68 | 0.44054 | 0.44054 |  | 73.7776 | Kimrskie Power networks
131 | 35/10 kv Unitsy | 4,0 +4,0 | 0.2159 | 0 |  | 0.2159 | 0 | 4.2 | 3.9841 | 3.9841 |  | 5.1406 | 131 | 35/10 kv Unitsy | 4,0 +4,0 | 0 | 0.2159 | 0 |  | 0.2159 | 0 | 4.2 | 3.9841 | 3.9841 |  | 5.1406 | Kimrskie Power networks
132 | 35/10 kv Fenevo | 2,5 +2,5 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 |  | 9.8 | 132 | 35/10 kv Fenevo | 2,5 +2,5 | 0 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 |  | 9.8 | Kimrskie Power networks
133 | 35/10 kv Frolovo | 2,5 +2,5 | 0.84562 | 0 |  | 0.84562 | 0 | 2.625 | 1.7794 | 1.7794 |  | 32.2142 | 133 | 35/10 kv Frolovo | 2,5 +2,5 | 0.21625 | 1.0619 | 0 |  | 1.0619 | 0 | 2.625 | 1.5631 | 1.5631 |  | 40.4523 | Kimrskie Power networks
134 | 110/10 kv Zarnitsa | 10,0+10,0 | 0.10899 | 0 |  | 0.10899 | 0 | 10.5 | 10.391 | 10.391 |  | 1.038 | 134 | 110/10 kv Zarnitsa | 10,0+10,0 | 0.017 | 0.12599 | 0 |  | 0.12599 | 0 | 10.5 | 10.374 | 10.374 |  | 1.1999 | Kimrskie Power networks
135 | 110/10 kv Zobnino | 2,5 +2,5 | 0.78084 | 0 |  | 0.78084 | 0 | 2.625 | 1.8442 | 1.8442 |  | 29.7461 | 135 | 110/10 kv Zobnino | 2,5 +2,5 | 0 | 0.78084 | 0 |  | 0.78084 | 0 | 2.625 | 1.8442 | 1.8442 |  | 29.7461 | Kimrskie Power networks
136 | 110/10 kv Inyakino | 25,0+25,0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 |  | 0.88642 | 136 | 110/10 kv Inyakino | 25,0+25,0 | 0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 |  | 0.88642 | Kimrskie Power networks
137 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 |  | 2.1341 | 137 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 |  | 2.1341 | Kimrskie Power networks
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3+6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738
138 | 110/35/10 kv Borki | 40,0+25,0 | 21.0011 | 0 |  | 21.0011 | 0 | 26.25 | 5.2489 | 5.2489 |  | 80.0043 | 138 | 110/35/10 kv Borki | 40,0+25 | 5.2045 | 26.2056 | 0 |  | 26.2056 | 0 | 26.25 | 0.044383 | 0.044383 |  | 99.8309 | Kimrskie Power networks
| Nom. capacity MV, MVA | 40,0+25,0 | 17.1797 | 0 |  | 17.1797 | 0 | 26.25 | 9.0703 |  |  |  |  | Nom. capacity MV, MVA | 40,0+25 | 4.782 | 21.9617 | 0 |  | 21.9617 | 0 | 26.25 | 4.2883
| Nom. capacity LV, MVA | 40,0+25,0 | 3.8214 | 0 |  | 3.8214 | 0 | 26.25 | 22.4286 |  |  |  |  | Nom. capacity LV, MVA | 40,0+25 | 0.4225 | 4.2439 | 0 |  | 4.2439 | 0 | 26.25 | 22.0061
139 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 3.9329 | 0.83421 | 24 hours | 3.0986 | 0 | 6.615 | 3.5164 | 3.5164 |  | 59.4536 | 139 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 0.21925 | 4.1521 | 0.83421 | 24 hours | 3.3179 | 0 | 6.615 | 3.2971 | 3.2971 |  | 62.768 | Kimrskie Power networks
| Nom. capacity MV, MVA | 6,3 +6,3 | 2.2383 | 0.83421 | 24 hours | 1.4041 | 0 | 6.615 | 5.2109 |  |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0.143 | 2.3813 | 0.83421 | 24 hours | 1.5471 | 0 | 6.615 | 5.0679
| Nom. capacity LV, MVA | 6,3 +6,3 | 1.6945 | 0 |  | 1.6945 | 0 | 6.615 | 4.9205 |  |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0.07625 | 1.7708 | 0 |  | 1.7708 | 0 | 6.615 | 4.8442
140 | 110/35/10 kv Goritsy | 6,3 +6,3 | 1.9018 | 0.13131 | 24 hours | 1.7705 | 0 | 6.615 | 4.8445 | 4.8445 |  | 28.7504 | 140 | 110/35/10 kv Goritsy | 6,3 +6,3 | 0.025 | 1.9268 | 0.13131 | 24 hours | 1.7955 | 0 | 6.615 | 4.8195 | 4.8195 |  | 29.1283 | Kimrskie Power networks
| Nom. capacity MV, MVA | 6,3 +6,3 | 0.13131 | 0.13131 | 24 hours | 0 | 0 | 6.615 | 6.615 |  |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0 | 0.13131 | 0.13131 | 24 hours | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3 +6,3 | 1.7705 | 0 |  | 1.7705 | 0 | 6.615 | 4.8445 |  |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0.025 | 1.7955 | 0 |  | 1.7955 | 0 | 6.615 | 4.8195
141 | 110/35/10 kv Luch | 16,0+16,0 | 16.7201 | 0 |  | 16.7201 | 0 | 16.8 | 0.079858 | 0.079858 |  | 99.5247 | 141 | 110/35/10 kv Luch | 16,0+16,0 | 7.2447 | 23.9649 | 0 |  | 23.9649 | 0 | 16.8 | -7.1649 | -7.1649 | MS is closed | 142.6482 | Kimrskie Power networks
| Nom. capacity MV, MVA | 16,0+16,0 | 12.994 | 0 |  | 12.994 | 0 | 16.8 | 3.806 |  |  |  |  | Nom. capacity MV, MVA | 16,0+16,0 | 2.4922 | 15.4863 | 0 |  | 15.4863 | 0 | 16.8 | 1.3137
| Nom. capacity LV, MVA | 16,0+16,0 | 3.7261 | 0 |  | 3.7261 | 0 | 16.8 | 13.0739 |  |  |  |  | Nom. capacity LV, MVA | 16,0+16,0 | 4.7525 | 8.4786 | 0 |  | 8.4786 | 0 | 16.8 | 8.3214
142 | 110/35/10 kv Prostor | 25,0+16,0 | 12.8011 | 0.45413 | 24 hours | 12.347 | 0 | 16.8 | 4.453 | 4.453 |  | 76.1969 | 142 | 110/35/10 kv Prostor | 25,0+16,0 | 1.2355 | 14.0366 | 0.45413 | 24 hours | 13.5825 | 0 | 16.8 | 3.2175 | 3.2175 |  | 83.5511 | Kimrskie Power networks
| Nom. capacity MV, MVA | 25,0+16,0 | 4.2514 | 0.45413 | 24 hours | 3.7973 | 0 | 16.8 | 13.0027 |  |  |  |  | Nom. capacity MV, MVA | 25,0+16,0 | 0.76 | 5.0114 | 0.45413 | 24 hours | 4.5573 | 0 | 16.8 | 12.2427
| Nom. capacity LV, MVA | 25,0+16,0 | 8.5497 | 0 |  | 8.5497 | 0 | 16.8 | 8.2503 |  |  |  |  | Nom. capacity LV, MVA | 25,0+16,0 | 0.4755 | 9.0252 | 0 |  | 9.0252 | 0 | 16.8 | 7.7748
143 | 110/35/10 kv Raduga | 40,0+25,0 | 25.7398 | 0.13 | 24 hours | 25.6098 | 0 | 26.25 | 0.64022 | 0.64022 |  | 98.0563 | 143 | 110/35/10 kv Raduga | 40,0+25 | 63.3461 | 89.0859 | 0.13 | 24 hours | 88.9559 | 0 | 26.25 | -62.7059 | -62.7059 | MS is closed | 339.3748 | Kimrskie Power networks
| Nom. capacity MV, MVA | 40,0+25,0 | 17.9833 | 0.13 | 24 hours | 17.8533 | 0 | 26.25 | 8.3967 |  |  |  |  | Nom. capacity MV, MVA | 40,0+25 | 0.1898 | 18.1731 | 0.13 | 24 hours | 18.0431 | 0 | 26.25 | 8.2069
| Nom. capacity LV, MVA | 40,0+25,0 | 7.7565 | 0 |  | 7.7565 | 0 | 26.25 | 18.4935 |  |  |  |  | Nom. capacity LV, MVA | 40,0+25 | 63.1563 | 70.9128 | 0 |  | 70.9128 | 0 | 26.25 | -44.6628
144 | 110/35/10 kv Roshcha | 10,0+10,0 | 4.2683 | 0.39963 | 24 hours | 3.8686 | 0 | 10.5 | 6.6314 | 6.6314 |  | 40.6502 | 144 | 110/35/10 kv Roshcha | 10,0+10,0 | 0.9585 | 5.2268 | 0.39963 | 24 hours | 4.8271 | 0 | 10.5 | 5.6729 | 5.6729 |  | 49.7787 | Kimrskie Power networks
| Nom. capacity MV, MVA | 10,0+10,0 | 0.8657 | 0.39963 | 24 hours | 0.46607 | 0 | 10.5 | 10.0339 |  |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.8657 | 0.39963 | 24 hours | 0.46607 | 0 | 10.5 | 10.0339
| Nom. capacity LV, MVA | 10,0+10,0 | 3.4026 | 0 |  | 3.4026 | 0 | 10.5 | 7.0974 |  |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0.9585 | 4.3611 | 0 |  | 4.3611 | 0 | 10.5 | 6.1389
145 | SS 110/10 kv Bibirevo | 2.5 | 0.1 | 1 | 24 hours | 1 | 0 | 1 | 0.9 | 0.9 |  | 3.8095 | 145 | SS 110/10 kv Bibirevo | 2.5 | 0 | 0.1 | 1 | 24 hours | 1 | 0 | 1 | 0.9 | 0.9 |  | 3.8095 | Nelidovskie Power networks
146 | SS 35/10 kv Bor | 1.6 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 |  | 11.9048 | 146 | SS 35/10 kv Bor | 1.6 | 0 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 |  | 11.9048 | Nelidovskie Power networks
147 | SS 110/10 kv Vorobyi | 2.5 | 0.3 | 1 | 24 hours | 1 | 0 | 1 | 0.7 | 0.7 |  | 11.4286 | 147 | SS 110/10 kv Vorobyi | 2.5 | 0 | 0.3 | 1 | 24 hours | 1 | 0 | 1 | 0.7 | 0.7 |  | 11.4286 | Nelidovskie Power networks
148 | SS 35/10 kv Glazomichi | 2.5 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 3.8095 | 148 | SS 35/10 kv Glazomichi | 2.5 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 3.8095 | Nelidovskie Power networks
149 | SS 35/10 kv Zharki | 10 | 2.2 | 0 |  | 0 | 0 | 0 | -2.2 | -2.2 | MS is closed | 20.9524 | 149 | SS 35/10 kv Zharki | 10 | 0.138 | 2.338 | 0 |  | 0 | 0 | 0 | -2.338 | -2.338 | MS is closed | 22.2667 | Nelidovskie Power networks
150 | SS 35/10 kv Zemtsy | 2.5 | 0.5 | 1 | 24 hours | 1 | 0 | 1 | 0.5 | 0.5 |  | 19.0476 | 150 | SS 35/10 kv Zemtsy | 2.5 | 0 | 0.5 | 1 | 24 hours | 1 | 0 | 1 | 0.5 | 0.5 |  | 19.0476 | Nelidovskie Power networks
151 | SS 35/10 kv Kovalevo | 2.5 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 |  | 7.619 | 151 | SS 35/10 kv Kovalevo | 2.5 | 0 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 |  | 7.619 | Nelidovskie Power networks
152 | SS 35/10 kv Korotyshi | 1.6 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 |  | 17.8571 | 152 | SS 35/10 kv Korotyshi | 1.6 | 0 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 |  | 17.8571 | Nelidovskie Power networks
153 | SS 110/10 kv Monino | 6.3 | 1.3 | 1 | 24 hours | 1 | 0 | 1 | -0.3 | -0.3 | MS is closed | 19.6523 | 153 | SS 110/10 kv Monino | 6.3 | 0.165 | 1.465 | 1 | 24 hours | 1 | 0 | 1 | -0.465 | -0.465 | MS is closed | 22.1466 | Nelidovskie Power networks
154 | SS 35/10 kv Ozerets | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | 11.9048 | 154 | SS 35/10 kv Ozerets | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | 11.9048 | Nelidovskie Power networks
155 | SS 35/10 kv Pozhnya | 1.6 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 |  | 11.9048 | 155 | SS 35/10 kv Pozhnya | 1.6 | 0.035 | 0.235 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.365 | 0.365 |  | 13.9881 | Nelidovskie Power networks
156 | SS 35/10 kv Polovtsovo | 1.6 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 |  | 23.8095 | 156 | SS 35/10 kv Polovtsovo | 1.6 | 0 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 |  | 23.8095 | Nelidovskie Power networks
157 | SS 110/10 kv Ponizovye | 2.5 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 |  | 11.4286 | 157 | SS 110/10 kv Ponizovye | 2.5 | 0.056 | 0.356 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.344 | 0.344 |  | 13.5619 | Nelidovskie Power networks
158 | SS 35/10 kv Sinkovo | 1 | 0.2 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0.1 | 0.1 |  | 19.0476 | 158 | SS 35/10 kv Sinkovo | 1 | 0.029 | 0.229 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0.071 | 0.071 |  | 21.8095 | Nelidovskie Power networks
159 | SS 35/10 kv Ulin | 1.6 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed | 17.8571 | 159 | SS 35/10 kv Ulin | 1.6 | 0 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed | 17.8571 | Nelidovskie Power networks
160 | SS 35/10 kv Kavelshchino | 2.5 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 7.619 | 160 | SS 35/10 kv Kavelshchino | 2.5 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 |  | 7.619 | Nelidovskie Power networks
161 | SS 35/10 kv Bologovo | 1,6+2,5 | 0.3 | 0.7 | 120 | -0.4 | 0 | 1.68 | 2.08 | 2.08 |  | 17.8571 | 161 | SS 35/10 kv Bologovo | 1,6+2,5 | 0.2425 | 0.5425 | 0.7 | 120 | -0.1575 | 0 | 1.68 | 1.8375 | 1.8375 |  | 32.2917 | Nelidovskie Power networks
162 | SS 35/10 kv Verkhovye | 1+2,5 | 0.2 | 1 | 120 | -0.8 | 0 | 1.05 | 1.85 | 1.85 |  | 19.0476 | 162 | SS 35/10 kv Verkhovye | 1+2,5 | 0 | 0.2 | 1 | 120 | -0.8 | 0 | 1.05 | 1.85 | 1.85 |  | 19.0476 | Nelidovskie Power networks
163 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0.3 | 0.7 | 120 | -0.4 | 0 | 1.68 | 2.08 | 2.08 |  | 17.8571 | 163 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0.073 | 0.373 | 0.7 | 120 | -0.327 | 0 | 1.68 | 2.007 | 2.007 |  | 22.2024 | Nelidovskie Power networks
164 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0.5 | 1 | 120 | -0.5 | 0 | 2.65 | 3.15 | 3.15 |  | 18.8679 | 164 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0 | 0.5 | 1 | 120 | -0.5 | 0 | 2.65 | 3.15 | 3.15 |  | 18.8679 | Nelidovskie Power networks
165 | SS 35/10 kv Ilyino | 1,6+1,6 | 0.6 | 0.9 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 |  | 35.7143 | 165 | SS 35/10 kv Ilyino | 1,6+1,6 | 0 | 0.6 | 0.9 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 |  | 35.7143 | Nelidovskie Power networks
166 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0.6 | 0.7 | 120 | -0.1 | 0 | 1.68 | 1.78 | 1.78 |  | 35.7143 | 166 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0.065 | 0.665 | 0.7 | 120 | -0.035 | 0 | 1.68 | 1.715 | 1.715 |  | 39.5833 | Nelidovskie Power networks
167 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 3.4 | 1.5 | 120 | 1.9 | 0 | 5.88 | 3.98 | 3.98 |  | 57.8231 | 167 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 0 | 3.4 | 1.5 | 120 | 1.9 | 0 | 5.88 | 3.98 | 3.98 |  | 57.8231 | Nelidovskie Power networks
168 | SS 35/10 kv St. Toropa | 4+4 | 1.8 | 0 |  | 1.8 | 0 | 4.5 | 2.7 | 2.7 |  | 40 | 168 | SS 35/10 kv St. Toropa | 4+4 | 0.05 | 1.85 | 0 |  | 1.85 | 0 | 4.5 | 2.65 | 2.65 |  | 41.1111 | Nelidovskie Power networks
169 | SS 110/35/10 kv Andreapol | 10+10 | 6.95 | 0.7 | 120 | 6.25 | 0 | 10.5 | 4.25 | 4.25 |  | 66.1905 | 169 | SS 110/35/10 kv Andreapol | 10+10 | 5.2416 | 12.1916 | 0.7 | 120 | 11.4916 | 0 | 10.5 | -0.99165 | -0.99165 | MS is closed | 116.111 | Nelidovskie Power networks
| Nom. capacity MV, MVA | 10+10 | 0.75 | 0 |  | 0.75 | 0 | 10.5 | 9.75 |  |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.34 | 1.09 | 0 |  | 1.09 | 0 | 10.5 | 9.41
| Nom. capacity LV, MVA | 10+10 | 6.2 | 0.7 | 120 | 5.5 | 0 | 10.5 | 5 |  |  |  |  | Nom. capacity LV, MVA | 10+10 | 4.9017 | 11.1016 | 0.7 | 120 | 10.4017 | 0 | 10.5 | 0.09835
170 | SS 110/35/10 kv Bely | 16+10 | 5.7 | 1 | 120 | 4.7 | 0 | 10.5 | 5.8 | 5.8 |  | 54.2857 | 170 | SS 110/35/10 kv Bely | 16+10 | 0.23425 | 5.9342 | 1 | 120 | 4.9342 | 0 | 10.5 | 5.5658 | 5.5658 |  | 56.5167 | Nelidovskie Power networks
| Nom. capacity MV, MVA | 16+10 | 3.1 | 0 |  | 3.1 | 0 | 10.5 | 7.4 |  |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.138 | 3.238 | 0 |  | 3.238 | 0 | 10.5 | 7.262
| Nom. capacity LV, MVA | 16+10 | 2.6 | 1 | 120 | 1.6 | 0 | 10.5 | 8.9 |  |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.09625 | 2.6963 | 1 | 120 | 1.6963 | 0 | 10.5 | 8.8038
171 | SS 110/35/10 kv Zapadnaya Dvina | 10+10 | 9.7 | 1 | 120 | 8.7 | 0 | 10.5 | 1.8 | 1.8 |  | 92.381 | 171 | SS 110/35/10 kv Zapadnaya Dvina | 10+10 | 0.15875 | 9.8588 | 1 | 120 | 8.8588 | 0 | 10.5 | 1.6413 | 1.6413 |  | 93.8929 | Nelidovskie Power networks
| Nom. capacity MV, MVA | 10+10 | 1.7 | 1 | 120 | 0.7 | 0 | 10.5 | 9.8 |  |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.05 | 1.75 | 1 | 120 | 0.75 | 0 | 10.5 | 9.75
| Nom. capacity LV, MVA | 10+10 | 8 | 0 |  | 8 | 0 | 10.5 | 2.5 |  |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.10875 | 8.1088 | 0 |  | 8.1088 | 0 | 10.5 | 2.3912
172 | SS 110/35/10 kv Toropets | 16+25 | 16.8 | 2.2 | 120 | 14.6 | 0 | 16.8 | 2.2 | 2.2 |  | 100 | 172 | SS 110/35/10 kv Toropets | 16+25 | 3.0475 | 19.8475 | 2.2 | 120 | 17.6475 | 0 | 16.8 | -0.8475 | -0.8475 | MS is closed | 118.1399 | Nelidovskie Power networks
| Nom. capacity MV, MVA | 16+25 | 4.9 | 1.2 | 120 | 3.7 | 0 | 16.8 | 13.1 |  |  |  |  | Nom. capacity MV, MVA | 16+25 | 0.173 | 5.073 | 1.2 | 120 | 3.873 | 0 | 16.8 | 12.927
| Nom. capacity LV, MVA | 16+25 | 11.9 | 1 | 120 | 10.9 | 0 | 16.8 | 5.9 |  |  |  |  | Nom. capacity LV, MVA | 16+25 | 2.8745 | 14.7745 | 1 | 120 | 13.7745 | 0 | 16.8 | 3.0255
173 | SS Bakhmutovo 35/10 kv | 2.5 | 0.50862 | 0.50862 | 120 | 0.50862 | 0 | 0.50862 | 0 | 0 |  | 19.376 | 173 | SS Bakhmutovo 35/10 kv | 2.5 | 0 | 0.50862 | 0.50862 | 120 | 0.50862 | 0 | 0.50862 | 0 | 0 |  | 19.376 | Rzhevskie Power networks
174 | SS Pyatnitskoe 35/10kv | 2.5 | 0.18165 | 0.18165 | 240 | 0.18165 | 0 | 0.18165 | 0 | 0 |  | 6.92 | 174 | SS Pyatnitskoe 35/10kv | 2.5 | 0.03 | 0.21165 | 0.18165 | 240 | 0.18165 | 0 | 0.18165 | -0.03 | -0.03 | MS is closed | 8.0629 | Rzhevskie Power networks
175 | SS Karamzino 35/10kv | 1.6 | 0.3633 | 0 |  | 0 | 0 | 0 | -0.3633 | -0.3633 | MS is closed | 21.625 | 175 | SS Karamzino 35/10kv | 1.6 | 0.075 | 0.4383 | 0 |  | 0 | 0 | 0 | -0.4383 | -0.4383 | MS is closed | 26.0893 | Rzhevskie Power networks
176 | SS Kn. Gory 35/10kv | 2.5 | 1.2715 | 0.23333 | 240 | 0.23333 | 0 | 0.23333 | -1.0382 | -1.0382 | MS is closed | 48.44 | 176 | SS Kn. Gory 35/10kv | 2.5 | 0.55 | 1.8216 | 0.23333 | 240 | 0.23333 | 0 | 0.23333 | -1.5882 | -1.5882 | MS is closed | 69.3924 | Rzhevskie Power networks
177 | SS Salino 35/10kv | 2.5 | 0.4498 | 0 |  | 0 | 0 | 0 | -0.4498 | -0.4498 | MS is closed | 17.1352 | 177 | SS Salino 35/10kv | 2.5 | 0.25 | 0.6998 | 0 |  | 0 | 0 | 0 | -0.6998 | -0.6998 | MS is closed | 26.659 | Rzhevskie Power networks
178 | SS Gusevo 35/10kv | 2.5 | 0.30448 | 0.30448 | 120 | 0.30448 | 0 | 0.30448 | 0 | 0 |  | 11.5992 | 178 | SS Gusevo 35/10kv | 2.5 | 0 | 0.30448 | 0.30448 | 120 | 0.30448 | 0 | 0.30448 | 0 | 0 |  | 11.5992 | Rzhevskie Power networks
179 | SS Mol.Tud 35/10kv | 2.5 | 0.45413 | 0.45413 | 120 | 0.45413 | 0 | 0.45413 | 0 | 0 |  | 17.3 | 179 | SS Mol.Tud 35/10kv | 2.5 | 0.015 | 0.46913 | 0.45413 | 120 | 0.45413 | 0 | 0.45413 | -0.015 | -0.015 | MS is closed | 17.8714 | Rzhevskie Power networks
180 | SS Ilyenki 35/10kv | 2.5 | 0.1429 | 0.1429 | 120 | 0.1429 | 0 | 0.1429 | 0 | 0 |  | 5.4437 | 180 | SS Ilyenki 35/10kv | 2.5 | 0 | 0.1429 | 0.1429 | 120 | 0.1429 | 0 | 0.1429 | 0 | 0 |  | 5.4437 | Rzhevskie Power networks
181 | SS Kadenka 35/10kv | 1 | 0.23614 | 0.23614 | 120 | 0.23614 | 0 | 0.23614 | 0 | 0 |  | 22.49 | 181 | SS Kadenka 35/10kv | 1 | 0 | 0.23614 | 0.23614 | 120 | 0.23614 | 0 | 0.23614 | 0 | 0 |  | 22.49 | Rzhevskie Power networks
182 | SS Rodnya 35/10kv | 2.5 | 0.4588 | 0.4588 | 120 | 0.4588 | 0 | 0.4588 | 0 | 0 |  | 17.4779 | 182 | SS Rodnya 35/10kv | 2.5 | 0.447 | 0.9058 | 0.4588 | 120 | 0.4588 | 0 | 0.4588 | -0.447 | -0.447 | MS is closed | 34.5065 | Rzhevskie Power networks
183 | SS Bernovo 35/10kv | 1.6 | 0.5792 | 0 |  | 0 | 0 | 0 | -0.5792 | -0.5792 | MS is closed | 34.4764 | 183 | SS Bernovo 35/10kv | 1.6 | 0 | 0.5792 | 0 |  | 0 | 0 | 0 | -0.5792 | -0.5792 | MS is closed | 34.4764 | Rzhevskie Power networks
184 | SS RMK 35/10kv | 10+10 | 13.67 | 8.1167 | 240 | 5.5533 | 0 | 10.5 | 4.9467 | 4.9467 |  | 130.1905 | 184 | SS RMK 35/10kv | 10+10 | 0.088 | 13.758 | 8.1167 | 240 | 5.6413 | 0 | 10.5 | 4.8587 | 4.8587 |  | 131.0286 | Rzhevskie Power networks
185 | SS Osuga 35/10kv | 2,5+2,5 | 0.23 | 0 |  | 0.23 | 0 | 2.625 | 2.395 | 2.395 |  | 8.7619 | 185 | SS Osuga 35/10kv | 2,5+2,5 | 0 | 0.23 | 0 |  | 0.23 | 0 | 2.625 | 2.395 | 2.395 |  | 8.7619 | Rzhevskie Power networks
186 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.58 | 0 |  | 1.58 | 0 | 2.625 | 1.045 | 1.045 |  | 60.1905 | 186 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.5415 | 3.1215 | 0 |  | 3.1215 | 0 | 2.625 | -0.4965 | -0.4965 | MS is closed | 118.9143 | Rzhevskie Power networks
187 | SS Kleshnevo 35/10kv | 4+4 | 0.88 | 0 |  | 0.88 | 0 | 4.2 | 3.32 | 3.32 |  | 20.9524 | 187 | SS Kleshnevo 35/10kv | 4+4 | 1.7625 | 2.6425 | 0 |  | 2.6425 | 0 | 4.2 | 1.5575 | 1.5575 |  | 62.9167 | Rzhevskie Power networks
188 | SS Zubtsov 35/10kv | 6,3+6,3 | 10.08 | 1.2167 | 120 | 8.8633 | 0 | 6.615 | -2.2483 | -2.2483 | MS is closed | 152.381 | 188 | SS Zubtsov 35/10kv | 6,3+6,3 | 2.509 | 12.589 | 1.2167 | 120 | 11.3723 | 0 | 6.615 | -4.7573 | -4.7573 | MS is closed | 190.3099 | Rzhevskie Power networks
189 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 2.6 | 1.2 | 240 | 1.4 | 0 | 5.88 | 4.48 | 4.48 |  | 44.2177 | 189 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 0.0625 | 2.6625 | 1.2 | 240 | 1.4625 | 0 | 5.88 | 4.4175 | 4.4175 |  | 45.2806 | Rzhevskie Power networks
190 | SS Stepurino 35/10kv | 4+4 | 1.28 | 0 |  | 1.28 | 0 | 4.2 | 2.92 | 2.92 |  | 30.4762 | 190 | SS Stepurino 35/10kv | 4+4 | 0 | 1.28 | 0 |  | 1.28 | 0 | 4.2 | 2.92 | 2.92 |  | 30.4762 | Rzhevskie Power networks
191 | SS Maksimovo 35/10kv | 2,5+2,5 | 0.42 | 0.42 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 |  | 16 | 191 | SS Maksimovo 35/10kv | 2,5+2,5 | 0 | 0.42 | 0.42 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 |  | 16 | Rzhevskie Power networks
192 | SS Lukovnikovo 35/10kv | 4+2,5 | 1.02 | 0 |  | 1.02 | 0 | 2.625 | 1.605 | 1.605 |  | 38.8571 | 192 | SS Lukovnikovo 35/10kv | 4+2,5 | 0.04 | 1.06 | 0 |  | 1.06 | 0 | 2.625 | 1.565 | 1.565 |  | 40.381 | Rzhevskie Power networks
193 | SS NTPF 110/10kv | 6,3+6,3 | 1.33 | 0 |  | 1.33 | 0 | 6.615 | 5.285 | 5.285 |  | 20.1058 | 193 | SS NTPF 110/10kv | 6,3+6,3 | 0.75 | 2.08 | 0 |  | 2.08 | 0 | 6.615 | 4.535 | 4.535 |  | 31.4437 | Rzhevskie Power networks
194 | SS Mostovaya 110/10kv | 6,3+6,3 | 1.7 | 0.46667 | 240 | 1.2333 | 0 | 6.615 | 5.3817 | 5.3817 |  | 25.6992 | 194 | SS Mostovaya 110/10kv | 6,3+6,3 | 0.4375 | 2.1375 | 0.46667 | 240 | 1.6708 | 0 | 6.615 | 4.9442 | 4.9442 |  | 32.3129 | Rzhevskie Power networks
195 | SS Rzhev 110/35/10kv | 40.5+40 | 48.2 | 5.1851 | 24 hours | 43.0149 | 0 | 42 | -1.0149 | -1.0149 | MS is closed | 114.7619 | 195 | SS Rzhev 110/35/10kv | 40.5+40 | 6.9635 | 55.1635 | 5.1851 | 24 hours | 49.9784 | 0 | 42 | -7.9784 | -7.9784 | MS is closed | 131.3417 | Rzhevskie Power networks
| Nom. capacity MV, MVA | 40.5+40 | 38.57 | 2.7684 | 24 hours | 35.8016 | 0 | 42 | 6.1984 |  |  |  |  | Nom. capacity MV, MVA | 40.5+40 | 6.8385 | 45.4085 | 2.7684 | 24 hours | 42.6401 | 0 | 42 | -0.64008
| Nom. capacity LV, MVA | 40.5+40 | 9.63 | 2.4167 | 120 | 7.2133 | 0 | 42 | 34.7867 |  |  |  |  | Nom. capacity LV, MVA | 40.5+40 | 0.125 | 9.755 | 2.4167 | 120 | 7.3383 | 0 | 42 | 34.6617
196 | SS Chertolino 110/35/10kv | 5,6+6,3 | 1.27 | 0.1 | 240 | 1.17 | 0 | 5.88 | 4.71 | 4.71 |  | 21.5986 | 196 | SS Chertolino 110/35/10kv | 5,6+6,3 | 0.03 | 1.3 | 0.1 | 240 | 1.2 | 0 | 5.88 | 4.68 | 4.68 |  | 22.1088 | Rzhevskie Power networks
| Nom. capacity MV, MVA | 5,6+6,3 | 0.1 | 0.1 | 240 | 0 | 0 | 5.88 | 5.88 |  |  |  |  | Nom. capacity MV, MVA | 5,6+6,3 | 0.03 | 0.13 | 0.1 | 240 | 0.03 | 0 | 5.88 | 5.85
| Nom. capacity LV, MVA | 5,6+6,3 | 1.17 | 0 |  | 1.17 | 0 | 5.88 | 4.71 |  |  |  |  | Nom. capacity LV, MVA | 5,6+6,3 | 0 | 1.17 | 0 |  | 1.17 | 0 | 5.88 | 4.71
197 | SS Olenino 110/35/10 | 16+10 | 4.36 | 0 |  | 4.36 | 0 | 10.5 | 6.14 | 6.14 |  | 41.5238 | 197 | SS Olenino 110/35/10 | 16+10 | 0.0275 | 4.3875 | 0 |  | 4.3875 | 0 | 10.5 | 6.1125 | 6.1125 |  | 41.7857 | Rzhevskie Power networks
| Nom. capacity MV, MVA | 16+10 | 0.97 | 0 |  | 0.97 | 0 | 10.5 | 9.53 |  |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.015 | 0.985 | 0 |  | 0.985 | 0 | 10.5 | 9.515
| Nom. capacity LV, MVA | 16+10 | 3.39 | 0 |  | 3.39 | 0 | 10.5 | 7.11 |  |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.0125 | 3.4025 | 0 |  | 3.4025 | 0 | 10.5 | 7.0975
198 | SS Staritsa 110/35/10kv | 16+16 | 12.39 | 4.2325 | 24 hours | 8.1575 | 0 | 16.8 | 8.6425 | 8.6425 |  | 73.75 | 198 | SS Staritsa 110/35/10kv | 16+16 | 2.1223 | 14.5122 | 4.2325 | 24 hours | 10.2797 | 0 | 16.8 | 6.5203 | 6.5203 |  | 86.3824 | Rzhevskie Power networks
| Nom. capacity MV, MVA | 16+16 | 3.76 | 3.2992 | 24 hours | 0.4608 | 0 | 16.8 | 16.3392 |  |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.487 | 4.247 | 3.2992 | 24 hours | 0.9478 | 0 | 16.8 | 15.8522
| Nom. capacity LV, MVA | 16+16 | 8.63 | 0.93333 | 240 | 7.6967 | 0 | 16.8 | 9.1033 |  |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.6353 | 10.2652 | 0.93333 | 240 | 9.3319 | 0 | 16.8 | 7.4681
199 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515 | 3.515 |  | 46.8632 | 199 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 0.6 | 3.7 | 0 |  | 3.7 | 0 | 6.615 | 2.915 | 2.915 |  | 55.9335 | Rzhevskie Power networks
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3+6,3 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515 |  |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.6 | 3.7 | 0 |  | 3.7 | 0 | 6.615 | 2.915
200 | SS Zolootval 110/10 | 2.5 | 0.42 | 0.42 | 24 hours | 0.42 | 0 | 0.42 | 0 | 0 |  | 16 | 200 | SS Zolootval 110/10 | 2.5 | 2.625 | 3.045 | 3.045 | 24 hours | 3.045 | 0 | 3.045 | 0 | 0 |  | 110.4762 | Tverskie Power networks
201 | SS Krasnogorskaya 35/10 | 1.6 | 0.83 | 0 |  | 0 | 0 | 0 | -0.83 | -0.83 | MS is closed | 49.4048 | 201 | SS Krasnogorskaya 35/10 | 1.6 | 0.10625 | 0.93625 | 0 |  | 0 | 0 | 0 | -0.93625 | -0.93625 | MS is closed | 55.7292 | Tverskie Power networks
202 | SS Lisitsky Bor 35/10 | 2.5 | 1.37 | 0 |  | 0 | 0 | 0 | -1.37 | -1.37 | MS is closed | 52.1905 | 202 | SS Lisitsky Bor 35/10 | 2.5 | 0.187 | 1.557 | 0 |  | 0 | 0 | 0 | -1.557 | -1.557 | MS is closed | 59.3143 | Tverskie Power networks
203 | SS Danilovskaya 35/10 | 2.5 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed | 19.0476 | 203 | SS Danilovskaya 35/10 | 2.5 | 0.86775 | 1.0108 | 0 |  | 0 | 0 | 0 | -1.0108 | -1.0108 | MS is closed | 38.5048 | Tverskie Power networks
204 | SS No.6 35/10 | 1 | 0.03 | 0 |  | 0 | 0 | 0 | -0.03 | -0.03 | MS is closed | 2.8571 | 204 | SS No.6 35/10 | 1 | 0 | 0.03 | 0 |  | 0 | 0 | 0 | -0.03 | -0.03 | MS is closed | 2.8571 | Tverskie Power networks
205 | SS No.1 35/6 | 1 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed | 47.619 | 205 | SS No.1 35/6 | 1 | 0 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed | 47.619 | Tverskie Power networks
| SS No.1 35/10 | 2.5 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed | 60.1905 |  | SS No.1 35/10 | 2.5 | 1.1027 | 2.6827 | 0 |  | 0 | 0 | 0 | -2.6827 | -2.6827 | MS is closed | 102.2 | Tverskie Power networks
206 | SS No.16 35/6 | 1 | 0.12 | 0 |  | 0 | 0 | 0 | -0.12 | -0.12 | MS is closed | 11.4286 | 206 | SS No.16 35/6 | 1 | 0 | 0.12 | 0 |  | 0 | 0 | 0 | -0.12 | -0.12 | MS is closed | 11.4286 | Tverskie Power networks
| SS No.16 35/10 | 2.5 | 0.85 | 0 |  | 0 | 0 | 0 | -0.85 | -0.85 | MS is closed | 32.381 |  | SS No.16 35/10 | 2.5 | 0 | 0.85 | 0 |  | 0 | 0 | 0 | -0.85 | -0.85 | MS is closed | 32.381 | Tverskie Power networks
207 | SS Zolotikha 35/10 | 2.5 | 0.8 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0 | 0 |  | 30.4762 | 207 | SS Zolotikha 35/10 | 2.5 | 0 | 0.8 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0 | 0 |  | 30.4762 | Tverskie Power networks
208 | SS Novy Stan 35/10 | 2.5 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 |  | 14.4762 | 208 | SS Novy Stan 35/10 | 2.5 | 0 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 |  | 14.4762 | Tverskie Power networks
209 | SS Romanovo 35/10 | 2.5 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 |  | 23.2381 | 209 | SS Romanovo 35/10 | 2.5 | 0 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 |  | 23.2381 | Tverskie Power networks
210 | SS Pervitino 35/10 | 1.6 | 0.34 | 0 |  | 0 | 0 | 0 | -0.34 | -0.34 | MS is closed | 20.2381 | 210 | SS Pervitino 35/10 | 1.6 | 0 | 0.34 | 0 |  | 0 | 0 | 0 | -0.34 | -0.34 | MS is closed | 20.2381 | Tverskie Power networks
211 | SS No. 8 35/10 | 2.5 | 1.53 | 0 |  | 0 | 0 | 0 | -1.53 | -1.53 | MS is closed | 58.2857 | 211 | SS No. 8 35/10 | 2.5 | 0.04125 | 1.5713 | 0 |  | 0 | 0 | 0 | -1.5713 | -1.5713 | MS is closed | 59.8571 | Tverskie Power networks
212 | SS Aleksino 35/6 | 2.5 | 1.02 | 0 |  | 0 | 0 | 0 | -1.02 | -1.02 | MS is closed | 38.8571 | 212 | SS Aleksino 35/6 | 2.5 | 1.804 | 2.824 | 0 |  | 0 | 0 | 0 | -2.824 | -2.824 | MS is closed | 107.581 | Tverskie Power networks
213 | SS Bezborodovo 35/10 | 2.5 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed | 60.1905 | 213 | SS Bezborodovo 35/10 | 2.5 | 0.5 | 2.08 | 0 |  | 0 | 0 | 0 | -2.08 | -2.08 | MS is closed | 79.2381 | Tverskie Power networks
214 | SS Medvedikha 110/10 | 2.5 | 0.57 | 0.57 | 24 hours | 0.57 | 0 | 0.57 | 0 | 0 |  | 21.7143 | 214 | SS Medvedikha 110/10 | 2.5 | 0.026 | 0.596 | 0.57 | 24 hours | 0.57 | 0 | 0.57 | -0.026 | -0.026 | MS is closed | 22.7048 | Tverskie Power networks
215 | SS Kivirichi 35/10 | 2.5 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 | -0.7 | MS is closed | 26.6667 | 215 | SS Kivirichi 35/10 | 2.5 | 0 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 | -0.7 | MS is closed | 26.6667 | Tverskie Power networks
216 | SS Dievo 35/10 | 2.5 | 0.22 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.03 | 0.03 |  | 8.381 | 216 | SS Dievo 35/10 | 2.5 | 0 | 0.22 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.03 | 0.03 |  | 8.381 | Tverskie Power networks
217 | SS No.17 35/10 | 4+4 | 0.62 | 0 |  | 0.62 | 0 | 4.2 | 3.58 | 3.58 |  | 14.7619 | 217 | SS No.17 35/10 | 4+4 | 0 | 0.62 | 0 |  | 0.62 | 0 | 4.2 | 3.58 | 3.58 |  | 14.7619 | Tverskie Power networks
218 | SS Kushalino 35/10 | 2,5+2,5 | 1.81 | 0 |  | 1.81 | 0 | 2.63 | 0.82 | 0.82 |  | 68.8213 | 218 | SS Kushalino 35/10 | 2,5+2,5 | 0.10344 | 1.9134 | 0 |  | 1.9134 | 0 | 2.63 | 0.71656 | 0.71656 |  | 72.7543 | Tverskie Power networks
219 | SS No.4 35/6 | 5,6+5,6 | 1.9 | 0 |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 |  | 32.3129 | 219 | SS No.4 35/6 | 5,6+5,6 | 0.965 | 2.865 | 0 |  | 2.865 | 0 | 5.88 | 3.015 | 3.015 |  | 48.7245 | Tverskie Power networks
220 | SS No.13 35/10/6 | 3,2+3,2 | 1.42 | 0 |  | 1.42 | 0 | 3.36 | 1.94 | 1.94 |  | 42.2619 | 220 | SS No.13 35/10/6 | 3,2+3,2 | 0 | 1.42 | 0 |  | 1.42 | 0 | 3.36 | 1.94 | 1.94 |  | 42.2619 | Tverskie Power networks
221 | SS No.27 35/6 | 10+10 | 13.45 | 0 |  | 13.45 | 0 | 10.5 | -2.95 | -2.95 | MS is closed | 128.0952 | 221 | SS No.27 35/6 | 10+10 | 0.06375 | 13.5137 | 0 |  | 13.5137 | 0 | 10.5 | -3.0137 | -3.0137 | MS is closed | 128.7024 | Tverskie Power networks
222 | SS Vagzhanovskaya 35/6 | 16+16 | 20.44 | 0 |  | 20.44 | 0 | 16.8 | -3.64 | -3.64 | MS is closed | 121.6667 | 222 | SS Vagzhanovskaya 35/6 | 16+16 | 0.0875 | 20.5275 | 0 |  | 20.5275 | 0 | 16.8 | -3.7275 | -3.7275 | MS is closed | 122.1875 | Tverskie Power networks
223 | SS Plant 1Maya 35/6 | 10+10 | 5.95 | 0 |  | 5.95 | 0 | 10.5 | 4.55 | 4.55 |  | 56.6667 | 223 | SS Plant 1Maya 35/6 | 10+10 | 2.5882 | 8.5382 | 0 |  | 8.5382 | 0 | 10.5 | 1.9618 | 1.9618 |  | 81.3167 | Tverskie Power networks
224 | SS Steklovolokno 35/6 | 10+10 | 6.05 | 0 |  | 6.05 | 0 | 10.5 | 4.45 | 4.45 |  | 57.619 | 224 | SS Steklovolokno 35/6 | 10+10 | 0.35375 | 6.4037 | 0 |  | 6.4037 | 0 | 10.5 | 4.0963 | 4.0963 |  | 60.9881 | Tverskie Power networks
225 | SS Sominka 35/10 | 16+16 | 14.05 | 0 |  | 14.05 | 0 | 16.8 | 2.75 | 2.75 |  | 83.631 | 225 | SS Sominka 35/10 | 16+16 | 0.0595 | 14.1095 | 0 |  | 14.1095 | 0 | 16.8 | 2.6905 | 2.6905 |  | 83.9851 | Tverskie Power networks
226 | SS Zavolzhskaya 35/6 | 7,5+10 | 7.83 | 0 |  | 7.83 | 0 | 7.88 | 0.05 | 0.05 |  | 99.3655 | 226 | SS Zavolzhskaya 35/6 | 7,5+10 | 0.0009375 | 7.8309 | 0 |  | 7.8309 | 0 | 7.88 | 0.049062 | 0.049062 |  | 99.3774 | Tverskie Power networks
227 | SS Kaloshvar 35/10 | 10+10 | 9.66 | 0 |  | 9.66 | 0 | 10.5 | 0.84 | 0.84 |  | 92 | 227 | SS Kaloshvar 35/10 | 10+10 | 3.9071 | 13.5671 | 0 |  | 13.5671 | 0 | 10.5 | -3.0671 | -3.0671 | MS is closed | 129.2107 | Tverskie Power networks
228 | SS Mamulino 110/10 | 6,3+6,3 | 1.27 | 0 |  | 1.27 | 0 | 6.62 | 5.35 | 5.35 |  | 19.1843 | 228 | SS Mamulino 110/10 | 6,3+6,3 | 9.1638 | 10.4337 | 0 |  | 10.4337 | 0 | 6.62 | -3.8138 | -3.8138 | MS is closed | 157.6095 | Tverskie Power networks
229 | SS Glazkovo 110/10 | 6,3+6,3 | 5.07 | 0 |  | 5.07 | 0 | 6.62 | 1.55 | 1.55 |  | 76.5861 | 229 | SS Glazkovo 110/10 | 6,3+6,3 | 0.75625 | 5.8262 | 0 |  | 5.8262 | 0 | 6.62 | 0.79375 | 0.79375 |  | 88.0098 | Tverskie Power networks
230 | SS Proletarskaya 110/10 | 16+16 | 8.7 | 0 |  | 8.7 | 0 | 16.8 | 8.1 | 8.1 |  | 51.7857 | 230 | SS Proletarskaya 110/10 | 16+16 | 1.0688 | 9.7688 | 0 |  | 9.7688 | 0 | 16.8 | 7.0312 | 7.0312 |  | 58.1473 | Tverskie Power networks
231 | SS Turginovo 35/10 | 6,3+6,3 | 3.5 | 0 |  | 3.5 | 0 | 6.62 | 3.12 | 3.12 |  | 52.8701 | 231 | SS Turginovo 35/10 | 6,3+6,3 | 0.7171 | 4.2171 | 0 |  | 4.2171 | 0 | 6.62 | 2.4029 | 2.4029 |  | 63.7024 | Tverskie Power networks
232 | SS Sakharovo 35/10 | 2,5+2,5 | 2.25 | 0 |  | 2.25 | 0 | 2.62 | 0.37 | 0.37 |  | 85.8779 | 232 | SS Sakharovo 35/10 | 2,5+2,5 | 0.99387 | 3.2439 | 0 |  | 3.2439 | 0 | 2.62 | -0.62387 | -0.62387 | MS is closed | 123.812 | Tverskie Power networks
233 | SS Golovino 35/10 | 2,5+2,5 | 0.73 | 0 |  | 0.73 | 0 | 2.62 | 1.89 | 1.89 |  | 27.8626 | 233 | SS Golovino 35/10 | 2,5+2,5 | 0.4835 | 1.2135 | 0 |  | 1.2135 | 0 | 2.62 | 1.4065 | 1.4065 |  | 46.3168 | Tverskie Power networks
234 | SS Kalikino 35/10 | 2+3,2 | 1.99 | 0 |  | 1.99 | 0 | 2.1 | 0.11 | 0.11 |  | 94.7619 | 234 | SS Kalikino 35/10 | 2+3,2 | 0.075 | 2.065 | 0 |  | 2.065 | 0 | 2.1 | 0.035 | 0.035 |  | 98.3333 | Tverskie Power networks
235 | SS Kvakshino 35/10 | 4+4 | 0.92 | 0 |  | 0.92 | 0 | 4.2 | 3.28 | 3.28 |  | 21.9048 | 235 | SS Kvakshino 35/10 | 4+4 | 0.025 | 0.945 | 0 |  | 0.945 | 0 | 4.2 | 3.255 | 3.255 |  | 22.5 | Tverskie Power networks
236 | SS Gorodnya 35/10 | 4+6,3 | 2.59 | 0 |  | 2.59 | 0 | 4.2 | 1.61 | 1.61 |  | 61.6667 | 236 | SS Gorodnya 35/10 | 4+6,3 | 0.35907 | 2.9491 | 0 |  | 2.9491 | 0 | 4.2 | 1.2509 | 1.2509 |  | 70.216 | Tverskie Power networks
237 | SS Ryazanovo 35/10 | 4+4 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 |  | 42.8571 | 237 | SS Ryazanovo 35/10 | 4+4 | 0 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 |  | 42.8571 | Tverskie Power networks
238 | SS Savvatyevo 35/10 | 1,6+2,5 | 0.55 | 0 |  | 0.55 | 0 | 1.68 | 1.13 | 1.13 |  | 32.7381 | 238 | SS Savvatyevo 35/10 | 1,6+2,5 | 0.0715 | 0.6215 | 0 |  | 0.6215 | 0 | 1.68 | 1.0585 | 1.0585 |  | 36.994 | Tverskie Power networks
239 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0.5 | 0 |  | 0.5 | 0 | 1.68 | 1.18 | 1.18 |  | 29.7619 | 239 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0.0425 | 0.5425 | 0 |  | 0.5425 | 0 | 1.68 | 1.1375 | 1.1375 |  | 32.2917 | Tverskie Power networks
240 | SS Glass plant 35/10 | 2,5+2,5 | 0.28 | 0 |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 |  | 10.6464 | 240 | SS Glass plant 35/10 | 2,5+2,5 | 0 | 0.28 | 0 |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 |  | 10.6464 | Tverskie Power networks
241 | SS Grishkino 35/10 | 4+4 | 2.92 | 0 |  | 2.92 | 0 | 4.2 | 1.28 | 1.28 |  | 69.5238 | 241 | SS Grishkino 35/10 | 4+4 | 7.5894 | 10.5094 | 0 |  | 10.5094 | 0 | 4.2 | -6.3094 | -6.3094 | MS is closed | 250.2232 | Tverskie Power networks
242 | SS No.2 35/3 | 1+1 | 0.32 | 0 |  | 0.32 | 0 | 1.05 | 0.73 | 0.73 |  | 30.4762 | 242 | SS No.2 35/3 | 1+1 | 0 | 0.32 | 0 |  | 0.32 | 0 | 1.05 | 0.73 | 0.73 |  | 30.4762 | Tverskie Power networks
243 | SS No.15 35/10 | 4+4 | 2.08 | 0 |  | 2.08 | 0 | 4.2 | 2.12 | 2.12 |  | 49.5238 | 243 | SS No.15 35/10 | 4+4 | 0.037 | 2.117 | 0 |  | 2.117 | 0 | 4.2 | 2.083 | 2.083 |  | 50.4048 | Tverskie Power networks
244 | SS Mednoe 35/10 | 6,3+4 | 2.83 | 0 |  | 2.83 | 0 | 4.2 | 1.37 | 1.37 |  | 67.381 | 244 | SS Mednoe 35/10 | 6,3+4 | 0.475 | 3.305 | 0 |  | 3.305 | 0 | 4.2 | 0.895 | 0.895 |  | 78.6905 | Tverskie Power networks
245 | SS Tolmachi 35/10 | 2,5+1,8 | 1.08 | 0 |  | 1.08 | 0 | 1.89 | 0.81 | 0.81 |  | 57.1429 | 245 | SS Tolmachi 35/10 | 2,5+1,8 | 0.0395 | 1.1195 | 0 |  | 1.1195 | 0 | 1.89 | 0.7705 | 0.7705 |  | 59.2328 | Tverskie Power networks
246 | SS No. 7 35/10 | 1,8+2,5 | 0.47 | 0 |  | 0.47 | 0 | 1.89 | 1.42 | 1.42 |  | 24.8677 | 246 | SS No. 7 35/10 | 1,8+2,5 | 0.0375 | 0.5075 | 0 |  | 0.5075 | 0 | 1.89 | 1.3825 | 1.3825 |  | 26.8519 | Tverskie Power networks
247 | SS No. 5 35/6 | 5,6+4 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 |  | 42.8571 | 247 | SS No. 5 35/6 | 5,6+4 | 0 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 |  | 42.8571 | Tverskie Power networks
248 | SS No. 9 35/6 | 5,6+7,5 | 4.5 | 0 |  | 4.5 | 0 | 5.88 | 1.38 | 1.38 |  | 76.5306 | 248 | SS No. 9 35/6 | 5,6+7,5 | 0.75625 | 5.2562 | 0 |  | 5.2562 | 0 | 5.88 | 0.62375 | 0.62375 |  | 89.392 | Tverskie Power networks
249 | SS No. 9 35/10 | 4+6,3 | 2.43 | 0 |  | 2.43 | 0 | 4.2 | 1.77 | 1.77 |  | 57.8571 | 249 | SS No. 9 35/10 | 4+6,3 | 0.18425 | 2.6143 | 0 |  | 2.6143 | 0 | 4.2 | 1.5857 | 1.5857 |  | 62.244 | Tverskie Power networks
250 | SS No. 10 35/6 | 1,8+1,8 | 1.42 | 0 |  | 1.42 | 0 | 1.89 | 0.47 | 0.47 |  | 75.1323 | 250 | SS No. 10 35/6 | 1,8+1,8 | 0.75625 | 2.1763 | 0 |  | 2.1763 | 0 | 1.89 | -0.28625 | -0.28625 | MS is closed | 115.1455 | Tverskie Power networks
251 | SS No. 11 35/10 kv | 10+6,3 | 4.517 | 0 |  | 4.517 | 0 | 6.62 | 2.103 | 2.103 |  | 68.2326 | 251 | SS No. 11 35/10 kv | 10+6,3 | 0.14375 | 4.6608 | 0 |  | 4.6608 | 0 | 6.62 | 1.9592 | 1.9592 |  | 70.4041 | Tverskie Power networks
252 | SS Dm.Gora 35/10 | 2,5+4 | 4.7 | 0 |  | 4.7 | 0 | 2.63 | -2.07 | -2.07 | MS is closed | 178.7072 | 252 | SS Dm.Gora 35/10 | 4+2,5 | 0.00125 | 4.7012 | 0 |  | 4.7012 | 0 | 2.63 | -2.0713 | -2.0713 | MS is closed | 178.7548 | Tverskie Power networks
253 | SS ZMI 35/6 | 10+16 | 2.6 | 0 |  | 2.6 | 0 | 10.5 | 7.9 | 7.9 |  | 24.7619 | 253 | SS ZMI 35/6 | 10+16 | 0.54375 | 3.1437 | 0 |  | 3.1437 | 0 | 10.5 | 7.3563 | 7.3563 |  | 29.9405 | Tverskie Power networks
254 | SS Izoplit 35/10 | 6,3+6,3 | 0.67 | 0 |  | 0.67 | 0 | 6.62 | 5.95 | 5.95 |  | 10.1208 | 254 | SS Izoplit 35/10 | 6,3+6,3 | 0 | 0.67 | 0 |  | 0.67 | 0 | 6.62 | 5.95 | 5.95 |  | 10.1208 | Tverskie Power networks
255 | SS Karacharovo 35/10 | 4+6,3 | 1.4 | 0 |  | 1.4 | 0 | 4.2 | 2.8 | 2.8 |  | 33.3333 | 255 | SS Karacharovo 35/10 | 4+6,3 | 0.20275 | 1.6027 | 0 |  | 1.6027 | 0 | 4.2 | 2.5972 | 2.5972 |  | 38.1607 | Tverskie Power networks
256 | SS Kr. Luch 35/6 | 2,5+3,2 | 2.25 | 0 |  | 2.25 | 0 | 2.63 | 0.38 | 0.38 |  | 85.5513 | 256 | SS Kr. Luch 35/6 | 2,5+3,2 | 0.11875 | 2.3687 | 0 |  | 2.3687 | 0 | 2.63 | 0.26125 | 0.26125 |  | 90.0665 | Tverskie Power networks
257 | SS Melkovo 35/6 | 1,6+2,5 | 0.98 | 0 |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 |  | 58.3333 | 257 | SS Melkovo 35/6 | 1,6+2,5 | 0.0125 | 0.9925 | 0 |  | 0.9925 | 0 | 1.68 | 0.6875 | 0.6875 |  | 59.0774 | Tverskie Power networks
258 | SS Selikhovo 35/6 | 2,5+2,5 | 0.93 | 0 |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 |  | 35.3612 | 258 | SS Selikhovo 35/6 | 2,5+2,5 | 0.4317 | 1.3617 | 0 |  | 1.3617 | 0 | 2.63 | 1.2683 | 1.2683 |  | 51.7757 | Tverskie Power networks
259 | SS Mokshino 35/10 | 6,3+6,3 | 2.73 | 0 |  | 2.73 | 0 | 6.62 | 3.89 | 3.89 |  | 41.2387 | 259 | SS Mokshino 35/10 | 6,3+6,3 | 0.95125 | 3.6812 | 0 |  | 3.6812 | 0 | 6.62 | 2.9388 | 2.9388 |  | 55.608 | Tverskie Power networks
260 | SS Energetik 35/10 | 4+2,5 | 1.25 | 0 |  | 1.25 | 0 | 2.63 | 1.38 | 1.38 |  | 47.5285 | 260 | SS Energetik 35/10 | 4+2,5 | 0.032 | 1.282 | 0 |  | 1.282 | 0 | 2.63 | 1.348 | 1.348 |  | 48.7452 | Tverskie Power networks
261 | SS Emmaus 35/10 | 2,5+4 | 2.17 | 0 |  | 2.17 | 0 | 2.63 | 0.46 | 0.46 |  | 82.5095 | 261 | SS Emmaus 35/10 | 2,5+4 | 0.21775 | 2.3878 | 0 |  | 2.3878 | 0 | 2.63 | 0.24225 | 0.24225 |  | 90.789 | Tverskie Power networks
262 | SS Yu.-Devichye 35/10 | 4+4 | 2.19 | 1.095 | 120 | 1.095 | 0 | 4.2 | 3.105 | 3.105 |  | 52.1429 | 262 | SS Yu.-Devichye 35/10 | 4+4 | 3.7912 | 5.9813 | 2.9906 | 120 | 2.9906 | 0 | 4.2 | 1.2094 | 1.2094 |  | 142.4107 | Tverskie Power networks
263 | SS No.18 35/6 | 10+10+10 | 19.49 | 0 |  | 19.49 | 0 | 21 | 1.51 | 1.51 |  | 92.8095 | 263 | SS No.18 35/6 | 10+10+10 | 0.06875 | 19.5587 | 0 |  | 19.5587 | 0 | 21 | 1.4412 | 1.4412 |  | 93.1369 | Tverskie Power networks
264 | SS Zatveretskaya 35/6 | 10+10+10 | 12.95 | 0 |  | 12.95 | 0 | 21 | 8.05 | 8.05 |  | 61.6667 | 264 | SS Zatveretskaya 35/6 | 10+10+10 | 0.9375 | 13.8875 | 0 |  | 13.8875 | 0 | 21 | 7.1125 | 7.1125 |  | 66.131 | Tverskie Power networks
265 | SS Pushkino 110/35/10 | 10 | 4.82 | 4.82 | 24 hours | 4.82 | 0 | 4.82 | 0 | 0 |  | 45.9048 | 265 | SS Pushkino 110/35/10 | 10 | 0.7171 | 5.5371 | 4.82 | 24 hours | 4.82 | 0 | 4.82 | -0.7171 | -0.7171 | MS is closed | 52.7343 | Tverskie Power networks
| Nom. capacity MV, MVA | 8.83 | 4.65 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0 |  |  |  |  | Nom. capacity MV, MVA | 8.83 | 0.7171 | 5.3671 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0
| Nom. capacity LV, MVA | 8.75 | 0.17 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | 0 |  |  |  |  | Nom. capacity LV, MVA | 8.75 | 0 | 0.17 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | 0
266 | SS Mechanical plant 110/10/6 | 40+40 | 21.2262 | 0 |  | 21.2262 | 0 | 42 | 20.7738 | 9.6555 |  | 50.5387 | 266 | SS Mechanical plant 110/10/6 | 40+40 | 0.35487 | 21.5811 | 0 |  | 21.5811 | 0 | 42 | 20.4189 | 9.3386 |  | 51.3836 | Tverskie Power networks
| Nom. capacity MV, MVA | 20+20 | 9.8818 | 0 |  | 9.8818 | 0 | 21 | 11.1182 |  |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.038 | 9.9198 | 0 |  | 9.9198 | 0 | 21 | 11.0802
| Nom. capacity LV, MVA | 20+20 | 11.3445 | 0 |  | 11.3445 | 0 | 21 | 9.6555 |  |  |  |  | Nom. capacity LV, MVA | 20+20 | 0.31688 | 11.6614 | 0 |  | 11.6614 | 0 | 21 | 9.3386
267 | SS Yuzhnaya 110/35/10 | 40+40 | 45.69 | 15.9 | 120 | 29.79 | 0 | 42 | 12.21 | 12.21 |  | 108.7857 | 267 | SS Yuzhnaya 110/35/10 | 40+40 | 2.7818 | 48.4718 | 15.9 | 120 | 32.5718 | 0 | 42 | 9.4283 | 9.4283 |  | 115.4089 | Tverskie Power networks
| Nom. capacity MV, MVA | 40+40 | 27.39 | 13.9 | 120 | 13.49 | 0 | 42 | 28.51 |  |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.974 | 28.364 | 13.9 | 120 | 14.464 | 0 | 42 | 27.536
| Nom. capacity LV, MVA | 40+40 | 18.3 | 2 | 120 | 16.3 | 0 | 42 | 25.7 |  |  |  |  | Nom. capacity LV, MVA | 40+40 | 1.8077 | 20.1077 | 2 | 120 | 18.1077 | 0 | 42 | 23.8923
268 | SS Severnaya 110/35/10 | 40+40 | 44.6817 | 18.165 | 120 | 26.5167 | 0 | 42 | 15.4833 | 15.4833 |  | 106.3851 | 268 | SS Severnaya 110/35/10 | 40+40 | 9.1054 | 53.7872 | 18.165 | 120 | 35.6222 | 0 | 42 | 6.3778 | 6.3778 |  | 128.0647 | Tverskie Power networks
| Nom. capacity MV, MVA | 40+40 | 18.165 | 18.165 | 120 | 0 | 0 | 42 | 42 |  |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.41419 | 18.5792 | 18.165 | 120 | 0.41419 | 0 | 42 | 41.5858
| Nom. capacity LV, MVA | 40+40 | 26.5167 | 0 |  | 26.5167 | 0 | 42 | 15.4833 |  |  |  |  | Nom. capacity LV, MVA | 40+40 | 8.6913 | 35.208 | 0 |  | 35.208 | 0 | 42 | 6.792
269 | SS Lazurnaya 110/35/10 | 40+40 | 19.7 | 6.47 | 120 | 13.23 | 0 | 42 | 28.77 | 28.77 |  | 46.9048 | 269 | SS Lazurnaya 110/35/10 | 40+40 | 17.3184 | 37.0184 | 6.47 | 120 | 30.5484 | 0 | 42 | 11.4516 | 11.4516 |  | 88.139 | Tverskie Power networks
| Nom. capacity MV, MVA | 40+40 | 15.46 | 6.47 | 120 | 8.99 | 0 | 42 | 33.01 |  |  |  |  | Nom. capacity MV, MVA | 40+40 | 8.7971 | 24.2571 | 6.47 | 120 | 17.7871 | 0 | 42 | 24.2129
| Nom. capacity LV, MVA | 40+40 | 4.24 | 0 |  | 4.24 | 0 | 42 | 37.76 |  |  |  |  | Nom. capacity LV, MVA | 40+40 | 8.5213 | 12.7613 | 0 |  | 12.7613 | 0 | 42 | 29.2387
270 | SS Earthmoving machine plant 110/10/6 | 40+40 | 13.6916 | 0 |  | 13.6916 | 0 | 42 | 28.3084 | 9.5246 |  | 32.599 | 270 | SS Earthmoving machine plant 110/10/6 | 40+40 | 4.2675 | 17.9591 | 0 |  | 17.9591 | 0 | 42 | 24.0409 | 8.9777 |  | 42.7597 | Tverskie Power networks
| Nom. capacity MV, MVA | 20+20 | 11.4754 | 0 |  | 11.4754 | 0 | 21 | 9.5246 |  |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.5469 | 12.0223 | 0 |  | 12.0223 | 0 | 21 | 8.9777
| Nom. capacity LV, MVA | 20+20 | 2.2161 | 0 |  | 2.2161 | 0 | 21 | 18.7839 |  |  |  |  | Nom. capacity LV, MVA | 20+20 | 3.7206 | 5.9368 | 0 |  | 5.9368 | 0 | 21 | 15.0632
271 | SS Mednovsky v-or 110/35/10 | 10+10 | 4.4271 | 4.43 | 120 | -0.00293 | 0 | 10.5 | 10.5029 | 10.498 |  | 42.1626 | 271 | SS Mednovsky v-or 110/35/10 | 10+10 | 0.96782 | 5.3949 | 4.43 | 120 | 0.96489 | 0 | 10.5 | 9.5351 | 9.5351 |  | 51.3799 | Tverskie Power networks
| Nom. capacity MV, MVA | 10+10 | 2.505 | 2.51 | 120 | -0.00496 | 0 | 10.5 | 10.505 |  |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.90907 | 3.4141 | 2.51 | 120 | 0.90411 | 0 | 10.5 | 9.5959
| Nom. capacity LV, MVA | 10+10 | 1.922 | 1.92 | 120 | 0.00203 | 0 | 10.5 | 10.498 |  |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.05875 | 1.9808 | 1.92 | 120 | 0.06078 | 0 | 10.5 | 10.4392
272 | SS Likhoslavl 110/35/10 | 25+25 | 15.06 | 6.3 | 120 | 8.76 | 0 | 26.25 | 17.49 | 17.49 |  | 57.3714 | 272 | SS Likhoslavl 110/35/10 | 25+25 | 0.4855 | 15.5455 | 6.3 | 120 | 9.2455 | 0 | 26.25 | 17.0045 | 17.0045 |  | 59.221 | Tverskie Power networks
| Nom. capacity MV, MVA | 25+25 | 6.3 | 6.3 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. capacity MV, MVA | 25+25 | 0.0375 | 6.3375 | 6.3 | 120 | 0.0375 | 0 | 26.25 | 26.2125
| Nom. capacity LV, MVA | 25+25 | 8.76 | 0 |  | 8.76 | 0 | 26.25 | 17.49 |  |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.448 | 9.208 | 0 |  | 9.208 | 0 | 26.25 | 17.042
273 | SS Bezborodovo 110/35/6 | 16+16 | 13.63 | 4.25 | 120 | 9.38 | 0 | 16.8 | 7.42 | 7.42 |  | 81.131 | 273 | SS Bezborodovo 110/35/6 | 16+16 | 1.1075 | 14.7375 | 4.25 | 120 | 10.4875 | 0 | 16.8 | 6.3125 | 6.3125 |  | 87.7232 | Tverskie Power networks
| Nom. capacity MV, MVA | 16+16 | 13.63 | 4.25 | 120 | 9.38 | 0 | 16.8 | 7.42 |  |  |  |  | Nom. capacity MV, MVA | 16+16 | 1.1075 | 14.7375 | 4.25 | 120 | 10.4875 | 0 | 16.8 | 6.3125
| Nom. capacity LV, MVA | 16+16 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8 |  |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8
274 | SS Redkino 110/35/6 | 40+40,5 | 25.27 | 8.53 | 120 | 16.74 | 0 | 42 | 25.26 | 25.26 |  | 60.1667 | 274 | SS Redkino 110/35/6 | 40+40,5 | 7.3695 | 32.6395 | 8.53 | 120 | 24.1095 | 0 | 42 | 17.8905 | 17.8905 |  | 77.7131 | Tverskie Power networks
| Nom. capacity MV, MVA | 40+40 | 19 | 8.53 | 120 | 10.47 | 0 | 42 | 31.53 |  |  |  |  | Nom. capacity MV, MVA | 40+40 | 3.6195 | 22.6195 | 8.53 | 120 | 14.0895 | 0 | 42 | 27.9105
| Nom. capacity LV, MVA | 40+40 | 6.27 | 0 |  | 6.27 | 0 | 42 | 35.73 |  |  |  |  | Nom. capacity LV, MVA | 40+40 | 3.75 | 10.02 | 0 |  | 10.02 | 0 | 42 | 31.98
275 | SS Rameshki 110/35/10 | 25+10 | 5.32 | 3.59 | 120 | 1.73 | 0 | 10.5 | 8.77 | 8.77 |  | 50.6667 | 275 | SS Rameshki 110/35/10 | 25+10 | 0.1315 | 5.4515 | 3.59 | 120 | 1.8615 | 0 | 10.5 | 8.6385 | 8.6385 |  | 51.919 | Tverskie Power networks
| Nom. capacity MV, MVA | 25+10 | 2.59 | 2.59 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  |  | Nom. capacity MV, MVA | 25+10 | 0.0395 | 2.6295 | 2.59 | 120 | 0.0395 | 0 | 10.5 | 10.4605
| Nom. capacity MV, MVA | 25+10 | 2.73 | 1 | 120 | 1.73 | 0 | 10.5 | 8.77 |  |  |  |  | Nom. capacity MV, MVA | 25+10 | 0.092 | 2.822 | 1 | 120 | 1.822 | 0 | 10.5 | 8.678
276 | SS Tuchevo 110/35/10 | 25+25 | 0.33 | 0.29 | 120 | 0.04 | 0 | 26.25 | 26.21 | 22.94 |  | 1.2571 | 276 | SS Tuchevo 110/35/10 | 25+25 | 0 | 0.33 | 0.29 | 120 | 0.04 | 0 | 26.25 | 26.21 | 22.94 |  | 1.2571 | Tverskie Power networks
| Nom. capacity MV, MVA | 22,06+22,06 | 0.29 | 0.29 | 120 | 0 | 0 | 23.17 | 23.17 |  |  |  |  | Nom. capacity MV, MVA | 22,06+22,06 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 23.17 | 23.17
| Nom. capacity MV, MVA | 21,89+21,89 | 0.04 | 0 |  | 0.04 | 0 | 22.98 | 22.94 |  |  |  |  | Nom. capacity MV, MVA | 21,89+21,89 | 0 | 0.04 | 0 |  | 0.04 | 0 | 22.98 | 22.94
277 | SS Strashevichi 35/10 kv | 4 | 0.74 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0 | 0 |  | 17.619 | 277 | SS Strashevichi 35/10 kv | 4 | 0 | 0.74 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0 | 0 |  | 17.619 | Torzhokskie Power networks
278 | SS Sukromlya 35/10 kv | 2.5 | 0.31 | 0.31 | 24 hours | 0.31 | 0 | 0.31 | 0 | 0 |  | 11.8095 | 278 | SS Sukromlya 35/10 kv | 2.5 | 0 | 0.31 | 0.31 | 24 hours | 0.31 | 0 | 0.31 | 0 | 0 |  | 11.8095 | Torzhokskie Power networks
279 | SS Kr. Gorodok 35/10 kv | 0.56 | 0.02 | 0 |  | 0 | 0 | 0 | -0.02 | -0.02 | MS is closed | 3.4014 | 279 | SS Kr. Gorodok 35/10 kv | 0.56 | 0 | 0.02 | 0 |  | 0 | 0 | 0 | -0.02 | -0.02 | MS is closed | 3.4014 | Torzhokskie Power networks
280 | SS Pryamukhino 35/10 kv | 2.5 | 0.52 | 0.52 | 24 hours | 0.52 | 0 | 0.52 | 0 | 0 |  | 19.8095 | 280 | SS Pryamukhino 35/10 kv | 2.5 | 0 | 0.52 | 0.52 | 24 hours | 0.52 | 0 | 0.52 | 0 | 0 |  | 19.8095 | Torzhokskie Power networks
281 | SS Pen 35/10 kv | 1.6 | 0.16 | 0 |  | 0 | 0 | 0 | -0.16 | -0.16 | MS is closed | 9.5238 | 281 | SS Pen 35/10 kv | 1.6 | 0 | 0.16 | 0 |  | 0 | 0 | 0 | -0.16 | -0.16 | MS is closed | 9.5238 | Torzhokskie Power networks
282 | SS Pechnikovo 35/10 kv | 2.5 | 0.09 | 0.09 | 24 hours | 0.09 | 0 | 0.09 | 0 | 0 |  | 3.4286 | 282 | SS Pechnikovo 35/10 kv | 2.5 | 0 | 0.09 | 0.09 | 24 hours | 0.09 | 0 | 0.09 | 0 | 0 |  | 3.4286 | Torzhokskie Power networks
283 | SS Maksimkovo 35/10 kv | 2.5 | 0.58 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0 | 0 |  | 22.0952 | 283 | SS Maksimkovo 35/10 kv | 2.5 | 0 | 0.58 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0 | 0 |  | 22.0952 | Torzhokskie Power networks
284 | SS Filistovo 35/10 kv | 1.6 | 0.16 | 0.16 | 24 hours | 0.16 | 0 | 0.16 | 0 | 0 |  | 9.5238 | 284 | SS Filistovo 35/10 kv | 1.6 | 0 | 0.16 | 0.16 | 24 hours | 0.16 | 0 | 0.16 | 0 | 0 |  | 9.5238 | Torzhokskie Power networks
285 | SS Okovtsy 35/10 kv | 1 | 0.59 | 0.59 | 24 hours | 0.59 | 0 | 0.59 | 0 | 0 |  | 56.1905 | 285 | SS Okovtsy 35/10 kv | 1 | 0.025 | 0.615 | 0.59 | 24 hours | 0.59 | 0 | 0.59 | -0.025 | -0.025 | MS is closed | 58.5714 | Torzhokskie Power networks
286 | SS Seliger 35/10 kv | 4 | 3.33 | 0 |  | 0 | 0 | 0 | -3.33 | -3.33 | MS is closed | 79.2857 | 286 | SS Seliger 35/10 kv | 4 | 1.689 | 5.019 | 0 |  | 0 | 0 | 0 | -5.019 | -5.019 | MS is closed | 119.5 | Torzhokskie Power networks
287 | SS Moshary 35/10 kv | 1.6 | 0.26 | 0 |  | 0 | 0 | 0 | -0.26 | -0.26 | MS is closed | 15.4762 | 287 | SS Moshary 35/10 kv | 1.6 | 0 | 0.26 | 0 |  | 0 | 0 | 0 | -0.26 | -0.26 | MS is closed | 15.4762 | Torzhokskie Power networks
288 | SS Voroshilovo 35/10 kv | 1 | 0.39 | 0 |  | 0 | 0 | 0 | -0.39 | -0.39 | MS is closed | 37.1429 | 288 | SS Voroshilovo 35/10 kv | 1 | 0 | 0.39 | 0 |  | 0 | 0 | 0 | -0.39 | -0.39 | MS is closed | 37.1429 | Torzhokskie Power networks
289 | SS Salutino 35/10 kv | 1.6 | 0.47 | 0 |  | 0 | 0 | 0 | -0.47 | -0.47 | MS is closed | 27.9762 | 289 | SS Salutino 35/10 kv | 1.6 | 0.0685 | 0.5385 | 0 |  | 0 | 0 | 0 | -0.5385 | -0.5385 | MS is closed | 32.0536 | Torzhokskie Power networks
290 | SS Moshki 35/10 kv | 2,5+2,5 | 2.77 | 0 |  | 2.77 | 0 | 2.63 | -0.14 | -0.14 | MS is closed | 105.3232 | 290 | SS Moshki 35/10 kv | 2,5+2,5 | 0.0805 | 2.8505 | 0 |  | 2.8505 | 0 | 2.63 | -0.2205 | -0.2205 | MS is closed | 108.384 | Torzhokskie Power networks
291 | SS Vysokoe 35/10 kv | 4+2,5 | 0.81 | 0 |  | 0.81 | 0 | 2.63 | 1.82 | 1.82 |  | 30.7985 | 291 | SS Vysokoe 35/10 kv | 4+2,5 | 0 | 0.81 | 0 |  | 0.81 | 0 | 2.63 | 1.82 | 1.82 |  | 30.7985 | Torzhokskie Power networks
292 | SS Bubenyevo 35/10 kv | 4+4 | 2.82 | 0 |  | 2.82 | 0 | 4.2 | 1.38 | 1.38 |  | 67.1429 | 292 | SS Bubenyevo 35/10 kv | 4+4 | 0.261 | 3.081 | 0 |  | 3.081 | 0 | 4.2 | 1.119 | 1.119 |  | 73.3571 | Torzhokskie Power networks
293 | SS B.Vishenye 35/10 kv | 2,5+2,5 | 0.91 | 0 |  | 0.91 | 0 | 2.63 | 1.72 | 1.72 |  | 34.6008 | 293 | SS B.Vishenye 35/10 kv | 2,5+2,5 | 0 | 0.91 | 0 |  | 0.91 | 0 | 2.63 | 1.72 | 1.72 |  | 34.6008 | Torzhokskie Power networks
294 | SS Budovo 35/10 kv | 2,5+2,5 | 1.77 | 0 |  | 1.77 | 0 | 2.63 | 0.86 | 0.86 |  | 67.3004 | 294 | SS Budovo 35/10 kv | 2,5+2,5 | 0.059 | 1.829 | 0 |  | 1.829 | 0 | 2.63 | 0.801 | 0.801 |  | 69.5437 | Torzhokskie Power networks
295 | SS Eltsy 35/10 kv | 4+4 | 0.84 | 0 |  | 0.84 | 0 | 4.2 | 3.36 | 3.36 |  | 20 | 295 | SS Eltsy 35/10 kv | 4+4 | 0 | 0.84 | 0 |  | 0.84 | 0 | 4.2 | 3.36 | 3.36 |  | 20 | Torzhokskie Power networks
296 | SS Selishche 35/10 kv | 6,3+4 | 1.37 | 0 |  | 1.37 | 0 | 4.2 | 2.83 | 2.83 |  | 32.619 | 296 | SS Selishche 35/10 kv | 6,3+4 | 1.6827 | 3.0528 | 0 |  | 3.0528 | 0 | 4.2 | 1.1473 | 1.1473 |  | 72.6845 | Torzhokskie Power networks
297 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.59 | 0 |  | 0.59 | 0 | 1.68 | 1.09 | 1.09 |  | 35.119 | 297 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.27625 | 0.86625 | 0 |  | 0.86625 | 0 | 1.68 | 0.81375 | 0.81375 |  | 51.5625 | Torzhokskie Power networks
298 | SS Krapivnaya 35/10 kv | 2,5+2,5 | 0.49 | 0 |  | 0.49 | 0 | 2.63 | 2.14 | 2.14 |  | 18.6312 | 298 | SS Krapivnaya 35/10 kv | 2,5+2,5 | 0 | 0.49 | 0 |  | 0.49 | 0 | 2.63 | 2.14 | 2.14 |  | 18.6312 | Torzhokskie Power networks
299 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 1.66 | 0 |  | 1.66 | 0 | 2.63 | 0.97 | 0.97 |  | 63.1179 | 299 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 0.3605 | 2.0205 | 0 |  | 2.0205 | 0 | 2.63 | 0.6095 | 0.6095 |  | 76.8251 | Torzhokskie Power networks
300 | SS KS-20 110/6 kv | 63+63 | 16.36 | 0 |  | 16.36 | 0 | 66.15 | 49.79 | 49.79 |  | 24.7317 | 300 | SS KS-20 110/6 kv | 63+63 | 0 | 16.36 | 0 |  | 16.36 | 0 | 66.15 | 49.79 | 49.79 |  | 24.7317 | Torzhokskie Power networks
301 | SS Poligrafkraski 110/10 kv | 10+10 | 6.08 | 0 |  | 6.08 | 0 | 10.5 | 4.42 | 4.42 |  | 57.9048 | 301 | SS Poligrafkraski 110/10 kv | 10+10 | 0.023 | 6.103 | 0 |  | 6.103 | 0 | 10.5 | 4.397 | 4.397 |  | 58.1238 | Torzhokskie Power networks
302 | SS NPS Torzhok 110/10 kv | 25+25 | 0.01 | 0 |  | 0.01 | 0 | 26.25 | 26.24 | 26.24 |  | 0.038095 | 302 | SS NPS Torzhok 110/10 kv | 25+25 | 0 | 0.01 | 0 |  | 0.01 | 0 | 26.25 | 26.24 | 26.24 |  | 0.038095 | Torzhokskie Power networks
303 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0.5 | 0 |  | 0.5 | 0 | 2.63 | 2.13 | 2.13 |  | 19.0114 | 303 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0 | 0.5 | 0 |  | 0.5 | 0 | 2.63 | 2.13 | 2.13 |  | 19.0114 | Torzhokskie Power networks
304 | SS Peno 110/10 kv | 6,3+6,3 | 4.05 | 0 |  | 4.05 | 0 | 6.62 | 2.57 | 2.57 |  | 61.1782 | 304 | SS Peno 110/10 kv | 6,3+6,3 | 0.16875 | 4.2188 | 0 |  | 4.2188 | 0 | 6.62 | 2.4013 | 2.4013 |  | 63.7273 | Torzhokskie Power networks
305 | SS Torzhok 110/35/10 kv | 25+40 | 23.54 | 7.38 | 120 | 16.16 | 0 | 26.25 | 10.09 | 10.09 |  | 89.6762 | 305 | SS Torzhok 110/35/10 kv | 25+40 | 6.249 | 29.789 | 7.38 | 120 | 22.409 | 0 | 26.25 | 3.841 | 3.841 |  | 113.4819 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 25+40 | 7.38 | 7.38 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. Capacity MV, MVA | 25+40 | 0.4005 | 7.7805 | 7.38 | 120 | 0.4005 | 0 | 26.25 | 25.8495
| Nom. Capacity LV, MVA | 25+40 | 16.16 | 0 |  | 16.16 | 0 | 26.25 | 10.09 |  |  |  |  | Nom. Capacity LV, MVA | 25+40 | 5.8485 | 22.0085 | 0 |  | 22.0085 | 0 | 26.25 | 4.2415
306 | SS Stroyindustriya 110/35/10 kv | 25+25 | 5.45 | 0.32 | 120 | 5.13 | 0 | 26.25 | 21.12 | 21.12 |  | 20.7619 | 306 | SS Stroyindustriya 110/35/10 kv | 25+25 | 0.033 | 5.483 | 0.32 | 120 | 5.163 | 0 | 26.25 | 21.087 | 21.087 |  | 20.8876 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 25+25 | 0.32 | 0.32 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 0.32 | 0.32 | 120 | 0 | 0 | 26.25 | 26.25
| Nom. Capacity LV, MVA | 25+25 | 5.13 | 0 |  | 5.13 | 0 | 26.25 | 21.12 |  |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.033 | 5.163 | 0 |  | 5.163 | 0 | 26.25 | 21.087
307 | SS Kuvshinovo 110/35/10 kv | 25+25 | 18.92 | 1.8 | 120 | 17.12 | 0 | 26.25 | 9.13 | 9.13 |  | 72.0762 | 307 | SS Kuvshinovo 110/35/10 kv | 25+25 | 0.06 | 18.98 | 1.8 | 120 | 17.18 | 0 | 26.25 | 9.07 | 9.07 |  | 72.3048 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 25+25 | 1.8 | 1.8 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 1.8 | 1.8 | 120 | 0 | 0 | 26.25 | 26.25
| Nom. Capacity LV, MVA | 25+25 | 17.12 | 0 |  | 17.12 | 0 | 26.25 | 9.13 |  |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.06 | 17.18 | 0 |  | 17.18 | 0 | 26.25 | 9.07
308 | SS Selizharovo 110/35/10 kv | 16+10 | 8.79 | 0 |  | 8.79 | 0 | 10.5 | 1.71 | 1.71 |  | 83.7143 | 308 | SS Selizharovo 110/35/10 kv | 16+10 | 2.2761 | 11.0661 | 0 |  | 11.0661 | 0 | 10.5 | -0.5661 | -0.5661 | MS is closed | 105.3914 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 16+10 | 2.13 | 0 |  | 2.13 | 0 | 10.5 | 8.37 |  |  |  |  | Nom. Capacity MV, MVA | 16+10 | 0 | 2.13 | 0 |  | 2.13 | 0 | 10.5 | 8.37
| Nom. Capacity LV, MVA | 16+10 | 6.66 | 0 |  | 6.66 | 0 | 10.5 | 3.84 |  |  |  |  | Nom. Capacity LV, MVA | 16+10 | 2.2761 | 8.9361 | 0 |  | 8.9361 | 0 | 10.5 | 1.5639
309 | SS NPS Borisovo 110/35/10 kv | 25+25 | 1.95 | 1.59 | 120 | 0.36 | 0 | 26.25 | 25.89 | 25.89 |  | 7.4286 | 309 | SS NPS Borisovo 110/35/10 kv | 25+25 | 0.025 | 1.975 | 1.59 | 120 | 0.385 | 0 | 26.25 | 25.865 | 25.865 |  | 7.5238 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 25+25 | 1.59 | 1.59 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0.025 | 1.615 | 1.59 | 120 | 0.025 | 0 | 26.25 | 26.225
| Nom. Capacity LV, MVA | 25+25 | 0.36 | 0 |  | 0.36 | 0 | 26.25 | 25.89 |  |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 0.36 | 0 |  | 0.36 | 0 | 26.25 | 25.89
310 | SS Ostashkov 110/35/10 kv | 25+25 | 16.88 | 0 |  | 16.88 | 0 | 26.25 | 9.37 | 9.37 |  | 64.3048 | 310 | SS Ostashkov 110/35/10 kv | 25+25 | 0.84175 | 17.7218 | 0 |  | 17.7218 | 0 | 26.25 | 8.5282 | 8.5282 |  | 67.5114 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 25+25 | 1.79 | 0 |  | 1.79 | 0 | 26.25 | 24.46 |  |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0.3605 | 2.1505 | 0 |  | 2.1505 | 0 | 26.25 | 24.0995
| Nom. Capacity LV, MVA | 25+25 | 15.09 | 0 |  | 15.09 | 0 | 26.25 | 11.16 |  |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.48125 | 15.5712 | 0 |  | 15.5712 | 0 | 26.25 | 10.6788
311 | SS N. Rozhok 110/35/10 kv | 10+10 | 15.57 | 0 |  | 15.57 | 0 | 10.5 | -5.07 | -5.07 | MS is closed | 148.2857 | 311 | SS N. Rozhok 110/35/10 kv | 10+10 | 1.849 | 17.419 | 0 |  | 17.419 | 0 | 10.5 | -6.919 | -6.919 | MS is closed | 165.8952 | Torzhokskie Power networks
| Nom. Capacity MV, MVA | 10+10 | 2.4 | 0 |  | 2.4 | 0 | 10.5 | 8.1 |  |  |  |  | Nom. Capacity MV, MVA | 10+10 | 1.689 | 4.089 | 0 |  | 4.089 | 0 | 10.5 | 6.411
| Nom. Capacity LV, MVA | 10+10 | 13.17 | 0 |  | 13.17 | 0 | 10.5 | -2.67 |  |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.16 | 13.33 | 0 |  | 13.33 | 0 | 10.5 | -2.83
Total: |  | 3921.72 | 1059.8548 | [9 empty] | 1: Total:; 3: 3921.72; 4: 244.6526; 5: 1304.3846
deficit | [9 empty] | -44.1936 |  |  | 1: deficit; Min. 12: -157.8283
proficit | [9 empty] | 1026.7936 |  |  | 1: proficit; Min. 12: 877.5442
[23 empty] | Quantity of SS having load less than 30 % |  |  | 135
[23 empty] | Quantity of SS having load less thah from 30 to 70 % |  |  | 109
[23 empty] | Quantity of SS having load less thah from 70 to 100 % |  |  | 34
[23 empty] | Quantity of SS having load more than 105 % |  |  | 35
Note on E154: Перевод нагрузки по 6 кВ на ПС Кимры
Note on E187: перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on E190: Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on E196: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on E199: Перевод нагрузки Т-1 ПС Стоянцы
Note on E202: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская
Note on T154: Перевод нагрузки по 6 кВ на ПС Кимры
Note on T187: перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on T190: Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on T196: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on T199: Перевод нагрузки Т-1 ПС Стоянцы
Note on T202: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская

## Курск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications | Expected load at main substation | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | MVA | Мin. | [11 empty] | МVА | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 13
One-transformer substations | [11 empty] | One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.68 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.62 | 1.01 | opened | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.016 | 1.696 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.604 | 0.999 | opened
| Nom. capacity MV, MVA | 6.3 | 1.29 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.01 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.011 | 1.301 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 0.999
| Nom. capacity MV, MVA | 6.3 | 0.39 | 4 | 24 hours | 4 | 0 | 4 | 3.61 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.005 | 0.395 | 4 | 24 hours | 4 | 0 | 4 | 3.605
2 | SS 110/10 Beketovo | 1*6,3 | 0.3 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.85 | 1.85 | opened | 2 | SS 110/10 Beketovo | 1*6,3 |  | 0.3 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.85 | 1.85 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.2 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.1 | 0.3 | opened | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.106 | 2.306 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 3.994 | 0.227 | opened
| Nom. capacity MV, MVA | 6.3 | 0.4 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.8 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 0.433 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.767
| Nom. capacity LV, MVA | 6.3 | 1.8 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.3 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.073 | 1.873 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.227
4 | SS 110/10 Voskhod | 1*10,0 | 0.2 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.3 | 2.3 | opened | 4 | SS 110/10 Voskhod | 1*10,0 | 0.039 | 0.239 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.261 | 2.261 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.57 | 6 | 24 hours | 6 | 0 | 6 | 5.43 | 1.73 | opened | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0 | 0.57 | 6 | 24 hours | 6 | 0 | 6 | 5.43 | 1.73 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.57 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.73 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.57 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.73
6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.45 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.71 | 0.62 | opened | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.016 | 0.466 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.694 | 0.62 | opened
| Nom. capacity MV, MVA | 10 | 0.41 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 4.09 |  |  |  | Nom. capacity MV, MVA | 10 | 0.016 | 0.426 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 4.074
| Nom. capacity LV, MVA | 10 | 0.04 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.62 |  |  |  | Nom. capacity LV, MVA | 10 |  | 0.04 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.62
7 | SS 110/10 Zabelye | 1*2,5 | 0.38 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.77 | 1.77 | opened | 7 | SS 110/10 Zabelye | 1*2,5 | 0.003 | 0.383 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.767 | 1.767 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.16 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened | 8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.16 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened
9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.95 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 4.18 | 1.12 | opened | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.46 | 1.41 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.72 | 0.66 | opened
| Nom. capacity MV, MVA | 10 | 0.54 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 3.06 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.54 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 3.06
| Nom. capacity LV, MVA | 10 | 0.41 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1.12 |  |  |  | Nom. capacity LV, MVA | 10 | 0.46 | 0.87 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.66
10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.73 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.48 | 0.48 | opened | 10 | SS 110/10 Malaya Loknya | 1*10,0 |  | 0.73 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.48 | 0.48 | opened
11 | SS 110/35/10 Maritsa | 1*6,3 | 0.71 | 6.24 | 24 hours | 6.24 | 0 | 6.24 | 5.53 | 1.21 | opened | 11 | SS 110/35/10 Maritsa | 1*6,3 | 0.011 | 0.721 | 6.24 | 24 hours | 6.24 | 0 | 6.24 | 5.519 | 1.199 | opened
| Nom. capacity MV, MVA | 6.3 |  | 4.32 | 24 hours | 4.32 | 0 | 4.32 | 4.32 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0 | 4.32 | 24 hours | 4.32 | 0 | 4.32 | 4.32
| Nom. capacity LV, MVA | 6.3 | 0.71 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 1.21 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.011 | 0.721 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 1.199
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 1.21 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 4.68 | 1.21 | opened | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.005 | 1.215 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 4.675 | 1.21 | opened
| Nom. capacity MV, MVA | 6.3 | 0.27 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.47 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.005 | 0.275 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.465
| Nom. capacity LV, MVA | 6.3 | 0.94 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.21 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.94 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.21
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.303 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.097 | 1.097 | opened
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened | 14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.7 | 9.8 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | -3.16 | -3.16 | closed
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.94 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.56 | 0.45 | opened | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 0.745 | 3.685 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 3.815 | 0.436 | opened
| Nom. capacity MV, MVA | 10 | 2.29 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 4.11 |  |  |  | Nom. capacity MV, MVA | 10 | 0.731 | 3.021 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.379
| Nom. capacity LV, MVA | 10 | 0.65 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.45 |  |  |  | Nom. capacity LV, MVA | 10 | 0.014 | 0.664 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.436
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.09 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.71 | 0.71 | opened | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.133 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.667 | 0.667 | opened
17 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.86 | 24 hours | 0.86 | 0 | 0.86 | 0.36 | 0.36 | opened | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.195 | 0.695 | 0.86 | 24 hours | 0.86 | 0 | 0.86 | 0.165 | 0.165 | opened
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened | 18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.41 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.02 | 1.02 | opened | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.015 | 0.425 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.005 | 1.005 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 1.17 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.17 | 0.17 | opened | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.015 | 1.185 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.155 | 0.155 | opened
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 |  | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.88 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.95 | 1.95 | opened | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.231 | 1.111 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.719 | 1.719 | opened
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.21 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.43 | 0.43 | opened | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.015 | 0.225 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.415 | 0.415 | opened
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.0977 | 0.4477 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9823 | 0.9823 | opened
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.015 | 0.385 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.765 | 1.765 | opened
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.045 | 0.645 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.115 | 1.115 | opened
27 | SS 35/10 Biryukovka | 1х1,6 | 0.16 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.4 | 0.4 | opened | 27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.16 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.4 | 0.4 | opened
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.19 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.48 | 0.48 | opened | 28 | SS 35/10 Bobrovka | 1 х 1,6 |  | 0.19 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.48 | 0.48 | opened
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.37 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.39 | 0.39 | opened | 29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.37 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.39 | 0.39 | opened
30 | SS 35/10 Budki | 1 х 1,0 | 0.12 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.52 | 0.52 | opened | 30 | SS 35/10 Budki | 1 х 1,0 |  | 0.12 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.52 | 0.52 | opened
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.35 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.25 | 1.25 | opened | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 |  | 0.35 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.25 | 1.25 | opened
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.037 | 0.257 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.383 | 0.383 | opened
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.24 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.19 | 1.19 | opened | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.016 | 0.256 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.174 | 1.174 | opened
34 | SS 35/10 Bykovo | 1 х 4,0 | 0.76 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.67 | 0.67 | opened | 34 | SS 35/10 Bykovo | 1 х 4,0 | 0.187 | 0.947 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.483 | 0.483 | opened
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.097 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.053 | 2.053 | opened | 35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.097 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.053 | 2.053 | opened
36 | SS 35/10 Vanino | 1 х 2,5 | 0.36 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.44 | 0.44 | opened | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.058 | 0.418 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.382 | 0.382 | opened
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.48 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.57 | 0.57 | opened | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.02 | 0.5 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.55 | 0.55 | opened
38 | SS 35/10 Water storage | 1 х 4,0 | 0.09 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 2.63 | 2.63 | opened | 38 | SS 35/10 Water storage | 1 х 4,0 | 3.516 | 3.606 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | -0.886 | -0.886 | closed
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened | 39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.24 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.66 | 0.66 | opened | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.254 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.646 | 0.646 | opened
41 | SS 35/10 Voronok | 1 х 4,0 | 1 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.1 | 1.1 | opened | 41 | SS 35/10 Voronok | 1 х 4,0 | 0.013 | 1.013 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.087 | 1.087 | opened
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.475 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.675 | 1.675 | opened | 42 | SS 35/10 Vyazovoe | 1 х 2,5 |  | 0.475 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.675 | 1.675 | opened
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.57 | 1.57 | opened
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.13 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.37 | 1.37 | opened | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.01 | 0.14 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.36 | 1.36 | opened
45 | SS 35/10 Glazovo | 1 х 2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 45 | SS 35/10 Glazovo | 1 х 2,5 |  | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.37 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.03 | 1.03 | opened | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.003 | 0.373 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.027 | 1.027 | opened
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened | 47 | SS 35/10 Gordeevka | 1 х 1,6 |  | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.51 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.25 | 0.25 | opened | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.044 | 0.554 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.206 | 0.206 | opened
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.36 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.74 | 0.74 | opened | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.0103 | 0.3703 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.7297 | 0.7297 | opened
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.47 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.96 | 0.96 | opened | 50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.47 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.96 | 0.96 | opened
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.042 | 0.432 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.998 | 0.998 | opened
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.23 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.62 | 2.62 | opened | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.005 | 0.235 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.615 | 2.615 | opened
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.28 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.66 | 0.66 | opened | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.006 | 0.286 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.654 | 0.654 | opened
54 | SS 35/10 Daryino | 1 х 2,5 | 0.24 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.56 | 1.56 | opened | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.032 | 0.272 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.528 | 1.528 | opened
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.53 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.27 | 0.27 | opened | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.026 | 0.556 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.244 | 0.244 | opened
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.36 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.71 | 0.71 | opened | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.025 | 0.385 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.685 | 0.685 | opened
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.3 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.55 | 0.55 | opened | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.038 | 0.338 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.512 | 0.512 | opened
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.011 | 0.281 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.869 | 1.869 | opened
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.043 | 0.643 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.197 | 0.197 | opened
60 | SS 35/10 Znamenka | 1 х 1,8 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened | 60 | SS 35/10 Znamenka | 1 х 1,8 |  | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened
61 | SS 35/10 Iskra | 1 х 2,5 | 0.35 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.23 | 0.23 | opened | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.033 | 0.383 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.197 | 0.197 | opened
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.35 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.45 | 0.45 | opened | 62 | SS 35/10 Kazanka | 1 х 4,0 |  | 0.35 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.45 | 0.45 | opened
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.13 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.67 | 1.67 | opened | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.01 | 0.14 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.66 | 1.66 | opened
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.4 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.24 | 0.24 | opened | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.009 | 0.409 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.231 | 0.231 | opened
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.48 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.26 | 0.26 | opened | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.202 | 0.682 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.058 | 0.058 | opened
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.95 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.58 | 0.58 | opened | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.031 | 0.981 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.549 | 0.549 | opened
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.36 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.48 | 0.48 | opened | 67 | SS 35/10 Kolontaevka | 1 х 2,5 |  | 0.36 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.48 | 0.48 | opened
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.3 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 1.12 | 1.12 | opened | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.022 | 0.322 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 1.098 | 1.098 | opened
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.4 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.36 | 0.36 | opened | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.009 | 0.409 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.351 | 0.351 | opened
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.106 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.324 | 1.324 | opened | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.12 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.31 | 1.31 | opened
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.59 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.14 | 0.14 | opened | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.022 | 0.612 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.118 | 0.118 | opened
72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.94 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.15 | 0.15 | opened | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.011 | 0.951 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.139 | 0.139 | opened
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.6 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.69 | 0.69 | opened | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.035 | 0.635 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.655 | 0.655 | opened
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.38 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.77 | 0.77 | opened | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0.008 | 0.388 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.762 | 0.762 | opened
75 | SS 35/10 lyubimovka-1 | 1 х 3,2 | 0.1 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.86 | 0.86 | opened | 75 | SS 35/10 lyubimovka-1 | 1 х 3,2 | 0.041 | 0.141 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.819 | 0.819 | opened
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.62 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.48 | 0.48 | opened | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.051 | 0.671 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.429 | 0.429 | opened
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.61 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.67 | 0.67 | opened | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.005 | 0.615 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.665 | 0.665 | opened
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.24 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.95 | 0.95 | opened | 78 | SS 35/10 М. Kryuki | 1 х 2,5 |  | 0.24 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.95 | 0.95 | opened
79 | SS 35/10 Markovo | 1 х 2,5 | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 | opened | 79 | SS 35/10 Markovo | 1 х 2,5 |  | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 | opened
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 1.01 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 0.32 | 0.32 | opened | 80 | SS 35/10 Marmyzhi | 1 х 2,5 |  | 1.01 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 0.32 | 0.32 | opened
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.58 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.57 | 1.57 | opened | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.013 | 0.593 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.557 | 1.557 | opened
82 | SS 35/10 Mokva | 1 х 4,0 | 0.59 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.56 | 1.56 | opened | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.011 | 0.601 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.549 | 1.549 | opened
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.026 | 0.226 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.874 | 0.874 | opened
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.18 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.72 | 0.72 | opened | 84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.18 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.72 | 0.72 | opened
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.015 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.055 | 1.055 | opened | 85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.015 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.055 | 1.055 | opened
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.107 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.193 | 4.193 | opened | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.107 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.193 | 4.193 | opened
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.008 | 0.508 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.642 | 1.642 | opened
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.07 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.33 | 1.33 | opened | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.078 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.322 | 1.322 | opened
89 | SS 35/10 Niva | 1 х 2,5 | 0.26 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.3 | 1.3 | opened | 89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.275 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.285 | 1.285 | opened
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.75 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.22 | 0.22 | opened | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0.005 | 0.755 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.215 | 0.215 | opened
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.36 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.28 | 0.28 | opened | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.01 | 0.37 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.27 | 0.27 | opened
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 2.19 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 0.78 | 0.78 | opened | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.66 | 2.85 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 0.12 | 0.12 | opened
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.2 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 2.12 | 2.12 | opened | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.41 | 0.61 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.71 | 1.71 | opened
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.13 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.27 | 1.27 | opened | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.13 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.27 | 1.27 | opened
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.33 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.07 | 1.07 | opened | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 |  | 0.33 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.07 | 1.07 | opened
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.74 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.41 | 1.41 | opened | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0.099 | 0.839 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.311 | 1.311 | opened
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.02 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.72 | 0.72 | opened | 97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.02 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.72 | 0.72 | opened
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.208 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.942 | 1.942 | opened | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.015 | 0.223 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.927 | 1.927 | opened
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.43 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.72 | 1.72 | opened | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.439 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.711 | 1.711 | opened
100 | SS 35/10 Pristen | 1 х 4,0 | 1.1 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 2.2 | 2.2 | opened | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.03 | 1.13 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 2.17 | 2.17 | opened
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.2 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.54 | 0.54 | opened | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.012 | 0.212 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.528 | 0.528 | opened
102 | SS 35/10 Reut | 1 х 2,5 | 0.15 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.71 | 0.71 | opened | 102 | SS 35/10 Reut | 1 х 2,5 |  | 0.15 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.71 | 0.71 | opened
103 | SS 35/10 Rovenka | 1 х 1,6 | 0.068 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.362 | 1.362 | opened | 103 | SS 35/10 Rovenka | 1 х 1,6 | 0.015 | 0.083 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.347 | 1.347 | opened
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.09 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.61 | 0.61 | opened | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.033 | 0.123 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.577 | 0.577 | opened
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.318 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.982 | 1.982 | opened | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 |  | 0.318 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.982 | 1.982 | opened
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.33 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.98 | 0.98 | opened | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.003 | 0.333 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.977 | 0.977 | opened
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.289 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.141 | 1.141 | opened | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.313 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.117 | 1.117 | opened
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.34 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.6 | 0.6 | opened | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.038 | 0.378 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.562 | 0.562 | opened
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.51 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.64 | 0.64 | opened | 109 | SS 35/10 Ryazanovo | 1 х 1,6 |  | 0.51 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.64 | 0.64 | opened
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.16 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 1.09 | 1.09 | opened | 110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.16 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 1.09 | 1.09 | opened
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.18 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.52 | 2.52 | opened | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0.005 | 0.185 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.515 | 2.515 | opened
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.346 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.084 | 1.084 | opened | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.051 | 0.397 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.033 | 1.033 | opened
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.075 | 0.675 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.085 | 1.085 | opened
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened | 114 | SS 35/10 Spasskoe | 1 х 1,6 |  | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.15 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.25 | 1.25 | opened | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.004 | 0.154 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.246 | 1.246 | opened
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.41 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.89 | 0.89 | opened | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.038 | 0.448 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.852 | 0.852 | opened
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.23 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 1.11 | 1.11 | opened | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.005 | 0.235 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 1.105 | 1.105 | opened
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.47 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.24 | 0.24 | opened | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.002 | 0.472 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.238 | 0.238 | opened
119 | SS 35/10 Telmana | 1 х 2,5 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.009 | 0.589 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.561 | 0.561 | opened
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.37 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.06 | 1.06 | opened | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.007 | 0.377 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.053 | 1.053 | opened
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 | opened | 121 | SS 35/10 Fateevka | 1 х 2,5 |  | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 | opened
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.15 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.57 | 1.57 | opened | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.015 | 0.165 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.555 | 1.555 | opened
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.011 | 0.251 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.849 | 0.849 | opened
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.11 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.74 | 0.74 | opened | 124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.11 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.74 | 0.74 | opened
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.018 | 0.298 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.132 | 1.132 | opened
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.23 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.2 | 1.2 | opened | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.011 | 0.241 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.189 | 1.189 | opened
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.5 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.97 | 0.97 | opened | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.013 | 0.513 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.957 | 0.957 | opened
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.14 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.71 | 0.71 | opened | 128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.14 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.71 | 0.71 | opened
129 | SS 35/10 Elevator | 1х6,3 | 0.23 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.37 | 0.37 | opened | 129 | SS 35/10 Elevator | 1х6,3 |  | 0.23 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.37 | 0.37 | открыт
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.2 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.44 | 0.44 | opened | 130 | SS 35/10 Yankovo | 1 х 1,6 |  | 0.2 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.44 | 0.44 | opened
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened | 131 | SS 35/10 Yasenki | 1 х 2,5 | 0.038 | 0.518 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.632 | 1.632 | opened
Two- and more transformer substations | [11 empty] | Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 24.23 | 0 | 0 | 24.23 | 0 | 26.25 | 2.02 | 2.02 | opened | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 24.23 | 0 | 0 | 24.23 | 0 | 26.25 | 2.02 | 2.02 | opened
2 | SS 110/10 ARZ | 6,3+10,0 | 3.15 | 0.9 | 45 | 2.25 | 0 | 6.62 | 4.37 | 4.37 | opened | 2 | SS 110/10 ARZ | 6,3+10,0 |  | 3.15 | 0.9 | 45 | 2.25 | 0 | 6.62 | 4.37 | 4.37 | opened
3 | SS 110/35/10 Atomgrad | 2*25 | 13.35 | 20.2 | 120 | -6.85 | 0 | 26.25 | 33.1 | 23.5 | opened | 3 | SS 110/35/10 Atomgrad | 2*25 | 0.081 | 13.431 | 20.2 | 120 | -6.769 | 0 | 26.25 | 33.019 | 23.441 | opened
| Nom. capacity MV, MVA | 25 | 1 | 10.6 | 120 | -9.6 | 0 | 26.25 | 35.85 |  |  |  | Nom. capacity MV, MVA | 25 | 0.098 | 1.098 | 10.6 | 120 | -9.502 | 0 | 26.25 | 35.752
| Nom. capacity lV, MVA | 25 | 12.35 | 9.6 | 120 | 2.75 | 0 | 26.25 | 23.5 |  |  |  | Nom. capacity lV, MVA | 25 | 0.059 | 12.409 | 9.6 | 120 | 2.809 | 0 | 26.25 | 23.441
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.44 | 0.6 | 120 | -0.16 | 0 | 6.62 | 6.78 | 6.78 | opened | 4 | SS 110/10 B. Zhirovo | 2*6,3 |  | 0.44 | 0.6 | 120 | -0.16 | 0 | 6.62 | 6.78 | 6.78 | opened
5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.96 | 6.19 | 15 | -5.23 | 0 | 5.88 | 11.11 | 5.43 | opened | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.012 | 0.972 | 6.19 | 15 | -5.218 | 0 | 5.88 | 11.098 | 5.429 | opened
| Ном. Мощность СН, МВА | 5,6+10,0 | 0.32 | 6 |  | -5.68 | 0 | 5.88 | 11.56 |  |  |  | Ном. Мощность СН, МВА | 5,6+10,0 | 0.011 | 0.331 | 6 | 0 | -5.669 | 0 | 5.88 | 11.549
| Nom. capacity LV, MVA | 5,6+10,0 | 0.64 | 0.19 | 120 | 0.45 | 0 | 5.88 | 5.43 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.001 | 0.641 | 0.19 | 120 | 0.451 | 0 | 5.88 | 5.429
6 | SS 110/35/10 Belaya | 2*16,0 | 6 | 12 | 120 | -6 | 0 | 16.8 | 22.8 | 13 | opened | 6 | SS 110/35/10 Belaya | 2*16,0 | 0.783 | 6.783 | 12 | 120 | -5.217 | 0 | 16.8 | 22.017 | 12.497 | opened
| Nom. capacity MV, MVA | 16 | 3.8 | 0 |  | 3.8 | 0 | 16.8 | 13 |  |  |  | Nom. capacity MV, MVA | 16 | 0.503 | 4.303 | 0 | 0 | 4.303 | 0 | 16.8 | 12.497
| Nom. capacity LV, MVA | 16 | 2.2 | 12 | 120 | -9.8 | 0 | 16.8 | 26.6 |  |  |  | Nom. capacity LV, MVA | 16 | 0.28 | 2.48 | 12 | 120 | -9.52 | 0 | 16.8 | 26.32
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.03 | 1.3 | 120 | -0.27 | 0 | 6.62 | 6.89 | 6.39 | opened | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.026 | 1.056 | 1.3 | 120 | -0.244 | 0 | 6.62 | 6.864 | 6.386 | opened
| Nom. capacity MV, MVA | 6.3 | 0.23 |  |  | 0.23 | 0 | 6.62 | 6.39 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.004 | 0.234 | 0 | 0 | 0.234 | 0 | 6.62 | 6.386
| Nom. capacity LV, MVA | 6.3 | 0.8 | 1.3 | 120 | -0.5 | 0 | 6.62 | 7.12 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.022 | 0.822 | 1.3 | 120 | -0.478 | 0 | 6.62 | 7.098
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.22 | 1.17 | 45 | 1.05 | 0 | 2.63 | 1.58 | 1.58 | opened | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.022 | 2.242 | 1.17 | 45 | 1.072 | 0 | 2.63 | 1.558 | 1.558 | opened
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 52.92 | 16.8 | 0 | 36.12 | 0 | 84.53 | 48.41 | 48.41 | opened | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.506 | 54.426 | 16.8 | 0 | 37.626 | 0 | 84.53 | 46.904 | 46.904 | opened
| Nom. capacity MV, MVA | 40,0+2*40,5 | 23.81 | 16.8 | 0 | 7.01 | 0 | 84.53 | 77.52 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 1.447 | 25.257 | 16.8 | 0 | 8.457 | 0 | 84.53 | 76.073
| Nom. capacity MV, MVA | 40,0+2*40,5 | 29.11 | 0 | 0 | 29.11 | 0 | 84.53 | 55.42 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.059 | 29.169 | 0 | 0 | 29.169 | 0 | 84.53 | 55.361
10 | SS 110/10 Vysokaya | 2*16,0 | 19.46 | 3.2 | 15 | 16.26 | 0 | 16.8 | 0.54 | 0.54 | opened | 10 | SS 110/10 Vysokaya | 2*16,0 |  | 19.46 | 3.2 | 15 | 16.26 | 0 | 16.8 | 0.54 | 0.54 | opened
11 | SS 110/35/10 Glushkovo | 2*10,0 | 7.95 | 8.04 | 120 | -0.09 | 0 | 10.5 | 10.59 | 7.59 | opened | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 0.579 | 8.529 | 8.04 | 120 | 0.489 | 0 | 10.5 | 10.011 | 7.55 | opened
| Nom. capacity MV, MVA | 10 | 3.6 | 6.6 | 120 | -3 | 0 | 10.5 | 13.5 |  |  |  | Nom. capacity MV, MVA | 10 | 0.539 | 4.139 | 6.6 | 120 | -2.461 | 0 | 10.5 | 12.961
| Nom. capacity LV, MVA | 10 | 4.35 | 1.44 | 80 | 2.91 | 0 | 10.5 | 7.59 |  |  |  | Nom. capacity LV, MVA | 10 | 0.04 | 4.39 | 1.44 | 80 | 2.95 | 0 | 10.5 | 7.55
12 | SS 110/10 Gorodskaya | 2*25,0 | 10.05 | 0 | 0 | 10.05 | 0 | 26.25 | 16.2 | 16.2 | opened | 12 | SS 110/10 Gorodskaya | 2*25,0 | 4.53 | 14.58 | 0 | 0 | 14.58 | 0 | 26.25 | 11.67 | 11.67 | opened
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 9.52 | 6.52 | 120 | 3 | 0 | 10.5 | 7.5 | 4.86 | opened | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 0.635 | 10.155 | 6.52 | 120 | 3.635 | 0 | 10.5 | 6.865 | 4.504 | opened
| Nom. capacity MV, MVA | 10+16,0 | 3.42 | 6.06 |  | -2.64 | 0 | 10.5 | 13.14 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 0.279 | 3.699 | 6.06 | 0 | -2.361 | 0 | 10.5 | 12.861
| Nom. capacity LV, MVA | 10+16,0 | 6.1 | 0.46 | 120 | 5.64 | 0 | 10.5 | 4.86 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.356 | 6.456 | 0.46 | 120 | 5.996 | 0 | 10.5 | 4.504
14 | SS 110/35/10 Dmitriev | 2*10,0 | 7.85 | 10.4 | 120 | -2.55 | 0 | 10.5 | 13.05 | 8.01 | opened | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 0.216 | 8.066 | 10.4 | 120 | -2.334 | 0 | 10.5 | 12.834 | 7.799 | opened
| Nom. capacity MV, MVA | 10 | 2.36 | 7.4 |  | -5.04 | 0 | 10.5 | 15.54 |  |  |  | Nom. capacity MV, MVA | 10 | 0.005 | 2.365 | 7.4 | 0 | -5.035 | 0 | 10.5 | 15.535
| Nom. capacity LV, MVA | 10 | 5.49 | 3 | 80 | 2.49 | 0 | 10.5 | 8.01 |  |  |  | Nom. capacity LV, MVA | 10 | 0.211 | 5.701 | 3 | 80 | 2.701 | 0 | 10.5 | 7.799
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.36 | 0.5 | 120 | -0.14 | 0 | 10.5 | 10.64 | 10.64 | opened | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.377 | 0.5 | 120 | -0.123 | 0 | 10.5 | 10.623 | 10.623 | opened
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 5.2 | 22.1 | 80 | -16.9 | 0 | 26.25 | 43.15 | 27.99 | opened | 16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.277 | 5.477 | 22.1 | 80 | -16.623 | 0 | 26.25 | 42.873 | 27.771 | opened
| Nom. capacity MV, MVA | 25 | 3.64 | 18.8 |  | -15.16 | 0 | 26.25 | 41.41 |  |  |  | Nom. capacity MV, MVA | 25 | 0.058 | 3.698 | 18.8 | 0 | -15.102 | 0 | 26.25 | 41.352
| Nom. capacity LV, MVA | 25 | 1.56 | 3.3 | 120 | -1.74 | 0 | 26.25 | 27.99 |  |  |  | Nom. capacity LV, MVA | 25 | 0.219 | 1.779 | 3.3 | 120 | -1.521 | 0 | 26.25 | 27.771
17 | SS 110/35/10 Kamyshi | 2*6,3 | 7.87 | 5.45 | 20 | 2.42 | 0 | 6.62 | 4.2 | 3.36 | opened | 17 | SS 110/35/10 Kamyshi | 2*6,3 | 3.889 | 11.759 | 5.45 | 20 | 6.309 | 0 | 6.62 | 0.311 | -0.458 | closed
| Nom. capacity MV, MVA | 6.3 | 6.71 | 3.45 |  | 3.26 | 0 | 6.62 | 3.36 |  |  |  | Nom. capacity MV, MVA | 6.3 | 3.818 | 10.528 | 3.45 | 0 | 7.078 | 0 | 6.62 | -0.458
| Nom. capacity LV, MVA | 6.3 | 1.16 | 2 | 20 | -0.84 | 0 | 6.62 | 7.46 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.071 | 1.231 | 2 | 20 | -0.769 | 0 | 6.62 | 7.389
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 11.37 | 6.97 | 120 | 4.4 | 0 | 15.75 | 11.35 | 11.35 | opened | 18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.424 | 11.794 | 6.97 | 120 | 4.824 | 0 | 15.75 | 10.926 | 10.926 | opened
| Nom. capacity MV, MVA | 15,0+16,0 | 10.12 | 6.6 |  | 3.52 | 0 | 15.75 | 12.23 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.338 | 10.458 | 6.6 | 0 | 3.858 | 0 | 15.75 | 11.892
| Nom. capacity LV, MVA | 15,0+16,0 | 1.25 | 0.37 | 120 | 0.88 | 0 | 15.75 | 14.87 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.086 | 1.336 | 0.37 | 120 | 0.966 | 0 | 15.75 | 14.784
19 | SS 110/35/10 Kilikino | 2*16,0 | 2.59 | 6.9 | 120 | -4.31 | 0 | 16.8 | 21.11 | 18.62 | opened | 19 | SS 110/35/10 Kilikino | 2*16,0 | 0.052 | 2.642 | 6.9 | 120 | -4.258 | 0 | 16.8 | 21.058 | 18.62 | opened
| Nom. capacity MV, MVA | 16 | 2.51 | 5 |  | -2.49 | 0 | 16.8 | 19.29 |  |  |  | Nom. capacity MV, MVA | 16 | 0.052 | 2.562 | 5 | 0 | -2.438 | 0 | 16.8 | 19.238
| Nom. capacity LV, MVA | 16 | 0.08 | 1.9 | 120 | -1.82 | 0 | 16.8 | 18.62 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.08 | 1.9 | 120 | -1.82 | 0 | 16.8 | 18.62
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 55.32 | 16.36 | 120 | 38.96 | 0 | 42 | 3.04 | 3.04 | opened | 20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.57 | 57.89 | 16.36 | 120 | 41.53 | 0 | 42 | 0.47 | 0.47 | opened
| Nom. capacity MV, MVA | 40 | 27.08 | 13.06 | 120 | 14.02 | 0 | 42 | 27.98 |  |  |  | Nom. capacity MV, MVA | 40 |  | 27.08 | 13.06 | 120 | 14.02 | 0 | 42 | 27.98
| Nom. capacity LV, MVA | 40 | 28.24 | 3.3 | 120 | 24.94 | 0 | 42 | 17.06 |  |  |  | Nom. capacity LV, MVA | 40 | 2.57 | 30.81 | 3.3 | 120 | 27.51 | 0 | 42 | 14.49
21 | SS 110/35/10 Klyukva | 2*16,0 | 2.59 | 1.2 | 120 | 1.39 | 0 | 16.8 | 15.41 | 15.41 | opened | 21 | SS 110/35/10 Klyukva | 2*16,0 | 0.307 | 2.897 | 1.2 | 120 | 1.697 | 0 | 16.8 | 15.103 | 15.103 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16 |  | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 2.59 | 1.2 | 120 | 1.39 | 0 | 16.8 | 15.41 |  |  |  | Nom. capacity LV, MVA | 16 | 0.307 | 2.897 | 1.2 | 120 | 1.697 | 0 | 16.8 | 15.103
22 | SS 110/10 Kompressornaya | 2*40,0 | 1.02 | 0 | 0 | 1.02 | 0 | 42 | 40.98 | 40.98 | opened | 22 | SS 110/10 Kompressornaya | 2*40,0 |  | 1.02 | 0 | 0 | 1.02 | 0 | 42 | 40.98 | 40.98 | opened
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 7.32 | 8 | 120 | -0.68 | 0 | 10.5 | 11.18 | 10.58 | opened | 23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.017 | 8.337 | 8 | 120 | 0.337 | 0 | 10.5 | 10.163 | 10.145 | opened
| Nom. capacity MV, MVA | 10,0+16,0 | 5.82 | 5.9 |  | -0.08 | 0 | 10.5 | 10.58 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.062 | 5.882 | 5.9 | 0 | -0.018 | 0 | 10.5 | 10.518
| Nom. capacity LV, MVA | 10,0+16,0 | 1.5 | 2.1 |  | -0.6 | 0 | 10.5 | 11.1 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.955 | 2.455 | 2.1 | 0 | 0.355 | 0 | 10.5 | 10.145
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 7.14 | 0 | 0 | 7.14 | 0 | 10.5 | 3.36 | 3.36 | opened | 24 | SS 110/10 Kotelnaya | 10,0+25,0 | 2.842 | 9.982 | 0 | 0 | 9.982 | 0 | 10.5 | 0.518 | 0.518 | opened
25 | SS 110/35/10 Kshen | 2*10,0 | 8.84 | 6.63 | 10 | 2.21 | 0 | 10.5 | 8.29 | 6.13 | opened | 25 | SS 110/35/10 Kshen | 2*10,0 | 1.816 | 10.656 | 6.63 | 10 | 4.026 | 0 | 10.5 | 6.474 | 4.717 | opened
| Nom. capacity MV, MVA | 10 | 3.9 | 6.06 |  | -2.16 | 0 | 10.5 | 12.66 |  |  |  | Nom. capacity MV, MVA | 10 | 0.403 | 4.303 | 6.06 | 0 | -1.757 | 0 | 10.5 | 12.257
| Nom. capacity LV, MVA | 10 | 4.94 | 0.57 | 120 | 4.37 | 0 | 10.5 | 6.13 |  |  |  | Nom. capacity LV, MVA | 10 | 1.413 | 6.353 | 0.57 | 120 | 5.783 | 0 | 10.5 | 4.717
26 | SS 110/6 Lesnaya | 2*40,0 | 1.99 | 0 | 0 | 1.99 | 0 | 42 | 40.01 | 40.01 | opened | 26 | SS 110/6 Lesnaya | 2*40,0 |  | 1.99 | 0 | 0 | 1.99 | 0 | 42 | 40.01 | 40.01 | opened
27 | SS 110/35/10 Lgov | 2*25,0 | 12.32 | 4 | 120 | 8.32 | 0 | 26.25 | 17.93 | 3.19 | opened | 27 | SS 110/35/10 Lgov | 2*25,0 | 0.294 | 12.614 | 4 | 120 | 8.614 | 0 | 26.25 | 17.636 | 2.896 | opened
| Nom. capacity MV, MVA | 25 | 1.01 |  |  | 1.01 | 0 | 10.5 | 9.49 |  |  |  | Nom. capacity MV, MVA | 25 | 0 | 1.01 | 0 | 0 | 1.01 | 0 | 10.5 | 9.49
| Nom. capacity LV, MVA | 25 | 11.31 | 4 | 120 | 7.31 | 0 | 10.5 | 3.19 |  |  |  | Nom. capacity LV, MVA | 25 | 0.294 | 11.604 | 4 | 120 | 7.604 | 0 | 10.5 | 2.896
28 | SS 110/35/10 Lukashevka | 2*16,0 | 7.38 | 10.6 | 120 | -3.22 | 0 | 16.8 | 20.02 | 16.12 | opened | 28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.057 | 7.437 | 10.6 | 120 | -3.163 | 0 | 16.8 | 19.963 | 16.12 | opened
| Nom. capacity MV, MVA | 16 | 1.4 | 5.3 |  | -3.9 | 0 | 16.8 | 20.7 |  |  |  | Nom. capacity MV, MVA | 16 | 0.057 | 1.457 | 5.3 | 0 | -3.843 | 0 | 16.8 | 20.643
| Nom. capacity LV, MVA | 16 | 5.98 | 5.3 | 120 | 0.68 | 0 | 16.8 | 16.12 |  |  |  | Nom. capacity LV, MVA | 16 |  | 5.98 | 5.3 | 120 | 0.68 | 0 | 16.8 | 16.12
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 3.24 | 13.1 | 120 | -9.86 | 0 | 6.62 | 16.48 | 7.18 | opened | 29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.126 | 3.366 | 13.1 | 120 | -9.734 | 0 | 6.62 | 16.354 | 7.175 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 2.5 | 11.8 |  | -9.3 | 0 | 6.62 | 15.92 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.121 | 2.621 | 11.8 | 0 | -9.179 | 0 | 6.62 | 15.799
| Nom. capacity LV, MVA | 6,3+10,0 | 0.74 | 1.3 |  | -0.56 | 0 | 6.62 | 7.18 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.005 | 0.745 | 1.3 | 0 | -0.555 | 0 | 6.62 | 7.175
30 | SS 110/35/6 Manturovo | 2*16,0 | 6.88 | 9.35 | 10 | -2.47 | 0 | 16.8 | 19.27 | 16.77 | opened | 30 | SS 110/35/6 Manturovo | 2*16,0 | 0.382 | 7.262 | 9.35 | 10 | -2.088 | 0 | 16.8 | 18.888 | 16.77 | opened
| Nom. capacity MV, MVA | 16 | 6.59 | 9.09 |  | -2.5 | 0 | 16.8 | 19.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.382 | 6.972 | 9.09 | 0 | -2.118 | 0 | 16.8 | 18.918
| Nom. capacity LV, MVA | 16 | 0.29 | 0.26 | 120 | 0.03 | 0 | 16.8 | 16.77 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.29 | 0.26 | 120 | 0.03 | 0 | 16.8 | 16.77
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 6.39 | 9.6 | 120 | -3.21 | 0 | 6.62 | 9.83 | 7.68 | opened | 31 | SS 110/35/10 8th Marta | 6,3+10,0 | 0.492 | 6.882 | 9.6 | 120 | -2.718 | 0 | 6.62 | 9.338 | 7.194 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 5.54 | 6.6 | 120 | -1.06 | 0 | 6.62 | 7.68 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.486 | 6.026 | 6.6 | 120 | -0.574 | 0 | 6.62 | 7.194
| Nom. capacity LV, MVA | 6,3+10,0 | 0.85 | 3 | 45 | -2.15 | 0 | 6.62 | 8.77 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.006 | 0.856 | 3 | 45 | -2.144 | 0 | 6.62 | 8.764
32 | SS 110/10 Martovskaya | 2*6,3 | 0.63 | 0.55 | 120 | 0.08 | 0 | 6.62 | 6.54 | 6.54 | opened | 32 | SS 110/10 Martovskaya | 2*6,3 | 0.288 | 0.918 | 0.55 | 120 | 0.368 | 0 | 6.62 | 6.252 | 6.252 | opened
33 | SS 110/35/10 Maryino | 10,0+25,0 | 7.16 | 8.11 | 120 | -0.95 | 0 | 10.5 | 11.45 | 10.06 | opened | 33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.087 | 7.247 | 8.11 | 120 | -0.863 | 0 | 10.5 | 11.363 | 10.05 | opened
| Nom. capacity MV, MVA | 10,0+25,0 | 3.51 | 4.9 |  | -1.39 | 0 | 10.5 | 11.89 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.077 | 3.587 | 4.9 | 0 | -1.313 | 0 | 10.5 | 11.813
| Nom. capacity LV, MVA | 10,0+25,0 | 3.65 | 3.21 |  | 0.44 | 0 | 10.5 | 10.06 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.01 | 3.66 | 3.21 | 0 | 0.45 | 0 | 10.5 | 10.05
34 | SS 110/35/10 Medvenka | 2*10,0 | 6.19 | 19.22 | 120 | -13.03 | 0 | 10.5 | 23.53 | 8.89 | opened | 34 | SS 110/35/10 Medvenka | 2*10,0 | 0.356 | 6.546 | 19.22 | 120 | -12.674 | 0 | 10.5 | 23.174 | 8.773 | opened
| Nom. capacity MV, MVA | 10 | 2.46 | 17.1 |  | -14.64 | 0 | 10.5 | 25.14 |  |  |  | Nom. capacity MV, MVA | 10 | 0.239 | 2.699 | 17.1 | 0 | -14.401 | 0 | 10.5 | 24.901
| Nom. capacity LV, MVA | 10 | 3.73 | 2.12 | 120 | 1.61 | 0 | 10.5 | 8.89 |  |  |  | Nom. capacity LV, MVA | 10 | 0.117 | 3.847 | 2.12 | 120 | 1.727 | 0 | 10.5 | 8.773
35 | SS 110/6 Neftyanaya | 2*10,0 | 0.144 |  |  | 0.144 | 0 | 10.5 | 10.356 | 10.356 | opened | 35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.144 | 0 | 0 | 0.144 | 0 | 10.5 | 10.356 | 10.356 | opened
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 9.8 | 26.86 | 120 | -17.06 | 0 | 16.8 | 33.86 | 17.86 | opened | 36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 0.7343 | 10.5343 | 26.86 | 120 | -16.3257 | 0 | 16.8 | 33.1257 | 17.162 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 1.4 | 17.4 | 0 | -16 | 0 | 16.8 | 32.8 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.0363 | 1.4363 | 17.4 | 0 | -15.9637 | 0 | 16.8 | 32.7637
| Nom. capacity LV, MVA | 16,0 + 25,0 | 8.4 | 9.46 |  | -1.06 | 0 | 16.8 | 17.86 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.698 | 9.098 | 9.46 | 0 | -0.362 | 0 | 16.8 | 17.162
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 9.58 | 15.5 | 120 | -5.92 | 0 | 16.8 | 22.72 | 14.11 | opened | 37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.201 | 9.781 | 15.5 | 120 | -5.719 | 0 | 16.8 | 22.519 | 13.989 | opened
| Nom. capacity MV, MVA | 16 | 5.88 | 14.5 |  | -8.62 | 0 | 16.8 | 25.42 |  |  |  | Nom. capacity MV, MVA | 16 | 0.08 | 5.96 | 14.5 | 0 | -8.54 | 0 | 16.8 | 25.34
| Nom. capacity LV, MVA | 16 | 3.69 | 1 | 120 | 2.69 | 0 | 16.8 | 14.11 |  |  |  | Nom. capacity LV, MVA | 16 | 0.121 | 3.811 | 1 | 120 | 2.811 | 0 | 16.8 | 13.989
38 | SS 110/35/10 Olkhovatka | 2 х 6,3 | 1.48 | 6.31 | 120 | -4.83 | 0 | 6.62 | 11.45 | 7.76 | opened | 38 | SS 110/35/10 Olkhovatka | 2 х 6,3 | 0.052 | 1.532 | 6.31 | 120 | -4.778 | 0 | 6.62 | 11.398 | 7.741 | opened
| Nom. capacity MV, MVA | 6.3 | 1.31 | 5 | 120 | -3.69 | 0 | 6.62 | 10.31 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 1.343 | 5 | 120 | -3.657 | 0 | 6.62 | 10.277
| Nom. capacity LV, MVA | 6.3 | 0.17 | 1.31 | 120 | -1.14 | 0 | 6.62 | 7.76 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.019 | 0.189 | 1.31 | 120 | -1.121 | 0 | 6.62 | 7.741
39 | SS 110/10 Paniki | 2 х 2,5 | 0.47 | 0.1 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened | 39 | SS 110/10 Paniki | 2 х 2,5 |  | 0.47 | 0.1 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened
40 | SS 110/35/10 Peny | 2 х 16,0 | 7.67 | 6.9 | 120 | 0.77 | 0 | 16.8 | 16.03 | 14.48 | opened | 40 | SS 110/35/10 Peny | 2 х 16,0 | 0.124 | 7.794 | 6.9 | 120 | 0.894 | 0 | 16.8 | 15.906 | 14.46 | opened
| Nom. capacity MV, MVA | 16 | 1.95 | 3.5 |  | -1.55 | 0 | 16.8 | 18.35 |  |  |  | Nom. capacity MV, MVA | 16 | 0.104 | 2.054 | 3.5 | 0 | -1.446 | 0 | 16.8 | 18.246
| Nom. capacity LV, MVA | 16 | 5.72 | 3.4 | 120 | 2.32 | 0 | 16.8 | 14.48 |  |  |  | Nom. capacity LV, MVA | 16 | 0.02 | 5.74 | 3.4 | 120 | 2.34 | 0 | 16.8 | 14.46
41 | SS 110/35/10 Pribor | 2 х 25,0 | 25.53 | 2.46 | 0 | 23.07 | 0 | 26.25 | 3.18 | 3.18 | opened | 41 | SS 110/35/10 Pribor | 2 х 25,0 | 1.85 | 27.38 | 2.46 | 0 | 24.92 | 0 | 26.25 | 1.33 | 1.33 | opened
| Nom. capacity MV, MVA | 25 |  |  |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 25 |  | 0 | 0 | 0 | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 25.53 | 2.46 | 0 | 23.07 | 0 | 26.25 | 3.18 |  |  |  | Nom. capacity LV, MVA | 25 | 1.85 | 27.38 | 2.46 | 0 | 24.92 | 0 | 26.25 | 1.33
42 | SS 110/10 Progress | 2 х 63,0 | 28.16 | 0 | 0 | 28.16 | 0 | 66.2 | 38.04 | 38.04 | opened | 42 | SS 110/10 Progress | 2 х 63,0 |  | 28.16 | 0 | 0 | 28.16 | 0 | 66.2 | 38.04 | 38.04 | opened
43 | SS 110/10 PTF | 6,3 + 10,0 | 6.27 | 0 | 0 | 6.27 | 0 | 6.62 | 0.35 | 0.35 | opened | 43 | SS 110/10 PTF | 6,3 + 10,0 |  | 6.27 | 0 | 0 | 6.27 | 0 | 6.62 | 0.35 | 0.35 | opened
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 1.25 | 15.7 | 120 | -14.45 | 0 | 10.5 | 24.95 | 16 | opened | 44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.007 | 1.257 | 15.7 | 120 | -14.443 | 0 | 10.5 | 24.943 | 15.993 | opened
| Nom. capacity MV, MVA | 10 | 0.35 | 9.3 |  | -8.95 | 0 | 10.5 | 19.45 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.35 | 9.3 | 0 | -8.95 | 0 | 10.5 | 19.45
| Nom. capacity LV, MVA | 10 | 0.9 | 6.4 |  | -5.5 | 0 | 10.5 | 16 |  |  |  | Nom. capacity LV, MVA | 10 | 0.007 | 0.907 | 6.4 | 0 | -5.493 | 0 | 10.5 | 15.993
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.08 | 21.4 | 45 | -19.32 | 0 | 6.62 | 25.94 | 9.56 | opened | 45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 0.401 | 2.481 | 21.4 | 45 | -18.919 | 0 | 6.62 | 25.539 | 9.482 | opened
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.42 | 17.8 |  | -16.38 | 0 | 6.62 | 23 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 0.323 | 1.743 | 17.8 | 0 | -16.057 | 0 | 6.62 | 22.677
| Nom. capacity LV, MVA | 6,3 + 10,0 | 0.66 | 3.6 | 45 | -2.94 | 0 | 6.62 | 9.56 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.078 | 0.738 | 3.6 | 45 | -2.862 | 0 | 6.62 | 9.482
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 16.99 | 3.25 | 10 | 13.74 | 0 | 33.1 | 19.36 | 19.36 | opened | 46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.536 | 17.526 | 3.25 | 10 | 14.276 | 0 | 33.1 | 18.824 | 18.824 | opened
| Nom. capacity MV, MVA | 31.5 | 11.46 | 1.7 |  | 9.76 | 0 | 33.1 | 23.34 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.528 | 11.988 | 1.7 | 0 | 10.288 | 0 | 33.1 | 22.812
| Nom. capacity LV, MVA | 31.5 | 5.53 | 1.55 | 120 | 3.98 | 0 | 33.1 | 29.12 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.008 | 5.538 | 1.55 | 120 | 3.988 | 0 | 33.1 | 29.112
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 16.47 | 11 | 120 | 5.47 | 0 | 16.8 | 11.33 | 11.33 | opened | 47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 0.704 | 17.174 | 11 | 120 | 6.174 | 0 | 16.8 | 10.626 | 10.626 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 9.76 | 7 |  | 2.76 | 0 | 16.8 | 14.04 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.646 | 10.406 | 7 | 0 | 3.406 | 0 | 16.8 | 13.394
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.71 | 4 | 120 | 2.71 | 0 | 16.8 | 14.09 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.058 | 6.768 | 4 | 120 | 2.768 | 0 | 16.8 | 14.032
48 | SS 110/10 Solovyinaya | 2 х 25,0 | 17.32 | 0 | 0 | 17.32 | 0 | 26.25 | 8.93 | 8.93 | opened | 48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 17.32 | 0 | 0 | 17.32 | 0 | 26.25 | 8.93 | 8.93 | opened
49 | SS 110/10 STK | 2 х 10,0 | 2.34 | 0 | 0 | 2.34 | 0 | 10.5 | 8.16 | 8.16 | opened | 49 | SS 110/10 STK | 2 х 10,0 |  | 2.34 | 0 | 0 | 2.34 | 0 | 10.5 | 8.16 | 8.16 | opened
50 | SS 110/10 Studenok | 2 х 6,3 | 2.89 | 0.7 | 120 | 2.19 | 0 | 6.62 | 4.43 | 4.43 | opened | 50 | SS 110/10 Studenok | 2 х 6,3 | 0.053 | 2.943 | 0.7 | 120 | 2.243 | 0 | 6.62 | 4.377 | 4.377 | opened
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 12.77 | 29 | 120 | -16.23 | 0 | 26.25 | 42.48 | 31.45 | opened | 51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.116 | 13.886 | 29 | 120 | -15.114 | 0 | 26.25 | 41.364 | 30.84 | opened
| Nom. capacity MV, MVA | 25 | 6.07 | 17.1 |  | -11.03 | 0 | 26.25 | 37.28 |  |  |  | Nom. capacity MV, MVA | 25 | 0.506 | 6.576 | 17.1 | 0 | -10.524 | 0 | 26.25 | 36.774
| Nom. capacity LV, MVA | 25 | 6.7 | 11.9 |  | -5.2 | 0 | 26.25 | 31.45 |  |  |  | Nom. capacity LV, MVA | 25 | 0.61 | 7.31 | 11.9 | 0 | -4.59 | 0 | 26.25 | 30.84
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 12.53 | 0 | 0 | 12.53 | 0 | 26.25 | 13.72 | 13.72 | opened | 52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.367 | 18.897 | 0 | 0 | 18.897 | 0 | 26.25 | 7.353 | 7.353 | opened
| Nom. capacity MV, MVA | 25 | 4.18 |  |  | 4.18 | 0 | 26.25 | 22.07 |  |  |  | Nom. capacity MV, MVA | 25 | 0.917 | 5.097 | 0 | 0 | 5.097 | 0 | 26.25 | 21.153
| Nom. capacity LV, MVA | 25 | 8.35 | 0 | 0 | 8.35 | 0 | 26.25 | 17.9 |  |  |  | Nom. capacity LV, MVA | 25 | 5.45 | 13.8 | 0 | 0 | 13.8 | 0 | 26.25 | 12.45
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 3.9 | 3.44 | 120 | 0.46 | 0 | 10.5 | 10.04 | 9.04 | opened | 53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.019 | 3.919 | 3.44 | 120 | 0.479 | 0 | 10.5 | 10.021 | 9.03 | opened
| Nom. capacity MV, MVA | 10 | 1 | 2 |  | -1 | 0 | 10.5 | 11.5 |  |  |  | Nom. capacity MV, MVA | 10 | 0.009 | 1.009 | 2 | 0 | -0.991 | 0 | 10.5 | 11.491
| Nom. capacity LV, MVA | 10 | 2.9 | 1.44 |  | 1.46 | 0 | 10.5 | 9.04 |  |  |  | Nom. capacity LV, MVA | 10 | 0.01 | 2.91 | 1.44 | 0 | 1.47 | 0 | 10.5 | 9.03
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 3.13 | 9.59 | 120 | -6.46 | 0 | 6.62 | 13.08 | 6.5 | opened | 54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.379 | 3.509 | 9.59 | 120 | -6.081 | 0 | 6.62 | 12.701 | 6.419 | opened
| Nom. capacity MV, MVA | 6,3 + 16,0 | 2.51 | 9.09 |  | -6.58 | 0 | 6.62 | 13.2 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.298 | 2.808 | 9.09 | 0 | -6.282 | 0 | 6.62 | 12.902
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.62 | 0.5 | 120 | 0.12 | 0 | 6.62 | 6.5 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.081 | 0.701 | 0.5 | 120 | 0.201 | 0 | 6.62 | 6.419
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.67 | 0.5 | 120 | 0.17 | 0 | 10.5 | 10.33 | 10 | opened | 55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.01 | 0.68 | 0.5 | 120 | 0.18 | 0 | 10.5 | 10.32 | 10 | opened
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.5 |  |  | 0.5 | 0 | 10.5 | 10 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0 | 0.5 | 0 | 0 | 0.5 | 0 | 10.5 | 10
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.17 | 0.5 | 120 | -0.33 | 0 | 10.5 | 10.83 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.01 | 0.18 | 0.5 | 120 | -0.32 | 0 | 10.5 | 10.82
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 5.99 | 17.4 | 120 | -11.41 | 0 | 16.8 | 28.21 | 17.12 | opened | 56 | SS 110/35/10 Fatezh | 2 х 16,0 | 0.723 | 6.713 | 17.4 | 120 | -10.687 | 0 | 16.8 | 27.487 | 16.991 | opened
| Nom. capacity MV, MVA | 16 | 1.71 | 12.8 |  | -11.09 | 0 | 16.8 | 27.89 |  |  |  | Nom. capacity MV, MVA | 16 | 0.594 | 2.304 | 12.8 | 0 | -10.496 | 0 | 16.8 | 27.296
| Nom. capacity LV, MVA | 16 | 4.28 | 4.6 | 120 | -0.32 | 0 | 16.8 | 17.12 |  |  |  | Nom. capacity LV, MVA | 16 | 0.129 | 4.409 | 4.6 | 120 | -0.191 | 0 | 16.8 | 16.991
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 4.025 | 12.34 | 120 | -8.315 | 0 | 26.25 | 34.565 | 24.905 | opened | 57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.108 | 4.133 | 12.34 | 120 | -8.207 | 0 | 26.25 | 34.457 | 24.903 | opened
| Nom. capacity MV, MVA | 25 | 2.45 | 12.12 |  | -9.67 | 0 | 26.25 | 35.92 |  |  |  | Nom. capacity MV, MVA | 25 | 0.106 | 2.556 | 12.12 | 0 | -9.564 | 0 | 26.25 | 35.814
| Nom. capacity LV, MVA | 25 | 1.565 | 0.22 | 10 | 1.345 | 0 | 26.25 | 24.905 |  |  |  | Nom. capacity LV, MVA | 25 | 0.002 | 1.567 | 0.22 | 10 | 1.347 | 0 | 26.25 | 24.903
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 2.61 | 6.3 | 80 | -3.69 | 0 | 7.88 | 11.57 | 8.3 | opened | 58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.134 | 2.744 | 6.3 | 80 | -3.556 | 0 | 7.88 | 11.436 | 8.184 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.63 | 3.9 |  | -3.27 | 0 | 7.88 | 11.15 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.018 | 0.648 | 3.9 | 0 | -3.252 | 0 | 7.88 | 11.132
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.98 | 2.4 | 80 | -0.42 | 0 | 7.88 | 8.3 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.116 | 2.096 | 2.4 | 80 | -0.304 | 0 | 7.88 | 8.184
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 6.09 | 9.38 | 10 | -3.29 | 0 | 16.8 | 20.09 | 15.72 | opened | 59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.282 | 6.372 | 9.38 | 10 | -3.008 | 0 | 16.8 | 19.808 | 15.603 | opened
| Nom. capacity MV, MVA | 16 | 4.72 | 9.09 |  | -4.37 | 0 | 16.8 | 21.17 |  |  |  | Nom. capacity MV, MVA | 16 | 0.165 | 4.885 | 9.09 | 0 | -4.205 | 0 | 16.8 | 21.005
| Nom. capacity LV, MVA | 16 | 1.37 | 0.29 | 120 | 1.08 | 0 | 16.8 | 15.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.117 | 1.487 | 0.29 | 120 | 1.197 | 0 | 16.8 | 15.603
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 3.13 | 8.25 | 120 | -5.12 | 0 | 6.62 | 11.74 | 6.67 | opened | 60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.064 | 3.194 | 8.25 | 120 | -5.056 | 0 | 6.62 | 11.676 | 6.665 | opened
| Nom. capacity MV, MVA | 6.3 | 1.93 | 7 |  | -5.07 | 0 | 6.62 | 11.69 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.059 | 1.989 | 7 | 0 | -5.011 | 0 | 6.62 | 11.631
| Nom. capacity LV, MVA | 6.3 | 1.2 | 1.25 | 129 | -0.05 | 0 | 6.62 | 6.67 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.005 | 1.205 | 1.25 | 129 | -0.045 | 0 | 6.62 | 6.665
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 3.75 | 13.73 | 120 | -9.98 | 0 | 10.5 | 20.48 | 12.58 | opened | 61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.268 | 4.018 | 13.73 | 120 | -9.712 | 0 | 10.5 | 20.212 | 12.517 | opened
| Nom. capacity MV, MVA | 10 | 3.3 | 11.2 |  | -7.9 | 0 | 10.5 | 18.4 |  |  |  | Nom. capacity MV, MVA | 10 | 0.205 | 3.505 | 11.2 | 0 | -7.695 | 0 | 10.5 | 18.195
| Nom. capacity LV, MVA | 10 | 0.45 | 2.53 | 120 | -2.08 | 0 | 10.5 | 12.58 |  |  |  | Nom. capacity LV, MVA | 10 | 0.063 | 0.513 | 2.53 | 120 | -2.017 | 0 | 10.5 | 12.517
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 9.15 | 12.9 | 120 | -3.75 | 0 | 26.5 | 30.25 | 21.27 | opened | 62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.496 | 9.646 | 12.9 | 120 | -3.254 | 0 | 26.5 | 29.754 | 21.086 | opened
| Nom. capacity MV, MVA | 25 | 3.14 | 12.12 |  | -8.98 | 0 | 26.5 | 35.48 |  |  |  | Nom. capacity MV, MVA | 25 | 0.312 | 3.452 | 12.12 | 0 | -8.668 | 0 | 26.5 | 35.168
| Nom. capacity LV, MVA | 25 | 6.01 | 0.78 | 120 | 5.23 | 0 | 26.5 | 21.27 |  |  |  | Nom. capacity LV, MVA | 25 | 0.184 | 6.194 | 0.78 | 120 | 5.414 | 0 | 26.5 | 21.086
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.45 | 6.31 | 10 | -3.86 | 0 | 7.88 | 11.74 | 7.09 | opened | 63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.1917 | 2.6417 | 6.31 | 10 | -3.6683 | 0 | 7.88 | 11.5483 | 7.052 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.41 | 6.06 |  | -4.65 | 0 | 7.88 | 12.53 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.1537 | 1.5637 | 6.06 | 0 | -4.4963 | 0 | 7.88 | 12.3763
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.04 | 0.25 | 10 | 0.79 | 0 | 7.88 | 7.09 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.038 | 1.078 | 0.25 | 10 | 0.828 | 0 | 7.88 | 7.052
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened | 64 | SS 35/10 Amosovka | 2 х 2,5 | 0.008 | 0.398 | 0.2 | 120 | 0.198 | 0 | 2.63 | 2.432 | 2.432 | opened
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.2 | 0.37 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened | 65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 |  | 0.2 | 0.37 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 |  | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.06 | 1.43 | 120 | -1.37 | 0 | 1.68 | 3.05 | 3.05 | opened | 67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.01 | 0.07 | 1.43 | 120 | -1.36 | 0 | 1.68 | 3.04 | 3.04 | opened
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 1.51 | 6.1 | 0 | -4.59 | 0 | 4.2 | 8.79 | 8.79 | opened | 68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.246 | 1.756 | 6.1 | 0 | -4.344 | 0 | 4.2 | 8.544 | 8.544 | opened
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.15 | 0.15 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 | opened | 69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.016 | 0.166 | 0.15 | 120 | 0.016 | 0 | 1.05 | 1.034 | 1.034 | opened
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.96 | 0.29 | 120 | 0.67 | 0 | 2.63 | 1.96 | 1.96 | opened | 70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.076 | 1.036 | 0.29 | 120 | 0.746 | 0 | 2.63 | 1.884 | 1.884 | opened
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.35 | 0.41 | 120 | -0.06 | 0 | 2.63 | 2.69 | 2.69 | opened | 71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.029 | 0.379 | 0.41 | 120 | -0.031 | 0 | 2.63 | 2.661 | 2.661 | opened
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.67 | 0.4 | 120 | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened | 72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.532 | 1.202 | 0.4 | 120 | 0.802 | 0 | 4.2 | 3.398 | 3.398 | opened
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.36 | 0.22 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.453 | 0.813 | 0.22 | 120 | 0.593 | 0 | 1.68 | 1.087 | 1.087 | opened
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.5 | 0.46 | 120 | 0.04 | 0 | 2.63 | 2.59 | 2.59 | opened | 74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.019 | 0.519 | 0.46 | 120 | 0.059 | 0 | 2.63 | 2.571 | 2.571 | opened
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.42 | 0 | 0 | 0.42 | 0 | 4.2 | 3.78 | 3.78 | opened | 75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.021 | 0.441 | 0 | 0 | 0.441 | 0 | 4.2 | 3.759 | 3.759 | opened
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 2.52 | 0.46 | 120 | 2.06 | 0 | 6.62 | 4.56 | 4.56 | opened | 76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.184 | 2.704 | 0.46 | 120 | 2.244 | 0 | 6.62 | 4.376 | 4.376 | opened
77 | SS 35/10 Vygornoe | 2 х 2,5 | 1.28 | 0.51 | 120 | 0.77 | 0 | 2.63 | 1.86 | 1.86 | opened | 77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.106 | 1.386 | 0.51 | 120 | 0.876 | 0 | 2.63 | 1.754 | 1.754 | opened
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.7 | 0.17 | 120 | 0.53 | 0 | 1.68 | 1.15 | 1.15 | opened | 78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.009 | 0.709 | 0.17 | 120 | 0.539 | 0 | 1.68 | 1.141 | 1.141 | opened
79 | SS 35/10 Gorodok | 2 х 4,0 | 1.62 | 0.7 | 45 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened | 79 | SS 35/10 Gorodok | 2 х 4,0 |  | 1.62 | 0.7 | 45 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened
80 | SS 35/10 Guevo | 2 х 2,5 | 1.14 | 1.69 | 20 | -0.55 | 0 | 2.63 | 3.18 | 3.18 | opened | 80 | SS 35/10 Guevo | 2 х 2,5 | 0.04 | 1.18 | 1.69 | 20 | -0.51 | 0 | 2.63 | 3.14 | 3.14 | opened
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.12 | 0.38 | 120 | -0.26 | 0 | 1.68 | 1.94 | 1.94 | opened | 81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.162 | 0.38 | 120 | -0.218 | 0 | 1.68 | 1.898 | 1.898 | opened
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 2.38 | 3.5 | 0 | -1.12 | 0 | 2.63 | 3.75 | 3.75 | opened | 82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 2.495 | 3.5 | 0 | -1.005 | 0 | 2.63 | 3.635 | 3.635 | opened
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.28 | 0.26 | 120 | 0.02 | 0 | 2.63 | 2.61 | 2.61 | opened | 83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.285 | 0.26 | 120 | 0.025 | 0 | 2.63 | 2.605 | 2.605 | opened
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 8.14 | 0 | 0 | 8.14 | 0 | 10.5 | 2.36 | 2.36 | opened | 84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 8.15 | 0 | 0 | 8.15 | 0 | 10.5 | 2.35 | 2.35 | opened
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 1.11 | 1.67 | 0 | -0.56 | 0 | 4.2 | 4.76 | 4.76 | opened | 85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 |  | 1.11 | 1.67 | 0 | -0.56 | 0 | 4.2 | 4.76 | 4.76 | opened
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.75 | 0.93 | 45 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened | 86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.085 | 0.835 | 0.93 | 45 | -0.095 | 0 | 1.68 | 1.775 | 1.775 | opened
87 | SS 35/10 Ivanino | 2 х 6,3 | 4.31 | 2.69 | 80 | 1.62 | 0 | 6.62 | 5 | 5 | opened | 87 | SS 35/10 Ivanino | 2 х 6,3 | 0.031 | 4.341 | 2.69 | 80 | 1.651 | 0 | 6.62 | 4.969 | 4.969 | opened
88 | ПС 35/10 Kalinovka | 1,8 + 2,5 | 0.64 | 0.5 | 120 | 0.14 | 0 | 1.89 | 1.75 | 1.75 | opened | 88 | ПС 35/10 Kalinovka | 1,8 + 2,5 |  | 0.64 | 0.5 | 120 | 0.14 | 0 | 1.89 | 1.75 | 1.75 | opened
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | opened | 89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.235 | 0.52 | 120 | -0.285 | 0 | 1.68 | 1.965 | 1.965 | opened
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened | 90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 17.109 | 6.25 | 20 | 10.859 | 0 | 10.5 | -0.359 | -0.359 | closed
91 | SS 35/10 Fodder plant | 4,0+6,3 | 0.71 | 0 | 0 | 0.71 | 0 | 4.2 | 3.49 | 3.49 | opened | 91 | SS 35/10 Fodder plant | 4,0+6,3 |  | 0.71 | 0 | 0 | 0.71 | 0 | 4.2 | 3.49 | 3.49 | opened
92 | SS 35/10 Fodder plant | 2 х 6,3 | 2.65 | 0.21 | 120 | 2.44 | 0 | 6.62 | 4.18 | 4.18 | opened | 92 | SS 35/10 Fodder plant | 2 х 6,3 | 0.069 | 2.719 | 0.21 | 120 | 2.509 | 0 | 6.62 | 4.111 | 4.111 | opened
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 1.83 | 1.14 | 80 | 0.69 | 0 | 3.36 | 2.67 | 2.67 | opened | 93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 |  | 1.83 | 1.14 | 80 | 0.69 | 0 | 3.36 | 2.67 | 2.67 | opened
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 2.51 | 1.56 | 80 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened | 94 | SS 35/10 Korenevo | 4,0 + 6,3 | 0.403 | 2.913 | 1.56 | 80 | 1.353 | 0 | 4.2 | 2.847 | 2.847 | opened
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.42 | 0.24 | 120 | 0.18 | 0 | 2.63 | 2.45 | 2.45 | opened | 95 | SS 35/10 Kremyanoe | 2,5 + 4,0 |  | 0.42 | 0.24 | 120 | 0.18 | 0 | 2.63 | 2.45 | 2.45 | opened
96 | SS 35/10 Krupets | 1,8 + 2,5 | 1.19 | 0.42 | 120 | 0.77 | 0 | 1.89 | 1.12 | 1.12 | opened | 96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.354 | 0.42 | 120 | 0.934 | 0 | 1.89 | 0.956 | 0.956 | opened
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.84 | 0.6 | 120 | 0.24 | 0 | 2.63 | 2.39 | 2.39 | opened | 97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.003 | 0.843 | 0.6 | 120 | 0.243 | 0 | 2.63 | 2.387 | 2.387 | opened
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened | 98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.003 | 0.133 | 0.17 | 120 | -0.037 | 0 | 2.63 | 2.667 | 2.667 | opened
99 | SS 35/10 Kurchatov | 2 х 10,0 | 6.62 | 4.5 | 80 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened | 99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 6.625 | 4.5 | 80 | 2.125 | 0 | 10.5 | 8.375 | 8.375 | opened
100 | SS 35/10 Kutok | 2 х 2,5 | 0.08 | 0.05 | 120 | 0.03 | 0 | 2.63 | 2.6 | 2.6 | opened | 100 | SS 35/10 Kutok | 2 х 2,5 | 0.005 | 0.085 | 0.05 | 120 | 0.035 | 0 | 2.63 | 2.595 | 2.595 | opened
101 | SS 35/10 Linets | 2 х 2,5 | 0.34 | 0.25 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened | 101 | SS 35/10 Linets | 2 х 2,5 | 0.016 | 0.356 | 0.25 | 120 | 0.106 | 0 | 2.63 | 2.524 | 2.524 | opened
102 | SS 35/10 Luch | 2 х 6,3 | 2.39 | 0.23 | 120 | 2.16 | 0 | 6.62 | 4.46 | 4.46 | opened | 102 | SS 35/10 Luch | 2 х 6,3 | 0.303 | 2.693 | 0.23 | 120 | 2.463 | 0 | 6.62 | 4.157 | 4.157 | opened
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.57 | 1.59 | 80 | -1.02 | 0 | 4.2 | 5.22 | 5.22 | opened | 103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.029 | 0.599 | 1.59 | 80 | -0.991 | 0 | 4.2 | 5.191 | 5.191 | opened
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.45 | 0.08 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened | 104 | SS 35/10 Matveevka | 2 х 2,5 | 0.02 | 0.47 | 0.08 | 120 | 0.39 | 0 | 2.63 | 2.24 | 2.24 | opened
105 | SS 35/10 Mayak | 2 х 2,5 | 0.26 | 0.3 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened | 105 | SS 35/10 Mayak | 2 х 2,5 | 0.006 | 0.266 | 0.3 | 120 | -0.034 | 0 | 2.63 | 2.664 | 2.664 | opened
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 1.6 | 1.7 | 80 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened | 106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.14 | 1.74 | 1.7 | 80 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.71 | 0.3 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 107 | SS 35/10 Murynovka | 2 х 4,0 | 0.178 | 0.888 | 0.3 | 120 | 0.588 | 0 | 4.2 | 3.612 | 3.612 | opened
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.36 | 0.63 | 120 | -0.27 | 0 | 2.63 | 2.9 | 2.9 | opened | 108 | SS 35/10 N. Borki | 2 х 2,5 | 0.011 | 0.371 | 0.63 | 120 | -0.259 | 0 | 2.63 | 2.889 | 2.889 | opened
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.32 | 0.03 | 80 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 109 | SS 35/10 Nikolskaya | 1,6 + 1,8 |  | 0.32 | 0.03 | 80 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
110 | SS 35/10 Novaya | 2 х 2,5 | 1.18 | 0.4 | 120 | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 110 | SS 35/10 Novaya | 2 х 2,5 | 0.246 | 1.426 | 0.4 | 120 | 1.026 | 0 | 2.63 | 1.604 | 1.604 | opened
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.44 | 0.19 | 120 | 0.25 | 0 | 2.63 | 2.38 | 2.38 | opened | 111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.036 | 0.476 | 0.19 | 120 | 0.286 | 0 | 2.63 | 2.344 | 2.344 | opened
112 | SS 35/10 Orlovka | 2 х 2,5 | 0.23 | 0.52 | 120 | -0.29 | 0 | 2.63 | 2.92 | 2.92 | opened | 112 | SS 35/10 Orlovka | 2 х 2,5 | 0.015 | 0.245 | 0.52 | 120 | -0.275 | 0 | 2.63 | 2.905 | 2.905 | opened
113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.25 | 0.2 | 120 | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened | 113 | SS 35/10 Osotskoe | 2 х 2,5 |  | 0.25 | 0.2 | 120 | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.13 | 0.74 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | opened | 114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.172 | 1.302 | 0.74 | 120 | 0.562 | 0 | 4.2 | 3.638 | 3.638 | opened
115 | SS 35/10 Panino | 2 х 2,5 | 0.27 | 0.11 | 80 | 0.16 | 0 | 2.63 | 2.47 | 2.47 | opened | 115 | SS 35/10 Panino | 2 х 2,5 |  | 0.27 | 0.11 | 80 | 0.16 | 0 | 2.63 | 2.47 | 2.47 | opened
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.61 | 0.52 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened | 116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.026 | 0.636 | 0.52 | 120 | 0.116 | 0 | 2.63 | 2.514 | 2.514 | opened
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.18 | 0.3 | 120 | 0.88 | 0 | 2.63 | 1.75 | 1.75 | opened | 117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.711 | 1.891 | 0.3 | 120 | 1.591 | 0 | 2.63 | 1.039 | 1.039 | opened
118 | SS 35/10 Platava | 2 х 2,5 | 0.86 | 0.26 | 120 | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 118 | SS 35/10 Platava | 2 х 2,5 | 0.012 | 0.872 | 0.26 | 120 | 0.612 | 0 | 2.63 | 2.018 | 2.018 | opened
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.21 | 0.46 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | opened | 119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.257 | 0.46 | 120 | -0.203 | 0 | 1.68 | 1.883 | 1.883 | opened
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.53 | 1.16 | 120 | -0.63 | 0 | 4.2 | 4.83 | 4.83 | opened | 120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.005 | 0.535 | 1.16 | 120 | -0.625 | 0 | 4.2 | 4.825 | 4.825 | opened
121 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened | 121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.45 | 0.3 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened | 122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.274 | 0.724 | 0.3 | 80 | 0.424 | 0 | 2.63 | 2.206 | 2.206 | opened
123 | SS 35/10 Pselets | 2 х 1,6 | 0.11 | 0.24 | 120 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened | 123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.11 | 0.24 | 120 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.59 | 0.43 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.014 | 0.604 | 0.43 | 120 | 0.174 | 0 | 1.68 | 1.506 | 1.506 | opened
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.6 | 0.32 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.024 | 0.624 | 0.32 | 120 | 0.304 | 0 | 2.625 | 2.321 | 2.321 | opened
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.54 | 0.44 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.337 | 0.877 | 0.44 | 120 | 0.437 | 0 | 2.625 | 2.188 | 2.188 | opened
127 | SS 35/10 Razvetye | 2 х 4,0 | 1.35 | 1.03 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | opened | 127 | SS 35/10 Razvetye | 2 х 4,0 | 0.388 | 1.738 | 1.03 | 120 | 0.708 | 0 | 4.2 | 3.492 | 3.492 | opened
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | opened | 128 | SS 35/10 V. Reutets | 2 х 4,0 |  | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | opened
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.061 | 0.361 | 0.29 | 120 | 0.071 | 0 | 1.68 | 1.609 | 1.609 | opened
130 | SS 35/10 Rubilnik | 2 х 2,5 | 1.4 | 1.18 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.045 | 1.445 | 1.18 | 80 | 0.265 | 0 | 2.625 | 2.36 | 2.36 | opened
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.28 | 0.08 | 20 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.007 | 0.287 | 0.08 | 20 | 0.207 | 0 | 1.68 | 1.473 | 1.473 | opened
132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.73 | 0.6 | 20 | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 132 | SS 35/10 Sapogovo | 2 х 2,5 | 0.056 | 1.786 | 0.6 | 20 | 1.186 | 0 | 2.63 | 1.444 | 1.444 | opened
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 3.65 | 2.25 | 80 | 1.4 | 0 | 6.615 | 5.215 | 5.215 | opened | 133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.124 | 3.774 | 2.25 | 80 | 1.524 | 0 | 6.615 | 5.091 | 5.091 | opened
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.75 | 1.4 | 45 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.027 | 2.777 | 1.4 | 45 | 1.377 | 0 | 4.2 | 2.823 | 2.823 | opened
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.29 | 0 | - | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened | 135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.042 | 0.332 | 0 | - | 0.332 | 0 | 2.625 | 2.293 | 2.293 | opened
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.35 | 0.6 | 120 | -0.25 | 0 | 2.63 | 2.88 | 2.88 | opened | 136 | SS 35/10 Seed plant | 2 х 2,5 | 0.04 | 0.39 | 0.6 | 120 | -0.21 | 0 | 2.63 | 2.84 | 2.84 | opened
137 | SS 35/10 Snagost | 2 х 4,0 | 0.88 | 0.05 | 10 | 0.83 | 0 | 4.2 | 3.37 | 3.37 | opened | 137 | SS 35/10 Snagost | 2 х 4,0 | 0.03 | 0.91 | 0.05 | 10 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
138 | SS 35/10 SOM | 1,6 + 4,0 | 1.15 | 0.08 | 10 | 1.07 | 0 | 1.68 | 0.61 | 0.61 | opened | 138 | SS 35/10 SOM | 1,6 + 4,0 | 0.056 | 1.206 | 0.08 | 10 | 1.126 | 0 | 1.68 | 0.554 | 0.554 | opened
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.49 | 0.69 | 120 | -0.2 | 0 | 3.36 | 3.56 | 3.56 | opened | 139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.036 | 0.526 | 0.69 | 120 | -0.164 | 0 | 3.36 | 3.524 | 3.524 | opened
140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.84 | 0.58 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened | 140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.027 | 0.867 | 0.58 | 80 | 0.287 | 0 | 2.625 | 2.338 | 2.338 | opened
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.41 | 0.2 | 80 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 141 | SS 35/10 Starkovo | 2 х 1,6 |  | 0.41 | 0.2 | 80 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
142 | CC 35/10 Starshee | 2 х 1,6 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened | 142 | CC 35/10 Starshee | 2 х 1,6 | 0.005 | 0.245 | 0.2 | 120 | 0.045 | 0 | 1.68 | 1.635 | 1.635 | opened
143 | SS 35/10 Teplitsy | 2 х 4,0 | 2.2 | 1.08 | 45 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | opened | 143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.052 | 2.252 | 1.08 | 45 | 1.172 | 0 | 4.2 | 3.028 | 3.028 | opened
144 | SS 35/10 Turovka | 2 х 2,5 | 0.5 | 0.6 | 120 | -0.1 | 0 | 2.63 | 2.73 | 2.73 | opened | 144 | SS 35/10 Turovka | 2 х 2,5 | 0.053 | 0.553 | 0.6 | 120 | -0.047 | 0 | 2.63 | 2.677 | 2.677 | opened
145 | SS 35/10 Uspenka | 2 х 2,5 | 1.28 | 1 | 80 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened | 145 | SS 35/10 Uspenka | 2 х 2,5 | 0.005 | 1.285 | 1 | 80 | 0.285 | 0 | 2.63 | 2.345 | 2.345 | opened
146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 27.41 | 5 | 10 | 22.41 | 0 | 26.25 | 3.84 | 3.84 | opened | 146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0.005 | 27.415 | 5 | 10 | 22.415 | 0 | 26.25 | 3.835 | 3.835 | opened
147 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.3 | 0.5 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | opened | 147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.3 | 0.5 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | opened
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.32 | 0.21 | 80 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.031 | 0.351 | 0.21 | 80 | 0.141 | 0 | 2.625 | 2.484 | 2.484 | opened
149 | SS 35/10 Shipy | 2 х 2,5 | 0.18 | 0.3 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | opened | 149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.192 | 0.3 | 120 | -0.108 | 0 | 2.625 | 2.733 | 2.733 | opened
150 | SS 35/10 Elevator | 4,0 + 6,3 | 1.7 | 0.6 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened | 150 | SS 35/10 Elevator | 4,0 + 6,3 |  | 1.7 | 0.6 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened
151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.46 | 4.7 | 80 | 3.76 | 0 | 10.5 | 6.74 | 6.74 | opened | 151 | SS 35/10 Yugo-Zapadnaya | 1 х 10,0 | 2.35 | 10.81 | 4.7 | 80 | 6.11 | 0 | 10.5 | 4.39 | 4.39 | opened
152 | SS 35/10 Reinforced concrete product plant | 2 х 2,5 | 1.5 | 3.9 | 120 | -2.4 | 0 | 2.625 | 5.025 | 5.025 | opened | 152 | SS 35/10 Reinforced concrete product plant | 2 х 2,5 |  | 1.5 | 3.9 | 120 | -2.4 | 0 | 2.625 | 5.025 | 5.025 | opened
| TOTAL: | 3193.5 | 743.228 | 773.71 | [5 empty] | 1183.087 |  |  | TOTAL: | 3188.5 | 61.891 | 805.119 | 773.71 | [5 empty] | 1128.204
| deficit | [8 empty] | 0 |  |  | deficit | [9 empty] | -4.863
| proficit | [8 empty] | 1183.087 |  |  | proficit | [9 empty] | 1133.067

## Брянск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kv Lopandino | 6.3 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 1 | SS 110/10 kv Lopandino | 6.3 | 0 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
2 | SS 110/35/10 kv Nerussa | 16 | 2.577 | 2.6 | 24 hours | -0.023 | 0 | 16.8 | 16.823 | 15.3 | opened | 2 | SS 110/35/10 kv Nerussa | 16 | 0 | 2.577 | 2.6 | 24 hours | -0.023 | 0 | 16.8 | 16.823 | 15.3 | opened
| Nom. capacity MV, MVA | 16 | 1.5 | 1.5 | 24 hours | 0 | 0 | 16.8 | 15.3 |  |  |  | Nom. capacity MV, MVA | 16 |  | 1.5 | 1.5 | 24 hours | 0 | 0 | 16.8 | 15.3
| Nom. capacity LV, MVA | 16 | 1.077 | 1.1 | 24 hours | -0.023 | 0 | 16.8 | 16.823 |  |  |  | Nom. capacity LV, MVA | 16 |  | 1.077 | 1.1 | 24 hours | -0.023 | 0 | 16.8 | 16.823
3 | SS 110/6 kv Svenskaya | 6.3 | 1.5 | 1.5 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 3 | SS 110/6 kv Svenskaya | 6.3 | 0.047 | 1.547 | 1.5 | 24 hours | 0.047 | 0 | 6.615 | 6.568 | 6.568 | opened
4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.016 | 0.377 | 0.361 | 24 hours | 0.016 | 0 | 6.615 | 6.599 | 6.599 | opened
5 | SS 110/6 kv Energoremont | 10 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 5 | SS 110/6 kv Energoremont | 10 | 0 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.018 | 0.689 | 0.671 | 24 hours | 0.018 | 0 | 10.5 | 10.482 | 10.482 | opened
2 | SS 110/10 kv Glybochka | 2.5 | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 2 | SS 110/10 kv Glybochka | 2.5 | 0.016 | 1.241 | 1.225 | 24 hours | 0.016 | 0 | 2.625 | 2.609 | 2.609 | opened
3 | SS 110/10 kv Desyatukha | 6.3 | 1.187 | 1.187 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 3 | SS 110/10 kv Desyatukha | 6.3 | 0.021 | 1.208 | 1.187 | 24 hours | 0.021 | 0 | 6.615 | 6.594 | 6.594 | opened
4 | SS 110/35/10 kv Ivaytenki | 6.3 | 1.588 | 1.6 | 24 hours | -0.012 | 0 | 6.615 | 6.627 | 5.698 | opened | 4 | SS 110/35/10 kv Ivaytenki | 6.3 | 0.03 | 1.609 | 1.6 | 24 hours | 0.009 | 0 | 6.615 | 6.606 | 5.698 | opened
| Nom. capacity MV, MVA | 6.3 | 0.917 | 0.9 | 24 hours | 0.017 | 0 | 6.615 | 5.698 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.917 | 0.9 | 24 hours | 0.017 | 0 | 6.615 | 5.698
| Nom. capacity LV, MVA | 6.3 | 0.671 | 0.7 | 24 hours | -0.029 | 0 | 6.615 | 6.644 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.03 | 0.701 | 0.7 | 24 hours | 0.001 | 0 | 6.615 | 6.614
5 | SS 110/35/10 kv Lugovaya | 16 | 4.718 | 4.7 | 24 hours | 0.018 | 0 | 16.8 | 16.782 | 12.971 | opened | 5 | SS 110/35/10 kv Lugovaya | 16 | 0.06 | 4.761 | 4.7 | 24 hours | 0.061 | 0 | 16.8 | 16.739 | 12.971 | opened
| Nom. capacity MV, MVA | 16 | 3.829 | 3.8 | 24 hours | 0.029 | 0 | 16.8 | 12.971 |  |  |  | Nom. capacity MV, MVA | 16 |  | 3.829 | 3.8 | 24 hours | 0.029 | 0 | 16.8 | 12.971
| Nom. capacity LV, MVA | 16 | 0.889 | 0.9 | 24 hours | -0.011 | 0 | 16.8 | 16.811 |  |  |  | Nom. capacity LV, MVA | 16 | 0.06 | 0.949 | 0.9 | 24 hours | 0.049 | 0 | 16.8 | 16.751
6 | SS 110/35/10 kv Pluskovo | 6.3 | 2.115 | 2.1 | 24 hours | 0.015 | 0 | 6.615 | 6.6 | 5.47 | opened | 6 | SS 110/35/10 kv Pluskovo | 6.3 | 0.082 | 2.197 | 2.1 | 24 hours | 0.097 | 0 | 6.615 | 6.518 | 5.47 | opened
| Nom. capacity MV, MVA | 6.3 | 1.145 | 1.1 | 24 hours | 0.045 | 0 | 6.615 | 5.47 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1.145 | 1.1 | 24 hours | 0.045 | 0 | 6.615 | 5.47
| Nom. capacity LV, MVA | 6.3 | 0.97 | 1 | 24 hours | -0.03 | 0 | 6.615 | 6.645 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.082 | 1.052 | 1 | 24 hours | 0.052 | 0 | 6.615 | 6.563
7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.019 | 0.419 | 0.419 | 24 hours | 0.419 | 0 | 0.419 | 0 | 0 | opened
8 | SS 35/10 kv Altukhovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 8 | SS 35/10 kv Altukhovskaya | 1.6 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
9 | SS 35/10 kv Domashovo | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 9 | SS 35/10 kv Domashovo | 2.5 | 0.091 | 0.491 | 0.491 | 24 hours | 0.491 | 0 | 0.491 | 0 | 0 | opened
10 | SS 35/6 kv Dronovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 10 | SS 35/6 kv Dronovskaya | 2.5 | 0 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
11 | SS 35/10 kv Kokorevskaya | 4 | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened | 11 | SS 35/10 kv Kokorevskaya | 4 | 0.003 | 0.903 | 0.903 | 24 hours | 0.903 | 0 | 0.903 | 0 | 0 | opened
12 | SS 35/6 kv Malopolpinskaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 12 | SS 35/6 kv Malopolpinskaya | 4 | 0.049 | 0.449 | 0.449 | 24 hours | 0.449 | 0 | 0.449 | 0 | 0 | opened
13 | SS 35/10 kv Morachevskaya | 1.6 | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 | opened | 13 | SS 35/10 kv Morachevskaya | 1.6 | 0 | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 | opened
14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.002 | 0.602 | 0.602 | 24 hours | 0.602 | 0 | 0.602 | 0 | 0 | opened
15 | SS 35/10 kv Svetovo | 2.5 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 | opened | 15 | SS 35/10 kv Svetovo | 2.5 | 0 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 | opened
16 | SS 35/10 kv Seshcha | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 16 | SS 35/10 kv Seshcha | 2.5 | 0 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
17 | SS 35/10 kv Sovkhoznaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 17 | SS 35/10 kv Sovkhoznaya | 4 | 0 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
18 | SS 35/10 kv Strachevskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 18 | SS 35/10 kv Strachevskaya | 2.5 | 0.025 | 0.425 | 0.425 | 24 hours | 0.425 | 0 | 0.425 | 0 | 0 | opened
19 | SS 35/10 kv Strashevichi | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 19 | SS 35/10 kv Strashevichi | 4 | 1.138 | 1.538 | 1.538 | 24 hours | 1.538 | 0 | 1.538 | 0 | 0 | opened
20 | SS 35/10 kv Usozhskaya | 2.5 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened | 20 | SS 35/10 kv Usozhskaya | 2.5 | 0.03 | 0.73 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0 | 0 | opened
21 | SS 35/10 kv Kharinovskaya | 1 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened | 21 | SS 35/10 kv Kharinovskaya | 1 | 0 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened
22 | SS 35/10 kv Kharitonovskaya | 4 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened | 22 | SS 35/10 kv Kharitonovskaya | 4 | 0.1 | 0.8 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0 | 0 | opened
23 | SS 35/10 kv Didovka | 2.5 | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened | 23 | SS 35/10 kv Didovka | 2.5 | 0.005 | 0.637 | 0.637 | 24 hours | 0.637 | 0 | 0.637 | 0 | 0 | opened
24 | SS 35/10 kv Molodkovo | 1 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 24 | SS 35/10 kv Molodkovo | 1 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.283 | 0.283 | 24 hours | 0.283 | 0 | 0.283 | 0 | 0 | opened | 25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.003 | 0.286 | 0.286 | 24 hours | 0.286 | 0 | 0.286 | 0 | 0 | opened
26 | SS 35/10 kv Radutinskaya | 1.6 | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened | 26 | SS 35/10 kv Radutinskaya | 1.6 | 0.022 | 0.561 | 0.561 | 24 hours | 0.561 | 0 | 0.561 | 0 | 0 | opened
27 | SS 35/6 kv Ushchepye | 1.6 | 0.825 | 0.825 | 24 hours | 0.825 | 0 | 0.825 | 0 | 0 | opened | 27 | SS 35/6 kv Ushchepye | 1.6 | 0.005 | 0.83 | 0.83 | 24 hours | 0.83 | 0 | 0.83 | 0 | 0 | opened
28 | SS 35/10 kv Ushchepye | 1.6 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened | 28 | SS 35/10 kv Ushchepye | 1.6 | 0 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened
29 | SS 35/10 kv Yakovskaya | 2.5 | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened | 29 | SS 35/10 kv Yakovskaya | 2.5 | 0.034 | 0.617 | 0.617 | 24 hours | 0.617 | 0 | 0.617 | 0 | 0 | opened
30 | SS 110/35/6 kv Aksinino | 40+40 | 16.83 | 0 | 0 | 16.83 | 0 | 42 | 25.17 | 25.17 | opened | 30 | SS 110/35/6 kv Aksinino | 40+40 | 0.005 | 16.8353 | 0 | 0 | 16.8353 | 0 | 42 | 25.1647 | 25.1647 | opened
| Nom. capacity MV, MVA | 40+40 | 14.45 | 0 | 0 | 14.45 | 0 | 42 | 27.55 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 14.45 | 0 | 0 | 14.45 | 0 | 42 | 27.55
| Nom. capacity LV, MVA | 40+40 | 2.38 | 0 | 0 | 2.38 | 0 | 42 | 39.62 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.005 | 2.385 | 0 | 0 | 2.385 | 0 | 42 | 39.615
31 | SS 110/10 kv Airport | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 31 | SS 110/10 kv Airport | 6,3+6,3 | 0.008 | 0.908 | 0 | 0 | 0.908 | 0 | 6.615 | 5.707 | 5.707 | opened
32 | SS 110/6 kv Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed | 32 | SS 110/6 kv Bezhitskaya | 25+40 | 3.182 | 37.752 | 0 | 0 | 37.752 | 0 | 26.25 | -11.502 | -11.502 | closed
33 | SS 110/6 kv Water intake | 6,3+6,3 | 1.9 | 0 | 0 | 1.9 | 0 | 6.615 | 4.715 | 4.715 | opened | 33 | SS 110/6 kv Water intake | 6,3+6,3 | 0.816 | 2.716 | 0 | 0 | 2.716 | 0 | 6.615 | 3.899 | 3.899 | opened
34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed | 34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 0.806 | 26.366 | 1.5 | 12 hours | 24.866 | 0 | 16.8 | -8.066 | -8.066 | closed
35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 3.7 | 0 | 0 | 3.7 | 0 | 4.2 | 0.5 | 0.5 |  | 35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 0.508 | 4.208 | 0 | 0 | 4.208 | 0 | 4.2 | -0.008 | -0.008 | opened
36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 39.51 | 0 | 0 | 39.51 | 0 | 42 | 2.49 | 2.49 | opened | 36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 3.226 | 42.736 | 0 | 0 | 42.736 | 0 | 42 | -0.736 | -0.736 | closed
| Nom. capacity MV, MVA | 40+63 | 20.72 | 0 | 0 | 20.72 | 0 | 42 | 21.28 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 20.72 | 0 | 0 | 20.72 | 0 | 42 | 21.28
| Nom. capacity LV, MVA | 40+63 | 18.79 | 0 | 0 | 18.79 | 0 | 42 | 23.21 |  |  |  | Nom. capacity LV, MVA | 40+63 | 3.226 | 22.016 | 0 | 0 | 22.016 | 0 | 42 | 19.984
37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened | 37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 0.05 | 9.41 | 0 | 0 | 9.41 | 0 | 16.8 | 7.39 | 7.39 | opened
| Nom. capacity MV, MVA | 16+16 | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33
| Nom. capacity LV, MVA | 16+16 | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.05 | 3.95 | 0 | 0 | 3.95 | 0 | 16.8 | 12.85
38 | SS 110/35/6 kv Dyatkovskaya | 25+25 | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -1.57 | -1.62 | closed | 38 | SS 110/35/6 kv Dyatkovskaya | 25+25 | 0 | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -1.57 | -1.62 | closed
| Nom. capacity MV, MVA | 25+25 | 8.85 | 8.9 | 12 hours | -0.05 | 0 | 26.25 | 17.4 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 8.85 | 8.9 | 12 hours | -0.05 | 0 | 26.25 | 17.4
| Nom. capacity LV, MVA | 25+25 | 27.87 | 0 | 0 | 27.87 | 0 | 26.25 | -1.62 |  |  |  | Nom. capacity LV, MVA | 25+25 |  | 27.87 | 0 | 0 | 27.87 | 0 | 26.25 | -1.62
39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | opened | 39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 0.133 | 15.802 | 5.2 | 6 hours | 10.602 | 0 | 16.8 | 6.198 | 6.198 | opened
| Nom. capacity MV, MVA | 16+25 | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8
| Nom. capacity LV, MVA | 16+25 | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.133 | 8.833 | 0 | 0 | 8.833 | 0 | 16.8 | 7.967
40 | SS 110/6 kv Zarechnaya | 10+10 | 5.92 | 0 | 0 | 5.92 | 0 | 10.5 | 4.58 | 4.58 | opened | 40 | SS 110/6 kv Zarechnaya | 10+10 | 1.183 | 7.103 | 0 | 0 | 7.103 | 0 | 10.5 | 3.397 | 3.397 | opened
41 | SS 110/35/6 kv Ivotskaya | 25+25 | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened | 41 | SS 110/35/6 kv Ivotskaya | 25+25 | 0 | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened
| Nom. capacity MV, MVA | 25+25 | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89
| Nom. capacity LV, MVA | 25+25 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kv Kamvolnaya | 16+25 | 17.09 | 0 | 0 | 17.09 | 0 | 16.8 | -0.29 | -0.29 | closed | 42 | SS 110/6 kv Kamvolnaya | 16+25 | 0.965 | 18.055 | 0 | 0 | 18.055 | 0 | 16.8 | -1.255 | -1.255 | closed
43 | SS 110/6 kv Karachevskaya | 16+25 | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened | 43 | SS 110/6 kv Karachevskaya | 16+25 | 0.197 | 11.097 | 0 | 0 | 11.097 | 0 | 16.8 | 5.703 | 5.703 | opened
44 | SS 110/6 kv Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed | 44 | SS 110/6 kv Karachizhskaya | 10+10 | 0.457 | 18.737 | 0 | 0 | 18.737 | 0 | 10.5 | -8.237 | -8.237 | yes
45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 0.059 | 7.159 | 1.4 | 6 hours | 5.759 | 0 | 10.5 | 4.741 | 4.741 | opened
| Nom. capacity MV, MVA | 10+16 | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6
| Nom. capacity LV, MVA | 10+16 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.059 | 5.259 | 0 | 0 | 5.259 | 0 | 10.5 | 5.241
46 | SS 110/35/10 kv Komarichi | 16+16 | 9.89 | 3.7 | 6 hours | 6.19 | 0 | 16.8 | 10.61 | 10.61 | opened | 46 | SS 110/35/10 kv Komarichi | 16+16 | 0.036 | 9.91 | 3.7 | 6 hours | 6.21 | 0 | 16.8 | 10.59 | 10.59 | opened
| Nom. capacity MV, MVA | 16+16 | 5 | 3.7 | 6 hours | 1.3 | 0 | 16.8 | 11.8 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5 | 3.7 | 6 hours | 1.3 | 0 | 16.8 | 11.8
| Nom. capacity LV, MVA | 16+16 | 4.89 | 0 | 0 | 4.89 | 0 | 16.8 | 11.91 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.036 | 4.926 | 0 | 0 | 4.926 | 0 | 16.8 | 11.874
47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 0.9 | 0 | 0 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | opened | 47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 0.008 | 0.908 | 0 | 0 | 0.908 | 0 | 2.625 | 1.717 | 1.717 | opened
48 | SS 110/6 kv Mamonovskaya | 10+16 | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed | 48 | SS 110/6 kv Mamonovskaya | 10+16 | 1.472 | 16.762 | 0 | 0 | 16.762 | 0 | 10.5 | -6.262 | -6.262 | closed
49 | SS 110/35/10 kv Maritskaya | 10+16 | 5.23 | 4.5 | 6 hours | 0.73 | 0 | 10.5 | 9.77 | 5.97 | opened | 49 | SS 110/35/10 kv Maritskaya | 10+16 | 0.01 | 5.23 | 4.5 | 6 hours | 0.73 | 0 | 10.5 | 9.77 | 5.97 | opened
| Nom. capacity MV, MVA | 10+16 | 4.53 | 4.5 | 6 hours | 0.03 | 0 | 10.5 | 5.97 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 4.53 | 4.5 | 6 hours | 0.03 | 0 | 10.5 | 5.97
| Nom. capacity LV, MVA | 10+16 | 0.7 | 0 | 0 | 0.7 | 0 | 10.5 | 9.8 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.01 | 0.71 | 0 | 0 | 0.71 | 0 | 10.5 | 9.79
50 | SS 110/6 kv Michurinskaya | 6,3+10 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 | 4.315 | opened | 50 | SS 110/6 kv Michurinskaya | 6,3+10 | 0.6 | 2.9 | 0 | 0 | 2.9 | 0 | 6.615 | 3.715 | 3.715 | opened
51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 2.4 | 0 | 0 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened | 51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 0.012 | 2.412 | 0 | 0 | 2.412 | 0 | 6.615 | 4.203 | 4.203 | opened
52 | SS 110/10 kv Polpinskaya | 16+16 | 3.6 | 0 | 0 | 3.6 | 0 | 16.8 | 13.2 | 13.2 | opened | 52 | SS 110/10 kv Polpinskaya | 16+16 | 0.129 | 3.729 | 0 | 0 | 3.729 | 0 | 16.8 | 13.071 | 13.071 | opened
53 | SS 110/6 kv Sovetskaya | 16+16+25 | 49.27 | 0 | 0 | 49.27 | 0 | 33.6 | -15.67 | -15.67 | closed | 53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 7.645 | 56.915 | 0 | 0 | 56.915 | 0 | 59.85 | 2.935 | 2.935 | opened
54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened | 54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 0.178 | 42.578 | 0 | 0 | 42.578 | 0 | 75.075 | 32.497 | 32.497 | opened
55 | SS 110/10 kv Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened | 55 | SS 110/10 kv Teplichnaya | 10+10 | 0.154 | 5.054 | 0 | 0 | 5.054 | 0 | 10.5 | 5.446 | 5.446 | opened
56 | SS 110/6 kv Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened | 56 | SS 110/6 kv Uritskaya | 20+20 | 0 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened
57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened | 57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 0.16 | 14.22 | 4.8 | 6 hours | 9.42 | 0 | 16.8 | 7.38 | 7.38 | opened
| Nom. capacity MV, MVA | 16+16 | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98
| Nom. capacity LV, MVA | 16+16 | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.16 | 9.4 | 0 | 0 | 9.4 | 0 | 16.8 | 7.4
58 | SS 110/6 kv Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed | 58 | SS 110/6 kv Yuzhnaya | 16+25 | 0.238 | 19.668 | 0 | 0 | 19.668 | 0 | 16.8 | -2.868 | -2.868 | closed
59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened | 59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 0.022 | 1.519 | 0 | 0 | 1.519 | 0 | 2.625 | 1.106 | 1.106 | opened
60 | SS 110/6 kv Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened | 60 | SS 110/6 kv Belaya Berezka | 16+25 | 0 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened
61 | SS 110/10 kv Valuets | 4+6,3 | 1.114 | 0 | 0 | 1.114 | 0 | 4.2 | 3.086 | 3.086 | opened | 61 | SS 110/10 kv Valuets | 4+6,3 | 0.092 | 1.206 | 0 | 0 | 1.206 | 0 | 4.2 | 2.994 | 2.994 | opened
62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 1.808 | 0.54 | 3 hours | 1.268 | 0 | 42 | 40.732 | 40.731 | opened | 62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 0 | 1.808 | 0.54 | 3 hours | 1.268 | 0 | 42 | 40.732 | 40.731 | opened
| Nom. capacity MV, MVA | 10+6,3 | 0.539 | 0.54 | 3 hours | -0.001 | 0 | 42 | 41.461 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.539 | 0.54 | 3 hours | -0.001 | 0 | 42 | 41.461
| Nom. capacity LV, MVA | 10+6,3 | 1.269 | 0 | 0 | 1.269 | 0 | 42 | 40.731 |  |  |  | Nom. capacity LV, MVA | 10+6,3 |  | 1.269 | 0 | 0 | 1.269 | 0 | 42 | 40.731
63 | SS 110/6 kv Vysokoe | 40+40 | 20.732 | 0 | 0 | 20.732 | 0 | 42 | 21.268 | 21.268 | opened | 63 | SS 110/6 kv Vysokoe | 40+40 | 0.029 | 20.761 | 0 | 0 | 20.761 | 0 | 42 | 21.239 | 21.239 | opened
64 | SS 110/10 kv Zalineynaya | 10+6,3 | 3.931 | 0 | 0 | 3.931 | 0 | 6.615 | 2.684 | 2.684 | opened | 64 | SS 110/10 kv Zalineynaya | 10+6,3 | 0.131 | 4.062 | 0 | 0 | 4.062 | 0 | 6.615 | 2.553 | 2.553 | opened
65 | SS 110/6 kv Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened | 65 | SS 110/6 kv Zapadnaya | 10+10 | 0.016 | 10.516 | 0 | 0 | 10.516 | 0 | 10.5 | -0.016 | -0.016 | opened
66 | SS 110/35/10 kv Klimovo | 16+16 | 9.213 | 1.64 | 6 hours | 7.573 | 0 | 42 | 34.427 | 34.427 | opened | 66 | SS 110/35/10 kv Klimovo | 16+16 | 0.153 | 9.269 | 1.64 | 6 hours | 7.629 | 0 | 42 | 34.371 | 34.371 | opened
| Ном. мощность СН, МВА | 16+16 | 3.123 | 1.64 | 6 hours | 1.483 | 0 | 42 | 38.877 |  |  |  | Ном. мощность СН, МВА | 16+16 |  | 3.123 | 1.64 | 6 hours | 1.483 | 0 | 42 | 38.877
| Ном. мощность НН, МВА | 16+16 | 6.09 | 0 | 0 | 6.09 | 0 | 42 | 35.91 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.153 | 6.243 | 0 | 0 | 6.243 | 0 | 42 | 35.757
67 | ПС 110/35/6 кВ Кожаны | 10+10 | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened | 67 | ПС 110/35/6 кВ Кожаны | 10+10 | 0.009 | 3.873 | 3.12 | 6 hours | 0.753 | 0 | 42 | 41.247 | 38.884 | opened
| Nom. capacity MV, MVA | 10+10 | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884
| Nom. capacity LV, MVA | 10+10 | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.009 | 0.757 | 0 | 0 | 0.757 | 0 | 42 | 41.243
68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 0.084 | 1.349 | 0 | 0 | 1.349 | 0 | 2.625 | 1.276 | 1.276 | opened
69 | SS 110/35/10 kv Pogar | 16+16+16 | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened | 69 | SS 110/35/10 kv Pogar | 16+16+16 | 0.142 | 10.586 | 1.8 | 6 hours | 8.786 | 0 | 42 | 33.214 | 33.109 | opened
| Nom. capacity MV, MVA | 16+16 | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197
| Nom. capacity LV, MVA | 16+16 | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.142 | 8.891 | 0 | 0 | 8.891 | 0 | 42 | 33.109
70 | SS 110/35/10 kv Pochepskaya | 16+25 | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened | 70 | SS 110/35/10 kv Pochepskaya | 16+25 | 1.732 | 14.726 | 2.21 | 3 hours | 12.516 | 0 | 42 | 29.484 | 29.481 | opened
| Nom. capacity MV, MVA | 16+25 | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792
| Nom. capacity LV, MVA | 16+25 | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213 |  |  |  | Nom. capacity LV, MVA | 16+25 | 1.732 | 12.519 | 0 | 0 | 12.519 | 0 | 42 | 29.481
71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened | 71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.006 | 0.545 | 0 | 0 | 0.545 | 0 | 2.625 | 2.08 | 2.08 | opened
72 | SS 110/35/10 kv Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened | 72 | SS 110/35/10 kv Starodub | 16+16 | 0.017 | 12.581 | 7.34 | 6 hours | 5.241 | 0 | 42 | 36.759 | 34.665 | opened
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.017 | 5.246 | 0 | 0 | 5.246 | 0 | 42 | 36.754
73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.97 | 0 | 0 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | opened | 73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.015 | 0.985 | 0 | 0 | 0.985 | 0 | 6.615 | 5.63 | 5.63 | opened
74 | SS 110/35/6 kv Surazh | 16+16 | 18 | 3.04 | 3 hours | 14.96 | 0 | 42 | 27.04 | 27.04 | opened | 74 | SS 110/35/6 kv Surazh | 16+16 | 0 | 18 | 3.04 | 6 hours | 14.96 | 0 | 42 | 27.04 | 27.04 | opened
| Nom. capacity MV, MVA | 16+16 | 4.7 | 3.04 | 3 hours | 1.66 | 0 | 42 | 37.3 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.7 | 3.04 | 6 hours | 1.66 | 0 | 42 | 37.3
| Nom. capacity LV, MVA | 16+16 | 13.3 | 0 | 0 | 13.3 | 0 | 42 | 28.7 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 13.3 | 0 | 0 | 13.3 | 0 | 42 | 28.7
75 | SS 110/10 kv Trubchevsk | 16+10 | 7.399 | 0 | 0 | 7.399 | 0 | 10.5 | 3.101 | 3.101 | opened | 75 | SS 110/10 kv Trubchevsk | 16+10 | 0.34 | 7.739 | 0 | 0 | 7.739 | 0 | 10.5 | 2.761 | 2.761 | opened
76 | SS 110/10 kv Shelomy | 6,3+6,3 | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened | 76 | SS 110/10 kv Shelomy | 6,3+6,3 | 0.011 | 1.016 | 0 | 0 | 1.016 | 0 | 6.615 | 5.599 | 5.599 | opened
77 | SS 110/35/6 kv Yubileynaya | 16+16 | 13.67 | 6.45 | 3 hours | 7.22 | 0 | 42 | 34.78 | 34.775 | opened | 77 | SS 110/35/6 kv Yubileynaya | 16+16 | 0.315 | 13.973 | 6.45 | 3 hours | 7.523 | 0 | 42 | 34.477 | 34.46 | opened
| Nom. capacity MV, MVA | 16+16 | 6.445 | 6.45 | 3 hours | -0.005 | 0 | 42 | 35.555 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.445 | 6.45 | 3 hours | -0.005 | 0 | 42 | 35.555
| Nom. capacity LV, MVA | 16+16 | 7.225 | 0 | 0 | 7.225 | 0 | 42 | 34.775 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.315 | 7.54 | 0 | 0 | 7.54 | 0 | 42 | 34.46
78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened | 78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 0 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened
79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 2.9 | 0 | 0 | 2.9 | 0 | 6.615 | 3.715 | 3.715 | opened | 79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 0.003 | 2.903 | 0 | 0 | 2.903 | 0 | 6.615 | 3.712 | 3.712 | opened
80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened | 80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
81 | SS 35/6 kv Bytosh | 3,2+6,3 | 2.2 | 0 | 0 | 2.2 | 0 | 3.36 | 1.16 | 1.16 | opened | 81 | SS 35/6 kv Bytosh | 3,2+6,3 | 0 | 2.2 | 0 | 0 | 2.2 | 0 | 3.36 | 1.16 | 1.16 | opened
82 | SS 35/6 kv Velyaminovskaya | 4+4 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened | 82 | SS 35/6 kv Velyaminovskaya | 4+4 | 0.007 | 1.307 | 0 | 0 | 1.307 | 0 | 4.2 | 2.893 | 2.893 | opened
83 | SS 35/6 kv Vetma | 2,5+2,5 | 0.2 | 0 | 0 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 83 | SS 35/6 kv Vetma | 2,5+2,5 | 0 | 0.2 | 0 | 0 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
84 | SS 35/6 kv Volodarskaya | 10+6,3 | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.515 | -4.515 | closed | 84 | SS 35/6 kv Volodarskaya | 10+6,3 | 0 | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.515 | -4.515 | closed
85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 0.013 | 1.113 | 0 | 0 | 1.113 | 0 | 2.625 | 1.512 | 1.512 | opened
86 | SS 35/6 kv Gorodskaya | 10+10 | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -0.38 | -0.38 | closed | 86 | SS 35/6 kv Gorodskaya | 10+10 | 0 | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -0.38 | -0.38 | closed
87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.017 | 0.617 | 0 | 0 | 0.617 | 0 | 4.2 | 3.583 | 3.583 | opened
88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0 | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 0.029 | 1.729 | 0 | 0 | 1.729 | 0 | 4.2 | 2.471 | 2.471 | opened
90 | SS 35/10 kv Igritskaya | 4+6,3 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened | 90 | SS 35/10 kv Igritskaya | 4+6,3 | 0.023 | 1.323 | 0 | 0 | 1.323 | 0 | 4.2 | 2.877 | 2.877 | opened
91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.1 | 0 | 0 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened | 91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.008 | 0.108 | 0 | 0 | 0.108 | 0 | 1.05 | 0.942 | 0.942 | opened
92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened | 92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened
93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.004 | 0.604 | 0 | 0 | 0.604 | 0 | 2.625 | 2.021 | 2.021 | opened
94 | SS 35/10 kv Luna | 1,6+1,6 | 1.1 | 0 | 0 | 1.1 | 0 | 1.68 | 0.58 | 0.58 | opened | 94 | SS 35/10 kv Luna | 1,6+1,6 | 0 | 1.1 | 0 | 0 | 1.1 | 0 | 1.68 | 0.58 | 0.58 | opened
95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 6.16 | 0 | 0 | 6.16 | 0 | 6.615 | 0.455 | 0.455 | opened | 95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 0.01 | 6.17 | 0 | 0 | 6.17 | 0 | 6.615 | 0.445 | 0.445 | opened
96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.021 | 0.821 | 0 | 0 | 0.821 | 0 | 1.68 | 0.859 | 0.859 | opened
97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.005 | 0.205 | 0 | 0 | 0.205 | 0 | 1.68 | 1.475 | 1.475 | opened
98 | SS 35/10 kv Norinskaya | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 98 | SS 35/10 kv Norinskaya | 4+4 | 0.02 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | opened
99 | SS 35/6 kv Paltso | 4+2,5 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 99 | SS 35/6 kv Paltso | 4+2,5 | 0.007 | 0.407 | 0 | 0 | 0.407 | 0 | 2.625 | 2.218 | 2.218 | opened
100 | SS 35/6 kv Pobeda | 4+4 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened | 100 | SS 35/6 kv Pobeda | 4+4 | 0.43 | 4.1 | 0 | 0 | 4.1 | 0 | 4.2 | 0.1 | 0.1 | opened
101 | SS 35/10 kv Pogreby | 4+4 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened | 101 | SS 35/10 kv Pogreby | 4+4 | 0.01 | 1.01 | 0 | 0 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened
102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened | 102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 0.071 | 1.071 | 0 | 0 | 1.071 | 0 | 1.68 | 0.609 | 0.609 | opened
103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
104 | SS 35/10 kv Rofnedinskaya | 4+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened | 104 | SS 35/10 kv Rofnedinskaya | 4+6,3 | 0.02 | 1.62 | 0 | 0 | 1.62 | 0 | 4.2 | 2.58 | 2.58 | opened
105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.8 | 0 | 0 | 0.8 | 0 | 4.2 | 3.4 | 3.4 | opened | 105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.01 | 0.81 | 0 | 0 | 0.81 | 0 | 4.2 | 3.39 | 3.39 | opened
106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened | 106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 0.215 | 4.015 | 0 | 0 | 4.015 | 0 | 6.615 | 2.6 | 2.6 | opened
107 | SS 35/6 kv Seshcha | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed | 107 | SS 35/6 kv Seshcha | 1,6+4 | 0.042 | 2.042 | 0 | 0 | 2.042 | 0 | 1.68 | -0.362 | -0.362 | closed
108 | SS 35/6 kv Star | 10+10 | 3 | 0 | 0 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened | 108 | SS 35/6 kv Star | 10+10 | 0 | 3 | 0 | 0 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened
109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.051 | 0.651 | 0 | 0 | 0.651 | 0 | 2.625 | 1.974 | 1.974 | opened
110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.039 | 0.539 | 0 | 0 | 0.539 | 0 | 1.68 | 1.141 | 1.141 | opened
111 | SS 35/6 kv Fokinskaya | 16+16 | 22.62 | 0 | 0 | 22.62 | 0 | 16.8 | -5.82 | -5.82 | closed | 111 | SS 35/6 kv Fokinskaya | 16+16+16 | 1.226 | 23.846 | 0 | 0 | 23.846 | 0 | 33.6 | 9.754 | 9.754 | opened
112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened | 112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 3.785 | 12.085 | 0 | 0 | 12.085 | 0 | 12.495 | 0.41 | 0.41 | opened
113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
114 | SS 35/10 kv Abarinskaya | 4+4 | 0.83 | 0 | 0 | 0.83 | 0 | 4.2 | 3.37 | 3.37 | opened | 114 | SS 35/10 kv Abarinskaya | 4+4 | 0.09 | 0.92 | 0 | 0 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened
115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0.6 | opened | 116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 0.041 | 1.121 | 0 | 0 | 1.121 | 0 | 1.68 | 0.559 | 0 | opened
117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.022 | 0.522 | 0 | 0 | 0.522 | 0 | 1.68 | 1.158 | 1.158 | opened
118 | SS 35/6 kv Water intake | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 118 | SS 35/6 kv Water intake | 2,5+2,5 | 0 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
119 | SS 35/10 kv Voronok | 2,5+3,2 | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened | 119 | SS 35/10 kv Voronok | 2,5+3,2 | 0.023 | 1.493 | 0 | 0 | 1.493 | 0 | 2.625 | 1.132 | 1.132 | opened
120 | SS 35/10 kv Gordeevka | 4+4 | 2.82 | 0 | 0 | 2.82 | 0 | 4.2 | 1.38 | 1.38 | opened | 120 | SS 35/10 kv Gordeevka | 4+4 | 0.055 | 2.875 | 0 | 0 | 2.875 | 0 | 4.2 | 1.325 | 1.325 | opened
121 | SS 35/10 kv Gridenki | 2,5+3,2 | 1.3 | 0 | 0 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened | 121 | SS 35/10 kv Gridenki | 2,5+3,2 | 0.113 | 1.413 | 0 | 0 | 1.413 | 0 | 2.625 | 1.212 | 1.212 | opened
122 | SS 35/10 kv Zavodskaya | 4+2,5 |  | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 122 | SS 35/10 kv Zavodskaya | 4+2,5 | 0.005 | 0.005 | 0 | 0 | 0.005 | 0 | 2.625 | 2.62 | 2.62 | opened
123 | SS 35/10 kv Istopki | 1,6+1,6 | 0.99 | 0 | 0 | 0.99 | 0 | 1.68 | 0.69 | 0.69 | opened | 123 | SS 35/10 kv Istopki | 1,6+1,6 | 0 | 0.99 | 0 | 0 | 0.99 | 0 | 1.68 | 0.69 | 0.69 | opened
124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened | 124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.024 | 0.694 | 0 | 0 | 0.694 | 0 | 1.68 | 0.986 | 0.986 | opened
125 | SS 35/10 kv Kivay | 2,5+2,5 | 1.88 | 0 | 0 | 1.88 | 0 | 2.625 | 0.745 | 0.745 | opened | 125 | SS 35/10 kv Kivay | 2,5+2,5 | 0.015 | 1.895 | 0 | 0 | 1.895 | 0 | 2.625 | 0.73 | 0.73 | opened
126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.035 | 0.615 | 0 | 0 | 0.615 | 0 | 1.68 | 1.065 | 1.065 | opened
127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 0.985 | 0 | 0 | 0.985 | 0 | 1.68 | 0.695 | 0.695 | opened | 127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 0.016 | 1.001 | 0 | 0 | 1.001 | 0 | 1.68 | 0.679 | 0.679 | opened
128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.013 | 0.373 | 0 | 0 | 0.373 | 0 | 2.625 | 2.252 | 2.252 | opened
129 | SS 35/10 kv Mglinskaya | 4+4 | 3.04 | 0 | 0 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | opened | 129 | SS 35/10 kv Mglinskaya | 4+4 | 0.026 | 3.066 | 0 | 0 | 3.066 | 0 | 4.2 | 1.134 | 1.134 | opened
130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened | 130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.021 | 0.531 | 0 | 0 | 0.531 | 0 | 1.68 | 1.149 | 1.149 | opened
131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.001 | 0.581 | 0 | 0 | 0.581 | 0 | 2.625 | 2.044 | 2.044 | opened
132 | SS 35/10 kv Putevaya | 6,3+6,3 | 5.24 | 0 | 0 | 5.24 | 0 | 6.615 | 1.375 | 1.375 | opened | 132 | SS 35/10 kv Putevaya | 6,3+6,3 | 0.044 | 5.284 | 0 | 0 | 5.284 | 0 | 6.615 | 1.331 | 1.331 | opened
133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 0.95 | 0 | 0 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened | 133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 0.01 | 0.96 | 0 | 0 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
134 | SS 35/10 kv Slava | 2,5+1,6 | 1.06 | 0 | 0 | 1.06 | 0 | 1.68 | 0.62 | 0.62 | opened | 134 | SS 35/10 kv Slava | 2,5+1,6 | 0.019 | 1.079 | 0 | 0 | 1.079 | 0 | 1.68 | 0.601 | 0.601 | opened
135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 3.22 | 0 | 0 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened | 135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 0.08 | 3.3 | 0 | 0 | 3.3 | 0 | 6.615 | 3.315 | 3.315 | opened
136 | SS 35/10 kv Solovyovka | 1,6+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened | 136 | SS 35/10 kv Solovyovka | 1,6+1,6 | 0.003 | 0.453 | 0 | 0 | 0.453 | 0 | 1.68 | 1.227 | 1.227 | opened
137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.42 | 0 | 0 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened | 137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.015 | 0.435 | 0 | 0 | 0.435 | 0 | 2.625 | 2.19 | 2.19 | opened
138 | SS 35/6 kv Tembr | 4+4+3,2 | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened | 138 | SS 35/6 kv Tembr | 4+4+3,2 | 0.07 | 7 | 0 | 0 | 7 | 0 | 7.56 | 0.56 | 0.56 | opened
139 | SS 35/10 kv Churovichi | 2,5+4 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 139 | SS 35/10 kv Churovichi | 2,5+4 | 0.026 | 0.836 | 0 | 0 | 0.836 | 0 | 2.625 | 1.789 | 1.789 | opened
140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 0.033 | 1.063 | 0 | 0 | 1.063 | 0 | 2.625 | 1.562 | 1.562 | opened
| Total: |  | 745.357 | [8 empty] | 2: Total:; 4: 34.033; 5: 779.0793
| deficit | [8 empty] | -59.395 |  | 2: deficit; Мin. 12: -45.803
| proficit | [8 empty] | 716.066 |  | 2: proficit; Мin. 12: 712.8387

## Воронеж
[11 empty] | Table 1 |  |  |  |  | 0 | [8 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note |  | No. | Object of main substation, voltage class | Expected deficit/proficit, MVA | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit/proficit of Main Substation, MVA | [5 empty] | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Transmission capacity of Main Susbstation, MVA | Expected deficit/proficit, MVA
|  |  | МVА | МVА | Мin. | [12 empty] | МVА | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-tranformer substations | [12 empty] | 1: One-tranformer substations
| SPN | [11 empty] | 2: SPN
1 | No. 44 | 10 | 0.06 | 0 | 0 | 0 | 0 | 0 | -0.06 | -0.06 |  |  | 1 | No. 44 | 10 | 2.07 | 2.13 | 0 | 0 | 2.13 | 0 | 0 | -2.13 | -2.13 | 110/6
2 | No. 7 | 2.5 | 0.22 | 3.5 | 0 | 3.5 | 0 | 3.5 | 3.28 | 3.28 |  |  | 2 | No. 7 | 2.5 | 3.49 | 3.71 | 3.5 | 0 | 0.21 | 0 | 3.5 | -0.21 | -0.21 | 35/6
3 | Stupino | 6.3 | 0.95 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.0875 | 0.0875 |  |  | 3 | Stupino | 6.3 | 0.06 | 1.01 | 1.0375 | 120 | -0.0275 | 0 | 1.0375 | 0.0275 | 0.0275 | 110/10
4 | P.Kommuna | 6.3 | 0.41 | 0.413 | 120 | 0.413 | 0 | 0.413 | 0.003 | 0.003 |  |  | 4 | P.Kommuna | 6.3 | 0 | 0.41 | 0.413 | 120 | -0.003 | 0 | 0.413 | 0.003 | 0.003 | 110/10
5 | No. 38 | 2.5 | 0.8 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0 | 0 |  |  | 5 | No. 38 | 2.5 | 0 | 0.8 | 0.8 | 120 | 0 | 0 | 0.8 | 0 | 0 | 35/10
6 | No. 46 | 4 | 0.03 | 0 | 0 | 0 | 0 | 0 | -0.03 | -0.03 |  |  | 6 | No. 46 | 4 | 0 | 0.03 | 0 | 0 | 0.03 | 0 | 0 | -0.03 | -0.03 | 35/6
7 | Istobnoe | 4 | 0.35 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.01 | 0.01 |  |  | 7 | Istobnoe | 4 | 0.01 | 0.36 | 0.36 | 120 | 0 | 0 | 0.36 | 0 | 0 | 35/10
8 | Rodina | 2.5 | 0.15 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.65 | 1.65 |  |  | 8 | Rodina | 2.5 | 1.63 | 1.78 | 1.8 | 120 | -0.02 | 0 | 1.8 | 0.02 | 0.02 | 35/10
9 | Vyaznovatovka | 2.5 | 0.45 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.05 | 1.05 |  |  | 9 | Vyaznovatovka | 2.5 | 1.02 | 1.47 | 1.5 | 120 | -0.03 | 0 | 1.5 | 0.03 | 0.03 | 35/10
10 | V. Turovo-1 | 3.2 | 1.31 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.09 | 0.09 |  |  | 10 | V. Turovo-1 | 3.2 | 0.02 | 1.33 | 1.4 | 120 | -0.07 | 0 | 1.4 | 0.07 | 0.07 | 35/10
11 | Semidesyatnoe | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  | 11 | Semidesyatnoe | 2.5 | 0.07 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | -0.36 | -0.36 | 35/10
12 | Arkhangelskoe | 2.5 | 0.58 | 0 | 0 | 0 | 0 | 0 | -0.58 | -0.58 |  |  | 12 | Arkhangelskoe | 2.5 | 0.07 | 0.65 | 0 | 0 | 0.65 | 0 | 0 | -0.65 | -0.65 | 35/10
13 | Khokhol-2 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 |  |  | 13 | Khokhol-2 | 2.5 | 0.11 | 1.11 | 0 | 0 | 1.11 | 0 | 0 | -1.11 | -1.11 | 35/10
14 | N.Olshanka | 4 | 0.73 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | 0.0274 | 0.0274 |  |  | 14 | N.Olshanka | 4 | 0.03 | 0.76 | 0.7574 | 120 | 0.0026 | 0 | 0.7574 | -0.0026 | -0.0026 | 35/10
15 | Troitskoe | 2.5 | 0.43 | 0 | 0 | 0 | 0 | 0 | -0.43 | -0.43 |  |  | 15 | Troitskoe | 2.5 | 0.01 | 0.44 | 0 | 0 | 0.44 | 0 | 0 | -0.44 | -0.44 | 35/10
16 | Zemlyansk | 4 | 0.91 | 0 | 0 | 0 | 0 | 0 | -0.91 | -0.91 |  |  | 16 | Zemlyansk | 4 | 0.01 | 0.92 | 0 | 0 | 0.92 | 0 | 0 | -0.92 | -0.92 | 35/10
17 | LosevoSES | 2.5 | 0.95 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.0036 | 0.0036 |  |  | 17 | LosevoSES | 2.5 | 0 | 0.95 | 0.9536 | 120 | -0.0036 | 0 | 0.9536 | 0.0036 | 0.0036 | 35/10
18 | Verny | 2.5 | 1.66 | 1.706 | 120 | 1.706 | 0 | 1.706 | 0.046 | 0.046 |  |  | 18 | Verny | 2.5 | 0.04 | 1.7 | 1.706 | 120 | -0.006 | 0 | 1.706 | 0.006 | 0.006 | 35/10
19 | Elevator | 2.5 | 0.81 | 0.848 | 120 | 0.848 | 0 | 0.848 | 0.038 | 0.038 |  |  | 19 | Elevator | 2.5 | 0.03 | 0.84 | 0.848 | 120 | -0.008 | 0 | 0.848 | 0.008 | 0.008 | 35/10
20 | Yubileynaya | 4 | 1.45 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.15 | 0.15 |  |  | 20 | Yubileynaya | 4 | 0.07 | 1.52 | 1.6 | 120 | -0.08 | 0 | 1.6 | 0.08 | 0.08 | 35/10
21 | Parusnoe | 4 | 3.07 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.0884 | 0.0884 |  |  | 21 | Parusnoe | 4 | 0.05 | 3.12 | 3.1584 | 120 | -0.0384 | 0 | 3.1584 | 0.0384 | 0.0384 | 35/10
22 | Rogachyovka | 4 | 1.91 | 1.9643 | 120 | 1.9643 | 0 | 1.9643 | 0.0543 | 0.0543 |  |  | 22 | Rogachyovka | 4 | 0.05 | 1.96 | 1.9643 | 120 | -0.0043 | 0 | 1.9643 | 0.0043 | 0.0043 | 35/10
23 | PTF Rassvet | 2.5 | 0.2 | 0.2 | 120 | 0.2 | 0 | 0.2 | 0 | 0 |  |  | 23 | PTF Rassvet | 2.5 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 0.2 | 0 | 0 | 35/10
24 | Dankovo | 2.5 | 0.87 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.029 | 0.029 |  |  | 24 | Dankovo | 2.5 | 0.02 | 0.89 | 0.899 | 120 | -0.009 | 0 | 0.899 | 0.009 | 0.009 | 35/10
| ЛЭС | [11 empty] | 2: LOG
25 | Bugaevka | 16 | 5.26 | 14 | 90 | 14 | 0 | 14 | 8.74 | 2.41 |  |  | 25 | Bugaevka | 16 | 0.19 | 5.45 | 14 | 90 | -8.55 | 0 | 14 | 8.55 | 2.22
| Sн. MV, МVА | 16 | 3.67 | 10 | 90 | 10 | 0 | 10 | 6.33 |  |  |  |  | Sн. MV, МVА | 16 | 0 | 3.67 | 10 | 90 | -6.33 | 0 | 10 | 6.33 |  | 110/35/10
| Sн. LV, МVА | 16 | 1.59 | 4 | 90 | 4 | 0 | 4 | 2.41 |  |  |  |  | Sн. LV, МVА | 16 | 0.19 | 1.78 | 4 | 90 | -2.22 | 0 | 4 | 2.22
26 | Dobrino | 10 | 1.03 | 6.6 | 90 | 6.6 | 0 | 6.6 | 5.57 | 2.31 |  |  | 26 | Dobrino | 10 | 0.12 | 1.15 | 6.6 | 90 | -5.45 | 0 | 6.6 | 5.45 | 2.19
| Sн. MV, МVА | 10 | 0.22 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.58 |  |  |  |  | Sн. MV, МVА | 10 | 0 | 0.22 | 5.8 | 90 | -5.58 | 0 | 5.8 | 5.58 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.81 | 3.12 | 90 | 3.12 | 0 | 3.12 | 2.31 |  |  |  |  | Sн. LV, МVА | 10 | 0.12 | 0.93 | 3.12 | 90 | -2.19 | 0 | 3.12 | 2.19
27 | N. Kalitva | 6.3 | 1.56 | 2 | 240 | 2 | 0 | 2 | 0.44 | 0.44 |  |  | 27 | N. Kalitva | 6.3 | 0.23 | 1.79 | 2 | 240 | -0.21 | 0 | 2 | 0.21 | 0.21 | 110/10
28 | Shishovka | 6.3 | 0.68 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.66 | 1.66 |  |  | 28 | Shishovka | 6.3 | 0.04 | 0.72 | 2.34 | 180 | -1.62 | 0 | 2.34 | 1.62 | 1.62 | 110/10
29 | Azovka | 10 | 1.47 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.65 | 1.65 |  |  | 29 | Azovka | 10 | 1.18 | 2.65 | 3.12 | 180 | -0.47 | 0 | 3.12 | 0.47 | 0.47 | 110/10
30 | Yurasovka | 2.5 | 0.64 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.92 | 0.92 |  |  | 30 | Yurasovka | 2.5 | 0.02 | 0.66 | 1.56 | 120 | -0.9 | 0 | 1.56 | 0.9 | 0.9 | 35/10
31 | Nerovnovka | 2.5 | 0.27 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.51 | 0.51 |  |  | 31 | Nerovnovka | 2.5 | 0.01 | 0.28 | 0.78 | 240 | -0.5 | 0 | 0.78 | 0.5 | 0.5 | 35/10
32 | Saprino | 1.8 | 0.34 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.46 | 1.46 |  |  | 32 | Saprino | 1.8 | 0.01 | 0.35 | 1.8 | 120 | -1.45 | 0 | 1.8 | 1.45 | 1.45 | 35/10
33 | Sergeevka | 4 | 0.34 | 0 | 0 | 0 | 0 | 0 | -0.34 | -0.34 |  |  | 33 | Sergeevka | 4 | 0.06 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | -0.4 | -0.4 | 35/10
34 | Stepanovka | 4 | 0.39 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.17 | 1.17 |  |  | 34 | Stepanovka | 4 | 0.02 | 0.41 | 1.56 | 240 | -1.15 | 0 | 1.56 | 1.15 | 1.15 | 35/10
35 | Kolodezhanskaya | 2.5 | 0.23 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.55 | 0.55 |  |  | 35 | Kolodezhanskaya | 2.5 | 0.05 | 0.28 | 0.78 | 180 | -0.5 | 0 | 0.78 | 0.5 | 0.5 | 35/10
36 | Andreevka | 2.5 | 0.07 | 0 | 0 | 0 | 0 | 0 | -0.07 | -0.07 |  |  | 36 | Andreevka | 2.5 | 0.02 | 0.09 | 0 | 0 | 0.09 | 0 | 0 | -0.09 | -0.09 | 35/10
37 | Kulikovka | 4 | 1.3 | 0 | 0 | 0 | 0 | 0 | -1.3 | -1.3 |  |  | 37 | Kulikovka | 4 | 0.2 | 1.5 | 0 | 0 | 1.5 | 0 | 0 | -1.5 | -1.5 | 35/10
38 | Lizinovka | 2.5 | 0.73 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.77 | 1.77 |  |  | 38 | Lizinovka | 2.5 | 0.05 | 0.78 | 2.5 | 240 | -1.72 | 0 | 2.5 | 1.72 | 1.72 | 35/10
39 | Sotnitskaya | 4 | 1.42 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.88 | 0.88 |  |  | 39 | Sotnitskaya | 4 | 0.03 | 1.45 | 2.3 | 120 | -0.85 | 0 | 2.3 | 0.85 | 0.85 | 35/10
40 | Kr. Polyana | 2.5 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 |  |  | 40 | Kr. Polyana | 2.5 | 0.02 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | -0.3 | -0.3 | 35/10
41 | Gumny | 4 | 0.92 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.64 | 0.64 |  |  | 41 | Gumny | 4 | 0.08 | 1 | 1.56 | 180 | -0.56 | 0 | 1.56 | 0.56 | 0.56 | 35/10
42 | Uryv | 2.5 | 0.55 | 0 | 0 | 0 | 0 | 0 | -0.55 | -0.55 |  |  | 42 | Uryv | 2.5 | 0.05 | 0.6 | 0 | 0 | 0.6 | 0 | 0 | -0.6 | -0.6 | 35/10
43 | Shubnoe | 2.5 | 0.63 | 1.17 | 180 | 1.17 | 0 | 1.17 | 0.54 | 0.54 |  |  | 43 | Shubnoe | 2.5 | 0.09 | 0.72 | 1.17 | 180 | -0.45 | 0 | 1.17 | 0.45 | 0.45 | 35/10
44 | Zaluzhnoe | 2.5 | 1.52 | 1.9 | 240 | 1.9 | 0 | 1.9 | 0.38 | 0.38 |  |  | 44 | Zaluzhnoe | 2.5 | 0.26 | 1.78 | 1.9 | 240 | -0.12 | 0 | 1.9 | 0.12 | 0.12 | 35/10
| BPN | [11 empty] | 2: BPN
46 | Anna-2 | 25 | 6.51 | 7.8 | 90 | 7.8 | 0 | 7.8 | 1.29 | 0.37 |  |  | 45 | Anna-2 | 25 | 0.03 | 6.54 | 7.8 | 90 | -1.26 | 0 | 7.8 | 1.26 | 0.37
| Sн. MV, МVА | 25 | 1.87 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.37 |  |  |  |  | Sн. MV, МVА | 25 | 0 | 1.87 | 2.24 | 90 | -0.37 | 0 | 2.24 | 0.37 |  | 110/35/10
| Sн. LV, МVА | 25 | 4.64 | 5.56 | 90 | 5.56 | 0 | 5.56 | 0.92 |  |  |  |  | Sн. LV, МVА | 25 | 0.03 | 4.67 | 5.56 | 90 | -0.89 | 0 | 5.56 | 0.89
47 | Vostochnaya | 10 | 3.69 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.11 | 1.11 |  |  | 46 | Vostochnaya | 10 | 0.93 | 4.62 | 4.8 | 30 | -0.18 | 0 | 4.8 | 0.18 | 0.18 | 35/6
48 | Bolshevik BESБЭС | 6.3 | 1.22 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.24 | 0.24 |  |  | 47 | Bolshevik BESБЭС | 6.3 | 0.01 | 1.23 | 1.46 | 60 | -0.23 | 0 | 1.46 | 0.23 | 0.23 | 110/10
49 | Rozhdestvo | 6.3 | 0.59 | 0.7 | 60 | 0.7 | 0 | 0.7 | 0.11 | 0.11 |  |  | 48 | Rozhdestvo | 6.3 | 0.02 | 0.61 | 0.7 | 60 | -0.09 | 0 | 0.7 | 0.09 | 0.09 | 110/10
50 | V. Toyda | 6.3 | 1.16 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.24 | 0.24 |  |  | 49 | V. Toyda | 6.3 | 0.01 | 1.17 | 1.4 | 90 | -0.23 | 0 | 1.4 | 0.23 | 0.23 | 110/10
51 | Vostochnaya-1 | 40 | 6.78 | 8.13 | 60 | 8.13 | 0 | 8.13 | 1.35 | 0.94 |  |  | 50 | Vostochnaya-1 | 40 | 0.92 | 7.7 | 8.13 | 60 | -0.43 | 0 | 8.13 | 0.43 | 0.13
| Sн. MV, МVА | 40 | 4.73 | 5.67 | 60 | 5.67 | 0 | 5.67 | 0.94 |  |  |  |  | Sн. MV, МVА | 40 | 0 | 4.73 | 5.67 | 60 | -0.94 | 0 | 5.67 | 0.94 |  | 110/35/6
| Sн. LV, МVА | 40 | 2.05 | 3.1 | 60 | 3.1 | 0 | 3.1 | 1.05 |  |  |  |  | Sн. LV, МVА | 40 | 0.92 | 2.97 | 3.1 | 60 | -0.13 | 0 | 3.1 | 0.13
52 | Makashevka | 2.5 | 0.4 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.08 | 0.08 |  |  | 51 | Makashevka | 2.5 | 0.02 | 0.42 | 0.48 | 180 | -0.06 | 0 | 0.48 | 0.06 | 0.06 | 35/10
53 | Mirolyubie | 4 | 0.42 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.08 | 0.08 |  |  | 52 | Mirolyubie | 4 | 0 | 0.42 | 0.5 | 60 | -0.08 | 0 | 0.5 | 0.08 | 0.08 | 35/10
54 | V. Zaton | 2.5 | 0.01 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0 | 0 |  |  | 53 | V. Zaton | 2.5 | 0 | 0.01 | 0.01 | 60 | 0 | 0 | 0.01 | 0 | 0 | 35/10
55 | Oktyabrskoe | 2.5 | 0.56 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.11 | 0.11 |  |  | 54 | Oktyabrskoe | 2.5 | 0.03 | 0.59 | 0.67 | 30 | -0.08 | 0 | 0.67 | 0.08 | 0.08 | 35/10
56 | Ilmen | 2.5 | 0.26 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.12 | 0.12 |  |  | 55 | Ilmen | 2.5 | 0.01 | 0.27 | 0.38 | 60 | -0.11 | 0 | 0.38 | 0.11 | 0.11 | 35/10
57 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 |  |  | 56 | Vikhlyaevka | 2.5 | 0 | 0.1 | 0.12 | 120 | -0.02 | 0 | 0.12 | 0.02 | 0.02 | 35/10
58 | N. Elan | 2.5 | 0.41 | 0 | 0 | 0 | 0 | 0 | -0.41 | -0.41 |  |  | 57 | N. Elan | 2.5 | 0 | 0.41 | 0 | 0 | 0.41 | 0 | 0 | -0.41 | -0.41 | 35/10
59 | B. Alabukhi | 2.5 | 0.78 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.15 | 0.15 |  |  | 58 | B. Alabukhi | 2.5 | 0.04 | 0.82 | 0.93 | 90 | -0.11 | 0 | 0.93 | 0.11 | 0.11 | 35/10
60 | Pykhovka | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  | 59 | Pykhovka | 2.5 | 0 | 0.29 | 0 | 0 | 0.29 | 0 | 0 | -0.29 | -0.29 | 35/10
61 | Е. Koleno | 4 | 2.78 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.55 | 0.55 |  |  | 60 | Е. Koleno | 4 | 0.03 | 2.81 | 3.33 | 120 | -0.52 | 0 | 3.33 | 0.52 | 0.52 | 35/10
62 | Podgornoe BESБЭС | 2.5 | 0.39 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.07 | 0.07 |  |  | 61 | Podgornoe BESБЭС | 2.5 | 0.01 | 0.4 | 0.46 | 180 | -0.06 | 0 | 0.46 | 0.06 | 0.06 | 35/10
63 | Mikhailovka-1 | 4 | 0.3 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.06 | 0.06 |  |  | 62 | Mikhailovka-1 | 4 | 0 | 0.3 | 0.36 | 60 | -0.06 | 0 | 0.36 | 0.06 | 0.06 | 35/10
64 | Mikhailovka | 2.5 | 0.42 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.08 | 0.08 |  |  | 63 | Mikhailovka | 2.5 | 0.01 | 0.43 | 0.5 | 60 | -0.07 | 0 | 0.5 | 0.07 | 0.07 | 35/10
65 | Gnilusha | 4 | 0.77 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.15 | 0.15 |  |  | 64 | Gnilusha | 4 | 0 | 0.77 | 0.92 | 180 | -0.15 | 0 | 0.92 | 0.15 | 0.15 | 35/10
66 | Mayskaya | 2.5 | 0.64 | 0 | 0 | 0 | 0 | 0 | -0.64 | -0.64 |  |  | 65 | Mayskaya | 2.5 | 0 | 0.64 | 0 | 0 | 0.64 | 0 | 0 | -0.64 | -0.64 | 35/10
67 | Khleborodnoe | 2.5 | 0.48 | 0 | 0 | 0 | 0 | 0 | -0.48 | -0.48 |  |  | 66 | Khleborodnoe | 2.5 | 0.02 | 0.5 | 0 | 0 | 0.5 | 0 | 0 | -0.5 | -0.5 | 35/10
68 | N. Kurlak | 4 | 0.5 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.1 | 0.1 |  |  | 67 | N. Kurlak | 4 | 0 | 0.5 | 0.6 | 120 | -0.1 | 0 | 0.6 | 0.1 | 0.1 | 35/10
69 | Nikolaevka | 4 | 1.46 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.04 | 0.04 |  |  | 68 | Nikolaevka | 4 | 0 | 1.46 | 1.5 | 120 | -0.04 | 0 | 1.5 | 0.04 | 0.04 | 35/10
70 | Vasilyevka BES | 2.5 | 0.33 | 0.39 | 180 | 0.39 | 0 | 0.39 | 0.06 | 0.06 |  |  | 69 | Vasilyevka BES | 2.5 | 0.02 | 0.35 | 0.39 | 180 | -0.04 | 0 | 0.39 | 0.04 | 0.04 | 35/10
71 | Avangard | 2.5 | 0.76 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.15 | 0.15 |  |  | 70 | Avangard | 2.5 | 0.01 | 0.77 | 0.91 | 120 | -0.14 | 0 | 0.91 | 0.14 | 0.14 | 35/10
72 | Orlovka | 2.5 | 0.4 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.08 | 0.08 |  |  | 71 | Orlovka | 2.5 | 0 | 0.4 | 0.48 | 90 | -0.08 | 0 | 0.48 | 0.08 | 0.08 | 35/10
73 | N. Chigla | 2.5 | 0.66 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.24 | 0.24 |  |  | 72 | N. Chigla | 2.5 | 0.15 | 0.81 | 0.9 | 120 | -0.09 | 0 | 0.9 | 0.09 | 0.09 | 35/10
74 | Troitskoe-1 | 1.6 | 0.11 | 0.11 | 120 | 0.11 | 0 | 0.11 | 0 | 0 |  |  | 73 | Troitskoe-1 | 1.6 | 0 | 0.11 | 0.11 | 120 | 0 | 0 | 0.11 | 0 | 0 | 35/10
75 | Tishanka | 2.5 | 1.26 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.25 | 0.25 |  |  | 74 | Tishanka | 2.5 | 0.03 | 1.29 | 1.51 | 120 | -0.22 | 0 | 1.51 | 0.22 | 0.22 | 35/10
| KPN | [11 empty] | 2: KPN
76 | Kalacheevskaya | 6.3 | 0.59 | 1 | 24 hours | 1 | 0 | 1 | 0.41 | 0.41 |  |  | 75 | Kalacheevskaya | 6.3 | 0 | 0.59 | 1 | 24 hours | -0.41 | 0 | 1 | 0.41 | 0.41 | 110/10
77 | B.Kazinka | 6.3 | 0.52 | 0 | 0 | 0 | 0 | 0 | -0.52 | -0.52 |  |  | 76 | B.Kazinka | 6.3 | 3.09 | 3.61 | 0 | 0 | 3.61 | 0 | 0 | -3.61 | -3.61
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110/35/10
| Sн. LV, МVА | 6.3 | 0.52 | 0 | 0 | 0 | 0 | 0 | -0.52 |  |  |  |  | Sн. LV, МVА | 6.3 | 3.09 | 3.61 | 0 | 0 | 3.61 | 0 | 0 | -3.61
78 | Derezovka | 6.3 | 0.34 | 0 | 0 | 0 | 0 | 0 | -0.34 | -0.34 |  |  | 77 | Derezovka | 6.3 | 0.06 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | -0.4 | -0.4 | 110/10
79 | Osetrovka | 6.3 | 0 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.5 | 1.5 |  |  | 78 | Osetrovka | 6.3 | 2.21 | 2.21 | 1.5 | 24 hours | 0.71 | 0 | 1.5 | -0.71 | -0.71 | 110/10
80 | sovkhoz Radchensky | 10 | 1.27 | 2 | 24 hours | 2 | 0 | 2 | 0.73 | -1.14 |  |  | 79 | sovkhoz Radchensky | 10 | 0.01 | 1.28 | 2 | 24 hours | -0.72 | 0 | 2 | 0.72 | -1.14
| Sн. MV, МVА | 10 | 1.14 | 0 | 24 hours | 0 | 0 | 0 | -1.14 |  |  |  |  | Sн. MV, МVА | 10 | 0 | 1.14 | 0 | 0 | 1.14 | 0 | 0 | -1.14 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.13 | 2 | 24 hours | 2 | 0 | 2 | 1.87 |  |  |  |  | Sн. LV, МVА | 10 | 0.01 | 0.14 | 2 | 24 hours | -1.86 | 0 | 2 | 1.86
81 | Klepovka | 4 | 1.37 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.13 | 0.13 |  |  | 80 | Klepovka | 4 | 0.09 | 1.46 | 1.5 | 120 | -0.04 | 0 | 1.5 | 0.04 | 0.04 | 35/10
82 | Krasnopolye | 4 | 0.36 | 1 | 120 | 1 | 0 | 1 | 0.64 | 0.64 |  |  | 81 | Krasnopolye | 4 | 0 | 0.36 | 1 | 120 | -0.64 | 0 | 1 | 0.64 | 0.64 | 35/10
83 | Nikolskoe | 2.5 | 0.46 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.04 | 1.04 |  |  | 82 | Nikolskoe | 2.5 | 0 | 0.46 | 1.5 | 45 | -1.04 | 0 | 1.5 | 1.04 | 1.04 | 35/10
84 | N. Liman | 2.5 | 0.39 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.11 | 1.11 |  |  | 83 | N. Liman | 2.5 | 0.01 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
85 | Bereznyagi | 2.5 | 0.25 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.25 | 1.25 |  |  | 84 | Bereznyagi | 2.5 | 0.03 | 0.28 | 1.5 | 45 | -1.22 | 0 | 1.5 | 1.22 | 1.22 | 35/10
86 | Kr.Flot | 2.5 | 0.26 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.24 | 1.24 |  |  | 85 | Kr.Flot | 2.5 | 0.08 | 0.34 | 1.5 | 45 | -1.16 | 0 | 1.5 | 1.16 | 1.16 | 35/10
87 | R. Zhuravka | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | -0.7 | -0.7 |  |  | 86 | R. Zhuravka | 2.5 | 0.06 | 0.76 | 0 | 0 | 0.76 | 0 | 0 | -0.76 | -0.76 | 35/10
88 | Gorokhovka | 2.5 | 0.54 | 1.5 | 45 | 1.5 | 0 | 1.5 | 0.96 | 0.96 |  |  | 87 | Gorokhovka | 2.5 | 0.04 | 0.58 | 1.5 | 45 | -0.92 | 0 | 1.5 | 0.92 | 0.92 | 35/10
89 | Livenka | 2.5 | 0.44 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0.06 | 0.06 |  |  | 88 | Livenka | 2.5 | 0.05 | 0.49 | 0.5 | 24 hours | -0.01 | 0 | 0.5 | 0.01 | 0.01 | 35/10
90 | R.Buylovka | 2.5 | 0.5 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1 | 1 |  |  | 89 | R.Buylovka | 2.5 | 0.04 | 0.54 | 1.5 | 45 | -0.96 | 0 | 1.5 | 0.96 | 0.96 | 35/10
91 | Shurinovka | 2.5 | 0.31 | 0 | 0 | 0 | 0 | 0 | -0.31 | -0.31 |  |  | 90 | Shurinovka | 2.5 | 0 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | 35/10
92 | Tvyordokhlebovka | 4 | 0.27 | 0 | 0 | 0 | 0 | 0 | -0.27 | -0.27 |  |  | 91 | Tvyordokhlebovka | 4 | 0.02 | 0.29 | 0 | 0 | 0.29 | 0 | 0 | -0.29 | -0.29 | 35/10
93 | Krinitsa | 2.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | -0.25 | -0.25 |  |  | 92 | Krinitsa | 2.5 | 0 | 0.25 | 0 | 0 | 0.25 | 0 | 0 | -0.25 | -0.25 | 35/10
94 | Krasnogorovka | 2.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.1 |  |  | 93 | Krasnogorovka | 2.5 | 0.01 | 0.11 | 0 | 0 | 0.11 | 0 | 0 | -0.11 | -0.11 | 35/10
| Two- and more transformer substations |  | 0.15 | [9 empty] | 2: Two- and more transformer substations
| SPN | [11 empty] | 2: SPN
95 | No.2 | 25+25 | 18.72 | 4.8 | 120 | 13.92 | 0 | 26.25 | 12.33 | 12.33 |  | 1.05 | 95 | No.2 | 25+25 | 11.69 | 30.41 | 4.8 | 120 | 25.61 | 0 | 26.25 | 0.64 | 0.64 | 110/6
96 | No.3 | 6,3 + 10 | 8.89 | 2.5 | 120 | 6.39 | 0 | 6.615 | 0.225 | 0.225 |  | 1.05 | 96 | No.3 | 6,3 + 10 | 0.39 | 9.28 | 2.5 | 120 | 6.78 | 0 | 6.615 | -0.165 | -0.165 | 35/6
97 | No. 4 | 10+10+15 | 14.72 | 0 | 0 | 14.72 | 0 | 21 | 6.28 | 6.28 |  | 1.05 | 97 | No. 4 | 10+10+15 | 0 | 14.72 | 0 | 0 | 14.72 | 0 | 21 | 6.28 | 6.28 | 35/6
98 | No. 6 | 25+32 | 15.85 | 1.6 | 120 | 14.25 | 0 | 26.25 | 12 | 12 |  | 1.05 | 98 | No. 6 | 25+32 | 3.3 | 19.15 | 1.6 | 120 | 17.55 | 0 | 26.25 | 8.7 | 8.7 | 110/6
99 | No. 8 | 4+4+4 | 6.88 | 0 | 0 | 6.88 | 0 | 8.4 | 1.52 | 1.52 |  | 1.05 | 99 | No. 8 | 4+4+4 | 0.34 | 7.22 | 0 | 0 | 7.22 | 0 | 8.4 | 1.18 | 1.18 | 35/6
100 | No. 9 | 16+25 | 23.6 | 3.3 | 120 | 20.3 | 0 | 16.8 | -3.5 | -3.5 |  | 1.05 | 100 | No. 9 | 16+25 | 10.19 | 33.79 | 3.3 | 120 | 30.49 | 0 | 16.8 | -13.69 | -13.69 | 110/6
101 | No. 10 | 20+20 | 30.4 | 13.3 | 120 | 17.1 | 0 | 21 | 3.9 | 3.9 |  | 1.05 | 101 | No. 10 | 20+20 | 7.38 | 37.78 | 13.3 | 120 | 24.48 | 0 | 21 | -3.48 | -3.48 | 35/6
102 | No. 13 | 6,3+6,3 | 9.52 | 1 | 120 | 8.52 | 0 | 6.615 | -1.905 | -1.905 |  | 1.05 | 102 | No. 13 | 6,3+6,3 | 3.09 | 12.61 | 4.2 | 120 | 8.41 | 0 | 6.615 | -1.795 | -1.795 | 35/10
103 | No. 14 | 31,5+31,5 | 16.06 | 1.3 | 120 | 14.76 | 0 | 33.075 | 18.315 | 18.315 |  | 1.05 | 103 | No. 14 | 31,5+31,5 | 0.54 | 16.6 | 1.3 | 120 | 15.3 | 0 | 33.075 | 17.775 | 17.775
| Sн. MV, МVА | 31,5+31,5 | 1.34 | 0 | 0 | 1.34 | 0 | 33.075 | 31.735 |  |  | 1.05 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 1.34 | 0 | 0 | 1.34 | 0 | 33.075 | 31.735 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5 | 14.72 | 1.3 | 120 | 13.42 | 0 | 33.075 | 19.655 |  |  | 1.05 |  | Sн. LV, МVА | 31,5+31,5 | 0.54 | 15.26 | 1.3 | 120 | 13.96 | 0 | 33.075 | 19.115
104 | No. 15 | 40,5+40,5+63,0 | 44.01 | 44.01 | 120 | 0 | 0 | 85.05 | 85.05 | 84.96 |  | 1.05 | 104 | No. 15 | 40,5+40,5+63,0 | 0.59 | 44.6 | 44.01 | 120 | 0.59 | 0 | 85.05 | 84.46 | 84.46
| Sн. MV, МVА | 40,5+40,5+63,0 | 44.1 | 44.01 | 120 | 0.09 | 0 | 85.05 | 84.96 |  |  | 1.05 |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 44.1 | 44.01 | 120 | 0.09 | 0 | 85.05 | 84.96 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  | 1.05 |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0.59 | 0.59 | 0 | 0 | 0.59 | 0 | 85.05 | 84.46
105 | No. 16 | 31,5+31,5+40,0 | 59.26 | 4 | 120 | 55.26 | 0 | 66.15 | 10.89 | 10.89 |  | 1.05 | 105 | No. 16 | 31,5+31,5+40,0 | 7.41 | 66.67 | 4 | 120 | 62.67 | 0 | 66.15 | 3.48 | 3.48
| Sн. MV, МVА | 31,5+31,5 | 10 | 0 | 0 | 10 | 0 | 33.075 | 23.075 |  |  | 1.05 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 10 | 0 | 0 | 10 | 0 | 33.075 | 23.075 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5+40,0 | 49.26 | 4 | 120 | 45.26 | 0 | 66.15 | 20.89 |  |  | 1.05 |  | Sн. LV, МVА | 31,5+31,5+40,0 | 7.41 | 56.67 | 4 | 120 | 52.67 | 0 | 66.15 | 13.48
106 | No. 18 | 6,3+6,3 | 2.19 | 0 | 0 | 2.19 | 0 | 6.615 | 4.425 | 4.425 |  | 1.05 | 106 | No. 18 | 6,3+6,3 | 0.13 | 2.32 | 0 | 0 | 2.32 | 0 | 6.615 | 4.295 | 4.295 | 110/10
107 | No. 20 | 25,0+6,3+16 | 18.74 | 5.6 | 120 | 13.14 | 0 | 26.25 | 13.11 | -3.025 |  | 1.05 | 107 | No. 20 | 25,0+6,3+16 | 2.22 | 20.96 | 5.6 | 120 | 15.36 | 0 | 26.25 | 10.89 | -5.245
| Sн. MV, МVА | 25,0+16,0 | 3.5 | 0 | 0 | 3.5 | 0 | 26.25 | 22.75 |  |  | 1.05 |  | Sн. MV, МVА | 25+16 | 0 | 3.5 | 0 | 0 | 3.5 | 0 | 26.25 | 22.75 |  | 110/35/10/6
| Sн. LV, МVА | 25,0+6,3 | 15.24 | 5.6 | 120 | 9.64 | 0 | 6.615 | -3.025 |  |  | 1.05 |  | Sн. LV, МVА | 25+6,3 | 2.22 | 17.46 | 5.6 | 120 | 11.86 | 0 | 6.615 | -5.245
108 | No. 21 | 25,0+20,0+40,0 | 37.18 | 4.6 | 120 | 32.58 | 0 | 45 | 12.42 | 12.42 |  | 1.05 | 108 | No. 21 | 25,0+20,0+40,0 | 20.03 | 57.21 | 4.6 | 180 | 52.61 | 0 | 45 | -7.61 | -7.61 | 110/35/6
109 | No. 22 | 10+10 | 4.7 | 1.4 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 |  | 1.05 | 109 | No. 22 | 10+10 | 2.69 | 7.39 | 1.4 | 120 | 5.99 | 0 | 10.5 | 4.51 | 4.51 | 35/6
110 | No. 23 | 7,5+6,3 | 6.82 | 0.8 | 120 | 6.02 | 0 | 6.615 | 0.595 | 0.595 |  | 1.05 | 110 | No. 23 | 7,5+6,3 | 0.75 | 7.57 | 0.8 | 120 | 6.77 | 0 | 6.615 | -0.155 | -0.155 | 35/6
111 | No. 24 | 3,2+4,0 | 1.97 | 0 | 0 | 1.97 | 0 | 3.36 | 1.39 | 1.39 |  | 1.05 | 111 | No. 24 | 3,2+4,0 | 0.04 | 2.01 | 0 | 0 | 2.01 | 0 | 3.36 | 1.35 | 1.35 | 35/6
112 | No. 25 | 40+25 | 39.18 | 3.8 | 120 | 35.38 | 0 | 26.25 | -9.13 | -9.13 |  | 1.05 | 112 | No. 25 | 40+25 | 8.26 | 47.44 | 3.8 | 120 | 43.64 | 0 | 26.25 | -17.39 | -17.39 | 110/6
113 | No. 27 | 32,0+32,0+32,0 | 38.9 | 3.3 | 180 | 35.6 | 0 | 67.2 | 31.6 | 31.6 |  | 1.05 | 113 | No. 27 | 32,0+32,0+32,0 | 17.48 | 56.38 | 3.3 | 180 | 53.08 | 0 | 67.2 | 14.12 | 14.12 | 110/6
114 | No. 28 | 10+10 | 12 | 0 | 0 | 12 | 0 | 10.5 | -1.5 | -1.5 |  | 1.05 | 114 | No. 28 | 10+10 | 3.45 | 15.45 | 0 | 0 | 15.45 | 0 | 10.5 | -4.95 | -4.95 | 110/10
115 | No.29 | 25+25 | 27.75 | 8.4 | 120 | 19.35 | 0 | 26.25 | 6.9 | 6.9 |  | 1.05 | 115 | No.29 | 25+25 | 3.8 | 31.55 | 8.4 | 120 | 23.15 | 0 | 26.25 | 3.1 | 3.1
| Sн. MV, МVА | 25+25 | 11.7 | 4.2 | 120 | 7.5 | 0 | 26.25 | 18.75 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 11.7 | 4.2 | 120 | 7.5 | 0 | 26.25 | 18.75 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 16.05 | 4.2 | 120 | 11.85 | 0 | 26.25 | 14.4 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 3.8 | 19.85 | 4.2 | 120 | 15.65 | 0 | 26.25 | 10.6
116 | No. 30 | 40+40 | 70.53 | 5.1 | 120 | 65.43 | 0 | 42 | -23.43 | -23.43 |  | 1.05 | 116 | No. 30 | 40+40 | 16.72 | 87.25 | 5.1 | 120 | 82.15 | 0 | 42 | -40.15 | -40.15
| Sн. MV, МVА | 40+40 | 12 | 0 | 0 | 12 | 0 | 42 | 30 |  |  | 1.05 |  | Sн. MV, МVА | 40+40 | 0 | 12 | 0 | 0 | 12 | 0 | 42 | 30 |  | 110/35/10
| Sн. LV, МVА | 40+40 | 58.53 | 5.1 | 120 | 53.43 | 0 | 42 | -11.43 |  |  | 1.05 |  | Sн. LV, МVА | 40+40 | 16.72 | 75.25 | 5.1 | 120 | 70.15 | 0 | 42 | -28.15
117 | No. 32 | 10+16 | 18.27 | 8 | 120 | 10.27 | 0 | 10.5 | 0.23 | 0.23 |  | 1.05 | 117 | No. 32 | 10+16 | 0.96 | 19.23 | 8 | 120 | 11.23 | 0 | 10.5 | -0.73 | -0.73
| Sн. MV, МVА | 10+16 | 15.6 | 8 | 120 | 7.6 | 0 | 10.5 | 2.9 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 15.6 | 8 | 120 | 7.6 | 0 | 10.5 | 2.9 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 2.67 | 0 | 0 | 2.67 | 0 | 10.5 | 7.83 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.96 | 3.63 | 0 | 0 | 3.63 | 0 | 10.5 | 6.87
118 | No. 33 | 4,0+4,0 | 1.55 | 0 | 0 | 1.55 | 0 | 4.2 | 2.65 | 2.65 |  | 1.05 | 118 | No. 33 | 4,0+4,0 | 0.3 | 1.85 | 0 | 0 | 1.85 | 0 | 4.2 | 2.35 | 2.35 | 35/10
119 | No. 34 | 2,5+1,8 | 2.32 | 0 | 0 | 2.32 | 0 | 1.89 | -0.43 | -0.43 |  | 1.05 | 119 | No. 34 | 2,5+1,8 | 0 | 2.32 | 0 | 0 | 2.32 | 0 | 1.89 | -0.43 | -0.43 | 35/6
120 | No.35 | 10+10 | 13.1 | 2.4 | 120 | 10.7 | 0 | 10.5 | -0.2 | -0.2 |  | 1.05 | 120 | No.35 | 10+10 | 0 | 13.1 | 2.4 | 120 | 10.7 | 0 | 10.5 | -0.2 | -0.2 | 35/6
121 | No. 36 | 6,3+10 | 1.33 | 0 | 0 | 1.33 | 0 | 6.615 | 5.285 | 5.285 |  | 1.05 | 121 | No. 36 | 6,3+10 | 3.5 | 4.83 | 0 | 0 | 4.83 | 0 | 6.615 | 1.785 | 1.785 | 110/35/10
122 | No. 39 | 25+25 | 27.82 | 7.1 | 120 | 20.72 | 0 | 26.25 | 5.53 | 5.53 |  | 1.05 | 122 | No. 39 | 25+25 | 2.95 | 30.77 | 4.1 | 120 | 26.67 | 0 | 26.25 | -0.42 | -0.42 | 110/6
123 | No. 41 | 10+10 | 10.6 | 0 | 0 | 10.6 | 0 | 10.5 | -0.1 | -0.1 |  | 1.05 | 123 | No. 41 | 10+10 | 0 | 10.6 | 0 | 0 | 10.6 | 0 | 10.5 | -0.1 | -0.1 | 35/6
124 | No. 42 | 25+40 | 16.59 | 1.6 | 120 | 14.99 | 0 | 26.25 | 11.26 | 11.26 |  | 1.05 | 124 | No. 42 | 25+40 | 9.01 | 25.6 | 1.6 | 120 | 24 | 0 | 26.25 | 2.25 | 2.25 | 110/6
125 | No. 43 | 63+63 | 18.63 | 1.6 | 60 | 17.03 | 0 | 66.15 | 49.12 | 49.12 |  | 1.05 | 125 | No. 43 | 63+63 | 8.24 | 26.87 | 1.6 | 60 | 25.27 | 0 | 66.15 | 40.88 | 40.88 | 110/6
126 | No. 45 | 63+63 | 27.28 | 7.1 | 120 | 20.18 | 0 | 66.15 | 45.97 | 45.97 |  | 1.05 | 126 | No. 45 | 63+63 | 28.71 | 55.99 | 7.1 | 120 | 48.89 | 0 | 66.15 | 17.26 | 17.26 | 110/6
127 | No. 47 | 25+25 | 13.46 | 0 | 0 | 13.46 | 0 | 26.25 | 12.79 | 12.79 |  | 1.05 | 127 | No. 47 | 25+25 | 0.03 | 13.49 | 0 | 0 | 13.49 | 0 | 26.25 | 12.76 | 12.76
| Sн. MV, МVА | 25+25 | 8.1 | 0 | 0 | 8.1 | 0 | 26.25 | 18.15 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 8.1 | 0 | 0 | 8.1 | 0 | 26.25 | 18.15 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 5.36 | 0 | 0 | 5.36 | 0 | 26.25 | 20.89 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.03 | 5.39 | 0 | 0 | 5.39 | 0 | 26.25 | 20.86
128 | Panino | 16+16 | 10.72 | 5.2 | 120 | 5.52 | 0 | 16.8 | 11.28 | 10.68 |  | 1.05 | 128 | Panino | 16+16 | 0.22 | 10.94 | 5.2 | 120 | 5.74 | 0 | 16.8 | 11.06 | 10.46
| Sн. MV, МVА | 16+16 | 4.4 | 5 | 120 | -0.6 | 0 | 16.8 | 17.4 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 4.4 | 5 | 120 | -0.6 | 0 | 16.8 | 17.4 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 6.32 | 0.2 | 120 | 6.12 | 0 | 16.8 | 10.68 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.22 | 6.54 | 0.2 | 120 | 6.34 | 0 | 16.8 | 10.46
129 | Kriusha | 2,5+2,5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 |  | 1.05 | 129 | Kriusha | 2,5+2,5 | 0.03 | 1 | 0 | 0 | 1 | 0 | 2.625 | 1.625 | 1.625 | 35/10
130 | Seed plant | 4+4 | 1.65 | 0 | 0 | 1.65 | 0 | 4.2 | 2.55 | 2.55 |  | 1.05 | 130 | Seed plant | 4+4 | 0.02 | 1.67 | 0 | 0 | 1.67 | 0 | 4.2 | 2.53 | 2.53 | 35/10
131 | Progress | 2,5+10 | 0.51 | 0.5315 | 120 | -0.0215 | 0 | 2.625 | 2.6465 | 2.6465 |  | 1.05 | 131 | Progress | 2,5+10 | 0.01 | 0.52 | 0.5315 | 120 | -0.0115 | 0 | 2.625 | 2.6365 | 2.6365 | 110/35/10
132 | Katukhovka | 2,5+2,5 | 0.38 | 0.385 | 120 | -0.005 | 0 | 2.625 | 2.63 | 2.63 |  | 1.05 | 132 | Katukhovka | 2,5+2,5 | 0.01 | 0.39 | 0.385 | 120 | 0.005 | 0 | 2.625 | 2.62 | 2.62 | 35/10
133 | Kr.Liman | 2,5+4,0 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 |  | 1.05 | 133 | Kr.Liman | 2,5+4,0 | 0.01 | 0.89 | 0 | 0 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | 35/10
134 | Ivanovka | 1,8+1,6 | 0.36 | 0.36 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 |  | 1.05 | 134 | Ivanovka | 1,8+1,6 | 0 | 0.36 | 0.36 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | 35/10
135 | Don | 2,5+2,5 | 2.85 | 0 | 0 | 2.85 | 0 | 2.625 | -0.225 | -0.225 |  | 1.05 | 135 | Don | 2,5+2,5 | 0.39 | 3.24 | 0 | 0 | 3.24 | 0 | 2.625 | -0.615 | -0.615 | 35/10
136 | Yablochnoe | 4+4 | 0.27 | 0 | 0 | 0.27 | 0 | 4.2 | 3.93 | 3.93 |  | 1.05 | 136 | Yablochnoe | 4+4 | 0.01 | 0.28 | 0 | 0 | 0.28 | 0 | 4.2 | 3.92 | 3.92 | 35/10
137 | St.Nikolskoe | 2,5+2,5 | 0.95 | 1.227 | 120 | -0.277 | 0 | 2.625 | 2.902 | 2.902 |  | 1.05 | 137 | St.Nikolskoe | 2,5+2,5 | 0.3 | 1.25 | 1.227 | 120 | 0.023 | 0 | 2.625 | 2.602 | 2.602 | 35/10
138 | Rudkino | 4,0+4,0 | 2.27 | 0 | 0 | 2.27 | 0 | 4.2 | 1.93 | 1.93 |  | 1.05 | 138 | Rudkino | 4,0+4,0 | 0.08 | 2.35 | 0 | 0 | 2.35 | 0 | 4.2 | 1.85 | 1.85 | 35/10
139 | Khokhol-1 | 6,3+6,3 | 4.96 | 0 | 0 | 4.96 | 0 | 6.615 | 1.655 | 1.655 |  | 1.05 | 139 | Khokhol-1 | 6,3+6,3 | 1.22 | 6.18 | 0 | 0 | 6.18 | 0 | 6.615 | 0.435 | 0.435 | 35/6
140 | No. 11 | 5,6+6,3 | 2.53 | 0.5 | 120 | 2.03 | 0 | 5.88 | 3.85 | 3.85 |  | 1.05 | 140 | No. 11 | 5,6+6,3 | 0 | 2.53 | 0.5 | 120 | 2.03 | 0 | 5.88 | 3.85 | 3.85
| Sн. MV, МVА | 5,6+6,3 | 0.5 | 0.5 | 120 | 0 | 0 | 5.88 | 5.88 |  |  | 1.05 |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 5.88 | 5.88 |  | 110/35/6
| Sн. LV, МVА | 5,6+6,3 | 2.03 | 0 | 0 | 2.03 | 0 | 5.88 | 3.85 |  |  | 1.05 |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.03 | 0 | 0 | 2.03 | 0 | 5.88 | 3.85
141 | Beryozovka | 4+4 | 3.22 | 0 | 0 | 3.22 | 0 | 4.2 | 0.98 | 0.98 |  | 1.05 | 141 | Beryozovka | 4+4 | 0.09 | 3.31 | 0 | 0 | 3.31 | 0 | 4.2 | 0.89 | 0.89 | 35/10
142 | N.Zhivotinnoe | 6,3+6,3 | 3.54 | 1 | 120 | 2.54 | 0 | 6.615 | 4.075 | 4.075 |  | 1.05 | 142 | N.Zhivotinnoe | 6,3+6,3 | 1.52 | 5.06 | 1 | 120 | 4.06 | 0 | 6.615 | 2.555 | 2.555 | 35/10
143 | Ramon-1 | 4+4+4 | 5.95 | 6.85 | 120 | -0.9 | 0 | 8.4 | 9.3 | 9.3 |  | 1.05 | 143 | Ramon-1 | 4+4+4 | 0.86 | 6.81 | 6.85 | 120 | -0.04 | 0 | 8.4 | 8.44 | 8.44 | 35/10/6
144 | Ramon-2 | 16,0+16,0 | 17.43 | 10.48 | 120 | 6.95 | 0 | 16.8 | 9.85 | 9.85 |  | 1.05 | 144 | Ramon-2 | 16,0+16,0 | 4.87 | 22.3 | 10.48 | 120 | 11.82 | 0 | 16.8 | 4.98 | 4.98
| Sн. MV, МVА | 16,0+16,0 | 13.8 | 6.85 | 0 | 6.95 | 0 | 16.8 | 9.85 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 13.8 | 6.85 | 0 | 6.95 | 0 | 16.8 | 9.85 |  | 110/35/10
| Sн. LV, МVА | 16,0+16,0 | 3.63 | 3.63 | 120 | 0 | 0 | 16.8 | 16.8 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 4.87 | 8.5 | 3.63 | 120 | 4.87 | 0 | 16.8 | 11.93
145 | Vereyka | 2,5+2,5 | 1.26 | 0 | 0 | 1.26 | 0 | 2.625 | 1.365 | 1.365 |  | 1.05 | 145 | Vereyka | 2,5+2,5 | 0.01 | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | 35/10
146 | Complex | 10+10 | 5.24 | 3.4 | 180 | 1.84 | 0 | 10.5 | 8.66 | 8.36 |  | 1.05 | 146 | Complex | 10+10 | 0 | 5.24 | 3.4 | 180 | 1.84 | 0 | 10.5 | 8.66 | 8.36
| Sн. MV, МVА | 10+10 | 2.8 | 3.1 | 180 | -0.3 | 0 | 10.5 | 10.8 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.8 | 3.1 | 180 | -0.3 | 0 | 10.5 | 10.8 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.44 | 0.3 | 180 | 2.14 | 0 | 10.5 | 8.36 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0 | 2.44 | 0.3 | 180 | 2.14 | 0 | 10.5 | 8.36
147 | N.Veduga | 16+16 | 4.54 | 2.9 | 120 | 1.64 | 0 | 16.8 | 15.16 | 15.16 |  | 1.05 | 147 | N.Veduga | 16+16 | 0 | 4.54 | 2.9 | 120 | 1.64 | 0 | 16.8 | 15.16 | 15.16
| Sн. MV, МVА | 16+16 | 2.9 | 2.9 | 120 | 0 | 0 | 16.8 | 16.8 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 2.9 | 2.9 | 120 | 0 | 0 | 16.8 | 16.8 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.64 | 0 | 0 | 1.64 | 0 | 16.8 | 15.16 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0 | 1.64 | 0 | 0 | 1.64 | 0 | 16.8 | 15.16
148 | Golosnovka | 2,5+2,5 | 0.49 | 0.512 | 120 | -0.022 | 0 | 2.625 | 2.647 | 2.647 |  | 1.05 | 148 | Golosnovka | 2,5+2,5 | 0.02 | 0.51 | 0.512 | 120 | -0.002 | 0 | 2.625 | 2.627 | 2.627 | 35/10
149 | Medvezhye | 3,2+4,0 | 1.11 | 0 | 0 | 1.11 | 0 | 3.36 | 2.25 | 2.25 |  | 1.05 | 149 | Medvezhye | 3,2+4,0 | 0.11 | 1.22 | 0 | 0 | 1.22 | 0 | 3.36 | 2.14 | 2.14 | 35/10
150 | St.Veduga | 4+4 | 1.22 | 0 | 0 | 1.22 | 0 | 4.2 | 2.98 | 2.98 |  | 1.05 | 150 | St.Veduga | 4+4 | 0.03 | 1.25 | 0 | 0 | 1.25 | 0 | 4.2 | 2.95 | 2.95 | 35/10
151 | M.Pokrovka | 2,5+2,5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 |  | 1.05 | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.57 | 0 | 0 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | 35/10
152 | V.Turovo-2 | 2,5+2,5 | 1.2 | 0.7 | 120 | 0.5 | 0 | 2.625 | 2.125 | 2.125 |  | 1.05 | 152 | V.Turovo-2 | 2,5+2,5 | 0.06 | 1.26 | 0.7 | 120 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | 35/10
153 | S.Lipyagi | 3,2+2,5 | 1.4 | 2.9638 | 120 | -1.5638 | 0 | 2.625 | 4.1888 | 4.1888 |  | 1.05 | 153 | S.Lipyagi | 3,2+2,5 | 1.69 | 3.09 | 2.9638 | 120 | 0.1262 | 0 | 2.625 | 2.4988 | 2.4988 | 35/10
154 | N.Devitsk | 25+16 | 5.77 | 8.2225 | 180 | -2.4525 | 0 | 16.8 | 19.2525 | 16.8 |  | 1.05 | 154 | N.Devitsk | 25+16 | 2.66 | 8.43 | 8.2225 | 180 | 0.2075 | 0 | 16.8 | 16.5925 | 16.563
| Sн. MV, МVА | 25+16 | 2.8 | 2.8 | 180 | 0 | 0 | 16.8 | 16.8 |  |  | 1.05 |  | Sн. MV, МVА | 25+16 | 0 | 2.8 | 2.8 | 180 | 0 | 0 | 16.8 | 16.8 |  | 110/35/10
| Sн. LV, МVА | 25+16 | 2.97 | 5.393 | 180 | -2.423 | 0 | 16.8 | 19.223 |  |  | 1.05 |  | Sн. LV, МVА | 25+16 | 2.66 | 5.63 | 5.393 | 180 | 0.237 | 0 | 16.8 | 16.563
155 | Repyevka | 4+4 | 2.68 | 0.5 | 120 | 2.18 | 0 | 4.2 | 2.02 | 2.02 |  | 1.05 | 155 | Repyevka | 4+4 | 0.02 | 2.7 | 0.5 | 120 | 2.2 | 0 | 4.2 | 2 | 2 | 35/10
156 | Krasnolipye | 16+16 | 11.22 | 2.9 | 120 | 8.32 | 0 | 16.8 | 8.48 | 8.48 |  | 1.05 | 156 | Krasnolipye | 16+16 | 0.03 | 11.25 | 2.9 | 120 | 8.35 | 0 | 16.8 | 8.45 | 8.45
| Sн. MV, МVА | 16+16 | 9.7 | 2.7 | 120 | 7 | 0 | 16.8 | 9.8 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 9.7 | 2.7 | 120 | 7 | 0 | 16.8 | 9.8 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.52 | 0.2 | 120 | 1.32 | 0 | 16.8 | 15.48 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.03 | 1.55 | 0.2 | 120 | 1.35 | 0 | 16.8 | 15.45
157 | Ulyanovka | 6,3+6,3 | 0.44 | 0.04 | 60 | 0.4 | 0 | 6.615 | 6.215 | 6.215 |  | 1.05 | 157 | Ulyanovka | 6,3+6,3 | 0.03 | 0.47 | 0.04 | 60 | 0.43 | 0 | 6.615 | 6.185 | 6.185 | 110/10
158 | МОB | 4+2,5 | 1.16 | 0.6 | 60 | 0.56 | 0 | 2.625 | 2.065 | 2.065 |  | 1.05 | 158 | МОB | 4+2,5 | 0.08 | 1.24 | 0.6 | 60 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | 35/10
159 | L.Rossosh | 6,3+6,3 | 4.34 | 0 | 0 | 4.34 | 0 | 6.615 | 2.275 | 2.275 |  | 1.05 | 159 | L.Rossosh | 6,3+6,3 | 0.24 | 4.58 | 0 | 0 | 4.58 | 0 | 6.615 | 2.035 | 2.035 | 35/10
160 | Kashirskoe | 2,5+2,5 | 0.67 | 0 | 0 | 0.67 | 0 | 2.625 | 1.955 | 1.955 |  | 1.05 | 160 | Kashirskoe | 2,5+2,5 | 0.05 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | 35/10
161 | Zaprudskoe | 2,5+2,5 | 1.62 | 0 | 0 | 1.62 | 0 | 2.625 | 1.005 | 1.005 |  | 1.05 | 161 | Zaprudskoe | 2,5+2,5 | 0.13 | 1.75 | 0 | 0 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | 35/10
162 | Moskovskoe | 10+10 | 11.48 | 1.8 | 120 | 9.68 | 0 | 10.5 | 0.82 | 0.1 |  | 1.05 | 162 | Moskovskoe | 10+10 | 0.02 | 11.5 | 1.8 | 120 | 9.7 | 0 | 10.5 | 0.8 | 0.1
| Sн. MV, МVА | 10+10 | 10.4 | 0 | 0 | 10.4 | 0 | 10.5 | 0.1 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 10.4 | 0 | 0 | 10.4 | 0 | 10.5 | 0.1 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.88 | 1.8 | 120 | -0.92 | 0 | 10.5 | 11.42 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.02 | 0.9 | 1.8 | 120 | -0.9 | 0 | 10.5 | 11.4
163 | Semenovka SES | 2,5+4,0 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 |  | 1.05 | 163 | Semenovka SES | 2,5+4,0 | 0.01 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | 35/10
164 | N. Baygora | 2,5+2,5 | 1.01 | 1.03 | 60 | -0.02 | 0 | 2.625 | 2.645 | 2.645 |  | 1.05 | 164 | N. Baygora | 2,5+2,5 | 0.02 | 1.03 | 1.03 | 60 | 0 | 0 | 2.625 | 2.625 | 2.625 | 35/10
165 | Shukaevka | 2,5+2,5 | 0.9 | 0.1 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 |  | 1.05 | 165 | Shukaevka | 2,5+2,5 | 0.03 | 0.93 | 0.1 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | 35/10
166 | Uglyanets | 4+2,5 | 2.91 | 0.8 | 120 | 2.11 | 0 | 2.625 | 0.515 | 0.515 |  | 1.05 | 166 | Uglyanets | 4+2,5 | 0.11 | 3.02 | 0.8 | 120 | 2.22 | 0 | 2.625 | 0.405 | 0.405 | 35/10
167 | V.Khava | 16+16 | 12.88 | 0.4 | 120 | 12.48 | 0 | 16.8 | 4.32 | 4.32 |  | 1.05 | 167 | V.Khava | 16+16 | 0.27 | 13.15 | 0.4 | 120 | 12.75 | 0 | 16.8 | 4.05 | 4.05
| Sн. MV, МVА | 16+16 | 5.7 | 0 | 0 | 5.7 | 0 | 16.8 | 11.1 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 16.8 | 11.1 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 7.18 | 0.4 | 120 | 6.78 | 0 | 16.8 | 10.02 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.27 | 7.45 | 0.4 | 120 | 7.05 | 0 | 16.8 | 9.75
168 | N. Usman-1 | 10,0+6,3 | 11.25 | 0 | 0 | 11.25 | 0 | 6.615 | -4.635 | -4.635 |  | 1.05 | 168 | N. Usman-1 | 10,0+6,3 | 5.14 | 16.39 | 0 | 0 | 16.39 | 0 | 6.615 | -9.775 | -9.775 | 35/10
169 | N. Usman-2 | 4+6,3 | 9.35 | 0 | 0 | 9.35 | 0 | 4.2 | -5.15 | -5.15 |  | 1.05 | 169 | N. Usman-2 | 4+6,3 | 1.71 | 11.06 | 0 | 0 | 11.06 | 0 | 4.2 | -6.86 | -6.86 | 35/10
170 | R.Khava | 4+4 | 3.01 | 0.2 | 120 | 2.81 | 0 | 4.2 | 1.39 | 1.39 |  | 1.05 | 170 | R.Khava | 4+4 | 0.08 | 3.09 | 0.2 | 120 | 2.89 | 0 | 4.2 | 1.31 | 1.31 | 35/10
171 | No. 31 | 16+25 | 23.15 | 5.6 | 120 | 17.55 | 0 | 16.8 | -0.75 | -0.75 |  | 1.05 | 171 | No. 31 | 16+25 | 0.18 | 23.33 | 5.6 | 120 | 17.73 | 0 | 16.8 | -0.93 | -0.93
| Sн. MV, МVА | 16+25 | 15 | 5.6 | 120 | 9.4 | 0 | 16.8 | 7.4 |  |  | 1.05 |  | Sн. MV, МVА | 16+25 | 0 | 15 | 5.6 | 120 | 9.4 | 0 | 16.8 | 7.4 |  | 110/35/10
| Sн. LV, МVА | 16+25 | 8.15 | 0 | 0 | 8.15 | 0 | 16.8 | 8.65 |  |  | 1.05 |  | Sн. LV, МVА | 16+25 | 0.18 | 8.33 | 0 | 0 | 8.33 | 0 | 16.8 | 8.47
172 | Maslovka | 2,5+4,0 | 2.25 | 0 | 0 | 2.25 | 0 | 2.625 | 0.375 | 0.375 |  | 1.05 | 172 | Maslovka | 2,5+4,0 | 0.36 | 2.61 | 0 | 0 | 2.61 | 0 | 2.625 | 0.015 | 0.015 | 35/10
| LPN | [11 empty] | 2: LPN
173 | Podgornaya - district Line Maintenance Service | 16+16 | 3.91 | 1.6 | 180 | 2.31 | 0 | 16.8 | 14.49 | 14.49 |  | 1.05 | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 0.47 | 4.38 | 1.6 | 180 | 2.78 | 0 | 16.8 | 14.02 | 14.02
| Sн. MV, МVА | 16+16 | 2 | 1.05 | 180 | 0.95 | 0 | 16.8 | 15.85 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 2 | 1.05 | 180 | 0.95 | 0 | 16.8 | 15.85 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.91 | 0.55 | 180 | 1.36 | 0 | 16.8 | 15.44 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.47 | 2.38 | 0.55 | 180 | 1.83 | 0 | 16.8 | 14.97
174 | Kantemirovka | 10+10 | 8.11 | 1.6 | 60 | 6.51 | 0 | 10.5 | 3.99 | 3.99 |  | 1.05 | 174 | Kantemirovka | 10+10 | 0.98 | 9.09 | 1.6 | 60 | 7.49 | 0 | 10.5 | 3.01 | 3.01
| Sн. MV, МVА | 10+10 | 5.4 | 1.4 | 60 | 4 | 0 | 10.5 | 6.5 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 5.4 | 1.4 | 60 | 4 | 0 | 10.5 | 6.5 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.71 | 0.2 | 60 | 2.51 | 0 | 10.5 | 7.99 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.98 | 3.69 | 0.2 | 60 | 3.49 | 0 | 10.5 | 7.01
175 | Rossosh | 16+16+40 | 21.3 | 2.68 | 120 | 18.62 | 0 | 33.6 | 14.98 | 14.98 |  | 1.05 | 175 | Rossosh | 16+16+40 | 0.35 | 21.65 | 2.68 | 120 | 18.97 | 0 | 33.6 | 14.63 | 14.63
| Sн. MV, МVА | 16+16+40 | 3.2 | 1.9 | 120 | 1.3 | 0 | 33.6 | 32.3 |  |  | 1.05 |  | Sн. MV, МVА | 16+16+40 | 0 | 3.2 | 1.9 | 120 | 1.3 | 0 | 33.6 | 32.3 |  | 110/35/10/6
| Sн. LV, МVА | 16+16+40 | 18.1 | 0.78 | 120 | 17.32 | 0 | 33.6 | 16.28 |  |  | 1.05 |  | Sн. LV, МVА | 16+16+40 | 0.35 | 18.45 | 0.78 | 120 | 17.67 | 0 | 33.6 | 15.93
176 | Kamenka r-naya | 16+16 | 3.25 | 0.97 | 120 | 2.28 | 0 | 16.8 | 14.52 | 14.52 |  | 1.05 | 176 | Kamenka r-naya | 16+16 | 0.27 | 3.52 | 0.97 | 120 | 2.55 | 0 | 16.8 | 14.25 | 14.25
| Sн. MV, МVА | 16+16 | 0.61 | 0 | 120 | 0.61 | 0 | 16.8 | 16.19 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 0.61 | 0 | 120 | 0.61 | 0 | 16.8 | 16.19 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.64 | 0.97 | 120 | 1.67 | 0 | 16.8 | 15.13 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.27 | 2.91 | 0.97 | 120 | 1.94 | 0 | 16.8 | 14.86
177 | Korotoyak | 6,3+10 | 3.35 | 0.47 | 180 | 2.88 | 0 | 6.615 | 3.735 | 3.735 |  | 1.05 | 177 | Korotoyak | 6,3+10 | 0.37 | 3.72 | 0.47 | 180 | 3.25 | 0 | 6.615 | 3.365 | 3.365
| Sн. MV, МVА | 6,3+10 | 1.44 | 0 | 180 | 1.44 | 0 | 6.615 | 5.175 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+10 | 0 | 1.44 | 0 | 180 | 1.44 | 0 | 6.615 | 5.175 |  | 110/35/10
| Sн. LV, МVА | 6,3+10 | 1.91 | 0.47 | 180 | 1.44 | 0 | 6.615 | 5.175 |  |  | 1.05 |  | Sн. LV, МVА | 6,3+10 | 0.37 | 2.28 | 0.47 | 180 | 1.81 | 0 | 6.615 | 4.805
178 | Ostrogozhsk | 40,5+40,5 | 12.84 | 2.4 | 60 | 10.44 | 0 | 42.525 | 32.085 | 32.085 |  | 1.05 | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 12.84 | 2.4 | 60 | 10.44 | 0 | 42.525 | 32.085 | 32.085
| Sн. MV, МVА | 40,5+40,5 | 12.63 | 2.4 | 60 | 10.23 | 0 | 42.525 | 32.295 |  |  | 1.05 |  | Sн. MV, МVА | 40,5+40,5 | 0 | 12.63 | 2.4 | 60 | 10.23 | 0 | 42.525 | 32.295 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5 | 0.21 | 0 | 60 | 0.21 | 0 | 42.525 | 42.315 |  |  | 1.05 |  | Sн. LV, МVА | 40,5+40,5 | 0 | 0.21 | 0 | 60 | 0.21 | 0 | 42.525 | 42.315
179 | Khrenovoe | 16+6,3 | 3.91 | 0 | 0 | 3.91 | 0 | 6.615 | 2.705 | 2.705 |  | 1.05 | 179 | Khrenovoe | 16+6,3 | 0.05 | 3.96 | 0 | 0 | 3.96 | 0 | 6.615 | 2.655 | 2.655
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 |  | Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  | 110/35/10
| Sн. LV, МVА | 16+6,3 | 3.91 | 0 | 0 | 3.91 | 0 | 6.615 | 2.705 |  |  | 1.05 |  | Sн. LV, МVА | 16+6,3 | 0.05 | 3.96 | 0 | 0 | 3.96 | 0 | 6.615 | 2.655
180 | Oil extraction plant | 25+25 | 20 | 7.9 | 120 | 12.1 | 0 | 26.25 | 14.15 | 14.15 |  | 1.05 | 180 | Oil extraction plant | 25+25 | 0.06 | 20.06 | 7.9 | 120 | 12.16 | 0 | 26.25 | 14.09 | 14.09
| Sн. MV, МVА | 25+25 | 7.9 | 7.9 | 120 | 0 | 0 | 26.25 | 26.25 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 7.9 | 7.9 | 120 | 0 | 0 | 26.25 | 26.25 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 12.1 | 0 | 0 | 12.1 | 0 | 26.25 | 14.15 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.06 | 12.16 | 0 | 0 | 12.16 | 0 | 26.25 | 14.09
181 | ANP | 6,3+6,3 | 1.35 | 0.39 | 120 | 0.96 | 0 | 6.615 | 5.655 | 5.655 |  | 1.05 | 181 | ANP | 6,3+6,3 | 2.81 | 4.16 | 0.39 | 120 | 3.77 | 0 | 6.615 | 2.845 | 2.845 | 110/6
182 | St. Kalitva | 6,3+6,3 | 1.33 | 0.86 | 240 | 0.47 | 0 | 6.615 | 6.145 | 6.145 |  | 1.05 | 182 | St. Kalitva | 6,3+6,3 | 0.05 | 1.38 | 0.86 | 240 | 0.52 | 0 | 6.615 | 6.095 | 6.095 | 110/10
183 | Nikanorovka | 2,5+6,3 | 0.5 | 0.5 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 |  | 1.05 | 183 | Nikanorovka | 2,5+6,3 | 0.07 | 0.57 | 0.5 | 240 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | 110/10
184 | PTF | 10+10 | 2.5 | 1 | 120 | 1.5 | 0 | 10.5 | 9 | 9 |  | 1.05 | 184 | PTF | 10+10 | 0.09 | 2.59 | 1 | 120 | 1.59 | 0 | 10.5 | 8.91 | 8.91 | 110/10
185 | Korshevo | 6,3+6,3 | 0.6 | 0.56 | 120 | 0.04 | 0 | 6.615 | 6.575 | 6.575 |  | 1.05 | 185 | Korshevo | 6,3+6,3 | 0.78 | 1.38 | 0.56 | 120 | 0.82 | 0 | 6.615 | 5.795 | 5.795 | 110/10
186 | Davydovka | 6,3+6,3 | 5.6 | 2.11 | 240 | 3.49 | 0 | 6.615 | 3.125 | 3.125 |  | 1.05 | 186 | Davydovka | 6,3+6,3 | 0.51 | 6.11 | 2.11 | 240 | 4 | 0 | 6.615 | 2.615 | 2.615 | 110/10
187 | the 2nd Pyatiletka | 6,3+6,3 | 1.03 | 0.66 | 120 | 0.37 | 0 | 6.615 | 6.245 | 6.245 |  | 1.05 | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.1 | 1.13 | 0.66 | 120 | 0.47 | 0 | 6.615 | 6.145 | 6.145 | 110/10
188 | Liskinskaya | 10+16 | 3 | 0.72 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.22 |  | 1.05 | 188 | Liskinskaya | 10+16 | 4.28 | 7.28 | 0.72 | 120 | 6.56 | 0 | 10.5 | 3.94 | 3.94 | 110/6
189 | Olkhovatka | 4+4 | 3.11 | 2.55 | 180 | 0.56 | 0 | 4.2 | 3.64 | 3.64 |  | 1.05 | 189 | Olkhovatka | 4+4 | 0.83 | 3.94 | 2.55 | 180 | 1.39 | 0 | 4.2 | 2.81 | 2.81 | 35/10
190 | Shaposhnikovka | 2,5+2,5 | 0.9 | 0.86 | 180 | 0.04 | 0 | 2.625 | 2.585 | 2.585 |  | 1.05 | 190 | Shaposhnikovka | 2,5+2,5 | 0.1 | 1 | 0.86 | 180 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | 35/10
191 | Karayashnik | 2,5+2,5 | 0.38 | 0.2875 | 180 | 0.0925 | 0 | 2.625 | 2.5325 | 2.5325 |  | 1.05 | 191 | Karayashnik | 2,5+2,5 | 0.03 | 0.41 | 0.2875 | 180 | 0.1225 | 0 | 2.625 | 2.5025 | 2.5025 | 35/10
192 | Saguny | 2,5+2,5 | 0.91 | 0.91 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 |  | 1.05 | 192 | Saguny | 2,5+2,5 | 0.05 | 0.96 | 0.91 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | 35/10
193 | Belogorye | 2,5+2,5 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 |  | 1.05 | 193 | Belogorye | 2,5+2,5 | 0.13 | 0.82 | 0 | 0 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | 35/10
194 | Taly | 4+4 | 1.17 | 0 | 0 | 1.17 | 0 | 4.2 | 3.03 | 3.03 |  | 1.05 | 194 | Taly | 4+4 | 0.11 | 1.28 | 0 | 0 | 1.28 | 0 | 4.2 | 2.92 | 2.92 | 35/10
195 | Titarevka | 2,5+2,5 | 0.89 | 0 | 0 | 0.89 | 0 | 2.625 | 1.735 | 1.735 |  | 1.05 | 195 | Titarevka | 2,5+2,5 | 0.13 | 1.02 | 0 | 0 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | 35/10
196 | Mitrofanovka | 4+4 | 2.64 | 0 | 0 | 2.64 | 0 | 4.2 | 1.56 | 1.56 |  | 1.05 | 196 | Mitrofanovka | 4+4 | 0.24 | 2.88 | 0 | 0 | 2.88 | 0 | 4.2 | 1.32 | 1.32 | 35/10
197 | Druzhba | 4+4 | 1.34 | 0.44 | 150 | 0.9 | 0 | 4.2 | 3.3 | 3.3 |  | 1.05 | 197 | Druzhba | 4+4 | 0.18 | 1.52 | 0.44 | 150 | 1.08 | 0 | 4.2 | 3.12 | 3.12 | 35/10
198 | Alexandrovka | 4+4 | 2.02 | 0 | 0 | 2.02 | 0 | 4.2 | 2.18 | 2.18 |  | 1.05 | 198 | Alexandrovka | 4+4 | 0.07 | 2.09 | 0 | 0 | 2.09 | 0 | 4.2 | 2.11 | 2.11 | 35/10
199 | Tkhorevka | 4+4 | 1.02 | 0.78 | 180 | 0.24 | 0 | 4.2 | 3.96 | 3.96 |  | 1.05 | 199 | Tkhorevka | 4+4 | 0.09 | 1.11 | 0.78 | 180 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | 35/10
200 | Marki | 2,5+2,5 | 0.34 | 0.27 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 |  | 1.05 | 200 | Marki | 2,5+2,5 | 0 | 0.34 | 0.27 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | 35/10
201 | Olkhov Log | 2,5+2,5 | 0.63 | 0.58 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 |  | 1.05 | 201 | Olkhov Log | 2,5+2,5 | 0 | 0.63 | 0.58 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | 35/10
202 | Boldyrevka | 2,5+2,5 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 |  | 1.05 | 202 | Boldyrevka | 2,5+2,5 | 0.23 | 1.04 | 0 | 0 | 1.04 | 0 | 2.625 | 1.585 | 1.585 | 35/10
203 | Pobeda | 4+4 | 0.58 | 0 | 0 | 0.58 | 0 | 4.2 | 3.62 | 3.62 |  | 1.05 | 203 | Pobeda | 4+4 | 0.05 | 0.63 | 0 | 0 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | 35/10
204 | Lipovka | 4+4 | 1.34 | 0 | 0 | 1.34 | 0 | 4.2 | 2.86 | 2.86 |  | 1.05 | 204 | Lipovka | 4+4 | 0.16 | 1.5 | 0 | 0 | 1.5 | 0 | 4.2 | 2.7 | 2.7 | 35/10
205 | Yudanovka | 2,5+2,5 | 0.83 | 0.81 | 180 | 0.02 | 0 | 2.625 | 2.605 | 2.605 |  | 1.05 | 205 | Yudanovka | 2,5+2,5 | 0.07 | 0.9 | 0.81 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | 35/10
206 | Mechetka | 2,5+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 |  | 1.05 | 206 | Mechetka | 2,5+1,6 | 0.04 | 0.49 | 0 | 0 | 0.49 | 0 | 1.68 | 1.19 | 1.19 | 35/10
207 | Petrovskaya | 4+4 | 1.25 | 0.03 | 180 | 1.22 | 0 | 4.2 | 2.98 | 2.98 |  | 1.05 | 207 | Petrovskaya | 4+4 | 0.87 | 2.12 | 0.03 | 180 | 2.09 | 0 | 4.2 | 2.11 | 2.11 | 35/10
208 | Sr. Ikorets | 4+4 | 2.94 | 0.06 | 120 | 2.88 | 0 | 4.2 | 1.32 | 1.32 |  | 1.05 | 208 | Sr. Ikorets | 4+4 | 0.83 | 3.77 | 0.06 | 120 | 3.71 | 0 | 4.2 | 0.49 | 0.49 | 35/10
209 | the 2nd Storozhevoe | 2,5+2,5 | 0.31 | 0 | 0 | 0.31 | 0 | 2.625 | 2.315 | 2.315 |  | 1.05 | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.02 | 0.33 | 0 | 0 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | 35/10
210 | Och. Sooruzheniya | 2,5+2,5 | 2.18 | 0.42 | 120 | 1.76 | 0 | 2.625 | 0.865 | 0.865 |  | 1.05 | 210 | Och. Sooruzheniya | 2,5+2,5 | 0.93 | 3.11 | 0.6 | 120 | 2.51 | 0 | 2.625 | 0.115 | 0.115 | 35/6
| BPN | [11 empty] | 2: BPN
211 | Borisoglebsk | 25+25 | 23.35 | 15.05 | 240 | 8.3 | 0 | 26.25 | 17.95 | 17.95 |  | 1.05 | 211 | Borisoglebsk | 25+25 | 0 | 23.35 | 24.9 | 240 | -1.55 | 0 | 26.25 | 27.8 | 26.6
| Sн. MV, МVА | 25+25 | 16.15 | 10.9 | 240 | 5.25 | 0 | 26.25 | 21 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 16.15 | 16.5 | 240 | -0.35 | 0 | 26.25 | 26.6 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 7.2 | 4.15 | 240 | 3.05 | 0 | 26.25 | 23.2 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0 | 7.2 | 8.4 | 240 | -1.2 | 0 | 26.25 | 27.45
212 | Kamenka | 10+10 | 5.01 | 2.79 | 180 | 2.22 | 0 | 10.5 | 8.28 | 8.28 |  | 1.05 | 212 | Kamenka | 10+10 | 0.01 | 5.02 | 6.01 | 180 | -0.99 | 0 | 10.5 | 11.49 | 10.6
| Sн. MV, МVА | 10+10 | 4.46 | 2.54 | 180 | 1.92 | 0 | 10.5 | 8.58 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 4.46 | 5.35 | 180 | -0.89 | 0 | 10.5 | 11.39 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.55 | 0.25 | 180 | 0.3 | 0 | 10.5 | 10.2 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 0.56 | 0.66 | 180 | -0.1 | 0 | 10.5 | 10.6
213 | Talovaya | 16+16 | 6.39 | 3.6 | 180 | 2.79 | 0 | 16.8 | 14.01 | 14.01 |  | 1.05 | 213 | Talovaya | 16+16 | 0.08 | 6.47 | 6.39 | 180 | 0.08 | 0 | 16.8 | 16.72 | 15.66
| Sн. MV, МVА | 16+16 | 5.33 | 3.6 | 180 | 1.73 | 0 | 16.8 | 15.07 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 5.33 | 6.39 | 180 | -1.06 | 0 | 16.8 | 17.86 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.06 | 0 | 0 | 1.06 | 0 | 16.8 | 15.74 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.08 | 1.14 | 0 | 0 | 1.14 | 0 | 16.8 | 15.66
214 | Anna | 25+25 | 11.77 | 7.8 | 150 | 3.97 | 0 | 26.25 | 22.28 | 22.28 |  | 1.05 | 214 | Anna | 25+25 | 0.14 | 11.91 | 14.11 | 150 | -2.2 | 0 | 26.25 | 28.45 | 27.14
| Sн. MV, МVА | 25+25 | 4.48 | 2.39 | 150 | 2.09 | 0 | 26.25 | 24.16 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 4.48 | 5.37 | 150 | -0.89 | 0 | 26.25 | 27.14 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.29 | 5.4 | 150 | 1.89 | 0 | 26.25 | 24.36 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.14 | 7.43 | 8.74 | 150 | -1.31 | 0 | 26.25 | 27.56
215 | Arkhangelskoe | 10+10 | 5.42 | 0.88 | 90 | 4.54 | 0 | 10.5 | 5.96 | 5.96 |  | 1.05 | 215 | Arkhangelskoe | 10+10 | 0.01 | 5.43 | 3.02 | 90 | 2.41 | 0 | 10.5 | 8.09 | 7.58
| Sн. MV, МVА | 10+10 | 2.52 | 0.88 | 90 | 1.64 | 0 | 10.5 | 8.86 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.52 | 3.02 | 90 | -0.5 | 0 | 10.5 | 11 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.91 | 0 | 0 | 2.91 | 0 | 10.5 | 7.59 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58
216 | Listopadovka | 10+10 | 3.54 | 1.63 | 90 | 1.91 | 0 | 10.5 | 8.59 | 8.59 |  | 1.05 | 216 | Listopadovka | 10+10 | 0.03 | 3.57 | 3.08 | 90 | 0.49 | 0 | 10.5 | 10.01 | 9.5
| Sн. MV, МVА | 10+10 | 2.57 | 1.63 | 90 | 0.94 | 0 | 10.5 | 9.56 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 2.57 | 3.08 | 90 | -0.51 | 0 | 10.5 | 11.01 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.97 | 0 | 0 | 0.97 | 0 | 10.5 | 9.53 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.03 | 1 | 0 | 0 | 1 | 0 | 10.5 | 9.5
217 | V. Karachan | 10+10 | 2.49 | 0.81 | 90 | 1.68 | 0 | 10.5 | 8.82 | 8.82 |  | 1.05 | 217 | V. Karachan | 10+10 | 0.01 | 2.5 | 1.18 | 90 | 1.32 | 0 | 10.5 | 9.18 | 8.99
| Sн. MV, МVА | 10+10 | 0.99 | 0.81 | 90 | 0.18 | 0 | 10.5 | 10.32 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 0.99 | 1.18 | 90 | -0.19 | 0 | 10.5 | 10.69 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.5 | 0 | 0 | 1.5 | 0 | 10.5 | 9 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.01 | 1.51 | 0 | 0 | 1.51 | 0 | 10.5 | 8.99
218 | Ternovka | 10+10 | 3.6 | 0.66 | 60 | 2.94 | 0 | 10.5 | 7.56 | 7.56 |  | 1.05 | 218 | Ternovka | 10+10 | 0.06 | 3.66 | 1.03 | 60 | 2.63 | 0 | 10.5 | 7.87 | 7.7
| Sн. MV, МVА | 10+10 | 0.86 | 0.66 | 60 | 0.2 | 0 | 10.5 | 10.3 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 0.86 | 1.03 | 60 | -0.17 | 0 | 10.5 | 10.67 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.74 | 0 | 0 | 2.74 | 0 | 10.5 | 7.76 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.06 | 2.8 | 0 | 0 | 2.8 | 0 | 10.5 | 7.7
219 | Narodnoe | 16+10 | 2.85 | 0.6 | 90 | 2.25 | 0 | 10.5 | 8.25 | 8.25 |  | 1.05 | 219 | Narodnoe | 16+10 | 0.06 | 2.91 | 0.93 | 90 | 1.98 | 0 | 10.5 | 8.52 | 8.37
| Sн. MV, МVА | 16+10 | 0.78 | 0.6 | 90 | 0.18 | 0 | 10.5 | 10.32 |  |  | 1.05 |  | Sн. MV, МVА | 16+10 | 0 | 0.78 | 0.93 | 90 | -0.15 | 0 | 10.5 | 10.65 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 2.07 | 0 | 0 | 2.07 | 0 | 10.5 | 8.43 |  |  | 1.05 |  | Sн. LV, МVА | 16+10 | 0.06 | 2.13 | 0 | 0 | 2.13 | 0 | 10.5 | 8.37
220 | N. Khopersk | 10+16 | 7.62 | 1.7 | 120 | 5.92 | 0 | 10.5 | 4.58 | 4.58 |  | 1.05 | 220 | N. Khopersk | 10+16 | 0.29 | 7.91 | 1.95 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.32
| Sн. MV, МVА | 10+16 | 1.63 | 1.7 | 120 | -0.07 | 0 | 10.5 | 10.57 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 1.63 | 1.95 | 120 | -0.32 | 0 | 10.5 | 10.82 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 5.89 | 0 | 0 | 5.89 | 0 | 10.5 | 4.61 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.29 | 6.18 | 0 | 0 | 6.18 | 0 | 10.5 | 4.32
221 | Ertil | 10+16 | 8.91 | 2.92 | 180 | 5.99 | 0 | 10.5 | 4.51 | 4.51 |  | 1.05 | 221 | Ertil | 10+16 | 0.08 | 8.99 | 1.4 | 180 | 7.59 | 0 | 10.5 | 2.91 | 2.91
| Sн. MV, МVА | 10+16 | 5.9 | 2.92 | 180 | 2.98 | 0 | 10.5 | 7.52 |  |  | 1.05 |  | Sн. MV, МVА | 10+16 | 0 | 5.9 | 1.4 | 180 | 4.5 | 0 | 10.5 | 6 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 3.01 | 0.08 | 0 | 2.93 | 0 | 10.5 | 7.57 |  |  | 1.05 |  | Sн. LV, МVА | 10+16 | 0.08 | 3.09 | 0 | 0 | 3.09 | 0 | 10.5 | 7.41
222 | Shchuchye | 6,3+6,3 | 3.15 | 1.09 | 180 | 2.06 | 0 | 6.615 | 4.555 | 4.555 |  | 1.05 | 222 | Shchuchye | 6,3+6,3 | 0.08 | 3.23 | 2.33 | 180 | 0.9 | 0 | 6.615 | 5.715 | 5.415
| Sн. MV, МVА | 6,3+6,3 | 1.51 | 0.84 | 180 | 0.67 | 0 | 6.615 | 5.945 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.51 | 1.81 | 180 | -0.3 | 0 | 6.615 | 6.915 |  | 110/35/10
| Sн.LV, МVА | 6,3+6,3 | 1.64 | 0.25 | 180 | 1.39 | 0 | 6.615 | 5.225 |  |  | 1.05 |  | Sн.LV, МVА | 6,3+6,3 | 0.08 | 1.72 | 0.52 | 180 | 1.2 | 0 | 6.615 | 5.415
223 | Dokuchaevo | 10+10 | 2.1 | 0.12 | 120 | 1.98 | 0 | 10.5 | 8.52 | 8.52 |  | 1.05 | 223 | Dokuchaevo | 10+10 | 0.03 | 2.13 | 0.45 | 120 | 1.68 | 0 | 10.5 | 8.82 | 8.82 | 110/10
224 | B. Gribanovka | 16+16 | 6.54 | 0.11 | 30 | 6.43 | 0 | 16.8 | 10.37 | 10.37 |  | 1.05 | 224 | B. Gribanovka | 16+16 | 0.15 | 6.69 | 0.24 | 30 | 6.45 | 0 | 16.8 | 10.35 | 10.35 | 110/10
225 | Khimmash | 16+16 | 5.93 | 4.47 | 240 | 1.46 | 0 | 16.8 | 15.34 | 15.34 |  | 1.05 | 225 | Khimmash | 16+16 | 0 | 5.93 | 7.1 | 240 | -1.17 | 0 | 16.8 | 17.97 | 17.97 | 110/6
226 | Chigorak | 2,5+4 | 0.8 | 0.74 | 90 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 226 | Chigorak | 2,5+4 | 0.11 | 0.91 | 0.96 | 90 | -0.05 | 0 | 2.625 | 2.675 | 2.675 | 35/10
227 | Tretyaki | 4+4 | 0.97 | 0 | 0 | 0.97 | 0 | 4.2 | 3.23 | 3.23 |  | 1.05 | 227 | Tretyaki | 4+4 | 0.03 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | 35/10
228 | Gubari | 2,5+2,5 | 0.36 | 0.06 | 180 | 0.3 | 0 | 2.625 | 2.325 | 2.325 |  | 1.05 | 228 | Gubari | 2,5+2,5 | 0.05 | 0.41 | 0.43 | 180 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | 35/10
229 | Tantsyrey | 2,5+2,5 | 0.89 | 0 | 0 | 0.89 | 0 | 2.625 | 1.735 | 1.735 |  | 1.05 | 229 | Tantsyrey | 2,5+2,5 | 0.04 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | 35/10
230 | Peski | 4+4 | 3.86 | 0 | 0 | 3.86 | 0 | 4.2 | 0.34 | 0.34 |  | 1.05 | 230 | Peski | 4+4 | 0.12 | 3.98 | 0 | 0 | 3.98 | 0 | 4.2 | 0.22 | 0.22 | 35/10
231 | M. Gribanovka | 1,6+1,6 | 0.72 | 0.31 | 30 | 0.41 | 0 | 1.68 | 1.27 | 1.27 |  | 1.05 | 231 | M. Gribanovka | 1,6+1,6 | 0.02 | 0.74 | 0.87 | 30 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | 35/10
232 | N. Karachan | 2,5+2,5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 |  | 1.05 | 232 | N. Karachan | 2,5+2,5 | 0 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | 35/10
233 | Kozlovka | 4+2,5 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 |  | 1.05 | 233 | Kozlovka | 4+2,5 | 0.03 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | 35/10
234 | K. Otdelets | 2,5+2,5 | 0.53 | 0 | 30 | 0.53 | 0 | 2.625 | 2.095 | 2.095 |  | 1.05 | 234 | K. Otdelets | 2,5+2,5 | 0 | 0.53 | 0.63 | 30 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | 35/10
235 | Esipovo | 2,5+2,5 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 |  | 1.05 | 235 | Esipovo | 2,5+2,5 | 0.02 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | 35/10
236 | Kiselnov | 2,5+2,5 | 0.46 | 0 | 0 | 0.46 | 0 | 2.625 | 2.165 | 2.165 |  | 1.05 | 236 | Kiselnov | 2,5+2,5 | 0 | 0.46 | 0 | 0 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | 35/10
237 | Krasnoe | 6,3+6,3 | 1.34 | 0 | 0 | 1.34 | 0 | 6.615 | 5.275 | 5.275 |  | 1.05 | 237 | Krasnoe | 6,3+6,3 | 0.01 | 1.35 | 0 | 0 | 1.35 | 0 | 6.615 | 5.265 | 5.265 | 35/10
238 | Troitskoe | 2,5+2,5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 |  | 1.05 | 238 | Troitskoe | 2,5+2,5 | 0.01 | 0.44 | 0 | 0 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | 35/10
239 | Ertil-gorod | 6,3+6,3 | 4.73 | 2.45 | 240 | 2.28 | 0 | 6.615 | 4.335 | 4.335 |  | 1.05 | 239 | Ertil-gorod | 6,3+6,3 | 0.06 | 4.79 | 5 | 240 | -0.21 | 0 | 6.615 | 6.825 | 6.825 | 35/10
240 | Rostoshi | 4+4 | 1.34 | 0 | 0 | 1.34 | 0 | 4.2 | 2.86 | 2.86 |  | 1.05 | 240 | Rostoshi | 4+4 | 0 | 1.34 | 0 | 0 | 1.34 | 0 | 4.2 | 2.86 | 2.86 | 35/10
241 | Vvedenka | 2,5+2,5 | 0.4 | 0 | 60 | 0.4 | 0 | 2.625 | 2.225 | 2.225 |  | 1.05 | 241 | Vvedenka | 2,5+2,5 | 0 | 0.4 | 0.48 | 60 | -0.08 | 0 | 2.625 | 2.705 | 2.705 | 35/10
242 | Sadovoe | 4+4 | 2.06 | 0 | 0 | 2.06 | 0 | 4.2 | 2.14 | 2.14 |  | 1.05 | 242 | Sadovoe | 4+4 | 0.03 | 2.09 | 0 | 0 | 2.09 | 0 | 4.2 | 2.11 | 2.11 | 35/10
243 | Rubashevka | 2,5+2,5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 |  | 1.05 | 243 | Rubashevka | 2,5+2,5 | 0 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | 35/10
244 | N. Nadezhdenka | 2,5+2,5 | 0.63 | 0.22 | 180 | 0.41 | 0 | 2.625 | 2.215 | 2.215 |  | 1.05 | 244 | N. Nadezhdenka | 2,5+2,5 | 0 | 0.63 | 0.75 | 180 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | 35/10
245 | Abramovka | 6,3+4 | 3.81 | 0.29 | 120 | 3.52 | 0 | 4.2 | 0.68 | 0.68 |  | 1.05 | 245 | Abramovka | 6,3+4 | 0.04 | 3.85 | 0.52 | 120 | 3.33 | 0 | 4.2 | 0.87 | 0.87 | 35/10
246 | Alexandrovka | 2,5+2,5 | 0.98 | 0.64 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 |  | 1.05 | 246 | Alexandrovka | 2,5+2,5 | 0.01 | 0.99 | 1.17 | 120 | -0.18 | 0 | 2.625 | 2.805 | 2.805 | 35/10
247 | N. Troitskaya | 4+4 | 0.29 | 0.2 | 120 | 0.09 | 0 | 4.2 | 4.11 | 4.11 |  | 1.05 | 247 | N. Troitskaya | 4+4 | 0 | 0.29 | 0.34 | 120 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | 35/10
| KPN | [11 empty] | 2: KPN
248 | Kalach-1 | 25+25 | 13.07 | 2.2 | 120 | 10.87 | 0 | 26.25 | 15.38 | 15.38 |  | 1.05 | 248 | Kalach-1 | 25+25 | 0.4 | 13.47 | 2.2 | 120 | 11.27 | 0 | 26.25 | 14.98 | 14.98
| Sн. MV, МVА | 25+25 | 6.59 | 1 | 120 | 5.59 | 0 | 26.25 | 20.66 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 6.59 | 1 | 120 | 5.59 | 0 | 26.25 | 20.66 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 6.51 | 1.2 | 120 | 5.31 | 0 | 26.25 | 20.94 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.4 | 6.91 | 1.2 | 120 | 5.71 | 0 | 26.25 | 20.54
249 | Kalach-2 | 16+16 | 7.2 | 2 | 24 hours | 5.2 | 0 | 16.8 | 11.6 | 11.6 |  | 1.05 | 249 | Kalach-2 | 16+16 | 0.45 | 7.65 | 2 | 24 hours | 5.65 | 0 | 16.8 | 11.15 | 11.15 | 110/10
250 | Buturlinovka-1 | 16+16 | 14.37 | 2 | 120 | 12.37 | 0 | 16.8 | 4.43 | 4.43 |  | 1.05 | 250 | Buturlinovka-1 | 16+16 | 0.01 | 14.38 | 2 | 120 | 12.38 | 0 | 16.8 | 4.42 | 4.42
| Sн. MV, МVА | 16+16 | 5.09 | 0 | 0 | 5.09 | 0 | 16.8 | 11.71 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 5.09 | 0 | 0 | 5.09 | 0 | 16.8 | 11.71 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 9.28 | 2 | 120 | 7.28 | 0 | 16.8 | 9.52 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.01 | 9.29 | 2 | 120 | 7.29 | 0 | 16.8 | 9.51
251 | Buturlinovka-2 | 16+6,3 | 5.27 | 1.5 | 120 | 3.77 | 0 | 6.615 | 2.845 | 2.845 |  | 1.05 | 251 | Buturlinovka-2 | 16+6,3 | 0.01 | 5.28 | 1.5 | 120 | 3.78 | 0 | 6.615 | 2.835 | 2.835 | 110/10
252 | N.Kislyai | 10+10 | 6.32 | 1.5 | 120 | 4.82 | 0 | 10.5 | 5.68 | 5.68 |  | 1.05 | 252 | N.Kislyai | 10+10 | 0.35 | 6.67 | 1.5 | 120 | 5.17 | 0 | 10.5 | 5.33 | 5.33
| Sн. MV, МVА | 10+10 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.03 | 1.5 | 120 | 1.53 | 0 | 10.5 | 8.97 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.35 | 3.38 | 1.5 | 120 | 1.88 | 0 | 10.5 | 8.62
253 | Kozlovka | 2,5+6,3 | 1.15 | 1.5 | 45 | -0.35 | 0 | 2.625 | 2.975 | 2.975 |  | 1.05 | 253 | Kozlovka | 2,5+6,3 | 0.18 | 1.33 | 1.5 | 45 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | 110/10
254 | Filippenkovo | 6,3+6,3 | 0.92 | 1.5 | 120 | -0.58 | 0 | 6.615 | 7.195 | 7.195 |  | 1.05 | 254 | Filippenkovo | 6,3+6,3 | 0.05 | 0.97 | 1.5 | 120 | -0.53 | 0 | 6.615 | 7.145 | 7.145 | 110/10
255 | Vorobyovka | 16+16 | 5.17 | 1.5 | 120 | 3.67 | 0 | 16.8 | 13.13 | 13.13 |  | 1.05 | 255 | Vorobyovka | 16+16 | 0.39 | 5.56 | 1.5 | 120 | 4.06 | 0 | 16.8 | 12.74 | 12.74
| Sн. MV, МVА | 16+16 | 3.33 | 0.5 | 120 | 2.83 | 0 | 16.8 | 13.97 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 3.33 | 0.5 | 120 | 2.83 | 0 | 16.8 | 13.97 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.84 | 1 | 120 | 0.84 | 0 | 16.8 | 15.96 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.39 | 2.23 | 1 | 120 | 1.23 | 0 | 16.8 | 15.57
256 | Solontsy | 6,3+6,3 | 1.98 | 1 | 24 hours | 0.98 | 0 | 6.615 | 5.635 | 5.635 |  | 1.05 | 256 | Solontsy | 6,3+6,3 | 0.03 | 2.01 | 1 | 24 hours | 1.01 | 0 | 6.615 | 5.605 | 5.605
| Sн. MV, МVА | 6,3+6,3 | 1.05 | 1 | 24 hours | 0.05 | 0 | 6.615 | 6.565 |  |  | 1.05 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.05 | 1 | 24 hours | 0.05 | 0 | 6.615 | 6.565 |  | 110/35/10
| Sн. LV, МVА | 6,3+6,3 | 0.93 | 0 | 0 | 0.93 | 0 | 6.615 | 5.685 |  |  | 1.05 |  | Sн. LV, МVА | 6,3+6,3 | 0.03 | 0.96 | 0 | 0 | 0.96 | 0 | 6.615 | 5.655
257 | Manino | 16+16 | 1.74 | 1.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 | 16.56 |  | 1.05 | 257 | Manino | 16+16 | 0.01 | 1.75 | 1.5 | 24 hours | 0.25 | 0 | 16.8 | 16.55 | 16.55
| Sн. MV, МVА | 16+16 | 0.59 | 0.5 | 24 hours | 0.09 | 0 | 16.8 | 16.71 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 0.59 | 0.5 | 24 hours | 0.09 | 0 | 16.8 | 16.71 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.15 | 1 | 24 hours | 0.15 | 0 | 16.8 | 16.65 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 0.01 | 1.16 | 1 | 24 hours | 0.16 | 0 | 16.8 | 16.64
258 | Petropavlovka | 10+10 | 4.13 | 2 | 120 | 2.13 | 0 | 10.5 | 8.37 | 8.37 |  | 1.05 | 258 | Petropavlovka | 10+10 | 0.17 | 4.3 | 2 | 120 | 2.3 | 0 | 10.5 | 8.2 | 8.2
| Sн. MV, МVА | 10+10 | 1.78 | 1 | 120 | 0.78 | 0 | 10.5 | 9.72 |  |  | 1.05 |  | Sн. MV, МVА | 10+10 | 0 | 1.78 | 1 | 120 | 0.78 | 0 | 10.5 | 9.72 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.35 | 1 | 120 | 1.35 | 0 | 10.5 | 9.15 |  |  | 1.05 |  | Sн. LV, МVА | 10+10 | 0.17 | 2.52 | 1 | 120 | 1.52 | 0 | 10.5 | 8.98
259 | V.Mamon | 16+10 | 6.08 | 2 | 120 | 4.08 | 0 | 10.5 | 6.42 | 6.42 |  | 1.05 | 259 | V.Mamon | 16+10 | 0.49 | 6.57 | 2 | 120 | 4.57 | 0 | 10.5 | 5.93 | 5.93
| Sн. MV, МVА | 16+10 | 1.94 | 0 | 0 | 1.94 | 0 | 10.5 | 8.56 |  |  | 1.05 |  | Sн. MV, МVА | 16+10 | 0 | 1.94 | 0 | 0 | 1.94 | 0 | 10.5 | 8.56 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 4.14 | 2 | 120 | 2.14 | 0 | 10.5 | 8.36 |  |  | 1.05 |  | Sн. LV, МVА | 16+10 | 0.49 | 4.63 | 2 | 120 | 2.63 | 0 | 10.5 | 7.87
260 | N.Mamon | 2,5+6,3 | 1.09 | 0 | 0 | 1.09 | 0 | 2.625 | 1.535 | 1.535 |  | 1.05 | 260 | N.Mamon | 2,5+6,3 | 0.05 | 1.14 | 0 | 0 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | 110/10
261 | Pavlovsk-2 | 25+25 | 17.6 | 1.5 | 120 | 16.1 | 0 | 26.25 | 10.15 | 10.15 |  | 1.05 | 261 | Pavlovsk-2 | 25+25 | 0.06 | 17.66 | 1.5 | 120 | 16.16 | 0 | 26.25 | 10.09 | 10.09
| Sн. MV, МVА | 25+25 | 9.62 | 1.5 | 120 | 8.12 | 0 | 26.25 | 18.13 |  |  | 1.05 |  | Sн. MV, МVА | 25+25 | 0 | 9.62 | 1.5 | 120 | 8.12 | 0 | 26.25 | 18.13 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 7.98 | 0 | 0 | 7.98 | 0 | 26.25 | 18.27 |  |  | 1.05 |  | Sн. LV, МVА | 25+25 | 0.06 | 8.04 | 0 | 0 | 8.04 | 0 | 26.25 | 18.21
262 | Bogucharskaya | 16+16 | 10.8 | 2 | 120 | 8.8 | 0 | 16.8 | 8 | 8 |  | 1.05 | 262 | Bogucharskaya | 16+16 | 1.82 | 12.62 | 2 | 120 | 10.62 | 0 | 16.8 | 6.18 | 6.18
| Sн. MV, МVА | 16+16 | 5.42 | 1 | 120 | 4.42 | 0 | 16.8 | 12.38 |  |  | 1.05 |  | Sн. MV, МVА | 16+16 | 0 | 5.42 | 1 | 120 | 4.42 | 0 | 16.8 | 12.38 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.38 | 1 | 120 | 4.38 | 0 | 16.8 | 12.42 |  |  | 1.05 |  | Sн. LV, МVА | 16+16 | 1.82 | 7.2 | 1 | 120 | 6.2 | 0 | 16.8 | 10.6
263 | Opornaya | 6,3+6,3 | 2.12 | 1.5 | 120 | 0.62 | 0 | 6.615 | 5.995 | 5.995 |  | 1.05 | 263 | Opornaya | 6,3+6,3 | 1.4 | 3.52 | 1.5 | 120 | 2.02 | 0 | 6.615 | 4.595 | 4.595 | 110/10
264 | Podgornaya | 2,5+2,5 | 0.81 | 1 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 |  | 1.05 | 264 | Podgornaya | 2,5+2,5 | 0.01 | 0.82 | 1 | 120 | -0.18 | 0 | 2.625 | 2.805 | 2.805 | 35/10
265 | Bolshevik | 4+2,5 | 2 | 1.5 | 45 | 0.5 | 0 | 2.625 | 2.125 | 2.125 |  | 1.05 | 265 | Bolshevik | 4+2,5 | 0.16 | 2.16 | 1.5 | 45 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | 35/10
266 | Semenovka | 2,5+1,8 | 0.77 | 1 | 80 | -0.23 | 0 | 1.89 | 2.12 | 2.12 |  | 1.05 | 266 | Semenovka | 2,5+1,8 | 0.03 | 0.8 | 1 | 80 | -0.2 | 0 | 1.89 | 2.09 | 2.09 | 35/10
267 | Popasnoe | 4+4 | 0.32 | 1.5 | 120 | -1.18 | 0 | 4.2 | 5.38 | 5.38 |  | 1.05 | 267 | Popasnoe | 4+4 | 0.02 | 0.34 | 1.5 | 120 | -1.16 | 0 | 4.2 | 5.36 | 5.36 | 35/10
268 | N.Kriusha | 2,5+2,5 | 1.09 | 1.5 | 45 | -0.41 | 0 | 2.625 | 3.035 | 3.035 |  | 1.05 | 268 | N.Kriusha | 2,5+2,5 | 0.03 | 1.12 | 1.5 | 45 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | 35/10
269 | N.Melovatka | 2,5+2,5 | 1.53 | 1.5 | 45 | 0.03 | 0 | 2.625 | 2.595 | 2.595 |  | 1.05 | 269 | N.Melovatka | 2,5+2,5 | 0.03 | 1.56 | 1.5 | 45 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
270 | Vasilyevka | 4+4 | 0.77 | 1.5 | 120 | -0.73 | 0 | 4.2 | 4.93 | 4.93 |  | 1.05 | 270 | Vasilyevka | 4+4 | 0.05 | 0.82 | 1.5 | 120 | -0.68 | 0 | 4.2 | 4.88 | 4.88 | 35/10
271 | V.Oktyabr | 4+4 | 0.96 | 1.5 | 120 | -0.54 | 0 | 4.2 | 4.74 | 4.74 |  | 1.05 | 271 | V.Oktyabr | 4+4 | 0.15 | 1.11 | 1.5 | 120 | -0.39 | 0 | 4.2 | 4.59 | 4.59 | 35/10
272 | V.Arkhangelskoe | 2,5+2,5 | 0.5 | 1.5 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 |  | 1.05 | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.07 | 0.57 | 1.5 | 45 | -0.93 | 0 | 2.625 | 3.555 | 3.555 | 35/10
273 | Leshchanaya | 2,5+2,5 | 1.5 | 1.5 | 45 | 0 | 0 | 2.625 | 2.625 | 2.625 |  | 1.05 | 273 | Leshchanaya | 2,5+2,5 | 0.18 | 1.68 | 1.5 | 45 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | 35/10
274 | Muzhichye | 4+2,5 | 0.54 | 1.5 | 45 | -0.96 | 0 | 2.625 | 3.585 | 3.585 |  | 1.05 | 274 | Muzhichye | 4+2,5 | 0.11 | 0.65 | 1.5 | 45 | -0.85 | 0 | 2.625 | 3.475 | 3.475 | 35/10
275 | Rudnya | 4+4 | 0.46 | 1.5 | 120 | -1.04 | 0 | 4.2 | 5.24 | 5.24 |  | 1.05 | 275 | Rudnya | 4+4 | 0 | 0.46 | 1.5 | 120 | -1.04 | 0 | 4.2 | 5.24 | 5.24 | 35/10
276 | St. Melovaya | 4+4 | 0.89 | 0 | 0 | 0.89 | 0 | 4.2 | 3.31 | 3.31 |  | 1.05 | 276 | St. Melovaya | 4+4 | 0.07 | 0.96 | 0 | 0 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | 35/10
277 | St. Kriusha | 2,5+4 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 |  | 1.05 | 277 | St. Kriusha | 2,5+4 | 0.04 | 1.14 | 0 | 0 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | 35/10
278 | Lozovaya | 4+4 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 |  | 1.05 | 278 | Lozovaya | 4+4 | 0.3 | 0.92 | 0 | 0 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | 35/10
279 | Pavlovsk-1 | 4+4 | 3.21 | 1 | 120 | 2.21 | 0 | 4.2 | 1.99 | 1.99 |  | 1.05 | 279 | Pavlovsk-1 | 4+4 | 0.17 | 3.38 | 1 | 120 | 2.38 | 0 | 4.2 | 1.82 | 1.82 | 35/10
280 | Losevo | 4+4 | 2.5 | 0 | 0 | 2.5 | 0 | 4.2 | 1.7 | 1.7 |  | 1.05 | 280 | Losevo | 4+4 | 0.05 | 2.55 | 0 | 0 | 2.55 | 0 | 4.2 | 1.65 | 1.65 | 35/10
281 | Gavrilsk | 4+4 | 0.53 | 0 | 0 | 0.53 | 0 | 4.2 | 3.67 | 3.67 |  | 1.05 | 281 | Gavrilsk | 4+4 | 0.01 | 0.54 | 0 | 0 | 0.54 | 0 | 4.2 | 3.66 | 3.66 | 35/10
282 | Pokrovka | 4+2,5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 |  | 1.05 | 282 | Pokrovka | 4+2,5 | 0.02 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | 35/10
283 | Vorontsovka | 4+4 | 2.44 | 1.5 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 |  | 1.05 | 283 | Vorontsovka | 4+4 | 0.59 | 3.03 | 1.5 | 120 | 1.53 | 0 | 4.2 | 2.67 | 2.67 | 35/10
284 | А.Donskaya | 2,5+2,5 | 1.09 | 1.5 | 45 | -0.41 | 0 | 2.625 | 3.035 | 3.035 |  | 1.05 | 284 | А.Donskaya | 2,5+2,5 | 0.05 | 1.14 | 1.5 | 45 | -0.36 | 0 | 2.625 | 2.985 | 2.985 | 35/10
285 | Petrovka | 2,5+4 | 1.36 | 1.5 | 45 | -0.14 | 0 | 2.625 | 2.765 | 2.765 |  | 1.05 | 285 | Petrovka | 2,5+4 | 0.04 | 1.4 | 1.5 | 45 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | 35/10
286 | Monastyrshchina | 4+4 | 0.88 | 1.5 | 120 | -0.62 | 0 | 4.2 | 4.82 | 4.82 |  | 1.05 | 286 | Monastyrshchina | 4+4 | 0.07 | 0.95 | 1.5 | 120 | -0.55 | 0 | 4.2 | 4.75 | 4.75 | 35/10
287 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 |  | 1.05 | 287 | Zhuravka | 1,8+2,5 | 0 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | 35/10
288 | Dyachenkovo | 2,5+2,5 | 1.48 | 1.5 | 45 | -0.02 | 0 | 2.625 | 2.645 | 2.645 |  | 1.05 | 288 | Dyachenkovo | 2,5+2,5 | 0.1 | 1.58 | 1.5 | 45 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | 35/10
289 | Radchenskaya | 1,6+2,5 | 0.83 | 0 | 0 | 0.83 | 0 | 1.68 | 0.85 | 0.85 |  | 1.05 | 289 | Radchenskaya | 1,6+2,5 | 0.04 | 0.87 | 0 | 0 | 0.87 | 0 | 1.68 | 0.81 | 0.81 | 35/10
290 | Rossiya | 4+4 | 1.07 | 1.5 | 120 | -0.43 | 0 | 4.2 | 4.63 | 4.63 |  | 1.05 | 290 | Rossiya | 4+4 | 0.07 | 1.14 | 1.5 | 120 | -0.36 | 0 | 4.2 | 4.56 | 4.56 | 35/10
291 | Pervomayskaya | 4+4 | 0.35 | 1.5 | 120 | -1.15 | 0 | 4.2 | 5.35 | 5.35 |  | 1.05 | 291 | Pervomayskaya | 4+4 | 0.01 | 0.36 | 1.5 | 120 | -1.14 | 0 | 4.2 | 5.34 | 5.34 | 35/10
292 | Podkolodnovka | 2,5+3,2 | 0.91 | 0 | 0 | 0.91 | 0 | 2.625 | 1.715 | 1.715 |  | 1.05 | 292 | Podkolodnovka | 2,5+3,2 | 0.05 | 0.96 | 0 | 0 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | 35/10
293 | Yuzhny | 2,5+2,5 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 |  | 1.05 | 293 | Yuzhny | 2,5+2,5 |  | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 | 35/10
| TOTAL: |  | 1299.6897 | [6 empty] | 1100.8693 |  |  | 2: TOTAL:; min. 12: 890.5323
| deficit | [8 empty] | 64.26 |  |  | 2: deficit; min. 12: 113.42
| proficit | [8 empty] | 1036.6093 |  |  | 2: proficit; min. 12: 777.1123

## Костромаэнерго
Calculation of transmission capacity of Main substations of the branch of IDGC of Centre, JSC Kostromaenergo following the results of winter measurement of the load maximum for October 2009
[9 empty] | table 1 | [11 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit /proficit of main substation, MVA |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main Susbstation, MVA | Deficit /proficit of Main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Sandogora 35/6 kv | 1 | 0.3 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.25 | 0.25 | opened | 1 | Sandogora 35/6 kv | 1 | 0.074 | 0.374 | 0.55 | 120 | -0.176 | 0 | 0.55 | 0.176 | 0.176 | opened
2 | Gridino 35/10 kv | 1.8 | 0.45 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.75 | 0.75 | opened | 2 | Gridino 35/10 kv | 1.8 | 0.409 | 0.859 | 1.2 | 120 | -0.341 | 0 | 1.2 | 0.341 | 0.341 | opened
3 | Novinki 35/10 kv | 1.8 | 0.09 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.35 | 1.35 | opened | 3 | Novinki 35/10 kv | 1.8 | 0.306 | 0.396 | 1.44 | 120 | -1.044 | 0 | 1.44 | 1.044 | 1.044 | opened
4 | Priskokovo 35/10kv | 2.5 | 1.32 | 1.45 | 120 | 1.45 | 0 | 1.45 | 0.13 | 0.13 | opened | 4 | Priskokovo 35/10kv | 2.5 | 0.116 | 1.436 | 1.45 | 120 | -0.014 | 0 | 1.45 | 0.014 | 0.014 | opened
5 | Grigortsevo 110/10 kv | 2.5 | 0.22 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.28 | 1.28 | opened | 5 | Grigortsevo 110/10 kv | 2.5 | 0.025 | 0.245 | 1.5 | 120 | -1.255 | 0 | 1.5 | 1.255 | 1.255 | opened
6 | Klementyevo 110/10 kv | 6.3 | 0.47 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.23 | 3.23 | opened | 6 | Klementyevo 110/10 kv | 6.3 | 3.01 | 3.48 | 3.7 | 120 | -0.22 | 0 | 3.7 | 0.22 | 0.22 | opened
7 | Rudino 35/10 kv | 2.5 | 0.43 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.07 | 1.07 | opened | 7 | Rudino 35/10 kv | 2.5 | 0 | 0.43 | 1.5 | 120 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened
8 | Stoyankovo 35/10 kv | 1.6 | 0.2 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.52 | 0.52 | opened | 8 | Stoyankovo 35/10 kv | 1.6 | 0.072 | 0.272 | 0.72 | 120 | -0.448 | 0 | 0.72 | 0.448 | 0.448 | opened
9 | Adishchevo 35/10 kv | 4 | 1.15 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.45 | 1.45 | opened | 9 | Adishchevo 35/10 kv | 4 | 0.931 | 2.081 | 2.6 | 120 | -0.519 | 0 | 2.6 | 0.519 | 0.519 | opened
10 | Stolbovo 110/10 kv | 10 | 0.41 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.19 | 4.19 | opened | 10 | Stolbovo 110/10 kv | 10 | 0.011 | 0.421 | 4.6 | 120 | -4.179 | 0 | 4.6 | 4.179 | 4.179 | opened
11 | Raslovo 35/10 kv | 2.5 | 0.73 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.65 | 0.65 | opened | 11 | Raslovo 35/10 kv | 2.5 | 0.299 | 1.029 | 1.38 | 120 | -0.351 | 0 | 1.38 | 0.351 | 0.351 | opened
12 | Andreevskoe 35/10 kv | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | opened | 12 | Andreevskoe 35/10 kv | 1.6 | 0.021 | 0.201 | 0.93 | 120 | -0.729 | 0 | 0.93 | 0.729 | 0.729 | opened
13 | Popadyino 35/10 kv | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | opened | 13 | Popadyino 35/10 kv | 1.6 | 0.118 | 0.338 | 0.88 | 120 | -0.542 | 0 | 0.88 | 0.542 | 0.542 | opened
14 | Elegino 110/10 kv | 2.5 | 0.18 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.8 | 0.8 | opened | 14 | Elegino 110/10 kv | 2.5 | 0.052 | 0.232 | 0.98 | 120 | -0.748 | 0 | 0.98 | 0.748 | 0.748 | opened
15 | Krenyovo 35/10 kv | 2.5 | 0.21 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.29 | 2.29 | opened | 15 | Krenyovo 35/10 kv | 2.5 | 0.128 | 0.338 | 2.5 | 24 hours | -2.162 | 0 | 2.5 | 2.162 | 2.162 | opened
16 | Semyonovskoe 35/10 kv | 1.6 | 0.28 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.32 | 1.32 | opened | 16 | Semyonovskoe 35/10 kv | 1.6 | 0.025 | 0.305 | 1.6 | 24 hours | -1.295 | 0 | 1.6 | 1.295 | 1.295 | opened
17 | Khimik 35/10 kv | 3.2 | 0.08 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.36 | 1.36 | opened | 17 | Khimik 35/10 kv | 3.2 | 0 | 0.08 | 1.44 | 120 | -1.36 | 0 | 1.44 | 1.36 | 1.36 | opened
18 | N. Beryozovets 35/10 kv | 2.5 | 0.24 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.19 | 0.19 | opened | 18 | N. Beryozovets 35/10 kv | 2.5 | 0.022 | 0.262 | 0.43 | 120 | -0.168 | 0 | 0.43 | 0.168 | 0.168 | opened
19 | Stepanovo 35/10 kv | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | opened | 19 | Stepanovo 35/10 kv | 4 | 0.111 | 0.431 | 2.32 | 120 | -1.889 | 0 | 2.32 | 1.889 | 1.889 | opened
20 | Gorbachevo 35/10 kv | 1 | 0.01 | 0.78 | 120 | 0.78 | 0 | 0.78 | 0.77 | 0.77 | opened | 20 | Gorbachevo 35/10 kv | 1 | 0.006 | 0.016 | 0.78 | 120 | -0.764 | 0 | 0.78 | 0.764 | 0.764 | opened
21 | Kalinino 35/10 kv | 1 | 0.12 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.44 | 0.44 | opened | 21 | Kalinino 35/10 kv | 1 | 0 | 0.12 | 0.56 | 120 | -0.44 | 0 | 0.56 | 0.44 | 0.44 | opened
22 | Kuzemino 35/10 kv | 1.6 | 0.27 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.33 | 1.33 | opened | 22 | Kuzemino 35/10 kv | 1.6 | 0.012 | 0.282 | 1.6 | 24 hours | -1.318 | 0 | 1.6 | 1.318 | 1.318 | opened
23 | Sovega 35/10 kv | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | opened | 23 | Sovega 35/10 kv | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | opened
24 | Lukovtsino 110/10 kv | 2.5 | 0.12 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.26 | 1.26 | opened | 24 | Lukovtsino 110/10 kv | 2.5 | 0 | 0.12 | 1.38 | 120 | -1.26 | 0 | 1.38 | 1.26 | 1.26 | opened
25 | Fyodorovskoe 110/10 kv | 2.5 | 0.03 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.47 | 1.47 | opened | 25 | Fyodorovskoe 110/10 kv | 2.5 | 0.01 | 0.04 | 1.5 | 120 | -1.46 | 0 | 1.5 | 1.46 | 1.46 | opened
26 | Pankratovo 35/10 kv | 1 | 0.08 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.31 | 0.31 | opened | 26 | Pankratovo 35/10 kv | 1 | 0 | 0.08 | 0.39 | 120 | -0.31 | 0 | 0.39 | 0.31 | 0.31 | opened
27 | Petrovskoe 35/10 kv | 1.6 | 0.23 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.54 | 0.54 | opened | 27 | Petrovskoe 35/10 kv | 1.6 | 0.024 | 0.254 | 0.77 | 120 | -0.516 | 0 | 0.77 | 0.516 | 0.516 | opened
28 | Kotelnikovo 35/10 kv | 1 | 0.1 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.16 | 0.16 | opened | 28 | Kotelnikovo 35/10 kv | 1 | 0.012 | 0.112 | 0.26 | 120 | -0.148 | 0 | 0.26 | 0.148 | 0.148 | opened
29 | Legitovo 35/10 kv | 2.5 | 0.33 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.77 | 0.77 | opened | 29 | Legitovo 35/10 kv | 2.5 | 0.02 | 0.35 | 1.1 | 120 | -0.75 | 0 | 1.1 | 0.75 | 0.75 | opened
30 | Sloboda 35/10 kv | 2.5 | 0.05 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 30 | Sloboda 35/10 kv | 2.5 | 0.009 | 0.059 | 0.85 | 120 | -0.791 | 0 | 0.85 | 0.791 | 0.791 | opened
31 | Zavrazhye 35/10 kv | 1.6 | 0.18 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.56 | 0.56 | opened | 31 | Zavrazhye 35/10 kv | 1.6 | 0.148 | 0.328 | 0.74 | 120 | -0.412 | 0 | 0.74 | 0.412 | 0.412 | opened
32 | Okulovo 35/10 kv | 1.6 | 0.17 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.73 | 0.73 | opened | 32 | Okulovo 35/10 kv | 1.6 | 0.336 | 0.506 | 0.9 | 120 | -0.394 | 0 | 0.9 | 0.394 | 0.394 | opened
33 | Chernyshevo 35/10 kv | 4 | 0.47 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.33 | 1.33 | opened | 33 | Chernyshevo 35/10 kv | 4 | 0.115 | 0.585 | 1.8 | 120 | -1.215 | 0 | 1.8 | 1.215 | 1.215 | opened
34 | Yakovlevo 110/35/10 kv | 10 | 0.08 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.22 | 5.22 | opened | 34 | Yakovlevo 110/35/10 kv | 10 | 0.056 | 0.136 | 5.3 | 120 | -5.164 | 0 | 5.3 | 5.164 | 5.164 | opened
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.08 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.22 |  |  |  | Nom. Capacity LV, MVA | 10 | 0.056 | 0.136 | 5.3 | 120 | -5.164 | 0 | 5.3 | 5.164
35 | Chermenino 35/10 kv | 1.6 | 0.08 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.78 | 0.78 | opened | 35 | Chermenino 35/10 kv | 1.6 | 0 | 0.08 | 0.86 | 120 | -0.78 | 0 | 0.86 | 0.78 | 0.78 | opened
36 | Nezhitino 35/10 kv | 1 | 0.12 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.42 | 0.42 | opened | 36 | Nezhitino 35/10 kv | 1 | 0.048 | 0.168 | 0.54 | 120 | -0.372 | 0 | 0.54 | 0.372 | 0.372 | opened
37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.37 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.62 | 0.62 | opened | 37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.13 | 0.5 | 0.99 | 120 | -0.49 | 0 | 0.99 | 0.49 | 0.49 | opened
38 | Gusevo 110/10 kv | 2.5 | 0.37 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.26 | 1.26 | opened | 38 | Gusevo 110/10 kv | 2.5 | 0.005 | 0.375 | 1.63 | 120 | -1.255 | 0 | 1.63 | 1.255 | 1.255 | opened
39 | Medveditsa 35/10 kv | 2.5 | 0.1 | 1.3 | 120 | 1.3 | 0 | 1.3 | 1.2 | 1.2 | opened | 39 | Medveditsa 35/10 kv | 2.5 | 0.024 | 0.124 | 1.3 | 120 | -1.176 | 0 | 1.3 | 1.176 | 1.176 | opened
40 | Novinskoe 110/10 kv | 2.5 | 0.05 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.18 | 1.18 | opened | 40 | Novinskoe 110/10 kv | 2.5 | 0 | 0.05 | 1.23 | 120 | -1.18 | 0 | 1.23 | 1.18 | 1.18 | opened
41 | Filino 35/10 kv | 1.6 | 0.35 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.61 | 0.61 | opened | 41 | Filino 35/10 kv | 1.6 | 0.248 | 0.598 | 0.96 | 120 | -0.362 | 0 | 0.96 | 0.362 | 0.362 | openedh
42 | Dyakonovo 110/10 kv | 2.5 | 0.25 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.88 | 0.88 | opened | 42 | Dyakonovo 110/10 kv | 2.5 | 0.086 | 0.336 | 1.13 | 120 | -0.794 | 0 | 1.13 | 0.794 | 0.794 | opened
43 | Oktyabrskaya 110/10 kv | 2.5 | 0.58 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.92 | 1.92 | opened | 43 | Oktyabrskaya 110/10 kv | 2.5 | 0.031 | 0.611 | 2.5 | 24 hours | -1.889 | 0 | 2.5 | 1.889 | 1.889 | opened
44 | Kuzhbal 35/10 kv | 2.5 | 0.27 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.21 | 1.21 | opened | 44 | Kuzhbal 35/10 kv | 2.5 | 0.019 | 0.289 | 1.48 | 120 | -1.191 | 0 | 1.48 | 1.191 | 1.191 | opened
45 | Nikolo-Poloma 110/10 kv | 2.5 | 0.95 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.18 | 0.18 | opened | 45 | Nikolo-Poloma 110/10 kv | 2.5 | 0.045 | 0.995 | 1.13 | 120 | -0.135 | 0 | 1.13 | 0.135 | 0.135 | opened
46 | Nikola 110/35/10 kv | 6.3 | 0.2 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.95 | 2.95 | opened | 46 | Nikola 110/35/10 kv | 6.3 | 0.037 | 0.237 | 3.15 | 120 | -2.913 | 0 | 3.15 | 2.913 | 2.913 | opened
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.2 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.95 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0.037 | 0.237 | 3.15 | 120 | -2.913 | 0 | 3.15 | 2.913
47 | Zavetluzhye 35/10 kv | 1.6 | 0.1 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.57 | 0.57 | opened | 47 | Zavetluzhye 35/10 kv | 1.6 | 0 | 0.1 | 0.67 | 120 | -0.57 | 0 | 0.67 | 0.57 | 0.57 | opened
48 | Talitsa 35/10 kv | 1.6 | 0.28 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.32 | 1.32 | opened | 48 | Talitsa 35/10 kv | 1.6 | 0 | 0.28 | 1.6 | 24 hours | -1.32 | 0 | 1.6 | 1.32 | 1.32 | opened
49 | Khoroshaya 35/10 kv | 2.5 | 0.05 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.9 | 1.9 | opened | 49 | Khoroshaya 35/10 kv | 2.5 | 0 | 0.05 | 1.95 | 120 | -1.9 | 0 | 1.95 | 1.9 | 1.9 | opened
50 | Zabegaevo 35/10 kv | 1.6 | 0.08 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.8 | 0.8 | opened | 50 | Zabegaevo 35/10 kv | 1.6 | 0.025 | 0.105 | 0.88 | 120 | -0.775 | 0 | 0.88 | 0.775 | 0.775 | opened
51 | Ilyinskoe 35/10 kv | 1.6 | 0.07 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.83 | 0.83 | opened | 51 | Ilyinskoe 35/10 kv | 1.6 | 0 | 0.07 | 0.9 | 120 | -0.83 | 0 | 0.9 | 0.83 | 0.83 | opened
52 | Luptyug 35/10 kv | 2.5 | 0.13 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.22 | 1.22 | opened | 52 | Luptyug 35/10 kv | 2.5 | 0.006 | 0.136 | 1.35 | 120 | -1.214 | 0 | 1.35 | 1.214 | 1.214 | opened
53 | Solovetskoe 35/10 kv | 1.6 | 0.08 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.64 | 0.64 | opened | 53 | Solovetskoe 35/10 kv | 1.6 | 0 | 0.08 | 0.72 | 120 | -0.64 | 0 | 0.72 | 0.64 | 0.64 | opened
54 | Gudkovo 110/10 kv | 2.5 | 0.08 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.3 | 1.3 | opened | 54 | Gudkovo 110/10 kv | 2.5 | 0.006 | 0.086 | 1.38 | 120 | -1.294 | 0 | 1.38 | 1.294 | 1.294 | opened
55 | Shortyug 110/10 kv | 6.3 | 0.38 | 3.47 | 120 | 3.47 | 0 | 3.47 | 3.09 | 3.09 | opened | 55 | Shortyug 110/10 kv | 6.3 | 0.073 | 0.453 | 3.47 | 120 | -3.017 | 0 | 3.47 | 3.017 | 3.017 | opened
56 | Yakshanga 110/10 kv | 6.3 | 1.17 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.3 | 2.3 | opened | 56 | Yakshanga 110/10 kv | 6.3 | 0.08 | 1.25 | 3.47 | 120 | -2.22 | 0 | 3.47 | 2.22 | 2.22 | opened
57 | Katunino 35/10 kv | 2.5 | 0.22 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.11 | 1.11 | opened | 57 | Katunino 35/10 kv | 2.5 | 0 | 0.22 | 1.33 | 120 | -1.11 | 0 | 1.33 | 1.11 | 1.11 | opened
58 | Konyovo 35/10 kv | 1.6 | 0.17 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.71 | 0.71 | opened | 58 | Konyovo 35/10 kv | 1.6 | 0 | 0.17 | 0.88 | 120 | -0.71 | 0 | 0.88 | 0.71 | 0.71 | opened
59 | Shekshema 110/10 kv | 6.3 | 0.28 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.22 | 2.22 | opened | 59 | Shekshema 110/10 kv | 6.3 | 0.05 | 0.33 | 2.5 | 24 hours | -2.17 | 0 | 2.5 | 2.17 | 2.17 | opened
60 | Golovino 35/10 kv | 1 | 0.05 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.07 | 0.07 | opened | 60 | Golovino 35/10 kv | 1 | 0 | 0.05 | 0.12 | 120 | -0.07 | 0 | 0.12 | 0.07 | 0.07 | opened
61 | Matveevskoe 35/10 kv | 1 | 0.02 | 0.69 | 120 | 0.69 | 0 | 0.69 | 0.67 | 0.67 | opened | 61 | Matveevskoe 35/10 kv | 1 | 0 | 0.02 | 0.69 | 120 | -0.67 | 0 | 0.69 | 0.67 | 0.67 | opened
62 | Pishchyovka 35/10 kv | 1 | 0.17 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.28 | 0.28 | opened | 62 | Pishchyovka 35/10 kv | 1 | 0.046 | 0.216 | 0.45 | 120 | -0.234 | 0 | 0.45 | 0.234 | 0.234 | opened
Two- and more transformer SS | [11 empty] | 1: Two- and more transformer SS
63 | Vasilyovo 110/35/10 kv | 10+10 | 2.04 | 0.86 | 120 | 1.18 | 0 | 10.5 | 9.32 | 9.32 | opened | 63 | Vasilyovo 110/35/10 kv | 10+10 | 4.381 | 6.421 | 0.86 | 120 | 5.561 | 0 | 10.5 | 4.939 | 4.939 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.75 | 0 | 120 | 0.75 | 0 | 10.5 | 9.75 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.75 | 0 | 120 | 0.75 | 0 | 10.5 | 9.75
| Nom. Capacity LV, MVA | 10+10 | 1.29 | 0.86 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 4.381 | 5.671 | 0.86 | 120 | 4.811 | 0 | 10.5 | 5.689
64 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 3.49 | 1.15 | 120 | 2.34 | 0 | 12.18 | 9.84 | 9.84 | opened | 64 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 0.395 | 3.885 | 1.15 | 120 | 2.735 | 0 | 12.18 | 9.445 | 9.445 | opened
| Nom. Capacity MV, MVA | 10+10+1,6 | 1.51 | 0 | 120 | 1.51 | 0 | 12.18 | 10.67 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 1.51 | 0 | 120 | 1.51 | 0 | 12.18 | 10.67
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.98 | 1.15 | 120 | 0.83 | 0 | 12.18 | 11.35 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.395 | 2.375 | 1.15 | 120 | 1.225 | 0 | 12.18 | 10.955
65 | Apraksino 35/10 kv | 2,5+2,5 | 1.69 | 0.425 | 120 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 65 | Apraksino 35/10 kv | 2,5+2,5 | 0.694 | 2.384 | 0.425 | 120 | 1.959 | 0 | 2.625 | 0.666 | 0.666 | opened
66 | Borshchino 35/10 kv | 4+4 | 0.66 | 0.62 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened | 66 | Borshchino 35/10 kv | 4+4 | 0.228 | 0.888 | 0.62 | 120 | 0.268 | 0 | 4.2 | 3.932 | 3.932 | opened
67 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened | 67 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.022 | 0.402 | 0.11 | 120 | 0.292 | 0 | 1.68 | 1.388 | 1.388 | opened
68 | Ilyinskoe 35/10 kv | 2,5+2,5 | 1.93 | 0.55 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | opened | 68 | Ilyinskoe 35/10 kv | 2,5+2,5 | 0.575 | 2.505 | 0.55 | 120 | 1.955 | 0 | 2.625 | 0.67 | 0.67 | opened
69 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.98 | 0.4 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 69 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.139 | 1.119 | 0.4 | 120 | 0.719 | 0 | 2.625 | 1.906 | 1.906 | opened
70 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.51 | 0.29 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 70 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.091 | 0.601 | 0.29 | 120 | 0.311 | 0 | 1.68 | 1.369 | 1.369 | opened
71 | Minskoe 35/10 kv | 2,5+2,5 | 1.13 | 0.43 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 71 | Minskoe 35/10 kv | 2,5+2,5 | 0.884 | 2.014 | 0.43 | 120 | 1.584 | 0 | 2.625 | 1.041 | 1.041 | opened
72 | Miskovo 35/6 kv | 1,8+1,8 | 0.36 | 0.2 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened | 72 | Miskovo 35/6 kv | 1,8+1,8 | 0.093 | 0.453 | 0.2 | 120 | 0.253 | 0 | 1.89 | 1.637 | 1.637 | opened
73 | Nikolskoe 35/6 kv | 4+4 | 2.42 | 0.92 | 120 | 1.5 | 0 | 4.2 | 2.7 | 2.7 | opened | 73 | Nikolskoe 35/6 kv | 4+4 | 0.964 | 3.384 | 0.92 | 120 | 2.464 | 0 | 4.2 | 1.736 | 1.736 | opened
74 | Samet 35/6 kv | 1,6+4 | 0.97 | 0 | 0 | 0.97 | 0 | 1.68 | 0.71 | 0.71 | opened | 74 | Samet 35/6 kv | 1,6+4 | 0.616 | 1.586 | 0 | 0 | 1.586 | 0 | 1.68 | 0.094 | 0.094 | opened
75 | Sukhonogovo 35/10 kv | 3,2+4 | 1.96 | 0 | 0 | 1.96 | 0 | 3.36 | 1.4 | 1.4 | opened | 75 | Sukhonogovo 35/10 kv | 3,2+4 | 0.565 | 2.525 | 0 | 0 | 2.525 | 0 | 3.36 | 0.835 | 0.835 | opened
76 | Sushchevo 35/10 kv | 4+4 | 3.24 | 0.76 | 120 | 2.48 | 0 | 4.2 | 1.72 | 1.72 | opened | 76 | Sushchevo 35/10 kv | 4+4 | 0.366 | 3.606 | 0.76 | 120 | 2.846 | 0 | 4.2 | 1.354 | 1.354 | opened
77 | EMZ 35/6 kv | 1+1 | 0.78 | 0 | 0 | 0.78 | 0 | 1.05 | 0.27 | 0.27 | opened | 77 | EMZ 35/6 kv | 1+1 | 0.006 | 0.786 | 0 | 0 | 0.786 | 0 | 1.05 | 0.264 | 0.264 | opened
78 | Krasnoe 110/35/10 kv | 16+16 | 9.76 | 0 | 0 | 9.76 | 0 | 16.8 | 7.04 | 7.04 | opened | 78 | Krasnoe 110/35/10 kv | 16+16 | 2.232 | 11.992 | 0 | 0 | 11.992 | 0 | 16.8 | 4.808 | 4.808 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.99 | 0 | 0 | 0.99 | 0 | 16.8 | 15.81 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.99 | 0 | 0 | 0.99 | 0 | 16.8 | 15.81
| Nom. Capacity LV, MVA | 16+16 | 8.77 | 0 | 0 | 8.77 | 0 | 16.8 | 8.03 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.232 | 11.002 | 0 | 0 | 11.002 | 0 | 16.8 | 5.798
79 | Isaevo 35/10 kv | 4+4 | 1.33 | 1.03 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 79 | Isaevo 35/10 kv | 4+4 | 3.085 | 4.415 | 1.03 | 120 | 3.385 | 0 | 4.2 | 0.815 | 0.815 | opened
80 | Chapaevo 35/10 kv | 2,5+2,5 | 0.78 | 0.43 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened | 80 | Chapaevo 35/10 kv | 2,5+2,5 | 0.103 | 0.883 | 0.43 | 120 | 0.453 | 0 | 2.625 | 2.172 | 2.172 | opened
81 | Chernevo 35/10 kv | 1,8+1,8 | 0.23 | 0.43 | 120 | -0.2 | 0 | 1.89 | 2.09 | 2.09 | opened | 81 | Chernevo 35/10 kv | 1,8+1,8 | 0.01 | 0.24 | 0.43 | 120 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | opened
82 | Nerekhta-1 110/35/10 kv | 25+25 | 17.94 | 2.75 | 120 | 15.19 | 0 | 26.25 | 11.06 | 11.06 | opened | 82 | Nerekhta-1 110/35/10 kv | 25+25 | 1.354 | 19.294 | 2.75 | 120 | 16.544 | 0 | 26.25 | 9.706 | 9.706 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.76 | 0 | 120 | 5.76 | 0 | 26.25 | 20.49 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.76 | 0 | 120 | 5.76 | 0 | 26.25 | 20.49
| Nom. Capacity LV, MVA | 25+25 | 10.38 | 2.75 | 120 | 7.63 | 0 | 26.25 | 18.62 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 1.354 | 11.734 | 2.75 | 120 | 8.984 | 0 | 26.25 | 17.266
| Nerekhta-1 110/10 kv | 16+16 | 1.8 | 2.2 | 120 | -0.4 | 0 | 16.8 | 17.2 |  | opened |  | Nerekhta-1 110/10 kv | 16+16 | 0 | 1.8 | 2.2 | 120 | -0.4 | 0 | 16.8 | 17.2 |  | opened
83 | Nerekhta-2 110/10/6 kv | 5,6+10 | 2.26 | 1.55 | 120 | 0.71 | 0 | 5.88 | 5.17 | 5.17 | opened | 83 | Nerekhta-2 110/10/6 kv | 5,6+10 | 1.322 | 3.582 | 1.55 | 120 | 2.032 | 0 | 5.88 | 3.848 | 3.848 | opened
84 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.36 | 0.41 | 120 | -0.05 | 0 | 1.68 | 1.73 | 1.73 | opened | 84 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.089 | 0.449 | 0.41 | 120 | 0.039 | 0 | 1.68 | 1.641 | 1.641 | opened
85 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.6 | 0.23 | 120 | 0.37 | 0 | 6.615 | 6.245 | 6.245 | opened | 85 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.011 | 0.611 | 0.23 | 120 | 0.381 | 0 | 6.615 | 6.234 | 6.234 | opened
86 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 4.81 | 0.76 | 120 | 4.05 | 0 | 6.615 | 2.565 | 2.565 | opened | 86 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 0.131 | 4.941 | 0.76 | 120 | 4.181 | 0 | 6.615 | 2.434 | 2.434 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 3.07 | 0 | 120 | 3.07 | 0 | 6.615 | 3.545 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 3.07 | 0 | 120 | 3.07 | 0 | 6.615 | 3.545
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.74 | 0.76 | 120 | 0.98 | 0 | 6.615 | 5.635 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.131 | 1.871 | 0.76 | 120 | 1.111 | 0 | 6.615 | 5.504
87 | Krasnaya Polyana 110/35/10 kv | 10+10 | 4.37 | 1.28 | 120 | 3.09 | 0 | 10.5 | 7.41 | 7.41 | opened | 87 | Krasnaya Polyana 110/35/10 kv | 10+10 | 0.131 | 4.501 | 1.28 | 120 | 3.221 | 0 | 10.5 | 7.279 | 7.279 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.41 | 0 | 120 | 1.41 | 0 | 10.5 | 9.09 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.41 | 0 | 120 | 1.41 | 0 | 10.5 | 9.09
| Nom. Capacity LV, MVA | 10+10 | 2.96 | 1.28 | 120 | 1.68 | 0 | 10.5 | 8.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.131 | 3.091 | 1.28 | 120 | 1.811 | 0 | 10.5 | 8.689
88 | Igodovo 35/10 kv | 1,6+1,6 | 0.34 | 0.25 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 88 | Igodovo 35/10 kv | 1,6+1,6 | 0.122 | 0.462 | 0.25 | 120 | 0.212 | 0 | 1.68 | 1.468 | 1.468 | opened
89 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.82 | 0.56 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | opened | 89 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.078 | 0.898 | 0.56 | 120 | 0.338 | 0 | 1.68 | 1.342 | 1.342 | opened
90 | Ostrovskoe 35/10 kv | 2,5+2,5 | 1.13 | 0.52 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | opened | 90 | Ostrovskoe 35/10 kv | 2,5+2,5 | 0.079 | 1.209 | 0.52 | 120 | 0.689 | 0 | 2.625 | 1.936 | 1.936 | opened
91 | Sudislavl 110/10 kv | 10+10 | 6 | 1.8 | 120 | 4.2 | 0 | 10.5 | 6.3 | 6.3 | opened | 91 | Sudislavl 110/10 kv | 10+10 | 0.857 | 6.857 | 1.8 | 120 | 5.057 | 0 | 10.5 | 5.443 | 5.443 | opened
92 | Voronye 35/10 kv | 1,8+1,8 | 0.51 | 0.4 | 120 | 0.11 | 0 | 1.89 | 1.78 | 1.78 | opened | 92 | Voronye 35/10 kv | 1,8+1,8 | 0.044 | 0.554 | 0.4 | 120 | 0.154 | 0 | 1.89 | 1.736 | 1.736 | opened
93 | Susanino 110/35/10 kv | 10+10 | 5.9 | 1.89 | 120 | 4.01 | 0 | 10.5 | 6.49 | 6.49 | opened | 93 | Susanino 110/35/10 kv | 10+10 | 0.579 | 6.479 | 1.89 | 120 | 4.589 | 0 | 10.5 | 5.911 | 5.911 | opened
| Nom. Capacity MV, MVA | 10+10 | 2.96 | 0 | 120 | 2.96 | 0 | 10.5 | 7.54 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 2.96 | 0 | 120 | 2.96 | 0 | 10.5 | 7.54
| Nom. Capacity LV, MVA | 10+10 | 2.94 | 1.89 | 120 | 1.05 | 0 | 10.5 | 9.45 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.579 | 3.519 | 1.89 | 120 | 1.629 | 0 | 10.5 | 8.871
94 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.16 | 0.07 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 94 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.016 | 0.176 | 0.07 | 120 | 0.106 | 0 | 2.625 | 2.519 | 2.519 | opened
95 | Airport 110/35/6 kv | 16+16 | 5.95 | 2.88 | 120 | 3.07 | 0 | 16.8 | 13.73 | 13.73 | opened | 95 | Airport 110/35/6 kv | 16+16 | 3.23 | 9.18 | 2.88 | 120 | 6.3 | 0 | 16.8 | 10.5 | 10.5 | opened
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.95 | 2.88 | 120 | 3.07 | 0 | 16.8 | 13.73 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 3.23 | 9.18 | 2.88 | 120 | 6.3 | 0 | 16.8 | 10.5
96 | Vostochnaya-2 110/35/10 kv | 25+25 | 25.58 | 0.02 | 120 | 25.56 | 0 | 26.25 | 0.69 | 0.69 | opened | 96 | Vostochnaya-2 110/35/10 kv | 25+25 | 0.613 | 26.193 | 0.02 | 120 | 26.173 | 0 | 26.25 | 0.077 | 0.077 | opened
| Nom. Capacity MV, MVA | 25+25 | 21.51 | 0 | 120 | 21.51 | 0 | 26.25 | 4.74 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 21.51 | 0 | 120 | 21.51 | 0 | 26.25 | 4.74
| Nom. Capacity LV, MVA | 25+25 | 4.07 | 0.02 | 120 | 4.05 | 0 | 26.25 | 22.2 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.613 | 4.683 | 0.02 | 120 | 4.663 | 0 | 26.25 | 21.587
97 | Kostroma-3 110/35/10 kv | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69 | 1.69 | opened | 97 | Kostroma-3 110/35/10 kv | 10+16 | 1.298 | 10.108 | 0 | 120 | 10.108 | 0 | 10.5 | 0.392 | 0.392 | opened
| Nom. Capacity MV, MVA | 10+16 | 1.76 | 0 | 120 | 1.76 | 0 | 10.5 | 8.74 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 1.76 | 0 | 120 | 1.76 | 0 | 10.5 | 8.74
| Nom. Capacity LV, MVA | 10+16 | 7.05 | 0 | 120 | 7.05 | 0 | 10.5 | 3.45 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.298 | 8.348 | 0 | 120 | 8.348 | 0 | 10.5 | 2.152
98 | Yuzhnaya 110/35/10 kv | 25+25 | 15.12 | 0 | 120 | 15.12 | 0 | 26.25 | 11.13 | 11.13 | opened | 98 | Yuzhnaya 110/35/10 kv | 25+25 | 7.77 | 22.89 | 0 | 120 | 22.89 | 0 | 26.25 | 3.36 | 3.36 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.55 | 0 | 120 | 5.55 | 0 | 26.25 | 20.7 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.55 | 0 | 120 | 5.55 | 0 | 26.25 | 20.7
| Nom. Capacity LV, MVA | 25+25 | 9.57 | 0 | 120 | 9.57 | 0 | 26.25 | 16.68 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 7.77 | 17.34 | 0 | 120 | 17.34 | 0 | 26.25 | 8.91
99 | Davydovskaya 110/10 kv | 25+25 | 8.08 | 0.02 | 120 | 8.06 | 0 | 26.25 | 18.19 | 18.19 | opened | 99 | Davydovskaya 110/10 kv | 25+25 | 8.59 | 16.67 | 0.02 | 120 | 16.65 | 0 | 26.25 | 9.6 | 9.6 | opened | put in 09.2009
100 | Kostroma-1 110/6 kv | 10+10 | 10.08 | 0 | 0 | 10.08 | 0 | 10.5 | 0.42 | 0.42 | opened | 100 | Kostroma-1 110/6 kv | 10+10 | 1.624 | 11.704 | 0 | 0 | 11.704 | 0 | 10.5 | -1.204 | -1.204 | closed
101 | Severnaya 110/6 kv | 20+25 | 17.9 | 0 | 0 | 17.9 | 0 | 21 | 3.1 | 3.1 | opened | 101 | Severnaya 110/6 kv | 20+25 | 6.421 | 24.321 | 0 | 0 | 24.321 | 0 | 21 | -3.321 | -3.321 | closed
102 | Strommashina 110/6 kv | 40+40 | 8.81 | 0 | 0 | 8.81 | 0 | 42 | 33.19 | 33.19 | opened | 102 | Strommashina 110/6 kv | 40+40 | 7.284 | 16.094 | 0 | 0 | 16.094 | 0 | 42 | 25.906 | 25.906 | opened
103 | Tsentralnaya 110/10/6 kv | 25+25 | 15.63 | 0 | 0 | 15.63 | 0 | 26.25 | 10.62 | 10.62 | opened | 103 | Tsentralnaya 110/10/6 kv | 25+25 | 11.614 | 27.244 | 0 | 0 | 27.244 | 0 | 26.25 | -0.994 | -0.994 | closed
104 | Baydarka 35/6 kv | 6,3+6,3 | 2.26 | 1.2 | 120 | 1.06 | 0 | 6.615 | 5.555 | 5.555 | opened | 104 | Baydarka 35/6 kv | 6,3+6,3 | 1.032 | 3.292 | 1.2 | 120 | 2.092 | 0 | 6.615 | 4.523 | 4.523 | opened
105 | Volzhskaya 35/6 kv | 4+4 | 1 | 0.76 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 105 | Volzhskaya 35/6 kv | 4+4 | 0.337 | 1.337 | 0.76 | 120 | 0.577 | 0 | 4.2 | 3.623 | 3.623 | opened
106 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 19.44 | 0 | 0 | 19.44 | 0 | 17.115 | -2.325 | -2.325 | closed | 106 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 2.099 | 21.539 | 0 | 0 | 21.539 | 0 | 17.115 | -4.424 | -4.424 | closed
107 | Karavaevo 35/10 kv | 6,3+6,3 | 3.92 | 0 | 0 | 3.92 | 0 | 6.615 | 2.695 | 2.695 | opened | 107 | Karavaevo 35/10 kv | 6,3+6,3 | 1.718 | 5.638 | 0 | 0 | 5.638 | 0 | 6.615 | 0.977 | 0.977 | opened
108 | Korkino 35/10 kv | 2,5+2,5 | 2.13 | 0.85 | 120 | 1.28 | 0 | 2.625 | 1.345 | 1.345 | opened | 108 | Korkino 35/10 kv | 2,5+2,5 | 0.537 | 2.667 | 0.85 | 120 | 1.817 | 0 | 2.625 | 0.808 | 0.808 | opened
109 | KPD 110/35/10 kv | 16+16 | 4.64 | 1.44 | 120 | 3.2 | 0 | 16.8 | 13.6 | 13.6 | opened | 109 | KPD 110/35/10 kv | 16+16 | 0 | 4.64 | 1.44 | 120 | 3.2 | 0 | 16.8 | 13.6 | 13.6 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.39 | 0 | 120 | 0.39 | 0 | 16.8 | 16.41 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.39 | 0 | 120 | 0.39 | 0 | 16.8 | 16.41
| Nom. Capacity LV, MVA | 16+16 | 4.25 | 1.44 | 120 | 2.81 | 0 | 16.8 | 13.99 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 0 | 4.25 | 1.44 | 120 | 2.81 | 0 | 16.8 | 13.99
110 | SM State district power station 110/35/6 kv | 10+16 | 6.75 | 0 | 0 | 6.75 | 0 | 10.5 | 3.75 | 3.75 | opened | 110 | SM State district power station 110/35/6 kv | 10+16 | 3.522 | 10.272 | 0 | 0 | 10.272 | 0 | 10.5 | 0.228 | 0.228 | opened
| Nom. Capacity MV, MVA | 10+16 | 0.71 | 0 | 0 | 0.71 | 0 | 10.5 | 9.79 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.71 | 0 | 0 | 0.71 | 0 | 10.5 | 9.79
| Nom. Capacity LV, MVA | 10+16 | 6.04 | 0 | 0 | 6.04 | 0 | 10.5 | 4.46 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 3.522 | 9.562 | 0 | 0 | 9.562 | 0 | 10.5 | 0.938
111 | Sidorovskoe 35/6 kv | 2,5+4 | 1.18 | 0.82 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 111 | Sidorovskoe 35/6 kv | 2,5+4 | 0.14 | 1.32 | 0.82 | 120 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
112 | Buy (r) 110/35/10 kv | 4+10 | 0.9 | 0 | 0 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened | 112 | Buy (r) 110/35/10 kv | 4+10 | 12.751 | 13.651 | 0 | 120 | 13.651 | 0 | 4.2 | -9.451 | -9.451 | closed
| Nom. Capacity MV, MVA | 4+10 | 0.9 | 0 | 0 | 0.9 | 0 | 4.2 | 3.3 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 12.345 | 13.245 | 0 | 120 | 13.245 | 0 | 4.2 | -9.045
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0.406 | 0.406 | 0 | 120 | 0.406 | 0 | 4.2 | 3.794
113 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 5.52 | 1.2 | 120 | 4.32 | 0 | 6.615 | 2.295 | 2.295 | opened | 113 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 1.335 | 6.855 | 1.2 | 120 | 5.655 | 0 | 6.615 | 0.96 | 0.96 | opened
114 | Zapadnaya 110/10 kv | 10+10 | 3.6 | 2.63 | 120 | 0.97 | 0 | 10.5 | 9.53 | 9.53 | opened | 114 | Zapadnaya 110/10 kv | 10+10 | 0.012 | 3.612 | 2.63 | 120 | 0.982 | 0 | 10.5 | 9.518 | 9.518 | opened
115 | Dor 35/10 kv | 1,6+1,6 | 0.52 | 0.06 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened | 115 | Dor 35/10 kv | 1,6+1,6 | 0.083 | 0.603 | 0.06 | 120 | 0.543 | 0 | 1.68 | 1.137 | 1.137 | opened
116 | Dyakonovo 35/10 kv | 1+1 | 0.24 | 0.26 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | opened | 116 | Dyakonovo 35/10 kv | 1+1 | 0.071 | 0.311 | 0.26 | 120 | 0.051 | 0 | 1.05 | 0.999 | 0.999 | opened
117 | Likurga 35/10 kv | 1,8+1,6 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 117 | Likurga 35/10 kv | 1,8+1,6 | 0.009 | 0.129 | 0.12 | 120 | 0.009 | 0 | 1.68 | 1.671 | 1.671 | opened
118 | Shushkodom 35/10 kv | 1+1 | 0.28 | 0.06 | 120 | 0.22 | 0 | 1.05 | 0.83 | 0.83 | opened | 118 | Shushkodom 35/10 kv | 1+1 | 0.012 | 0.292 | 0.06 | 120 | 0.232 | 0 | 1.05 | 0.818 | 0.818 | opened
119 | Novaya 110/35/10 kv | 6,3+6,3 | 1.54 | 0.64 | 120 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 119 | Novaya 110/35/10 kv | 6,3+6,3 | 0.76 | 2.3 | 0.64 | 120 | 1.66 | 0 | 6.615 | 4.955 | 4.955 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.34 | 0 | 120 | 0.34 | 0 | 6.615 | 6.275 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.34 | 0 | 120 | 0.34 | 0 | 6.615 | 6.275
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.2 | 0.64 | 120 | 0.56 | 0 | 6.615 | 6.055 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.76 | 1.96 | 0.64 | 120 | 1.32 | 0 | 6.615 | 5.295
120 | Orekhovo 110/35/10 kv | 6,3+6,3 | 1.84 | 0 | 120 | 1.84 | 0 | 6.615 | 4.775 | 4.775 | opened | 120 | Orekhovo 110/35/10 kv | 6,3+6,3 | 0.179 | 2.019 | 0 | 120 | 2.019 | 0 | 6.615 | 4.596 | 4.596 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.2 | 0 | 120 | 1.2 | 0 | 6.615 | 5.415 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.2 | 0 | 120 | 1.2 | 0 | 6.615 | 5.415
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.64 | 0 | 120 | 0.64 | 0 | 6.615 | 5.975 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.179 | 0.819 | 0 | 120 | 0.819 | 0 | 6.615 | 5.796
121 | Loparevo 110/10 kv | 2,5+2,5 | 0.36 | 0.55 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 121 | Loparevo 110/10 kv | 2,5+2,5 | 0.273 | 0.633 | 0.55 | 120 | 0.083 | 0 | 2.625 | 2.542 | 2.542 | opened
122 | Poultry farm 35/10 kv | 4+4 | 1 | 1.28 | 120 | -0.28 | 0 | 4.2 | 4.48 | 4.48 | opened | 122 | Poultry farm 35/10 kv | 4+4 | 0 | 1 | 1.28 | 120 | -0.28 | 0 | 4.2 | 4.48 | 4.48 | opened
123 | Kabanovo 35/10 kv | 2,5+2,5 | 0.12 | 0.22 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 123 | Kabanovo 35/10 kv | 2,5+2,5 | 0.011 | 0.131 | 0.22 | 120 | -0.089 | 0 | 2.625 | 2.714 | 2.714 | opened
124 | Levkovo 35/10 kv | 1,6+1,6 | 0.4 | 0.74 | 120 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | opened | 124 | Levkovo 35/10 kv | 1,6+1,6 | 0 | 0.4 | 0.74 | 120 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | opened
125 | Pronino 35/10 kv | 4+2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 125 | Pronino 35/10 kv | 4+2,5 | 0.015 | 0.375 | 0.2 | 120 | 0.175 | 0 | 2.625 | 2.45 | 2.45 | opened
126 | Toltunovo 35/10 kv | 2,5+2,5 | 0.16 | 0.13 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 126 | Toltunovo 35/10 kv | 2,5+2,5 | 0.299 | 0.459 | 0.13 | 120 | 0.329 | 0 | 2.625 | 2.296 | 2.296 | opened
127 | Soligalich 110/35/10 kv | 10+10 | 3.7 | 1.7 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | opened | 127 | Soligalich 110/35/10 kv | 10+10 | 1.063 | 4.763 | 1.7 | 120 | 3.063 | 0 | 10.5 | 7.437 | 7.437 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.7 | 0 | 120 | 0.7 | 0 | 10.5 | 9.8 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.7 | 0 | 120 | 0.7 | 0 | 10.5 | 9.8
| Nom. Capacity LV, MVA | 10+10 | 3 | 1.7 | 120 | 1.3 | 0 | 10.5 | 9.2 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.063 | 4.063 | 1.7 | 120 | 2.363 | 0 | 10.5 | 8.137
128 | Pochinok 35/10 kv | 1,6+2,5 | 0.48 | 0.34 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 128 | Pochinok 35/10 kv | 1,6+2,5 | 0.028 | 0.508 | 0.34 | 120 | 0.168 | 0 | 1.68 | 1.512 | 1.512 | opened
129 | Chukhloma 110/35/10 kv | 6,3+6,3 | 1.6 | 2.06 | 120 | -0.46 | 0 | 6.615 | 7.075 | 6.615 | opened | 129 | Chukhloma 110/35/10 kv | 6,3+6,3 | 0.678 | 2.278 | 2.06 | 120 | 0.218 | 0 | 6.615 | 6.397 | 6.397 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0 | 120 | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.6 | 2.06 | 120 | -0.46 | 0 | 6.615 | 7.075 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.678 | 2.278 | 2.06 | 120 | 0.218 | 0 | 6.615 | 6.397
130 | Suday 35/10 kv | 1,6+1,6 | 0.64 | 0.49 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 130 | Suday 35/10 kv | 1,6+1,6 | 0.072 | 0.712 | 0.49 | 120 | 0.222 | 0 | 1.68 | 1.458 | 1.458 | opened
131 | Antropovo (r) 110/35/10 kv | 6,3+16 | 4.31 | 0.38 | 120 | 3.93 | 0 | 6.615 | 2.685 | 2.685 | opened | 131 | Antropovo (r) 110/35/10 kv | 6,3+16 | 0.229 | 4.539 | 0.38 | 120 | 4.159 | 0 | 6.615 | 2.456 | 2.456 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675
| Nom. Capacity LV, MVA | 6,3+16 | 1.37 | 0.38 | 120 | 0.99 | 0 | 6.615 | 5.625 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.229 | 1.599 | 0.38 | 120 | 1.219 | 0 | 6.615 | 5.396
132 | Palkino 35/10 kv | 2,5+4 | 0.66 | 0.45 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 132 | Palkino 35/10 kv | 2,5+4 | 0.102 | 0.762 | 0.45 | 120 | 0.312 | 0 | 2.625 | 2.313 | 2.313 | opened
133 | Slovinka 35/10 kv | 1,6+1,6 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened | 133 | Slovinka 35/10 kv | 1,6+1,6 | 0.006 | 0.156 | 0.1 | 120 | 0.056 | 0 | 1.68 | 1.624 | 1.624 | opened
134 | Kady 110/35/10 kv | 10+10 | 2.73 | 0.69 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | opened | 134 | Kady 110/35/10 kv | 10+10 | 0.517 | 3.247 | 0.69 | 120 | 2.557 | 0 | 10.5 | 7.943 | 7.943 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.83 | 0 | 120 | 0.83 | 0 | 10.5 | 9.67 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.83 | 0 | 120 | 0.83 | 0 | 10.5 | 9.67
| Nom. Capacity LV, MVA | 10+10 | 1.9 | 0.69 | 120 | 1.21 | 0 | 10.5 | 9.29 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.517 | 2.417 | 0.69 | 120 | 1.727 | 0 | 10.5 | 8.773
135 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.1 | 0.1 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 135 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.025 | 0.125 | 0.1 | 120 | 0.025 | 0 | 1.68 | 1.655 | 1.655 | opened
136 | Ilyinskoe 110/35/10 kv | 10+10 | 4.13 | 0.04 | 120 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened | 136 | Ilyinskoe 110/35/10 kv | 10+10 | 0.012 | 4.142 | 0.04 | 120 | 4.102 | 0 | 10.5 | 6.398 | 6.398 | opened
| Nom. Capacity MV, MVA | 10+10 | 4.06 | 0 | 120 | 4.06 | 0 | 10.5 | 6.44 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 4.06 | 0 | 120 | 4.06 | 0 | 10.5 | 6.44
| Nom. Capacity LV, MVA | 10+10 | 0.07 | 0.04 | 120 | 0.03 | 0 | 10.5 | 10.47 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.012 | 0.082 | 0.04 | 120 | 0.042 | 0 | 10.5 | 10.458
137 | Kologriv 35/10 kv | 4+4 | 1.42 | 1.42 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 137 | Kologriv 35/10 kv | 4+4 | 0.239 | 1.659 | 1.42 | 120 | 0.239 | 0 | 4.2 | 3.961 | 3.961 | opened
138 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.2 | 0.08 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 138 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.034 | 0.234 | 0.08 | 120 | 0.154 | 0 | 1.68 | 1.526 | 1.526 | opened
139 | Makaryev-1 110/35/10 kv | 10+10 | 1.65 | 0.8 | 120 | 0.85 | 0 | 10.5 | 9.65 | 8.85 | opened | 139 | Makaryev-1 110/35/10 kv | 10+10 | 0.174 | 1.824 | 0.8 | 120 | 1.024 | 0 | 10.5 | 9.476 | 8.85 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.65 | 0 | 120 | 1.65 | 0 | 10.5 | 8.85 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.65 | 0 | 120 | 1.65 | 0 | 10.5 | 8.85
| Nom. Capacity MV, MVA | 10+10 | 0 | 0.8 | 120 | -0.8 | 0 | 10.5 | 11.3 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.174 | 0.174 | 0.8 | 120 | -0.626 | 0 | 10.5 | 11.126
140 | Gorchukha 35/10 kv | 2,5+2,5 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened | 140 | Gorchukha 35/10 kv | 2,5+2,5 | 0.034 | 0.784 | 0 | 0 | 0.784 | 0 | 2.625 | 1.841 | 1.841 | opened
141 | Makaryev-2 35/10 kv | 4+4 | 1.5 | 1.58 | 120 | -0.08 | 0 | 4.2 | 4.28 | 4.28 | opened | 141 | Makaryev-2 35/10 kv | 4+4 | 0.455 | 1.955 | 1.58 | 120 | 0.375 | 0 | 4.2 | 3.825 | 3.825 | opened
142 | Timoshino 35/10 kv | 1+1 | 0.12 | 0 | 0 | 0.12 | 0 | 1.05 | 0.93 | 0.93 | opened | 142 | Timoshino 35/10 kv | 1+1 | 0.084 | 0.204 | 0 | 0 | 0.204 | 0 | 1.05 | 0.846 | 0.846 | opened
143 | Unzha 35/10 kv | 1+1,6 | 0.25 | 0.1 | 120 | 0.15 | 0 | 1.05 | 0.9 | 0.9 | opened | 143 | Unzha 35/10 kv | 1+1,6 | 0.025 | 0.275 | 0.1 | 120 | 0.175 | 0 | 1.05 | 0.875 | 0.875 | opened
144 | Yakimovo 35/10 kv | 1,6+2,5 | 0.15 | 0.32 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened | 144 | Yakimovo 35/10 kv | 1,6+2,5 | 0.018 | 0.168 | 0.32 | 120 | -0.152 | 0 | 1.68 | 1.832 | 1.832 | opened
145 | BKhZ 110/6 kv | 25+25 | 0.72 | 0 | 0 | 0.72 | 0 | 26.25 | 25.53 | 25.53 | opened | 145 | BKhZ 110/6 kv | 25+25 | 0.162 | 0.882 | 0 | 0 | 0.882 | 0 | 26.25 | 25.368 | 25.368 | opened
146 | Sosnovka 35/10 kv | 2,5+1,6 | 0.22 | 0.15 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | opened | 146 | Sosnovka 35/10 kv | 2,5+1,6 | 0.06 | 0.28 | 0.15 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
147 | Georgievskoe 35/10 kv | 2,5+2,5 | 1.62 | 1.23 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened | 147 | Georgievskoe 35/10 kv | 2,5+2,5 | 0.696 | 2.316 | 1.23 | 120 | 1.086 | 0 | 2.625 | 1.539 | 1.539 | opened
148 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 7.36 | 3.6 | 120 | 3.76 | 0 | 48.615 | 44.855 | 44.855 | opened | 148 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 0.783 | 8.143 | 3.6 | 120 | 4.543 | 0 | 48.615 | 44.072 | 44.072 | opened
| Nom. Capacity MV, MVA | 40+40+6,3 | 1.19 | 0 | 120 | 1.19 | 0 | 48.615 | 47.425 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 1.19 | 0 | 120 | 1.19 | 0 | 48.615 | 47.425
| Nom. Capacity LV, MVA | 40+40+6,3 | 6.17 | 3.6 | 120 | 2.57 | 0 | 48.615 | 46.045 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.783 | 6.953 | 3.6 | 120 | 3.353 | 0 | 48.615 | 45.262
149 | Vozherovo 35/10 kv | 1,6+1,6 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 149 | Vozherovo 35/10 kv | 1,6+1,6 | 0 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
150 | Matveevo 35/10 kv | 1,8+4 | 0.38 | 0.42 | 120 | -0.04 | 0 | 1.89 | 1.93 | 1.93 | opened | 150 | Matveevo 35/10 kv | 1,8+4 | 0.031 | 0.411 | 0.42 | 120 | -0.009 | 0 | 1.89 | 1.899 | 1.899 | opened
151 | Parfenyevo 35/10 kv | 4+4 | 2.02 | 1.89 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | opened | 151 | Parfenyevo 35/10 kv | 4+4 | 0.764 | 2.784 | 1.89 | 120 | 0.894 | 0 | 4.2 | 3.306 | 3.306 | opened
152 | Vokhma 110/35/10 kv | 6,3+16 | 4.85 | 0 | 0 | 4.85 | 0 | 6.615 | 1.765 | 1.765 | opened | 152 | Vokhma 110/35/10 kv | 6,3+16 | 0.488 | 5.338 | 0 | 0 | 5.338 | 0 | 6.615 | 1.277 | 1.277 | opened
| Nom. Capacity MV, MVA | 6,3+8 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity MV, MVA | 6,3+8 | 0 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315
| Nom. Capacity LV, MVA | 6,3+8 | 2.55 | 0 | 0 | 2.55 | 0 | 6.615 | 4.065 |  |  |  | Nom. Capacity LV, MVA | 6,3+8 | 0.488 | 3.038 | 0 | 0 | 3.038 | 0 | 6.615 | 3.577
153 | Lapshino 35/10 kv | 2,5+2,5 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 153 | Lapshino 35/10 kv | 2,5+2,5 | 0 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
154 | Spass 35/10 kv | 1,6+2,5 | 0.4 | 0.35 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened | 154 | Spass 35/10 kv | 1,6+2,5 | 0.012 | 0.412 | 0.35 | 120 | 0.062 | 0 | 1.68 | 1.618 | 1.618 | opened
155 | Bogovarovo 35/10 kv | 2,5+4 | 1.47 | 1 | 120 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened | 155 | Bogovarovo 35/10 kv | 2,5+4 | 0.273 | 1.743 | 1 | 120 | 0.743 | 0 | 2.625 | 1.882 | 1.882 | opened
156 | Pavino 110/35/10 kv | 10+6,3 | 1.96 | 0 | 0 | 1.96 | 0 | 6.615 | 4.655 | 4.655 | opened | 156 | Pavino 110/35/10 kv | 10+6,3 | 0.088 | 2.048 | 0 | 0 | 2.048 | 0 | 6.615 | 4.567 | 4.567 | opened
| Nom. Capacity MV, MVA | 10+6,3 | 0.36 | 0 | 0 | 0.36 | 0 | 6.615 | 6.255 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.36 | 0 | 0 | 0.36 | 0 | 6.615 | 6.255
| Nom. Capacity LV, MVA | 10+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 6.615 | 5.015 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.088 | 1.688 | 0 | 0 | 1.688 | 0 | 6.615 | 4.927
157 | Ledengskaya 35/10 kv | 1,6+4 | 0.07 | 0.07 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 157 | Ledengskaya 35/10 kv | 1,6+4 | 0.011 | 0.081 | 0.07 | 120 | 0.011 | 0 | 1.68 | 1.669 | 1.669 | opened
158 | Pyshchug 110/35/10 kv | 6,3+6,3 | 2.09 | 0 | 0 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened | 158 | Pyshchug 110/35/10 kv | 6,3+6,3 | 0.22 | 2.31 | 0 | 0 | 2.31 | 0 | 6.615 | 4.305 | 4.305 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.97 | 0 | 0 | 1.97 | 0 | 6.615 | 4.645 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.22 | 2.19 | 0 | 0 | 2.19 | 0 | 6.615 | 4.425
159 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 1.55 | 0.75 | 120 | 0.8 | 0 | 4.2 | 3.4 | 3.4 | opened | 159 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 0.133 | 1.683 | 0.75 | 120 | 0.933 | 0 | 4.2 | 3.267 | 3.267 | opened
| Nom. Capacity MV, MVA | 10+4 | 0.55 | 0 | 120 | 0.55 | 0 | 4.2 | 3.65 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.55 | 0 | 120 | 0.55 | 0 | 4.2 | 3.65
| Nom. Capacity LV, MVA | 10+4 | 1 | 0.75 | 120 | 0.25 | 0 | 4.2 | 3.95 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.133 | 1.133 | 0.75 | 120 | 0.383 | 0 | 4.2 | 3.817
160 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.27 | 0.27 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 160 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.024 | 0.294 | 0.27 | 120 | 0.024 | 0 | 1.68 | 1.656 | 1.656 | opened
161 | Sharya (r) 110/35/6 kv | 20+25 | 14.09 | 2 | 120 | 12.09 | 0 | 21 | 8.91 | 8.91 | opened | 161 | Sharya (r) 110/35/6 kv | 20+25 | 0.581 | 14.671 | 2 | 120 | 12.671 | 0 | 21 | 8.329 | 8.329 | opened
| Nom. Capacity MV, MVA | 20+25 | 8.24 | 0 | 120 | 8.24 | 0 | 21 | 12.76 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 8.24 | 0 | 120 | 8.24 | 0 | 21 | 12.76
| Nom. Capacity LV, MVA | 20+25 | 5.85 | 2 | 120 | 3.85 | 0 | 21 | 17.15 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.581 | 6.431 | 2 | 120 | 4.431 | 0 | 21 | 16.569
162 | Industrial hub 110/6/6 kv | 25+25 | 3.15 | 2.5 | 120 | 0.65 | 0 | 26.25 | 25.6 | 25.6 | opened | 162 | Industrial hub 110/6/6 kv | 25+25 | 0.778 | 3.928 | 2.5 | 120 | 1.428 | 0 | 26.25 | 24.822 | 24.822 | opened
163 | Krivyachka 35/10 kv | 1,6+1 | 0.47 | 0.57 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened | 163 | Krivyachka 35/10 kv | 1,6+1 | 0.041 | 0.511 | 0.57 | 120 | -0.059 | 0 | 1.05 | 1.109 | 1.109 | opened
164 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 164 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.031 | 0.831 | 0 | 0 | 0.831 | 0 | 1.68 | 0.849 | 0.849 | opened
165 | Tsentralnaya 35/6 kv | 10+10 | 8.1 | 3 | 120 | 5.1 | 0 | 10.5 | 5.4 | 5.4 | opened | 165 | Tsentralnaya 35/6 kv | 10+10 | 3.44 | 11.54 | 3 | 120 | 8.54 | 0 | 10.5 | 1.96 | 1.96 | opened
| Total over Kostromaenergo | 1706 | 349.09 | [8 empty] | 2: Total over Kostromaenergo; 3: 1706; 5: 462.839
| deficit | [8 empty] | -2.325 |  | 2: deficit; Min. 12: -19.394
| proficit | [8 empty] | 572.88 |  | 2: proficit; Min. 12: 476.834
|  | Head of perspective and technical development service | [6 empty] | N.I.Burmistrov
|  | Deputy Director for technical issues- chief engineer of the branch of IDGC of Centre, JSC - "Kostromaenergo" | [6 empty] | E.A.Smirnov

## Орелэнерго
table 1
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit /proficit of main substation, MVA |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main Susbstation, MVA | Deficit /proficit of Main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kv Almazovo | 2.5 | 0.33 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.5 | 0.5 | opened | 1 | SS 35/10 kv Almazovo | 2.5 | 0.035 | 0.365 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.465 | 0.465 | opened
2 | SS 35/10 kv Voronets | 2.5 | 0.25 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.66 | 0.66 | opened | 2 | SS 35/10 kv Voronets | 2.5 | 0 | 0.25 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.66 | 0.66 | opened
3 | SS 35/10 kv Gostoml | 2.5 | 0.62 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.04 | 0.04 | opened | 3 | SS 35/10 kv Gostoml | 2.5 | 0.018 | 0.638 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.022 | 0.022 | opened
4 | SS 35/10 kv Gubkino | 3.2 | 0.51 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.05 | 1.05 | opened | 4 | SS 35/10 kv Gubkino | 3.2 | 0.038 | 0.548 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.012 | 1.012 | opened
5 | SS 35/10 kv Devyztino | 1.6 | 0.3 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.41 | 0.41 | opened | 5 | SS 35/10 kv Devyztino | 1.6 | 0.012 | 0.312 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.398 | 0.398 | opened
6 | SS 35/10 kv Kamenka | 2.5 | 0.61 | 0.63 | 30 | 0.63 | 0 | 0.63 | 0.02 | 0.02 | opened | 6 | SS 35/10 kv Kamenka | 2.5 | 0.015 | 0.625 | 0.63 | 30 | 0.63 | 0 | 0.63 | 0.005 | 0.005 | opened
7 | SS 35/10 kv Kozminskaya | 2.5 | 0.33 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.96 | 0.96 | opened | 7 | SS 35/10 kv Kozminskaya | 2.5 | 0.027 | 0.357 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.933 | 0.933 | opened
8 | SS 110/35/10 kv Malorkhangelskaya | 10 | 4.26 | 6.14 | 60 | 1.88 | 0 | 6.14 | 1.88 | 1.88 | opened | 8 | SS 110/35/10 kv Malorkhangelskaya | 10 | 3.048 | 7.308 | 6.14 | 60 | 6.14 | 0 | 6.14 | -1.168 | -1.168 | closed
| Nom. capacity MV, MVA | 10 | 1.94 | 1.94 | 60 | [6 empty] | 2: Nom. capacity MV, MVA; 3: 10; 4: 0; 5: 1.94; MVA 6: 1.94; Min. 7: 60
| Nom. capacity LV, MVA | 10 | 2.32 | 4.2 | 60 | 1.88 | 0 | 4.2 | 1.88 |  |  |  | Nom. capacity LV, MVA | 10 | 3.048 | 5.368 | 4.2 | 60 | 4.2 | 0 | 4.2 | -1.168
9 | SS 110/35/10 kv Novopolevo | 16 | 3.87 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.16 | -0.16 | closed | 9 | SS 110/35/10 kv Novopolevo | 16 | 0.114 | 3.984 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.274 | -0.274 | closed
| Nom. capacity MV, MVA | 16 | 2.6 | 2.6 | 30 | [7 empty] | Nom. capacity MV, MVA | 16 | 0 | 2.6 | 2.6 | 30 | 2.6 | 0 | 2.6 | 0
| Nom. capacity LV, MVA | 16 | 1.27 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.16 |  |  |  | Nom. capacity LV, MVA | 16 | 0.114 | 1.384 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.274
10 | SS 35/10 kv Nikolskaya | 2.5 | 0.52 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.81 | 0.81 | opened | 10 | SS 35/10 kv Nikolskaya | 2.5 | 0.005 | 0.525 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.805 | 0.805 | opened
11 | SS 35/10 kv Paramonovo | 1.8 | 0.28 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.2 | 0.2 | opened | 11 | SS 35/10 kv Paramonovo | 1.8 | 0.027 | 0.307 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.173 | 0.173 | opened
12 | SS 35/10 kv Senkovo | 1.6 | 0.29 | 1.29 | 30 | 1.29 | 0 | 1.29 | 1 | 1 | opened | 12 | SS 35/10 kv Senkovo | 1.6 | 0.026 | 0.316 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.974 | 0.974 | opened
13 | SS 35/10 kv Somovo | 2.5 | 0.27 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.69 | 0.69 | opened | 13 | SS 35/10 kv Somovo | 2.5 | 0.004 | 0.274 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.686 | 0.686 | opened
14 | SS 110/35/10 kv Trosna | 16 | 3.61 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.55 | 0.55 | opened | 14 | SS 110/35/10 kv Trosna | 16 | 0.048 | 3.658 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.502 | 0.502 | opened
| Nom. capacity MV, MVA | 16 | 2.36 | 2.36 | 45 | [7 empty] | Nom. capacity MV, MVA | 16 | 0 | 2.36 | 2.36 | 45 | 2.36 | 0 | 2.36 | 0
| Nom. capacity LV, MVA | 16 | 1.25 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.55 |  |  |  | Nom. capacity LV, MVA | 16 | 0.048 | 1.298 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.502
15 | SS 35/10 kv Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | opened | 15 | SS 35/10 kv Shablykino | 5.6 | 0.004 | 0.104 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.696 | 0.696 | opened
16 | SS 35/10 kv Yuryevo | 2.5 | 0.12 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.95 | 0.95 | opened | 16 | SS 35/10 kv Yuryevo | 2.5 | 0 | 0.12 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.95 | 0.95 | opened
17 | SS 110/35/10 kv Region V | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 | 1.36 | opened | 17 | SS 110/35/10 kv Region V | 10 | 0.2 | 4.24 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.16 | 1.16 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | [8 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 |  |  |  | Nom. capacity LV, MVA | 10 | 0.2 | 4.24 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.16
18 | SS 110/10 kv Pishchevaya | 6.3 | 2.45 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.575 | -0.575 | closed | 18 | SS 110/10 kv Pishchevaya | 6.3 | 2.353 | 4.803 | 1.875 | 60 | 1.875 | 0 | 1.875 | -2.928 | -2.928 | closed
19 | SS 110/10 kv Telchye | 3.2 | 2.08 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.62 | -0.62 | closed | 19 | SS 110/10 kv Telchye | 3.2 | 0.209 | 2.289 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.829 | -0.829 | closed
20 | SS 110/10 kv B.Chern | 2.5 | 0.22 | 1 | 120 | 1 | 0 | 1 | 0.78 | 0.78 | opened | 20 | SS 110/10 kv B.Chern | 2.5 | 0 | 0.22 | 1 | 120 | 1 | 0 | 1 | 0.78 | 0.78 | opened
21 | SS 35/10 kv Bashkatovo | 1.6 | 0.31 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.49 | 0.49 | opened | 21 | SS 35/10 kv Bashkatovo | 1.6 | 0.018 | 0.328 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.472 | 0.472 | opened
22 | SS 35/10 kv Vysokoe | 1.6 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | opened | 22 | SS 35/10 kv Vysokoe | 1.6 | 0 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | opened
23 | SS 35/10 kv Gladkoe | 2.5 | 0.27 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.19 | 1.19 | opened | 23 | SS 35/10 kv Gladkoe | 2.5 | 0 | 0.27 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.19 | 1.19 | opened
24 | SS 35/10 kv Lykovo | 2.5 | 0.7 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.54 | 0.54 | opened | 24 | SS 35/10 kv Lykovo | 2.5 | 0.031 | 0.731 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.509 | 0.509 | opened
25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened | 25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.27 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.41 | 0.41 | opened | 26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.014 | 0.284 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.396 | 0.396 | opened
27 | SS 35/10 kv Koptevo | 2.5 | 0.22 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.22 | 0.22 | opened | 27 | SS 35/10 kv Koptevo | 2.5 | 0 | 0.22 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.22 | 0.22 | opened
28 | SS 110/35/10/6 kv Meat processing factory | 10 | 2.11 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.02 | 0.02 | opened | 28 | SS 110/35/10/6 kv Meat processing factory | 10 | 0.012 | 2.122 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.008 | 0.008 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | [7 empty] | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 2.11 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.02 |  |  |  | Nom. capacity LV, MVA | 10 | 0.012 | 2.122 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.008
29 | SS 110/35/10 kv Shatilovo | 10 | 1.11 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.42 | -0.42 | closed | 29 | SS 110/35/10 kv Shatilovo | 10 | 0.007 | 1.117 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.427 | -0.427 | closed
| Nom. capacity MV, MVA | 10 | 0.48 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.32 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.48 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.32
| Nom. capacity LV, MVA | 10 | 0.63 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.1 |  |  |  | Nom. capacity LV, MVA | 10 | 0.007 | 0.637 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.107
30 | SS 110/35/10 kv Sovkhoznaya | 10 | 5.23 | 6.66 | 120 | 6.66 | 0 | 6.66 | 1.43 | 1.43 | opened | 30 | SS 110/35/10 kv Sovkhoznaya | 10 | 0.07 | 5.3 | 6.66 | 120 | 6.66 | 0 | 6.66 | 1.36 | 1.36 | opened
| Nom. capacity MV, MVA | 10 | 4.32 | 4.32 | 120 | 4.32 | [6 empty] | Nom. capacity MV, MVA | 10 | 0 | 4.32 | 4.32 | 120 | 4.32 | 0 | 4.32 | 0
| Nom. capacity LV, MVA | 10 | 0.91 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.43 |  |  |  | Nom. capacity LV, MVA | 10 | 0.07 | 0.98 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.36
31 | SS 35/10 kv Danilovskaya | 1.6 | 0.11 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.43 | 0.43 | opened | 31 | SS 35/10 kv Danilovskaya | 1.6 | 0 | 0.11 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.43 | 0.43 | opened
32 | SS 35/10 kv Korseevo | 1.8 | 0.07 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.81 | 0.81 | opened | 32 | SS 35/10 kv Korseevo | 1.8 | 0 | 0.07 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.81 | 0.81 | opened
33 | SS 35/10 kv Lipovets | 2.5 | 0.66 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.73 | 0.73 | opened | 33 | SS 35/10 kv Lipovets | 2.5 | 0.007 | 0.667 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.723 | 0.723 | opened
34 | SS 35/10 kv Misaylovo | 1.6 | 0.32 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.28 | 1.28 | opened | 34 | SS 35/10 kv Misaylovo | 1.6 | 0.004 | 0.324 | 1.6 |  | 1.6 | 0 | 1.6 | 1.276 | 1.276 | opened
35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.25 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.06 | 0.06 | opened | 35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.009 | 0.259 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.051 | 0.051 | opened
36 | SS 35/10 kv Pankovo | 1.8 | 0.48 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.32 | 1.32 | opened | 36 | SS 35/10 kv Pankovo | 1.8 | 0.011 | 0.491 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.309 | 1.309 | opened
37 | SS 35/10 kv SSK | 1.6 | 0.1 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.5 | 1.5 | opened | 37 | SS 35/10 kv SSK | 1.6 | 0 | 0.1 | 1.6 |  | 1.6 | 0 | 1.6 | 1.5 | 1.5 | opened
38 | SS 35/10 kv Sudbishchi | 2.5 | 0.54 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.96 | 1.96 | opened | 38 | SS 35/10 kv Sudbishchi | 2.5 | 0.012 | 0.552 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.948 | 1.948 | opened
39 | SS 35/10 kv Tim | 1.6 | 0.6 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1 | 1 | opened | 39 | SS 35/10 kv Tim | 1.6 | 0.013 | 0.613 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.987 | 0.987 | opened
40 | SS 35/10 kv Topki | 1 | 0.3 | 1 | 24 hours | 1 | 0 | 1 | 0.7 | 0.7 | opened | 40 | SS 35/10 kv Topki | 1 | 0.006 | 0.306 | 1 | 24 hours | 1 | 0 | 1 | 0.694 | 0.694 | opened
41 | SS 35/10 kv Yarishche | 2.5 | 0.37 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.13 | 2.13 | opened | 41 | SS 35/10 kv Yarishche | 2.5 | 0.021 | 0.391 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.109 | 2.109 | opened
42 | SS 110/10 kv Alshanskaya | 10+10 | 4.45 | 3.88 | 30 | 0.57 | 0 | 10.5 | 9.93 | 9.93 | opened | 42 | SS 110/10 kv Alshanskaya | 10+10 | 0.175 | 4.625 | 3.88 | 30 | 0.745 | 0 | 10.5 | 9.755 | 9.755 | opened
43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.52 | 0.93 | 90 | -0.41 | 0 | 2.625 | 3.035 | 3.035 | opened | 43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.022 | 0.542 | 0.93 | 90 | -0.388 | 0 | 2.625 | 3.013 | 3.013 | opened
44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.73 | 0 | - | 0.73 | 0 | 1.68 | 0.95 | 0.95 | opened | 44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0 | 0.73 | 0 |  | 0.73 | 0 | 1.68 | 0.95 | 0.95 | opened
45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.61 | 3.06 | 90 | -0.45 | 0 | 10.5 | 10.95 | 10.5 | opened | 45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 1.482 | 4.092 | 3.06 | 90 | 1.032 | 0 | 10.5 | 9.468 | 9.468 | opened
| Nom. capacity MV, MVA | 10+10 | 2.43 | 2.43 | 90 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.43 | 2.43 | 90 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 0.18 | 0.63 | 90 | -0.45 | 0 | 10.5 | 10.95 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.482 | 1.662 | 0.63 | 90 | 1.032 | 0 | 10.5 | 9.468
46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.86 | 0.64 | 60 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.012 | 0.872 | 0.64 | 60 | 0.232 | 0 | 1.68 | 1.448 | 1.448 | opened
47 | SS 35/10 kv Biofactory | 6,3+6,3 | 2.22 | 2.05 | 90 | 0.17 | 0 | 6.615 | 6.445 | 6.445 | opened | 47 | SS 35/10 kv Biofactory | 6,3+6,3 | 0.328 | 2.548 | 2.05 | 90 | 0.498 | 0 | 6.615 | 6.117 | 6.117 | opened
48 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.89 | 1.46 | 30 | 2.43 | 0 | 2.625 | 0.195 | 0.195 | opened | 48 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 1.762 | 5.652 | 1.46 | 30 | 4.192 | 0 | 2.625 | -1.567 | -1.567 | closed
49 | SS 110/10 kv Vostochnaya | 15+15 | 14.1 | 5.87 | 120 | 8.23 |  | 15.75 | 7.52 | 7.52 | opened | 49 | SS 110/10 kv Vostochnaya | 15+15 | 0.294 | 14.394 | 5.87 | 120 | 8.524 |  | 15.75 | 7.226 | 7.226 | opened
50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 3.49 | 0.45 | 60 | 3.04 | 0 | 10.5 | 7.46 | 7.46 | opened | 50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 0.013 | 3.503 | 0.45 | 60 | 3.053 | 0 | 10.5 | 7.447 | 7.447 | opened
| Nom. capacity MV, MVA | 10+10 | 0.3 | 0 | 0 | 0.3 | 0 | 10.5 | 10.2 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.3 | 0 |  | 0.3 | 0 | 10.5 | 10.2
| Nom. capacity LV, MVA | 10+10 | 3.19 | 0.45 | 60 | 2.74 | 0 | 10.5 | 7.76 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.013 | 3.203 | 0.45 | 60 | 2.753 | 0 | 10.5 | 7.747
51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 11.89 | 3.98 | 180 | 7.91 | 0 | 16.8 | 8.89 | 8.89 | opened | 51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 0.466 | 12.356 | 3.98 | 180 | 8.376 | 0 | 16.8 | 8.424 | 8.424 | opened
52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 1.08 | 0.64 | 60 | 0.44 | 0 | 1.89 | 1.45 | 1.45 | opened | 52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 0.018 | 1.098 | 0.64 | 60 | 0.458 | 0 | 1.89 | 1.432 | 1.432 | opened
53 | SS 110/6 kv Zavodskaya | 40+25 | 11.48 | 4.39 | 150 | 7.09 | 0 | 26.25 | 19.16 | 19.16 | opened | 53 | SS 110/6 kv Zavodskaya | 40+25 | 0 | 11.48 | 4.39 | 150 | 7.09 | 0 | 26.25 | 19.16 | 19.16 | opened
54 | SS 110/6 kv Zapadnaya | 25+25 | 26.59 | 0 | 120 | 26.59 | 0 | 26.25 | -0.34 | -0.34 | closed | 54 | SS 110/6 kv Zapadnaya | 25+25 | 19.118 | 45.708 | 5.37 | 120 | 40.338 | 0 | 26.25 | -14.088 | -14.088 | closed
55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 1.81 | 1.48 | 60 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 0.231 | 2.041 | 1.48 | 60 | 0.561 | 0 | 2.625 | 2.064 | 2.064 | opened
56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 1.06 | 1.18 | 30 | -0.12 | 0 | 1.68 | 1.8 | 1.8 | opened | 56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 0.035 | 1.095 | 1.18 | 30 | -0.085 | 0 | 1.68 | 1.765 | 1.765 | opened
57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 6.85 | 1.44 | 90 | 5.41 | 0 | 10.5 | 5.09 | 5.09 | opened | 57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.346 | 12.196 | 1.44 | 90 | 10.756 | 0 | 10.5 | -0.256 | -0.256 | closed
| Nom. capacity MV, MVA | 10+10 | 3.58 | 1 | 90 | 2.58 | 0 | 10.5 | 7.92 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 3.58 | 1 | 90 | 2.58 | 0 | 10.5 | 7.92
| Nom. capacity LV, MVA | 10+10 | 3.27 | 0.44 | 90 | 2.83 | 0 | 10.5 | 7.67 |  |  |  | Nom. capacity LV, MVA | 10+10 | 5.346 | 8.616 | 0.44 | 90 | 8.176 | 0 | 10.5 | 2.324
58 | SS 110/35/10 kv Kromskaya | 16+16 | 8.4 | 6.83 | 45 | 1.57 | 0 | 16.8 | 15.23 | 15.23 | opened | 58 | SS 110/35/10 kv Kromskaya | 16+16 | 0.077 | 8.477 | 6.83 | 45 | 1.647 | 0 | 16.8 | 15.153 | 15.153 | opened
| Nom. capacity MV, MVA | 16+16 | 5 | 5 | 45 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0 | 5 | 5 | 45 | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16+16 | 3.4 | 1.83 | 45 | 1.57 | 0 | 16.8 | 15.23 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.077 | 3.477 | 1.83 | 45 | 1.647 | 0 | 16.8 | 15.153
59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 1.15 | 0.95 | 30 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 0.014 | 1.164 | 0.95 | 30 | 0.214 | 0 | 2.625 | 2.411 | 2.411 | opened
60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | opened | 60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.005 | 0.705 | 0 |  | 0.705 | 0 | 1.68 | 0.975 | 0.975 | opened
61 | SS 35/10 kv Kutafino | 1,6+1,6 | 0.57 | 0.83 | 30 | -0.26 | 0 | 1.68 | 1.94 | 1.94 | opened | 61 | SS 35/10 kv Kutafino | 1,6+1,6 | 6.069 | 6.639 | 0.83 | 30 | 5.809 | 0 | 1.68 | -4.129 | -4.129 | closed
62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.69 | 1.59 | 30 | -0.9 | 0 | 2.625 | 3.525 | 3.525 | opened | 62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.042 | 0.732 | 1.59 | 30 | -0.858 | 0 | 2.625 | 3.483 | 3.483 | opened
63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.44 | 0.47 | 60 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened | 63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0 | 0.44 | 0.47 | 60 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened
64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.41 | 0.99 | 90 | -0.58 | 0 | 1.89 | 2.47 | 2.47 | opened | 64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0 | 0.41 | 0.99 | 90 | -0.58 | 0 | 1.89 | 2.47 | 2.47 | opened
65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.41 | 1.7 | 30 | -1.29 | 0 | 5.88 | 7.17 | 7.17 | opened | 65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.353 | 0.763 | 1.7 | 30 | -0.937 | 0 | 5.88 | 6.817 | 6.817 | opened
66 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 6.89 | 1.41 | 90 | 5.48 | 0 | 10.5 | 5.02 | 5.02 | opened | 66 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 0.712 | 7.602 | 1.41 | 90 | 6.192 | 0 | 10.5 | 4.308 | 4.308 | opened
| Nom. capacity MV, MVA | 10+10 | 0.86 | 0.86 | 90 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.86 | 0.86 | 90 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 6.03 | 0.55 | 90 | 5.48 | 0 | 10.5 | 5.02 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.712 | 6.742 | 0.55 | 90 | 6.192 | 0 | 10.5 | 4.308
67 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.93 | 1.63 | 45 | -0.7 | 0 | 2.625 | 3.325 | 3.325 | opened | 67 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.014 | 0.944 | 1.63 | 45 | -0.686 | 0 | 2.625 | 3.311 | 3.311 | opened
68 | SS 35/10 kv N.Petrovka | 2,5+1,6 | 0.57 | 0.73 | 60 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | opened | 68 | SS 35/10 kv N.Petrovka | 2,5+1,6 | 0 | 0.57 | 0.73 | 60 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | opened
69 | SS 35/10 kv Putimets | 2,5+2,5 | 0.39 | 1.53 | 90 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened | 69 | SS 35/10 kv Putimets | 2,5+2,5 | 0.146 | 0.536 | 1.53 | 90 | -0.994 | 0 | 2.625 | 3.619 | 3.619 | opened
70 | SS 110/10 kv Pishchevaya | 40+25 | 6.42 | 2.22 | 60 | 4.2 | 0 | 26.25 | 22.05 | 22.05 | opened | 70 | SS 110/10 kv Pishchevaya | 40+25 | 0.155 | 6.575 | 2.22 | 60 | 4.355 | 0 | 26.25 | 21.895 | 21.895 | opened
71 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.44 | 0.65 | 90 | -0.21 | 0 | 2.625 | 2.835 | 2.835 | opened | 71 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0 | 0.44 | 0.65 | 90 | -0.21 | 0 | 2.625 | 2.835 | 2.835 | opened
72 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 3.94 | 1.98 | 45 | 1.96 | 0 | 10.5 | 8.54 | 8.54 | opened | 72 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 0.351 | 4.291 | 1.98 | 45 | 2.311 | 0 | 10.5 | 8.189 | 8.189 | opened
| Nom. capacity MV, MVA | 10+10 | 1.41 | 1.41 | 45 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.41 | 1.41 | 45 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 2.53 | 0.57 | 45 | 1.96 | 0 | 10.5 | 8.54 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.351 | 2.881 | 0.57 | 45 | 2.311 | 0 | 10.5 | 8.189
73 | SS 35/10 kv Streletskaya | 4+4 | 2.33 | 0.91 | 90 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened | 73 | SS 35/10 kv Streletskaya | 4+4 | 0.051 | 2.381 | 0.91 | 90 | 1.471 | 0 | 4.2 | 2.729 | 2.729 | opened
74 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 28.03 | 3.86 | 180 | 24.17 | 0 | 68.25 | 44.08 | 18.92 | opened | 74 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 1 | 36.21 | 3.86 | 180 | 32.35 | 0 | 68.25 | 35.9 | 35.9 | opened
| Nom. Capacity MV; МVА | 20+20 | 7.18 | 5.1 | 90 | 2.08 | 0 | 21 | 18.92 |  |  |  | Nom. Capacity MV; МVА | 20+20 |  | 7.18 | 5.1 | 90 | 2.08 | 0 | 21 | 18.92
| Nom. capcity LV; МVА | 20+20+25+40 | 28.03 | 3.86 | 180 | 24.17 | 0 | 68.25 | 44.08 |  |  |  | Nom. capcity LV; МVА | 20+20+25+40 | 1 | 29.03 | 3.86 | 180 | 25.17 | 0 | 68.25 | 43.08
75 | SS 35/10 kv Soskovskaya | 4+3,2 | 1.25 | 0.64 | 90 | 0.61 | 0 | 3.36 | 2.75 | 2.75 | opened | 75 | SS 35/10 kv Soskovskaya | 4+3,2 | 0.042 | 1.292 | 0.64 | 90 | 0.652 | 0 | 3.36 | 2.708 | 2.708 | opened
76 | SS 35/10 kv Trosna | 5,6+3,2 | 0.98 | 1.76 | 30 | -0.78 | 0 | 3.36 | 4.14 | 4.14 | opened | 76 | SS 35/10 kv Trosna | 5,6+3,2 | 0.048 | 1.028 | 1.76 | 30 | -0.732 | 0 | 3.36 | 4.092 | 4.092 | opened
77 | SS 110/10 kv Khimmash | 25+25 | 5.6 | 1.51 | 120 | 4.09 | 0 | 26.25 | 22.16 | 22.16 | opened | 77 | SS 110/10 kv Khimmash | 25+25 | 5.947 | 11.547 | 1.51 | 120 | 10.037 | 0 | 26.25 | 16.213 | 16.213 | opened
78 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0.93 | 0 | - | 0.93 | 0 | 5.88 | 4.95 | 4.95 | opened | 78 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0 | 0.93 | 0 |  | 0.93 | 0 | 5.88 | 4.95 | 4.95 | opened
79 | SS 35/10 kv Khotynetskaya | 4+2,5 | 2.31 | 1.49 | 80 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | opened | 79 | SS 35/10 kv Khotynetskaya | 4+2,5 | 0.236 | 2.546 | 1.49 | 80 | 1.056 | 0 | 2.625 | 1.569 | 1.569 | opened
80 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.55 | 1.03 | 80 | -0.48 | 0 | 1.68 | 2.16 | 2.16 | opened | 80 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.164 | 0.714 | 1.03 | 80 | -0.316 | 0 | 1.68 | 1.996 | 1.996 | opened
81 | SS 110/10/6 kv Tsentralnaya | 25+25 | 14.12 | 3.46 | 135 | 10.66 | 0 | 26.25 | 15.59 | 15.59 | opened | 81 | SS 110/10/6 kv Tsentralnaya | 25+25 | 0 | 14.12 | 3.46 | 135 | 10.66 | 0 | 26.25 | 15.59 | 15.59 | opened
82 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 2.5 | 1.36 | 30 | 1.14 | 0 | 6.615 | 5.475 | 5.475 | opened | 82 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 0.005 | 2.505 | 1.36 | 30 | 1.145 | 0 | 6.615 | 5.47 | 5.47 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 0.81 | 0.54 | 30 | 0.27 | 0 | 6.615 | 6.345 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0.81 | 0.54 | 30 | 0.27 | 0 | 6.615 | 6.345
| Nom. capacity LV, MVA | 6,3+6,3 | 1.69 | 0.82 | 30 | 0.87 | 0 | 6.615 | 5.745 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.005 | 1.695 | 0.82 | 30 | 0.875 | 0 | 6.615 | 5.74
83 | SS 110/35/10 kv Shakhovo | 10+10 | 2.12 | 2.55 | 120 | -0.43 | 0 | 10.5 | 10.93 | 10.5 | opened | 83 | SS 110/35/10 kv Shakhovo | 10+10 | 0.329 | 2.449 | 2.55 | 120 | -0.101 | 0 | 10.5 | 10.601 | 10.601 | opened
| Nom. capacity MV, MVA | 10+10 | 0.39 | 0.39 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.39 | 0.39 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 1.73 | 2.16 | 120 | -0.43 | 0 | 10.5 | 10.93 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.329 | 2.059 | 2.16 | 120 | -0.101 | 0 | 10.5 | 10.601
84 | SS 35/10 kv Shepino | 2,5+1,6 | 1.57 | 1.1 | 120 | 0.47 | 0 | 1.68 | 1.21 | 1.21 | opened | 84 | SS 35/10 kv Shepino | 2,5+1,6 | 0.064 | 1.634 | 1.1 | 120 | 0.534 | 0 | 1.68 | 1.146 | 1.146 | opened
85 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 8.59 | 0.74 | 60 | 7.85 | 0 | 26.25 | 18.4 | 18.4 | opened | 85 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 0 | 8.59 | 0.74 | 60 | 7.85 | 0 | 26.25 | 18.4 | 18.4 | opened
86 | SS 110/10 kv Yuzhnaya | 10+10 | 5.86 | 1.05 | 90 | 4.81 | 0 | 10.5 | 5.69 | 5.69 | opened | 86 | SS 110/10 kv Yuzhnaya | 10+10 | 1.215 | 7.075 | 1.05 | 90 | 6.025 | 0 | 10.5 | 4.475 | 4.475 | opened
87 | SS 220/110/10 kv Mtsensk | 40+40 | 9.73 | 0 | - | 9.73 | 0 | 42 | 32.27 | 32.27 | opened | 87 | SS 220/110/10 kv Mtsensk | 40+40 | 0.394 | 10.124 | 0 |  | 10.124 | 0 | 42 | 31.876 | 31.876 | opened
88 | SS 110/35/10 kv Kommash | 10+16 | 9.42 | 4.65 | 90 | 4.77 | 0 | 10.5 | 5.73 | 5.73 | opened | 88 | SS 110/35/10 kv Kommash | 10+16 | 0.047 | 9.467 | 4.65 | 90 | 4.817 | 0 | 10.5 | 5.683 | 5.683 | opened
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 9.42 | 4.65 | 90 | 4.77 | 0 | 10.5 | 5.73 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.047 | 9.467 | 4.65 | 90 | 4.817 | 0 | 10.5 | 5.683
89 | SS 110/35/10 kv Novosergievka | 6,3+10 | 2.57 | 4.13 | 120 | -1.56 | 0 | 6.615 | 8.175 | 6.615 | opened | 89 | SS 110/35/10 kv Novosergievka | 6,3+10 | 0 | 2.57 | 4.13 | 120 | -1.56 | 0 | 6.615 | 8.175 | 8.175 | opened
| Nom. capacity MV, MVA | 6,3+10 | 2.4 | 2.4 | 120 | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0 | 2.4 | 2.4 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3+10 | 0.17 | 1.73 | 120 | -1.56 | 0 | 6.615 | 8.175 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.17 | 1.73 | 120 | -1.56 | 0 | 6.615 | 8.175
90 | SS 110/10 kv 1 Voin | 6,3+6,3 | 0.98 | 1.83 | 120 | -0.85 | 0 | 6.615 | 7.465 | 7.465 | opened | 90 | SS 110/10 kv 1 Voin | 6,3+6,3 | 1.09 | 2.07 | 1.83 | 120 | 0.24 | 0 | 6.615 | 6.375 | 6.375 | opened
91 | SS 110/35/10 kv Zalegoshch | 10+16 | 5.31 | 3.95 | 120 | 1.36 | 0 | 10.5 | 9.14 | 9.14 | opened | 91 | SS 110/35/10 kv Zalegoshch | 10+16 | 0.66 | 5.97 | 3.95 | 120 | 2.02 | 0 | 10.5 | 8.48 | 8.48 | opened
| Nom. capacity MV, MVA | 10+16 | 2.39 | 2.39 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 2.39 | 2.39 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 2.92 | 1.56 | 120 | 1.36 | 0 | 10.5 | 9.14 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.66 | 3.58 | 1.56 | 120 | 2.02 | 0 | 10.5 | 8.48
92 | SS 110/10 kv Kochety | 2,5+2,5 | 0.46 | 0.66 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | opened | 92 | SS 110/10 kv Kochety | 2,5+2,5 | 0 | 0.46 | 0.66 | 120 | -0.2 | 0 | 2.625 | 2.825 | 2.825 | opened
93 | SS 110/35/10 kv Bolkhov | 10+10 | 7.33 | 4.1 | 120 | 3.23 | 0 | 10.5 | 7.27 | 7.27 | opened | 93 | SS 110/35/10 kv Bolkhov | 10+10 | 0.022 | 7.352 | 4.1 | 120 | 3.252 | 0 | 10.5 | 7.248 | 7.248 | opened
| Nom. capacity MV, MVA | 10+10 | 2.45 | 2.45 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.45 | 2.45 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 4.88 | 1.65 | 120 | 3.23 | 0 | 10.5 | 7.27 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.022 | 4.902 | 1.65 | 120 | 3.252 | 0 | 10.5 | 7.248
94 | SS 110/35/10 kv Novosil | 10+10 | 3.45 | 2.98 | 120 | 0.47 | 0 | 10.5 | 10.03 | 10.03 | opened | 94 | SS 110/35/10 kv Novosil | 10+10 | 0.008 | 3.458 | 2.98 | 120 | 0.478 | 0 | 10.5 | 10.022 | 10.022 | opened
| Nom. capacity MV, MVA | 10+10 | 1.46 | 1.46 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.46 | 1.46 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 1.99 | 1.52 | 120 | 0.47 | 0 | 10.5 | 10.03 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.008 | 1.998 | 1.52 | 120 | 0.478 | 0 | 10.5 | 10.022
95 | SS 110/35/10 kv Znamenskaya | 10+10 | 1.56 | 1.78 | 120 | -0.22 | 0 | 10.5 | 10.72 | 10.5 | opened | 95 | SS 110/35/10 kv Znamenskaya | 10+10 | 0.021 | 1.581 | 1.78 | 120 | -0.199 | 0 | 10.5 | 10.699 | 10.699 | opened
| Nom. capacity MV, MVA | 10+10 | 0.34 | 0.34 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.34 | 0.34 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 1.22 | 1.44 | 120 | -0.22 | 0 | 10.5 | 10.72 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.021 | 1.241 | 1.44 | 120 | -0.199 | 0 | 10.5 | 10.699
96 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0.48 | 0.48 | 120 | 0 | 0 | 1.89 | 1.89 | 1.89 | opened | 96 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0.004 | 0.484 | 0.48 | 120 | 0.004 | 0 | 1.89 | 1.886 | 1.886 | opened
97 | SS 35/10 kv Podberyozovo | 4+1 | 0.23 | 0.59 | 120 | -0.36 | 0 | 1.05 | 1.41 | 1.41 | opened | 97 | SS 35/10 kv Podberyozovo | 4+1 | 0 | 0.23 | 0.59 | 120 | -0.36 | 0 | 1.05 | 1.41 | 1.41 | opened
98 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.5 | 0 |  | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 98 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.006 | 0.506 | 0 |  | 0.506 | 0 | 1.68 | 1.174 | 1.174 | opened
99 | SS 35/10 kv Alyoshnya | 1+1 | 0.44 | 0.24 | 120 | 0.2 | 0 | 1.05 | 0.85 | 0.85 | opened | 99 | SS 35/10 kv Alyoshnya | 1+1 | 0.002 | 0.442 | 0.24 | 120 | 0.202 | 0 | 1.05 | 0.848 | 0.848 | opened
100 | SS 35/10 kv Lomovoe | 2,5+2,5 | 1.03 | 0 | - | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 100 | SS 35/10 kv Lomovoe | 2,5+2,5 | 0 | 1.03 | 0 |  | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened
101 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.72 | 0.63 | 120 | 0.09 |  | 2.625 | 2.535 | 2.535 | opened | 101 | SS 35/10 kv Mokhovoe | 2,5+4 | 0 | 0.72 | 0.63 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
102 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.22 | 0.47 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | opened | 102 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0 | 0.22 | 0.47 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | opened
103 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.17 | 0 | - | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 103 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.007 | 0.177 | 0 |  | 0.177 | 0 | 2.625 | 2.448 | 2.448 | opened
104 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.69 | 0.67 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 104 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.04 | 0.73 | 0.67 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
105 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.43 | 0.37 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened | 105 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.001 | 0.431 | 0.37 | 120 | 0.061 | 0 | 1.68 | 1.619 | 1.619 | opened
106 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.32 | 0.69 | 120 | -0.37 | 0 | 2.625 | 2.995 | 2.995 | opened | 106 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.021 | 0.341 | 0.69 | 120 | -0.349 | 0 | 2.625 | 2.974 | 2.974 | opened
107 | SS 35/10 kv Odinok | 1,6+1,6 | 0.44 | 0 | - | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened | 107 | SS 35/10 kv Odinok | 1,6+1,6 | 0.004 | 0.444 | 0 |  | 0.444 | 0 | 1.68 | 1.236 | 1.236 | opened
108 | SS 35/10 kv Uzkoe | 1,6+1 | 0.15 | 0.25 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened | 108 | SS 35/10 kv Uzkoe | 1,6+1 | 0 | 0.15 | 0.25 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened
109 | SS 35/10 kv Korsakovo | 2,5+4 | 0.83 | 0.69 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 109 | SS 35/10 kv Korsakovo | 2,5+4 | 0.009 | 0.839 | 0.69 | 120 | 0.149 | 0 | 2.625 | 2.476 | 2.476 | opened
110 | SS 35/10 kv Paramonovo | 4+2,5 | 0.71 | 0.76 | 120 | -0.05 | 0 | 2.625 | 2.675 | 2.675 | opened | 110 | SS 35/10 kv Paramonovo | 4+2,5 | 0.006 | 0.716 | 0.76 | 120 | -0.044 | 0 | 2.625 | 2.669 | 2.669 | opened
111 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.21 | 0 | - | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 111 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.006 | 0.216 | 0 |  | 0.216 | 0 | 1.68 | 1.464 | 1.464 | opened
112 | SS 110/35/10 kv Verkhovye I | 16+10 | 6.25 | 3.65 | 120 | 2.6 | 0 | 10.5 | 7.9 | 7.9 | opened | 112 | SS 110/35/10 kv Verkhovye I | 16+10 | 1.214 | 7.464 | 3.65 | 120 | 3.814 | 0 | 10.5 | 6.686 | 6.686 | opened
| Nom. capacity MV, MVA | 16+10 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 16+10 | 4.2 | 1.6 | 120 | 2.6 | 0 | 10.5 | 7.9 |  |  |  | Nom. capacity LV, MVA | 16+10 | 1.214 | 5.414 | 1.6 | 120 | 3.814 | 0 | 10.5 | 6.686
113 | SS 110/35/10 kv Verkhovye II | 40+40 | 10.2 | 0.3 | - | 9.9 | 0 | 42 | 32.1 | 32.1 | opened | 113 | SS 110/35/10 kv Verkhovye II | 40+40 | 0 | 10.2 | 0.3 |  | 9.9 | 0 | 42 | 32.1 | 32.1 | opened
| Nom. capacity MV, MVA | 40+40 | 0.3 | 0.3 | - | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0 | 0.3 | 0.3 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, MVA | 40+40 | 9.9 | 0 | - | 9.9 | 0 | 42 | 32.1 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 9.9 | 0 |  | 9.9 | 0 | 42 | 32.1
114 | SS 110/35/10 kv Dolgoe | 16+10 | 5.84 | 3.38 | 120 | 2.46 | 0 | 10.5 | 8.04 | 8.04 | opened | 114 | SS 110/35/10 kv Dolgoe | 16+10 | 0.007 | 5.847 | 3.38 | 120 | 2.467 | 0 | 10.5 | 8.033 | 8.033 | opened
| Nom. capacity MV, MVA | 16+10 | 2.38 | 2.38 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0 | 2.38 | 2.38 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 16+10 | 3.46 | 1 | 120 | 2.46 | 0 | 10.5 | 8.04 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.007 | 3.467 | 1 | 120 | 2.467 | 0 | 10.5 | 8.033
115 | SS 110/35/10 kv Kolpny-110 | 10+16 | 4.03 | 2.79 | 120 | 1.24 | 0 | 10.5 | 9.26 | 9.26 | opened | 115 | SS 110/35/10 kv Kolpny-110 | 10+16 | 0.031 | 4.061 | 2.79 | 120 | 1.271 | 0 | 10.5 | 9.229 | 9.229 | opened
| Nom. capacity MV, MVA | 10+16 | 2.46 | 2.46 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 2.46 | 2.46 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 1.57 | 0.33 | 120 | 1.24 | 0 | 10.5 | 9.26 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.031 | 1.601 | 0.33 | 120 | 1.271 | 0 | 10.5 | 9.229
116 | SS 110/35/10 kv Kr. Zarya | 10+10 | 4.51 | 1.54 | 120 | 2.97 | 0 | 10.5 | 7.53 | 7.53 | opened | 116 | SS 110/35/10 kv Kr. Zarya | 10+10 | 0.013 | 4.523 | 1.54 | 120 | 2.983 | 0 | 10.5 | 7.517 | 7.517 | opened
| Nom. capacity MV, MVA | 10+10 | 1.29 | 1.29 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.29 | 1.29 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 3.22 | 0.25 | 120 | 2.97 | 0 | 10.5 | 7.53 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.013 | 3.233 | 0.25 | 120 | 2.983 | 0 | 10.5 | 7.517
117 | SS 110/35/10 kv Pokrovskaya | 10+10 | 5.3 | 2.84 | 120 | 2.46 | 0 | 10.5 | 8.04 | 8.04 | opened | 117 | SS 110/35/10 kv Pokrovskaya | 10+10 | 0.269 | 5.569 | 2.84 | 120 | 2.729 | 0 | 10.5 | 7.771 | 7.771 | opened
| Nom. capacity MV, MVA | 10+10 | 2.12 | 2.12 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.12 | 2.12 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 3.18 | 0.72 | 120 | 2.46 | 0 | 10.5 | 8.04 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.269 | 3.449 | 0.72 | 120 | 2.729 | 0 | 10.5 | 7.771
118 | SS 110/35/6 kv Cherkasskaya | 40+25 | 19.17 | 13.39 | 120 | 5.78 | 0 | 26.25 | 20.47 | 20.47 | opened | 118 | SS 110/35/6 kv Cherkasskaya | 40+25 | 0.006 | 19.176 | 13.39 | 120 | 5.786 | 0 | 26.25 | 20.464 | 20.464 | opened
| Nom. capacity MV, MVA | 40+25 | 10.84 | 10.84 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 40+25 | 0 | 10.84 | 10.84 | 120 | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 40+25 | 8.33 | 2.55 | 120 | 5.78 | 0 | 26.25 | 20.47 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0.006 | 8.336 | 2.55 | 120 | 5.786 | 0 | 26.25 | 20.464
119 | SS 110/6 kv Plastmass | 16+16 | 10.6 | 0 | - | 10.6 | 0 | 16.8 | 6.2 | 6.2 | opened | 119 | SS 110/6 kv Plastmass | 16+16 | 0 | 10.6 | 0 |  | 10.6 | 0 | 16.8 | 6.2 | 6.2 | opened
120 | SS 110/10 kv PM | 10+10 | 4.3 | 0 | - | 4.3 | 0 | 10.5 | 6.2 | 6.2 | opened | 120 | SS 110/10 kv PM | 10+10 | 0 | 4.3 | 0 |  | 4.3 | 0 | 10.5 | 6.2 | 6.2 | opened
121 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.92 | 1.85 | 120 | -0.93 | 0 | 6.615 | 7.545 | 7.545 | opened | 121 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.015 | 0.935 | 1.85 | 120 | -0.915 | 0 | 6.615 | 7.53 | 7.53 | opened
122 | SS 110/10 kv R.Brod | 5,6+10 | 1.89 | 0.29 | 120 | 1.6 | 0 | 5.88 | 4.28 | 4.28 | opened | 122 | SS 110/10 kv R.Brod | 5,6+10 | 0.559 | 2.449 | 0.29 | 120 | 2.159 | 0 | 5.88 | 3.721 | 3.721 | opened
123 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.4 | 0.13 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened | 123 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.035 | 0.435 | 0.13 | 120 | 0.305 | 0 | 1.68 | 1.375 | 1.375 | opened
124 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 1.04 | 0.65 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened | 124 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 0.024 | 1.064 | 0.65 | 120 | 0.414 | 0 | 2.625 | 2.211 | 2.211 | opened
125 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0.78 | 0.43 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened | 125 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0 | 0.78 | 0.43 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened
126 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.85 | 0.56 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 126 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.027 | 0.877 | 0.56 | 120 | 0.317 | 0 | 1.68 | 1.363 | 1.363 | opened
127 | SS 35/10 kv Droskovo | 4+2,5 | 1.53 | 0 | - | 1.53 | 0 | 2.625 | 1.095 | 1.095 | opened | 127 | SS 35/10 kv Droskovo | 4+2,5 | 0.047 | 1.577 | 0 |  | 1.577 | 0 | 2.625 | 1.048 | 1.048 | opened
128 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 1.26 | 0.39 | 120 | 0.87 | 0 | 6.615 | 5.745 | 5.745 | opened | 128 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 0 | 1.26 | 0.39 | 120 | 0.87 | 0 | 6.615 | 5.745 | 5.745 | opened
129 | SS 35/10 kv Krutoe | 2,5+1,6 | 1.33 | 0.87 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened | 129 | SS 35/10 kv Krutoe | 2,5+1,6 | 0.079 | 1.409 | 0.87 | 120 | 0.539 | 0 | 1.68 | 1.141 | 1.141 | opened
130 | SS 35/10 kv Mezentsevo | 4+6,3 | 2.1 | 1.11 | 80 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | opened | 130 | SS 35/10 kv Mezentsevo | 4+6,3 | 0.121 | 2.221 | 1.11 | 80 | 1.111 | 0 | 4.2 | 3.089 | 3.089 | opened
131 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.14 | 0 | - | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 131 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.008 | 0.148 | 0 |  | 0.148 | 0 | 1.68 | 1.532 | 1.532 | opened
132 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0.28 | 0.39 | - | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened | 132 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0 | 0.28 | 0.39 |  | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened
133 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 1.14 | 0.54 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 133 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 0.046 | 1.186 | 0.54 | 80 | 0.646 | 0 | 2.625 | 1.979 | 1.979 | opened
134 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.3 | 1.67 | 120 | -1.37 | 0 | 3.36 | 4.73 | 4.73 | opened | 134 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.009 | 0.309 | 1.67 | 120 | -1.361 | 0 | 3.36 | 4.721 | 4.721 | opened
135 | SS 35/6 kv Pushkarskaya | 4+4 | 5.16 | 0 |  | 5.16 | 0 | 4.2 | -0.96 | -0.96 | closed | 135 | SS 35/6 kv Pushkarskaya | 4+4 | 0 | 5.16 | 0 |  | 5.16 | 0 | 4.2 | -0.96 | -0.96 | closed
136 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0.44 | 0.25 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 136 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0 | 0.44 | 0.25 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
137 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.94 | 0.7 | 80 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | opened | 137 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.059 | 0.999 | 0.7 | 80 | 0.299 | 0 | 2.625 | 2.326 | 2.326 | opened
138 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.09 | 1.5 | 120 | -0.41 | 0 | 2.625 | 3.035 | 3.035 | opened | 138 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.044 | 2.134 | 1.5 | 120 | 0.634 | 0 | 2.625 | 1.991 | 1.991 | opened
139 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.39 | 0.33 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened | 139 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.004 | 0.394 | 0.33 | 120 | 0.064 | 0 | 1.68 | 1.616 | 1.616 | opened
140 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0.3 | 0 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 140 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0 | 0.3 | 0 |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
141 | SS 35/10 kv Urynok | 1,6+1,6 | 0.99 | 0.52 | 20 | 0.47 | 0 | 1.68 | 1.21 | 1.21 | opened | 141 | SS 35/10 kv Urynok | 1,6+1,6 | 0.006 | 0.996 | 0.52 | 20 | 0.476 | 0 | 1.68 | 1.204 | 1.204 | opened
142 | SS 35/10 kv Khomutovo | 4+4 | 1.66 | 0.31 | 80 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 142 | SS 35/10 kv Khomutovo | 4+4 | 0 | 1.66 | 0.31 | 80 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened
| Total: | [10 empty] | 2: Total:; 4: 73.842; 5: 647.692
| deficit | [8 empty] | -3.075 |  | 2: deficit; Min. 12: -26.626
| proficit | [8 empty] | 588.875 |  | 2: proficit; Min. 12: 574.421

## ярославль
[9 empty] | Table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 0.27 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.53 | 0.53 | opened | 1 | SS 35/10 Matveevo | 1.6 | 0.024 | 0.294 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.506 | 0.506 | opened
2 | SS 35/10 Mikhailovskoe | 6.3 | 1.43 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.19 | 5.19 | opened | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.433 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.187 | 5.187 | opened
3 | SS 35/10 Shirinye | 2.5 | 1.79 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.31 | 0.31 | opened | 3 | SS 35/10 Shirinye | 2.5 | 0.21 | 2 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.1 | 0.1 | opened
4 | SS 110/10 Pokrov | 2.5 | 0.3 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1 | 1 | opened | 4 | SS 110/10 Pokrov | 2.5 | 0 | 0.3 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1 | 1 | opened
5 | SS 35/10 Obnora | 1.6 | 0.18 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.92 | 0.92 | opened | 5 | SS 35/10 Obnora | 1.6 | 0.005 | 0.185 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.915 | 0.915 | opened
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 8.67 |  |  | 8.67 | 0 | 10.5 | 1.83 | 1.83 | opened | 6 | SS 110/35/10 Abbakumtsevo | 25+25 | 0.387 | 11.4665 |  |  | 11.4665 | 0 | 10.5 | -0.96645 | -0.96645 | closed
| Nom. capacity MV, МVА | 10+10 | 5.75 |  |  | 5.75 | 0 | 10.5 | 4.75 |  |  | 2: Nom. capacity MV, МVА; 3: 25+25; 5: 8.5465; Мin. 8: 8.5465; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 1.9535
| Nom. capacity LV, МVА | 10+10 | 2.92 |  |  | 2.92 | 0 | 10.5 | 7.58 |  |  | 2: Nom. capacity LV, МVА; 3: 25+25; 5: 2.92; Мin. 8: 2.92; Мin. 9: 0; Мin. 10: 10.5; Мin. 11: 7.58
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.15 |  |  | 1.15 | 0 | 1.68 | 0.53 | 0.53 | opened | 7 | SS 35/10 Ananyino | 1,6+1,6 | 0.3726 | 1.5226 |  |  | 1.5226 | 0 | 1.68 | 0.1574 | 0.1574 | opened
8 | SS 110/10/10 Bragino | 40+40 | 34.1 | 2.38 | 120 | 31.72 | 0 | 42 | 10.28 | 10.28 | opened | 8 | SS 110/10/10 Bragino | 40+40 | 11.6563 | 45.7563 | 2.38 | 120 | 43.3763 | 0 | 42 | -1.3763 | -1.3763 | closed
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.91 | 0.1 | 120 | 0.81 | 0 | 4.2 | 3.39 | 3.39 | opened | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.44 | 1.35 | 0.1 | 120 | 1.25 | 0 | 4.2 | 2.95 | 2.95 | opened
10 | SS 35/10 Vatolino | 2,5+4,0 | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -0.85 | закрыт | 10 | SS 35/10 Vatolino | 2,5+4,0 | 0.478 | 3.958 |  |  | 3.958 | 0 | 2.63 | -1.328 | -1.328 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 5.37 |  |  | 5.37 | 0 | 6.62 | 1.25 | 1.25 | opened | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.3957 | 5.7657 |  |  | 5.7657 | 0 | 6.62 | 0.8543 | 0.8543 | opened
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 2 |  |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.1684 | 2.1684 |  |  | 2.1684 | 0 | 4.2 | 2.0316 | 2.0316 | opened
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.78 |  |  | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.057 | 0.837 |  |  | 0.837 | 0 | 1.68 | 0.843 | 0.843 | opened
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.74 |  |  | 1.74 | 0 | 4.2 | 2.46 | 2.46 | opened | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 0.8934 | 2.6334 |  |  | 2.6334 | 0 | 4.2 | 1.5666 | 1.5666 | opened
15 | SS 35/10 Volna | 2,5+2,5 | 3.06 |  |  | 3.06 | 0 | 2.63 | -0.43 | -0.43 | закрыт | 15 | SS 35/10 Volna | 2,5+2,5 | 0.066 | 3.126 |  |  | 3.126 | 0 | 2.63 | -0.496 | -0.496 | closed
16 | SS 35/10 Vyatskoe | 4,0+4,0 | 1.92 | 0.17 | 120 | 1.75 | 0 | 4.2 | 2.45 | 2.45 | opened | 16 | SS 35/10 Vyatskoe | 4,0+4,0 | 0.094 | 2.014 | 0.17 | 120 | 1.844 | 0 | 4.2 | 2.356 | 2.356 | opened
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.68 | 0.2 | 120 | 0.48 | 0 | 2.63 | 2.15 | 2.15 | opened | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0 | 0.68 | 0.2 | 120 | 0.48 | 0 | 2.63 | 2.15 | 2.15 | opened
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 3.41 | 0.37 | 120 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | opened | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.313 | 3.723 | 0.37 | 120 | 3.353 | 0 | 4.2 | 0.847 | 0.847 | opened
19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.14 | 1.02 | 120 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | opened | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 0.8609 | 3.0009 | 1.02 | 120 | 1.9809 | 0 | 4.2 | 2.2191 | 2.2191 | opened
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 2.1 |  |  | 2.1 | 0 | 6.62 | 4.52 | 4.52 | opened | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0.011 | 2.111 |  |  | 2.111 | 0 | 6.62 | 4.509 | 4.509 | opened
21 | SS 110/6 Depo | 16+16 | 2.37 |  |  | 2.37 | 0 | 16.8 | 14.43 | 14.43 | opened | 21 | SS 110/6 Depo | 16+16 | 11.862 | 14.232 |  |  | 14.232 | 0 | 16.8 | 2.568 | 2.568 | opened
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.79 | 1.17 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.097 | 1.887 | 1.17 | 120 | 0.717 | 0 | 1.68 | 0.963 | 0.963 | opened
23 | SS 110/10 Druzhba | 16+16 | 6.8 | 0.16 | 120 | 6.64 | 0 | 16.8 | 10.16 | 10.16 | opened | 23 | SS 110/10 Druzhba | 16+16 | 0.3323 | 7.1323 | 0.16 | 120 | 6.9723 | 0 | 16.8 | 9.8277 | 9.8277 | opened
24 | SS 35/10 Dubki | 6,3+6,3 | 3.48 | 0.67 | 120 | 2.81 | 0 | 6.62 | 3.81 | 3.81 | opened | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.2885 | 3.7685 | 0.67 | 120 | 3.0985 | 0 | 6.62 | 3.5215 | 3.5215 | opened
25 | SS 35/10 Dybino | 2,5+2,5 | 1.16 |  |  | 1.16 | 0 | 2.63 | 1.47 | 1.47 | opened | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.3165 | 1.4765 |  |  | 1.4765 | 0 | 2.63 | 1.1535 | 1.1535 | opened
26 | SS 35/6 Zavolzhskaya | 10+10 | 10.31 |  |  | 10.31 | 0 | 10.5 | 0.19 | 0.19 | opened | 26 | SS 35/6 Zavolzhskaya | 10+10 | 1.9928 | 12.3028 |  |  | 12.3028 | 0 | 10.5 | -1.8028 | -1.8028 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 37.53 |  |  | 37.53 | 0 | 42 | 4.47 | 4.47 | opened | 27 | SS 110/6/6 Institutskaya | 40+40 | 4.7488 | 42.2788 |  |  | 42.2788 | 0 | 42 | -0.27883 | -0.27883 | closed
28 | SS 35/10 Koza | 1,6+1,6 | 0.41 | 0.16 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | opened | 28 | SS 35/10 Koza | 1,6+1,6 | 0.014 | 0.424 | 0.16 | 120 | 0.264 | 0 | 1.68 | 1.416 | 1.416 | opened
29 | SS 110/35/6 Konstatinovo | 20+20 | 10.53 | 0.1 | 120 | 10.43 | 0 | 21 | 10.57 | 10.57 | opened | 29 | SS 110/35/6 Konstatinovo | 20+20 | 0.025 | 11.0525 | 0.1 | 120 | 10.9525 | 0 | 21 | 10.0475 | 10.0475 | opened
| Nom. capacity MV, МVА | 20+20 | 6.85 |  |  | 6.85 | 0 | 21 | 14.15 |  |  |  | Nom. capacity MV, МVА | 20+20 | 0 | 7.3725 |  |  | 7.3725 | 0 | 21 | 13.6275
| Nom. capacity LV, МVА | 20+20 | 3.68 | 0.1 | 120 | 3.58 | 0 | 21 | 17.42 |  |  |  | Nom. capacity LV, МVА | 20+20 | 0 | 3.68 | 0.1 | 120 | 3.58 | 0 | 21 | 17.42
30 | SS 35/10 Kurba | 2,5+2,5 | 1.79 | 0.71 | 120 | 1.08 | 0 | 2.63 | 1.55 | 1.55 | opened | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.033 | 1.823 | 0.71 | 120 | 1.113 | 0 | 2.63 | 1.517 | 1.517 | opened
31 | SS 35/10 Lesnye Polyany | 10+10 | 5.38 | 0.48 | 120 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened | 31 | SS 35/10 Lesnye Polyany | 10+10 | 0.9501 | 6.3301 | 0.48 | 120 | 5.8501 | 0 | 10.5 | 4.6499 | 4.6499 | opened
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 4.72 | 3.69 | 120 | 1.03 | 0 | 6.62 | 5.59 | 5.59 | opened | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 2.319 | 7.039 | 3.69 | 120 | 3.349 | 0 | 6.62 | 3.271 | 3.271 | opened
33 | SS 35/10 Nekrasovo | 10+10 | 11.67 |  |  | 11.67 | 0 | 10.5 | -1.17 | -1.17 | закрыт | 33 | SS 35/10 Nekrasovo | 10+10 | 1.0332 | 12.7032 |  |  | 12.7032 | 0 | 10.5 | -2.2032 | -2.2032 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.88 | 0.38 | 120 | 0.5 | 0 | 2.63 | 2.13 | 2.13 | opened | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.035 | 0.915 | 0.38 | 120 | 0.535 | 0 | 2.63 | 2.095 | 2.095 | opened
35 | SS 110/35/6 Oil refinary plant | 25+25 | 16.93 |  |  | 16.93 | 0 | 26.25 | 9.32 | 9.32 | opened | 35 | SS 110/35/6 Oil refinary plant | 25+25 | 7.025 | 17.3367 |  |  | 17.3367 | 0 | 26.25 | 8.9133 | 8.9133 | opened
| Nom. capacity MV, МVА | 25+25 | 7.07 |  |  | 7.07 | 0 | 26.25 | 19.18 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0 | 7.4767 |  |  | 7.4767 | 0 | 26.25 | 18.7733
| Nom. capacity LV, МVА | 25+25 | 9.86 |  |  | 9.86 | 0 | 26.25 | 16.39 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0 | 9.86 |  |  | 9.86 | 0 | 26.25 | 16.39
36 | SS 110/6/6 Orion | 40+40 | 16.01 |  |  | 16.01 | 0 | 42 | 25.99 | 25.99 |  | 36 | SS 110/6/6 Orion | 40+40 | 6.5893 | 22.5993 |  |  | 22.5993 | 0 | 42 | 19.4007 | 19.4007 | opened
37 | SS 110/35/6 Pavlovskaya | 20+25 | 25.25 |  |  | 25.25 | 0 | 21 | -4.25 | -4.25 | закрыт | 37 | SS 110/35/6 Pavlovskaya | 20+25 | 0.196 | 25.4065 |  |  | 25.4065 | 0 | 21 | -4.4065 | -4.4065 | closed
| Nom. capacity MV, МVА | 20+25 | 8.55 |  |  | 8.55 | 0 | 21 | 12.45 |  |  |  | Nom. capacity MV, МVА | 20+25 | 0 | 8.7065 |  |  | 8.7065 | 0 | 21 | 12.2935
| Nom. capaity LV, МVА | 20+25 | 16.7 |  |  | 16.7 | 0 | 21 | 4.3 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0 | 16.7 |  |  | 16.7 | 0 | 21 | 4.3
38 | SS 110/10 Pereval | 16+16 | 5.59 |  |  | 5.59 | 0 | 16.8 | 11.21 | 11.21 | opened | 38 | SS 110/10 Pereval | 16+16 | 2.2678 | 7.8578 |  |  | 7.8578 | 0 | 16.8 | 8.9422 | 8.9422 | opened
39 | SS 110/6/6 Perekop | 25+25 | 10.42 |  |  | 10.42 | 0 | 26.25 | 15.83 | 15.83 | opened | 39 | SS 110/6/6 Perekop | 25+25 | 3.3402 | 13.7602 |  |  | 13.7602 | 0 | 26.25 | 12.4898 | 12.4898 | opened
40 | SS 110/6/6 Poligraf | 40+40 | 45.91 |  |  | 45.91 | 0 | 42 | -3.91 | -3.91 | закрыт | 40 | SS 110/6/6 Poligraf | 40+40 | 5.6285 | 51.5385 |  |  | 51.5385 | 0 | 42 | -9.5385 | -9.5385 | closed
41 | SS 110/35/10 Prechistoe | 10+10 | 5.62 | 0.24 | 120 | 5.38 | 0 | 10.5 | 5.12 | 5.12 | opened | 41 | SS 110/35/10 Prechistoe | 10+10 | 0.2999 | 5.7232 | 0.24 | 120 | 5.4832 | 0 | 10.5 | 5.0168 | 5.0168 | opened
| Nom. capacity MV, МVА | 10+10 | 2.44 |  |  | 2.44 | 0 | 10.5 | 8.06 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 2.5432 |  |  | 2.5432 | 0 | 10.5 | 7.9568
| Nom. capacity LV, МVА | 10+10 | 3.18 | 0.24 | 120 | 2.94 | 0 | 10.5 | 7.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 3.18 | 0.24 | 120 | 2.94 | 0 | 10.5 | 7.56
42 | SS 35/10 Preventorium | 2,5+2,5 | 1.21 | 0.39 | 120 | 0.82 | 0 | 2.63 | 1.81 | 1.81 | opened | 42 | SS 35/10 Preventorium | 2,5+2,5 | 3.0263 | 4.2363 | 0.39 | 120 | 3.8463 | 0 | 2.63 | -1.2163 | -1.2163 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.53 | 0.04 | 120 | 0.49 | 0 | 2.63 | 2.14 | 2.14 | opened | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0 | 0.53 | 0.04 | 120 | 0.49 | 0 | 2.63 | 2.14 | 2.14 | opened
44 | SS 110/6/6 Severnaya | 63+63 | 38.17 |  |  | 38.17 | 0 | 66.15 | 27.98 | 27.98 | opened | 44 | SS 110/6/6 Severnaya | 63+63 | 16.3969 | 54.5669 |  |  | 54.5669 | 0 | 66.15 | 11.5831 | 11.5831 | opened
45 | SS 35/10 Sereda | 2,5+2,5 | 1.5 | 0.11 | 120 | 1.39 | 0 | 2.63 | 1.24 | 1.24 | opened | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.1405 | 1.6405 | 0.11 | 120 | 1.5305 | 0 | 2.63 | 1.0995 | 1.0995 | opened
46 | SS 110/6 Tormoznaya | 16+16 | 12.31 |  |  | 12.31 | 0 | 16.8 | 4.49 | 4.49 | opened | 46 | SS 110/6 Tormoznaya | 16+16 | 0.632 | 12.942 |  |  | 12.942 | 0 | 16.8 | 3.858 | 3.858 | opened
47 | SS 110/6 Petrol station pump | 16+16 | 6.43 |  |  | 6.43 | 0 | 16.8 | 10.37 | 10.37 | opened | 47 | SS 110/6 Petrol station pump | 16+16 | 0.6 | 7.03 |  |  | 7.03 | 0 | 16.8 | 9.77 | 9.77 | opened
48 | SS 35/10 Troitsa | 2,5+2,5 | 0.66 | 0.14 | 120 | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.005 | 0.665 | 0.14 | 120 | 0.525 | 0 | 2.63 | 2.105 | 2.105 | opened
49 | SS 35/10 Tunoshna | 4,0+2,5 | 1.53 | 0.01 | 120 | 1.52 | 0 | 2.63 | 1.11 | 1.11 | opened | 49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.113 | 1.643 |  | 120 | 1.643 | 0 | 2.63 | 0.987 | 0.987 | opened
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.83 |  |  | 6.83 | 0 | 6.62 | -0.21 | -0.21 | закрыт | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.1022 | 6.9322 |  |  | 6.9322 | 0 | 6.62 | -0.3122 | -0.3122 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.6 |  |  | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.036 | 0.636 |  |  | 0.636 | 0 | 2.63 | 1.994 | 1.994 | opened
52 | SS 35/10 Urozhay | 4,0+4,0 | 1.63 | 0.74 | 120 | 0.89 | 0 | 4.2 | 3.31 | 3.31 | opened | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.524 | 2.154 | 0.74 | 120 | 1.414 | 0 | 4.2 | 2.786 | 2.786 | opened
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.46 | 0.28 | 120 | 0.31 | 0 | 3.36 | 3.05 | 2.74 | opened | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 0.012 | 0.9 | 0.28 | 120 | 0.62 | 0 | 3.36 | 2.74 | 2.74 | opened
| Nom. capacity MV, МVА | 6.3 | 2.56 | [8 empty] | 2: Nom. capacity MV, МVА; 3: 6.3; 4: 0
| Nom. capacity LV, МVА | 6.3 | 0.9 | 0.28 | 120 | 0.62 | 0 | 3.36 | 2.74 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.9 | 0.28 | 120 | 0.62 | 0 | 3.36 | 2.74
54 | SS 110/10 Chayka | 25+25 | 16.2 |  |  | 16.2 | 0 | 26.25 | 10.05 | 10.05 | opened | 54 | SS 110/10 Chayka | 25+25 | 18.706 | 34.906 |  |  | 34.906 | 0 | 26.25 | -8.656 | -8.656 | closed
55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.53 | 0.19 | 120 | 1.34 | 0 | 2.63 | 1.29 | 1.29 | opened | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 0.3 | 1.83 | 0.19 | 120 | 1.64 | 0 | 2.63 | 0.99 | 0.99 | opened
56 | SS 35/10 Shchedrino | 4,0+4,0 | 1.51 |  |  | 1.51 | 0 | 4.2 | 2.69 | 2.69 | opened | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.399 | 1.909 |  |  | 1.909 | 0 | 4.2 | 2.291 | 2.291 | opened
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 29.43 |  |  | 29.43 | 0 | 42 | 12.57 | 12.57 | opened | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 7.366 | 36.796 |  |  | 36.796 | 0 | 42 | 5.204 | 5.204 | opened
58 | SS 110/10/6 Yartsevo | 25+25 | 5.48 |  |  | 5.48 | 0 | 26.25 | 20.77 | 20.77 | opened | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.351 | 5.831 |  |  | 5.831 | 0 | 26.25 | 20.419 | 20.419 | opened
59 | SS 110/10 Altynovo | 6,3+6,3 | 3.19 |  |  | 3.19 | 0 | 6.62 | 3.43 | 3.43 | opened | 59 | SS 110/10 Altynovo | 6,3+6,3 | 0.447 | 3.637 |  |  | 3.637 | 0 | 6.62 | 2.983 | 2.983 | opened
60 | SS 110/35/10 Borisogleb | 10+16 | 7.8 |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | opened | 60 | SS 110/35/10 Borisogleb | 10+16 | 0.7925 | 8.0516 |  |  | 8.0516 | 0 | 10.5 | 2.4484 | 2.4484 | opened
| Nom. capacity MV, МVА | 10+16 | 1.33 |  |  | 1.33 | 0 | 10.5 | 9.17 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0 | 1.5816 |  |  | 1.5816 | 0 | 10.5 | 8.9184
| Nom. capacity LV, МVА | 10+16 | 6.47 |  |  | 6.47 | 0 | 10.5 | 4.03 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0 | 6.47 |  |  | 6.47 | 0 | 10.5 | 4.03
61 | SS 110/35/10 Vasilkovo | 10+10 | 2.02 | 0.28 | 120 | 1.74 | 0 | 10.5 | 8.76 | 8.76 | opened | 61 | SS 110/35/10 Vasilkovo | 10+10 | 0.045 | 2.3205 | 0.28 | 120 | 2.0405 | 0 | 10.5 | 8.4595 | 8.4595 | opened
| Nom. capacity MV, МVА | 10+10 | 1.44 |  |  | 1.44 | 0 | 10.5 | 9.06 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 1.7405 |  |  | 1.7405 | 0 | 10.5 | 8.7595
| Nom. capacity LV, МVА | 10+10 | 0.58 | 0.28 | 120 | 0.3 | 0 | 10.5 | 10.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 0.58 | 0.28 | 120 | 0.3 | 0 | 10.5 | 10.2
62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.34 | 0.09 | 120 | 0.25 | 0 | 6.62 | 6.37 | 6.37 | opened | 62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0 | 0.34 | 0.09 | 120 | 0.25 | 0 | 6.62 | 6.37 | 6.37 | opened
63 | SS 110/6 Gavrilov Yam | 16+16 | 13.53 |  |  | 13.53 | 0 | 16.8 | 3.27 | 3.27 | opened | 63 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 13.53 |  |  | 13.53 | 0 | 16.8 | 3.27 | 3.27 | opened
64 | SS 110/6 Kinoplyonka | 6,3+10 | 9.57 |  |  | 9.57 | 0 | 6.62 | -2.95 | -2.95 | закрыт | 64 | SS 110/6 Kinoplyonka | 6,3+10 | 2.941 | 12.511 |  |  | 12.511 | 0 | 6.62 | -5.891 | -5.891 | closed
65 | SS 110/35/10 Klimatino | 6,3+6,3 | 1.85 |  |  | 1.85 | 0 | 6.62 | 4.77 | 4.77 | opened | 65 | SS 110/35/10 Klimatino | 6,3+6,3 | 0.015 | 1.85 |  |  | 1.85 | 0 | 6.62 | 4.77 | 4.77 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.63 |  |  | 0.63 | 0 | 6.62 | 5.99 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.63 |  |  | 0.63 | 0 | 6.62 | 5.99
| Nom. capacity LV, МVА | 6,3+6,3 | 1.22 |  |  | 1.22 | 0 | 6.62 | 5.4 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 1.22 |  |  | 1.22 | 0 | 6.62 | 5.4
66 | SS 110/35/10 Nila | 6,3+6,3 | 7.61 | 0.37 | 120 | 7.24 | 0 | 6.62 | -0.62 | -0.62 | закрыт | 66 | SS 110/35/10 Nila | 6,3+6,3 | 2.297 | 1.78 | 0.37 | 120 | 1.41 | 0 | 6.62 | 5.21 | 5.21 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 5.83 |  |  | 5.83 | 0 | 6.62 | 0.79 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  |  | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 6,3+6,3 | 1.78 | 0.37 | 120 | 1.41 | 0 | 6.62 | 5.21 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 1.78 | 0.37 | 120 | 1.41 | 0 | 6.62 | 5.21
67 | SS 110/35/6 Pereslavl | 25+25 | 22.95 |  |  | 22.95 | 0 | 26.25 | 3.3 | 3.3 | opened | 67 | SS 110/35/6 Pereslavl | 25+25 | 0.832 | 29.7585 |  |  | 29.7585 | 0 | 26.25 | -3.5085 | -3.5085 | closed
| Nom. capacity MV, МVА | 25+25 | 9.44 |  |  | 9.44 | 0 | 26.25 | 16.81 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0 | 16.2485 |  |  | 16.2485 | 0 | 26.25 | 10.0015
| Nom. capacity LV, МVА | 25+25 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74
68 | SS 110/10 Ploski | 2,5+2,5 | 1.47 |  |  | 1.47 | 0 | 2.63 | 1.16 | 1.16 | opened | 68 | SS 110/10 Ploski | 2,5+2,5 | 0.207 | 1.677 |  |  | 1.677 | 0 | 2.63 | 0.953 | 0.953 | opened
69 | SS 110/35/10 Rostov | 25+20 | 20.15 |  |  | 20.15 | 0 | 21 | 0.85 | 0.85 | opened | 69 | SS 110/35/10 Rostov | 25+20 | 1.152 | 20.433 |  |  | 20.433 | 0 | 21 | 0.567 | 0.567 | opened
| Nom. capacity MV, МVА | 25+20 | 1.83 |  |  | 1.83 | 0 | 21 | 19.17 |  |  |  | Nom. capacity MV, МVА | 25+20 | 0 | 2.113 |  |  | 2.113 | 0 | 21 | 18.887
| Nom. Capacity LV, МVА | 25+20 | 18.32 |  |  | 18.32 | 0 | 21 | 2.68 |  |  |  | Nom. Capacity LV, МVА | 25+20 | 0 | 18.32 |  |  | 18.32 | 0 | 21 | 2.68
70 | SS 110/35/10 Technical school | 6,3+6,3 | 5.27 |  |  | 5.27 | 0 | 6.62 | 1.35 | 1.35 | opened | 70 | SS 110/35/10 Technical school | 6,3+6,3 | 2.7885 | 6.7013 |  |  | 6.7013 | 0 | 6.62 | -0.08135 | -0.08135 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 2.47 |  |  | 2.47 | 0 | 6.62 | 4.15 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 3.9013 |  |  | 3.9013 | 0 | 6.62 | 2.7186
| Nom. capacity LV, МVА | 6,3+6,3 | 2.8 |  |  | 2.8 | 0 | 6.62 | 3.82 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 2.8 |  |  | 2.8 | 0 | 6.62 | 3.82
71 | SS 110/35/10 Uglich | 25+25 | 22.82 |  |  | 22.82 | 0 | 26.25 | 3.43 | 3.43 | opened | 71 | SS 110/35/10 Uglich | 25+25 | 2.3065 | 22.9085 |  |  | 22.9085 | 0 | 26.25 | 3.3415 | 3.3415 | closed
| Nom. capacidty MV, МVА | 25+25 | 17.79 |  |  | 17.79 | 0 | 26.25 | 8.46 |  |  |  | Nom. capacidty MV, МVА | 25+25 | 0 | 17.8785 |  |  | 17.8785 | 0 | 26.25 | 8.3715
| Nom. capacity LV, МVА | 25+25 | 5.03 |  |  | 5.03 | 0 | 26.25 | 21.22 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0 | 5.03 |  |  | 5.03 | 0 | 26.25 | 21.22
72 | SS 110/10 Ustye | 10+10 | 3.86 | 0.32 | 120 | 3.54 | 0 | 10.5 | 6.96 | 6.96 | opened | 72 | SS 110/10 Ustye | 10+10 | 0.152 | 4.012 | 0.32 | 120 | 3.692 | 0 | 10.5 | 6.808 | 6.808 | opened
73 | SS 110/10 Shurskol | 10+10 | 1.97 | 1.01 | 120 | 0.96 | 0 | 10.5 | 9.54 | 9.54 | opened | 73 | SS 110/10 Shurskol | 10+10 | 0.193 | 2.163 | 1.01 | 120 | 1.153 | 0 | 10.5 | 9.347 | 9.347 | opened
74 | SS 110/10 Yur.Sloboda | 10+10 | 8.32 | 0.23 | 120 | 8.09 | 0 | 10.5 | 2.41 | 2.41 | opened | 74 | SS 110/10 Yur.Sloboda | 10+10 | 1.183 | 9.503 | 0.23 | 120 | 9.273 | 0 | 10.5 | 1.227 | 1.227 | opened
75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.52 |  |  | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened | 75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.021 | 0.541 |  |  | 0.541 | 0 | 2.63 | 2.089 | 2.089 | opened
76 | SS 35/6 Batki | 1,6+1,6 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | opened | 76 | SS 35/6 Batki | 1,6+1,6 | 0.0748 | 1.2548 |  |  | 1.2548 | 0 | 1.68 | 0.4252 | 0.4252 | opened
77 | SS 35/10 Beregovaya | 1.6 | 0.18 | 1.64 | 24 hours | 1.64 | 0 | 1.64 | 1.46 | 1.46 | opened | 77 | SS 35/10 Beregovaya | 1.6 | 0.005 | 0.185 | 1.64 | 24 hours | 1.64 | 0 | 1.64 | 1.455 | 1.455 | opened
78 | SS 35/10 Berendeevo | 2,5+2,5 | 1.63 | 0.12 | 24 hours | 1.51 | 0 | 2.63 | 1.12 | 1.12 | opened | 78 | SS 35/10 Berendeevo | 2,5+2,5 | 0.332 | 1.962 |  |  | 1.962 | 0 | 2.63 | 0.668 | 0.668 | opened
79 | SS 35/10 Vorzha | 1,8+1,8 | 0.39 | 0.3 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 79 | SS 35/10 Vorzha | 1,8+1,8 | 0.265 | 0.655 | 0.3 | 120 | 0.355 | 0 | 1.89 | 1.535 | 1.535 | opened
80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.79 | 0.21 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.06 | 0.85 | 0.21 | 120 | 0.64 | 0 | 1.68 | 1.04 | 1.04 | opened
81 | SS 35/10 Glebovo | 2,5+2,5 | 2.76 |  |  | 2.76 | 0 | 2.63 | -0.13 | -0.13 | закрыт | 81 | SS 35/10 Glebovo | 2,5+2,5 | 1.2931 | 4.0531 |  |  | 4.0531 | 0 | 2.63 | -1.4231 | -1.4231 | closed
82 | SS 35/10 Gorki | 2,5+2,5 | 1.13 |  |  | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 82 | SS 35/10 Gorki | 2,5+2,5 | 0.127 | 1.257 |  |  | 1.257 | 0 | 2.63 | 1.373 | 1.373 | opened
83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.26 |  |  | 1.26 | 0 | 1.68 | 0.42 | 0.42 | opened | 83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.022 | 1.282 |  |  | 1.282 | 0 | 1.68 | 0.398 | 0.398 | opened
84 | SS 35/10 Zaozerye | 2,5+1,6 | 1.12 |  |  | 1.12 | 0 | 1.68 | 0.56 | 0.56 | opened | 84 | SS 35/10 Zaozerye | 2,5+1,6 | 0.034 | 1.154 |  |  | 1.154 | 0 | 1.68 | 0.526 | 0.526 | opened
85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 1.46 |  |  | 1.46 | 0 | 2.63 | 1.17 | 1.17 | opened | 85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0485 | 1.5085 |  |  | 1.5085 | 0 | 2.63 | 1.1215 | 1.1215 | opened
86 | SS 35/10 Kibernetik | 6,3+6,3 | 2.45 |  |  | 2.45 | 0 | 6.62 | 4.17 | 4.17 | opened | 86 | SS 35/10 Kibernetik | 6,3+6,3 | 3.184 | 5.634 |  |  | 5.634 | 0 | 6.62 | 0.986 | 0.986 | opened
87 | SS 35/10 Klementyevo | 2.5 | 0.29 | 0.69 | 24 hours | 0.69 | 0 | 0.69 | 0.4 | 0.4 | opened | 87 | SS 35/10 Klementyevo | 2.5 | 0.006 | 0.296 | 0.69 | 24 hours | 0.69 | 0 | 0.69 | 0.394 | 0.394 | opened
88 | SS 35/10 Krasnoe | 4,0+4,0 | 1.09 | 0.3 | 120 | 0.79 | 0 | 4.2 | 3.41 | 3.41 | opened | 88 | SS 35/10 Krasnoe | 4,0+4,0 | 0.793 | 1.883 | 0.3 | 120 | 1.583 | 0 | 4.2 | 2.617 | 2.617 | opened
89 | SS 35/10 Kulakovo | 2,5+2,5 | 1.66 |  |  | 1.66 | 0 | 2.63 | 0.97 | 0.97 | opened | 89 | SS 35/10 Kulakovo | 2,5+2,5 | 0.125 | 1.785 |  |  | 1.785 | 0 | 2.63 | 0.845 | 0.845 | opened
90 | SS 35/6 Kupan | 2,5+2,5 | 2.58 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | opened | 90 | SS 35/6 Kupan | 2,5+2,5 | 0.601 | 3.181 |  |  | 3.181 | 0 | 2.63 | -0.551 | -0.551 | closed
91 | SS 35/10 Markovo | 2,5+2,5 | 0.82 | 0.27 | 120 | 0.55 | 0 | 2.63 | 2.08 | 2.08 | opened | 91 | SS 35/10 Markovo | 2,5+2,5 | 0.275 | 1.095 | 0.27 | 120 | 0.825 | 0 | 2.63 | 1.805 | 1.805 | opened
92 | SS 35/10 Nagorye | 4,0+4,0 | 3.23 |  |  | 3.23 | 0 | 4.2 | 0.97 | 0.97 | opened | 92 | SS 35/10 Nagorye | 4+4 | 0.346 | 3.576 |  |  | 3.576 | 0 | 4.2 | 0.624 | 0.624 | opened
93 | SS 35/10 Porechye | 6,3+6,3 | 1.9 | 0.61 | 120 | 1.29 | 0 | 6.62 | 5.33 | 5.33 | opened | 93 | SS 35/10 Porechye | 6,3+6,3 | 0.061 | 1.961 | 0.61 | 120 | 1.351 | 0 | 6.62 | 5.269 | 5.269 | opened
94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened | 94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.0065 | 0.8565 |  |  | 0.8565 | 0 | 2.63 | 1.7735 | 1.7735 | opened
95 | SS 35/10 Ramenye | 2,5+2,5 | 0.8 | 0.26 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened | 95 | SS 35/10 Ramenye | 2,5+2,5 | 0.0265 | 0.8265 | 0.26 | 120 | 0.5665 | 0 | 2.63 | 2.0635 | 2.0635 | opened
96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 1.51 |  |  | 1.51 | 0 | 1.68 | 0.17 | 0.17 | opened | 96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 0.041 | 1.551 |  |  | 1.551 | 0 | 1.68 | 0.129 | 0.129 | opened
97 | SS 35/10 Saraevo | 1+1,6 | 0.84 |  |  | 0.84 | 0 | 1.05 | 0.21 | 0.21 | opened | 97 | SS 35/10 Saraevo | 1+1,6 | 0.682 | 1.522 |  |  | 1.522 | 0 | 1.05 | -0.472 | -0.472 | closed
98 | SS 35/10 Selifontovo | 2,5+2,5 | 1.87 | 0.16 | 120 | 1.71 | 0 | 2.63 | 0.92 | 0.92 | opened | 98 | SS 35/10 Selifontovo | 2,5+2,5 | 0.249 | 2.119 | 0.16 | 120 | 1.959 | 0 | 2.63 | 0.671 | 0.671 | opened
99 | SS 35/10 Semibratovo | 4,0+4,0 | 0.78 | 0.25 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 99 | SS 35/10 Semibratovo | 4+4 | 0.01 | 0.79 | 0.25 | 120 | 0.25 | 0 | 0.25 | -0.54 | -0.54 | closed
100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.94 |  |  | 0.94 | 0 | 1.68 | 0.74 | 0.74 | opened | 100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.2681 | 1.2081 |  |  | 1.2081 | 0 | 1.68 | 0.4719 | 0.4719 | opened
101 | SS 35/10 Solomidino | 2.5 | 0.57 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | 0.24 | 0.24 | opened | 101 | SS 35/10 Solomidino | 2.5 | 1.2906 | 1.8606 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | -1.0506 | -1.0506 | closed
102 | SS 35/10 Stavotino | 4,0+4,0 | 1.72 | 0.51 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened | 102 | SS 35/10 Stavotino | 4+4 | 0.7935 | 2.5135 | 0.51 | 120 | 2.0035 | 0 | 4.2 | 2.1965 | 2.1965 | opened
103 | SS 35/10 Urusovo | 2,5+2,5 | 0.79 | 0.06 | 120 | 0.73 | 0 | 2.63 | 1.9 | 1.9 | opened | 103 | SS 35/10 Urusovo | 2,5+2,5 | 0.003 | 0.793 | 0.06 | 120 | 0.733 | 0 | 2.63 | 1.897 | 1.897 | opened
104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.87 |  |  | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened | 104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.151 | 1.021 |  |  | 1.021 | 0 | 2.63 | 1.609 | 1.609 | opened
105 | SS 35/10 Choporovo | 2,5+2,5 | 0.54 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened | 105 | SS 35/10 Choporovo | 2,5+2,5 | 0.117 | 0.657 |  |  | 0.657 | 0 | 2.63 | 1.973 | 1.973 | opened
106 | SS 35/10 Shchurovo | 2,5+2,5 | 1.31 | 0.27 | 120 | 1.04 | 0 | 2.63 | 1.59 | 1.59 | opened | 106 | SS 35/10 Shchurovo | 2,5+2,5 | 0.0255 | 1.3355 | 0.27 | 120 | 1.0655 | 0 | 2.63 | 1.5645 | 1.5645 | opened
107 | SS 35/10 Neksans | 10+10 | 1.2 |  |  | 1.2 | 0 | 10.5 | 9.3 | 9.3 | opened | 107 | SS 35/10 Neksans | 10+10 | 0 | 1.2 |  |  | 1.2 | 0 | 10.5 | 9.3 | 9.3 | opened
108 | SS 35/6 Pribrezhnaya | 10+10 | 11.28 |  |  | 11.28 | 0 | 10.5 | -0.78 | -0.78 | закрыт | 108 | SS 35/6 Pribrezhnaya | 10+10 | 0 | 11.28 |  |  | 11.28 | 0 | 10.5 | -0.78 | -0.78 | closed
109 | SS 110/10 Product pipeline | 6,3+6,3 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened | 109 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened
110 | SS 110/10 Nekouz | 6,3+6,3 | 4.3 | 0.1 | 120 | 4.2 | 0 | 6.62 | 2.42 | 2.42 | opened | 110 | SS 110/10 Nekouz | 6,3+6,3 | 0.00135 | 4.3014 | 0.1 | 120 | 4.2013 | 0 | 6.62 | 2.4186 | 2.4186 | opened
111 | SS 110/6 Yuzhnaya | 25+25 | 21.25 |  |  | 21.25 | 0 | 26.25 | 5 | 5 | opened | 111 | SS 110/6 Yuzhnaya | 25+25 | 0 | 21.25 |  |  | 21.25 | 0 | 26.25 | 5 | 5 | opened
112 | SS 110/10 Optika | 10+10 | 4.9 | 1.18 | 120 | 3.72 | 0 | 10.5 | 6.78 | 6.78 | opened | 112 | SS 110/10 Optika | 10+10 | 0.33 | 5.23 | 1.18 | 120 | 4.05 | 0 | 10.5 | 6.45 | 6.45 | opened
113 | SS 110/6 Poligrafmash | 16+16 | 10.4 |  |  | 10.4 | 0 | 16.8 | 6.4 | 6.4 | opened | 113 | SS 110/6 Poligrafmash | 16+16 | 0.18 | 10.58 |  |  | 10.58 | 0 | 16.8 | 6.22 | 6.22 | opened
114 | SS 110/6/6 Zapadnaya | 63+63 | 52.3 |  |  | 52.3 | 0 | 66.15 | 13.85 | 13.85 | opened | 114 | SS 110/6/6 Zapadnaya | 63+63 | 0.8655 | 53.1655 |  |  | 53.1655 | 0 | 66.15 | 12.9845 | 12.9845 | opened
115 | SS 110/35/6 Volzhskaya | 40+40 | 26 |  |  | 26 | 0 | 42 | 16 | 16 | opened | 115 | SS 110/35/6 Volzhskaya | 40+40 | 0.022 | 26 |  |  | 26 | 0 | 42 | 16 | 16 | opened
| Nom. capacity MV, МVА | 40+40 | [9 empty] | 2: Nom. capacity MV, МVА; 3: 40+40; 4: 0
| Nom. capacity LV, МVА | 40+40 | 26 |  |  | 7.9 | 0 | 42 | 34.1 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0 | 26 |  |  | 26 | 0 | 42 | 16
116 | SS 110/35/6 Levoberezhnaya | 16+16 | 12.2 |  |  | 12.2 | 0 | 16.8 | 4.6 | 4.6 | opened | 116 | SS 110/35/6 Levoberezhnaya | 16+16 | 0.178 | 5.6257 |  |  | 5.6257 | 0 | 16.8 | 11.1743 | 11.1743 | opened
| Nom. capacity MV, МVА | 16+16 | 0.84 |  |  | 0.84 | 0 | 16.8 | 15.96 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 1.2657 |  |  | 1.2657 | 0 | 16.8 | 15.5343
| Nom. capacity LV, МVА | 16+16 | 4.36 |  |  | 4.36 | 0 | 16.8 | 12.44 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0 | 4.36 |  |  | 4.36 | 0 | 16.8 | 12.44
117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 2.4 |  |  | 2.4 | 0 | 7.88 | 5.48 | 5.48 | opened | 117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 0.01 | 2.4 |  |  | 2.4 | 0 | 7.88 | 5.48 | 5.48 | opened
| Nom. capacity MV, МVА | 7,5+7,5 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 | 0 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43
| Nom. capacity LV, МVА | 7,5+7,5 | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93
118 | SS 110/6 Dock yard | 10+10 | 4.4 |  |  | 4.4 | 0 | 10.5 | 6.1 | 6.1 | opened | 118 | SS 110/6 Dock yard | 10+10 | 0.056 | 4.456 |  |  | 4.456 | 0 | 10.5 | 6.044 | 6.044 | opened
119 | SS 110/6 Selekhovo | 6,3+6,3 | 3.4 |  |  | 3.4 | 0 | 6.62 | 3.22 | 3.22 | opened | 119 | SS 110/6 Selekhovo | 6,3+6,3 | 0.102 | 3.502 |  |  | 3.502 | 0 | 6.62 | 3.118 | 3.118 | opened
120 | SS 35/6 Kamenniki | 4,0+4,0 | 2.32 |  |  | 2.32 | 0 | 4.2 | 1.88 | 1.88 | opened | 120 | SS 35/6 Kamenniki | 4+4 | 0.149 | 2.469 |  |  | 2.469 | 0 | 4.2 | 1.731 | 1.731 | opened
121 | SS 35/10 Shashkovo | 1,6+1,6 | 1.49 | 0.52 | 120 | 0.97 | 0 | 1.68 | 0.71 | 0.71 | opened | 121 | SS 35/10 Shashkovo | 1,6+1,6 | 0.1976 | 1.6876 | 0.52 | 120 | 1.1676 | 0 | 1.68 | 0.5124 | 0.5124 | opened
122 | SS 110/6 Мукуену | 25+25 | 17.75 |  |  | 17.75 | 0 | 26.25 | 8.5 | 8.5 | opened | 122 | SS 110/6 Мукуену | 25+25 | 2.652 | 20.402 |  |  | 20.402 | 0 | 26.25 | 5.848 | 5.848 | opened
123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.08 | 0.73 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 0.532 | 2.612 | 0.73 | 120 | 1.882 | 0 | 4.2 | 2.318 | 2.318 | opened
124 | SS 35/10 Arefino | 2,5+2,5 | 1.65 | 0.52 | 120 | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 124 | SS 35/10 Arefino | 2,5+2,5 | 0.127 | 1.777 | 0.52 | 120 | 1.257 | 0 | 2.63 | 1.373 | 1.373 | opened
125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.62 |  |  | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.045 | 0.665 |  |  | 0.665 | 0 | 1.68 | 1.015 | 1.015 | opened
126 | SS 35/10 Pokrov | 1,6+1,6 | 0.58 | 0.87 | 120 | -0.29 | 0 | 1.68 | 1.97 | 1.97 | opened | 126 | SS 35/10 Pokrov | 1,6+1,6 | 0.0015 | 0.5815 | 0.87 | 120 | -0.2885 | 0 | 1.68 | 1.9685 | 1.9685 | opened
127 | SS 35/10 Anikovo | 2,5+2,5 | 0.88 | 0.04 | 120 | 0.84 | 0 | 2.63 | 1.79 | 1.79 | opened | 127 | SS 35/10 Anikovo | 2,5+2,5 | 0.0395 | 0.9195 | 0.04 | 120 | 0.8795 | 0 | 2.63 | 1.7505 | 1.7505 | opened
128 | SS 35/10 Novoe selo | 2,5+2,5 | 1.13 |  |  | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.304 | 1.434 |  |  | 1.434 | 0 | 2.63 | 1.196 | 1.196 | opened
129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 4.6 |  |  | 4.6 | 0 | 6.62 | 2.02 | 2.02 | opened | 129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.1594 | 4.7594 |  |  | 4.7594 | 0 | 6.62 | 1.8606 | 1.8606 | opened
130 | SS 35/10 Breytovo | 4,0+4,0 | 3.92 |  |  | 3.92 | 0 | 4.2 | 0.28 | 0.28 | opened | 130 | SS 35/10 Breytovo | 4+4 | 1.177 | 5.097 |  |  | 5.097 | 0 | 4.2 | -0.897 | -0.897 | closed
131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.83 | 0.21 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.008 | 0.838 | 0.21 | 120 | 0.628 | 0 | 1.68 | 1.052 | 1.052 | opened
132 | SS 35/10 Znamovo | 2,5+2,5 | 1.03 | 0.25 | 120 | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 132 | SS 35/10 Znamovo | 2,5+2,5 | 0.053 | 1.083 | 0.25 | 120 | 0.833 | 0 | 2.63 | 1.797 | 1.797 | opened
133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 1.18 |  |  | 1.18 | 0 | 2.63 | 1.45 | 1.45 | opened | 133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0 | 1.18 |  |  | 1.18 | 0 | 2.63 | 1.45 | 1.45 | opened
134 | SS 35/10 Zapolye | 2,5+2,5 | 0.6 |  |  | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 134 | SS 35/10 Zapolye | 2,5+2,5 | 0.012 | 0.612 |  |  | 0.612 | 0 | 2.63 | 2.018 | 2.018 | opened
135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.31 | 0.82 | 120 | 0.49 | 0 | 1.68 | 1.19 | 1.19 | opened | 135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.03 | 1.34 | 0.82 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
136 | SS 35/10 Latskoe | 1,6+2,5 | 0.43 | 0.1 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened | 136 | SS 35/10 Latskoe | 1,6+2,5 | 0 | 0.43 | 0.1 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
137 | SS 35/10 Borok | 2,5+4,0 | 1.25 | 0.46 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | opened | 137 | SS 35/10 Borok | 2,5+4 | 0.142 | 1.392 | 0.46 | 120 | 0.932 | 0 | 2.63 | 1.698 | 1.698 | opened
138 | SS 35/10 Myshkin | 4,0+6,3 | 3.97 | 0.41 | 120 | 3.56 | 0 | 4.2 | 0.64 | 0.64 | opened | 138 | SS 35/10 Myshkin | 4+6,3 | 0.536 | 4.506 | 0.41 | 120 | 4.096 | 0 | 4.2 | 0.104 | 0.104 | opened
139 | SS 110/10 Volga | 6,3+5,6 | 2.03 |  |  | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened | 139 | SS 110/10 Volga | 6,3+5,6 | 0 | 2.03 |  |  | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened
140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 2.38 | 0.29 | 120 | 2.09 | 0 | 2.63 | 0.54 | 0.54 | opened | 140 | SS 35/10 Krasnaya Gorka | 4+2,5 | 0.139 | 2.519 | 0.29 | 120 | 2.229 | 0 | 2.63 | 0.401 | 0.401 | opened
141 | SS 110/35/6 Vostochnaya | 25+25 | 19.29 |  |  | 19.29 | 0 | 26.25 | 6.96 | 6.96 | opened | 141 | SS 110/35/6 Vostochnaya | 25+25 | 0.1424 | 19.707 |  |  | 19.707 | 0 | 26.25 | 6.543 | 6.543 | opened
| Nom. capacity MV, МVА | 25+25 | 2.95 |  |  | 2.95 | 0 | 26.25 | 23.3 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0 | 3.367 |  |  | 3.367 | 0 | 26.25 | 22.883
| Nom. capacity LV, МVА | 25+25 | 16.34 |  |  | 16.34 | 0 | 26.25 | 9.91 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0 | 16.34 |  |  | 16.34 | 0 | 26.25 | 9.91
142 | SS 110/35/10 Zalesye | 10+10 | 8.54 | 1.65 | 120 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | opened | 142 | SS 110/35/10 Zalesye | 10+10 | 0.024 | 8.593 | 1.65 | 120 | 6.943 | 0 | 10.5 | 3.557 | 3.557 | opened
| Nom. capacity MV, МVА | 10+10 | 1.92 |  |  | 1.92 | 0 | 10.5 | 8.58 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 1.973 |  |  | 1.973 | 0 | 10.5 | 8.527
| Nom. capacity LV, МVА | 10+10 | 6.62 | 1.65 | 120 | 4.97 | 0 | 10.5 | 5.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 6.62 | 1.65 | 120 | 4.97 | 0 | 10.5 | 5.53
143 | SS 110/10 Lugovaya | 6,3+6,3 | 3.7 |  |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 | opened | 143 | SS 110/10 Lugovaya | 6,3+6,3 | 0.105 | 3.805 |  |  | 3.805 | 0 | 6.62 | 2.815 | 2.815 | opened
144 | SS 110/35/10 Lom | 10+10 | 8.06 | 1.07 | 120 | 6.99 | 0 | 10.5 | 3.51 | 3.51 | opened | 144 | SS 110/35/10 Lom | 10+10 | 0.1928 | 8.5924 | 1.07 | 120 | 7.5224 | 0 | 10.5 | 2.9776 | 2.9776 | opened
| Nom. capacity MV, МVА | 10+10 | 6.65 |  |  | 6.65 | 0 | 10.5 | 3.85 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 7.1824 |  |  | 7.1824 | 0 | 10.5 | 3.3176
| Nom. capacity LV, МVА | 10+10 | 1.41 | 1.07 | 120 | 0.34 | 0 | 10.5 | 10.16 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 1.41 | 1.07 | 120 | 0.34 | 0 | 10.5 | 10.16
145 | SS 35/10 Varegovo | 2,5+1,6 | 0.88 |  |  | 0.88 | 0 | 1.68 | 0.8 | 0.8 | opened | 145 | SS 35/10 Varegovo | 2,5+1,6 | 0.069 | 0.949 |  |  | 0.949 | 0 | 1.68 | 0.731 | 0.731 | opened
146 | SS 110/35/10 Shestikhino | 10+10 | 5.14 | 0.27 | 120 | 4.87 | 0 | 10.5 | 5.63 | 5.63 | opened | 146 | SS 110/35/10 Shestikhino | 10+10 | 0.156 | 6.4185 | 0.27 | 120 | 6.1485 | 0 | 10.5 | 4.3515 | 4.3515 | opened
| Nom. capacity MV, МVА | 10+10 | 4.59 |  |  | 4.59 | 0 | 10.5 | 5.91 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 5.8685 |  |  | 5.8685 | 0 | 10.5 | 4.6315
| Nom. capacity LV, МVА | 10+10 | 0.55 | 0.27 | 120 | 0.28 | 0 | 10.5 | 10.22 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 0.55 | 0.27 | 120 | 0.28 | 0 | 10.5 | 10.22
147 | SS 110/35/10 Kryukovo | 6.3 | 4.28 | 0.87 | 24 hours | 3.41 | 0 | 6.62 | 3.21 | 2.64 | opened | 147 | SS 110/35/10 Kryukovo | 6.3 | 0 | 4.548 | 0.87 | 24 hours | 3.678 | 0 | 6.62 | 2.942 | 2.372 | opened
| Nom. capacidty MV, МVА | 6.3 | 3.98 |  |  | 3.98 | 0 | 6.62 | 2.64 |  |  |  | Nom. capacidty MV, МVА | 6.3 | 0 | 4.248 |  |  | 4.248 | 0 | 6.62 | 2.372
| Nom. capacity LV, МVА | 6.3 | 0.3 | 0.87 | 24 hours | -0.57 | 0 | 6.62 | 7.19 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.3 | 0.87 | 24 hours | -0.57 | 0 | 6.62 | 7.19
148 | SS 35/10 Beloe | 2.5 | 0.73 | 1.24 | 24 hours | 1.24 | 0 | 1.24 | 0.51 | 0.51 | opened | 148 | SS 35/10 Beloe | 2.5 | 0.015 | 0.745 | 1.24 | 24 hours | 1.24 | 0 | 1.24 | 0.495 | 0.495 | opened
149 | SS 110/35/10 Glebovo | 10 | 5.13 | 0.6 | 24 hours | 4.53 | 0 | 10.5 | 5.97 | 5.97 | opened | 149 | SS 110/35/10 Glebovo | 10 | 0.479 | 5.426 | 0.6 | 24 hours | 4.826 | 0 | 10.5 | 5.674 | 5.674 | opened
| Nom. capacity MV, МVА | 10 | 3.02 |  |  | 3.02 | 0 | 10.5 | 7.48 |  |  |  | Nom. capacity MV, МVА | 10 | 0 | 3.316 |  |  | 3.316 | 0 | 10.5 | 7.184
| Nom. capacity LV, МVА | 10 | 2.11 | 0.6 | 24 hours | 1.51 | 0 | 10.5 | 8.99 |  |  |  | Nom. capacity LV, МVА | 10 | 0 | 2.11 | 0.6 | 24 hours | 1.51 | 0 | 10.5 | 8.99
150 | SS 35/10 Ermakovo | 1.6 | 0.83 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.04 | 0.04 | opened | 150 | SS 35/10 Ermakovo | 1.6 | 0.13 | 0.96 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | -0.09 | -0.09 | closed
151 | SS 35/10 Milyushino | 1.6 | 0.72 | 0.88 | 24 hours | 0.88 | 0 | 0.88 | 0.16 | 0.16 | opened | 151 | SS 35/10 Milyushino | 1.6 | 0.05 | 0.77 | 0.88 | 24 hours | 0.88 | 0 | 0.88 | 0.11 | 0.11 | opened
152 | SS 35/10 Sutka | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 152 | SS 35/10 Sutka | 2.5 | 0.022 | 0.622 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | -0.022 | -0.022 | closed
153 | SS 35/10 Sit | 1.6 | 0.53 | 0.55 | 24 hours | 0.55 | 0 | 0.55 | 0.02 | 0.02 | opened | 153 | SS 35/10 Sit | 1.6 | 0.3383 | 0.8683 | 0.55 | 24 hours | 0.55 | 0 | 0.55 | -0.3183 | -0.3183 | closed
154 | SS 35/10 Gorelovo | 1.6 | 0.38 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0.23 | 0.23 | opened | 154 | SS 35/10 Gorelovo | 1.6 | 0.276 | 0.656 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | -0.046 | -0.046 | closed
155 | SS 35/6 Pishchalkino | 1.6 | 0.94 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.74 | 0.74 | opened | 155 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.94 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.74 | 0.74 | opened
156 | SS 35/6 Varegovo | 1.6 | 0.22 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.46 | 1.46 | opened | 156 | SS 35/6 Varegovo | 1.6 | 0 | 0.22 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.46 | 1.46 | opened
| Total: | 2619.3 | 869.07 | [8 empty] | 2: Total:; 3: 2619.3; 5: 1001.998
| deficit | [8 empty] | 15.3 |  | 2: deficit; Мin. 12: 14.4387
| proficit | [8 empty] | 547.73 |  | 2: proficit; Мin. 12: 392.612
Deputy Director for technical
[13 empty] | issues- chief engineer | [8 empty] | E.V. Turapin

## Смоленскэнерго
[9 empty] | table 1 | [13 empty] | table2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the mode n-1, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.18 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.52 | 0.52 | opened | 1 | Gerchiki 35/10 | 2.5 | 0.4 | 0.58 | 0.7 | 24 hours | -0.12 | 0 | 0.7 | 0.12 | 0.12 | opened
2 | Verkhovye 35/10 | 4 | 0.6 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.76 | 0.76 | opened | 2 | Verkhovye 35/10 | 4 | 0.02 | 0.62 | 1.36 | 24 hours | -0.74 | 0 | 1.36 | 0.74 | 0.74 | opened
3 | Neykovo 35/10 | 2.5 | 0.22 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.51 | 1.51 | opened | 3 | Neykovo 35/10 | 2.5 | 0 | 0.22 | 1.73 | 24 hours | -1.51 | 0 | 1.73 | 1.51 | 1.51 | opened
4 | Merlino 110/35/10 | 6.3 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 | opened | 4 | Merlino 110/35/10 | 6.3 | 0.1 | 0.48 | 0.48 | 24 hours | 0 | 0 | 0.48 | 0 | 0 | opened
| Nom. capacity MV, МVА | 6.3 | 0.15 | 0.15 | 24 hours | 0.15 | 0 | 0.15 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0 | 0.15 | 0.15 | 24 hours | 0 | 0 | 0.15 | 0
| Nom. capacity LV, МVА | 6.3 | 0.25 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.1 | 0.35 | 0.35 | 24 hours | 0 | 0 | 0.35 | 0
5 | Belyaevo 35/10 | 1.6 | 0.21 | 2.11 | 24 hours | 2.11 | 0 | 2.11 | 1.9 | 1.9 | opened | 5 | Belyaevo 35/10 | 1.6 | 0.1 | 0.31 | 2.11 | 24 hours | -1.8 | 0 | 2.11 | 1.8 | 1.8 | opened
6 | Zaozerye 35/10 | 1.6 | 0.16 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.69 | 0.69 | opened | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.16 | 0.85 | 24 hours | -0.69 | 0 | 0.85 | 0.69 | 0.69 | opened
7 | Selezni 35/10 | 2.5 | 0.48 | 2.21 | 24 hours | 2.21 | 0 | 2.21 | 1.73 | 1.73 | opened | 7 | Selezni 35/10 | 2.5 | 0 | 0.48 | 2.21 | 24 hours | -1.73 | 0 | 2.21 | 1.73 | 1.73 | opened
8 | Logovo 110/10 | 6.3 | 0.4 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.96 | 0.96 | opened | 8 | Logovo 110/10 | 6.3 | 0 | 0.4 | 1.36 | 24 hours | -0.96 | 0 | 1.36 | 0.96 | 0.96 | opened
9 | Dubrovka 35/10 | 2.5 | 0.24 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 1.12 | 1.12 | opened | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.34 | 1.36 | 24 hours | -1.02 | 0 | 1.36 | 1.02 | 1.02 | opened
10 | Svistovichi 35/10 | 2.5 | 0.12 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.73 | 0.73 | opened | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.12 | 0.85 | 24 hours | -0.73 | 0 | 0.85 | 0.73 | 0.73 | opened
11 | Elsha 35/10 | 1.6 | 0.03 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.82 | 0.82 | opened | 11 | Elsha 35/10 | 1.6 | 0 | 0.03 | 0.85 | 24 hours | -0.82 | 0 | 0.85 | 0.82 | 0.82 | opened
12 | Sapsho 35/10 | 4 | 0.82 | 2.12 | 24 hours | 2.12 | 0 | 2.12 | 1.3 | 1.3 | opened | 12 | Sapsho 35/10 | 4 | 0.18 | 1 | 2.12 | 24 hours | -1.12 | 0 | 2.12 | 1.12 | 1.12 | opened
13 | Divo 110/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 13 | Divo 110/10 | 2.5 | 0.16 | 0.38 | 0.85 | 24 hours | -0.47 | 0 | 0.85 | 0.47 | 0.47 | opened
14 | Vachkovo 35/10 | 2.5 | 0.61 | 1.02 | 24 hours | 1.02 | 0 | 1.02 | 0.41 | 0.41 | opened | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.61 | 1.02 | 24 hours | -0.41 | 0 | 1.02 | 0.41 | 0.41 | opened
15 | Zamoshye 35/10 | 2.5 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
16 | Loino 35/10 | 2.5 | 0.12 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.73 | 0.73 | opened | 16 | Loino 35/10 | 2.5 | 0 | 0.12 | 0.85 | 24 hours | -0.73 | 0 | 0.85 | 0.73 | 0.73 | opened
17 | Rokot 35/10 | 2.5 | 0.25 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.05 | 1.05 | opened | 17 | Rokot 35/10 | 2.5 | 0 | 0.25 | 1.3 | 24 hours | -1.05 | 0 | 1.3 | 1.05 | 1.05 | opened
18 | Nikontsy 35/10 | 2.5 | 0.07 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.78 | 0.78 | opened | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.07 | 0.85 | 24 hours | -0.78 | 0 | 0.85 | 0.78 | 0.78 | opened
19 | Batishchevo 35/10 | 2.5 | 0.21 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.52 | 1.52 | opened | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.21 | 1.73 | 24 hours | -1.52 | 0 | 1.73 | 1.52 | 1.52 | opened
20 | Vasino 35/10 | 2.5 | 0.34 | 0 | 24 hours | 0 | 0 | 0 | -0.34 | -0.34 | closed | 20 | Vasino 35/10 | 2.5 | 0 | 0.34 | 0 | 24 hours | 0.34 | 0 | 0 | -0.34 | -0.34 | closed
21 | Bulgakovo 35/10 | 2.5 | 0.19 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.54 | 1.54 | opened | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.19 | 1.73 | 24 hours | -1.54 | 0 | 1.73 | 1.54 | 1.54 | opened
22 | Spas-Ugly 35/10 | 1.6 | 0.19 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.49 | 0.49 | opened | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.19 | 0.68 | 24 hours | -0.49 | 0 | 0.68 | 0.49 | 0.49 | opened
23 | Tretyakovo 35/10 | 4 | 0.34 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.21 | 2.21 | opened | 23 | Tretyakovo 35/10 | 4 | 0 | 0.34 | 2.55 | 24 hours | -2.21 | 0 | 2.55 | 2.21 | 2.21 | opened
24 | Velisto 35/10 | 2.5 | 0.06 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.24 | 1.24 | opened | 24 | Velisto 35/10 | 2.5 | 0 | 0.06 | 1.3 | 24 hours | -1.24 | 0 | 1.3 | 1.24 | 1.24 | opened
25 | Baturino 35/10 | 1.6 | 0.09 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.76 | 0.76 | opened | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.27 | 0.85 | 24 hours | -0.58 | 0 | 0.85 | 0.58 | 0.58 | opened
26 | Pechatniki 35/10 | 2.5 | 0.6 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.86 | 2.86 | opened | 26 | Pechatniki 35/10 | 2.5 | 0 | 0.6 | 3.46 | 24 hours | -2.86 | 0 | 3.46 | 2.86 | 2.86 | opened
27 | Garistovo 35/10 | 1.6 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 27 | Garistovo 35/10 | 1.6 | 0 | 0.23 | 0.85 | 24 hours | -0.62 | 0 | 0.85 | 0.62 | 0.62 | opened
28 | Bezzaboty 35/10 | 2.5 | 0.17 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.56 | 1.56 | opened | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.17 | 1.73 | 24 hours | -1.56 | 0 | 1.73 | 1.56 | 1.56 | opened
29 | Vysokoe 35/10 | 2.5 | 0.13 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.42 | 2.42 | opened | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.13 | 2.55 | 24 hours | -2.42 | 0 | 2.55 | 2.42 | 2.42 | opened
30 | Zaytsevo 35/10 | 1.6 | 0.3 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.55 | 0.55 | opened | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.3 | 0.85 | 24 hours | -0.55 | 0 | 0.85 | 0.55 | 0.55 | opened
31 | Saveevo 35/10 | 2.5 | 0.6 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.25 | 0.25 | opened | 31 | Saveevo 35/10 | 2.5 | 0 | 0.6 | 0.85 | 24 hours | -0.25 | 0 | 0.85 | 0.25 | 0.25 | opened
32 | Gorenovo 35/10 | 1.6 | 0.16 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.39 | 2.39 | opened | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.16 | 2.55 | 24 hours | -2.39 | 0 | 2.55 | 2.39 | 2.39 | opened
33 | Shpunty 35/10 | 2.5 | 0.27 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.58 | 0.58 | opened | 33 | Shpunty 35/10 | 2.5 | 0.42 | 0.69 | 0.85 | 24 hours | -0.16 | 0 | 0.85 | 0.16 | 0.16 | opened
34 | Kadino 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 34 | Kadino 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
35 | Stegrimovo 35/10 | 2.5 | 0.21 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.68 | 2.68 | opened | 35 | Stegrimovo 35/10 | 2.5 | 0 | 0.21 | 2.89 | 24 hours | -2.68 | 0 | 2.89 | 2.68 | 2.68 | opened
36 | Zhukovo 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
37 | Mikshino 35/10 | 2.5 | 0.11 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.62 | 1.62 | opened | 37 | Mikshino 35/10 | 2.5 | 0 | 0.11 | 1.73 | 24 hours | -1.62 | 0 | 1.73 | 1.62 | 1.62 | opened
38 | Petrovichi 35/10 | 2.5 | 0.17 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.38 | 2.38 | opened | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.17 | 2.55 | 24 hours | -2.38 | 0 | 2.55 | 2.38 | 2.38 | opened
39 | Mikulichi 35/10 | 2.5 | 0.4 | 4.59 | 24 hours | 4.59 | 0 | 4.59 | 4.19 | 4.19 | opened | 39 | Mikulichi 35/10 | 2.5 | 0.07 | 0.47 | 4.59 | 24 hours | -4.12 | 0 | 4.59 | 4.12 | 4.12 | opened
40 | Nedeykovichi 35/10 | 2.5 | 0.24 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.61 | 0.61 | opened | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.24 | 0.85 | 24 hours | -0.61 | 0 | 0.85 | 0.61 | 0.61 | opened
41 | Posyolki 110/35/10 | 6.3 | 0.54 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.4 | 0.4 | opened | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.54 | 0.94 | 24 hours | -0.4 | 0 | 0.94 | 0.4 | 0.4 | opened
42 | Kuzmichi 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
43 | Maksheevo 110/10 | 6.3 | 0.38 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.17 | 2.17 | opened | 43 | Maksheevo 110/10 | 6.3 | 0 | 0.38 | 2.55 | 24 hours | -2.17 | 0 | 2.55 | 2.17 | 2.17 | opened
44 | Putkovo 35/10 | 1.8 | 0.16 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.69 | 0.69 | opened | 44 | Putkovo 35/10 | 1.8 | 0.06 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
45 | Uspenskoe 35/10 | 2.5 | 0.4 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.15 | 2.15 | opened | 45 | Uspenskoe 35/10 | 2.5 | 0 | 0.4 | 2.55 | 24 hours | -2.15 | 0 | 2.55 | 2.15 | 2.15 | opened
46 | Kalpita 35/10 | 1.6 | 0.056 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.794 | 0.794 | opened | 46 | Kalpita 35/10 | 1.6 | 0 | 0.056 | 0.85 | 24 hours | -0.794 | 0 | 0.85 | 0.794 | 0.794 | opened
47 | Kasnya 110/10 | 2.5 | 0.5 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.96 | 2.96 | opened | 47 | Kasnya 110/10 | 2.5 | 0 | 0.5 | 3.46 | 24 hours | -2.96 | 0 | 3.46 | 2.96 | 2.96 | opened
48 | Akatovo 35/10 | 1.6 | 0.94 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 1.95 | 1.95 | opened | 48 | Akatovo 35/10 | 1.6 | 1.2 | 2.14 | 2.89 | 24 hours | -0.75 | 0 | 2.89 | 0.75 | 0.75 | opened
49 | Gorki 35/10 | 1.6 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 49 | Gorki 35/10 | 1.6 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
50 | Druzhba 35/10 | 2.5 | 0.81 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.04 | 0.04 | opened | 50 | Druzhba 35/10 | 2.5 | 0 | 0.81 | 0.85 | 24 hours | -0.04 | 0 | 0.85 | 0.04 | 0.04 | opened
51 | NS-21 110/10 | 16 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened
52 | NS-22 110/35/10 | 25 | 2.76 | 2.76 | 24 hours | 2.76 | 0 | 2.76 | 0 | 0 | opened | 52 | NS-22 110/35/10 | 25 | 1.32 | 4.08 | 4.08 | 24 hours | 0 | 0 | 4.08 | 0 | 0 | opened
| Nom. capacity MV, МVА | 25 | 2.76 | 2.76 | 24 hours | 2.76 | 0 | 2.76 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 1.32 | 4.08 | 4.08 | 24 hours | 0 | 0 | 4.08 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.4 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.06 | 3.06 | opened | 53 | Shuyskoe 35/10 | 2.5 | 0.05 | 0.45 | 3.46 | 24 hours | -3.01 | 0 | 3.46 | 3.01 | 3.01 | opened
54 | Torbeevo 110/10 | 6.3 | 0.28 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.61 | 2.61 | opened | 54 | Torbeevo 110/10 | 6.3 | 0.08 | 0.36 | 2.89 | 24 hours | -2.53 | 0 | 2.89 | 2.53 | 2.53 | opened
55 | Leuzdovo 35/10 | 1 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 55 | Leuzdovo 35/10 | 1 | 0.3 | 0.42 | 0.68 | 24 hours | -0.26 | 0 | 0.68 | 0.26 | 0.26 | opened
56 | Maltsevo 35/10 | 2.5 | 0.16 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.57 | 1.57 | opened | 56 | Maltsevo 35/10 | 2.5 | 0.01 | 0.17 | 1.73 | 24 hours | -1.56 | 0 | 1.73 | 1.56 | 1.56 | opened
57 | Avrora 35/10 | 2.5 | 0.14 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.54 | 0.54 | opened | 57 | Avrora 35/10 | 2.5 | 2.77 | 2.91 | 0.68 | 24 hours | 2.23 | 0 | 0.68 | -2.23 | -2.23 | closed
58 | Bekhteevo 35/10 | 2.5 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 58 | Bekhteevo 35/10 | 2.5 | 0.07 | 0.19 | 0.68 | 24 hours | -0.49 | 0 | 0.68 | 0.49 | 0.49 | opened
59 | Sereda 35/10 | 2.5 | 0.11 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.57 | 0.57 | opened | 59 | Sereda 35/10 | 2.5 | 0 | 0.11 | 0.68 | 24 hours | -0.57 | 0 | 0.68 | 0.57 | 0.57 | opened
60 | Mikhali 35/10 | 2.5 | 0.08 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.77 | 0.77 | opened | 60 | Mikhali 35/10 | 2.5 | 0 | 0.08 | 0.85 | 24 hours | -0.77 | 0 | 0.85 | 0.77 | 0.77 | opened
61 | Mytishino 35/10 | 1.6 | 0.09 | 0 | 24 hours | 0 | 0 | 0 | -0.09 | -0.09 | closed | 61 | Mytishino 35/10 | 1.6 | 0 | 0.09 | 0 | 24 hours | 0.09 | 0 | 0 | -0.09 | -0.09 | closed
62 | Zakharyevskoe 35/10 | 1.6 | 0.017 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.833 | 0.833 | opened | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.017 | 0.85 | 24 hours | -0.833 | 0 | 0.85 | 0.833 | 0.833 | opened
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 63 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 24 hours | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
64 | Baskakovka 35/10 | 4 | 0.25 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.48 | 1.48 | opened | 64 | Baskakovka 35/10 | 4 | 0 | 0.25 | 1.73 | 24 hours | -1.48 | 0 | 1.73 | 1.48 | 1.48 | opened
65 | Ekimtsevo 110/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
Two-transformer SS | [11 empty] | 1: Two-transformer SS
65 | Smolensk 1 110/35/6 | 40+40 | 41.67 | 5.68 | 120 | 35.99 | 0 | 42 | 6.01 | 6.01 | opened | 65 | Smolensk 1 110/35/6 | 40+40 | 15.63 | 57.3 | 12.68 | 120 | 44.62 | 0 | 42 | -2.62 | -2.62 | closed
| Nom. capavity MV, МVА | 40+40 | 4.9 | 3.76 |  | 1.14 | 0 | 42 | 40.86 |  |  |  | Nom. capavity MV, МVА | 40+40 | 5.86 | 10.76 | 10.76 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 36.77 | 1.92 | 120 | 34.85 | 0 | 42 | 7.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 9.77 | 46.54 | 1.92 | 120 | 44.62 | 0 | 42 | -2.62
66 | Water intake 35/6 | 4+4 | 3.35 | 1.2 | 120 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | opened | 66 | Water intake 35/6 | 4+4 | 2.83 | 6.18 | 1.2 | 120 | 4.98 | 0 | 4.2 | -0.78 | -0.78 | closed
67 | Tychinino 35/10 | 4+4 | 0.9 | 0.91 | 120 | -0.01 | 0 | 4.2 | 4.21 | 4.21 | opened | 67 | Tychinino 35/10 | 4+4 | 0.11 | 1.01 | 0.91 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
68 | Ryaиtsevo 35/10 | 4+4 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | opened | 68 | Ryaиtsevo 35/10 | 4+4 | 2.92 | 4.79 | 0 | 120 | 4.79 | 0 | 4.2 | -0.59 | -0.59 | closed
69 | Smolensk 2 110/6 | 40+40 | 14.64 | 6.41 | 120 | 8.23 | 0 | 42 | 33.77 | 33.77 | opened | 69 | Smolensk 2 110/6 | 40+40 | 1.48 | 16.12 | 6.41 | 120 | 9.71 | 0 | 42 | 32.29 | 32.29 | opened
70 | Vostochnaya 110/6 | 25+16 | 10.14 | 0 | 120 | 10.14 | 0 | 16.8 | 6.66 | 6.66 | opened | 70 | Vostochnaya 110/6 | 25+16 | 0 | 10.14 | 0 | 120 | 10.14 | 0 | 16.8 | 6.66 | 6.66 | opened
71 | Diffuzion 110/6 | 25+25 | 14.1 | 1.06 | 120 | 13.04 | 0 | 26.25 | 13.21 | 13.21 | opened | 71 | Diffuzion 110/6 | 25+25 | 13.02 | 27.12 | 1.06 | 120 | 26.06 | 0 | 26.25 | 0.19 | 0.19 | opened
72 | Zavodskaya 110/35/10 | 16+16 | 0 | 17.07 | 120 | -17.07 | 0 | 16.8 | 33.87 | 22.45 | opened | 72 | Zavodskaya 110/35/10 | 16+16 | 12.1 | 12.1 | 7.74 | 120 | 4.36 | 0 | 16.8 | 12.44 | 12.35 | opened
| Nom. capacity MV, МVА | 16+16 | 0 | 11.42 |  | -11.42 | 0 | 16.8 | 28.22 |  |  |  | Nom. capacity MV, МVА | 16+16 | 2.09 | 2.09 | 2.09 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0 | 5.65 | 120 | -5.65 | 0 | 16.8 | 22.45 |  |  |  | Nom. capacity LV, МVА | 16+16 | 10.1 | 10.1 | 5.65 | 120 | 4.45 | 0 | 16.8 | 12.35
73 | Yasennaya 35/6 | 10+10 | 11.21 | 0 | 120 | 11.21 | 0 | 10.5 | -0.71 | -0.71 | closed | 73 | Yasennaya 35/6 | 10+10 | 1.06 | 12.27 | 0 | 120 | 12.27 | 0 | 10.5 | -1.77 | -1.77 | closed
74 | Gnezodovo 35/6 | 7,5+7,5 | 6.2 | 0.42 | 120 | 5.78 | 0 | 7.875 | 2.095 | 2.095 | opened | 74 | Gnezodovo 35/6 | 7,5+7,5 | 1.02 | 7.22 | 0.42 | 120 | 6.8 | 0 | 7.875 | 1.075 | 1.075 | opened
75 | Zapadnaya 110/6 | 25+16 | 12.99 | 0.63 | 120 | 12.36 | 0 | 16.8 | 4.44 | 4.44 | opened | 75 | Zapadnaya 110/6 | 25+16 | 7.56 | 20.55 | 0.63 | 120 | 19.92 | 0 | 16.8 | -3.12 | -3.12 | closed
76 | Katyn 2 110/35/10 | 10+16 | 4.24 | 4.24 | 120 | 0 | 0 | 10.5 | 10.5 | 8.4 | opened | 76 | Katyn 2 110/35/10 | 10+16 | 11.04 | 15.28 | 9.53 | 120 | 5.75 | 0 | 10.5 | 4.75 | 2.65 | opened
| Nom. capacity MV, МVА | 10+16 | 4.24 | 4.24 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 5.29 | 9.53 | 9.53 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.1 | 0 | 120 | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.75 | 7.85 | 0 | 120 | 7.85 | 0 | 10.5 | 2.65
77 | Katyn 1 35/10 | 4+4 | 1.63 | 0.05 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | opened | 77 | Katyn 1 35/10 | 4+4 | 2.91 | 4.54 | 0.05 | 120 | 4.49 | 0 | 4.2 | -0.29 | -0.29 | closed
78 | Lubnya 35/10 | 4+4 | 1.45 | 0.13 | 120 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | opened | 78 | Lubnya 35/10 | 4+4 | 1.98 | 3.43 | 0.13 | 120 | 3.3 | 0 | 4.2 | 0.9 | 0.9 | opened
79 | Kozino 110/35/10 | 10+10 | 9.28 | 6.28 | 120 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened | 79 | Kozino 110/35/10 | 10+10 | 6.06 | 15.34 | 10.64 | 120 | 4.7 | 0 | 10.5 | 5.8 | 5.8 | opened
| Nom. capacity MV, МVА | 10+10 | 6.27 | 6.27 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.36 | 10.63 | 10.63 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 3.01 | 0.01 | 120 | 3 | 0 | 10.5 | 7.5 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.69 | 4.7 | 0.01 | 120 | 4.69 | 0 | 10.5 | 5.81
80 | Odintsovo 35/10 | 6,3+6,3 | 4.28 | 2.15 | 120 | 2.13 | 0 | 6.615 | 4.485 | 4.485 | opened | 80 | Odintsovo 35/10 | 6,3+6,3 | 3.55 | 7.83 | 2.15 | 120 | 5.68 | 0 | 6.615 | 0.935 | 0.935 | opened
81 | Trudilovo 35/10 | 2,5+2,5 | 1.18 | 0.08 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 81 | Trudilovo 35/10 | 2,5+2,5 | 0.71 | 1.89 | 0.08 | 120 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | opened
83 | Pronino 110/35/6 | 10+10 | 5.95 | 4.46 | 120 | 1.49 | 0 | 10.5 | 9.01 | 9.01 | opened | 83 | Pronino 110/35/6 | 10+10 | 2.06 | 8.01 | 6.46 | 120 | 1.55 | 0 | 10.5 | 8.95 | 8.95 | opened
| Nom. capacity MV, МVА | 10+10 | 3.27 | 3.27 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2 | 5.27 | 5.27 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.68 | 1.19 | 120 | 1.49 | 0 | 10.5 | 9.01 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.06 | 2.74 | 1.19 | 120 | 1.55 | 0 | 10.5 | 8.95
84 | Olsha 35/10 | 2,5+2,5 | 0.72 | 0 | 120 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 84 | Olsha 35/10 | 2,5+2,5 | 1.43 | 2.15 | 0 | 120 | 2.15 | 0 | 2.625 | 0.475 | 0.475 | opened
85 | Krasny bor 35/6 | 4+4 | 2.39 | 0 | 120 | 2.39 | 0 | 4.2 | 1.81 | 1.81 | opened | 85 | Krasny bor 35/6 | 4+4 | 0.57 | 2.96 | 0 | 120 | 2.96 | 0 | 4.2 | 1.24 | 1.24 | opened
86 | Severnaya 110/35/6 | 25+25 | 24 | 9.53 | 120 | 14.47 | 0 | 26.25 | 11.78 | 11.78 | opened | 86 | Severnaya 110/35/6 | 25+25 | 6.52 | 30.52 | 13.89 | 120 | 16.63 | 0 | 26.25 | 9.62 | 9.62 | opened
| Nom. capacity MV, МVА | 25+25 | 6.94 | 6.94 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.36 | 11.3 | 11.3 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 17.06 | 2.59 | 120 | 14.47 | 0 | 26.25 | 11.78 |  |  |  | Nom. capacity LV, МVА | 25+25 | 2.16 | 19.22 | 2.59 | 120 | 16.63 | 0 | 26.25 | 9.62
87 | Peсhersk 35/6 | 4+4 | 2.54 | 0.34 | 120 | 2.2 | 0 | 4.2 | 2 | 2 | opened | 87 | Peсhersk 35/6 | 4+4 | 3.51 | 6.05 | 0.34 | 120 | 5.71 | 0 | 4.2 | -1.51 | -1.51 | closed
88 | Kolodnya 35/6 | 6,3+4 | 3.68 | 0 | 120 | 3.68 | 0 | 4.2 | 0.52 | 0.52 | opened | 88 | Kolodnya 35/6 | 6,3+4 | 0.85 | 4.53 | 0 | 120 | 4.53 | 0 | 4.2 | -0.33 | -0.33 | closed
89 | Tsentralnaya 110/10/6 | 25+25 | 18.8 | 5.79 | 120 | 13.01 | 0 | 26.25 | 13.24 | 13.24 | opened | 89 | Tsentralnaya 110/10/6 | 25+25 | 3.27 | 22.07 | 8 | 120 | 14.07 | 0 | 26.25 | 12.18 | 12.18 | opened
| Nom. capacity MV, МVА | 25+25 | 0.03 | 0.03 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 2.21 | 2.24 | 2.24 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 18.77 | 5.76 | 120 | 13.01 | 0 | 26.25 | 13.24 |  |  |  | Nom. capacity LV, МVА | 25+25 | 1.06 | 19.83 | 5.76 | 120 | 14.07 | 0 | 26.25 | 12.18
90 | Chernushki 110/10/6 | 25+25 | 21 | 2.12 | 120 | 18.88 | 0 | 26.25 | 7.37 | 7.37 | opened | 90 | Chernushki 110/10/6 | 25+25 | 12.98 | 33.98 | 2.12 | 120 | 31.86 | 0 | 26.25 | -5.61 | -5.61 | closed
| Nom. capacity MV, МVА | 25+25 | 7.29 | 0 |  | 7.29 | 0 | 26.25 | 18.96 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.92 | 13.21 | 0 |  | 13.21 | 0 | 26.25 | 13.04
| Nom. Capacity LV, МVА | 25+25 | 13.71 | 2.12 | 120 | 11.59 | 0 | 26.25 | 14.66 |  |  |  | Nom. Capacity LV, МVА | 25+25 | 7.06 | 20.77 | 2.12 | 120 | 18.65 | 0 | 26.25 | 7.6
91 | Yuzhnaya 110/35/6 | 40+40 | 46.58 | 20.63 | 120 | 25.95 | 0 | 42 | 16.05 | 16.05 | opened | 91 | Yuzhnaya 110/35/6 | 40+40 | 21.21 | 67.79 | 23.31 | 120 | 44.48 | 0 | 42 | -2.48 | -2.48 | closed
| Nom. capacity MV, МVА | 40+40 | 14.91 | 14.91 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, МVА | 40+40 | 2.68 | 17.59 | 17.59 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 31.67 | 5.72 | 120 | 25.95 | 0 | 42 | 16.05 |  |  |  | Nom. capacity LV, МVА | 40+40 | 18.52 | 50.19 | 5.72 | 120 | 44.47 | 0 | 42 | -2.47
92 | Karyernaya 110/35/6 | 16+16 | 9.15 | 3.18 | 120 | 5.97 | 0 | 16.8 | 10.83 | 10.83 | opened | 92 | Karyernaya 110/35/6 | 16+16 | 4.45 | 13.6 | 6.18 | 120 | 7.42 | 0 | 16.8 | 9.38 | 9.38 | opened
| Nom. capacity MV, МВА | 16+16 | 3.18 | 3.18 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МВА | 16+16 | 3 | 6.18 | 6.18 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 5.97 | 0 | 120 | 5.97 | 0 | 16.8 | 10.83 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.45 | 7.42 | 0 | 120 | 7.42 | 0 | 16.8 | 9.38
93 | Koshchino 35/10 | 4+4 | 0.72 | 0.11 | 120 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | opened | 93 | Koshchino 35/10 | 4+4 | 0.02 | 0.74 | 0.11 | 120 | 0.63 | 0 | 4.2 | 3.57 | 3.57 | opened
94 | Kommunar 35/10 | 2,5+2,5 | 0.46 | 0.03 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 94 | Kommunar 35/10 | 2,5+2,5 | 0 | 0.46 | 0.03 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
95 | Kasplya 110/35/10 | 10+10 | 3.38 | 3.08 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened | 95 | Kasplya 110/35/10 | 10+10 | 5.48 | 8.86 | 7.84 | 120 | 1.02 | 0 | 10.5 | 9.48 | 9.47 | opened
| Nom. capacity MV, МVА | 10+10 | 2.22 | 2.22 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.76 | 6.98 | 6.98 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.16 | 0.86 | 120 | 0.3 | 0 | 10.5 | 10.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.73 | 1.89 | 0.86 | 120 | 1.03 | 0 | 10.5 | 9.47
96 | Apolye 35/10 | 2,5+2,5 | 0.57 | 0.17 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 96 | Apolye 35/10 | 2,5+2,5 | 0.02 | 0.59 | 0.17 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened
97 | Zhukovskaya 35/10 | 4+4 | 2.04 | 0.19 | 120 | 1.85 | 0 | 4.2 | 2.35 | 2.35 | opened | 97 | Zhukovskaya 35/10 | 4+4 | 3.29 | 5.33 | 0.19 | 120 | 5.14 | 0 | 4.2 | -0.94 | -0.94 | closed
98 | Mazaltsevo 110/35/10 | 10+10 | 3.25 | 2.57 | 120 | 0.68 | 0 | 10.5 | 9.82 | 9.82 | opened | 98 | Mazaltsevo 110/35/10 | 10+10 | 6.66 | 9.91 | 8.76 | 120 | 1.15 | 0 | 10.5 | 9.35 | 9.35 | opened
| Nom. capacity MV, МVА | 10+10 | 2.31 | 2.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 6.19 | 8.5 | 8.5 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.94 | 0.26 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.47 | 1.41 | 0.26 | 120 | 1.15 | 0 | 10.5 | 9.35
99 | Petrishchevo 35/10 | 1,6+2,5 | 0.13 | 0.01 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 99 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0.13 | 0.01 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened
100 | Krasny 110/35/10 | 10+10 | 2.69 | 0.77 | 120 | 1.92 | 0 | 10.5 | 8.58 | 8.58 | opened | 100 | Krasny 110/35/10 | 10+10 | 3.37 | 6.06 | 1.94 | 120 | 4.12 | 0 | 10.5 | 6.38 | 6.38 | opened
| Nom. capacity MV, МVА | 10+10 | 0.31 | 0.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.17 | 1.48 | 1.48 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.38 | 0.46 | 120 | 1.92 | 0 | 10.5 | 8.58 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.2 | 4.58 | 0.46 | 120 | 4.12 | 0 | 10.5 | 6.38
101 | Voloelovo 35/10 | 2,5+2,5 | 0.18 | 0.01 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 101 | Voloelovo 35/10 | 2,5+2,5 | 0 | 0.18 | 0.01 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
102 | Kryukovo 35/10 | 2,5+2,5 | 0.13 | 0.26 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | opened | 102 | Kryukovo 35/10 | 2,5+2,5 | 0 | 0.13 | 0.26 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | opened
103 | Miganovo 35/10 | 2,5+2,5 | 1.11 | 0.49 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 103 | Miganovo 35/10 | 2,5+2,5 | 1.17 | 2.28 | 0.49 | 120 | 1.79 | 0 | 2.625 | 0.835 | 0.835 | opened
104 | Velizh 110/35/10 | 10+10 | 5.93 | 0.69 | 120 | 5.24 | 0 | 10.5 | 5.26 | 5.26 | opened | 104 | Velizh 110/35/10 | 10+10 | 1.64 | 7.57 | 0.79 | 120 | 6.78 | 0 | 10.5 | 3.72 | 3.72 | opened
| Nom. capacity MV, МVА | 10+10 | 0.02 | 0.02 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.1 | 0.12 | 0.12 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 5.91 | 0.67 | 120 | 5.24 | 0 | 10.5 | 5.26 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.54 | 7.45 | 0.67 | 120 | 6.78 | 0 | 10.5 | 3.72
105 | Chepli 35/10 | 2,5+2,5 | 0.32 | 0.09 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened | 105 | Chepli 35/10 | 2,5+2,5 | 0 | 0.32 | 0.09 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened
106 | Demidov 110/35/10 | 10+16 | 5.44 | 1.03 | 120 | 4.41 | 0 | 10.5 | 6.09 | 6.09 | opened | 106 | Demidov 110/35/10 | 10+16 | 3.53 | 8.97 | 1.27 | 120 | 7.7 | 0 | 10.5 | 2.8 | 2.8 | opened
| Nom. capacity MV, МVА | 10+16 | 0.85 | 0.85 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.24 | 1.09 | 1.09 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.59 | 0.18 | 120 | 4.41 | 0 | 10.5 | 6.09 |  |  |  | Nom. capacity LV, МVА | 10+16 | 3.29 | 7.88 | 0.18 | 120 | 7.7 | 0 | 10.5 | 2.8
107 | Staroe selo 35/10 | 2,5+2,5 | 0.38 | 0.17 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 107 | Staroe selo 35/10 | 2,5+2,5 | 0 | 0.38 | 0.17 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
108 | Zakrutye 35/10 | 2,5+2,5 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 108 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
109 | Zaborye 35/10 | 1,6+2,5 | 0.3 | 0.21 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 109 | Zaborye 35/10 | 1,6+2,5 | 0.02 | 0.32 | 0.21 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
110 | Mikhailovskoe 110/35/10 | 10+10 | 1.35 | 0.72 | 120 | 0.63 | 0 | 10.5 | 9.87 | 9.87 | opened | 110 | Mikhailovskoe 110/35/10 | 10+10 | 0.4 | 1.75 | 0.9 | 120 | 0.85 | 0 | 10.5 | 9.65 | 9.65 | opened
| Nom. capacity MV, МVА | 10+10 | 0.3 | 0.3 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.18 | 0.48 | 0.48 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.05 | 0.42 | 120 | 0.63 | 0 | 10.5 | 9.87 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 1.27 | 0.42 | 120 | 0.85 | 0 | 10.5 | 9.65
111 | Kardymovo 110/35/10 | 10+16 | 4.83 | 2.26 | 120 | 2.57 | 0 | 10.5 | 7.93 | 7.93 | opened | 111 | Kardymovo 110/35/10 | 10+16 | 7.72 | 12.55 | 4.43 | 120 | 8.12 | 0 | 10.5 | 2.38 | 2.38 | opened
| Nom. capacity MV, МVА | 10+16 | 1.64 | 1.64 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 2.17 | 3.81 | 3.81 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 3.19 | 0.62 | 120 | 2.57 | 0 | 10.5 | 7.93 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.55 | 8.74 | 0.62 | 120 | 8.12 | 0 | 10.5 | 2.38
112 | Sinkovo 35/6 | 4+2,5 | 0.17 | 0.16 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 112 | Sinkovo 35/6 | 4+2,5 | 0 | 0.17 | 0.16 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
113 | Kamenka 35/10 | 2,5+2,5 | 2.32 | 0.42 | 120 | 1.9 | 0 | 2.625 | 0.725 | 0.725 | opened | 113 | Kamenka 35/10 | 2,5+2,5 | 1.19 | 3.51 | 0.42 | 120 | 3.09 | 0 | 2.625 | -0.465 | -0.465 | closed
114 | Solovyovo 35/10 | 4+4 | 0.29 | 0.04 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 114 | Solovyovo 35/10 | 4+4 | 0.13 | 0.42 | 0.04 | 120 | 0.38 | 0 | 4.2 | 3.82 | 3.82 | opened
115 | Rudnya (FGC) 110/35/10 | 10+16 | 8.34 | 1.64 | 120 | 6.7 | 0 | 10.5 | 3.8 | 3.8 | opened | 115 | Rudnya (FGC) 110/35/10 | 10+16 | 2.24 | 10.58 | 2.15 | 120 | 8.43 | 0 | 10.5 | 2.07 | 2.07 | opened
| Nom. capacity MV, МVА | 10+16 | 0.71 | 0.71 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.51 | 1.22 | 1.22 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.63 | 0.93 | 120 | 6.7 | 0 | 10.5 | 3.8 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.73 | 9.36 | 0.93 | 120 | 8.43 | 0 | 10.5 | 2.07
116 | Zhichitsy 35/10 | 2,5+2,5 | 0.14 | 0.75 | 120 | -0.61 | 0 | 2.625 | 3.235 | 3.235 | opened | 116 | Zhichitsy 35/10 | 2,5+2,5 | 0 | 0.14 | 0.75 | 120 | -0.61 | 0 | 2.625 | 3.235 | 3.235 | opened
117 | Mikulino 35/10 | 6,3+6,3 | 0.72 | 1.1 | 120 | -0.38 | 0 | 6.615 | 6.995 | 6.995 | opened | 117 | Mikulino 35/10 | 6,3+6,3 | 0.18 | 0.9 | 1.1 | 120 | -0.2 | 0 | 6.615 | 6.815 | 6.815 | opened
118 | Lyubavichi 35/10 | 2,5+2,5 | 0.51 | 0.74 | 120 | -0.23 | 0 | 2.625 | 2.855 | 2.855 | opened | 118 | Lyubavichi 35/10 | 2,5+2,5 | 0.3 | 0.81 | 0.74 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
119 | Kazimirovo 35/10 | 4+4 | 0.28 | 0.02 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened | 119 | Kazimirovo 35/10 | 4+4 | 0.03 | 0.31 | 0.02 | 120 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
120 | Golynki 110/35/6 | 25+25 | 5.16 | 2.88 | 120 | 2.28 | 0 | 26.25 | 23.97 | 23.97 | opened | 120 | Golynki 110/35/6 | 25+25 | 6.24 | 11.4 | 8.58 | 120 | 2.82 | 0 | 26.25 | 23.43 | 23.43 | opened
| Nom. Capacity MV, МVА | 25+25 | 2.72 | 2.72 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, МVА | 25+25 | 5.7 | 8.42 | 8.42 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 2.44 | 0.16 | 120 | 2.28 | 0 | 26.25 | 23.97 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.54 | 2.98 | 0.16 | 120 | 2.82 | 0 | 26.25 | 23.43
121 | Belei 35/10 | 2,5+2,5 | 1.77 | 0.75 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | opened | 121 | Belei 35/10 | 2,5+2,5 | 4.49 | 6.26 | 0.75 | 120 | 5.51 | 0 | 2.625 | -2.885 | -2.885 | closed
122 | Ponizovye 110/35/10 | 6,3+6,3 | 2.35 | 1.18 | 120 | 1.17 | 0 | 6.615 | 5.445 | 5.445 | opened | 122 | Ponizovye 110/35/10 | 6,3+6,3 | 0.18 | 2.53 | 1.18 | 120 | 1.35 | 0 | 6.615 | 5.265 | 5.265 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.12 | 1.12 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 1.12 | 1.12 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.23 | 0.06 | 120 | 1.17 | 0 | 6.615 | 5.445 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.18 | 1.41 | 0.06 | 120 | 1.35 | 0 | 6.615 | 5.265
123 | Klyarinovo 35/10 | 2,5+2,5 | 0.28 | 0.19 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 123 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0.19 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
124 | Safonovo 110/6 | 15+20 | 10.24 | 0.06 | 120 | 10.18 | 0 | 15.75 | 5.57 | 5.57 | opened | 124 | Safonovo 110/6 | 15+20 | 5.94 | 16.18 | 0.06 | 120 | 16.12 | 0 | 15.75 | -0.37 | -0.37 | closed
125 | Gornaya 110/35/6 | 25+25 | 11.43 | 10.48 | 120 | 0.95 | 0 | 26.25 | 25.3 | 25.3 | opened | 125 | Gornaya 110/35/6 | 25+25 | 3.23 | 14.66 | 10.6 | 120 | 4.06 | 0 | 26.25 | 22.19 | 22.19 | opened
| Nom. capacity MV, МVА | 25+25 | 5.81 | 5.81 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0.12 | 5.93 | 5.93 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 5.62 | 4.67 | 120 | 0.95 | 0 | 26.25 | 25.3 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.11 | 8.73 | 4.67 | 120 | 4.06 | 0 | 26.25 | 22.19
126 | Water intake 35/6 | 6,3+4 | 1.67 | 0.69 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 126 | Water intake 35/6 | 6,3+4 | 0.06 | 1.73 | 0.69 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened
127 | Vadino 35/10 | 4+4 | 1.36 | 0 | 120 | 1.36 | 0 | 4.2 | 2.84 | 2.84 | opened | 127 | Vadino 35/10 | 4+4 | 1.91 | 3.27 | 0 | 120 | 3.27 | 0 | 4.2 | 0.93 | 0.93 | opened
128 | ZSSK 35/6 | 4+4 | 1.66 | 0.75 | 120 | 0.91 | 0 | 4.2 | 3.29 | 3.29 | opened | 128 | ZSSK 35/6 | 4+4 | 1.53 | 3.19 | 0.75 | 120 | 2.44 | 0 | 4.2 | 1.76 | 1.76 | opened
129 | Yanovo 35/10 | 4+6,3 | 0.48 | 0.05 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened | 129 | Yanovo 35/10 | 4+6,3 | 0 | 0.48 | 0.05 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened
130 | Kapyrevshchina 35/10 | 4+4 | 1.25 | 0.22 | 120 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | opened | 130 | Kapyrevshchina 35/10 | 4+4 | 0 | 1.25 | 0.22 | 120 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | opened
131 | Miropolye 35/10 | 2,5+2,5 | 0.6 | 0 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 131 | Miropolye 35/10 | 2,5+2,5 | 0 | 0.6 | 0 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
132 | Izdeshkovo 110/35/10 | 5,6+6,3 | 3.78 | 1.59 | 120 | 2.19 | 0 | 5.88 | 3.69 | 1.69 | opened | 132 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.51 | 5.29 | 2.87 | 120 | 2.42 | 0 | 5.88 | 3.46 | 3.46 | opened
| Nom. capacity MV, МVА | 5,6+6,3 | 1.16 | 1.16 |  | 0 | 1 | 5.88 | 4.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 1.28 | 2.44 | 2.44 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.62 | 0.43 | 120 | 2.19 | 2 | 5.88 | 1.69 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.23 | 2.85 | 0.43 | 120 | 2.42 | 0 | 5.88 | 3.46
133 | Alferovo 35/10 | 2,5+2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 133 | Alferovo 35/10 | 2,5+2,5 | 0.4 | 0.76 | 0.2 | 120 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened
134 | Kasulino 35/10 | 2,5+2,5 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 134 | Kasulino 35/10 | 2,5+2,5 | 0.52 | 0.73 | 0 | 120 | 0.73 | 0 | 2.625 | 1.895 | 1.895 | opened
135 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.32 | 0.15 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened | 135 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.35 | 0.67 | 0.15 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
136 | Glinka 110/35/10 | 10+6,3 | 1.49 | 0.34 | 120 | 1.15 | 0 | 6.615 | 5.465 | 3.465 | opened | 136 | Glinka 110/35/10 | 10+6,3 | 0.43 | 1.92 | 0.52 | 120 | 1.4 | 0 | 6.615 | 5.215 | 5.215 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.23 | 0.23 |  | 0 | 1 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.18 | 0.41 | 0.41 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.26 | 0.11 | 120 | 1.15 | 2 | 6.615 | 3.465 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.25 | 1.51 | 0.11 | 120 | 1.4 | 0 | 6.615 | 5.215
137 | Dobromino 35/10 | 2,5+2,5 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 137 | Dobromino 35/10 | 2,5+2,5 | 0.14 | 0.35 | 0 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened
138 | Bely kholm 35/10 | 1,6+1,6 | 0.03 | 0 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 138 | Bely kholm 35/10 | 1,6+1,6 | 0.04 | 0.07 | 0 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | opened
139 | Dukhovshchina 110/35/10 | 10+10 | 3.24 | 1.46 | 120 | 1.78 | 0 | 10.5 | 8.72 | 8.72 | opened | 139 | Dukhovshchina 110/35/10 | 10+10 | 0.49 | 3.73 | 1.46 | 120 | 2.27 | 0 | 10.5 | 8.23 | 8.23 | opened
| Nom. capacity MV, МVА | 10+10 | 1.2 | 1.2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 1.2 | 1.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.04 | 0.26 | 120 | 1.78 | 0 | 10.5 | 8.72 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.49 | 2.53 | 0.26 | 120 | 2.27 | 0 | 10.5 | 8.23
140 | Zimets 35/10 | 4+4 | 0.1 | 0.06 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened | 140 | Zimets 35/10 | 4+4 | 0 | 0.1 | 0.06 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened
141 | Beresnevo 35/10 | 1,6+1,6 | 0.22 | 0.01 | 120 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 141 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.22 | 0.01 | 120 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
142 | Prechistoe 110/35/10 | 6,3+6,3 | 0.57 | 0.14 | 120 | 0.43 | 0 | 6.615 | 6.185 | 6.185 | opened | 142 | Prechistoe 110/35/10 | 6,3+6,3 | 0.36 | 0.93 | 0.14 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.13 | 0 |  | 0.13 | 0 | 6.615 | 6.485 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 0.49 | 0 |  | 0.49 | 0 | 6.615 | 6.125
| Nom. capacity LV, МVА | 6,3+6,3 | 0.44 | 0.14 | 120 | 0.3 | 0 | 6.615 | 6.315 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.44 | 0.14 | 120 | 0.3 | 0 | 6.615 | 6.315
143 | Vorontsovo 35/10 | 2,5+2,5 | 0.14 | 0.07 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 143 | Vorontsovo 35/10 | 2,5+2,5 | 0 | 0.14 | 0.07 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
144 | Ozsyorny 35/10 | 6,3+6,3 | 1.08 | 0.01 | 120 | 1.07 | 0 | 6.615 | 5.545 | 5.545 | opened | 144 | Ozsyorny 35/10 | 6,3+6,3 | 0.34 | 1.42 | 0.01 | 120 | 1.41 | 0 | 6.615 | 5.205 | 5.205 | opened
145 | Igorevskaya 110/10 | 10+10 | 9.47 | 0 | 120 | 9.47 | 0 | 10.5 | 1.03 | 1.03 | opened | 145 | Igorevskaya 110/10 | 10+10 | 0.6 | 10.07 | 0 | 120 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | opened
146 | Kanyutino 110/35/10 | 5,6+6,3 | 2.74 | 1.68 | 120 | 1.06 | 0 | 5.88 | 4.82 | 4.82 | opened | 146 | Kanyutino 110/35/10 | 5,6+6,3 | 0.49 | 3.23 | 3.23 | 120 | 0 | 0 | 5.88 | 5.88 | 5.88 | opened
| Nom. capacity LV, МVА | 5,6+6,3 | 2.53 | 2.53 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.49 | 3.02 | 3.02 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.21 | 0.21 | 120 | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.21 | 0.21 | 120 | 0 | 0 | 5.88 | 5.88
147 | Bogolyubovo 35/10 | 2,5+2,5 | 0.85 | 0.25 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 147 | Bogolyubovo 35/10 | 2,5+2,5 | 0 | 0.85 | 0.25 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
148 | Kholm-Zhirki 35/10 | 2,5+4 | 3.08 | 0.4 | 120 | 2.68 | 0 | 2.625 | -0.055 | -0.055 | closed | 148 | Kholm-Zhirki 35/10 | 2,5+4 | 0.3 | 3.38 | 0.4 | 120 | 2.98 | 0 | 2.625 | -0.355 | -0.355 | closed
149 | Dorogobuzh 1 110/35/10 | 16+16 | 5.64 | 2.19 | 120 | 3.45 | 0 | 16.8 | 13.35 | 13.35 | opened | 149 | Dorogobuzh 1 110/35/10 | 16+16 | 0.55 | 6.19 | 2.19 | 120 | 4 | 0 | 16.8 | 12.8 | 12.8 | opened
| Nom. capacity MV, МVА | 16+16 | 1.67 | 1.67 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 1.67 | 1.67 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 3.97 | 0.52 | 120 | 3.45 | 0 | 16.8 | 13.35 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.55 | 4.52 | 0.52 | 120 | 4 | 0 | 16.8 | 12.8
150 | Kaskovo 35/10 | 1,6+4 | 0.72 | 0.09 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened | 150 | Kaskovo 35/10 | 1,6+4 | 0 | 0.72 | 0.09 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened
151 | Usvyatye 35/10 | 2,5+4 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 151 | Usvyatye 35/10 | 2,5+4 | 0 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened
152 | Ushakovo 35/10 | 1,6+2,5 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 152 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
153 | Artek 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 153 | Artek 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
154 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.04 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened | 154 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0 | 0.04 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened
155 | Elnya 110/35/10 | 16+16 | 5.77 | 2.36 | 120 | 3.41 | 0 | 16.8 | 13.39 | 13.39 | opened | 155 | Elnya 110/35/10 | 16+16 | 0.41 | 6.18 | 2.43 | 120 | 3.75 | 0 | 16.8 | 13.05 | 13.05 | opened
| Nom. capacity MV, МVА | 16+16 | 1.82 | 1.82 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.07 | 1.89 | 1.89 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 3.95 | 0.54 | 10 | 3.41 | 0 | 16.8 | 13.39 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.34 | 4.29 | 0.54 | 120 | 3.75 | 0 | 16.8 | 13.05
156 | Pavlovo 35/10 | 2,5+2,5 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 156 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
157 | Sharapovo 35/10 | 4+4 | 0.63 | 1 | 120 | -0.37 | 0 | 4.2 | 4.57 | 4.57 | opened | 157 | Sharapovo 35/10 | 4+4 | 0 | 0.63 | 1 | 120 | -0.37 | 0 | 4.2 | 4.57 | 4.57 | opened
158 | Korobets 35/10 | 2,5+2,5 | 0.76 | 0.17 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 158 | Korobets 35/10 | 2,5+2,5 | 0 | 0.76 | 0.17 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
159 | Baltuty 35/10 | 2,5+2,5 | 0.42 | 0 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened | 159 | Baltuty 35/10 | 2,5+2,5 | 0.07 | 0.49 | 0 | 120 | 0.49 | 0 | 2.625 | 2.135 | 2.135 | opened
160 | Lapino 110/35/10 | 5,6+5,6 | 0.89 | 0.48 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | opened | 160 | Lapino 110/35/10 | 5,6+5,6 | 0.09 | 0.98 | 0.57 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | opened
| Nom. capacity MV, МVА | 5,6+5,6 | 0.48 | 0.48 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0.09 | 0.57 | 0.57 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47
161 | Mutishche 35/10 | 1,6+2,5 | 0.17 | 0.08 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 161 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.17 | 0.08 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
162 | Suetovo 110/35/10 | 6,3+6,3 | 2.22 | 1.38 | 120 | 0.84 | 0 | 6.615 | 5.775 | 5.775 | opened | 162 | Suetovo 110/35/10 | 6,3+6,3 | 1.32 | 3.54 | 2.46 | 120 | 1.08 | 0 | 6.615 | 5.535 | 5.535 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.8 | 0.8 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1.08 | 1.88 | 1.88 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.42 | 0.58 | 120 | 0.84 | 0 | 6.615 | 5.775 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.66 | 0.58 | 120 | 1.08 | 0 | 6.615 | 5.535
163 | Pushkino 35/10 | 2,5+2,5 | 0.44 | 0.04 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 163 | Pushkino 35/10 | 2,5+2,5 | 1.08 | 1.52 | 0.04 | 120 | 1.48 | 0 | 2.625 | 1.145 | 1.145 | opened
164 | Yartsevo 1 110/10 | 40+40 | 13.94 | 5.34 | 120 | 8.6 | 0 | 42 | 33.4 | 33.4 | opened | 164 | Yartsevo 1 110/10 | 40+40 | 5.58 | 19.52 | 5.34 | 120 | 14.18 | 0 | 42 | 27.82 | 27.82 | opened
165 | Yartsevo 2 110/10 | 16+16 | 12 | 0.75 | 120 | 11.25 | 0 | 16.8 | 5.55 | 5.55 | opened | 165 | Yartsevo 2 110/10 | 16+16 | 4.23 | 16.23 | 0.75 | 120 | 15.48 | 0 | 16.8 | 1.32 | 1.32 | opened
166 | Saprykino 110/35/10 | 6,3+6,3 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | opened | 166 | Saprykino 110/35/10 | 6,3+6,3 | 0.11 | 1.08 | 0.4 | 120 | 0.68 | 0 | 6.615 | 5.935 | 5.935 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.11 | 1.08 | 0.4 | 120 | 0.68 | 0 | 6.615 | 5.935
167 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.58 | 0 | 120 | 2.58 | 0 | 6.615 | 4.035 | 4.035 | opened | 167 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.23 | 2.81 | 0 | 120 | 2.81 | 0 | 6.615 | 3.805 | 3.805 | opened
168 | Egoryevo 35/10 | 6,3+6,3 | 4.55 | 0 | 120 | 4.55 | 0 | 6.615 | 2.065 | 2.065 | opened | 168 | Egoryevo 35/10 | 6,3+6,3 | 1.3 | 5.85 | 0 | 120 | 5.85 | 0 | 6.615 | 0.765 | 0.765 | opened
169 | Shalomino 35/10 | 1,6+2,5 | 0.75 | 0.13 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 169 | Shalomino 35/10 | 1,6+2,5 | 0 | 0.75 | 0.13 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened
170 | Roslavl 110/35/6 | 25+40 | 22.72 | 1.4 | 120 | 21.32 | 0 | 26.25 | 4.93 | 4.93 | opened | 170 | Roslavl 110/35/6 | 25+40 | 3.87 | 26.59 | 1.4 | 120 | 25.19 | 0 | 26.25 | 1.06 | 1.06 | opened
| Nom. capacity MV, МVА | 25+40 | 9.05 | 1.4 |  | 7.65 | 0 | 26.25 | 18.6 |  |  |  | Nom. capacity MV, МVА | 25+40 | 1.45 | 10.5 | 1.4 |  | 9.1 | 0 | 26.25 | 17.15
| Nom. сapacity LV, МVА | 25+40 | 13.67 | 0 | 120 | 13.67 | 0 | 26.25 | 12.58 |  |  |  | Nom. сapacity LV, МVА | 25+40 | 2.42 | 16.09 | 0 | 120 | 16.09 | 0 | 26.25 | 10.16
171 | Meet processing plant 35/6 | 6,3+6,3 | 0.73 | 0 | 120 | 0.73 | 0 | 6.615 | 5.885 | 5.885 | opened | 171 | Meet processing plant 35/6 | 6,3+6,3 | 0.11 | 0.84 | 0 | 120 | 0.84 | 0 | 6.615 | 5.775 | 5.775 | opened
172 | Perenka 35/10 | 4+4 | 0.37 | 0 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened | 172 | Perenka 35/10 | 4+4 | 0 | 0.37 | 0 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened
173 | Khoroshevo 35/10 | 2,5+4 | 1.31 | 0 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened | 173 | Khoroshevo 35/10 | 2,5+4 | 0 | 1.31 | 0 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened
174 | Lipovka 35/10 | 2,5+2,5 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened | 174 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
175 | Kirilly 35/10 | 2,5+2,5 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 175 | Kirilly 35/10 | 2,5+2,5 | 1.34 | 2.18 | 0 | 120 | 2.18 | 0 | 2.625 | 0.445 | 0.445 | opened
176 | Desnogorsk 110/35/10 | 25+25 | 19.5 | 3.53 | 120 | 15.97 | 0 | 26.25 | 10.28 | 10.28 | opened | 176 | Desnogorsk 110/35/10 | 25+25 | 1.41 | 20.91 | 3.16 | 120 | 17.75 | 0 | 26.25 | 8.5 | 8.5 | opened
| Nom. capacity MV, МVА | 25+25 | 3.53 | 3.53 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 1.41 | 4.94 | 3.16 |  | 1.78 | 0 | 26.25 | 24.47
| Nom. capacidty LV, МVА | 25+25 | 15.97 | 0 | 120 | 15.97 | 0 | 26.25 | 10.28 |  |  |  | Nom. capacidty LV, МVА | 25+25 | 0 | 15.97 | 0 | 120 | 15.97 | 0 | 26.25 | 10.28
177 | Ekimovichi 35/10 | 4+4 | 2.61 | 0.24 | 120 | 2.37 | 0 | 4.2 | 1.83 | 1.83 | opened | 177 | Ekimovichi 35/10 | 4+4 | 0 | 2.61 | 0.24 | 120 | 2.37 | 0 | 4.2 | 1.83 | 1.83 | opened
178 | Ivanovskaya 35/10 | 2,5+2,5 | 0.45 | 0.07 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened | 178 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.45 | 0.07 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
179 | Kokhany 35/10 | 1,6+1,6 | 0.4 | 0.09 | 120 | 0.31 | 0 | 1.68 | 1.37 | 1.37 | opened | 179 | Kokhany 35/10 | 1,6+1,6 | 0.09 | 0.49 | 0.09 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened
180 | Koski 35/10 | 4+4 | 0.92 | 0 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened | 180 | Koski 35/10 | 4+4 | 0 | 0.92 | 0 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened
181 | Industrialnaya 110/35/6 | 16+16 | 4.85 | 0.51 | 120 | 4.34 | 0 | 16.8 | 12.46 | 4.565 | opened | 181 | Industrialnaya 110/35/6 | 16+16 | 1.42 | 6.27 | 0.51 | 120 | 5.76 | 0 | 16.8 | 11.04 | 5.475 | opened
| Nom. capacity MV, МVА | 16,3+5,3 | 0.51 | 0.51 |  | 0 | 1 | 5.565 | 4.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0 | 0.51 | 0.51 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 4.34 | 0 | 120 | 4.34 | 2 | 11.235 | 4.895 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 1.42 | 5.76 | 0 | 120 | 5.76 | 0 | 11.235 | 5.475
182 | Astapkovichi 35/10 | 2,5+2,5 | 0.74 | 0 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened | 182 | Astapkovichi 35/10 | 2,5+2,5 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened
183 | Barsuki 110/35/10 | 6,3+6,3 | 0.87 | 0.55 | 120 | 0.32 | 0 | 6.615 | 6.295 | 6.295 | opened | 183 | Barsuki 110/35/10 | 6,3+6,3 | 0.28 | 1.15 | 0.83 | 120 | 0.32 | 0 | 6.615 | 6.295 | 6.295 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.55 | 0.55 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.28 | 0.83 | 0.83 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.32 | 0 | 120 | 0.32 | 0 | 6.615 | 6.295 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.32 | 0 | 120 | 0.32 | 0 | 6.615 | 6.295
184 | Bogdanovo 35/10 | 4+4 | 0.41 | 0 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 184 | Bogdanovo 35/10 | 4+4 | 0.28 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 | 3.51 | opened
185 | Prigorye 110/35/10 | 10+2,5 | 1.08 | 0.53 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened | 185 | Prigorye 110/35/10 | 10+2,5 | 0.12 | 1.2 | 0.65 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened
| Nom. capacity MV, МVА | 10+2,5 | 0.53 | 0.53 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0.12 | 0.65 | 0.65 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.55 | 0 | 120 | 0.55 | 0 | 2.625 | 2.075 |  |  |  | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0.55 | 0 | 120 | 0.55 | 0 | 2.625 | 2.075
186 | Bekhovo 35/10 | 2,5+2,5 | 0.34 | 0 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened | 186 | Bekhovo 35/10 | 2,5+2,5 | 0.12 | 0.46 | 0 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
187 | Pochinok 110/35/10 | 10+16 | 7.46 | 2.81 | 120 | 4.65 | 0 | 10.5 | 5.85 | 5.85 | opened | 187 | Pochinok 110/35/10 | 10+16 | 2.43 | 9.89 | 3.89 | 120 | 6 | 0 | 10.5 | 4.5 | 4.5 | opened
| Nom. capacidty MV, МVА | 10+16 | 2.73 | 2.73 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacidty MV, МVА | 10+16 | 1.08 | 3.81 | 3.81 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.73 | 0.08 | 120 | 4.65 | 0 | 10.5 | 5.85 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.35 | 6.08 | 0.08 | 120 | 6 | 0 | 10.5 | 4.5
188 | Divinskaya 35/10 | 4+4 | 1.41 | 0.17 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened | 188 | Divinskaya 35/10 | 4+4 | 0.04 | 1.45 | 0.17 | 120 | 1.28 | 0 | 4.2 | 2.92 | 2.92 | opened
189 | Shatalovo 35/10 | 2,5+2,5 | 1.95 | 0 | 120 | 1.95 | 0 | 2.625 | 0.675 | 0.675 | opened | 189 | Shatalovo 35/10 | 2,5+2,5 | 0 | 1.95 | 0 | 120 | 1.95 | 0 | 2.625 | 0.675 | 0.675 | opened
190 | Panskaya 35/10 | 6,3+6,3 | 0.95 | 0 | 120 | 0.95 | 0 | 6.615 | 5.665 | 5.665 | opened | 190 | Panskaya 35/10 | 6,3+6,3 | 1.04 | 1.99 | 0 | 120 | 1.99 | 0 | 6.615 | 4.625 | 4.625 | opened
191 | Stodolishche 110/35/10 | 6,3+6,3 | 2.98 | 1.65 | 120 | 1.33 | 0 | 6.615 | 5.285 | 5.285 | opened | 191 | Stodolishche 110/35/10 | 6,3+6,3 | 3.63 | 6.61 | 2.65 | 120 | 3.96 | 0 | 6.615 | 2.655 | 2.655 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.2 | 1.2 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1 | 2.2 | 2.2 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.78 | 0.45 | 120 | 1.33 | 0 | 6.615 | 5.285 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.63 | 4.41 | 0.45 | 120 | 3.96 | 0 | 6.615 | 2.655
192 | Belik 35/10 | 2,5+2,5 | 0.14 | 0.33 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 192 | Belik 35/10 | 2,5+2,5 | 0 | 0.14 | 0.33 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened
193 | Pervomayskaya 35/10 | 4+4 | 1.24 | 0 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened | 193 | Pervomayskaya 35/10 | 4+4 | 0.73 | 1.97 | 0 | 120 | 1.97 | 0 | 4.2 | 2.23 | 2.23 | opened
194 | Vaskovo 110/35/10 | 6,3+6,3 | 2.53 | 2.07 | 120 | 0.46 | 0 | 6.615 | 6.155 | 6.155 | opened | 194 | Vaskovo 110/35/10 | 6,3+6,3 | 0.28 | 2.81 | 2.56 | 120 | 0.25 | 0 | 6.615 | 6.365 | 6.365 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 2.07 | 2.07 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.28 | 2.35 | 2.35 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.46 | 0.21 | 120 | 0.25 | 0 | 6.615 | 6.365 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.46 | 0.21 | 120 | 0.25 | 0 | 6.615 | 6.365
195 | Strigino 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 195 | Strigino 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
196 | Komintern 35/10 | 2,5+2,5 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened | 196 | Komintern 35/10 | 2,5+2,5 | 0 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
197 | Monastyrshchina 110/35/10 | 10+10 | 5.86 | 2.31 | 120 | 3.55 | 0 | 10.5 | 6.95 | 6.95 | opened | 197 | Monastyrshchina 110/35/10 | 10+10 | 0.13 | 5.99 | 2.31 | 120 | 3.68 | 0 | 10.5 | 6.82 | 6.82 | opened
| Nom. Capacity MV, МVА | 10+10 | 2.31 | 2.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. Capacity MV, МVА | 10+10 | 0 | 2.31 | 2.31 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 3.55 | 0 | 120 | 3.55 | 0 | 10.5 | 6.95 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.13 | 3.68 | 0 | 120 | 3.68 | 0 | 10.5 | 6.82
198 | N.Mikhailov 35/10 | 4+4 | 0.96 | 0 | 120 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | opened | 198 | N.Mikhailov 35/10 | 4+4 | 0 | 0.96 | 0 | 120 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | opened
199 | Tatarsk 35/10 | 3,2+4 | 1.14 | 0 | 120 | 1.14 | 0 | 3.36 | 2.22 | 2.22 | opened | 199 | Tatarsk 35/10 | 3,2+4 | 0 | 1.14 | 0 | 120 | 1.14 | 0 | 3.36 | 2.22 | 2.22 | opened
200 | Turki 35/10 | 1,6+1,6 | 0.2 | 0 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 200 | Turki 35/10 | 1,6+1,6 | 0 | 0.2 | 0 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
201 | Sozh 35/10 | 4+4 | 0.35 | 0 | 120 | 0.35 | 0 | 4.2 | 3.85 | 3.85 | opened | 201 | Sozh 35/10 | 4+4 | 0 | 0.35 | 0 | 120 | 0.35 | 0 | 4.2 | 3.85 | 3.85 | opened
202 | Khislavichi 110/35/10 | 16+16 | 3.43 | 1.51 | 120 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened | 202 | Khislavichi 110/35/10 | 16+16 | 0.49 | 3.92 | 1.71 | 120 | 2.21 | 0 | 16.8 | 14.59 | 14.59 | opened
| Nom. capacity MV, МVА | 16+16 | 1.33 | 1.33 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.2 | 1.53 | 1.53 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.1 | 0.18 | 120 | 1.92 | 0 | 16.8 | 14.88 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.29 | 2.39 | 0.18 | 120 | 2.21 | 0 | 16.8 | 14.59
203 | Gorodishche 35/10 | 1,8+2,5 | 0.99 | 0 | 120 | 0.99 | 0 | 1.89 | 0.9 | 0.9 | opened | 203 | Gorodishche 35/10 | 1,8+2,5 | 0 | 0.99 | 0 | 120 | 0.99 | 0 | 1.89 | 0.9 | 0.9 | opened
204 | Komarovka 35/10 | 4+4 | 0.31 | 0.02 | 120 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened | 204 | Komarovka 35/10 | 4+4 | 0 | 0.31 | 0.02 | 120 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
205 | Cherepovo 35/10 | 2,5+2,5 | 0.75 | 0 | 120 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened | 205 | Cherepovo 35/10 | 2,5+2,5 | 0.05 | 0.8 | 0 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
206 | Studenets 35/10 | 1,6+2,5 | 0.37 | 0.01 | 120 | 0.36 | 0 | 1.68 | 1.32 | 1.32 | opened | 206 | Studenets 35/10 | 1,6+2,5 | 0.15 | 0.52 | 0.01 | 120 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened
207 | Shumyachi 110/35/10 | 10+10 | 5.41 | 3.46 | 120 | 1.95 | 0 | 10.5 | 8.55 | 8.55 | opened | 207 | Shumyachi 110/35/10 | 10+10 | 1.52 | 6.93 | 4.4 | 120 | 2.53 | 0 | 10.5 | 7.97 | 7.97 | opened
| Nom. capacity MV, МVА | 10+10 | 2.82 | 2.82 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.94 | 3.76 | 3.76 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.59 | 0.64 | 120 | 1.95 | 0 | 10.5 | 8.55 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.58 | 3.17 | 0.64 | 120 | 2.53 | 0 | 10.5 | 7.97
208 | Ershichi 110/35/10 | 10+10 | 2.17 | 0.56 | 120 | 1.61 | 0 | 10.5 | 8.89 | 8.89 | opened | 208 | Ershichi 110/35/10 | 10+10 | 0.65 | 2.82 | 0.69 | 120 | 2.13 | 0 | 10.5 | 8.37 | 8.37 | opened
| Nom. capacity MV, МVА | 10+10 | 0.34 | 0.34 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 0.47 | 0.47 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.83 | 0.22 | 120 | 1.61 | 0 | 10.5 | 8.89 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.52 | 2.35 | 0.22 | 120 | 2.13 | 0 | 10.5 | 8.37
209 | Rukhan 35/10 | 2,5+2,5 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened | 209 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
210 | Vyazma 1 110/35/10 | 40+40 | 34.49 | 11.83 | 120 | 22.66 | 0 | 42 | 19.34 | 19.34 | opened | 210 | Vyazma 1 110/35/10 | 40+40 | 20.14 | 54.63 | 15.76 | 120 | 38.87 | 0 | 42 | 3.13 | 3.13 | opened
| Nom. capacity MV, МVА | 40+40 | 22.28 | 11.27 | 121 | 11.01 | 0 | 42 | 30.99 |  |  |  | Nom. capacity MV, МVА | 40+40 | 10.88 | 33.16 | 15.2 |  | 17.96 | 0 | 42 | 24.04
| Nom. capacity LV, МVА | 40+40 | 12.21 | 0.56 | 122 | 11.65 | 0 | 42 | 30.35 |  |  |  | Nom. capacity LV, МVА | 40+40 | 9.26 | 21.47 | 0.56 | 120 | 20.91 | 0 | 42 | 21.09
211 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2 | 0 | 120 | 2 | 0 | 6.615 | 4.615 | 4.615 | opened | 211 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 3.07 | 5.07 | 0 | 120 | 5.07 | 0 | 6.615 | 1.545 | 1.545 | opened
212 | Khmelita 35/10 | 1,6+2,5 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened | 212 | Khmelita 35/10 | 1,6+2,5 | 0.03 | 0.41 | 0.11 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
213 | Isakovo 35/10 | 2,5+4 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 213 | Isakovo 35/10 | 2,5+4 | 0 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
214 | Rizskoe 35/10 | 2,5+2,5 | 0.67 | 0.01 | 120 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | opened | 214 | Rizskoe 35/10 | 2,5+2,5 | 0.22 | 0.89 | 0.01 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
215 | Beryozka 35/10 | 4+4 | 0.61 | 0 | 120 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | opened | 215 | Beryozka 35/10 | 4+4 | 0.25 | 0.86 | 0 | 120 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
216 | Shimanovo 35/10 | 1,8+4 | 0.51 | 0.32 | 120 | 0.19 | 0 | 1.89 | 1.7 | 1.7 | opened | 216 | Shimanovo 35/10 | 1,8+4 | 0.08 | 0.59 | 0.32 | 120 | 0.27 | 0 | 1.89 | 1.62 | 1.62 | opened
217 | Kaydakovo 35/10 | 4+4 | 1.17 | 0.2 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | opened | 217 | Kaydakovo 35/10 | 4+4 | 0.13 | 1.3 | 0.2 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened
218 | Flour mill 35/10 | 10+10 | 6.76 | 0.13 | 120 | 6.63 | 0 | 10.5 | 3.87 | 3.87 | opened | 218 | Flour mill 35/10 | 10+10 | 6.83 | 13.59 | 0.13 | 120 | 13.46 | 0 | 10.5 | -2.96 | -2.96 | closed
219 | Kikino 35/10 | 2,5+2,5 | 0.42 | 0.41 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 219 | Kikino 35/10 | 2,5+2,5 | 0.21 | 0.63 | 0.41 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
220 | Vyazma 2 110/10 | 16+16 | 13.39 | 0 | 120 | 13.39 | 0 | 16.8 | 3.41 | 3.41 | opened | 220 | Vyazma 2 110/10 | 16+16 | 4.04 | 17.43 | 0 | 120 | 17.43 | 0 | 16.8 | -0.63 | -0.63 | closed
221 | Tumanovo 110/35/10 | 6,3+6,3 | 2.32 | 1.16 | 120 | 1.16 | 0 | 6.615 | 5.455 | 5.455 | opened | 221 | Tumanovo 110/35/10 | 6,3+6,3 | 0.06 | 2.38 | 1.16 | 120 | 1.22 | 0 | 6.615 | 5.395 | 5.395 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.82 | 0.82 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.82 | 0.82 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.5 | 0.34 | 120 | 1.16 | 0 | 6.615 | 5.455 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.06 | 1.56 | 0.34 | 120 | 1.22 | 0 | 6.615 | 5.395
222 | Rossiya 110/35/10 | 10+16 | 2.46 | 1.7 | 120 | 0.76 | 0 | 10.5 | 9.74 | 9.74 | opened | 222 | Rossiya 110/35/10 | 10+16 | 0.6 | 3.06 | 2.02 | 120 | 1.04 | 0 | 10.5 | 9.46 | 9.46 | opened
| Nom. capacity MV, МVА | 10+16 | 1.38 | 1.38 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.32 | 1.7 | 1.7 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.08 | 0.32 | 120 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.28 | 1.36 | 0.32 | 120 | 1.04 | 0 | 10.5 | 9.46
223 | Semlevo 35/10 | 2,5+4 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 223 | Semlevo 35/10 | 2,5+4 | 0.06 | 0.9 | 0 | 120 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | opened
224 | Artyomovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 224 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
225 | Gagarin 110/35/10 | 25+25 | 25 | 4.78 | 120 | 20.22 | 0 | 26.25 | 6.03 | 6.03 | opened | 225 | Gagarin 110/35/10 | 25+25 | 10.77 | 35.77 | 6.82 | 120 | 28.95 | 0 | 26.25 | -2.7 | -2.7 | closed
| Nom. capacity MV, МVА | 25+25 | 4.95 | 3.06 |  | 1.89 | 0 | 26.25 | 24.36 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.27 | 9.22 | 5.1 |  | 4.12 | 0 | 26.25 | 22.13
| Nom. capacity LV, МVА | 25+25 | 20.05 | 1.72 | 120 | 18.33 | 0 | 26.25 | 7.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 6.5 | 26.55 | 1.72 | 120 | 24.83 | 0 | 26.25 | 1.42
226 | Rodomanovo 35/10 | 4+4 | 1.02 | 1.18 | 120 | -0.16 | 0 | 4.2 | 4.36 | 4.36 | opened | 226 | Rodomanovo 35/10 | 4+4 | 0.9 | 1.92 | 1.18 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
227 | Klushino 35/10 | 4+4 | 0.82 | 0.57 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 227 | Klushino 35/10 | 4+4 | 0.69 | 1.51 | 0.57 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | opened
228 | Ivino 35/10 | 1,6+1,6 | 0.14 | 0 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 228 | Ivino 35/10 | 1,6+1,6 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
229 | Karmanovo 35/10 | 4+4 | 3.29 | 0.21 | 120 | 3.08 | 0 | 4.2 | 1.12 | 1.12 | opened | 229 | Karmanovo 35/10 | 4+4 | 1.32 | 4.61 | 0.21 | 120 | 4.4 | 0 | 4.2 | -0.2 | -0.2 | closed
230 | Sverchkovo 35/10 | 2,5+2,5 | 1.46 | 0.75 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened | 230 | Sverchkovo 35/10 | 2,5+2,5 | 0.13 | 1.59 | 0.75 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
231 | Lesnaya 35/10 | 4+4 | 1.01 | 0 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened | 231 | Lesnaya 35/10 | 4+4 | 0 | 1.01 | 0 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened
232 | Tesovo 35/10 | 1,6+2,5 | 0.49 | 0.48 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 232 | Tesovo 35/10 | 1,6+2,5 | 0.03 | 0.52 | 0.48 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened
233 | Svetotekhnika 110/10 | 16+16 | 4.05 | 0.97 | 120 | 3.08 | 0 | 16.8 | 13.72 | 13.72 | opened | 233 | Svetotekhnika 110/10 | 16+16 | 3.8 | 7.85 | 0.97 | 120 | 6.88 | 0 | 16.8 | 9.92 | 9.92 | opened
234 | Mishino 110/35/10 | 10+10 | 2.83 | 2.2 | 120 | 0.63 | 0 | 10.5 | 9.87 | 9.87 | opened | 234 | Mishino 110/35/10 | 10+10 | 1.14 | 3.97 | 3.1 | 120 | 0.87 | 0 | 10.5 | 9.63 | 9.63 | opened
| Nom. capacity MV, МVА | 10+10 | 1.66 | 1.66 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.8 | 2.46 | 2.46 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.17 | 0.64 | 120 | 0.53 | 0 | 10.5 | 9.97 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.34 | 1.51 | 0.64 | 120 | 0.87 | 0 | 10.5 | 9.63
235 | Nikolskoe 35/10 | 6,3+6,3 | 1.58 | 0.59 | 120 | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened | 235 | Nikolskoe 35/10 | 6,3+6,3 | 0.67 | 2.25 | 0.59 | 120 | 1.66 | 0 | 6.615 | 4.955 | 4.955 | opened
236 | Bekrino 35/10 | 2,5+2,5 | 0.53 | 0.09 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened | 236 | Bekrino 35/10 | 2,5+2,5 | 0 | 0.53 | 0.09 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened
237 | Trubnaya 110/10 | 25+25 | 5.22 | 1.57 | 120 | 3.65 | 0 | 26.25 | 22.6 | 22.6 | opened | 237 | Trubnaya 110/10 | 25+25 | 4.91 | 10.13 | 1.57 | 120 | 8.56 | 0 | 26.25 | 17.69 | 17.69 | opened
238 | Temkino 110/35/10 | 10+10 | 3.23 | 0.71 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | opened | 238 | Temkino 110/35/10 | 10+10 | 2.65 | 5.88 | 1.89 | 120 | 3.99 | 0 | 10.5 | 6.51 | 6.51 | opened
| Nom. capacity MV, МVА | 10+10 | 0.46 | 0.46 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.18 | 1.64 | 1.64 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.77 | 0.25 | 120 | 2.52 | 0 | 10.5 | 7.98 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.47 | 4.24 | 0.25 | 120 | 3.99 | 0 | 10.5 | 6.51
239 | Narytka 35/10 | 2,5+2,5 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 239 | Narytka 35/10 | 2,5+2,5 | 0 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
240 | Novodugino 110/35/10 | 10+10 | 4.31 | 2.03 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.22 | opened | 240 | Novodugino 110/35/10 | 10+10 | 0.61 | 4.92 | 2.5 | 120 | 2.42 | 0 | 10.5 | 8.08 | 8.08 | opened
| Nom. capacity MV, МVА | 10+10 | 1.55 | 1.55 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.47 | 2.02 | 2.02 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.76 | 0.48 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.14 | 2.9 | 0.48 | 120 | 2.42 | 0 | 10.5 | 8.08
241 | Vysokoe 35/10 | 1,6+4 | 0.82 | 0.42 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened | 241 | Vysokoe 35/10 | 1,6+4 | 0.39 | 1.21 | 0.42 | 120 | 0.79 | 0 | 1.68 | 0.89 | 0.89 | opened
242 | Khotkovo 35/10 | 4+4 | 0.74 | 0.26 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened | 242 | Khotkovo 35/10 | 4+4 | 0 | 0.74 | 0.26 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened
243 | Dneprovsk 110/35/10 | 10+10 | 2.89 | 2.77 | 120 | 0.12 | 0 | 10.5 | 10.38 | 10.38 | opened | 243 | Dneprovsk 110/35/10 | 10+10 | 0.77 | 3.66 | 3.54 | 120 | 0.12 | 0 | 10.5 | 10.38 | 10.38 | opened
| Nom. capacity MV, МVА | 10+10 | 2.61 | 2.61 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.77 | 3.38 | 3.38 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.28 | 0.16 | 120 | 0.12 | 0 | 10.5 | 10.38 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 0.28 | 0.16 | 120 | 0.12 | 0 | 10.5 | 10.38
244 | Lipetsy 35/10 | 2,5+2,5 | 0.36 | 0.75 | 120 | -0.39 | 0 | 2.625 | 3.015 | 3.015 | opened | 244 | Lipetsy 35/10 | 2,5+2,5 | 0.1 | 0.46 | 0.75 | 120 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | opened
245 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.43 | 0.7 | 120 | -0.27 | 0 | 1.68 | 1.95 | 1.95 | opened | 245 | Nakhimovskaya 35/10 | 1,6+1,6 | 0 | 0.43 | 0.7 | 120 | -0.27 | 0 | 1.68 | 1.95 | 1.95 | opened
246 | Sychevka 110/35/10 | 16+25 | 8.15 | 1.47 | 120 | 6.68 | 0 | 16.8 | 10.12 | 10.12 | opened | 246 | Sychevka 110/35/10 | 16+25 | 4.44 | 12.59 | 1.78 | 120 | 10.81 | 0 | 16.8 | 5.99 | 5.99 | opened
| Nom. capacity MV, МVА | 16+25 | 3.11 | 0.7 |  | 2.41 | 0 | 16.8 | 14.39 |  |  |  | Nom. capacity MV, МVА | 16+25 | 3.22 | 6.33 | 1.01 |  | 5.32 | 0 | 16.8 | 11.48
| Nom. capacfity LV, МVА | 16+25 | 5.04 | 0.77 | 120 | 4.27 | 0 | 16.8 | 12.53 |  |  |  | Nom. capacfity LV, МVА | 16+25 | 1.22 | 6.26 | 0.77 | 120 | 5.49 | 0 | 16.8 | 11.31
247 | Sutormino 35/10 | 1,8+4 | 0.22 | 0.06 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened | 247 | Sutormino 35/10 | 1,8+4 | 0 | 0.22 | 0.06 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened
248 | Karavaevo 35/10 | 4+4 | 0.77 | 0.29 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened | 248 | Karavaevo 35/10 | 4+4 | 0.38 | 1.15 | 0.29 | 120 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
249 | Lukino 35/10 | 4+1,6 | 0.01 | 0.51 | 120 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened | 249 | Lukino 35/10 | 4+1,6 | 0 | 0.01 | 0.51 | 120 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened
250 | Subbotniki 110/10 | 6,3+6,3 | 0.77 | 0 | 120 | 0.77 | 0 | 6.615 | 5.845 | 5.845 | opened | 250 | Subbotniki 110/10 | 6,3+6,3 | 0.37 | 1.14 | 0 | 120 | 1.14 | 0 | 6.615 | 5.475 | 5.475 | opened
251 | Ugra 110/10 | 6,3+6,3 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675 | 3.675 | opened | 251 | Ugra 110/10 | 6,3+6,3 | 0.13 | 3.07 | 0 | 120 | 3.07 | 0 | 6.615 | 3.545 | 3.545 | opened
252 | Znamenka 110/35/10 | 10+10 | 2.13 | 1.19 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.56 | opened | 252 | Znamenka 110/35/10 | 10+10 | 2.72 | 4.85 | 1.32 | 120 | 3.53 | 0 | 10.5 | 6.97 | 6.97 | opened
| Nom. capacity MV, МVА | 10+10 | 1.16 | 1.16 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 1.29 | 1.29 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.97 | 0.03 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.59 | 3.56 | 0.03 | 120 | 3.53 | 0 | 10.5 | 6.97
253 | Losmino 35/10 | 2,5+2,5 | 0.58 | 0.4 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 253 | Losmino 35/10 | 2,5+2,5 | 0 | 0.58 | 0.4 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
254 | Vskhody 110/35/10 | 6,3+6,3 | 1.42 | 0.82 | 120 | 0.6 | 0 | 6.615 | 6.015 | 6.015 | opened | 254 | Vskhody 110/35/10 | 6,3+6,3 | 0.11 | 1.53 | 0.82 | 120 | 0.71 | 0 | 6.615 | 5.905 | 5.905 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.81 | 0.81 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.81 | 0.81 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.61 | 0.01 | 120 | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.11 | 0.72 | 0.01 | 120 | 0.71 | 0 | 6.615 | 5.905
| Total: | 3150.6 | 670.46 | [8 empty] | 2: Total:; 3: 3150.6; 4: 254.66; 5: 925.12
| deficit | [8 empty] | -1.195 |  | 2: deficit; Мin. 12: -33.265
| proficit | [8 empty] | 1033.302 |  | 2: proficit; Мin. 12: 822.062

## Тамбовэнерго
[9 empty] | table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS 110 kv | [11 empty] | 1: SS 110 kv
1 | Tambovskaya No.2 | 40 + 25 | 18.55 |  |  | 18.55 | 0 | 26.25 | 7.7 | 7.7 | opened | 1 | Tambovskaya No.2 | 40 + 25 | 0 | 18.55 |  |  | 18.55 | 0 | 26.25 | 7.7 | 7.7 | opened
2 | Tambovskaya No.3 | 2*25 | 13.26 |  |  | 13.26 | 0 | 26.25 | 12.99 | 12.99 | opened | 2 | Tambovskaya No.3 | 2*25 | 0 | 13.26 |  |  | 13.26 | 0 | 26.25 | 12.99 | 12.99 | opened
3 | Tambovskaya No.5 | 16 + 12,5 | 13.77 |  |  | 13.77 | 0 | 13.125 | -0.645 | -0.645 | closed | 3 | Tambovskaya No.5 | 16 + 12,5 | 1.75 | 15.52 |  |  | 15.52 | 0 | 13.125 | -2.395 | -2.395 | closed
4 | Tambovskaya No.7 | 2*25 | 18.76 |  |  | 18.76 | 0 | 26.25 | 7.49 | 7.49 | opened | 4 | Tambovskaya No.7 | 2*25 | 0 | 18.76 |  |  | 18.76 | 0 | 26.25 | 7.49 | 7.49 | opened
5 | Pigment | 2*63 | 30.51 | 27.68 | 80 | 2.83 | 0 | 66.15 | 63.32 | 63.32 | opened | 5 | Pigment | 2*63 | 0 | 30.51 | 27.68 | 80 | 2.83 | 0 | 66.15 | 63.32 | 63.32 | opened
6 | Tambovskaya No.8 | 2*16 | 11.6 |  |  | 11.6 | 0 | 16.8 | 5.2 | 5.2 | opened | 6 | Tambovskaya No.8 | 2*16 | 0.39 | 11.99 |  |  | 11.99 | 0 | 16.8 | 4.81 | 4.81 | opened
7 | SS 110/35/6 Malinovskaya | 2*40 | 11.5 | 4.75 | 120 | 6.75 | 0 | 42 | 35.25 | 35.25 | opened | 7 | SS 110/35/6 Malinovskaya | 2*40 | 0 | 11.5 | 4.75 | 120 | 6.75 | 0 | 42 | 35.25 | 35.25 | opened
8 | SS 110/35/10 Tambovskaya No.6 | 2*10 | 8.74 | 1.25 | 120 | 7.49 | 0 | 10.5 | 3.01 | 3.01 | opened | 8 | SS 110/35/10 Tambovskaya No.6 | 2*10 | 2.1 | 10.84 | 1.25 | 120 | 9.59 | 0 | 10.5 | 0.91 | 0.91 | opened
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 3.18 | 1.62 | 120 | 1.56 | 0 | 6.615 | 5.055 | 5.055 | opened | 9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5.56 | 8.74 | 7.18 | 120 | 1.56 | 0 | 6.615 | 5.055 | 5.055 | opened
10 | SS 110/35/10 Komsomolskaya | 2*10 | 7.24 | 4 | 80 | 3.24 | 0 | 10.5 | 7.26 | 7.26 | opened | 10 | SS 110/35/10 Komsomolskaya | 2*10 | 0.6 | 7.84 | 4 | 80 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened
11 | SS 110/10 М.Talinskaya | 10 | 0.52 | 0.52 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 11 | SS 110/10 М.Talinskaya | 10 | 5.56 | 6.08 | 0.52 | 24 hours | 5.56 | 0 | 10.5 | 4.94 | 4.94 | opened
12 | SS 110/35/10 Promyshlennaya | 2*40 | 23.04 | 10.2 | 120 | 12.84 | 0 | 42 | 29.16 | 29.16 | opened | 12 | SS 110/35/10 Promyshlennaya | 2*40 | 0.26 | 23.3 | 10.2 | 120 | 13.1 | 0 | 42 | 28.9 | 28.9 | opened
13 | SS 110/35/10 Arzhenskaya | 2*10 | 3.92 | 3.92 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 13 | SS 110/35/10 Arzhenskaya | 2*10 | 0 | 3.92 | 3.92 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.56 |  |  | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 14 | SS 110/10 Teleshovskaya | 2*2,5 | 0 | 0.56 |  |  | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened
15 | SS 110/6 Oktyabrskaya | 2*25 | 6.11 |  |  | 6.11 | 0 | 26.25 | 20.14 | 20.14 | opened | 15 | SS 110/6 Oktyabrskaya | 2*25 | 0.28 | 6.39 |  |  | 6.39 | 0 | 26.25 | 19.86 | 19.86 | opened
16 | SS 110/10 Spasskaya | 2*6,3 | 1.97 |  |  | 1.97 | 0 | 6.615 | 4.645 | 4.645 | opened | 16 | SS 110/10 Spasskaya | 2*6,3 | 0 | 1.97 |  |  | 1.97 | 0 | 6.615 | 4.645 | 4.645 | opened
17 | SS 110/35/10 Kuzminskaya | 16+10 | 5.15 | 5.02 | 45 | 0.13 | 0 | 10.5 | 10.37 | 10.37 | opened | 17 | SS 110/35/10 Kuzminskaya | 16+10 | 0 | 5.15 | 5.02 | 45 | 0.13 | 0 | 10.5 | 10.37 | 10.37 | opened
18 | SS 110/35/10 Sampurskaya | 10+16 | 5.67 | 4.33 | 80 | 1.34 | 0 | 10.5 | 9.16 | 9.16 | opened | 18 | SS 110/35/10 Sampurskaya | 10+16 | 0 | 5.67 | 4.33 | 80 | 1.34 | 0 | 10.5 | 9.16 | 9.16 | opened
19 | SS 110/6 Tennery | 2*10 | 1.1 |  |  | 1.1 | 0 | 10.5 | 9.4 | 9.4 | opened | 19 | SS 110/6 Tennery | 2*10 | 0 | 1.1 |  |  | 1.1 | 0 | 10.5 | 9.4 | 9.4 | opened
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 19.93 | 3.04 | 120 | 16.89 | 0 | 21 | 4.11 | 4.11 | opened | 20 | SS 110/35/6 Rasskazovskaya | 25+20 | 0 | 19.93 | 3.04 | 120 | 16.89 | 0 | 21 | 4.11 | 4.11 | opened
21 | SS 110/35/10 Volchkovskaya | 2*10 | 4.11 | 0.95 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened | 21 | SS 110/35/10 Volchkovskaya | 2*10 | 0 | 4.11 | 0.95 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 3.75 | 1.66 | 120 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened | 22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 0 | 3.75 | 1.66 | 120 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened
23 | SS 110/35/10 Khmelevskaya | 2*10 | 1.6 | 0.92 | 120 | 0.68 | 0 | 10.5 | 9.82 | 9.82 | opened | 23 | SS 110/35/10 Khmelevskaya | 2*10 | 0 | 1.6 | 0.92 | 120 | 0.68 | 0 | 10.5 | 9.82 | 9.82 | opened
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.66 | 2.84 | 80 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 0 | 5.66 | 2.84 | 80 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened
25 | SS 110/35/10 Nikiforovskaya | 10+16 | 5.89 | 2.81 | 120 | 3.08 | 0 | 10.5 | 7.42 | 7.42 | opened | 25 | SS 110/35/10 Nikiforovskaya | 10+16 | 0 | 5.89 | 2.81 | 120 | 3.08 | 0 | 10.5 | 7.42 | 7.42 | opened
26 | SS 110/10 Novo-Seslavinskaya | 2.5 | 0.47 | 0.47 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 26 | SS 110/10 Novo-Seslavinskaya | 2.5 | 0 | 0.47 | 0.47 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
27 | SS 110/10 Nov. Arkhangelskaya | 2.5 | 0.19 | 0.19 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 27 | SS 110/10 Nov. Arkhangelskaya | 2.5 | 0.2 | 0.39 | 0.19 | 24 hours | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 28 | SS 110/10 Ilovayskaya | 2*2,5 | 0 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
29 | SS 110/35/10 Yuzhnaya | 16 | 8.51 | 8.51 | 24 hours | 0 | 0 | 16.8 | 16.8 | 16.8 | opened | 29 | SS 110/35/10 Yuzhnaya | 16 | 0 | 8.51 | 8.51 | 24 hours | 0 | 0 | 16.8 | 16.8 | 16.8 | opened
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 17.83 | 9.45 | 120 | 8.38 | 0 | 33.075 | 24.695 | 24.695 | opened | 30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 0.31 | 18.14 | 9.45 | 120 | 8.69 | 0 | 33.075 | 24.385 | 24.385 | opened
31 | SS 110/35/10 Sosnovskaya | 2*16 | 6.6 | 6.6 | 80 | 0 | 0 | 16.8 | 16.8 | 16.8 | opened | 31 | SS 110/35/10 Sosnovskaya | 2*16 | 0 | 6.6 | 6.6 | 80 | 0 | 0 | 16.8 | 16.8 | 16.8 | opened
32 | SS 110/35/10 Pichaevskaya | 2*10 | 4.19 | 4.19 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 32 | SS 110/35/10 Pichaevskaya | 2*10 | 0 | 4.19 | 4.19 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
33 | SS 110/35/10 Algasovskaya | 2*40 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened | 33 | SS 110/35/10 Algasovskaya | 2*40 | 0 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened
34 | SS 110/35/6 Morshanskaya | 40+25 | 13.06 | 7.2005 | 120 | 5.8595 | 0 | 26.25 | 20.3905 | 20.3905 | opened | 34 | SS 110/35/6 Morshanskaya | 40+25 | 0 | 13.06 | 7.2005 | 120 | 5.8595 | 0 | 26.25 | 20.3905 | 20.3905 | opened
35 | SS 110/35/6 Kamvolnaya | 16+25 | 9.12 | 7.2 | 80 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened | 35 | SS 110/35/6 Kamvolnaya | 16+25 | 0 | 9.12 | 7.2 | 80 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 0.63 | 0.63 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 0.3 | 0.93 | 0.93 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 37 | SS 110/35/10 Nashchekinskaya | 2*10 | 0 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
38 | SS 110/10 Shachinskaya | 2.5 | 0.05 | 0.054495 | 24 hours | -0.004495 | 0 | 2.625 | 2.6295 | 2.6295 | opened | 38 | SS 110/10 Shachinskaya | 2.5 | 0 | 0.05 | 0.054495 | 24 hours | -0.004495 | 0 | 2.625 | 2.6295 | 2.6295 | opened
39 | SS 110/35/10 Uvarovskaya | 16+16 | 9.46 | 9.027 | 45 | 0.43301 | 0 | 16.8 | 16.367 | 16.367 | opened | 39 | SS 110/35/10 Uvarovskaya | 16+16 | 0 | 9.46 | 9.027 | 45 | 0.43301 | 0 | 16.8 | 16.367 | 16.367 | opened
40 | SS 110/35/10 Muchkapskaya | 2*10 | 3.77 | 1.3519 | 120 | 2.4181 | 0 | 10.5 | 8.0819 | 8.0819 | opened | 40 | SS 110/35/10 Muchkapskaya | 2*10 | 0 | 3.77 | 1.3519 | 120 | 2.4181 | 0 | 10.5 | 8.0819 | 8.0819 | opened
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.71 | 0.66667 | 120 | 0.043333 | 0 | 2.625 | 2.5817 | 2.5817 | opened | 41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0 | 0.71 | 0.66667 | 120 | 0.043333 | 0 | 2.625 | 2.5817 | 2.5817 | opened
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.4 | 1.2921 | 120 | 0.10795 | 0 | 10.5 | 10.3921 | 10.3921 | opened | 42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 0 | 1.4 | 1.2921 | 120 | 0.10795 | 0 | 10.5 | 10.3921 | 10.3921 | opened
43 | SS 110/10 Shpikulovskaya | 2*2,5 | 0.67 | 0.61404 | 120 | 0.055965 | 0 | 2.625 | 2.569 | 2.569 | opened | 43 | SS 110/10 Shpikulovskaya | 2*2,5 | 0 | 0.67 | 0.61404 | 120 | 0.055965 | 0 | 2.625 | 2.569 | 2.569 | opened
44 | SS 110/35/10 Zherdevskaya | 2*16 | 6.32 | 5.6533 | 80 | 0.66675 | 0 | 16.8 | 16.1333 | 16.1333 | opened | 44 | SS 110/35/10 Zherdevskaya | 2*16 | 0 | 6.32 | 5.6533 | 80 | 0.66675 | 0 | 16.8 | 16.1333 | 16.1333 | opened
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.52 | 0.58824 | 120 | 3.9318 | 0 | 10.5 | 6.5682 | 6.5682 | opened | 45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 0 | 4.52 | 0.58824 | 120 | 3.9318 | 0 | 10.5 | 6.5682 | 6.5682 | opened
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.47 | 0.42105 | 120 | 0.048947 | 0 | 2.625 | 2.5761 | 2.5761 | opened | 46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0 | 0.47 | 0.42105 | 120 | 0.048947 | 0 | 2.625 | 2.5761 | 2.5761 | opened
47 | SS 110/35/10 Tokarevskaya | 2*25 | 7.54 | 6.0846 | 120 | 1.4554 | 0 | 26.25 | 24.7946 | 24.7946 | opened | 47 | SS 110/35/10 Tokarevskaya | 2*25 | 0 | 7.54 | 6.0846 | 120 | 1.4554 | 0 | 26.25 | 24.7946 | 24.7946 | opened
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 1.02 | 0.90918 | 120 | 0.11082 | 0 | 6.615 | 6.5042 | 6.5042 | opened | 48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 0 | 1.02 | 0.90918 | 120 | 0.11082 | 0 | 6.615 | 6.5042 | 6.5042 | opened
49 | SS 110/35/10 Mordovskaya | 2*10 | 4.41 | 1.8937 | 120 | 2.5163 | 0 | 10.5 | 7.9837 | 7.9837 | opened | 49 | SS 110/35/10 Mordovskaya | 2*10 | 0 | 4.41 | 1.8937 | 120 | 2.5163 | 0 | 10.5 | 7.9837 | 7.9837 | opened
50 | SS 110/35/10 Pavlovskaya | 10 | 1.56 | 1.56 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 50 | SS 110/35/10 Pavlovskaya | 10 | 0 | 1.56 | 1.56 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 13.09 | 5.989 | 120 | 7.101 | 0 | 26.25 | 19.149 | 19.149 | opened | 51 | SS 110/35/10 Kirsanovskaya | 2*25 | 0 | 13.09 | 5.989 | 120 | 7.101 | 0 | 26.25 | 19.149 | 19.149 | opened
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 7.92 | 3.41 | 120 | 4.51 | 0 | 16.8 | 12.29 | 12.29 | opened | 52 | SS 110/35/10 Inzhavinskaya | 2*16 | 0.21 | 8.13 | 3.41 | 120 | 4.72 | 0 | 16.8 | 12.08 | 12.08 | opened
53 | SS 110/35/10 Umyotskaya | 2*10 | 4.9 | 4.5 | 80 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | opened | 53 | SS 110/35/10 Umyotskaya | 2*10 | 0 | 4.9 | 4.5 | 80 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | opened
54 | SS 110/35/10 Kovylskaya | 2*10 | 1.97 | 1.347 | 120 | 0.623 | 0 | 10.5 | 9.877 | 9.877 | opened | 54 | SS 110/35/10 Kovylskaya | 2*10 | 0 | 1.97 | 1.347 | 120 | 0.623 | 0 | 10.5 | 9.877 | 9.877 | opened
55 | SS 110/10 Inokovskaya | 2.5 | 0.18 | 0.184 | 24 hours | -0.004 | 0 | 2.625 | 2.629 | 2.629 | opened | 55 | SS 110/10 Inokovskaya | 2.5 | 0 | 0.18 | 0.184 | 24 hours | -0.004 | 0 | 2.625 | 2.629 | 2.629 | opened
SS 35 kv | [11 empty] | 1: SS 35 kv
56 | SS 35/6 Pervomayskaya | 2*2,5 | 1.94 |  |  | 1.94 | 0 | 2.625 | 0.685 | 0.685 | opened | 56 | SS 35/6 Pervomayskaya | 2*2,5 | 0 | 1.94 |  |  | 1.94 | 0 | 2.625 | 0.685 | 0.685 | opened
57 | SS 35/10 Picherskaya | 2*2,5 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened | 57 | SS 35/10 Picherskaya | 2*2,5 | 0 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
58 | SS 35/10 Osinovskaya | 2*2,5 | 0.88 |  |  | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 58 | SS 35/10 Osinovskaya | 2*2,5 | 0 | 0.88 |  |  | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
59 | SS 35/10 Koptevskaya | 2*2,5 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 59 | SS 35/10 Koptevskaya | 2*2,5 | 0 | 0.19 |  |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
60 | SS 35/10 Sayukinskaya | 2,5+4 | 0.5 | 0.5 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 60 | SS 35/10 Sayukinskaya | 2,5+4 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
61 | SS 35/10 Zelyonaya (TES) | 2*4 | 2 |  |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened | 61 | SS 35/10 Zelyonaya (TES) | 2*4 | 0 | 2 |  |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened
62 | SS 35/10 Pyatiletka | 2*4 | 0.27 |  |  | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened | 62 | SS 35/10 Pyatiletka | 2*4 | 0 | 0.27 |  |  | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened
63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.92 |  |  | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0 | 0.92 |  |  | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
64 | SS 35/10 Platonovskaya | 2*6,3 | 3.06 | 0.24 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 64 | SS 35/10 Platonovskaya | 2*6,3 | 0 | 3.06 | 0.24 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened
65 | SS 35/10 Znamenskaya | 2*4 | 2.49 | 1.54 | 120 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened | 65 | SS 35/10 Znamenskaya | 2*4 | 0 | 2.49 | 1.54 | 120 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened
66 | SS 35/10 Sukhotinskaya | 2.5 | 0.35 | 0 | 24 hours | 0.35 | 0 | 0 | -0.35 | -0.35 | closed | 66 | SS 35/10 Sukhotinskaya | 2.5 | 0 | 0.35 | 0 | 24 hours | 0.35 | 0 | 0 | -0.35 | -0.35 | closed
67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.98 |  |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened | 67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0 | 0.98 |  |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened
68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
69 | SS 35/10 Stepnaya | 2*4 | 1.7 | 1.7 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 69 | SS 35/10 Stepnaya | 2*4 | 0 | 1.7 | 1.7 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
70 | SS 35/10 Ivanovskaya (TES) | 2*4 | 0.97 | 0.97 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 70 | SS 35/10 Ivanovskaya (TES) | 2*4 | 0 | 0.97 | 0.97 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.47 | 0.47 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.12 | 0.59 | 0.47 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened
72 | SS 35/10 Gorelskaya | 4+6,3 | 1.71 | 1.71 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 72 | SS 35/10 Gorelskaya | 4+6,3 | 0.15 | 1.86 | 1.71 | 80 | 0.15 | 0 | 4.2 | 4.05 | 4.05 | opened
73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
74 | SS 35/10 Avangardskaya | 2*2,5 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened | 74 | SS 35/10 Avangardskaya | 2*2,5 | 0 | 0.34 |  |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened
75 | SS 35/10 Suravskaya | 1,6+2,5 | 0.45 | 0.45 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 75 | SS 35/10 Suravskaya | 1,6+2,5 | 0 | 0.45 | 0.45 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
76 | SS 35/10 Seleznzyovskaya | 2*4 | 3.6 |  |  | 3.6 | 0 | 4.2 | 0.6 | 0.6 | opened | 76 | SS 35/10 Seleznzyovskaya | 4+4 | 0.78 | 4.38 |  |  | 4.38 | 0 | 4.2 | -0.18 | -0.18 | closed
77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.3 | 0.68 | 80 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 0 | 1.3 | 0.68 | 80 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened
78 | SS 35/10 Viktorskaya | 2.5 | 0.57 |  |  | 0.57 | 0 | 0 | -0.57 | -0.57 | closed | 78 | SS 35/10 Viktorskaya | 2.5 | 0 | 0.57 |  |  | 0.57 | 0 | 0 | -0.57 | -0.57 | closed
79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.61 |  |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | opened | 79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0 | 0.61 |  |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | opened
80 | SS 35/10 Avdeevskaya | 2*2,5 | 0.72 |  |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 80 | SS 35/10 Avdeevskaya | 2*2,5 | 0 | 0.72 |  |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
81 | SS 35/10 Tatanovskaya | 2*2,5 | 2.14 |  |  | 2.14 | 0 | 2.625 | 0.485 | 0.485 | opened | 81 | SS 35/10 Tatanovskaya | 2*2,5 | 0.45 | 2.59 | 0.15 | 120 | 2.44 | 0 | 2.625 | 0.185 | 0.185 | opened
82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 3.02 | 0.63 | 60 | 2.39 | 0 | 2.63 | 0.24 | 0.24 | opened | 82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 0.21 | 3.23 | 0.63 | 60 | 2.6 | 0 | 2.63 | 0.03 | 0.03 | opened
83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 5.38 |  |  | 5.38 | 0 | 6.615 | 1.235 | 1.235 | opened | 83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 0.12 | 5.5 |  |  | 5.5 | 0 | 6.615 | 1.115 | 1.115 | opened
84 | SS 35/10 Bokinskaya | 2*6,3 | 3.04 | 0.92 | 30 | 2.12 | 0 | 6.615 | 4.495 | 4.495 | opened | 84 | SS 35/10 Bokinskaya | 2*6,3 | 0.84 | 3.88 | 0.92 | 30 | 2.96 | 0 | 6.615 | 3.655 | 3.655 | opened
85 | SS 35/10 Stolovskaya | 4 | 0.52 | 0.52 | 24 hours | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 85 | SS 35/10 Stolovskaya | 4 | 0 | 0.52 | 0.52 | 24 hours | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
86 | SS 35/10 Tulinovskaya | 2*2,5 | 1.32 |  |  | 1.32 | 0 | 2.625 | 1.305 | 1.305 | opened | 86 | SS 35/10 Tulinovskaya | 2*2,5 | 0 | 1.32 |  |  | 1.32 | 0 | 2.625 | 1.305 | 1.305 | opened
87 | SS 35/6 Macaroni factory | 1.6 | 0.04 |  |  | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened | 87 | SS 35/6 Macaroni factory | 1.6 | 0 | 0.04 |  |  | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened
88 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.09 |  |  | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened | 88 | SS 35/10 Serebryakovskaya | 2*1,6 | 0 | 1.09 |  |  | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened
89 | SS 35/10 B.Doroga | 2*1,6 | 0.34 | 0.34 | 60 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 89 | SS 35/10 B.Doroga | 2*1,6 | 0 | 0.34 | 0.34 | 60 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
91 | SS 35/10 Vishnevskaya | 2*2,5 | 0.37 | 0.26 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 91 | SS 35/10 Vishnevskaya | 2*2,5 | 0 | 0.37 | 0.26 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.32 | 0.32 | 50 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0 | 0.32 | 0.32 | 50 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
93 | SS 35/10 Glazkovskaya | 2*4 | 0.82 | 0.71 | 120 | 0.11 | 0 | 4.2 | 4.09 | 4.09 | opened | 93 | SS 35/10 Glazkovskaya | 2*4 | 0 | 0.82 | 0.71 | 120 | 0.11 | 0 | 4.2 | 4.09 | 4.09 | opened
94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
95 | SS 35/6 Donskaya | 6,3+10 | 3.65 | 3.65 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 95 | SS 35/6 Donskaya | 6,3+10 | 0 | 3.65 | 3.65 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
96 | SS 35/10 Druzhba | 2.5 | 0.16 | 0.16 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 96 | SS 35/10 Druzhba | 2.5 | 0 | 0.16 | 0.16 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.35 | 0.23 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0 | 0.35 | 0.23 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.33 | 0.25 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened | 98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0 | 0.33 | 0.25 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened
99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.28 | 1.08 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 0 | 1.28 | 1.08 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
100 | SS 35/10 KIM | 2,5+4 | 0.86 | 0.74 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 100 | SS 35/10 KIM | 2,5+4 | 0 | 0.86 | 0.74 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
101 | SS 35/10 Klenskaya | 2*2,5 | 0.23 | 0.22 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 101 | SS 35/10 Klenskaya | 2*2,5 | 0.5 | 0.73 | 0.22 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.82 | 0.6 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0 | 0.82 | 0.6 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
103 | SS 35/10 Komintern | 2*2,5 | 0.26 | 0.22 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 103 | SS 35/10 Komintern | 2*2,5 | 0.57 | 0.83 | 0.22 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | opened
104 | SS 35/10 Kochetovskaya | 6.3 | 0.2 | 0.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 104 | SS 35/10 Kochetovskaya | 6.3 | 0.11 | 0.31 | 0.2 | 24 hours | 0.11 | 0 | 6.615 | 6.505 | 6.505 | opened
105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.14 | 0.14 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0 | 0.14 | 0.14 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 0.85 | 0.66 | 24 hours | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 0 | 0.85 | 0.66 | 24 hours | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.34 | 0.28 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened | 107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0 | 0.34 | 0.28 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened
108 | SS 35/10 Petrovskaya | 2*4 | 2.88 | 1.2 | 120 | 1.68 | 0 | 4.2 | 2.52 | 2.52 | opened | 108 | SS 35/10 Petrovskaya | 2*4 | 0 | 2.88 | 1.2 | 120 | 1.68 | 0 | 4.2 | 2.52 | 2.52 | opened
109 | SS 35/10 Prigorodnaya | 2*5,6 | 0.71 | 0.62 | 120 | 0.09 | 0 | 5.88 | 5.79 | 5.79 | opened | 109 | SS 35/10 Prigorodnaya | 2*5,6 | 0 | 0.71 | 0.62 | 120 | 0.09 | 0 | 5.88 | 5.79 | 5.79 | opened
110 | SS 35/6 Progress | 2*10 | 8.49 |  |  | 8.49 | 0 | 10.5 | 2.01 | 2.01 | opened | 110 | SS 35/6 Progress | 2*10 | 0 | 8.49 |  |  | 8.49 | 0 | 10.5 | 2.01 | 2.01 | opened
111 | SS 35/10 Raninskaya | 1.6 | 0.32 | 0.32 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 111 | SS 35/10 Raninskaya | 1.6 | 0 | 0.32 | 0.32 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.19 |  |  | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0 | 0.19 |  |  | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened
113 | SS 35/10 Saburovskaya | 2*2,5 | 1.99 |  |  | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened | 113 | SS 35/10 Saburovskaya | 2*2,5 | 0 | 1.99 |  |  | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened
114 | SS 35/10 Sestryonskaya | 1.6 | 0.49 |  |  | 0.49 | 0 | 0 | -0.49 | -0.49 | closed | 114 | SS 35/10 Sestryonskaya | 1.6 | 0 | 0.49 |  |  | 0.49 | 0 | 0 | -0.49 | -0.49 | closed
115 | SS 35/10 Sitovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 115 | SS 35/10 Sitovskaya | 1.6 | 0 | 0.5 | 0.5 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
116 | SS 35/10 Skobelevskaya | 1.6 | 0.24 | 0.24 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 116 | SS 35/10 Skobelevskaya | 1.6 | 0 | 0.24 | 0.24 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
117 | SS 35/10 Ustyinskaya | 2.5 | 1.06 | 1.06 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 117 | SS 35/10 Ustyinskaya | 2.5 | 0 | 1.06 | 1.06 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
118 | SS 35/10 Yurlovskaya | 2*2,5 | 0.41 |  |  | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened | 118 | SS 35/10 Yurlovskaya | 2*2,5 | 0 | 0.41 |  |  | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened
119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0.7 |  |  | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0 | 0.7 |  |  | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
120 | SS 35/10 Agroprom | 2*4 | 1.42 |  |  | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened | 120 | SS 35/10 Agroprom | 2*4 | 0 | 1.42 |  |  | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened
121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.34 |  |  | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened | 121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0 | 0.34 |  |  | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened
122 | SS 35/10 Vanovskaya | 2*2,5 | 0.07 | 0.07 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 122 | SS 35/10 Vanovskaya | 2*2,5 | 0 | 0.07 | 0.07 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
123 | SS 35/10 Vyazhlinskaya | 1.8 | 1.04 | 0.81 | 24 hours | 0.23 | 0 | 1.89 | 1.66 | 1.66 | opened | 123 | SS 35/10 Vyazhlinskaya | 1.8 | 0 | 1.04 | 0.81 | 24 hours | 0.23 | 0 | 1.89 | 1.66 | 1.66 | opened
124 | SS 35/10 Kryukovskaya | 2*2,5 | 0.66 | 0.6593 | 120 | 0.000697 | 0 | 2.625 | 2.6243 | 2.6243 | opened | 124 | SS 35/10 Kryukovskaya | 2*2,5 | 0 | 0.66 | 0.6593 | 120 | 0.000697 | 0 | 2.625 | 2.6243 | 2.6243 | opened
125 | SS 35/6 Lugovaya | 4 | 0.95 | 0.94977 | 24 hours | 0.00023 | 0 | 4.2 | 4.1998 | 4.1998 | opened | 125 | SS 35/6 Lugovaya | 4 | 0 | 0.95 | 0.94977 | 24 hours | 0.00023 | 0 | 4.2 | 4.1998 | 4.1998 | opened
126 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.15 | 0.1467 | 120 | 0.003296 | 0 | 2.625 | 2.6217 | 2.6217 | opened | 126 | SS 35/10 Lyubvinskaya | 2*2,5 | 0 | 0.15 | 0.1467 | 120 | 0.003296 | 0 | 2.625 | 2.6217 | 2.6217 | opened
127 | SS 35/10 Morshanskaya | 2*4 | 2.29 |  |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | opened | 127 | SS 35/10 Morshanskaya | 2*4 | 0 | 2.29 |  |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | opened
128 | SS 35/10 Piterskaya | 2.5 | 0.93 | 0.93 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 128 | SS 35/10 Piterskaya | 2.5 | 0 | 0.93 | 0.93 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
129 | SS 35/10 Rakshinskaya | 2*4 | 1.62 | 1.6137 | 80 | 0.006256 | 0 | 4.2 | 4.1937 | 4.1937 | opened | 129 | SS 35/10 Rakshinskaya | 2*4 | 0 | 1.62 | 1.6137 | 80 | 0.006256 | 0 | 4.2 | 4.1937 | 4.1937 | opened
130 | SS 35/10 Rybinskaya | 2*2,5 | 1.05 | 1.0536 | 80 | -0.00357 | 0 | 2.625 | 2.6286 | 2.6286 | opened | 130 | SS 35/10 Rybinskaya | 2*2,5 | 0 | 1.05 | 1.0536 | 80 | -0.00357 | 0 | 2.625 | 2.6286 | 2.6286 | opened
131 | SS 35/10 Serpovskaya | 2*2,5 | 0.7 | 0.7 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 131 | SS 35/10 Serpovskaya | 2*2,5 | 0 | 0.7 | 0.7 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
132 | SS 35/10 St.Tomnikovskaya | 1 | 0.09 | 0.092555 | 24 hours | -0.002555 | 0 | 1.05 | 1.0526 | 1.0526 | opened | 132 | SS 35/10 St.Tomnikovskaya | 1 | 0 | 0.09 | 0.092555 | 24 hours | -0.002555 | 0 | 1.05 | 1.0526 | 1.0526 | opened
133 | SS 35/10 Chernitovskaya | 2.5 | 0.4 | 0.39963 | 24 hours | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened | 133 | SS 35/10 Chernitovskaya | 2.5 | 0 | 0.4 | 0.39963 | 24 hours | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened
134 | SS 35/10 Bondarskaya | 2*2,5 | 0.93 | 0.93 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 134 | SS 35/10 Bondarskaya | 2*2,5 | 0.55 | 1.48 | 0.93 | 80 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened
135 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.53 | 0.53457 | 80 | -0.00457 | 0 | 1.68 | 1.6846 | 1.6846 | opened | 135 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0 | 0.53 | 0.53457 | 80 | -0.00457 | 0 | 1.68 | 1.6846 | 1.6846 | opened
136 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened | 136 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened
137 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.71 | 0.71276 | 120 | -0.00276 | 0 | 2.625 | 2.6278 | 2.6278 | opened | 137 | SS 35/10 Egorovskaya | 2,5+3,2 | 0 | 0.71 | 0.71276 | 120 | -0.00276 | 0 | 2.625 | 2.6278 | 2.6278 | opened
138 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.15 |  |  | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 138 | SS 35/10 Kershinskaya | 1,6+2,5 | 0 | 0.15 |  |  | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
139 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.05 | 0.054495 | 120 | -0.004495 | 0 | 1.68 | 1.6845 | 1.6845 | opened | 139 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0 | 0.05 | 0.054495 | 120 | -0.004495 | 0 | 1.68 | 1.6845 | 1.6845 | opened
140 | SS 35/10 Lipovskaya | 2.5 | 0.27 | 0.26988 | 24 hours | 0.00012 | 0 | 2.625 | 2.6249 | 2.6249 | opened | 140 | SS 35/10 Lipovskaya | 2.5 | 0 | 0.27 | 0.26988 | 24 hours | 0.00012 | 0 | 2.625 | 2.6249 | 2.6249 | opened
141 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.11 | 0.11 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 141 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0 | 0.11 | 0.11 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
142 | SS 35/10 Mitropolskaya | 2.5 | 0.28 | 0.28 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 142 | SS 35/10 Mitropolskaya | 2.5 | 0.44 | 0.72 | 0.28 | 24 hours | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened
143 | SS 35/10 P.Uglovskaya | 1.6 | 0.35 | 0.35292 | 24 hours | -0.00292 | 0 | 1.68 | 1.6829 | 1.6829 | opened | 143 | SS 35/10 P.Uglovskaya | 1.6 | 0 | 0.35 | 0.35292 | 24 hours | -0.00292 | 0 | 1.68 | 1.6829 | 1.6829 | opened
144 | SS 35/10 Rudovskaya | 2*2,5 | 0.52 |  |  | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 144 | SS 35/10 Rudovskaya | 2*2,5 | 0 | 0.52 |  |  | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
145 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.23 | 0.23 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 145 | SS 35/10 V.Yaroslavskaya | 2.5 | 0 | 0.23 | 0.23 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
146 | SS 35/10 Degtyanskaya | 2.5 | 0.9 | 0.9 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 146 | SS 35/10 Degtyanskaya | 2.5 | 0 | 0.9 | 0.9 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
147 | SS 35/10 Zelenaya (MoES) | 1.6 | 0.18 | 0.17992 | 24 hours | 8e-05 | 0 | 1.68 | 1.6799 | 1.6799 | opened | 147 | SS 35/10 Zelenaya (MoES) | 1.6 | 0 | 0.18 | 0.17992 | 24 hours | 8e-05 | 0 | 1.68 | 1.6799 | 1.6799 | opened
148 | SS 35/10 Kulevatovskaya | 2*4 | 1.81 | 1.81 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 148 | SS 35/10 Kulevatovskaya | 2*4 | 0.12 | 1.93 | 1.81 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
149 | SS 35/10 Kulevatovskaya | 4+2,5 | 0.2 | 0.20362 | 120 | -0.003621 | 0 | 2.625 | 2.6286 | 2.6286 | opened | 149 | SS 35/10 Kulevatovskaya | 4+2,5 | 0 | 0.2 | 0.20362 | 120 | -0.003621 | 0 | 2.625 | 2.6286 | 2.6286 | opened
150 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 150 | SS 35/10 Gryaznovskaya | 2*2,5 | 0 | 0.09 |  |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
151 | SS 35/10 Otyasskaya | 2*2,5 | 0.4 | 0.39963 | 120 | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened | 151 | SS 35/10 Otyasskaya | 2*2,5 | 0 | 0.4 | 0.39963 | 120 | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened
152 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.19 | 0.1903 | 24 hours | -0.0003 | 0 | 1.68 | 1.6803 | 1.6803 | opened | 152 | SS 35/10 P.Vasilyevskaya | 1.6 | 0 | 0.19 | 0.1903 | 24 hours | -0.0003 | 0 | 1.68 | 1.6803 | 1.6803 | opened
153 | SS 35/10 Podlesnaya | 2*2,5 | 0.42 | 0.41935 | 120 | 0.000648 | 0 | 2.625 | 2.6244 | 2.6244 | opened | 153 | SS 35/10 Podlesnaya | 2*2,5 | 0 | 0.42 | 0.41935 | 120 | 0.000648 | 0 | 2.625 | 2.6244 | 2.6244 | opened
154 | SS 35/10 Tr.Roslyayskaya (МоES) | 2*2,5 | 0.38 | 0.38146 | 120 | -0.001465 | 0 | 2.625 | 2.6265 | 2.6265 | opened | 154 | SS 35/10 Tr.Roslyayskaya (МоES) | 2*2,5 | 0.28 | 0.66 | 0.38146 | 120 | 0.27853 | 0 | 2.625 | 2.3465 | 2.3465 | opened
155 | SS 35/10 Zherdevskaya | 10 | 2.51 | 2.25 | 24 hours | 0.26 | 0 | 10.5 | 10.24 | 10.24 | opened | 155 | SS 35/10 Zherdevskaya | 10 | 0 | 2.51 | 2.25 | 24 hours | 0.26 | 0 | 10.5 | 10.24 | 10.24 | opened
156 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 156 | SS 35/10 Sukmanovskaya | 2*2,5 | 0 | 0.16 |  |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
157 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.29 | 0.29 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 157 | SS 35/10 Tugolukovskaya | 2,5+4 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
158 | SS 35/10 Artemovskaya | 2*2,5 | 0.39 | 0.35 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 158 | SS 35/10 Artemovskaya | 2*2,5 | 0 | 0.39 | 0.35 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
159 | SS 35/10 RSKhO | 2,5+4 | 1.29 | 1.16 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 159 | SS 35/10 RSKhO | 2,5+4 | 0 | 1.29 | 1.16 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
160 | SS 35/10 Maksimovskaya | 2*1,6 | 0.2 | 0.18 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened | 160 | SS 35/10 Maksimovskaya | 2*1,6 | 0 | 0.2 | 0.18 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened
161 | SS 35/10 Burnakskaya | 5,6+6,3 | 1.9 |  |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened | 161 | SS 35/10 Burnakskaya | 5,6+6,3 | 0 | 1.9 |  |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened
162 | SS 35/10 Poletaevskaya | 2*4 | 0.22 | 0.19 | 120 | 0.03 | 2.18 | 4.2 | 1.99 | 1.99 | opened | 162 | SS 35/10 Poletaevskaya | 2*4 | 0 | 0.22 | 0.19 | 120 | 0.03 | 2.18 | 4.2 | 1.99 | 1.99 | opened
163 | SS 35/10 T.Roslyayskaya (housing-operational service) | 4+2,5 | 0.98 |  |  | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 163 | SS 35/10 T.Roslyayskaya (housing-operational service) | 4+2,5 | 0 | 0.98 |  |  | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened
164 | SS 35/10 Pioner | 1,6+2,5 | 1.24 | 0.72 | 60 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened | 164 | SS 35/10 Pioner | 1,6+2,5 | 0 | 1.24 | 0.72 | 60 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
165 | SS 35/10 Lvovskaya | 2*2,5 | 0.53 | 0.47 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened | 165 | SS 35/10 Lvovskaya | 2*2,5 | 0 | 0.53 | 0.47 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
166 | SS 35/10 Nadezhdinskaya | 1.6 | 0.28 | 0.28 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 166 | SS 35/10 Nadezhdinskaya | 1.6 | 0 | 0.28 | 0.28 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
167 | SS 35/10 Kuleshovskaya | 2.5 | 0.26 | 0.26 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 167 | SS 35/10 Kuleshovskaya | 2.5 | 0 | 0.26 | 0.26 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
168 | SS 35/10 Chernyaevskaya | 4+2,5 | 1.49 |  |  | 1.49 | 0 | 2.625 | 1.135 | 1.135 | opened | 168 | SS 35/10 Chernyaevskaya | 4+2,5 | 0 | 1.49 |  |  | 1.49 | 0 | 2.625 | 1.135 | 1.135 | opened
169 | SS 35/10 Ivanovskaya (housing operational service) | 2*2,5 | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 169 | SS 35/10 Ivanovskaya (housing operational service) | 2*2,5 | 0 | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
170 | SS 35/10 Shulginskaya | 2*4 | 1 | 0.02 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 170 | SS 35/10 Shulginskaya | 2*4 | 0 | 1 | 0.02 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened
171 | SS 35/10 Lavrovskaya | 2*2,5 | 0.14 |  |  | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 171 | SS 35/10 Lavrovskaya | 2*2,5 | 0 | 0.14 |  |  | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
172 | SS 35/10 N.Sergievskaya | 3.2 | 0.49 | 0.49 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 172 | SS 35/10 N.Sergievskaya | 3.2 | 0 | 0.49 | 0.49 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
173 | SS 35/10 Kamenskaya | 2*2,5 | 0.31 |  |  | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 173 | SS 35/10 Kamenskaya | 2*2,5 | 0 | 0.31 |  |  | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
174 | SS 35/10 Protasovskaya | 4+2,5 | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 174 | SS 35/10 Protasovskaya | 4+2,5 | 0 | 0.33 |  |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
175 | SS 35/10 Chakinskaya | 4 | 0.37 |  |  | 0.37 | 0 | 0 | -0.37 | -0.37 | closed | 175 | SS 35/10 Chakinskaya | 4 | 0 | 0.37 |  |  | 0.37 | 0 | 0 | -0.37 | -0.37 | closed
176 | SS 35/10 Lukinskaya | 2.5 | 0.22 | 0.22 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 176 | SS 35/10 Lukinskaya | 2.5 | 0 | 0.22 | 0.22 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
177 | SS 35/10 Zolotovskaya | 2.5 | 0.37 | 0.37 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 177 | SS 35/10 Zolotovskaya | 2.5 | 0 | 0.37 | 0.37 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
178 | SS 35/10 Mozdokskaya | 2.5 | 0.2 |  |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed | 178 | SS 35/10 Mozdokskaya | 2.5 | 0 | 0.2 |  |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed
179 | SS 35/10 Oblovskaya | 2*2,5 | 0.69 | 0.65 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 179 | SS 35/10 Oblovskaya | 2*2,5 | 0 | 0.69 | 0.65 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
180 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.35 | 0.07 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 180 | SS 35/10 V.Vershinskaya | 2,5+4 | 0 | 0.35 | 0.07 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
181 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.14 |  |  | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 181 | SS 35/10 Luchevskaya | 2,5+1,6 | 0 | 0.14 |  |  | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
182 | SS 35/10 Olshanskaya | 4+2,5 | 1.12 | 0.32 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 182 | SS 35/10 Olshanskaya | 4+2,5 | 0 | 1.12 | 0.32 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
183 | SS 35/10 Pavlodarskaya | 2.5 | 0.1 | 0.1 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 183 | SS 35/10 Pavlodarskaya | 2.5 | 0 | 0.1 | 0.1 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
184 | SS 35/10 Berezovskaya | 2*2,5 | 0.22 |  |  | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 184 | SS 35/10 Berezovskaya | 2*2,5 | 0 | 0.22 |  |  | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
185 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 185 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
186 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.24 |  |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 186 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0 | 0.24 |  |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
187 | SS 35/10 Shapkinskaya | 2*4 | 0.86 |  |  | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 187 | SS 35/10 Shapkinskaya | 2*4 | 0 | 0.86 |  |  | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
188 | SS 35/10 Maryinskaya | 2*1,6 | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 188 | SS 35/10 Maryinskaya | 2*1,6 | 0 | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
189 | SS 35/10 Irskaya | 1,6+2,5 | 0.37 | 0.345 | 120 | 0.025 | 0 | 1.68 | 1.655 | 1.655 | opened | 189 | SS 35/10 Irskaya | 1,6+2,5 | 0 | 0.37 | 0.345 | 120 | 0.025 | 0 | 1.68 | 1.655 | 1.655 | opened
190 | SS 35/10 Zavodskaya | 2*4 | 1.25 | 1.25 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 190 | SS 35/10 Zavodskaya | 2*4 | 0 | 1.25 | 1.25 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
191 | SS 35/10 Kalaisskaya | 2.5 | 0.58 | 0.58 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 191 | SS 35/10 Kalaisskaya | 2.5 | 0 | 0.58 | 0.58 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
192 | SS 35/10 Sokolovskaya | 2*2,5 | 1.02 | 1.02 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 192 | SS 35/10 Sokolovskaya | 2*2,5 | 0 | 1.02 | 1.02 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
193 | SS 35/10 Veterinarnaya | 2.5 | 0.13 | 0.13 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 193 | SS 35/10 Veterinarnaya | 2.5 | 0 | 0.13 | 0.13 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
194 | SS 35/10 Glukhovskaya | 2.5 | 0.09 | 0.09 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 194 | SS 35/10 Glukhovskaya | 2.5 | 0 | 0.09 | 0.09 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
195 | SS 35/10 Orzhevskaya | 2.5 | 0.47 | 0.47 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 195 | SS 35/10 Orzhevskaya | 2.5 | 0 | 0.47 | 0.47 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
196 | SS 35/10 Umyotskaya | 2*4 | 1.54 | 1.54 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 196 | SS 35/10 Umyotskaya | 2*4 | 0 | 1.54 | 1.54 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
197 | SS 35/10 Gavrilovskaya | 2*4 | 1.07 | 0.996 | 120 | 0.074 | 0 | 4.2 | 4.126 | 4.126 | opened | 197 | SS 35/10 Gavrilovskaya | 2*4 | 0 | 1.07 | 0.996 | 120 | 0.074 | 0 | 4.2 | 4.126 | 4.126 | opened
198 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.76 | 0.76 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 198 | SS 35/10 Peresypkinskaya | 2*2,5 | 0 | 0.76 | 0.76 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
199 | SS 35/10 Annenskaya | 2*2,5 | 0.87 | 0.806 | 80 | 0.064 | 0 | 2.625 | 2.561 | 2.561 | opened | 199 | SS 35/10 Annenskaya | 2*2,5 | 0.4 | 1.27 | 0.806 | 80 | 0.464 | 0 | 2.625 | 2.161 | 2.161 | opened
200 | SS 35/10 Annenskaya | 2*2,5 | 0.33 | 0.33 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 200 | SS 35/10 Annenskaya | 2*2,5 | 0 | 0.33 | 0.33 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
201 | SS 35/10 Nikitenskaya | 2,5+1,6 | 0.15 | 0.135 | 120 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | opened | 201 | SS 35/10 Nikitenskaya | 2,5+1,6 | 0 | 0.15 | 0.135 | 120 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | opened
202 | SS 35/10 Balykleyskaya | 2*2,5 | 0.49 | 0.414 | 120 | 0.076 | 0 | 2.625 | 2.549 | 2.549 | opened | 202 | SS 35/10 Balykleyskaya | 2*2,5 | 0 | 0.49 | 0.414 | 120 | 0.076 | 0 | 2.625 | 2.549 | 2.549 | opened
203 | SS 35/10 Karavainskaya | 2*1,6 | 0.58 | 0.548 | 80 | 0.032 | 0 | 1.68 | 1.648 | 1.648 | opened | 203 | SS 35/10 Karavainskaya | 2*1,6 | 0 | 0.58 | 0.548 | 80 | 0.032 | 0 | 1.68 | 1.648 | 1.648 | opened
204 | SS 35/10 Poultry plant | 2*2,5 |  |  |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 204 | SS 35/10 Poultry plant | 2*2,5 | 0 | 0 |  |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
205 | SS 35/10 Pavlovskaya | 3.2 | 0.28 | 0.28 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 205 | SS 35/10 Pavlovskaya | 3.2 | 0 | 0.28 | 0.28 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
| Total: | 2384.7 | 485.95 | [8 empty] | 2: Total:; 3: 2384.7; 5: 509.11
| deficit | [8 empty] | -2.625 |  | 2: deficit; Мин. 12: -4.555
| proficit | [8 empty] | 996.597 |  | 2: proficit; Мин. 12: 981.377

## Белгород
[11 empty] | Table 1 | [12 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  | МVА | МVА | Мin. | [11 empty] | МVА | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS-110/35/10 kv D.Polyana | 6.3 | 1.453 | 1.457 | 45 | 1.457 | 0 | 1.457 | 0.004 | 0 |  | 1 | SS-110/35/10 kv D.Polyana | 6.3 | 0 | 1.453 | 1.457 | 45 | -0.004 | 0 | 1.457 | 0.004 | 0
| Sн. MV, МVА | 6.3 | 0.958 | 0.958 |  | 0.958 | 0 | 0.958 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0.958 | 0.958 | 0 | 0 | 0 | 0.958 | 0 | 0
| Sн. LV, МVА | 6.3 | 0.495 | 0.499 |  | 0.499 | 0 | 0.499 | 0.004 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.495 | 0.499 | 0 | -0.004 | 0 | 0.499 | 0.004 | 0
2 | SS-110/35/10kv Konshino | 6.3 | 0.383 | 0.39 | 20 | 0.39 | 0 | 0.39 | 0.007 | 0 |  | 2 | SS-110/35/10kv Konshino | 6.3 | 0 | 0.383 | 0.39 | 20 | -0.007 | 0 | 0.39 | 0.007 | 0
| Sн. MV, МVА | 6.3 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 0.383 | 0.39 |  | 0.39 | 0 | 0.39 | 0.007 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.383 | 0.39 | 0 | -0.007 | 0 | 0.39 | 0.007
3 | SS-110/35/10kv Orositelnaya | 16 | 11.607 | 11.607 | 120 | 11.607 | 0 | 11.607 | 0 | 0 |  | 3 | SS-110/35/10kv Orositelnaya | 16 | 0.03 | 11.637 | 11.607 | 120 | 0.03 | 0 | 11.607 | -0.03 | -0.03
| Sн. MV, МVА | 16 | 8.606 | 8.606 |  | 8.606 | 0 | 8.606 | 0 |  |  |  | Sн. MV, МVА | 16 | 0 | 8.606 | 8.606 | 0 | 0 | 0 | 8.606 | 0
| Sн. LV, МVА | 16 | 3.001 | 3.001 |  | 3.001 | 0 | 3.001 | 0 |  |  |  | Sн. LV, МVА | 16 | 0 | 3.001 | 3.001 | 0 | 0 | 0 | 3.001 | 0
4 | SS-110/35/6kv Pishcheprom | 25 | 6.431 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.248 | 0 |  | 4 | SS-110/35/6kv Pishcheprom | 25 | 0.7426 | 7.1736 | 6.679 | 120 | 0.4946 | 0 | 6.679 | -0.4946 | -0.4946
| Sн. MV, МVА | 12.5 | 2.022 | 2.022 |  | 2.022 | 0 | 2.022 | 0 |  |  |  | Sн. MV, МVА | 12.5 | 0 | 2.022 | 2.022 | 0 | 0 | 0 | 2.022 | 0
| Sн. LV, МVА | 12.5 | 4.409 | 4.657 |  | 4.657 | 0 | 4.657 | 0.248 |  |  |  | Sн. LV, МVА | 12.5 | 0.7426 | 5.1516 | 4.657 | 0 | 0.4946 | 0 | 4.657 | -0.4946
5 | SS-110/35/10kv Rovenki | 16 | 2.29 | 3.44 | 120 | 3.44 | 0 | 3.44 | 1.15 | 1.15 |  | 5 | SS-110/35/10kv Rovenki | 16 | 0.06 | 2.35 | 3.44 | 120 | -1.09 | 0 | 3.44 | 1.09 | 1.09
| Sн. MV, МVА | 16 | 0 | 4 |  | 4 | 0 | 4 | 4 |  |  |  | Sн. MV, МVА | 16 | 0 | 0 | 4 | 0 | -4 | 0 | 4 | 4
| Sн. LV, МVА | 16 | 2.29 | 3.44 |  | 3.44 | 0 | 3.44 | 1.15 |  |  |  | Sн. LV, МVА | 16 | 0.06 | 2.35 | 3.44 | 0 | -1.09 | 0 | 3.44 | 1.09
6 | SS-110/35/10kv Serebryanka | 10 | 1.234 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.546 | 0 |  | 6 | SS-110/35/10kv Serebryanka | 10 | 0 | 1.234 | 1.78 | 45 | -0.546 | 0 | 1.78 | 0.546 | 0
| Sн. MV, МVА | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1.234 | 1.78 |  | 1.78 | 0 | 1.78 | 0.546 |  |  |  | Sн. LV, MVА | 10 | 0 | 1.234 | 1.78 | 0 | -0.546 | 0 | 1.78 | 0.546
7 | SS-35/10kv Afanasyevka | 1.6 | 0.70565 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.059246 | -0.059246 |  | 7 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.70565 | 0.6464 | 45 | 0.059246 | 0 | 0.6464 | -0.059246 | -0.059246
8 | SS-35/10kv Borisovka | 1.6 | 0.6377 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.045804 | 0.045804 |  | 8 | SS-35/10kv Borisovka | 1.6 | 0 | 0.6377 | 0.6835 | 45 | -0.045804 | 0 | 0.6835 | 0.045804 | 0.045804
9 | SS-35/10kv Borisy | 1.6 | 0.51253 | 0 | 20 | 0 | 0 | 0 | -0.51253 | -0.51253 |  | 9 | SS-35/10kv Borisy | 1.6 | 0 | 0.51253 | 0 | 20 | 0.51253 | 0 | 0 | -0.51253 | -0.51253
10 | SS-35/10kv Gostishchevo | 4 | 2.5809 | 2.64 | 80 | 2.64 | 0 | 2.64 | 0.059085 | 0.059085 |  | 10 | SS-35/10kv Gostishchevo | 4 | 0.162 | 2.7429 | 2.64 | 80 | 0.10291 | 0 | 2.64 | -0.10291 | -0.10291
11 | SS-35/10kv Gruzskoe | 1.6 | 0.61905 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.43095 | 0.43095 |  | 11 | SS-35/10kv Gruzskoe | 1.6 | 0.025 | 0.64405 | 1.05 | 80 | -0.40595 | 0 | 1.05 | 0.40595 | 0.40595
12 | SS-35/10kv Zemsnaryad | 1.6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | SS-35/10kv Zemsnaryad | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0.38773 | 0 |  | 0 | 0 | 0 | -0.38773 | -0.38773 |  | 13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.38773 | 0 | 0 | 0.38773 | 0 | 0 | -0.38773 | -0.38773
14 | SS-35/10kv Kamyzino | 2.5 | 1.1346 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.59359 | -0.59359 |  | 14 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.1346 | 0.541 | 45 | 0.59359 | 0 | 0.541 | -0.59359 | -0.59359
15 | SS-35/10kv Koloskovo | 2.5 | 1.6498 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | 0.012776 | 0.012776 |  | 15 | SS-35/10kv Koloskovo | 2.5 | 0.03 | 1.6798 | 1.6626 | 45 | 0.017224 | 0 | 1.6626 | -0.017224 | -0.017224
16 | SS-35/10jkv Kryukovo | 2.5 | 1.5379 | 1.55 | 45 | 1.55 | 0 | 1.55 | 0.012079 | 0.012079 |  | 16 | SS-35/10jkv Kryukovo | 2.5 | 0.029 | 1.5669 | 1.55 | 45 | 0.016921 | 0 | 1.55 | -0.016921 | -0.016921
17 | SS-35/10kv Kushchino | 1.6 | 0.38137 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.028734 | 0.028734 |  | 17 | SS-35/10kv Kushchino | 1.6 | 0 | 0.38137 | 0.4101 | 80 | -0.028734 | 0 | 0.4101 | 0.028734 | 0.028734
18 | SS-35/10kv Lopukhinka | 2.5 | 0.38666 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.020343 | 0.020343 |  | 18 | SS-35/10kv Lopukhinka | 2.5 | 0 | 0.38666 | 0.407 | 20 | -0.020343 | 0 | 0.407 | 0.020343 | 0.020343
19 | SS-35/10kv Malakeevo | 2.5 | 1.3202 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.059782 | 0.059782 |  | 19 | SS-35/10kv Malakeevo | 2.5 | 0.01 | 1.3302 | 1.38 | 120 | -0.049782 | 0 | 1.38 | 0.049782 | 0.049782
20 | SS-35/10kv Murom | 2.5 | 1.2542 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.28576 | 0.28576 |  | 20 | SS-35/10kv Murom | 2.5 | 0.075 | 1.3292 | 1.54 | 45 | -0.21076 | 0 | 1.54 | 0.21076 | 0.21076
21 | SS-35/10kv Nikolaevka | 2.5 | 0.65277 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | 0.011927 | 0.011927 |  | 21 | SS-35/10kv Nikolaevka | 2.5 | 0.014 | 0.66677 | 0.6647 | 45 | 0.0020725 | 0 | 0.6647 | -0.0020725 | -0.0020725
22 | SS-35/10kv Nikolskoe | 4 | 1.6697 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.88968 | -0.88968 |  | 22 | SS-35/10kv Nikolskoe | 4 | 0.0405 | 1.7102 | 0.78 | 120 | 0.93018 | 0 | 0.78 | -0.93018 | -0.93018
23 | SS-35/10kv Pokrovka | 4 | 0.67755 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.044451 | 0.044451 |  | 23 | SS-35/10kv Pokrovka | 4 | 0.168 | 0.84555 | 0.722 | 45 | 0.12355 | 0 | 0.722 | -0.12355 | -0.12355
24 | SS-35/10kv Pyatnitskoe | 4 | 2.4286 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.58861 | -0.58861 |  | 24 | SS-35/10kv Pyatnitskoe | 4 | 0.71037 | 3.139 | 1.84 | 80 | 1.299 | 0 | 1.84 | -1.299 | -1.299
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0.463 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.213 | 1.213 |  | 25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0 | 0.463 | 1.676 | 80 | -1.213 | 0 | 1.676 | 1.213 | 1.213
26 | SS-35/10kv Svistovka | 2.5 | 0.64045 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.04675 | 0.04675 |  | 26 | SS-35/10kv Svistovka | 2.5 | 0 | 0.64045 | 0.6872 | 45 | -0.04675 | 0 | 0.6872 | 0.04675 | 0.04675
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0.54595 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.17785 | 0.17785 |  | 27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0 | 0.54595 | 0.7238 | 120 | -0.17785 | 0 | 0.7238 | 0.17785 | 0.17785
28 | SS-35/10kv Kharkovskoe | 2.5 | 0.4473 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.2324 | 0.2324 |  | 28 | SS-35/10kv Kharkovskoe | 2.5 | 0 | 0.4473 | 0.6797 | 120 | -0.2324 | 0 | 0.6797 | 0.2324 | 0.2324
29 | SS-35/10kv Tserkovnaya | 2.5 | 1.1275 | 1 | 80 | 1 | 0 | 1 | -0.12755 | -0.12755 |  | 29 | SS-35/10kv Tserkovnaya | 2.5 | 0.18 | 1.3075 | 1 | 80 | 0.30755 | 0 | 1 | -0.30755 | -0.30755
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 9.9792 | 3.561 | 45 | 6.4182 | 0 | 16.8 | 10.3818 | 10.3818 |  | 30 | SS-110/6kv Automobile maintenance plant | 16+16 | 0.12075 | 10.1 | 3.561 | 45 | 6.539 | 0 | 16.8 | 10.261 | 10.261
31 | SS-110/35/10kv Aydar | 16+10 | 8.4408 | 8.95 | 120 | -0.50918 | 0 | 10.5 | 11.0092 | 10.5 |  | 31 | SS-110/35/10kv Aydar | 16+10 | 0.25 | 8.6908 | 8.95 | 120 | -0.25918 | 0 | 10.5 | 10.7592 | 10.5
| Sн. MV, МVА | 16+10 | 7.29 | 7.29 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 7.29 | 7.29 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 16+10 | 1.1508 | 1.66 |  | -0.50918 | 0 | 10.5 | 11.0092 |  |  |  | Sн. LV, МVА | 16+10 | 0.25 | 1.4008 | 1.66 |  | -0.25918 | 0 | 10.5 | 10.7592
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12.534 | 8.37 | 80 | 4.164 | 0 | 16.8 | 12.636 | 12.636 |  | 32 | SS-110/35/10kv Alexandrovka | 16+16 | 0.2742 | 12.8082 | 8.37 | 80 | 4.4382 | 0 | 16.8 | 12.3618 | 12.3618
| Sн. MV, МVА | 16+16 | 6.697 | 6.697 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 6.697 | 6.697 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 5.837 | 1.673 |  | 4.164 | 0 | 16.8 | 12.636 |  |  |  | Sн. LV, МVА | 16+16 | 0.2742 | 6.1112 | 1.673 |  | 4.4382 | 0 | 16.8 | 12.3618
33 | SS-110/35/10kv Alexeevka | 25+16+25 | 44.0632 | 5.322 | 120 | 38.7412 | 0 | 43.05 | 4.3088 | 4.3088 |  | 33 | SS-110/35/10kv Alexeevka | 25+16+25 | 1.6552 | 45.7184 | 5.322 | 120 | 40.3964 | 0 | 43.05 | 2.6536 | 2.6536
| Sн. MV, МVА | 25+16+25 | 19.821 | 3.102 |  | 16.719 | 0 | 43.05 | 26.331 |  |  |  | Sн. MV, МVА | 25+16+25 | 0 | 19.821 | 3.102 |  | 16.719 | 0 | 43.05 | 26.331
| Sн. LV, МVА | 25+16+25 | 24.2422 | 2.22 |  | 22.0222 | 0 | 43.05 | 21.0278 |  |  |  | Sн. LV, МVА | 25+16+25 | 1.6552 | 25.8974 | 2.22 |  | 23.6774 | 0 | 43.05 | 19.3726
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 9.383 | 8.87 | 45 | 0.513 | 0 | 10.5 | 9.987 | 9.984 |  | 34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 0 | 9.383 | 8.87 | 45 | 0.513 | 0 | 10.5 | 9.987 | 9.984
| Sн. MV, МVА | 10+16 | 8.867 | 8.867 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 8.867 | 8.867 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+16 | 0.516 | 0 |  | 0.516 | 0 | 10.5 | 9.984 |  |  |  | Sн. LV, МVА | 10+16 | 0 | 0.516 | 0 |  | 0.516 | 0 | 10.5 | 9.984
35 | SS-110/6kv Belgorod-1 | 40+48 | 44.5181 | 0 | 120 | 44.5181 | 0 | 42 | -2.5181 | -2.5181 |  | 35 | SS-110/6kv Belgorod-1 | 40+48 | 5.4077 | 49.9258 | 0 | 120 | 49.9258 | 0 | 42 | -7.9258 | -7.9258
36 | SS-110/35/10kv Borisovka | 16+16 | 14.4143 | 11.433 | 120 | 2.9813 | 0 | 16.8 | 13.8187 | 5.4187 |  | 36 | SS-110/35/10kv Borisovka | 16+16 | 0.129 | 14.5433 | 11.433 | 120 | 3.1103 | 0 | 16.8 | 13.6897 | 5.2897
| Sн. MV, МVА | 16+8 | 8.133 | 8.133 |  | 0 | 0 | 8.4 | 8.4 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 8.133 | 8.133 |  | 0 | 0 | 8.4 | 8.4
| Sн. LV, МVА | 16+8 | 6.2813 | 3.3 |  | 2.9813 | 0 | 8.4 | 5.4187 |  |  |  | Sн. LV, МVА | 16+8 | 0.129 | 6.4103 | 3.3 |  | 3.1103 | 0 | 8.4 | 5.2897
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9.036 | 11.5 | 120 | -2.464 | 0 | 10.5 | 12.964 | 10.532 |  | 37 | SS-110/35/10kv V.Pokrovka | 10+10 | 0.03 | 9.066 | 11.5 | 120 | -2.434 | 0 | 10.5 | 12.934 | 10.532
| Sн. MV, МVА | 10+10 | 7.768 | 7.8 |  | -0.032 | 0 | 10.5 | 10.532 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 7.768 | 7.8 |  | -0.032 | 0 | 10.5 | 10.532
| Sн. LV, МVА | 10+10 | 1.268 | 3.7 |  | -2.432 | 0 | 10.5 | 12.932 |  |  |  | Sн. LV, МVА | 10+10 | 0.03 | 1.298 | 3.7 |  | -2.402 | 0 | 10.5 | 12.902
38 | SS-110/35/10kv Veydelevka | 10+10 | 7.9503 | 8.83 | 120 | -0.8797 | 0 | 10.5 | 11.3797 | 10.5 |  | 38 | SS-110/35/10kv Veydelevka | 10+10 | 0.257 | 8.2073 | 8.83 | 120 | -0.6227 | 0 | 10.5 | 11.1227 | 10.5
| Sн. MV, МVА | 10+10 | 3.955 | 3.955 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 3.955 | 3.955 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+10 | 3.9953 | 4.875 |  | -0.8797 | 0 | 10.5 | 11.3797 |  |  |  | Sн. LV, МVА | 10+10 | 0.257 | 4.2523 | 4.875 |  | -0.6227 | 0 | 10.5 | 11.1227
39 | SS-110/6kv Vitamin plant | 25+25 | 11.7863 | 1.46 | 45 | 10.3263 | 0 | 26.25 | 15.9237 | 15.9237 |  | 39 | SS-110/6kv Vitamin plant | 25+25 | 0.772 | 12.5583 | 1.46 | 45 | 11.0983 | 0 | 26.25 | 15.1517 | 15.1517
40 | SS-110/35/10kv Volokonovka | 25+25 | 15.9084 | 10.651 | 120 | 5.2574 | 0 | 26.25 | 20.9926 | 20.9926 |  | 40 | SS-110/35/10kv Volokonovka | 25+25 | 3.499 | 19.4074 | 10.651 | 120 | 8.7564 | 0 | 26.25 | 17.4936 | 17.4936
| Sн. MV, МVА | 25+25 | 8.576 | 8.576 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 8.576 | 8.576 |  | 0 | 0 | 26.25 | 26.25
| Sн. LV, МVА | 25+25 | 7.3324 | 2.075 |  | 5.2574 | 0 | 26.25 | 20.9926 |  |  |  | Sн. LV, МVА | 25+25 | 3.499 | 10.8314 | 2.075 |  | 8.7564 | 0 | 26.25 | 17.4936
41 | SS-110/35/6kv Vostochnaya | 25+25 | 41.987 | 25.07 | 120 | 16.917 | 0 | 26.25 | 9.333 | 7.447 |  | 41 | SS-110/35/6kv Vostochnaya | 25+25 | 1.4211 | 43.4081 | 25.07 | 120 | 18.3381 | 0 | 26.25 | 7.9119 | 6.0259
| Sн. MV, МVА | 25+25 | 19.414 | 21.3 |  | -1.886 | 0 | 26.25 | 28.136 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 19.414 | 21.3 |  | -1.886 | 0 | 26.25 | 28.136
| Sн. LV, МVА | 25+25 | 22.573 | 3.77 |  | 18.803 | 0 | 26.25 | 7.447 |  |  |  | Sн. LV, МVА | 25+25 | 1.4211 | 23.9941 | 3.77 |  | 20.2241 | 0 | 26.25 | 6.0259
42 | SS-110/10/6kv Golofeevka | 25+25 | 1.8481 | 0 |  | 1.8481 | 0 | 26.25 | 24.4019 | 11.277 |  | 42 | SS-110/10/6kv Golofeevka | 25+25 | 0 | 1.8481 | 0 |  | 1.8481 | 0 | 26.25 | 24.4019 | 11.277
| Sн. MV, МVА | 12,5+12,5 | 1.848 | 0 |  | 1.848 | 0 | 13.125 | 11.277 |  |  |  | Sн. MV, МVА | 12,5+12,5 | 0 | 1.848 | 0 |  | 1.848 | 0 | 13.125 | 11.277
| Sн. LV, МVА | 12,5+12,5 | 6.5362e-05 | 0 |  | 6.5362e-05 | 0 | 13.125 | 13.1249 |  |  |  | Sн. LV, МVА | 12,5+12,5 | 0 | 6.5362e-05 | 0 |  | 6.5362e-05 | 0 | 13.125 | 13.1249
43 | SS-110/10kv Gotnya | 16+16 | 8.9986 | 6.43 | 120 | 2.5686 | 0 | 16.8 | 14.2314 | 14.2314 |  | 43 | SS-110/10kv Gotnya | 16+16 | 0.182 | 9.1806 | 6.43 | 120 | 2.7506 | 0 | 16.8 | 14.0494 | 14.0494
44 | SS-110/35/10kv Grayvoron | 16+16 | 15.2094 | 13.953 | 80 | 1.2564 | 0 | 16.8 | 15.5436 | 15.5436 |  | 44 | SS-110/35/10kv Grayvoron | 16+16 | 0.1699 | 15.3793 | 13.953 | 80 | 1.4263 | 0 | 16.8 | 15.3737 | 15.3737
| Sн. MV, МVА | 16+25 | 10.903 | 10.903 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+25 | 0 | 10.903 | 10.903 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+25 | 4.3064 | 3.05 |  | 1.2564 | 0 | 16.8 | 15.5436 |  |  |  | Sн. LV, МVА | 16+25 | 0.1699 | 4.4763 | 3.05 |  | 1.4263 | 0 | 16.8 | 15.3737
45 | SS-110/6kv Donets | 40+40 | 26.0404 | 6.73 | 120 | 19.3104 | 0 | 42 | 22.6896 | 22.6896 |  | 45 | SS-110/6kv Donets | 40+40 | 2.3367 | 28.3771 | 6.73 | 120 | 21.6471 | 0 | 42 | 20.3529 | 20.3529
46 | SS-110/10kv Dubovoe | 40+40 | 22.9597 | 11.23 | 120 | 11.7297 | 0 | 42 | 30.2703 | 30.2703 |  | 46 | SS-110/10kv Dubovoe | 40+40 | 10.7255 | 33.6852 | 11.23 | 120 | 22.4552 | 0 | 42 | 19.5448 | 19.5448
47 | SS-110/35/6kv Zhuravliki | 40+25 | 13.1662 | 12.4 | 120 | 0.76617 | 0 | 42 | 41.2338 | 41.2338 |  | 47 | SS-110/35/6kv Zhuravliki | 40+25 | 0.1736 | 13.3398 | 12.4 | 120 | 0.93977 | 0 | 42 | 41.0602 | 41.0602
| Sн. MV, МVА | 40+25 | 6.227 | 6.227 |  | 0 | 0 | 42 | 42 |  |  |  | Sн. MV, МVА | 40+25 | 0 | 6.227 | 6.227 |  | 0 | 0 | 42 | 42
| Sн. LV, МVА | 40+25 | 6.9392 | 6.173 |  | 0.76617 | 0 | 42 | 41.2338 |  |  |  | Sн. LV, МVА | 40+25 | 0.1736 | 7.1128 | 6.173 |  | 0.93977 | 0 | 42 | 41.0602
48 | SS-110/10kv Zapadnaya | 16+16 | 16.9475 | 1.249 | 80 | 15.6985 | 0 | 16.8 | 1.1015 | 1.1015 |  | 48 | SS-110/10kv Zapadnaya | 16+16 | 3.5025 | 20.45 | 1.249 | 80 | 19.201 | 0 | 16.8 | -2.401 | -2.401
49 | SS-110/35/10kv Ivnya | 10+10 | 6.018 | 6.16 | 80 | -0.14205 | 0 | 10.5 | 10.642 | 10.5 |  | 49 | SS-110/35/10kv Ivnya | 10+10 | 0.196 | 6.214 | 6.16 | 80 | 0.053952 | 0 | 10.5 | 10.446 | 10.446
| Sн. MV, МVА | 10+10 | 2.375 | 2.375 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.375 | 2.375 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+10 | 3.643 | 3.785 |  | -0.14205 | 0 | 10.5 | 10.642 |  |  |  | Sн. LV, МVА | 10+10 | 0.196 | 3.839 | 3.785 |  | 0.053952 | 0 | 10.5 | 10.446
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 11.3866 | 7.7116 | 120 | 3.675 | 0 | 16.8 | 13.125 | 13.125 |  | 50 | SS-110/35/10kv K.Gvardiya | 16+16 | 0.179 | 11.5656 | 7.7116 | 120 | 3.854 | 0 | 16.8 | 12.946 | 12.946
| Sн. MV, МVА | 16+16 | 4.854 | 4.854 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.854 | 4.854 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 6.5326 | 2.8576 |  | 3.675 | 0 | 16.8 | 13.125 |  |  |  | Sн. LV, МVА | 16+16 | 0.179 | 6.7116 | 2.8576 |  | 3.854 | 0 | 16.8 | 12.946
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 11.6977 | 9.65 | 80 | 2.0477 | 0 | 26.25 | 24.2023 | 19.9363 |  | 51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 0.07 | 11.7677 | 9.65 | 80 | 2.1177 | 0 | 26.25 | 24.1323 | 19.8663
| Sн. MV, МVА | 25+25 | 1.384 | 1.384 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 1.384 | 1.384 |  | 0 | 0 | 26.25 | 26.25
| Sн. LV, МVА | 25+25 | 10.3137 | 4 |  | 6.3137 | 0 | 26.25 | 19.9363 |  |  |  | Sн. LV, МVА | 25+25 | 0.07 | 10.3837 | 4 |  | 6.3837 | 0 | 26.25 | 19.8663
52 | SS-110/35/10kv Korocha | 16+10+16 | 18.4946 | 2.019 | 20 | 16.4756 | 0 | 27.3 | 10.8244 | 10.8244 |  | 52 | SS-110/35/10kv Korocha | 16+10+16 | 0.3373 | 18.8319 | 2.019 | 20 | 16.8129 | 0 | 27.3 | 10.4871 | 10.4871
| Sн. MV, МVА | 16+10+16 | 7.286 | 1.719 |  | 5.567 | 0 | 27.3 | 21.733 |  |  |  | Sн. MV, МVА | 16+10+16 | 0 | 7.286 | 1.719 |  | 5.567 | 0 | 27.3 | 21.733
| Sн. LV, МVА | 16+10+16 | 11.2086 | 0.3 |  | 10.9086 | 0 | 27.3 | 16.3914 |  |  |  | Sн. LV, МVА | 16+10+16 | 0.3373 | 11.5459 | 0.3 |  | 11.2459 | 0 | 27.3 | 16.0541
53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 10.8277 | 9.158 | 120 | 1.6697 | 0 | 10.5 | 8.8303 | 8.826 |  | 53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 1.3161 | 12.1438 | 9.158 | 120 | 2.9858 | 0 | 10.5 | 7.5142 | 7.5142
| Sн. MV, МVА | 10+10 | 5.194 | 3.52 |  | 1.674 | 0 | 10.5 | 8.826 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.194 | 3.52 |  | 1.674 | 0 | 10.5 | 8.826
| Sн. LV, МVА | 10+10 | 5.6337 | 5.638 |  | -0.004347 | 0 | 10.5 | 10.5043 |  |  |  | Sн. LV, МVА | 10+10 | 1.3161 | 6.9498 | 5.638 |  | 1.3118 | 0 | 10.5 | 9.1882
54 | SS-110/35/10kv Maximovka | 16+16 | 10.7359 | 11.48 | 45 | -0.7441 | 0 | 16.8 | 17.5441 | 16.8 |  | 54 | SS-110/35/10kv Maximovka | 16+16 | 0.12 | 10.8559 | 11.48 | 45 | -0.6241 | 0 | 16.8 | 17.4241 | 16.8
| Sн. MV, МVА | 16+16 | 9.449 | 9.449 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 9.449 | 9.449 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 1.2869 | 2.031 |  | -0.7441 | 0 | 16.8 | 17.5441 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 1.2869 | 2.031 |  | -0.7441 | 0 | 16.8 | 17.5441
55 | SS-110/35/10kv N.Oskol | 25+31,5 | 19.8083 | 9.119 | 80 | 10.6893 | 0 | 26.25 | 15.5607 | 14.7647 |  | 55 | SS-110/35/10kv N.Oskol | 25+31,5 | 3.6349 | 23.4432 | 9.119 | 80 | 14.3242 | 0 | 26.25 | 11.9258 | 11.1298
| Sн. MV, МVА | 25+31,5 | 7.034 | 7.83 |  | -0.796 | 0 | 26.25 | 27.046 |  |  |  | Sн. MV, МVА | 25+31,5 | 0 | 7.034 | 7.83 |  | -0.796 | 0 | 26.25 | 27.046
| Sн. LV, МVА | 25+31,5 | 12.7743 | 1.289 |  | 11.4853 | 0 | 26.25 | 14.7647 |  |  |  | Sн. LV, МVА | 25+31,5 | 3.6349 | 16.4092 | 1.289 |  | 15.1202 | 0 | 26.25 | 11.1298
56 | SS-110/10kv Obukhovskaya | 25+25 | 2.351 | 0 |  | 2.351 | 0 | 26.25 | 23.899 | 23.899 |  | 56 | SS-110/10kv Obukhovskaya | 25+25 | 0.01 | 2.361 | 0 |  | 2.361 | 0 | 26.25 | 23.889 | 23.889
57 | SS-110/6kv Ochistnye | 16+16 | 6.5595 | 0 |  | 6.5595 | 0 | 16.8 | 10.2405 | 10.2405 |  | 57 | SS-110/6kv Ochistnye | 16+16 | 0.09 | 6.6495 | 0 |  | 6.6495 | 0 | 16.8 | 10.1505 | 10.1505
58 | SS-110/10kv Promyshlennaya | 25+25 | 14.983 | 0 |  | 14.983 | 0 | 26.25 | 11.267 | 11.267 |  | 58 | SS-110/10kv Promyshlennaya | 25+25 | 3.3163 | 18.2993 | 0 |  | 18.2993 | 0 | 26.25 | 7.9507 | 7.9507
59 | SS-110/10kv Poultry plant | 16+16 | 10.559 | 1.296 | 80 | 9.263 | 0 | 16.8 | 7.537 | 7.537 |  | 59 | SS-110/10kv Poultry plant | 16+16 | 3.06 | 13.619 | 1.296 | 80 | 12.323 | 0 | 16.8 | 4.477 | 4.477
60 | SS-110/10kv Pushkarnaya | 40+40 | 27.735 | 0 | 60 | 27.735 | 0 | 42 | 14.265 | 14.265 |  | 60 | SS-110/10kv Pushkarnaya | 40+40 | 2.708 | 30.443 | 0 | 60 | 30.443 | 0 | 42 | 11.557 | 11.557
61 | SS-110/35/10kv Rakitnoe | 10+10 | 9.2018 | 8.98 | 120 | 0.22184 | 0 | 10.5 | 10.2782 | 10.2782 |  | 61 | SS-110/35/10kv Rakitnoe | 10+10 | 0.2902 | 9.492 | 8.98 | 120 | 0.51204 | 0 | 10.5 | 9.988 | 9.988
| Sн. MV, МVА | 10+10 | 6.407 | 6.407 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 6.407 | 6.407 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+10 | 2.7948 | 2.573 |  | 0.22184 | 0 | 10.5 | 10.2782 |  |  |  | Sн. LV, МVА | 10+10 | 0.2902 | 3.085 | 2.573 |  | 0.51204 | 0 | 10.5 | 9.988
62 | SS-110/35/6kv Rudnik | 25+25 | 14.117 | 10.46 | 45 | 3.657 | 0 | 26.25 | 22.593 | 21.474 |  | 62 | SS-110/35/6kv Rudnik | 25+25 | 8.384 | 22.501 | 10.46 | 45 | 12.041 | 0 | 26.25 | 14.209 | 13.09
| Sн. MV, МVА | 25+25 | 9.341 | 10.46 |  | -1.119 | 0 | 26.25 | 27.369 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 9.341 | 10.46 |  | -1.119 | 0 | 26.25 | 27.369
| Sн. LV, МVА | 25+25 | 4.776 | 0 |  | 4.776 | 0 | 26.25 | 21.474 |  |  |  | Sн. LV, МVА | 25+25 | 8.384 | 13.16 | 0 |  | 13.16 | 0 | 26.25 | 13.09
63 | SS-110/10kv Severnaya | 40+40 | 11.1616 | 3.312 | 45 | 7.8496 | 0 | 42 | 34.1504 | 34.1504 |  | 63 | SS-110/10kv Severnaya | 40+40 | 12.2199 | 23.3815 | 3.312 | 45 | 20.0695 | 0 | 42 | 21.9305 | 21.9305
64 | SS-110/35/10kv Skorodnoe | 16+16 | 11.5224 | 10.36 | 120 | 1.1624 | 0 | 16.8 | 15.6376 | 15.6376 |  | 64 | SS-110/35/10kv Skorodnoe | 16+16 | 0.069 | 11.5914 | 10.36 | 120 | 1.2314 | 0 | 16.8 | 15.5686 | 15.5686
| Sн. MV, МVА | 16+16 | 7.562 | 7.562 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.562 | 7.562 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 3.9604 | 2.798 |  | 1.1624 | 0 | 16.8 | 15.6376 |  |  |  | Sн. LV, МVА | 16+16 | 0.069 | 4.0294 | 2.798 |  | 1.2314 | 0 | 16.8 | 15.5686
65 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 28.8772 | 0 |  | 28.8772 | 0 | 47.25 | 18.3728 | 18.3728 |  | 65 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 0.31391 | 29.1911 | 0 |  | 29.1911 | 0 | 47.25 | 18.0589 | 18.0589
| Sн. MV, МVА | 20+25+25 | 6.331 | 0 |  | 6.331 | 0 | 47.25 | 40.919 |  |  |  | Sн. MV, МVА | 20+25+25 | 0 | 6.331 | 0 |  | 6.331 | 0 | 47.25 | 40.919
| Sн. LV, МVА | 20+25+25 | 22.5462 | 0 |  | 22.5462 | 0 | 47.25 | 24.7038 |  |  |  | Sн. LV, МVА | 20+25+25 | 0.31391 | 22.8601 | 0 |  | 22.8601 | 0 | 47.25 | 24.3899
66 | SS-110/35/10kv Streletskaya | 16+16 | 4.2243 | 2.23 | 80 | 1.9943 | 0 | 16.8 | 14.8057 | 6.4057 |  | 66 | SS-110/35/10kv Streletskaya | 16+16 | 0.225 | 4.4493 | 2.23 | 80 | 2.2193 | 0 | 16.8 | 14.5807 | 6.1807
| Sн. MV, МVА | 16+8 | 0 | 0 |  | 0 | 0 | 8.4 | 8.4 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 0 | 0 |  | 0 | 0 | 8.4 | 8.4
| Sн. LV, МVА | 16+8 | 4.2243 | 2.23 |  | 1.9943 | 0 | 8.4 | 6.4057 |  |  |  | Sн. LV, МVА | 16+8 | 0.225 | 4.4493 | 2.23 |  | 2.2193 | 0 | 8.4 | 6.1807
67 | SS-110/6kv Stroitel | 15+15 | 13.298 | 0 |  | 13.298 | 0 | 15.75 | 2.452 | 2.452 |  | 67 | SS-110/6kv Stroitel | 15+15 | 1.1361 | 14.4341 | 0 |  | 14.4341 | 0 | 15.75 | 1.3159 | 1.3159
68 | SS-110/35/10kv Tomarovka | 16+16 | 12.5522 | 3.46 | 45 | 9.0922 | 0 | 16.8 | 7.7078 | 7.7078 |  | 68 | SS-110/35/10kv Tomarovka | 16+16 | 0.414 | 12.9662 | 3.46 | 45 | 9.5062 | 0 | 16.8 | 7.2938 | 7.2938
| Sн. MV, МVА | 16+16 | 4.379 | 3.46 |  | 0.919 | 0 | 16.8 | 15.881 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.379 | 3.46 |  | 0.919 | 0 | 16.8 | 15.881
| Sн. LV, МVА | 16+16 | 8.1732 | 0 |  | 8.1732 | 0 | 16.8 | 8.6268 |  |  |  | Sн. LV, МVА | 16+16 | 0.414 | 8.5872 | 0 |  | 8.5872 | 0 | 16.8 | 8.2128
69 | SS-110/6kv Chemical plant | 32+32 | 10.0162 | 5.56 | 45 | 4.4562 | 0 | 33.6 | 29.1438 | 29.1438 |  | 69 | SS-110/6kv Chemical plant | 32+32 | 0.089 | 10.1052 | 5.56 | 45 | 4.5452 | 0 | 33.6 | 29.0548 | 29.0548
70 | SS-110/10kv Tsentralnaya | 40+40 | 22.8863 | 0 |  | 22.8863 | 0 | 42 | 19.1137 | 19.1137 |  | 70 | SS-110/10kv Tsentralnaya | 40+40 | 1.6445 | 24.5308 | 0 |  | 24.5308 | 0 | 42 | 17.4692 | 17.4692
71 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23.7143 | 20.54 | 80 | 3.1743 | 0 | 26.25 | 23.0757 | 23.0757 |  | 71 | SS-110/35/10kv Cheremoshnoe | 25+25 | 0.3615 | 24.0758 | 20.54 | 80 | 3.5358 | 0 | 26.25 | 22.7142 | 22.7142
| Sн. MV, МVА | 25+25 | 22.176 | 19.676 |  | 2.5 | 0 | 26.25 | 23.75 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 22.176 | 19.676 |  | 2.5 | 0 | 26.25 | 23.75
| Sн. LV, МVА | 25+25 | 1.5383 | 0 |  | 1.5383 | 0 | 26.25 | 24.7117 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 1.5383 | 0 |  | 1.5383 | 0 | 26.25 | 24.7117
72 | SS-110/35/10kv Chernyanka | 16+25 | 14.7605 | 5.969 | 120 | 8.7915 | 0 | 16.8 | 8.0085 | 8.0085 |  | 72 | SS-110/35/10kv Chernyanka | 16+25 | 0.7993 | 15.5598 | 5.969 | 120 | 9.5908 | 0 | 16.8 | 7.2092 | 7.2092
| Sн. MV, МVА | 16+25 | 5.969 | 5.969 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+25 | 0 | 5.969 | 5.969 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+25 | 8.7915 | 0 |  | 8.7915 | 0 | 16.8 | 8.0085 |  |  |  | Sн. LV, МVА | 16+25 | 0.7993 | 9.5908 | 0 |  | 9.5908 | 0 | 16.8 | 7.2092
73 | SS-110/35/6kv Shebekino | 40+40 | 25.5429 | 16.65 | 120 | 8.8929 | 0 | 42 | 33.1071 | 33.1071 |  | 73 | SS-110/35/6kv Shebekino | 40+40 | 0.93043 | 26.4734 | 16.65 | 120 | 9.8234 | 0 | 42 | 32.1766 | 32.1766
| Sн. MV, МVА | 40+40 | 14.582 | 11.682 |  | 2.9 | 0 | 42 | 39.1 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 14.582 | 11.682 |  | 2.9 | 0 | 42 | 39.1
| Sн. LV, МVА | 40+40 | 10.9609 | 4.968 |  | 5.9929 | 0 | 42 | 36.0071 |  |  |  | Sн. LV, МVА | 40+40 | 0.93043 | 11.8914 | 4.968 |  | 6.9234 | 0 | 42 | 35.0766
74 | SS-110/10kv Sheino | 3,2+10 | 2.4086 | 0 |  | 2.4086 | 0 | 3.36 | 0.95136 | 0.95136 |  | 74 | SS-110/10kv Sheino | 3,2+10 | 0.215 | 2.6236 | 0 |  | 2.6236 | 0 | 3.36 | 0.73636 | 0.73636
75 | SS-110/10/6kv Yuzhnaya | 40+40 | 43.0909 | 12.94 | 120 | 30.1509 | 0 | 42 | 11.8491 | 11.8491 |  | 75 | SS-110/10/6kv Yuzhnaya | 40+40 | 3.7444 | 46.8353 | 12.94 | 120 | 33.8953 | 0 | 42 | 8.1047 | 8.1047
| Sн. MV, МVА | 40+40 | 6.8549 | 3.42 |  | 3.4349 | 0 | 42 | 38.5651 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 6.8549 | 3.42 |  | 3.4349 | 0 | 42 | 38.5651
| Sн. LV, МVА | 40+40 | 36.236 | 9.52 |  | 26.716 | 0 | 42 | 15.284 |  |  |  | Sн. LV, МVА | 40+40 | 3.7444 | 39.9804 | 9.52 |  | 30.4604 | 0 | 42 | 11.5396
76 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0.68343 | 0.43267 | 120 | 0.25076 | 0 | 2.625 | 2.3742 | 2.3742 |  | 76 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0.01 | 0.69343 | 0.43267 | 120 | 0.26076 | 0 | 2.625 | 2.3642 | 2.3642
77 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 0.85294 | 0.46639 | 120 | 0.38655 | 0 | 2.625 | 2.2384 | 2.2384 |  | 77 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 2.15 | 3.0029 | 0.46639 | 120 | 2.5366 | 0 | 2.625 | 0.088446 | 0.088446
78 | SS-35/10kv Alexeevka (kor.) | 4+4 | 2.7122 | 0 |  | 2.7122 | 0 | 4.2 | 1.4878 | 1.4878 |  | 78 | SS-35/10kv Alexeevka (kor.) | 4+4 | 0.22178 | 2.934 | 0 |  | 2.934 | 0 | 4.2 | 1.266 | 1.266
79 | SS-35/10kv Annovka | 2,5+2,5 | 0.82901 | 0.44652 | 80 | 0.38249 | 0 | 2.625 | 2.2425 | 2.2425 |  | 79 | SS-35/10kv Annovka | 2,5+2,5 | 0.0115 | 0.84051 | 0.44652 | 80 | 0.39399 | 0 | 2.625 | 2.231 | 2.231
80 | SS-35/10kv Artelnoe | 6,3+6,3 | 6.0242 | 0.55 | 45 | 5.4742 | 0 | 6.615 | 1.1408 | 1.1408 |  | 80 | SS-35/10kv Artelnoe | 6,3+6,3 | 0.03 | 6.0542 | 0.55 | 45 | 5.5042 | 0 | 6.615 | 1.1108 | 1.1108
81 | SS-35/10kv B.Dvory | 4+4 | 2.4199 | 1.191 | 120 | 1.2289 | 0 | 4.2 | 2.9711 | 2.9711 |  | 81 | SS-35/10kv B.Dvory | 4+4 | 0.084 | 2.5039 | 1.191 | 120 | 1.3129 | 0 | 4.2 | 2.8871 | 2.8871
82 | SS-35/10kv B.Ivanovka | 4+4 | 0.98132 | 0.62488 | 80 | 0.35644 | 0 | 4.2 | 3.8436 | 3.8436 |  | 82 | SS-35/10kv B.Ivanovka | 4+4 | 0.022 | 1.0033 | 0.62488 | 80 | 0.37844 | 0 | 4.2 | 3.8216 | 3.8216
83 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0.71309 | 0.44779 | 45 | 0.2653 | 0 | 2.625 | 2.3597 | 2.3597 |  | 83 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0 | 0.71309 | 0.44779 | 45 | 0.2653 | 0 | 2.625 | 2.3597 | 2.3597
84 | SS-35/10kv B.Ples | 2,5+2,5 | 0.68493 | 0.606 | 45 | 0.078931 | 0 | 2.625 | 2.5461 | 2.5461 |  | 84 | SS-35/10kv B.Ples | 2,5+2,5 | 0 | 0.68493 | 0.606 | 45 | 0.078931 | 0 | 2.625 | 2.5461 | 2.5461
85 | SS-35/10kv B.Troitsa | 6,3+6,3 | 4.2829 | 2.83 | 45 | 1.4529 | 0 | 6.615 | 5.1621 | 5.1621 |  | 85 | SS-35/10kv B.Troitsa | 6,3+6,3 | 0.529 | 4.8119 | 2.83 | 45 | 1.9819 | 0 | 6.615 | 4.6331 | 4.6331
86 | SS-35/10kv Belovskoe | 4+4 | 3.6674 | 1.21 | 80 | 2.4574 | 0 | 4.2 | 1.7426 | 1.7426 |  | 86 | SS-35/10kv Belovskoe | 4+4 | 1.0175 | 4.6849 | 1.21 | 80 | 3.4749 | 0 | 4.2 | 0.72513 | 0.72513
87 | SS-35/10kv Belyanka | 2,5+4 | 2.1233 | 1.3214 | 45 | 0.80191 | 0 | 2.625 | 1.8231 | 1.8231 |  | 87 | SS-35/10kv Belyanka | 2,5+4 | 0.139 | 2.2623 | 1.3214 | 45 | 0.94091 | 0 | 2.625 | 1.6841 | 1.6841
88 | SS-35/10kv Bessonovka | 6,3+6,3 | 6.1466 | 0.918 | 120 | 5.2286 | 0 | 6.615 | 1.3864 | 1.3864 |  | 88 | SS-35/10kv Bessonovka | 6,3+6,3 | 0.01 | 6.1566 | 0.918 | 120 | 5.2386 | 0 | 6.615 | 1.3764 | 1.3764
89 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.89313 | 0.522 | 45 | 0.37113 | 0 | 1.68 | 1.3089 | 1.3089 |  | 89 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.033 | 0.92613 | 0.522 | 45 | 0.40413 | 0 | 1.68 | 1.2759 | 1.2759
90 | SS-35/10kv V.Mikhailovka | 4+4 | 2.3356 | 1.45 | 80 | 0.88559 | 0 | 4.2 | 3.3144 | 3.3144 |  | 90 | SS-35/10kv V.Mikhailovka | 4+4 | 0.022 | 2.3576 | 1.45 | 80 | 0.90759 | 0 | 4.2 | 3.2924 | 3.2924
91 | SS-35/10kv Varvarovka | 2,5+2,5 | 1.8017 | 1.0795 | 120 | 0.7222 | 0 | 2.625 | 1.9028 | 1.9028 |  | 91 | SS-35/10kv Varvarovka | 2,5+2,5 | 0.1 | 1.9017 | 1.0795 | 120 | 0.8222 | 0 | 2.625 | 1.8028 | 1.8028
92 | SS-35/10kv Vengerovka | 2,5+2,5 | 1.0438 | 0.4 | 120 | 0.64378 | 0 | 2.625 | 1.9812 | 1.9812 |  | 92 | SS-35/10kv Vengerovka | 2,5+2,5 | 0.015 | 1.0588 | 0.4 | 120 | 0.65878 | 0 | 2.625 | 1.9662 | 1.9662
93 | SS-35/10kv Verkhopenye | 2,5+4 | 1.6176 | 1.0177 | 45 | 0.59993 | 0 | 2.625 | 2.0251 | 2.0251 |  | 93 | SS-35/10kv Verkhopenye | 2,5+4 | 0.015 | 1.6326 | 1.0177 | 45 | 0.61493 | 0 | 2.625 | 2.0101 | 2.0101
94 | SS-35/10kv Viktoropol | 2,5+4 | 1.2991 | 0.95536 | 120 | 0.34378 | 0 | 2.625 | 2.2812 | 2.2812 |  | 94 | SS-35/10kv Viktoropol | 2,5+4 | 0.01 | 1.3091 | 0.95536 | 120 | 0.35378 | 0 | 2.625 | 2.2712 | 2.2712
95 | SS-35/10kv Vislaya Dubrava | 4+4 | 2.5729 | 0.616 | 80 | 1.9569 | 0 | 4.2 | 2.2431 | 2.2431 |  | 95 | SS-35/10kv Vislaya Dubrava | 4+4 | 0 | 2.5729 | 0.616 | 80 | 1.9569 | 0 | 4.2 | 2.2431 | 2.2431
96 | SS-35/10kv Vladimirovka | 4+4 | 0.82947 | 0 |  | 0.82947 | 0 | 4.2 | 3.3705 | 3.3705 |  | 96 | SS-35/10kv Vladimirovka | 4+4 | 0.0045 | 0.83397 | 0 |  | 0.83397 | 0 | 4.2 | 3.366 | 3.366
97 | SS-35/10kv Water storage | 4+6,3 | 2.3374 | 0.305 | 45 | 2.0324 | 0 | 4.2 | 2.1676 | 2.1676 |  | 97 | SS-35/10kv Water storage | 4+6,3 | 0.055 | 2.3924 | 0.305 | 45 | 2.0874 | 0 | 4.2 | 2.1126 | 2.1126
98 | SS-35/6kv Vostochnaya | 4+4 | 3.8357 | 1.43 | 120 | 2.4057 | 0 | 4.2 | 1.7943 | 1.7943 |  | 98 | SS-35/6kv Vostochnaya | 4+4 | 0.18 | 4.0157 | 1.43 | 120 | 2.5857 | 0 | 4.2 | 1.6143 | 1.6143
99 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1.7363 | 0.99513 | 120 | 0.7412 | 0 | 2.625 | 1.8838 | 1.8838 |  | 99 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 0.01 | 1.7463 | 0.99513 | 120 | 0.7512 | 0 | 2.625 | 1.8738 | 1.8738
100 | SS-35/10kv Glinnoe | 6,3+6,3 | 2.3586 | 1.4036 | 80 | 0.95502 | 0 | 6.615 | 5.66 | 5.66 |  | 100 | SS-35/10kv Glinnoe | 6,3+6,3 | 0 | 2.3586 | 1.4036 | 80 | 0.95502 | 0 | 6.615 | 5.66 | 5.66
101 | SS-35/10kv Golovchino | 2,5+2,5 | 2.8532 | 0.617 | 45 | 2.2362 | 0 | 2.625 | 0.38878 | 0.38878 |  | 101 | SS-35/10kv Golovchino | 2,5+2,5 | 0.051 | 2.9042 | 0.617 | 45 | 2.2872 | 0 | 2.625 | 0.33778 | 0.33778
102 | SS-35/10kv Gora-Podol | 2,5+4 | 2.1262 | 0.9085 | 45 | 1.2177 | 0 | 2.625 | 1.4073 | 1.4073 |  | 102 | SS-35/10kv Gora-Podol | 2,5+4 | 0.05 | 2.1762 | 0.9085 | 45 | 1.2677 | 0 | 2.625 | 1.3573 | 1.3573
103 | SS-35/10kv Gorodishche | 4+4 | 2.0102 | 0 |  | 2.0102 | 0 | 4.2 | 2.1898 | 2.1898 |  | 103 | SS-35/10kv Gorodishche | 4+4 | 0.1502 | 2.1604 | 0 |  | 2.1604 | 0 | 4.2 | 2.0396 | 2.0396
104 | SS-35/10kv Dmitrievka | 4+4 | 1.1117 | 0.78237 | 80 | 0.32936 | 0 | 4.2 | 3.8706 | 3.8706 |  | 104 | SS-35/10kv Dmitrievka | 4+4 | 0.528 | 1.6397 | 0.78237 | 80 | 0.85736 | 0 | 4.2 | 3.3426 | 3.3426
105 | SS-35/10kv Dorogoshch | 4+4 | 2.336 | 1.054 | 45 | 1.282 | 0 | 4.2 | 2.918 | 2.918 |  | 105 | SS-35/10kv Dorogoshch | 4+4 | 0.015 | 2.351 | 1.054 | 45 | 1.297 | 0 | 4.2 | 2.903 | 2.903
106 | SS-35/10kv Dragunka | 2,5+2,5 | 0.91285 | 0.62999 | 80 | 0.28285 | 0 | 2.625 | 2.3421 | 2.3421 |  | 106 | SS-35/10kv Dragunka | 2,5+2,5 | 0.0825 | 0.99535 | 0.62999 | 80 | 0.36535 | 0 | 2.625 | 2.2596 | 2.2596
107 | SS-35/10kv Zhuravlevka | 2,5+4 | 1.0482 | 0.274 | 80 | 0.77423 | 0 | 2.625 | 1.8508 | 1.8508 |  | 107 | SS-35/10kv Zhuravlevka | 2,5+4 | 0.8366 | 1.8848 | 0.274 | 80 | 1.6108 | 0 | 2.625 | 1.0142 | 1.0142
108 | SS-35/6kv Zhuravliki | 10+10 | 2.7748 | 4.051 | 120 | -1.2762 | 0 | 10.5 | 11.7762 | 11.7762 |  | 108 | SS-35/6kv Zhuravliki | 10+10 | 0.52 | 3.2948 | 4.051 | 120 | -0.75621 | 0 | 10.5 | 11.2562 | 11.2562
109 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.5591 | 0.42 | 80 | 0.1391 | 0 | 2.625 | 2.4859 | 2.4859 |  | 109 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.75 | 1.3091 | 0.42 | 80 | 0.8891 | 0 | 2.625 | 1.7359 | 1.7359
110 | SS-35/6kv Zapadnaya | 10+10+10 | 6.669 | 1.707 | 120 | 4.962 | 0 | 21 | 16.038 | 16.038 |  | 110 | SS-35/6kv Zapadnaya | 10+10+10 | 0.0077 | 6.6767 | 1.707 | 120 | 4.9697 | 0 | 21 | 16.0303 | 16.0303
111 | SS-35/10kv Zozuli | 6,3+6,3 | 6.1054 | 3.88 | 80 | 2.2254 | 0 | 6.615 | 4.3896 | 4.3896 |  | 111 | SS-35/10kv Zozuli | 6,3+6,3 | 0.0629 | 6.1683 | 3.88 | 80 | 2.2883 | 0 | 6.615 | 4.3267 | 4.3267
112 | SS-35/10kv Ivitsa | 2,5+2,5 | 0.75033 | 0.58603 | 80 | 0.1643 | 0 | 2.625 | 2.4607 | 2.4607 |  | 112 | SS-35/10kv Ivitsa | 2,5+2,5 | 0 | 0.75033 | 0.58603 | 80 | 0.1643 | 0 | 2.625 | 2.4607 | 2.4607
113 | SS-35/10kv Ilovka | 4+4 | 2.5108 | 2.056 | 45 | 0.45485 | 0 | 4.2 | 3.7452 | 3.7452 |  | 113 | SS-35/10kv Ilovka | 4+4 | 0.08 | 2.5908 | 2.056 | 45 | 0.53485 | 0 | 4.2 | 3.6652 | 3.6652
114 | SS-35/10kv Istobnoe | 4+2,5 | 1.3347 | 0.93935 | 120 | 0.39532 | 0 | 2.625 | 2.2297 | 2.2297 |  | 114 | SS-35/10kv Istobnoe | 4+2,5 | 0 | 1.3347 | 0.93935 | 120 | 0.39532 | 0 | 2.625 | 2.2297 | 2.2297
115 | SS-35/10kv Kazatskaya | 2,5+4 | 1.0803 | 0.87141 | 45 | 0.20887 | 0 | 2.625 | 2.4161 | 2.4161 |  | 115 | SS-35/10kv Kazatskaya | 2,5+4 | 0.255 | 1.3353 | 0.87141 | 45 | 0.46387 | 0 | 2.625 | 2.1611 | 2.1611
116 | SS-35/10kv Kazinka | 4+4 | 2.7215 | 0.736 | 120 | 1.9855 | 0 | 4.2 | 2.2145 | 2.2145 |  | 116 | SS-35/10kv Kazinka | 4+4 | 0.052 | 2.7735 | 0.736 | 120 | 2.0375 | 0 | 4.2 | 2.1625 | 2.1625
117 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1.0111 | 0.712 | 120 | 0.29912 | 0 | 2.625 | 2.3259 | 2.3259 |  | 117 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 0 | 1.0111 | 0.712 | 120 | 0.29912 | 0 | 2.625 | 2.3259 | 2.3259
118 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3.3551 | 0.7035 | 120 | 2.6516 | 0 | 6.615 | 3.9634 | 3.9634 |  | 118 | SS-35/10kv Kirovskaya | 6,3+6,3 | 0.194 | 3.5491 | 0.7035 | 120 | 2.8456 | 0 | 6.615 | 3.7694 | 3.7694
119 | SS-35/10kv Kotovo | 2,5+2,5 | 2.2315 | 1.648 | 20 | 0.58345 | 0 | 2.625 | 2.0416 | 2.0416 |  | 119 | SS-35/10kv Kotovo | 2,5+2,5 | 0.174 | 2.4055 | 1.648 | 20 | 0.75745 | 0 | 2.625 | 1.8676 | 1.8676
120 | SS-35/10kv Kochetovka | 2,5+4 | 0.925 | 0.6286 | 45 | 0.2964 | 0 | 2.625 | 2.3286 | 2.3286 |  | 120 | SS-35/10kv Kochetovka | 2,5+4 | 0 | 0.925 | 0.6286 | 45 | 0.2964 | 0 | 2.625 | 2.3286 | 2.3286
121 | SS-35/10kv Krasnoe | 4+2,5 | 1.4836 | 1.1395 | 80 | 0.34407 | 0 | 2.625 | 2.2809 | 2.2809 |  | 121 | SS-35/10kv Krasnoe | 4+2,5 | 0.03 | 1.5136 | 1.1395 | 80 | 0.37407 | 0 | 2.625 | 2.2509 | 2.2509
122 | SS-35/10kv Kretovo | 4+2,5 | 1.2222 | 0.67818 | 120 | 0.54399 | 0 | 2.625 | 2.081 | 2.081 |  | 122 | SS-35/10kv Kretovo | 4+2,5 | 0.017 | 1.2392 | 0.67818 | 120 | 0.56099 | 0 | 2.625 | 2.064 | 2.064
123 | SS-35/10kv Kurasovka | 4+4 | 2.9712 | 1.797 | 80 | 1.1742 | 0 | 4.2 | 3.0258 | 3.0258 |  | 123 | SS-35/10kv Kurasovka | 4+4 | 0.065 | 3.0362 | 1.797 | 80 | 1.2392 | 0 | 4.2 | 2.9608 | 2.9608
124 | SS-35/6kv Lebedi | 4+5,6 | 4.2778 | 0.581 | 120 | 3.6968 | 0 | 4.2 | 0.50325 | 0.50325 |  | 124 | SS-35/6kv Lebedi | 4+5,6 | 0.19 | 4.4678 | 0.581 | 120 | 3.8868 | 0 | 4.2 | 0.31325 | 0.31325
125 | SS-35/6kv Ledovaya | 4+4 | 2.6408 | 1.321 | 80 | 1.3198 | 0 | 4.2 | 2.8802 | 2.8802 |  | 125 | SS-35/6kv Ledovaya | 4+4 | 0.175 | 2.8158 | 1.321 | 80 | 1.4948 | 0 | 4.2 | 2.7052 | 2.7052
126 | SS-35/10kv Livenka | 4+4 | 2.0098 | 1.541 | 120 | 0.46885 | 0 | 4.2 | 3.7312 | 3.7312 |  | 126 | SS-35/10kv Livenka | 4+4 | 0.781 | 2.7908 | 1.541 | 120 | 1.2498 | 0 | 4.2 | 2.9502 | 2.9502
127 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0.87131 | 0.66672 | 80 | 0.2046 | 0 | 2.625 | 2.4204 | 2.4204 |  | 127 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0 | 0.87131 | 0.66672 | 80 | 0.2046 | 0 | 2.625 | 2.4204 | 2.4204
128 | SS-35/10kv M.Pristan | 6,3+6,3 | 6.3025 | 1.81 | 45 | 4.4925 | 0 | 6.615 | 2.1225 | 2.1225 |  | 128 | SS-35/10kv M.Pristan | 6,3+6,3 | 0.525 | 6.8275 | 1.81 | 45 | 5.0175 | 0 | 6.615 | 1.5975 | 1.5975
129 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.82513 | 0.60716 | 80 | 0.21797 | 0 | 2.625 | 2.407 | 2.407 |  | 129 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.042 | 0.86713 | 0.60716 | 80 | 0.25997 | 0 | 2.625 | 2.365 | 2.365
130 | SS-35/10kv Malinovka | 10+10 | 6.2085 | 1.357 | 120 | 4.8515 | 0 | 10.5 | 5.6485 | 5.6485 |  | 130 | SS-35/10kv Malinovka | 10+10 | 1.314 | 7.5225 | 1.357 | 120 | 6.1655 | 0 | 10.5 | 4.3345 | 4.3345
131 | SS-35/10kv Mandrovo | 2,5+2,5 | 1.3454 | 0.65565 | 80 | 0.68976 | 0 | 2.625 | 1.9352 | 1.9352 |  | 131 | SS-35/10kv Mandrovo | 2,5+2,5 | 0 | 1.3454 | 0.65565 | 80 | 0.68976 | 0 | 2.625 | 1.9352 | 1.9352
132 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1.0881 | 0.643 | 80 | 0.44506 | 0 | 2.625 | 2.1799 | 2.1799 |  | 132 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 0 | 1.0881 | 0.643 | 80 | 0.44506 | 0 | 2.625 | 2.1799 | 2.1799
133 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1.0776 | 0.59315 | 120 | 0.48443 | 0 | 2.625 | 2.1406 | 2.1406 |  | 133 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 0.01 | 1.0876 | 0.59315 | 120 | 0.49443 | 0 | 2.625 | 2.1306 | 2.1306
134 | SS-35/10kv N.Derevnya | 6,3+4 | 4.6246 | 2.78 | 120 | 1.8446 | 0 | 4.2 | 2.3554 | 2.3554 |  | 134 | SS-35/10kv N.Derevnya | 6,3+4 | 0.2697 | 4.8943 | 2.78 | 120 | 2.1143 | 0 | 4.2 | 2.0857 | 2.0857
135 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 1.5956 | 0.842 | 45 | 0.75359 | 0 | 6.615 | 5.8614 | 5.8614 |  | 135 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 0.138 | 1.7336 | 0.842 | 45 | 0.89159 | 0 | 6.615 | 5.7234 | 5.7234
136 | SS-35/10kv N.Ukolovo | 4+2,5 | 1.6545 | 0.57 | 80 | 1.0845 | 0 | 2.625 | 1.5405 | 1.5405 |  | 136 | SS-35/10kv N.Ukolovo | 4+2,5 | 0 | 1.6545 | 0.57 | 80 | 1.0845 | 0 | 2.625 | 1.5405 | 1.5405
137 | SS-35/10kv N.Khutornoe | 2,5+4 | 0.30823 | 0.19 | 80 | 0.11823 | 0 | 2.625 | 2.5068 | 2.5068 |  | 137 | SS-35/10kv N.Khutornoe | 2,5+4 | 0 | 0.30823 | 0.19 | 80 | 0.11823 | 0 | 2.625 | 2.5068 | 2.5068
138 | SS-35/10kv Neminushchee | 2,5+4 | 1.0176 | 0.65147 | 80 | 0.36609 | 0 | 2.625 | 2.2589 | 2.2589 |  | 138 | SS-35/10kv Neminushchee | 2,5+4 | 0 | 1.0176 | 0.65147 | 80 | 0.36609 | 0 | 2.625 | 2.2589 | 2.2589
139 | SS-35/10kv Nechaevka | 4+4 | 1.8217 | 0.451 | 120 | 1.3707 | 0 | 4.2 | 2.8293 | 2.8293 |  | 139 | SS-35/10kv Nechaevka | 4+4 | 0.0766 | 1.8983 | 0.451 | 120 | 1.4473 | 0 | 4.2 | 2.7527 | 2.7527
140 | SS-35/10kv Nikitovka | 2,5+2,5 | 1.8019 | 1.4354 | 80 | 0.36645 | 0 | 2.625 | 2.2585 | 2.2585 |  | 140 | SS-35/10kv Nikitovka | 2,5+2,5 | 0.009 | 1.8109 | 1.4354 | 80 | 0.37545 | 0 | 2.625 | 2.2495 | 2.2495
141 | SS-35/10kv Novenkoe | 4+4 | 2.1525 | 1.7332 | 80 | 0.41931 | 0 | 4.2 | 3.7807 | 3.7807 |  | 141 | SS-35/10kv Novenkoe | 4+4 | 0 | 2.1525 | 1.7332 | 80 | 0.41931 | 0 | 4.2 | 3.7807 | 3.7807
142 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 8.1276 | 0.872 | 80 | 7.2556 | 0 | 6.615 | -0.64061 | -0.64061 |  | 142 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.817 | 8.9446 | 0.872 | 80 | 8.0726 | 0 | 6.615 | -1.4576 | -1.4576
143 | SS-35/10kv Orlik | 4+4 | 2.0824 | 0.553 | 80 | 1.5294 | 0 | 4.2 | 2.6706 | 2.6706 |  | 143 | SS-35/10kv Orlik | 4+4 | 0.077 | 2.1594 | 0.553 | 80 | 1.6064 | 0 | 4.2 | 2.5936 | 2.5936
144 | SS-35/10kv Podolkhi | 2,5+2,5 | 1.5603 | 1.1225 | 45 | 0.43784 | 0 | 2.625 | 2.1872 | 2.1872 |  | 144 | SS-35/10kv Podolkhi | 2,5+2,5 | 0.023 | 1.5833 | 1.1225 | 45 | 0.46084 | 0 | 2.625 | 2.1642 | 2.1642
145 | SS-35/10kv Popovka | 6,3+4 | 1.1758 | 0.64636 | 80 | 0.52942 | 0 | 4.2 | 3.6706 | 3.6706 |  | 145 | SS-35/10kv Popovka | 6,3+4 | 0 | 1.1758 | 0.64636 | 80 | 0.52942 | 0 | 4.2 | 3.6706 | 3.6706
146 | SS-35/10kv Prelestnoe | 4+4 | 2.3992 | 0 |  | 2.3992 | 0 | 4.2 | 1.8008 | 1.8008 |  | 146 | SS-35/10kv Prelestnoe | 4+4 | 0.44 | 2.8392 | 0 |  | 2.8392 | 0 | 4.2 | 1.3608 | 1.3608
147 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5.6912 | 0 |  | 5.6912 | 0 | 6.615 | 0.92376 | 0.92376 |  | 147 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 0.1 | 5.7912 | 0 |  | 5.7912 | 0 | 6.615 | 0.82376 | 0.82376
148 | SS-35/10kv Prilepy | 2,5+2,5 | 0.49609 | 0.37638 | 80 | 0.11972 | 0 | 2.625 | 2.5053 | 2.5053 |  | 148 | SS-35/10kv Prilepy | 2,5+2,5 | 0 | 0.49609 | 0.37638 | 80 | 0.11972 | 0 | 2.625 | 2.5053 | 2.5053
149 | SS-35/10kv Printsevka | 2,5+2,5 | 1.114 | 0.352 | 120 | 0.76204 | 0 | 2.625 | 1.863 | 1.863 |  | 149 | SS-35/10kv Printsevka | 2,5+2,5 | 0.646 | 1.76 | 0.352 | 120 | 1.408 | 0 | 2.625 | 1.217 | 1.217
150 | SS-35/10kv Radkovka | 6,3+6,3 | 2.5116 | 0.164 | 45 | 2.3476 | 0 | 6.615 | 4.2674 | 4.2674 |  | 150 | SS-35/10kv Radkovka | 6,3+6,3 | 0.234 | 2.7456 | 0.164 | 45 | 2.5816 | 0 | 6.615 | 4.0334 | 4.0334
151 | SS-35/10kv Razdornoe | 2,5+2,5 | 1.1029 | 0.662 | 80 | 0.44089 | 0 | 2.625 | 2.1841 | 2.1841 |  | 151 | SS-35/10kv Razdornoe | 2,5+2,5 | 0.07 | 1.1729 | 0.662 | 80 | 0.51089 | 0 | 2.625 | 2.1141 | 2.1141
152 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1.693 | 0.88491 | 80 | 0.80806 | 0 | 2.625 | 1.8169 | 1.8169 |  | 152 | SS-35/10kv Repyakhovka | 2,5+2,5 | 0.03 | 1.723 | 0.88491 | 80 | 0.83806 | 0 | 2.625 | 1.7869 | 1.7869
153 | SS-35/10kv Rzhevka | 10+10 | 5.9105 | 2.53 | 45 | 3.3805 | 0 | 10.5 | 7.1195 | 7.1195 |  | 153 | SS-35/10kv Rzhevka | 10+10 | 0.01 | 5.9205 | 2.53 | 45 | 3.3905 | 0 | 10.5 | 7.1095 | 7.1095
154 | SS-35/10kv Rovenki | 4+4 | 2.9281 | 1.7393 | 120 | 1.1888 | 0 | 4.2 | 3.0112 | 3.0112 |  | 154 | SS-35/10kv Rovenki | 4+4 | 0 | 2.9281 | 1.7393 | 120 | 1.1888 | 0 | 4.2 | 3.0112 | 3.0112
155 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1.5623 | 0 |  | 1.5623 | 0 | 2.625 | 1.0627 | 1.0627 |  | 155 | SS-35/10kv Rogovatoe | 2,5+2,5 | 0 | 1.5623 | 0 |  | 1.5623 | 0 | 2.625 | 1.0627 | 1.0627
156 | SS-35/10kv Saprykino | 2,5+2,5 | 0.45462 | 0.22751 | 120 | 0.22711 | 0 | 2.625 | 2.3979 | 2.3979 |  | 156 | SS-35/10kv Saprykino | 2,5+2,5 | 0 | 0.45462 | 0.22751 | 120 | 0.22711 | 0 | 2.625 | 2.3979 | 2.3979
157 | SS-35/6kv Severnaya | 6,3+6,3 | 6.9665 | 4.8049 | 120 | 2.1616 | 0 | 6.615 | 4.4534 | 4.4534 |  | 157 | SS-35/6kv Severnaya | 6,3+6,3 | 0.1295 | 7.096 | 4.8049 | 120 | 2.2911 | 0 | 6.615 | 4.3239 | 4.3239
158 | SS-35/10kv Setishche | 2,5+2,5 | 1.7003 | 1.0621 | 80 | 0.6382 | 0 | 2.625 | 1.9868 | 1.9868 |  | 158 | SS-35/10kv Setishche | 2,5+2,5 | 0.01 | 1.7103 | 1.0621 | 80 | 0.6482 | 0 | 2.625 | 1.9768 | 1.9768
159 | SS-35/10kv Slonovka | 4+4 | 1.698 | 1.1306 | 120 | 0.56739 | 0 | 4.2 | 3.6326 | 3.6326 |  | 159 | SS-35/10kv Slonovka | 4+4 | 0.022 | 1.72 | 1.1306 | 120 | 0.58939 | 0 | 4.2 | 3.6106 | 3.6106
160 | SS-35/6kv St.Oskol -2 | 16+16 | 9.3714 | 1.21 | 80 | 8.1614 | 0 | 16.8 | 8.6386 | 8.6386 |  | 160 | SS-35/6kv St.Oskol -2 | 16+16 | 0.3194 | 9.6908 | 1.21 | 80 | 8.4808 | 0 | 16.8 | 8.3192 | 8.3192
161 | SS-35/10kv Starikovo | 2,5+2,5 | 2.803 | 1.3453 | 45 | 1.4577 | 0 | 2.625 | 1.1673 | 1.1673 |  | 161 | SS-35/10kv Starikovo | 2,5+2,5 | 0.035 | 2.838 | 1.3453 | 45 | 1.4927 | 0 | 2.625 | 1.1323 | 1.1323
162 | SS-35/10kv Tavrovo | 10+10 | 7.7046 | 0.531 | 45 | 7.1736 | 0 | 10.5 | 3.3264 | 3.3264 |  | 162 | SS-35/10kv Tavrovo | 10+10 | 0.9769 | 8.6815 | 0.531 | 45 | 8.1505 | 0 | 10.5 | 2.3495 | 2.3495
163 | SS-35/10kv Terebrino | 2,5+2,5 | 0.69752 | 0.44978 | 80 | 0.24773 | 0 | 2.625 | 2.3773 | 2.3773 |  | 163 | SS-35/10kv Terebrino | 2,5+2,5 | 0 | 0.69752 | 0.44978 | 80 | 0.24773 | 0 | 2.625 | 2.3773 | 2.3773
164 | SS-35/10kv Urazovo | 6,3+6,3 | 4.571 | 1.39 | 120 | 3.181 | 0 | 6.615 | 3.434 | 3.434 |  | 164 | SS-35/10kv Urazovo | 6,3+6,3 | 0.022 | 4.593 | 1.39 | 120 | 3.203 | 0 | 6.615 | 3.412 | 3.412
165 | SS-35/10kv Utochka | 1,6+2,5 | 0.74863 | 0.47242 | 80 | 0.27621 | 0 | 1.68 | 1.4038 | 1.4038 |  | 165 | SS-35/10kv Utochka | 1,6+2,5 | 0.015 | 0.76363 | 0.47242 | 80 | 0.29121 | 0 | 1.68 | 1.3888 | 1.3888
166 | SS-35/6kv Fedoseevka | 4+4 | 1.9262 | 0 |  | 1.9262 | 0 | 4.2 | 2.2738 | 2.2738 |  | 166 | SS-35/6kv Fedoseevka | 4+4 | 0.104 | 2.0302 | 0 |  | 2.0302 | 0 | 4.2 | 2.1698 | 2.1698
167 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0.90356 | 0.78681 | 45 | 0.11676 | 0 | 1.68 | 1.5632 | 1.5632 |  | 167 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0 | 0.90356 | 0.78681 | 45 | 0.11676 | 0 | 1.68 | 1.5632 | 1.5632
168 | SS-35/10kv Kholodnoe | 4+4 | 1.7614 | 0 |  | 1.7614 | 0 | 4.2 | 2.4386 | 2.4386 |  | 168 | SS-35/10kv Kholodnoe | 4+4 | 0 | 1.7614 | 0 |  | 1.7614 | 0 | 4.2 | 2.4386 | 2.4386
169 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1.6135 | 1.3513 | 20 | 0.26228 | 0 | 6.615 | 6.3527 | 6.3527 |  | 169 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 0.65 | 2.2635 | 1.3513 | 20 | 0.91228 | 0 | 6.615 | 5.7027 | 5.7027
170 | SS-35/10kv Shatalovka | 6,3+6,3 | 1.9373 | 0 |  | 1.9373 | 0 | 6.615 | 4.6777 | 4.6777 |  | 170 | SS-35/10kv Shatalovka | 6,3+6,3 | 0.048 | 1.9853 | 0 |  | 1.9853 | 0 | 6.615 | 4.6297 | 4.6297
171 | SS-35/10kv Shakhovka | 2,5+2,5 | 1.5261 | 0.79066 | 80 | 0.73541 | 0 | 2.625 | 1.8896 | 1.8896 |  | 171 | SS-35/10kv Shakhovka | 2,5+2,5 | 0 | 1.5261 | 0.79066 | 80 | 0.73541 | 0 | 2.625 | 1.8896 | 1.8896
172 | SS-35/10kv Shishino | 4+6,3 | 3.3728 | 1.03 | 80 | 2.3428 | 0 | 4.2 | 1.8572 | 1.8572 |  | 172 | SS-35/10kv Shishino | 4+6,3 | 0.071 | 3.4438 | 1.03 | 80 | 2.4138 | 0 | 4.2 | 1.7862 | 1.7862
173 | SS-35/10kv Yablonovo | 4+4 | 1.6831 | 1.1284 | 80 | 0.55464 | 0 | 4.2 | 3.6454 | 3.6454 |  | 173 | SS-35/10kv Yablonovo | 4+4 | 0.03 | 1.7131 | 1.1284 | 80 | 0.58464 | 0 | 4.2 | 3.6154 | 3.6154
174 | SS-35/10kv Yarskoe | 2,5+2,5 | 0.51053 | 0.14648 | 80 | 0.36405 | 0 | 2.625 | 2.2609 | 2.2609 |  | 174 | SS-35/10kv Yarskoe | 2,5+2,5 | 0 | 0.51053 | 0.14648 | 80 | 0.36405 | 0 | 2.625 | 2.2609 | 2.2609
| TOTAL: | 3177.2 | 1015.675 | 453.9275 |  | 609.8623 | [5 empty] | 2: TOTAL:; 3: 3177.2; 4: 87.2867; 5: 1102.9617; МVА 6: 453.9275; min. 8: 649.0342
| deficit | [8 empty] | -2.3835 |  | 2: deficit; min. 12: -2.404
| proficit | [8 empty] | 944.8247 |  | 2: proficit; min. 12: 858.5999

## липецк
Table 1
No. | Object of main substation, voltage class | Current deficit | [9 empty] | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  | Note |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | MVA | Мin. | [11 empty] | МVА | min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 2: One-transformer substations
1 | SS 110/10kv Lev Tolstoy | 10 | 2.3642 | 1 | 30 | 1 | 0 | 1 | -1.3642 | -1.3642 | closed | 1 | SS 110/10kv Lev Tolstoy | 10 | 0.05 | 2.4142 | 1 | 30 | 1 | 0 | 1 | -1.4142 | -1.4142 | closed
2 | SS 110/10 kv Dvurechki | 6.3 | 2.6469 | 0.31 | 120 | 0.31 | 0 | 0.31 | -2.3369 | -2.3369 | closed | 2 | SS 110/10 kv Dvurechki | 6.3 | 0.114 | 2.7609 | 0.31 | 120 | 0.31 | 0 | 0.31 | -2.4509 | -2.4509 | closed
3 | SS 35/10 kv Vesyoloe | 2.5 | 0.070668 | 0.37 | 120 | 0.37 | 0 | 0.37 | 0.29933 | 0.29933 | opened | 3 | SS 35/10 kv Vesyoloe | 2.5 |  | 0.070668 | 0.37 | 120 | 0.37 | 0 | 0.37 | 0.29933 | 0.29933 | opened
4 | SS 35/10 kv Kr.Palna | 3.2 | 0.90067 | 0.5 | 120 | 0.5 | 0 | 0.5 | -0.40067 | -0.40067 | closed | 4 | SS 35/10 kv Kr.Palna | 3.2 | 0.15 | 1.0507 | 0.5 | 120 | 0.5 | 0 | 0.5 | -0.55067 | -0.55067 | closed
5 | SS 35/10 kv Kamenka | 2.5 | 0.64259 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.27259 | -0.27259 | closed | 5 | SS 35/10 kv Kamenka | 2.5 | 0.5 | 1.1426 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.77259 | -0.77259 | closed
6 | SS 35/10 kv Krasotynovka | 2.5 | 0.25461 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.045389 | 0.045389 | opened | 6 | SS 35/10 kv Krasotynovka | 2.5 |  | 0.25461 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.045389 | 0.045389 | opened
7 | SS 35/10 kv Ozyorki | 2.5 | 0.11224 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | 0.25776 | 0.25776 | opened | 7 | SS 35/10 kv Ozyorki | 2.5 |  | 0.11224 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | 0.25776 | 0.25776 | opened
8 | SS 35/10 kv Pankratovka | 2.5 | 0.61834 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.24834 | -0.24834 | closed | 8 | SS 35/10 kv Pankratovka | 2.5 |  | 0.61834 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.24834 | -0.24834 | closed
9 | SS 35/10 kv Preobrazhenye | 2.5 | 0.41154 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | -0.011535 | -0.011535 | closed | 9 | SS 35/10 kv Preobrazhenye | 2.5 |  | 0.41154 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | -0.011535 | -0.011535 | closed
10 | SS 35/10 kv Yakovlevo | 2.5 | 0.71603 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | -0.34603 | -0.34603 | closed | 10 | SS 35/10 kv Yakovlevo | 2.5 |  | 0.71603 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | -0.34603 | -0.34603 | closed
11 | SS 110/10kv Terbunsky gonchar | 25 | без нагрузки | [8 empty] | 1: 11; 2: SS 110/10kv Terbunsky gonchar; 3: 25; 4: 15
12 | SS 35/10 kv Pervomayskaya | 2.5 | 0.73439 | 0.25 | 90 | 0.25 | 0 | 0.25 | -0.48439 | -0.48439 | closed | 12 | SS 35/10 kv Pervomayskaya | 2.5 |  | 0.73439 | 0.25 | 90 | 0.25 | 0 | 0.25 | -0.48439 | -0.48439 | closed
13 | SS 35/10 kv Kamennaya Lubna | 2.5 | 0.81839 | 0.75 | 90 | 0.75 | 0 | 0.75 | -0.068394 | -0.068394 | closed | 13 | SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.81839 | 0.75 | 90 | 0.75 | 0 | 0.75 | -0.068394 | -0.068394 | closed
14 | SS 35/10 kv Znamenka | 2.5 | 0.85477 | 0.75 | 24 hours | 0.75 | 0 | 0.75 | -0.10477 | -0.10477 | closed | 14 | SS 35/10 kv Znamenka | 2.5 | 0.045 | 0.89977 | 0.75 | 24 hours | 0.75 | 0 | 0.75 | -0.14977 | -0.14977 | closed
15 | SS 35/10 kv Pikovo | 2.5 | 0.51407 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.23593 | 0.23593 | opened | 15 | SS 35/10 kv Pikovo | 2.5 |  | 0.51407 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.23593 | 0.23593 | opened
16 | SS 35/10 kv Nikolskoe | 4 | 0.44167 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.15833 | 0.15833 | opened | 16 | SS 35/10 kv Nikolskoe | 4 |  | 0.44167 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.15833 | 0.15833 | opened
17 | SS 35/10 kv Peskovatka | 1.6 | 0.14394 | 0.48 | 120 | 0.48 | 0 | 0.48 | 0.33606 | 0.33606 | opened | 17 | SS 35/10 kv Peskovatka | 1.6 |  | 0.14394 | 0.48 | 120 | 0.48 | 0 | 0.48 | 0.33606 | 0.33606 | opened
18 | SS 35/6 kv Druzhba | 5.6 | КРУНН-6кВ не наши | [7 empty] | opened | 1: 18; 2: SS 35/6 kv Druzhba; 3: 5.6; min. 13: opened
19 | SS 35/10 kv SOM | 1.6 | 0.1 | 0.16 | 120 | 0.16 | 0 | 0.16 | 0.06 | 0.06 | opened | 1: 19; 2: SS 35/10 kv SOM; 3: 1.6; min. 13: opened
20 | SS 35/6 kv Novonikolaevka | 4 | 0.69027 | 0.6 | 120 | 0.6 | 0 | 0.6 | -0.09027 | -0.09027 | closed | 20 | SS 35/6 kv Novonikolaevka | 4 |  | 0.69027 | 0.6 | 120 | 0.6 | 0 | 0.6 | -0.09027 | -0.09027 | closed
21 | SS 35/10 kv Sindyakino | 2.5 | 0.94458 | 0.2 | 60 | 0.2 | 0 | 0.2 | -0.74458 | -0.74458 | closed | 21 | SS 35/10 kv Sindyakino | 2.5 | 0.02 | 0.96458 | 0.2 | 60 | 0.2 | 0 | 0.2 | -0.76458 | -0.76458 | closed
22 | SS 35/10 kv Kurino | 2.5 | 0.3088 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.071195 | 0.071195 | opened | 22 | SS 35/10 kv Kurino | 2.5 | 0.02 | 0.32881 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.051195 | 0.051195 | opened
23 | SS 35/10 kv Novodubovoe | 2.5 | 0.54703 | 0.5 | 60 | 0.5 | 0 | 0.5 | -0.047026 | -0.047026 | closed | 23 | SS 35/10 kv Novodubovoe | 2.5 | 0.011 | 0.55803 | 0.5 | 60 | 0.5 | 0 | 0.5 | -0.058026 | -0.058026 | closed
24 | SS 35/10 kv Beryozovka | 2.5 | 1.1444 | 0.75 | 120 | 0.75 | 0 | 0.75 | -0.39439 | -0.39439 | closed | 24 | SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0.75 | 120 | 0.75 | 0 | 0.75 | -0.39439 | -0.39439 | closed
25 | SS 110/6 kv Agregatnaya | 16+16 | 13.1489 | 0 | 0 | 13.1489 | 0 | 16.8 | 3.6511 | 3.6511 | opened | 25 | SS 110/6 kv Agregatnaya | 16+16 | 2.6 | 15.7489 | 0 | 0 | 15.7489 | 0 | 16.8 | 1.0511 | 1.0511 | opened
26 | SS 110/6 kv Zapadnaya | 40+40 | 10.9119 | 0 | 0 | 10.9119 | 0 | 42 | 31.0881 | 31.0881 | opened | 26 | SS 110/6 kv Zapadnaya | 40+40 | 0.229 | 11.1409 | 0 | 0 | 11.1409 | 0 | 42 | 30.8591 | 30.8591 | opened
27 | SS 110/10 kv Kashary | 2,5+6,3 | 1.3621 | 0.25 | 120 | 1.1121 | 0 | 2.625 | 1.5129 | 1.5129 | opened | 27 | SS 110/10 kv Kashary | 2,5+6,3 | 0.63 | 1.9921 | 0.25 | 120 | 1.7421 | 0 | 2.625 | 0.88288 | 0.88288 | opened
28 | SS 110/6 kv Tabak | 16+16 | 13.4234 | 4.8 | 120 | 8.6234 | 0 | 16.8 | 8.1766 | 8.1766 | opened | 28 | SS 110/6 kv Tabak | 16+16 | 0.028 | 13.4514 | 4.8 | 120 | 8.6514 | 0 | 16.8 | 8.1486 | 8.1486 | opened
29 | SS 110/10 kv Lukoshkino | 10+2,5 | 0.9942 | 0 | 0 | 0.9942 | 0 | 2.625 | 1.6308 | 1.6308 | opened | 29 | SS 110/10 kv Lukoshkino | 10+2,5 | 0.01 | 1.0042 | 0 | 0 | 1.0042 | 0 | 2.625 | 1.6208 | 1.6208 | opened
30 | SS 110/10kv Niva | 10+10 | 4.3648 | 1 | 120 | 3.3648 | 0 | 10.5 | 7.1352 | 7.1352 | opened | 30 | SS 110/10kv Niva | 10+10 | 0.122 | 4.4868 | 1 | 120 | 3.4868 | 0 | 10.5 | 7.0132 | 7.0132 | opened
31 | SS 110/10 kv Olkhovets | 2,5+2,5 | 1.4807 | 0.63 | 120 | 0.85073 | 0 | 2.625 | 1.7743 | 1.7743 | opened | 31 | SS 110/10 kv Olkhovets | 2,5+2,5 | 0.034 | 1.5147 | 0.63 | 120 | 0.88473 | 0 | 2.625 | 1.7403 | 1.7403 | opened
32 | SS 110/10 kv Kuyman | 2,5+2,5 | 0.54767 | 0.63 | 120 | -0.082326 | 0 | 2.625 | 2.7073 | 2.7073 | opened | 32 | SS 110/10 kv Kuyman | 2,5+2,5 |  | 0.54767 | 0.63 | 120 | -0.082326 | 0 | 2.625 | 2.7073 | 2.7073 | opened
33 | SS 110/10 kv Lutoshkino | 2,5+2,5 | 0.2728 | 0.75 | 120 | -0.4772 | 0 | 2.625 | 3.1022 | 3.1022 | opened | 33 | SS 110/10 kv Lutoshkino | 2,5+2,5 |  | 0.2728 | 0.75 | 120 | -0.4772 | 0 | 2.625 | 3.1022 | 3.1022 | opened
34 | SS 110/10 kv Krugloe | 2,5+2,5 | 0.58197 | 0.75 | 120 | -0.16803 | 0 | 2.625 | 2.793 | 2.793 | opened | 34 | SS 110/10 kv Krugloe | 2,5+2,5 |  | 0.58197 | 0.75 | 120 | -0.16803 | 0 | 2.625 | 2.793 | 2.793 | opened
35 | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 40.3158 | 4.5 | 30 | 35.8158 | 0 | 42 | 6.1842 | 6.1842 | * | 35 | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 1.673 | 41.9888 | 4.5 | 30 | 37.4888 | 0 | 42 | 4.5112 | 4.5112 | *
36 | SS 110/6 kv Privokzalnaya | 20+20+25 | 43.4403 | 1.38 | 30 | 42.0603 | 0 | 42 | -0.0603 | -0.0603 | opened | 36 | SS 110/6 kv Privokzalnaya | 20+20+25 | 0.354 | 43.7943 | 1.38 | 30 | 42.4143 | 0 | 42 | -0.4143 | -0.4143 | closed
37 | SS 110/10/6 kv Yuzhnaya | 40+40 | 40.3574 | 6 | 30 | 34.3574 | 0 | 42 | 7.6426 | 7.6426 | opened | 37 | SS 110/10/6 kv Yuzhnaya | 40+40 | 0.16 | 40.5174 | 6 | 30 | 34.5174 | 0 | 42 | 7.4826 | 7.4826 | opened
38 | SS 110/6 kv Sitovka | 10+10 | 4.0819 | 1.29 | 30 | 2.7919 | 0 | 10.5 | 7.7081 | 7.7081 | * | 38 | SS 110/6 kv Sitovka | 10+10 |  | 4.0819 | 1.29 | 30 | 2.7919 | 0 | 10.5 | 7.7081 | 7.7081 | *
39 | SS 110/6 kv LTP | 6,3+10 | 4.9599 | 0 | 0 | 4.9599 | 0 | 6.615 | 1.6551 | 1.6551 | opened | 39 | SS 110/6 kv LTP | 6,3+10 |  | 4.9599 | 0 | 0 | 4.9599 | 0 | 6.615 | 1.6551 | 1.6551 | opened
40 | SS 110/6 kv KPD | 10+10 | 2.768 | 0 | 0 | 2.768 | 0 | 10.5 | 7.732 | 7.732 | opened | 40 | SS 110/6 kv KPD | 10+10 | 0.1 | 2.868 | 0 | 0 | 2.868 | 0 | 10.5 | 7.632 | 7.632 | opened
41 | SS 110/10 kv Oktyabskaya | 40+40 | 14.7822 | 4 | 30 | 10.7822 | 0 | 42 | 31.2178 | 31.2178 | opened | 41 | SS 110/10 kv Oktyabskaya | 40+40 | 0.158 | 14.9402 | 4 | 30 | 10.9402 | 0 | 42 | 31.0598 | 31.0598 | opened
42 | SS 110/6 kv Teplichnaya | 15+15 | 6.6823 | 0 | 0 | 6.6823 | 0 | 15.75 | 9.0677 | 9.0677 | opened | 42 | SS 110/6 kv Teplichnaya | 15+15 | 0.005 | 6.6873 | 0 | 0 | 6.6873 | 0 | 15.75 | 9.0627 | 9.0627 | opened
43 | SS 110/6 kv GPP-2 LTZ | 63+63 | 12.4211 | 0 | 0 | 12.4211 | 0 | 66.15 | 53.7289 | 53.7289 | opened | 43 | SS 110/6 kv GPP-2 LTZ | 63+63 | 0.22 | 12.6411 | 0 | 0 | 12.6411 | 0 | 66.15 | 53.5089 | 53.5089 | opened
44 | SS 35/10 kv Avangard | 4+4 | 0.6296 | 0.6 | 120 | 0.0296 | 0 | 4.2 | 4.1704 | 4.1704 | opened | 44 | SS 35/10 kv Avangard | 4+4 | 0.217 | 0.8466 | 0.6 | 120 | 0.2466 | 0 | 4.2 | 3.9534 | 3.9534 | opened
45 | SS 35/10 kv Afanasysevo | 2,5+2,5 | 1.6472 | 0.37 | 120 | 1.2772 | 0 | 2.625 | 1.3478 | 1.3478 | opened | 45 | SS 35/10 kv Afanasysevo | 2,5+2,5 | 0.01 | 1.6572 | 0.37 | 120 | 1.2872 | 0 | 2.625 | 1.3378 | 1.3378 | opened
46 | SS 35/10 kv Babarykino | 2,5+2,5 | 0.2754 | 0.37 | 120 | -0.094604 | 0 | 2.625 | 2.7196 | 2.7196 | opened | 46 | SS 35/10 kv Babarykino | 2,5+2,5 | 0.015 | 0.2904 | 0.37 | 120 | -0.079604 | 0 | 2.625 | 2.7046 | 2.7046 | opened
47 | SS 35/10 kv Avrora | 2,5+2,5 | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened | 47 | SS 35/10 kv Avrora | 2,5+2,5 |  | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened
48 | SS 35/10 kv B.Boyovka | 2,5+2,5 | 0.29982 | 0.37 | 120 | -0.070182 | 0 | 2.625 | 2.6952 | 2.6952 | opened | 48 | SS 35/10 kv B.Boyovka | 2,5+2,5 | 0.01 | 0.30982 | 0.37 | 120 | -0.060182 | 0 | 2.625 | 2.6852 | 2.6852 | opened
49 | SS 35/10 kv Borki | 2,5+2,5 | 0.95644 | 0.37 | 120 | 0.58644 | 0 | 2.625 | 2.0386 | 2.0386 | opened | 49 | SS 35/10 kv Borki | 2,5+2,5 | 0.64 | 1.5964 | 0.37 | 120 | 1.2264 | 0 | 2.625 | 1.3986 | 1.3986 | opened
50 | SS 35/6kv Vostochnaya | 10+16 | 13.051 | 1 | 120 | 12.051 | 0 | 10.5 | -1.551 | -1.551 |  | 50 | SS 35/6kv Vostochnaya | 10+16 | 0.0796 | 13.1306 | 1 | 120 | 12.1306 | 0 | 10.5 | -1.6306 | -1.6306
51 | SS 35/10 kv Vasilyevka | 2,5+2,5 | 0.30242 | 0.37 | 120 | -0.067584 | 0 | 2.625 | 2.6926 | 2.6926 | opened | 51 | SS 35/10 kv Vasilyevka | 2,5+2,5 | 0.002 | 0.30442 | 0.37 | 120 | -0.065584 | 0 | 2.625 | 2.6906 | 2.6906 | opened
52 | SS 35/10 kv Voronets | 4+4 | 1.4393 | 0.6 | 120 | 0.83933 | 0 | 4.2 | 3.3607 | 3.3607 | opened | 52 | SS 35/10 kv Voronets | 4+4 | 0.048 | 1.4873 | 0.6 | 120 | 0.88733 | 0 | 4.2 | 3.3127 | 3.3127 | opened
53 | SS 35/6 kv Golikovo | 1,8+1,6 | 1.4722 | 0 | 0 | 1.4722 | 0 | 1.68 | 0.20776 | 0.20776 | opened | 53 | SS 35/6 kv Golikovo | 1,8+1,6 |  | 1.4722 | 0 | 0 | 1.4722 | 0 | 1.68 | 0.20776 | 0.20776 | opened
54 | SS 35/10 kv Gatishche | 2,5+2,5 | 0.23642 | 0 | 0 | 0.23642 | 0 | 2.625 | 2.3886 | 2.3886 | opened | 54 | SS 35/10 kv Gatishche | 2,5+2,5 |  | 0.23642 | 0 | 0 | 0.23642 | 0 | 2.625 | 2.3886 | 2.3886 | opened
55 | SS 35/10 kv Gnilusha | 6,3+6,3 | 1.0515 | 0.63 | 120 | 0.42153 | 0 | 6.615 | 6.1935 | 6.1935 | opened | 55 | SS 35/10 kv Gnilusha | 6,3+6,3 |  | 1.0515 | 0.63 | 120 | 0.42153 | 0 | 6.615 | 6.1935 | 6.1935 | opened
56 | SS 35/10kv Gryzlovo | 2,5+2,5 | 0.63393 | 0.37 | 120 | 0.26393 | 0 | 2.625 | 2.3611 | 2.3611 | opened | 56 | SS 35/10kv Gryzlovo | 2,5+2,5 |  | 0.63393 | 0.37 | 120 | 0.26393 | 0 | 2.625 | 2.3611 | 2.3611 | opened
57 | SS 35/10 kv Zhernovnoe | 2,5+2,5 | 0.32909 | 0.37 | 120 | -0.04091 | 0 | 2.625 | 2.6659 | 2.6659 | opened | 57 | SS 35/10 kv Zhernovnoe | 2,5+2,5 | 0.8 | 1.1291 | 0.37 | 120 | 0.75909 | 0 | 2.625 | 1.8659 | 1.8659 | opened
58 | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 2.1204 | 0 | 0 | 2.1204 | 0 | 1.68 | -0.44038 | -0.44038 |  | 58 | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.082 | 2.2024 | 0 | 0 | 2.2024 | 0 | 1.68 | -0.52238 | -0.52238
59 | SS 35/10 kv Zakharovka | 2,5+2,5 | 0.24318 | 0.37 | 120 | -0.12682 | 0 | 2.625 | 2.7518 | 2.7518 | opened | 59 | SS 35/10 kv Zakharovka | 2,5+2,5 |  | 0.24318 | 0.37 | 120 | -0.12682 | 0 | 2.625 | 2.7518 | 2.7518 | opened
60 | SS 35/10 kv Kazaki | 4+4 | 2.7713 | 0 | 0 | 2.7713 | 0 | 4.2 | 1.4287 | 1.4287 | opened | 60 | SS 35/10 kv Kazaki | 4+4 | 0.007 | 2.7783 | 0 | 0 | 2.7783 | 0 | 4.2 | 1.4217 | 1.4217 | opened
61 | SS 35/10 kv Kolesovo | 6,3+6,3 | 1.1639 | 0.63 | 120 | 0.53394 | 0 | 6.615 | 6.0811 | 6.0811 | opened | 61 | SS 35/10 kv Kolesovo | 6,3+6,3 | 0.044 | 1.2079 | 0.63 | 120 | 0.57794 | 0 | 6.615 | 6.0371 | 6.0371 | opened
62 | SS 35/10 kv Knyazevo | 2,5+2,5 | 0.37326 | 0.37 | 120 | 0.0032569 | 0 | 2.625 | 2.6217 | 2.6217 | opened | 62 | SS 35/10 kv Knyazevo | 2,5+2,5 | 0.022 | 0.39526 | 0.37 | 120 | 0.025257 | 0 | 2.625 | 2.5997 | 2.5997 | opened
63 | SS 35/10 kv Kirillovo | 2,5+2,5 | 0.2676 | 0.37 | 120 | -0.1024 | 0 | 2.625 | 2.7274 | 2.7274 | opened | 63 | SS 35/10 kv Kirillovo | 2,5+2,5 |  | 0.2676 | 0.37 | 120 | -0.1024 | 0 | 2.625 | 2.7274 | 2.7274 | opened
64 | SS 35/10 kv Ksizovo | 2,5+2,5 | 0.28007 | 0.37 | 120 | -0.089927 | 0 | 2.625 | 2.7149 | 2.7149 | opened | 64 | SS 35/10 kv Ksizovo | 2,5+2,5 |  | 0.28007 | 0.37 | 120 | -0.089927 | 0 | 2.625 | 2.7149 | 2.7149 | opened
65 | SS 35/10 kv Lamskoe | 2,5+2,5 | 1.8543 | 0.37 | 120 | 1.4843 | 0 | 2.625 | 1.1407 | 1.1407 | opened | 65 | SS 35/10 kv Lamskoe | 2,5+2,5 | 0.003 | 1.8573 | 0.37 | 120 | 1.4873 | 0 | 2.625 | 1.1377 | 1.1377 | opened
66 | SS 35/10 kv Kazachye | 2,5+2,5 | 0.60016 | 0.37 | 120 | 0.23016 | 0 | 2.625 | 2.3948 | 2.3948 | opened | 66 | SS 35/10 kv Kazachye | 2,5+2,5 | 0.045 | 0.64516 | 0.37 | 120 | 0.27516 | 0 | 2.625 | 2.3498 | 2.3498 | opened
67 | SS 35/10 kv Lebyazhye | 2,5+1,6 | 0.37066 | 0.24 | 120 | 0.13066 | 0 | 1.68 | 1.5493 | 1.5493 | opened | 67 | SS 35/10 kv Lebyazhye | 2,5+1,6 | 0.002 | 0.37266 | 0.24 | 120 | 0.13266 | 0 | 1.68 | 1.5473 | 1.5473 | opened
68 | SS 35/10 kv Lomovets | 1,6+2,5 | 0.33463 | 0.24 | 120 | 0.094632 | 0 | 1.68 | 1.5854 | 1.5854 | opened | 68 | SS 35/10 kv Lomovets | 1,6+2,5 | 0.022 | 0.35663 | 0.24 | 120 | 0.11663 | 0 | 1.68 | 1.5634 | 1.5634 | opened
69 | SS 35/10 kv Olshanets | 2,5+4 | 1.0891 | 0 | 0 | 1.0891 | 0 | 2.625 | 1.5359 | 1.5359 | opened | 69 | SS 35/10 kv Olshanets | 2,5+4 | 0.01 | 1.0991 | 0 | 0 | 1.0991 | 0 | 2.625 | 1.5259 | 1.5259 | opened
70 | SS 35/10 kv Ploskoe | 4+4 | 3.4918 | 0.6 | 120 | 2.8918 | 0 | 4.2 | 1.3082 | 1.3082 | opened | 70 | SS 35/10 kv Ploskoe | 4+4 | 0.09 | 3.5818 | 0.6 | 120 | 2.9818 | 0 | 4.2 | 1.2182 | 1.2182 | opened
71 | SS 35/10 kv Stegalovka | 2,5+3,2 | 0.37845 | 0.37 | 120 | 0.0084531 | 0 | 2.625 | 2.6165 | 2.6165 | opened | 71 | SS 35/10 kv Stegalovka | 2,5+3,2 | 0.01 | 0.38845 | 0.37 | 120 | 0.018453 | 0 | 2.625 | 2.6065 | 2.6065 | opened
72 | SS 35/10 kv Solidarnost | 4+4 | 1.3432 | 0.6 | 120 | 0.74321 | 0 | 4.2 | 3.4568 | 3.4568 | opened | 72 | SS 35/10 kv Solidarnost | 4+4 | 0.087 | 1.4302 | 0.6 | 120 | 0.83021 | 0 | 4.2 | 3.3698 | 3.3698 | opened
73 | SS 35/10 kv Timiryazevo | 4+4 | 0.82532 | 0.6 | 120 | 0.22532 | 0 | 4.2 | 3.9747 | 3.9747 | opened | 73 | SS 35/10 kv Timiryazevo | 4+4 | 0.005 | 0.83032 | 0.6 | 120 | 0.23032 | 0 | 4.2 | 3.9697 | 3.9697 | opened
74 | SS 35/10 kv Talitsa | 2,5+2,5 | 1.6732 | 0 | 0 | 1.6732 | 0 | 2.625 | 0.95184 | 0.95184 | opened | 74 | SS 35/10 kv Talitsa | 2,5+2,5 | 0.023 | 1.6962 | 0 | 0 | 1.6962 | 0 | 2.625 | 0.92884 | 0.92884 | opened
75 | SS 35/10 kv the II Terbuny | 2,5+2,5 | 0.80783 | 0.37 | 120 | 0.43783 | 0 | 2.625 | 2.1872 | 2.1872 | opened | 75 | SS 35/10 kv the II Terbuny | 2,5+2,5 | 1.07 | 1.8778 | 0.37 | 120 | 1.5078 | 0 | 2.625 | 1.1172 | 1.1172 | opened
76 | SS 35/10 kv Tikhii Don | 4+4 | 0.41985 | 0.6 | 120 | -0.18015 | 0 | 4.2 | 4.3802 | 4.3802 | opened | 76 | SS 35/10 kv Tikhii Don | 4+4 | 0.015 | 0.43485 | 0.6 | 120 | -0.16515 | 0 | 4.2 | 4.3652 | 4.3652 | opened
77 | SS 35/10 kv Khitrovo | 6,3+6,3 | 0.77734 | 0 | 0 | 0.77734 | 0 |  | -0.77734 | -0.77734 | closed | 77 | SS 35/10 kv Khitrovo | 6,3+6,3 |  | 0.77734 | 0 | 0 | 0.77734 | 0 |  | -0.77734 | -0.77734 | closed
78 | SS 35/10 kv Chernava | 2,5+2,5 | 1.6591 | 0 | 0 | 1.6591 | 0 | 2.625 | 0.96587 | 0.96587 | opened | 78 | SS 35/10 kv Chernava | 2,5+2,5 | 0.005 | 1.6641 | 0 | 0 | 1.6641 | 0 | 2.625 | 0.96087 | 0.96087 | opened
79 | SS 35/10 kv Chernoles | 2,5+2,5 | 0.2702 | 0 | 0 | 0.2702 | 0 | 2.625 | 2.3548 | 2.3548 | opened | 79 | SS 35/10 kv Chernoles | 2,5+2,5 |  | 0.2702 | 0 | 0 | 0.2702 | 0 | 2.625 | 2.3548 | 2.3548 | opened
80 | SS 35/6 kv SS No. 5 | 6,3+3,2 | 1.149 | 0 | 0 | 1.149 | 0 |  | -1.149 | -1.149 | closed | 80 | SS 35/6 kv SS No. 5 | 6,3+3,2 |  | 1.149 | 0 | 0 | 1.149 | 0 |  | -1.149 | -1.149 | closed
81 | SS 35/10 kv Krasnoe | 4+4 | 3.3505 | 0.4 | 120 | 2.9505 | 0 | 4.2 | 1.2495 | 1.2495 | opened | 81 | SS 35/10 kv Krasnoe | 4+4 | 0.052 | 3.4025 | 0.4 | 120 | 3.0025 | 0 | 4.2 | 1.1975 | 1.1975 | opened
82 | SS 35/10 kv Tyoploe | 2,5+2,5 | 1.1016 | 0.25 | 120 | 0.85158 | 0 | 2.625 | 1.7734 | 1.7734 | opened | 82 | SS 35/10 kv Tyoploe | 2,5+2,5 | 0.006 | 1.1076 | 0.25 | 120 | 0.85758 | 0 | 2.625 | 1.7674 | 1.7674 | opened
83 | SS 35/10 kv Dankov-village | 6,3+4 | 4.5726 | 0.4 | 120 | 4.1726 | 0 | 4.2 | 0.027386 | 0.027386 | opened | 83 | SS 35/10 kv Dankov-village | 6,3+6,3 | 0.19 | 4.7626 | 0.4 | 120 | 4.3626 | 0 | 6.615 | 2.2524 | 2.2524 | opened
84 | SS 35/10 kv Kolybelskaya | 2,5+2,5 | 1.0184 | 0 | 0 | 1.0184 | 0 | 2.625 | 1.6066 | 1.6066 | opened | 84 | SS 35/10 kv Kolybelskaya | 2,5+2,5 |  | 1.0184 | 0 | 0 | 1.0184 | 0 | 2.625 | 1.6066 | 1.6066 | opened
85 | SS 35/10 kv Topki | 2,5+2,5 | 0.2728 | 0.5 | 120 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened | 85 | SS 35/10 kv Topki | 2,5+2,5 |  | 0.2728 | 0.5 | 120 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened
86 | SS 35/10 kv Agronom | 4+6,3 | 1.6494 | 0.8 | 120 | 0.84943 | 0 | 4.2 | 3.3506 | 3.3506 | opened | 86 | SS 35/10 kv Agronom | 4+6,3 |  | 1.6494 | 0.8 | 120 | 0.84943 | 0 | 4.2 | 3.3506 | 3.3506 | opened
87 | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 1.8013 | 0.5 | 120 | 1.3013 | 0 | 2.625 | 1.3237 | 1.3237 | opened | 87 | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 0.0255 | 1.8268 | 0.5 | 120 | 1.3268 | 0 | 2.625 | 1.2982 | 1.2982 | opened
88 | SS 35/10 kv Gagarino | 1,8+1,8 | 0.45466 | 0.36 | 120 | 0.094663 | 0 |  | -0.094663 | -0.094663 | closed | 88 | SS 35/10 kv Gagarino | 1,8+1,8 |  | 0.45466 | 0.36 | 120 | 0.094663 | 0 |  | -0.094663 | -0.094663 | closed
89 | SS 35/10 kv Ranenburg | 1,6+1,6 | 1.5852 | 0.16 | 120 | 1.4252 | 0 | 1.68 | 0.25483 | 0.25483 | opened | 89 | SS 35/10 kv Ranenburg | 1,6+1,6 | 0.015 | 1.6002 | 0.16 | 120 | 1.4402 | 0 | 1.68 | 0.23983 | 0.23983 | opened
90 | SS 35/10 kv Sergievka | 2,5+2,5 | 0.41829 | 0.25 | 120 | 0.16829 | 0 | 2.625 | 2.4567 | 2.4567 | opened | 90 | SS 35/10 kv Sergievka | 2,5+2,5 |  | 0.41829 | 0.25 | 120 | 0.16829 | 0 | 2.625 | 2.4567 | 2.4567 | opened
91 | SS 35/10 kv Drezgalovo | 1,6+1,6 | 0.37464 | 0.48 | 120 | -0.10536 | 0 | 1.68 | 1.7854 | 1.7854 | opened | 91 | SS 35/10 kv Drezgalovo | 1,6+1,6 |  | 0.37464 | 0.48 | 120 | -0.10536 | 0 | 1.68 | 1.7854 | 1.7854 | opened
92 | SS 35/10 kv Dolgoe | 2,5+2,5 | 0.25461 | 0 | 0 | 0.25461 | 0 | 2.625 | 2.3704 | 2.3704 | opened | 92 | SS 35/10 kv Dolgoe | 2,5+2,5 |  | 0.25461 | 0 | 0 | 0.25461 | 0 | 2.625 | 2.3704 | 2.3704 | opened
93 | SS 35/10 kv Voskresenovka | 1,6+1,6 | 0.60016 | 0 | 0 | 0.60016 | 0 | 1.68 | 1.0798 | 1.0798 | opened | 93 | SS 35/10 kv Voskresenovka | 1,6+1,6 | 0.01 | 0.61016 | 0 | 0 | 0.61016 | 0 | 1.68 | 1.0698 | 1.0698 | opened
94 | SS 35/10 kv Saprykino | 1,6+2,5 | 0.45033 | 0.16 | 120 | 0.29033 | 0 | 1.68 | 1.3897 | 1.3897 | opened | 94 | SS 35/10 kv Saprykino | 1,6+2,5 |  | 0.45033 | 0.16 | 120 | 0.29033 | 0 | 1.68 | 1.3897 | 1.3897 | opened
95 | SS 35/10 kv Nopolyanye | 2,5+2,5 | 0.57452 | 0 | 0 | 0.57452 | 0 | 2.625 | 2.0505 | 2.0505 | opened | 95 | SS 35/10 kv Nopolyanye | 2,5+2,5 | 0.012 | 0.58652 | 0 | 0 | 0.58652 | 0 | 2.625 | 2.0385 | 2.0385 | opened
96 | SS 35/10 kv Vednoe | 2,5+2,5 | 1.2003 | 0.25 | 120 | 0.95031 | 0 | 2.625 | 1.6747 | 1.6747 | opened | 96 | SS 35/10 kv Vednoe | 2,5+2,5 | 0.007 | 1.2073 | 0.25 | 120 | 0.95731 | 0 | 2.625 | 1.6677 | 1.6677 | opened
97 | SS 35/10 kv Bigildino | 2,5+2,5 | 0.98121 | 0 | 0 | 0.98121 | 0 | 2.625 | 1.6438 | 1.6438 | opened | 97 | SS 35/10 kv Bigildino | 2,5+2,5 |  | 0.98121 | 0 | 0 | 0.98121 | 0 | 2.625 | 1.6438 | 1.6438 | opened
98 | SS 35/10 kv Kultura | 2,5+2,5 | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened | 98 | SS 35/10 kv Kultura | 2,5+2,5 | 0.005 | 0.95763 | 0.37 | 120 | 0.58763 | 0 | 2.625 | 2.0374 | 2.0374 | opened
99 | SS 35/10 kv Baryatino | 2,5+2,5 | 0.29653 | 0 | 0 | 0.29653 | 0 | 2.625 | 2.3285 | 2.3285 | opened | 99 | SS 35/10 kv Baryatino | 2,5+2,5 |  | 0.29653 | 0 | 0 | 0.29653 | 0 | 2.625 | 2.3285 | 2.3285 | opened
100 | SS 35/10 kv B.Popovo | 2,5+2,5 | 1.3822 | 0.5 | 120 | 0.88218 | 0 | 2.625 | 1.7428 | 1.7428 | opened | 100 | SS 35/10 kv B.Popovo | 2,5+2,5 | 0.008 | 1.3902 | 0.5 | 120 | 0.89018 | 0 | 2.625 | 1.7348 | 1.7348 | opened
101 | SS 35/10 kv B. Izbishchi | 2,5+2,5 | 1.364 | 0.37 | 120 | 0.99399 | 0 | 2.625 | 1.631 | 1.631 | opened | 101 | SS 35/10 kv B. Izbishchi | 2,5+2,5 |  | 1.364 | 0.37 | 120 | 0.99399 | 0 | 2.625 | 1.631 | 1.631 | opened
102 | SS 35/10 kv Polibino | 2,5+2,5 | 0.29376 | 0 | 0 | 0.29376 | 0 | 2.625 | 2.3312 | 2.3312 | opened | 102 | SS 35/10 kv Polibino | 2,5+2,5 | 0.02 | 0.31376 | 0 | 0 | 0.31376 | 0 | 2.625 | 2.3112 | 2.3112 | opened
103 | SS 35/10 kv Dubrava | 2,5+2,5 | 0.17321 | 0 | 0 | 0.17321 | 0 | 2.625 | 2.4518 | 2.4518 | opened | 103 | SS 35/10 kv Dubrava | 2,5+2,5 |  | 0.17321 | 0 | 0 | 0.17321 | 0 | 2.625 | 2.4518 | 2.4518 | opened
104 | SS 35/10 kv Khrushchevo | 2,5+2,5 | 0.446 | 0 | 0 | 0.446 | 0 | 2.625 | 2.179 | 2.179 | opened | 104 | SS 35/10 kv Khrushchevo | 2,5+2,5 | 0.03 | 0.476 | 0 | 0 | 0.476 | 0 | 2.625 | 2.149 | 2.149 | opened
105 | SS 35/10 kv B. Verkh | 2,5+2,5 | 0.87295 | 0.25 | 120 | 0.62295 | 0 | 2.625 | 2.002 | 2.002 | opened | 105 | SS 35/10 kv B. Verkh | 2,5+2,5 |  | 0.87295 | 0.25 | 120 | 0.62295 | 0 | 2.625 | 2.002 | 2.002 | opened
106 | SS 35/10 kv Golovinshchino | 2,5+2,5 | 0.31177 | 0 | 0 | 0.31177 | 0 | 2.625 | 2.3132 | 2.3132 | opened | 106 | SS 35/10 kv Golovinshchino | 2,5+2,5 |  | 0.31177 | 0 | 0 | 0.31177 | 0 | 2.625 | 2.3132 | 2.3132 | opened
107 | SS 35/10 kv Yablonevoe | 2,5+2,5 | 0.51442 | 0.25 | 120 | 0.26442 | 0 | 2.625 | 2.3606 | 2.3606 | opened | 107 | SS 35/10 kv Yablonevoe | 2,5+2,5 | 0.01837 | 0.53279 | 0.25 | 120 | 0.28279 | 0 | 2.625 | 2.3422 | 2.3422 | opened
108 | SS 35/10 kv Politovo | 2,5+2,5 | 0.88958 | 0 | 0 | 0.88958 | 0 | 2.625 | 1.7354 | 1.7354 | opened | 108 | SS 35/10 kv Politovo | 2,5+2,5 |  | 0.88958 | 0 | 0 | 0.88958 | 0 | 2.625 | 1.7354 | 1.7354 | opened
109 | SS 35/10 kv Complex | 4+4 | 0.83398 | 1.2 | 120 | -0.36602 | 0 | 4.2 | 4.566 | 4.566 | opened | 109 | SS 35/10 kv Complex | 4+4 |  | 0.83398 | 1.2 | 120 | -0.36602 | 0 | 4.2 | 4.566 | 4.566 | opened
110 | SS 35/10 kv No.1 | 4+4 | 3.742 | 0.45 | 120 | 3.292 | 0 | 4.2 | 0.90801 | 0.90801 | opened | 110 | SS 35/10 kv No.1 | 4+4 | 0.165 | 3.907 | 0.45 | 120 | 3.457 | 0 | 4.2 | 0.74301 | 0.74301 | opened
111 | SS 35/6 kv No. 2 | 1+1+1 | 0.70844 | 0 | 0 | 0.70844 | 0 | 2.1 | 1.3916 | 1.3916 | opened | 111 | SS 35/6 kv No. 2 | 1+1+1 | 0.1 | 0.80844 | 0 | 0 | 0.80844 | 0 | 2.1 | 1.2916 | 1.2916 | opened
112 | SS 35/10 kv No. 3 | 2,5+2,5 | 1.1761 | 0.25 | 120 | 0.92605 | 0 | 2.625 | 1.6989 | 1.6989 | opened | 112 | SS 35/10 kv No. 3 | 2,5+2,5 | 0.0865 | 1.2626 | 0.25 | 120 | 1.0126 | 0 | 2.625 | 1.6124 | 1.6124 | opened
113 | SS 35/6 kv No. 4 | 4+4 | 2.6921 | 0.4 | 120 | 2.2921 | 0 | 4.2 | 1.9079 | 1.9079 | opened | 113 | SS 35/6 kv No. 4 | 4+4 | 0.073 | 2.7651 | 0.4 | 120 | 2.3651 | 0 | 4.2 | 1.8349 | 1.8349 | opened
114 | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 4.0735 | 0.56 | 120 | 3.5135 | 0 | 5.88 | 2.3665 | 2.3665 | opened | 114 | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 1.087 | 5.1605 | 0.56 | 120 | 4.6005 | 0 | 5.88 | 1.2795 | 1.2795 | opened
115 | SS 35/10 kv Butyrki | 5,6+4 | 5.7765 | 0.4 | 120 | 5.3765 | 0 | 4.2 | -1.1765 | -1.1765 | opened | 115 | SS 35/10 kv Butyrki | 5,6+4 | 0.6 | 6.3765 | 0.4 | 120 | 5.9765 | 0 | 4.2 | -1.7765 | -1.7765 | opened
116 | SS 35/10 kv Yarlukovo | 3,2+4 | 2.7334 | 0.32 | 120 | 2.4134 | 0 | 3.36 | 0.9466 | 0.9466 | opened | 116 | SS 35/10 kv Yarlukovo | 3,2+4 | 0.251 | 2.9844 | 0.32 | 120 | 2.6644 | 0 | 3.36 | 0.6956 | 0.6956 | opened
117 | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 0.45413 | 0.16 | 120 | 0.29413 | 0 | 1.68 | 1.3859 | 1.3859 | opened | 117 | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 0.005 | 0.45913 | 0.16 | 120 | 0.29912 | 0 | 1.68 | 1.3809 | 1.3809 | opened
118 | SS 35/10 kv Pravda | 4+2,5 | 1.2534 | 0.25 | 120 | 1.0034 | 0 | 2.625 | 1.6216 | 1.6216 | opened | 118 | SS 35/10 kv Pravda | 4+2,5 | 0.01 | 1.2634 | 0.25 | 120 | 1.0134 | 0 | 2.625 | 1.6116 | 1.6116 | opened
119 | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 | 0.55775 | 0.38 | 120 | 0.17775 | 0 | 2.625 | 2.4472 | 2.4472 | opened | 119 | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 |  | 0.55775 | 0.38 | 120 | 0.17775 | 0 | 2.625 | 2.4472 | 2.4472 | opened
120 | SS 35/10 kv Matyra | 4+3,2 | 3.0054 | 0.45 | 120 | 2.5554 | 0 | 3.36 | 0.80464 | 0.80464 | opened | 120 | SS 35/10 kv Matyra | 4+3,2 | 0.176 | 3.1814 | 0.45 | 120 | 2.7314 | 0 | 3.36 | 0.62864 | 0.62864 | opened
121 | SS 35/10 kv Vperyod | 4+4 | 0.79926 | 0.8 | 120 | -0.00074 | 0 | 4.2 | 4.2007 | 4.2007 | opened | 121 | SS 35/10 kv Vperyod | 4+4 | 0.03 | 0.82926 | 0.8 | 120 | 0.02926 | 0 | 4.2 | 4.1707 | 4.1707 | opened
122 | SS 35/10 kv Maley | 4+2,5 | 0.3633 | 0.38 | 120 | -0.0167 | 0 | 2.625 | 2.6417 | 2.6417 | opened | 122 | SS 35/10 kv Maley | 4+2,5 |  | 0.3633 | 0.38 | 120 | -0.0167 | 0 | 2.625 | 2.6417 | 2.6417 | opened
123 | SS 35/10 kv SKhТ | 2,5+1,6 | 0.67055 | 0.48 | 120 | 0.19055 | 0 | 1.68 | 1.4895 | 1.4895 | opened | 123 | SS 35/10 kv SKhТ | 2,5+1,6 | 0.545 | 1.2155 | 0.48 | 120 | 0.73555 | 0 | 1.68 | 0.94445 | 0.94445 | opened
124 | SS 35/10 kv Soshki | 4+4 | 0.27507 | 0.4 | 120 | -0.12493 | 0 | 4.2 | 4.3249 | 4.3249 | opened | 124 | SS 35/10 kv Soshki | 4+4 | 0.04 | 0.31507 | 0.4 | 120 | -0.08493 | 0 | 4.2 | 4.2849 | 4.2849 | opened
125 | SS 35/6 kv Tavolzhanka | 4+4 | 2.7092 | 0.4 | 120 | 2.3092 | 0 | 4.2 | 1.8908 | 1.8908 | opened | 125 | SS 35/6 kv Tavolzhanka | 4+4 | 0.9705 | 3.6797 | 0.4 | 120 | 3.2797 | 0 | 4.2 | 0.92032 | 0.92032 | opened
126 | SS 35/10 kv Trubetchino | 2,5+2,5 | 1.0588 | 0.15 | 120 | 0.90876 | 0 | 2.625 | 1.7162 | 1.7162 | opened | 126 | SS 35/10 kv Trubetchino | 2,5+2,5 | 0.046 | 1.1048 | 0.15 | 120 | 0.95476 | 0 | 2.625 | 1.6702 | 1.6702 | opened
127 | SS 35/10 kv Ratchino | 2,5+2,5 | 0.96274 | 0.75 | 120 | 0.21274 | 0 | 2.625 | 2.4123 | 2.4123 | opened | 127 | SS 35/10 kv Ratchino | 2,5+2,5 | 0.005 | 0.96774 | 0.75 | 120 | 0.21774 | 0 | 2.625 | 2.4073 | 2.4073 | opened
128 | SS 35/10 kv Kalikino | 3,2+3,2 | 1.6321 | 0.3 | 120 | 1.3321 | 0 | 3.36 | 2.0279 | 2.0279 | opened | 128 | SS 35/10 kv Kalikino | 3,2+3,2 | 0.01 | 1.6421 | 0.3 | 120 | 1.3421 | 0 | 3.36 | 2.0179 | 2.0179 | opened
129 | SS 35/10 kv Borisovka | 4+2,5 | 2.7429 | 0.37 | 120 | 2.3729 | 0 | 2.625 | 0.25209 | 0.25209 | opened | 129 | SS 35/10 kv Borisovka | 4+2,5 | 0.56 | 3.3029 | 0.37 | 120 | 2.9329 | 0 | 2.625 | -0.30791 | -0.30791 | closed
130 | SS 35/10 kv Vvedenka | 4+4 | 3.0586 | 0.2 | 120 | 2.8586 | 0 | 4.2 | 1.3414 | 1.3414 | opened | 130 | SS 35/10 kv Vvedenka | 4+4 | 0.638 | 3.6966 | 0.2 | 120 | 3.4966 | 0 | 4.2 | 0.70336 | 0.70336 | opened
131 | SS 35/10 kv Gryaznoe | 4+4 | 2.5009 | 0 | 0 | 2.5009 | 0 | 4.2 | 1.6991 | 1.6991 | opened | 131 | SS 35/10 kv Gryaznoe | 4+4 | 0.025 | 2.5259 | 0 | 0 | 2.5259 | 0 | 4.2 | 1.6741 | 1.6741 | opened
132 | SS 35/10 kv Borino | 4+4 | 4.3596 | 0.2 | 120 | 4.1596 | 0 | 4.2 | 0.0404 | 0.0404 | opened | 132 | SS 35/10 kv Borino | 6,3+6,3 | 0.351 | 4.7106 | 0.2 | 120 | 4.5106 | 0 | 6.615 | 2.1044 | 2.1044 | opened
133 | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 1.1626 | 0.5 | 120 | 0.66256 | 0 | 2.625 | 1.9624 | 1.9624 | opened | 133 | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 0.042 | 1.2046 | 0.5 | 120 | 0.70456 | 0 | 2.625 | 1.9204 | 1.9204 | opened
134 | SS 35/10 kv Troitskaya | 2,5+4 | 2.285 | 0.25 | 120 | 2.035 | 0 | 2.625 | 0.59002 | 0.59002 | opened | 134 | SS 35/10 kv Troitskaya | 2,5+4 | 0.099 | 2.384 | 0.25 | 120 | 2.134 | 0 | 2.625 | 0.49102 | 0.49102 | opened
135 | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.80445 | 0 | 0 | 0.80445 | 0 | 2.625 | 1.8205 | 1.8205 | opened | 135 | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.005 | 0.80945 | 0 | 0 | 0.80945 | 0 | 2.625 | 1.8155 | 1.8155 | opened
136 | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.7266 | 0 | 0 | 0.7266 | 0 | 2.625 | 1.8984 | 1.8984 | opened | 136 | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.014 | 0.7406 | 0 | 0 | 0.7406 | 0 | 2.625 | 1.8844 | 1.8844 | opened
137 | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.95288 | 0.13 | 120 | 0.82288 | 0 | 2.625 | 1.8021 | 1.8021 | opened | 137 | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.007 | 0.95988 | 0.13 | 120 | 0.82988 | 0 | 2.625 | 1.7951 | 1.7951 | opened
138 | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 4.8129 | 0.63 | 120 | 4.1829 | 0 | 6.615 | 2.4321 | 2.4321 | opened | 138 | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 0.017 | 4.8299 | 0.63 | 120 | 4.1999 | 0 | 6.615 | 2.4151 | 2.4151 | opened
139 | SS 35/10 kv Sentsovo | 10+10 | 6.8603 | 0.5 | 120 | 6.3603 | 0 | 10.5 | 4.1397 | 4.1397 | opened | 139 | SS 35/10 kv Sentsovo | 10+10 | 0.026 | 6.8863 | 0.5 | 120 | 6.3863 | 0 | 10.5 | 4.1137 | 4.1137 | opened
140 | SS 35/10 kv Meet processing factory | 6,3+6,3 | 4.8578 | 1.26 | 0 | 3.5978 | 0 | 6.62 | 3.0222 | 3.0222 | opened | 140 | SS 35/10 kv Meet processing factory | 6,3+6,3 | 0.55 | 5.4078 | 1.26 | 0 | 4.1478 | 0 | 6.62 | 2.4722 | 2.4722 | opened
141 | SS 35/6 kv Poultry plant | 4+4 | 2.9894 | 0 | 0 | 2.9894 | 0 | 4.2 | 1.2106 | 1.2106 | opened | 141 | SS 35/6 kv Poultry plant | 4+4 | 0.005 | 2.9944 | 0 | 0 | 2.9944 | 0 | 4.2 | 1.2056 | 1.2056 | opened
142 | SS 35/6 kv Water intake | 10+10 | 1.1292 | 0 | 0 | 1.1292 | 0 | 10.5 | 9.3708 | 9.3708 | opened | 142 | SS 35/6 kv Water intake | 10+10 | 0.1325 | 1.2617 | 0 | 0 | 1.2617 | 0 | 10.5 | 9.2383 | 9.2383 | opened
143 | SS 35/10 kv Petrovskaya | 2,5+4 | 1.3698 | 0.25 | 120 | 1.1198 | 0 | 2.625 | 1.5052 | 1.5052 | opened | 143 | SS 35/10 kv Petrovskaya | 2,5+4 | 0.005 | 1.3748 | 0.25 | 120 | 1.1248 | 0 | 2.625 | 1.5002 | 1.5002 | opened
144 | SS 35/10 kv Lebedyanka | 2,5+2,5 | 0.33008 | 0.25 | 120 | 0.080084 | 0 | 2.625 | 2.5449 | 2.5449 | opened | 144 | SS 35/10 kv Lebedyanka | 2,5+2,5 |  | 0.33008 | 0.25 | 120 | 0.080084 | 0 | 2.625 | 2.5449 | 2.5449 | opened
145 | SS 35/10 kv Novocherkutino | 4+4 | 0.833 | 0.4 | 120 | 0.433 | 0 | 4.2 | 3.767 | 3.767 | opened | 145 | SS 35/10 kv Novocherkutino | 4+4 |  | 0.833 | 0.4 | 120 | 0.433 | 0 | 4.2 | 3.767 | 3.767 | opened
146 | SS 35/10 kv Ivanovka | 2,5+2,5 | 0.92659 | 0 | 0 | 0.92659 | 0 | 2.625 | 1.6984 | 1.6984 | opened | 146 | SS 35/10 kv Ivanovka | 2,5+2,5 |  | 0.92659 | 0 | 0 | 0.92659 | 0 | 2.625 | 1.6984 | 1.6984 | opened
147 | SS 35/10 kv Poddubrovka | 2,5+2,5 | 1.1335 | 0.3 | 0 | 0.8335 | 0 | 2.625 | 1.7915 | 1.7915 | opened | 147 | SS 35/10 kv Poddubrovka | 2,5+2,5 | 0.025 | 1.1585 | 0.3 | 0 | 0.8585 | 0 | 2.625 | 1.7665 | 1.7665 | opened
148 | SS 35/10 kv Plavitsa | 1,6+1,6 | 0.69494 | 0.16 | 120 | 0.53494 | 0 | 1.68 | 1.1451 | 1.1451 | opened | 148 | SS 35/10 kv Plavitsa | 1,6+1,6 | 0.005 | 0.69994 | 0.16 | 120 | 0.53994 | 0 | 1.68 | 1.1401 | 1.1401 | opened
149 | SS 35/10 kv Parshinovka | 1,6+2,5 | 0.34842 | 0 | 0 | 0.34842 | 0 | 1.68 | 1.3316 | 1.3316 | opened | 149 | SS 35/10 kv Parshinovka | 1,6+2,5 |  | 0.34842 | 0 | 0 | 0.34842 | 0 | 1.68 | 1.3316 | 1.3316 | opened
150 | SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 1.2103 | 0.32 | 120 | 0.89031 | 0 | 3.36 | 2.4697 | 2.4697 | opened | 150 | SS 35/10 kv Talitsky Chamlyk | 3,2+4 |  | 1.2103 | 0.32 | 120 | 0.89031 | 0 | 3.36 | 2.4697 | 2.4697 | opened
151 | SS 35/10 kv Demshinka | 2,5+2,5 | 0.21383 | 0.25 | 120 | -0.036172 | 0 | 2.625 | 2.6612 | 2.6612 | opened | 151 | SS 35/10 kv Demshinka | 2,5+2,5 |  | 0.21383 | 0.25 | 120 | -0.036172 | 0 | 2.625 | 2.6612 | 2.6612 | opened
152 | SS 35/10 kv Bereznyagovka | 1,6+1,6 | 0.81742 | 0.24 | 120 | 0.57742 | 0 | 1.68 | 1.1026 | 1.1026 | opened | 152 | SS 35/10 kv Bereznyagovka | 1,6+1,6 |  | 0.81742 | 0.24 | 120 | 0.57742 | 0 | 1.68 | 1.1026 | 1.1026 | opened
153 | SS 35/10 kv Dmitrievka | 2,5+2,5 | 0.41382 | 0.38 | 120 | 0.033816 | 0 | 2.625 | 2.5912 | 2.5912 | opened | 153 | SS 35/10 kv Dmitrievka | 2,5+2,5 |  | 0.41382 | 0.38 | 120 | 0.033816 | 0 | 2.625 | 2.5912 | 2.5912 | opened
154 | SS 35/10 kv Pashkovo | 2,5+2,5 | 1.0513 | 0.38 | 120 | 0.67132 | 0 | 2.625 | 1.9537 | 1.9537 | opened | 154 | SS 35/10 kv Pashkovo | 2,5+2,5 |  | 1.0513 | 0.38 | 120 | 0.67132 | 0 | 2.625 | 1.9537 | 1.9537 | opened
155 | SS 35/10 kv Moskovka | 1,6+1,6 | 0.52678 | 0.24 | 120 | 0.28679 | 0 | 1.68 | 1.3932 | 1.3932 | opened | 155 | SS 35/10 kv Moskovka | 1,6+1,6 | 0.028 | 0.55478 | 0.24 | 120 | 0.31478 | 0 | 1.68 | 1.3652 | 1.3652 | opened
156 | SS 35/10 kv Bochinovka | 4+4 | 2.5189 | 0.6 | 120 | 1.9189 | 0 | 4.2 | 2.2811 | 2.2811 | opened | 156 | SS 35/10 kv Bochinovka | 4+4 | 1.175 | 3.6939 | 0.6 | 120 | 3.0939 | 0 | 4.2 | 1.1061 | 1.1061 | opened
157 | SS 35/10 kv Fyodorovka | 2,5+2,5 | 0.33008 | 0.38 | 120 | -0.049916 | 0 | 2.625 | 2.6749 | 2.6749 | opened | 157 | SS 35/10 kv Fyodorovka | 2,5+2,5 |  | 0.33008 | 0.38 | 120 | -0.049916 | 0 | 2.625 | 2.6749 | 2.6749 | opened
158 | SS 35/10 kv Kulikovo | 2,5+2,5 | 0.30586 | 0 | 0 | 0.30586 | 0 | 2.625 | 2.3191 | 2.3191 | opened | 158 | SS 35/10 kv Kulikovo | 2,5+2,5 | 0.002 | 0.30786 | 0 | 0 | 0.30786 | 0 | 2.625 | 2.3171 | 2.3171 | opened
159 | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 1.0536 | 0.25 | 120 | 0.80357 | 0 | 2.625 | 1.8214 | 1.8214 | opened | 159 | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 0.205 | 1.2586 | 0.25 | 120 | 1.0086 | 0 | 2.625 | 1.6164 | 1.6164 | opened
160 | SS 35/10 kv Dmitryashevka | 2,5+2,5 | 0.12369 | 0.25 | 120 | -0.12631 | 0 | 2.625 | 2.7513 | 2.7513 | opened | 160 | SS 35/10 kv Dmitryashevka | 2,5+2,5 |  | 0.12369 | 0.25 | 120 | -0.12631 | 0 | 2.625 | 2.7513 | 2.7513 | opened
161 | SS 35/10 kv Rechnaya | 4+4 | 0.49045 | 0.6 | 120 | -0.10955 | 0 | 4.2 | 4.3095 | 4.3095 | opened | 161 | SS 35/10 kv Rechnaya | 4+4 | 0.016 | 0.50645 | 0.6 | 120 | -0.093545 | 0 | 4.2 | 4.2935 | 4.2935 | opened
162 | SS 35/10 kv Negachevka | 2,5+2,5 | 0 | 0.25 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | opened | 162 | SS 35/10 kv Negachevka | 2,5+2,5 | 0.0015 | 0.0015 | 0.25 | 120 | -0.2485 | 0 | 2.625 | 2.8735 | 2.8735 | opened
163 | SS 35/10 kv Karamyshevo | 10+10 | 0.49045 | 1 | 120 | -0.50955 | 0 | 10.5 | 11.0095 | 11.0095 | opened | 163 | SS 35/10 kv Karamyshevo | 10+10 | 0.041 | 0.53146 | 1 | 120 | -0.46854 | 0 | 10.5 | 10.9685 | 10.9685 | opened
164 | SS 35/10 kv Tyushevka | 1,6+1,6 |  | 0.08 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened | 164 | SS 35/10 kv Tyushevka | 1,6+1,6 |  | 0 | 0.08 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened
165 | SS 110/35/10 kv Terbuny-110 | 10+10 | 8.7815 | 11 |  | -2.2185 | 0 | 10.5 | 12.7185 | 5.7946 | opened | 165 | SS 110/35/10 kv Terbuny-110 | 10+25 |  | 9.9475 | 11 |  | -1.0525 | 0 | 10.5 | 0.5525 | 0.5525 | opened
| Nom. Capacity MV, МVA | 10+10 | 3.0761 | 10 | 10 | -6.9239 | 0 | 10.5 | 7.4239 |  |  |  | Nom. Capacity MV, МVA | 10+10 |  | 3.0761 | 10 | 10 | -6.9239 | 0 | 10.5 | 7.4239
| Nom. capacity LV, МVA | 10+10 | 5.7054 | 1 | 120 | 4.7054 | 0 | 10.5 | 5.7946 |  |  |  | Nom. capacity LV, МVA | 10+10 | 1.166 | 6.8714 | 1 | 120 | 5.8714 | 0 | 10.5 | 4.6286
166 | SS 110/35/10 kv Dolgorukovo | 6,3+10 | 6.1983 | 6.93 |  | -0.73168 | 0 | 6.615 | 7.3467 | 2.9808 | opened | 166 | SS 110/35/10 kv Dolgorukovo | 6,3+10 |  | 6.2163 | 6.93 |  | -0.71368 | 0 | 6.615 | 0.39868 | 0.39868 | opened
| Nom. capacity MV, МVA | 6,3+10 | 3.6342 | 6.3 | 10 | -2.6658 | 0 | 6.615 | 2.9808 |  |  |  | Nom. capacity MV, МVA | 6,3+10 |  | 3.6342 | 6.3 | 10 | -2.6658 | 0 | 6.615 | 2.9808
| Nom. capacity LV, МVA | 6,3+10 | 2.5641 | 0.63 | 120 | 1.9341 | 0 | 6.615 | 4.6809 |  |  |  | Nom. capacity LV, МVA | 6,3+10 | 0.018 | 2.5821 | 0.63 | 120 | 1.9521 | 0 | 6.615 | 4.6629
167 | SS 110/35/10 kv Volovo | 10+10 | 3.1984 | 3.8 |  | -0.60159 | 0 | 10.5 | 11.1016 | 8.3016 | opened | 167 | SS 110/35/10 kv Volovo | 10+10 |  | 3.2034 | 3.8 |  | -0.59659 | 0 | 10.5 | 7.2966 | 7.2966 | opened
| Nom. capacity MV, МVA | 10+10 | 0 | 2.8 | 20 | -2.8 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVA | 10+10 |  | 0 | 2.8 | 20 | -2.8 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 3.1984 | 1 | 120 | 2.1984 | 0 | 10.5 | 8.3016 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.005 | 3.2034 | 1 | 120 | 2.2034 | 0 | 10.5 | 8.2966
168 | SS 110/35/10 kv Izmalkovo | 10+10 | 6.1332 | 2.5 |  | 3.6332 | 0 | 10.5 | 6.8668 | 6.8668 | opened | 168 | SS 110/35/10 kv Izmalkovo | 10+10 |  | 6.1842 | 2.5 |  | 3.6842 | 0 | 10.5 | 6.8158 | 6.8158 | opened
| Nom. capacity MV, МVА | 10+10 | 2.4595 | 1.5 | 20 | 0.95951 | 0 | 10.5 | 8.0405 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.4595 | 1.5 | 20 | 0.95951 | 0 | 10.5 | 9.5405
| Nom. capacity LV, МVА | 10+10 | 3.6737 | 1 | 120 | 2.6737 | 0 | 10.5 | 7.8263 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.051 | 3.7247 | 1 | 120 | 2.7247 | 0 | 10.5 | 7.7753
169 | SS 110/35/10 kv Gorokhovskaya | 16+16 | 10.0313 | 9.6 |  | 0.43135 | 0 | 16.8 | 16.3687 | 9.9134 | opened | 169 | SS 110/35/10 kv Gorokhovskaya | 16+16 |  | 10.1833 | 9.6 |  | 0.58335 | 0 | 16.8 | 16.2167 | 9.9134 | opened
| Nom. capacity MV, МVА | 16+16 | 6.8866 | 8 | 20 | -1.1134 | 0 | 16.8 | 9.9134 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.8866 | 8 | 20 | -1.1134 | 0 | 16.8 | 9.9134
| Nom. capacity LV, МVА | 16+16 | 3.1447 | 1.6 | 120 | 1.5447 | 0 | 16.8 | 15.2553 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.152 | 3.2967 | 1.6 | 120 | 1.6967 | 0 | 16.8 | 15.1033
170 | SS 110/35/10 kv Donskaya | 10+10 | 5.4128 | 3 |  | 2.4128 | 0 | 10.5 | 8.0872 | 8.0872 | opened | 170 | SS 110/35/10 kv Donskaya | 10+10 |  | 5.4398 | 3 |  | 2.4398 | 0 | 10.5 | 8.0602 | 8.0602 | opened
| Nom. capacity MV, МVА | 10+10 | 2.1124 | 2 | 20 | 0.11241 | 0 | 10.5 | 8.3876 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.1124 | 2 | 20 | 0.11241 | 0 | 10.5 | 10.3876
| Nom. capacity LV, МVА | 10+10 | 3.3004 | 1 | 120 | 2.3004 | 0 | 10.5 | 8.1996 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.027 | 3.3274 | 1 | 120 | 2.3274 | 0 | 10.5 | 8.1726
171 | SS 110/35/10 kv Lebedyan | 16+16 | 20.4417 | 17.6 |  | 2.8417 | 0 | 16.8 | 13.9583 | 7.1975 | opened | 171 | SS 110/35/10 kv Lebedyan | 16+16 |  | 20.6057 | 17.6 |  | 3.0057 | 0 | 16.8 | 13.7943 | 7.1975 | opened
| Nom. capacity MV, МVА | 16+16 | 9.6025 | 16 | 10 | -6.3975 | 0 | 16.8 | 7.1975 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 9.6025 | 16 | 10 | -6.3975 | 0 | 16.8 | 7.1975
| Nom. capacity LV, МVА | 16+16 | 10.8392 | 1.6 | 120 | 9.2392 | 0 | 16.8 | 7.5608 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.164 | 11.0032 | 1.6 | 120 | 9.4032 | 0 | 16.8 | 7.3968
172 | SS 110/35/10 kv Chaplygin-novaya | 16+16 | 9.4414 | 33.6 |  | -24.1586 | 0 | 16.8 | 40.9586 | 9.9411 | opened | 172 | SS 110/35/10 kv Chaplygin-novaya | 16+16 |  | 9.4674 | 33.6 |  | -24.1326 | 0 | 16.8 | 7.3326 | 7.3326 | opened
| Nom. capacity MV, МVА | 16+16 | 6.8589 | 32 | 10 | -25.1411 | 0 | 16.8 | 9.9411 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.8589 | 32 | 10 | -25.1411 | 0 | 16.8 | 9.9411
| Nom. capacity LV, МVА | 16+16 | 2.5825 | 1.6 | 120 | 0.98249 | 0 | 16.8 | 15.8175 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.026 | 2.6085 | 1.6 | 120 | 1.0085 | 0 | 16.8 | 15.7915
173 | SS 110/35/10 kv Kompressornaya | 16+16 | 5.5166 | 33.6 |  | -28.0834 | 0 | 16.8 | 44.8834 | 12.5565 | opened | 173 | SS 110/35/10 kv Kompressornaya | 16+16 |  | 5.5246 | 33.6 |  | -28.0754 | 0 | 16.8 | 11.2754 | 11.2754 | opened
| Nom. Capacity MV, МVА | 16+16 | 4.2435 | 32 | 10 | -27.7565 | 0 | 16.8 | 12.5565 |  |  |  | Nom. Capacity MV, МVА | 16+16 |  | 4.2435 | 32 | 10 | -27.7565 | 0 | 16.8 | 12.5565
| Nom. capacity LV, МVА | 16+16 | 1.2731 | 1.6 | 120 | -0.32694 | 0 | 16.8 | 17.1269 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.008 | 1.2811 | 1.6 | 120 | -0.31894 | 0 | 16.8 | 15.5189
174 | SS 110/35/10 kv Rossiya | 16+16 | 1.7147 | 26.8 |  | -25.0853 | 0 | 16.8 | 41.8853 | 15.9513 | opened | 174 | SS 110/35/10 kv Rossiya | 16+16 |  | 1.7161 | 26.8 |  | -25.0839 | 0 | 16.8 | 15.0839 | 15.0839 | opened
| Nom. capacity MV, МVА | 16+16 | 0.8487 | 26 |  | -25.1513 | 0 | 16.8 | 15.9513 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 0.8487 | 26 |  | -25.1513 | 0 | 16.8 | 15.9513
| Nom. capacity LV, МVА | 16+16 | 0.86603 | 0.8 | 120 | 0.066025 | 0 | 16.8 | 16.734 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.0014 | 0.86743 | 0.8 | 120 | 0.067425 | 0 | 16.8 | 16.7326
175 | SS 110/35/10 kv Beryozovka | 16+10 | 2.1498 | 25 |  | -22.8502 | 0 | 10.5 | 33.3502 | 9.58 | opened | 175 | SS 110/35/10 kv Beryozovka | 16+10 |  | 2.1998 | 25 |  | -22.8002 | 0 | 10.5 | 8.3002 | 8.3002 | opened
| Nom. capacity MV, МVА | 16+10 | 0.92 | 24 | 10 | -23.08 | 0 | 10.5 | 9.58 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 0.92 | 24 | 10 | -23.08 | 0 | 10.5 | 9.58
| Nom. capacity LV, МVА | 16+10 | 1.2298 | 1 | 120 | 0.22976 | 0 | 10.5 | 10.2702 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.05 | 1.2798 | 1 | 120 | 0.27976 | 0 | 10.5 | 10.2202
176 | SS 110/35/10 kv Astapovo | 16+16 | 3.4139 | 32.8 |  | -29.3861 | 0 | 16.8 | 46.1861 | 14.9917 | opened | 176 | SS 110/35/10 kv Astapovo | 16+16 |  | 3.4519 | 32.8 |  | -29.3481 | 0 | 16.8 | 13.3481 | 13.3481 | opened
| Nom. capacity MV, МVА | 16+16 | 1.8083 | 32 | 10 | -30.1917 | 0 | 16.8 | 14.9917 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 1.8083 | 32 | 10 | -30.1917 | 0 | 16.8 | 14.9917
| Nom. capacity LV, МVА | 16+16 | 1.6056 | 0.8 | 120 | 0.80561 | 0 | 16.8 | 15.9944 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.038 | 1.6436 | 0.8 | 120 | 0.84361 | 0 | 16.8 | 15.9564
177 | SS 110/35/10 kv Khimicheskaya | 16+16 | 9.732 | 15.6 |  | -5.868 | 0 | 16.8 | 22.668 | 9.0466 | opened | 177 | SS 110/35/10 kv Khimicheskaya | 16+16 |  | 9.8 | 15.6 |  | -5.8 | 0 | 16.8 | 7 | 7 | opened
| Nom. capacity MV, МVА | 16+16 | 7.7534 | 14 | 10 | -6.2466 | 0 | 16.8 | 9.0466 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 7.7534 | 14 | 10 | -6.2466 | 0 | 16.8 | 9.0466
| Nom. capacity LV, МVА | 16+16 | 1.9787 | 1.6 | 120 | 0.37869 | 0 | 16.8 | 16.4213 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.068 | 2.0467 | 1.6 | 120 | 0.44669 | 0 | 16.8 | 16.3533
178 | SS 110/35/6 kv Bugor | 15+15+25 | 30.8 | 0.5 |  | 30.3 | 0 | 26.25 | -4.05 | -4.05 | closed | 178 | SS 110/35/6 kv Bugor | 15+15+25 |  | 33.772 | 0.5 |  | 33.272 | 0 | 26.25 | -7.022 | -7.022 | closed
| Nom. capacity MV, МVА | 15+15+25 | 9.8 | 0 | 0 | 9.8 | 0 | 26.25 | 16.45 |  |  |  | Nom. capacity MV, МVА | 15+15+25 |  | 9.8 | 0 | 0 | 9.8 | 0 | 26.25 | 16.45
| Nom. capacity LV, МVА | 15+15+25 | 21 | 0.5 | 40 | 20.5 | 0 | 26.25 | 5.75 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 2.972 | 23.972 | 0.5 | 40 | 23.472 | 0 | 26.25 | 2.778
179 | SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 29.3754 | 3.5 |  | 25.8754 | 0 | 54.6 | 28.7246 | -1.836 | closed | 179 | SS 110/35/6 kvВ Tsementnaya | 63+32+20 |  | 29.3754 | 0 |  | 29.3754 | 0 | 54.6 | 25.2246 | -1.836 | closed
| Nom. capacity MV, МVА | 63+20 | 22.836 | 0 | 0 | 22.836 | 0 | 21 | -1.836 |  |  |  | Nom. capacity MV, МVА | 63+20 |  | 22.836 | 0 | 0 | 22.836 | 0 | 21 | -1.836
| Nom. capacity LV, МVА | 63+32+20 | 6.5394 | 3.5 | 30 | 3.0394 | 0 | 54.6 | 51.5606 |  |  |  | Nom. capacity LV, МVА | 63+32+20 |  | 6.5394 | 0 | 30 | 6.5394 | 0 | 54.6 | 48.0606
180 | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 6.8551 | 10 |  | -3.1449 | 0 | 52.5 | 55.6449 | 1.2632 | opened | 180 | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 |  | 7.3051 | 10 |  | -2.6949 | 0 | 52.5 | 45.1949 | -3.7368 | closed
| Nom. capacity MV, МVА | 31.5 | 3.7368 | 5 | 10 | -1.2632 | 0 | 5 | 1.2632 |  |  |  | Nom. capacity MV, МVА | 31.5 |  | 3.7368 | 5 | 10 | -1.2632 | 0 | 0 | -3.7368
| Nom. capacity LV, МVА | 25+25+31,5 | 3.1183 | 5 | 120 | -1.8817 | 0 | 52.5 | 54.3817 |  |  |  | Nom. capacity LV, МVА | 25+25+31,5 | 0.45 | 3.5683 | 5 | 120 | -1.4317 | 0 | 52.5 | 48.9317
181 | SS 110/35/10 kv Usman | 16+16 | 14.5932 | 17.6 |  | -3.0068 | 0 | 16.8 | 19.8068 | 9.1888 | opened | 181 | SS 110/35/10 kv Usman | 16+16 |  | 15.0282 | 17.6 |  | -2.5718 | 0 | 16.8 | 1.7718 | 1.7718 | opened
| Nom. capacity MV, МVА | 16+16 | 5.382 | 16 | 10 | -10.618 | 0 | 16.8 | 11.418 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 5.382 | 16 | 10 | -10.618 | 0 | 16.8 | 11.418
| Nom. Capacity LV, МVА | 16+16 | 9.2112 | 1.6 | 120 | 7.6112 | 0 | 16.8 | 9.1888 |  |  |  | Nom. Capacity LV, МVА | 16+16 | 0.435 | 9.6462 | 1.6 | 120 | 8.0462 | 0 | 16.8 | 8.7538
182 | SS 110/35/10 kv Aksai | 10+10 | 5.9425 | 11.4 |  | -5.4574 | 0 | 10.5 | 15.9574 | 6.7632 | opened | 182 | SS 110/35/10 kv Aksai | 10+10 |  | 6.0225 | 11.4 |  | -5.3774 | 0 | 10.5 | 4.4775 | 4.4775 | opened
| Nom. Capacity MV, МVА | 10+10 | 3.7368 | 10 | 10 | -6.2632 | 0 | 10.5 | 6.7632 |  |  |  | Nom. Capacity MV, МVА | 10+10 |  | 3.7368 | 10 | 10 | -6.2632 | 0 | 10.5 | 6.7632
| Nom. capacity LV, МVА | 10+10 | 2.2058 | 1.4 | 120 | 0.80575 | 0 | 10.5 | 9.6943 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.08 | 2.2858 | 1.4 | 120 | 0.88575 | 0 | 10.5 | 9.6143
183 | SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 4.3631 | 7 |  | -2.6369 | 0 | 6.615 | 9.2519 | 3.4214 | opened | 183 | SS 110/35/10 kv Nikolskaya | 6,3+6,3 |  | 4.3631 | 7 |  | -2.6369 | 0 | 6.615 | 2.2519 | 2.2519 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 3.1936 | 6.3 | 10 | -3.1064 | 0 | 6.615 | 3.4214 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 3.1936 | 6.3 | 10 | -3.1064 | 0 | 6.615 | 3.4214
| Nom. capacity LV, МVА | 6,3+6,3 | 1.1695 | 0.7 | 120 | 0.46948 | 0 | 6.615 | 6.1455 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 |  | 1.1695 | 0.7 | 120 | 0.46948 | 0 | 6.615 | 6.1455
184 | SS 110/35/10 kv Khvorostyanka | 10+16 | 11.2592 | 7 |  | 4.2592 | 0 | 10.5 | 6.2408 | 1.9054 | opened | 184 | SS 110/35/10 kv Khvorostyanka | 10+16 |  | 11.2732 | 7 |  | 4.2732 | 0 | 10.5 | 6.2268 | 6.2268 | opened
| Nom. capacity MV, МVА | 10+16 | 8.5946 | 6 | 10 | 2.5946 | 0 | 10.5 | 1.9054 |  |  |  | Nom. capacity MV, МVА | 10+16 |  | 8.5946 | 6 | 10 | 2.5946 | 0 | 10.5 | 7.9054
| Nom. capacity LV, МVА | 10+16 | 2.6645 | 1 | 120 | 1.6645 | 0 | 10.5 | 8.8355 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.014 | 2.6785 | 1 | 120 | 1.6785 | 0 | 10.5 | 8.8215
185 | SS 110/35/10 kv Dobrinka | 16+10 | 6.9312 | 5.1 |  | 1.8312 | 0 | 10.5 | 8.6688 | 7.5651 | opened | 185 | SS 110/35/10 kv Dobrinka | 16+10 |  | 7.3452 | 5.1 |  | 2.2452 | 0 | 10.5 | 8.2548 | 7.5651 | opened
| Nom. capacity СН, МВА | 16+10 | 2.9349 | 3.5 | 20 | -0.56505 | 0 | 10.5 | 7.5651 |  |  |  | Nom. capacity СН, МВА | 16+10 |  | 2.9349 | 3.5 | 20 | -0.56505 | 0 | 10.5 | 7.5651
| Nom. capacity LV, МVА | 16+10 | 3.9963 | 1.6 | 120 | 2.3963 | 0 | 10.5 | 8.1037 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.414 | 4.4103 | 1.6 | 120 | 2.8103 | 0 | 10.5 | 7.6897
186 | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 1.0795 | 4.13 |  | -3.0505 | 0 | 6.615 | 9.6655 | 6.2413 | opened | 186 | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 |  | 1.0895 | 4.13 |  | -3.0405 | 0 | 6.615 | 5.5255 | 5.5255 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.37368 | 3.5 | 20 | -3.1263 | 0 | 6.615 | 6.2413 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 0.37368 | 3.5 | 20 | -3.1263 | 0 | 6.615 | 6.2413
| Nom. capacity LV, МVА | 6,3+6,3 | 0.70584 | 0.63 | 120 | 0.07584 | 0 | 6.615 | 6.5392 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.01 | 0.71584 | 0.63 | 120 | 0.08584 | 0 | 6.615 | 6.5292
187 | SS 110/35/10 kv Kazinka | 16+16 | 13.2042 | 7.6 |  | 5.6042 | 0 | 16.8 | 11.1958 | 7.6941 | opened | 187 | SS 110/35/10 kv Kazinka | 16+16 |  | 13.6192 | 7.6 |  | 6.0192 | 0 | 16.8 | 10.7808 | 10.7808 | opened
| Nom. capacity MV, МVА | 16+16 | 9.1059 | 7.3 | 10 | 1.8059 | 0 | 16.8 | 7.6941 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 9.1059 | 7.3 | 10 | 1.8059 | 0 | 16.8 | 14.9941
| Nom. capacity LV, МVА | 16+16 | 4.0984 | 0.3 | 120 | 3.7984 | 0 | 16.8 | 13.0016 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.415 | 4.5134 | 0.3 | 120 | 4.2134 | 0 | 16.8 | 12.5866
188 | SS 110/35/10 kv Dobroe | 16+16 | 9.9897 | 9.2 |  | 0.78971 | 0 | 16.8 | 16.0103 | 10.6796 | opened | 188 | SS 110/35/10 kv Dobroe | 16+16 |  | 10.2727 | 9.2 |  | 1.0727 | 0 | 16.8 | 15.7273 | 15.7273 | opened
| Nom. capacity MV, МVА | 16+16 | 6.1204 | 6 | 10 | 0.12039 | 0 | 16.8 | 10.6796 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.1204 | 6 | 10 | 0.12039 | 0 | 16.8 | 16.6796
| Nom. capacity LV, МVА | 16+16 | 3.8693 | 3.2 | 120 | 0.66932 | 0 | 16.8 | 16.1307 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.283 | 4.1523 | 3.2 | 120 | 0.95232 | 0 | 16.8 | 15.8477
189 | SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 7.8348 | 5.63 |  | 2.2048 | 0 | 6.615 | 4.4102 | 1.0721 | opened | 189 | SS 110/35/6 kv Novaya Derevnya | 10+6,3 |  | 7.8758 | 5.63 |  | 2.2458 | 0 | 6.615 | 4.3692 | 4.3692 | opened
| Nom. capacity MV, МVА | 10+6,3 | 5.5429 | 5 | 10 | 0.54292 | 0 | 6.615 | 1.0721 |  |  |  | Nom. capacity MV, МVА | 10+6,3 |  | 5.5429 | 5 | 10 | 0.54292 | 0 | 6.615 | 6.0721
| Nom. capacity LV, МVА | 10+6,3 | 2.2919 | 0.63 | 120 | 1.6619 | 0 | 6.615 | 4.9531 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.041 | 2.3329 | 0.63 | 120 | 1.7029 | 0 | 6.615 | 4.9121
190 | SS 110/35/6 kv Verbilovo | 10+6,3 | 0.90462 | 2 |  | -1.0954 | 0 | 6.62 | 7.7154 | 5.7154 | opened | 190 | SS 110/35/6 kv Verbilovo | 10+6,3 |  | 0.91462 | 2 |  | -1.0854 | 0 | 6.62 | 5.7054 | 5.7054 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0 | 2 | 10 | -2 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МVА | 10+6,3 |  | 0 | 2 | 10 | -2 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 10+6,3 | 0.90462 | 0 | 0 | 0.90462 | 0 | 6.62 | 5.7154 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.01 | 0.91462 | 0 | 0 | 0.91462 | 0 | 6.62 | 5.7054
191 | SS 110/35/10 kv Khlevnoe | 16+16 | 8.7676 | 7.4 |  | 1.3676 | 0 | 16.8 | 15.4324 | 11.7744 | opened | 191 | SS 110/35/10 kv Khlevnoe | 16+16 |  | 10.1416 | 7.4 |  | 2.7416 | 0 | 16.8 | 14.0584 | 14.0584 | opened
| Nom. capacity MV, МVА | 16+16 | 5.0256 | 5 | 10 | 0.02565 | 0 | 16.8 | 11.7744 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 5.0256 | 5 | 10 | 0.02565 | 0 | 16.8 | 16.7743
| Nom. capacity LV, МVА | 16+16 | 3.742 | 2.4 | 120 | 1.342 | 0 | 16.8 | 15.458 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.374 | 5.116 | 2.4 | 120 | 2.716 | 0 | 16.8 | 14.084
192 | SS 110/35/10 kv Naberezhnoe | 6,3+10 | 1.6732 | 6.93 |  | -5.2568 | 0 | 6.62 | 11.8768 | 5.747 | opened | 192 | SS 110/35/10 kv Naberezhnoe | 6,3+10 |  | 1.6982 | 6.93 |  | -5.2318 | 0 | 6.62 | 11.8518 | 6.4248 | opened
| Nom. capacity MV, МVА | 6,3+10 | 0.87295 | 6.3 | 10 | -5.427 | 0 | 6.62 | 5.747 |  |  |  | Nom. capacity MV, МVА | 6,3+10 |  | 0.87295 | 6.3 | 10 | -5.427 | 0 | 6.62 | 12.047
| Nom. capacity LV, МVА | 6,3+10 | 0.80021 | 0.63 | 120 | 0.17021 | 0 | 6.62 | 6.4498 |  |  |  | Nom. capacity LV, МVА | 6,3+10 | 0.025 | 0.82521 | 0.63 | 120 | 0.19521 | 0 | 6.62 | 6.4248
193 | SS 110/35/10 kv Chaplygin | 7,5+6,3 | 8.5927 | 0.63 |  | 7.9627 | 0 | 6.62 | -1.3427 | -1.3427 | closed | 193 | SS 110/35/10 kv Chaplygin | 7,5+6,3 |  | 8.7427 | 0.63 |  | 8.1127 | 0 | 6.62 | -1.4927 | -1.4927 | closed
| Nom. capacity MV, МVА | 7,5+6,3 | 3.1177 | 0 | 0 | 3.1177 | 0 | 6.62 | 3.5023 |  |  |  | Nom. capacity MV, МVА | 7,5+6,3 |  | 3.1177 | 0 | 0 | 3.1177 | 0 | 6.62 | 3.5023
| Nom. capacity LV, МVА | 7,5+6,3 | 5.475 | 0.63 | 120 | 4.845 | 0 | 6.62 | 1.775 |  |  |  | Nom. capacity LV, МVА | 7,5+6,3 | 0.15 | 5.625 | 0.63 | 120 | 4.995 | 0 | 6.62 | 1.625
194 | SS 110/35/10 kv Troekurovo | 10+6,3 | 0.84004 | 10.63 |  | -9.79 | 0 | 6.62 | 16.41 | 6.3169 | opened | 194 | SS 110/35/10 kv Troekurovo | 10+6,3 |  | 0.84004 | 10.63 |  | -9.79 | 0 | 6.62 | 5.78 | 5.78 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.30311 | 10 | 10 | -9.6969 | 0 | 6.62 | 6.3169 |  |  |  | Nom. capacity MV, МVА | 10+6,3 |  | 0.30311 | 10 | 10 | -9.6969 | 0 | 6.62 | 6.3169
| Nom. capacity LV, МVА | 10+6,3 | 0.53694 | 0.63 | 120 | -0.093064 | 0 | 6.62 | 6.7131 |  |  |  | Nom. capacity LV, МVА | 10+6,3 |  | 0.53694 | 0.63 | 120 | -0.093064 | 0 | 6.62 | 6.0831
| Total | 2515.6 | 653.6513 | [8 empty] | 2: Total; 3: 2522.5; 5: 681.1692
| deficit | [8 empty] | -19.392 |  | 2: deficit; min. 12: -28.5644
| proficit | [8 empty] | 660.23 |  | 2: proficit; min. 12: 634.83