## Липецк
Appendix 2
Calculation of transmission capacity of Main substations of the branch "Lipetskenergo" of IDGC of Centre, JSC following the results of winter measurement of peak load of 2009.
table 1
No. | Object of main substation, voltage class | Current deficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA |  | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | Min.
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
| SS 110/10kv Lev Tolstoy | 10 |  | 2.63 | 1.6 | 30 | 1.03 | 0 | 1.6 | -1.03 | -1.03 | closed
| SS 110/10 kv Dvurechki | 6.3 |  | 2.03 | 0.1 | 70 | 1.93 | 0 | 0.1 | -1.93 | -1.93 | closed
| SS 35/10 kv Vesyoloe | 2.5 |  | 0.070668 | 0.8 | 100 | -0.72933 | 0 | 0.8 | 0.72933 | 0.72933 | opened
| SS 35/10 kv Kr.Palna | 3.2 |  | 0.73 | 1.2 | 70 | -0.47 | 0 | 1.2 | 0.47 | 0.47 | opened
| SS 35/10 kv Kamenka | 2.5 |  | 0.93 | 1.5 | 60 | -0.57 | 0 | 1.5 | 0.57 | 0.57 | opened
| SS 35/10 kv Krasotynovka | 2.5 |  | 0.43 | 1.5 | 50 | -1.07 | 0 | 1.5 | 1.07 | 1.07 | opened
| SS 35/10 kv Ozyorki | 2.5 |  | 0.13 | 0 | 0 | 0.13 | 0 | 0 | -0.13 | -0.13 | closed
| SS 35/10 kv Pankratovka | 2.5 |  | 0.63 | 1.2 | 90 | -0.57 | 0 | 1.2 | 0.57 | 0.57 | opened
| SS 35/10 kv Preobrazhenye | 2.5 |  | 0.46 | 0 | 0 | 0.46 | 0 | 0 | -0.46 | -0.46 | closed
| SS 35/10 kv Yakovlevo | 2.5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 0 | -0.9 | -0.9 | closed
| SS 110/10kv Terbunsky gonchar | 25 |  | 4: without load
| SS 35/10 kv Pervomayskaya | 2.5 |  | 0.85 | 0.3 | 60 | 0.55 | 0 | 0.3 | -0.55 | -0.55 | closed
| SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.91 | 0.9 | 90 | 0.01 | 0 | 0.9 | -0.01 | -0.01 | closed
| SS 35/10 kv Znamenka | 2.5 |  | 0.87 | 0.4 | 8 hours | 0.47 | 0 | 0.4 | -0.47 | -0.47 | closed
| SS 35/10 kv Pikovo | 2.5 |  | 0.59 | 0.5 | 60 | 0.09 | 0 | 0.5 | -0.09 | -0.09 | closed
| SS 35/10 kv Nikolskoe | 4 |  | 0.28 | 0.8 | 150 | -0.52 | 0 | 0.8 | 0.52 | 0.52 | opened
| SS 35/10 kv Peskovatka | 1.6 |  | 1.14 | 0.24 | 70 | 0.9 | 0 | 0.24 | -0.9 | -0.9 | closed
| SS 35/6 kv Druzhba | 5.6 |  | 4: Integrated distribution device of low voltage-6kv not ours; Min. 12: opened
| SS 35/10 kv SOM | 1.6 |  | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | closed
| SS 35/6 kv Novonikolaevka | 4 |  | 0.68 | 0 | 0 | 0.68 | 0 | 0 | -0.68 | -0.68 | closed
| SS 35/10 kv Sindyakino | 2.5 |  | 0.36 | 0.4 | 90 | -0.04 | 0 | 0.4 | 0.04 | 0.04 | opened
| SS 35/10 kv Kurino | 2.5 |  | 0.5 | 0 | 0 | 0.5 | 0 | 0 | -0.5 | -0.5 | closed
| SS 35/10 kv Novodubovoe | 2.5 |  | 0.88 | 0 | 0 | 0.88 | 0 | 0 | -0.88 | -0.88 | closed
| SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0 | 0 | 1.1444 | 0 | 0 | -1.1444 | -1.1444 | closed
| SS 35/6 kv Karyer | 4 |  | 4: without load
Two- and more transformer substations (for two voltage levels)
| SS 110/6 kv Agregatnaya | 16+16 | 32 | 15.14 | 0 | 0 | 15.14 | 0 | 16.8 | 1.66 | 1.66 | opened
| SS 110/6 kv Zapadnaya | 40+40 | 80 | 17.44 | 0 | 0 | 17.44 | 0 | 42 | 24.56 | 24.56 | opened
| SS 110/10 kv Kashary | 2,5+6,3 | 8.8 | 1.54 | 2.3 | 100 | -0.76 | 0 | 2.625 | 3.385 | 3.385 | opened
| SS 110/6 kv Tabak | 16+16 | 32 | 9.48 | 3.2 | 20 | 6.28 | 0 | 16.8 | 10.52 | 10.52 | opened
| SS 110/10 kv Lukoshkino | 10+2,5 | 12.5 | 1.07 | 0 | 0 | 1.07 | 0 | 2.625 | 1.555 | 1.555 | opened
| SS 110/10kv Niva | 10+10 | 20 | 5.09 | 1 | 100 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened
| SS 110/10 kv Olkhovets | 2,5+2,5 | 5 | 1.72 | 0.8 | 100 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
| SS 110/10 kv Kuyman | 2,5+2,5 | 5 | 1.1 | 1 | 100 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | *
| SS 110/10 kv Lutoshkino | 2,5+2,5 | 5 | 0.2728 | 0.5 | 60 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened
| SS 110/10 kv Krugloe | 2,5+2,5 | 5 | 0.62 | 0.5 | 60 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
| SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 80 | 45.62 | 4.5 | 30 | 41.12 | 0 | 42 | 0.88 | 0.88 | *
| SS 110/6 kv Privokzalnaya | 20+20+25 | 65 | 49.71 | 1.38 | 30 | 48.33 | 0 | 42 | -6.33 | -6.33 | closed
| SS 110/10/6 kv Yuzhnaya | 40+40 | 80 | 43.07 | 6 | 30 | 37.07 | 0 | 42 | 4.93 | 4.93 | *
| SS 110/6 kv Sitovka | 10+10 | 20 | 4.1 | 1.29 | 30 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | *
| SS 110/6 kv LTP | 6,3+10 | 16.3 | 2.33 | 0 | 0 | 2.33 | 0 | 6.615 | 4.285 | 4.285 | *
| SS 110/6 kv KPD | 10+10 | 20 | 2.31 | 0 | 0 | 2.31 | 0 | 10.5 | 8.19 | 8.19 | *
| SS 110/10 kv Oktyabskaya | 40+40 | 80 | 19.12 | 4 | 30 | 15.12 | 0 | 42 | 26.88 | 26.88 | *
| SS 110/10 kv Universitetskaya | 40+40 |  | 0 | 0 | 0 | 0 | 0 | 42 | 42 | 42 | opened
| SS 110/6 kv Teplichnaya | 15+15 | 30 | 7.58 | 0 | 0 | 7.58 | 0 | 15.75 | 8.17 | 8.17 | *
| SS 110/6 kv GPP-2 LTZ | 63+63 | 126 | 12.14 | 0 | 0 | 12.14 | 0 | 66.15 | 54.01 | 54.01 | *
| SS 35/10 kv Avangard | 4+4 | 8 | 1.1 | 1.2 | 110 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
| SS 35/10 kv Afanasysevo | 2,5+2,5 | 5 | 1.81 | 0 | 0 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | opened
| SS 35/10 kv Babarykino | 2,5+2,5 | 5 | 1.07 | 1.4 | 120 | -0.33 | 0 | 2.625 | 2.955 | 2.955 | opened
| SS 35/10 kv Avrora | 2,5+2,5 | 5 | 0.88 | 1.2 | 110 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened
| SS 35/10 kv B.Boyovka | 2,5+2,5 | 5 | 0.36 | 1.5 | 120 | -1.14 | 0 | 2.625 | 3.765 | 3.765 | opened
| SS 35/10 kv Borki | 2,5+2,5 | 5 | 0.85 | 0 | 0 | 0.85 | 0 | 2.625 | 1.775 | 1.775 | opened
| SS 35/6kv Vostochnaya | 10+16 | 26 | 8.72 | 4.8 | 20 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | opened
| SS 35/10 kv Vasilyevka | 2,5+2,5 | 5 | 0.52 | 1.5 | 90 | -0.98 | 0 | 2.625 | 3.605 | 3.605 | opened
| SS 35/10 kv Voronets | 4+4 | 8 | 2.15 | 1.2 | 110 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened
| SS 35/6 kv Golikovo | 1,8+1,6 | 3.4 | 0.11 | 0 | 0 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
| SS 35/10 kv Gatishche | 2,5+2,5 | 5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
| SS 35/10 kv Gnilusha | 6,3+6,3 | 12.6 | 1.36 | 1.2 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | opened
| SS 35/10kv Gryzlovo | 2,5+2,5 | 5 | 0.54 | 0.8 | 110 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | opened
| SS 35/10 kv Zhernovnoe | 2,5+2,5 | 5 | 0.62 | 1.5 | 100 | -0.88 | 0 | 2.625 | 3.505 | 3.505 | opened
| SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 4.8 | 2.35 | 0 | 0 | 2.35 | 0 | 1.68 | -0.67 | -0.67 | closed
| SS 35/10 kv Zakharovka | 2,5+2,5 | 5 | 0.42 | 0.8 | 60 | -0.38 | 0 | 2.625 | 3.005 | 3.005 | opened
| SS 35/10 kv Kazaki | 4+4 | 8 | 2.84 | 0 | 0 | 2.84 | 0 | 4.2 | 1.36 | 1.36 | opened
| SS 35/10 kv Kolesovo | 6,3+6,3 | 12.6 | 1.38 | 1.5 | 90 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | opened
| SS 35/10 kv Knyazevo | 2,5+2,5 | 5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
| SS 35/10 kv Kirillovo | 2,5+2,5 | 5 | 0.42 | 1.5 | 70 | -1.08 | 0 | 2.625 | 3.705 | 3.705 | opened
| SS 35/10 kv Ksizovo | 2,5+2,5 | 5 | 0.32 | 0 | 0 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
| SS 35/10 kv Lamskoe | 2,5+2,5 | 5 | 1.98 | 1.2 | 100 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened
| SS 35/10 kv Kazachye | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
| SS 35/10 kv Lebyazhye | 2,5+1,6 | 4.1 | 0.44 | 0 | 0 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened
| SS 35/10 kv Lomovets | 1,6+2,5 | 4.1 | 0.24 | 0 | 0 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
| SS 35/10 kv Olshanets | 2,5+4 | 6.5 | 1.27 | 0 | 0 | 1.27 | 0 | 2.625 | 1.355 | 1.355 | opened
| SS 35/10 kv Ploskoe | 4+4 | 8 | 3.76 | 3 | 70 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened
| SS 35/10 kv Stegalovka | 2,5+3,2 | 5.7 | 0.66 | 1.1 | 70 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | opened
| SS 35/10 kv Solidarnost | 4+4 | 8 | 1.3 | 1.2 | 70 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
| SS 35/10 kv Timiryazevo | 4+4 | 8 | 0.92 | 0.8 | 45 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
| SS 35/10 kv Talitsa | 2,5+2,5 | 5 | 1.55 | 1.5 | 110 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
| SS 35/10 kv the II Terbuny | 2,5+2,5 | 5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened
| SS 35/10 kv Tikhii Don | 4+4 | 8 | 0.45 | 0.8 | 50 | -0.35 | 0 | 4.2 | 4.55 | 4.55 | opened
| SS 35/10 kv Khitrovo | 6,3+6,3 | 12.6 | 0.36 | 0 | 0 | 0.36 | 0 | 6.615 | 6.255 | 6.255 | opened
| SS 35/10 kv Chernava | 2,5+2,5 | 5 | 2.02 | 0 | 0 | 2.02 | 0 | 2.625 | 0.605 | 0.605 | opened
| SS 35/10 kv Chernoles | 2,5+2,5 | 5 | 0.18 | 0 | 0 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
| SS 35/6 kv SS No. 5 | 6,3+3,2 | 9.5 | 0.48 | 0 | 0 | 0.48 | 0 | 3.36 | 2.88 | 2.88 | opened
| SS 35/10 kv Krasnoe | 4+4 | 8 | 3.51 | 1 | 120 | 2.51 | 0 | 4.2 | 1.69 | 1.69 | opened
| SS 35/10 kv Tyoploe | 2,5+2,5 | 5 | 1.35 | 1 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened
| SS 35/10 kv Dankov-selskaya | 6,3+4 | 10.3 | 5.61 | 2 | 120 | 3.61 | 0 | 4.2 | 0.59 | 0.59 | opened
| SS 35/10 kv Kolybelskaya | 2,5+2,5 | 5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 | opened
| SS 35/10 kv Topki | 2,5+2,5 | 5 | 0.52 | 0.5 | 60 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
| SS 35/10 kv Agronom | 4+6,3 | 10.3 | 2.02 | 1 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened
| SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 5 | 2.14 | 0.5 | 60 | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened
| SS 35/10 kv Gagarino | 1,8+1,8 | 3.6 | 0.45 | 0.5 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened
| SS 35/10 kv Ranenburg | 1,6+1,6 | 3.2 | 1.95 | 0.5 | 60 | 1.45 | 0 | 1.68 | 0.23 | 0.23 | opened
| SS 35/10 kv Sergievka | 2,5+2,5 | 5 | 0.44 | 0.5 | 60 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
| SS 35/10 kv Drezgalovo | 1,6+1,6 | 3.2 | 0.37 | 0.5 | 60 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened
| SS 35/10 kv Dolgoe | 2,5+2,5 | 5 | 0.29 | 0 | 0 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
| SS 35/10 kv Voskresenovka | 1,6+1,6 | 3.2 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened
| SS 35/10 kv Saprykino | 1,6+2,5 | 4.1 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened
| SS 35/10 kv Nopolyanye | 2,5+2,5 | 5 | 0.63 | 0 | 0 | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
| SS 35/10 kv Vednoe | 2,5+2,5 | 5 | 1.15 | 0.5 | 180 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened
| SS 35/10 kv Bigildino | 2,5+2,5 | 5 | 1.3 | 0.5 | 60 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
| SS 35/10 kv Kultura | 2,5+2,5 | 5 | 1.1 | 0.5 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
| SS 35/10 kv Boryatino | 2,5+2,5 | 5 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
| SS 35/10 kv B.Popovo | 2,5+2,5 | 5 | 1.81 | 0.5 | 60 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened
| SS 35/10 kv B. Izbishchi | 2,5+2,5 | 5 | 1.8 | 0.5 | 60 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened
| SS 35/10 kv Polibino | 2,5+2,5 | 5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
| SS 35/10 kv Dubrava | 2,5+2,5 | 5 | 0.15 | 0 | 0 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened
| SS 35/10 kv Khrushchevo | 2,5+2,5 | 5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened
| SS 35/10 kv B. Verkh | 2,5+2,5 | 5 | 1.01 | 0.5 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
| SS 35/10 kv Golovinshchino | 2,5+2,5 | 5 | 0.55 | 0 | 0 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened
| SS 35/10 kv Yablonevoe | 2,5+2,5 | 5 | 0.59 | 0 | 0 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
| SS 35/10 kv Politovo | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened
| SS 35/10 kv Complex | 4+4 | 8 | 0.91 | 1 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | opened
| SS 35/10 kv No.1 | 4+4 | 8 | 3.38 | 0 | 0 | 3.38 | 0 | 4.2 | 0.82 | 0.82 | opened
| SS 35/6 kv No. 2 | 1+1+1 | 3 | 3.49 | 0 | 0 | 3.49 | 0 | 1.05 | -2.44 | -2.44 | closed
| SS 35/10 kv No. 3 | 2,5+2,5 | 5 | 1.26 | 0.46 | 90 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | *
| SS 35/6 kv No. 4 | 4+4 | 8 | 2.63 | 0 | 0 | 2.63 | 0 | 4.2 | 1.57 | 1.57 | *
| SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 11.9 | 4.5 | 0 | 0 | 4.5 | 0 | 5.88 | 1.38 | 1.38 | opened
| SS 35/10 kv Butyrki | 5,6+4 | 9.6 | 7.13 | 0 | 0 | 7.13 | 0 | 4.2 | -2.93 | -2.93 | closed
| SS 35/10 kv Yarlukovo | 3,2+4 | 7.2 | 3.4 | 1.5 | 80 | 1.9 | 0 | 3.36 | 1.46 | 1.46 | opened
| SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 3.2 | 0.49 | 0.22 | 70 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened
| SS 35/10 kv Pravda | 4+2,5 | 6.5 | 1.03 | 2.06 | 100 | -1.03 | 0 | 2.625 | 3.655 | 3.655 | opened
| SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 | 5 | 0.63 | 0.18 | 70 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
| SS 35/10 kv Matyra | 4+3,2 | 7.2 | 4.68 | 0 | 0 | 4.68 | 0 | 3.36 | -1.32 | -1.32 | closed
| SS 35/10 kv Vperyod | 4+4 | 8 | 0.88 | 0.32 | 80 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | opened
| SS 35/10 kv Maley | 4+2,5 | 6.5 | 0.48 | 0.12 | 70 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
| SS 35/10 kv SKhТ | 2,5+1,6 | 4.1 | 0.96 | 0 | 0 | 0.96 | 0 | 1.68 | 0.72 | 0.72 | opened
| SS 35/10 kv Soshki | 4+4 | 8 | 0.8 | 0.2 | 80 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened
| SS 35/6 kv Tavolzhanka | 4+4 | 8 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened
| SS 35/10 kv Trubetchino | 2,5+2,5 | 5 | 1.71 | 0 | 0 | 1.71 | 0 | 2.625 | 0.915 | 0.915 | *
| SS 35/10 kv Ratchino | 2,5+2,5 | 5 | 1.11 | 0.12 | 70 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | *
| SS 35/10 kv Kalikino | 3,2+3,2 | 6.4 | 1.94 | 0.42 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | *
| SS 35/10 kv Borisovka | 4+2,5 | 6.5 | 2.74 | 0 | 0 | 2.74 | 0 | 2.625 | -0.115 | -0.115 | closed
| SS 35/10 kv Vvedenka | 4+4 | 8 | 4 | 0.14 | 70 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | *
| SS 35/10 kv Gryaznoe | 4+4 | 8 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | *
| SS 35/10 kv Borino | 4+4 | 8 | 4.24 | 1.2 | 90 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | *
| SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 5 | 1.6 | 1.88 | 100 (45) | -0.28 | 0 | 2.625 | 2.905 | 2.905 | *
| SS 35/10 kv Troitskaya | 2,5+4 | 6.5 | 2.33 | 0.6 | 70 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | *
| SS 35/6 kv Veshalovka | 2,5+2,5 | 5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | *
| SS 35/10 kv Pruzhinki | 2,5+2,5 | 5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | *
| SS 35/10 kv Stebaevo | 2,5+2,5 | 5 | 0.95 | 0.28 | 80 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | *
| SS 35/10 kv Khleboprodukty | 6,3+6,3 | 12.6 | 3.52 | 0.6 | 100 | 2.92 | 0 | 6.615 | 3.695 | 3.695 | *
| SS 35/10 kv Sentsovo | 10+10 | 20 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 | 5.3 | *
| SS 35/10 kv Meet processing factory | 6,3+6,3 | 12.6 | 4.46 | 1.6 | 110 | 2.86 | 0 | 6.62 | 3.76 | 3.76 | *
| SS 35/6 kv Poultry plant | 4+4 | 8 | 1.93 | 0 | 0 | 1.93 | 0 | 4.2 | 2.27 | 2.27 | *
| SS 35/6 kv Water intake | 10+10 | 20 | 0.43 | 0 | 0 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | *
| SS 35/10 kv Petrovskaya | 2,5+4 | 6.5 | 1.11 | 1.06 | 90 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
| SS 35/10 kv Lebedyanka | 2,5+2,5 | 5 | 0.81 | 0.68 | 90 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
| SS 35/10 kv Novocherkutino | 4+4 | 8 | 0.97 | 1.02 | 100 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | opened
| SS 35/10 kv Ivanovka | 2,5+2,5 | 5 | 1.06 | 0 | 0 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened
| SS 35/10 kv Poddubrovka | 2,5+2,5 | 5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | opened
| SS 35/10 kv Plavitsa | 1,6+1,6 | 3.2 | 0.91 | 0.46 | 90 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
| SS 35/10 kv Parshinovka | 1,6+2,5 | 4.1 | 0.22 | 0 | 0 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
| SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 7.2 | 2.2 | 1.28 | 100 | 0.92 | 0 | 3.36 | 2.44 | 2.44 | opened
| SS 35/10 kv Demshinka | 2,5+2,5 | 5 | 0.27 | 0 | 0 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened
| SS 35/10 kv Bereznyagovka | 1,6+1,6 | 3.2 | 0.62 | 0.46 | 80 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
| SS 35/10 kv Dmitrievka | 2,5+2,5 | 5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened
| SS 35/10 kv Pashkovo | 2,5+2,5 | 5 | 1.89 | 0 | 0 | 1.89 | 0 | 2.625 | 0.735 | 0.735 | opened
| SS 35/10 kv Moskovka | 1,6+1,6 | 3.2 | 0.77 | 0 | 0 | 0.77 | 0 | 1.68 | 0.91 | 0.91 | opened
| SS 35/10 kv Bochinovka | 4+4 | 8 | 3.14 | 1.18 | 90 | 1.96 | 0 | 4.2 | 2.24 | 2.24 | opened
| SS 35/10 kv Fyodorovka | 2,5+2,5 | 5 | 0.54 | 0.5 | 70 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
| SS 35/10 kv Kulikovo | 2,5+2,5 | 5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
| SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 5 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | *
| SS 35/10 kv Dmitryashevka | 2,5+2,5 | 5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | *
| SS 35/10 kv Rechnaya | 4+4 | 8 | 1.57 | 1.06 | 100 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | *
| SS 35/10 kv Negachevka | 2,5+2,5 | 5 | 0.44 | 0.22 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | *
| SS 35/10 kv Karamyshevo | 10+10 | 20 | 0.56 | 0.1 | 70 | 0.46 | 0 | 10.5 | 10.04 | 10.04 | opened
| SS 35/10 kv Tyushevka | 1,6+1,6 | 3.2 | 0.96 | 0.1 | 70 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | *
| SS 35/10 kv Sselki | 10+10 |  | 4: 0
Two- and more transformer substations (for three voltage levels)
| SS 110/35/10 kv Terbuny-110 | 10+10 | 20 | 9.26 | 3.5 |  | 5.76 | 0 | 10.5 | 4.74 | 4.71 | opened
| Nom. Capacity MV, МVA | 10+10 |  | 3.47 | 3.5 | 30 | -0.03 | 0 | 10.5 | 10.53
| Nom. capacity LV, МVA | 10+10 |  | 5.79 | 0 | 0 | 5.79 | 0 | 10.5 | 4.71
| SS 110/35/10 kv Dolgorukovo | 6,3+10 | 16.3 | 6.98 | 4 |  | 2.98 | 0 | 6.615 | 3.635 | 3.525 | opened
| Nom. capacity MV, МVA | 6,3+10 |  | 3.89 | 4 | 45 | -0.11 | 0 | 6.615 | 6.725
| Nom. capacity LV, МVA | 6,3+10 |  | 3.09 | 0 | 0 | 3.09 | 0 | 6.615 | 3.525
| SS 110/35/10 kv Volovo | 10+10 | 20 | 2.07 | 0.89 |  | 1.18 | 0 | 10.5 | 9.32 | 9.32 | opened
| Nom. capacity MV, МVA | 10+10 |  | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 |  | 2.07 | 0.89 | 60 | 1.18 | 0 | 10.5 | 9.32
| SS 110/35/10 kv Izmalkovo | 10+10 | 20 | 5 | 1.2 |  | 3.8 | 0 | 10.5 | 6.7 | 6.7 | opened
| Nom. capacity MV, МVА | 10+10 |  | 2.82 | 1.2 | 30 | 1.62 | 0 | 10.5 | 8.88
| Nom. capacity LV, МVА | 10+10 |  | 2.18 | 0 | 0 | 2.18 | 0 | 10.5 | 8.32
| SS 110/35/10 kv Gorokhovskaya | 16+16 | 32 | 10.52 | 7.2 |  | 3.32 | 0 | 16.8 | 13.48 | 13.48 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.94 | 6 | 30 | 0.94 | 0 | 16.8 | 15.86
| Nom. capacity LV, МVА | 16+16 |  | 3.58 | 1.2 | 120 | 2.38 | 0 | 16.8 | 14.42
| SS 110/35/10 kv Donskaya | 10+10 | 20 | 7.1 | 4.89 |  | 2.21 | 0 | 10.5 | 8.29 | 8.25 | opened
| Nom. capacity MV, МVА | 10+10 |  | 3.96 | 4 | 30 | -0.04 | 0 | 10.5 | 10.54
| Nom. capacity LV, МVА | 10+10 |  | 3.14 | 0.89 | 120 | 2.25 | 0 | 10.5 | 8.25
| SS 110/35/10 kv Lebedyan | 16+16 | 32 | 15.92 | 9 |  | 6.92 | 0 | 16.8 | 9.88 | 9.88 | opened
| Nom. capacity MV, МVА | 16+16 |  | 7.2 | 6 | 60 | 1.2 | 0 | 16.8 | 15.6
| Nom. capacity LV, МVА | 16+16 |  | 8.72 | 3 | 120 | 5.72 | 0 | 16.8 | 11.08
| SS 110/35/10 kv Chaplygin-novaya | 16+16 | 32 | 7.58 | 4.5 |  | 3.08 | 0 | 16.8 | 13.72 | 13.72 | opened
| Nom. capacity MV, МVА | 16+16 |  | 3.4 | 2.5 | 20 | 0.9 | 0 | 16.8 | 15.9
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 2 | 100 | 2.18 | 0 | 16.8 | 14.62
| SS 110/35/10 kv Kompressornaya | 16+16 | 32 | 4.81 | 3.2 |  | 1.61 | 0 | 16.8 | 15.19 | 15.19 | opened
| Nom. Capacity MV, МVА | 16+16 |  | 2.51 | 2.2 | 20 | 0.31 | 0 | 16.8 | 16.49
| Nom. capacity LV, МVА | 16+16 |  | 2.3 | 1 | 60 | 1.3 | 0 | 16.8 | 15.5
| SS 110/35/10 kv Rossiya | 16+16 | 32 | 5.6 | 3.8 |  | 1.8 | 0 | 16.8 | 15 | 15 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.67 | 3 | 60 | 1.67 | 0 | 16.8 | 15.13
| Nom. capacity LV, МVА | 16+16 |  | 0.93 | 0.8 | 100 | 0.13 | 0 | 16.8 | 16.67
| SS 110/35/10 kv Beryozovka | 16+10 | 26 | 4.58 | 3 |  | 1.58 | 0 | 10.5 | 8.92 | 8.92 | opened
| Nom. capacity MV, МVА | 16+10 |  | 3.37 | 3 | 60 | 0.37 | 0 | 10.5 | 10.13
| Nom. capacity LV, МVА | 16+10 |  | 1.21 | 0 | 0 | 1.21 | 0 | 10.5 | 9.29
| SS 110/35/10 kv Astapovo | 16+16 | 32 | 4.62 | 3 |  | 1.62 | 0 | 16.8 | 15.18 | 15.18 | opened
| Nom. capacity MV, МVА | 16+16 |  | 2.74 | 2 | 60 | 0.74 | 0 | 16.8 | 16.06
| Nom. capacity LV, МVА | 16+16 |  | 1.88 | 1 | 60 | 0.88 | 0 | 16.8 | 15.92
| SS 110/35/10 kv Khimicheskaya | 16+16 | 32 | 8.46 | 5.5 |  | 2.96 | 0 | 16.8 | 13.84 | 13.84 | opened
| Nom. capacity MV, МVА | 16+16 |  | 6.34 | 4.5 | 60 | 1.84 | 0 | 16.8 | 14.96
| Nom. capacity LV, МVА | 16+16 |  | 2.12 | 1 | 60 | 1.12 | 0 | 16.8 | 15.68
| SS 110/35/6 kv Bugor | 15+15+25 | 55 | 36.17 | 0.5 |  | 35.67 | 1 | 31.5 | -5.17 | -5.17 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.37 | 0 | 0 | 9.37 | 0 | 31.5 | 22.13
| Nom. capacity LV, МVА | 15+15+25 |  | 26.8 | 0.5 | 40 | 26.3 | 1 | 31.5 | 4.2
| SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 115 | 47.33 | 0 |  | 47.33 | 0 | 54.6 | 7.27 | -6.45 | closed
| Nom. capacity MV, МVА | 63+20 |  | 27.45 | 0 | 0 | 27.45 | 0 | 21 | -6.45
| Nom. capacity LV, МVА | 63+32+20 |  | 19.88 | 0 | 30 | 19.88 | 0 | 54.6 | 34.72
| SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 81.5 | 11.03 | 2.5 |  | 8.53 | 0 | 52.5 | 43.97 | -3.6 | closed
| Nom. capacity MV, МVА | 31.5 |  | 5.6 | 2 | 10 | 3.6 | 0 | 2 | -3.6
| Nom. capacity LV, МVА | 25+25 |  | 5.43 | 0.5 | 80 | 4.93 | 0 | 26.25 | 21.32
| SS 110/35/10 kv Usman | 16+16 | 32 | 15.28 | 6.5 |  | 8.78 | 0 | 16.8 | 8.02 | 7.93 | opened
| Nom. capacity MV, МVА | 16+16 |  | 4.91 | 5 | 20 | -0.09 | 0 | 16.8 | 16.89
| Nom. Capacity LV, МVА | 16+16 |  | 10.37 | 1.5 | 100 | 8.87 | 0 | 16.8 | 7.93
| SS 110/35/10 kv Aksai | 10+10 | 20 | 8.32 | 1.12 |  | 7.2 | 0 | 10.5 | 3.3 | 3.3 | opened
| Nom. Capacity MV, МVА | 10+10 |  | 5.82 | 0.5 | 20 | 5.32 | 0 | 10.5 | 5.18
| Nom. capacity LV, МVА | 10+10 |  | 2.5 | 0.62 | 80 | 1.88 | 0 | 10.5 | 8.62
| SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 12.6 | 4.91 | 3.34 |  | 1.57 | 0 | 6.615 | 5.045 | 5.045 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 3.55 | 3 | 10 | 0.55 | 0 | 6.615 | 6.065
| Nom. capacity LV, МVА | 6,3+6,3 |  | 1.36 | 0.34 | 80 | 1.02 | 0 | 6.615 | 5.595
| SS 110/35/10 kv Khvorostyanka | 10+16 | 26 | 12.41 | 6.72 |  | 5.69 | 0 | 10.5 | 4.81 | 4.81 | opened
| Nom. capacity MV, МVА | 10+16 |  | 9.32 | 6.5 | 20 | 2.82 | 0 | 10.5 | 7.68
| Nom. capacity LV, МVА | 10+16 |  | 3.09 | 0.22 | 80 | 2.87 | 0 | 10.5 | 7.63
| SS 110/35/10 kv Dobrinka | 16+10 | 26 | 6.89 | 5.68 |  | 1.21 | 0 | 10.5 | 9.29 | 8.88 | opened
| Nom. capacity СН, МВА | 16+10 |  | 3.59 | 4 | 80 | -0.41 | 0 | 10.5 | 10.91
| Nom. capacity LV, МVА | 16+10 |  | 3.3 | 1.68 | 100 | 1.62 | 0 | 10.5 | 8.88
| SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 12.6 | 1.39 | 0.4 |  | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened
| Nom. capacity MV, МVА | 6,3+6,3 |  | 0.62 | 0 | 0 | 0.62 | 0 | 6.615 | 5.995
| Nom. capacity LV, МVА | 6,3+6,3 |  | 0.77 | 0.4 | 90 | 0.37 | 0 | 6.615 | 6.245
| SS 110/35/10 kv Kazinka | 16+16 | 32 | 15.81 | 0 |  | 15.81 | 0 | 16.8 | 0.99 | 0.99 | opened
| Nom. capacity MV, МVА | 16+16 |  | 10.36 | 0 | 0 | 10.36 | 0 | 16.8 | 6.44
| Nom. capacity LV, МVА | 16+16 |  | 5.45 | 0 | 0 | 5.45 | 0 | 16.8 | 11.35
| SS 110/35/10 kv Dobroe | 16+16 | 32 | 11.4 | 3 |  | 8.4 | 0 | 16.8 | 8.4 | 8.4 | *
| Nom. capacity MV, МVА | 16+16 |  | 6.22 | 3 | 20 | 3.22 | 0 | 16.8 | 13.58
| Nom. capacity LV, МVА | 16+16 |  | 5.18 | 0 | 0 | 5.18 | 0 | 16.8 | 11.62
| SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 16.3 | 7.64 | 5 |  | 2.64 | 0 | 6.615 | 3.975 | 3.975 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 5.4 | 5 | 10 | 0.4 | 0 | 6.615 | 6.215
| Nom. capacity LV, МVА | 10+6,3 |  | 2.24 | 0 | 0 | 2.24 | 0 | 6.615 | 4.375
| SS 110/35/6 kv Verbilovo | 10+6,3 | 16.3 | 3.96 | 0 |  | 3.96 | 0 | 6.62 | 2.66 | 2.66 | *
| Nom. capacity MV, МVА | 10+6,3 |  | 2.76 | 0 | 0 | 2.76 | 0 | 6.62 | 3.86
| Nom. capacity LV, МVА | 10+6,3 |  | 1.2 | 0 | 0 | 1.2 | 0 | 6.62 | 5.42
| SS 110/35/10 kv Khlevnoe | 16+16 | 32 | 10.04 | 0 |  | 10.04 | 0 | 16.8 | 6.76 | 6.76 | *
| Nom. capacity MV, МVА | 16+16 |  | 5.86 | 0 | 0 | 5.86 | 0 | 16.8 | 10.94
| Nom. capacity LV, МVА | 16+16 |  | 4.18 | 0 | 0 | 4.18 | 0 | 16.8 | 12.62
| SS 110/35/10 kv Naberezhnoe | 6,3+10 | 16.3 | 2.46 | 4.5 |  | -2.04 | 0 | 6.62 | 8.66 | 5.45 | opened
| Nom. capacity MV, МVА | 6,3+10 |  | 1.29 | 4.5 | 10 | -3.21 | 0 | 6.62 | 9.83
| Nom. capacity LV, МVА | 6,3+10 |  | 1.17 | 0 | 0 | 1.17 | 0 | 6.62 | 5.45
| SS 110/35/10 kv Chaplygin | 7,5+6,3 | 13.8 | 5.54 | 4.5 |  | 1.04 | 0 | 6.62 | 5.58 | 5.58 | opened
| Nom. capacity MV, МVА | 7,5+6,3 |  | 0 | 0 | 0 | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 7,5+6,3 |  | 5.54 | 4.5 | 30 | 1.04 | 0 | 6.62 | 5.58
| SS 110/35/10 kv Troekurovo | 10+6,3 | 16.3 | 1.75 | 0.5 |  | 1.25 | 0 | 6.62 | 5.37 | 5.32 | opened
| Nom. capacity MV, МVА | 10+6,3 |  | 1.3 | 0 | 0 | 1.3 | 0 | 6.62 | 5.32
| Nom. capacity LV, МVА | 10+6,3 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 6.62 | 6.67
| Total: | 2515.6 | 2515.6 | 4: 731.9979; Min. 11: 678.3721
| deficit |  |  | Min. 11: -38.7994
| proficit |  |  | Min. 11: 442.8977; Min. 12: taking into account *
* Restriction to connected capacity according to working schedule of the grid of 110,220kv (according to data of Lipetsk Regional Dispatching Office)
Note on E33: krutko_eg: нагрузка 1 МВт, введена в сентябре
Note on E176: krutko_eg: введена в сентябре, потебители неподключены