## Свод
[11 empty] | Table 1 | [14 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note |  |  | No. | Object of main substation, voltage class | Ожидаемый дефицит /профицит | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity MVA | Current deficit/ proficit, MVA | [5 empty] | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity of Main substation, MVA | Expected dificit / proficit, MVA
|  |  | MVA | MVA | Min. | [13 empty] | MVA | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [13 empty] | 1: One-transformer substations
| SPS | [12 empty] | 2: SPS
1 | No. 44 | 10 | 0.021 | 0 | 0 | 0 | 0 | 0 | -0.021 | -0.021 |  |  |  | 1 | No. 44 | 10 | 2.07 | 2.091 | 0 | 0 | 2.091 | 0 | 0 | -2.091 | -2.091 | 110/6
2 | No. 7 | 2.5 | 0.483 | 2.5 | 0 | 2.5 | 0 | 2.5 | 2.017 | 2.017 |  |  |  | 2 | No. 7 | 2.5 | 3.49 | 3.973 | 2.5 | 0 | 1.473 | 0 | 2.5 | -1.473 | -1.473 | 35/6
3 | Stupino | 6.3 | 0.953 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.0845 | 0.0845 |  |  |  | 3 | Stupino | 6.3 | 0.06 | 1.013 | 1.0375 | 120 | -0.0245 | 0 | 1.0375 | 0.0245 | 0.0245 | 110/10
4 | P.Kommuna | 6.3 | 0.455 | 0.5 | 120 | 0.5 | 0 | 0.5 | 0.045 | 0.045 |  |  |  | 4 | P.Kommuna | 6.3 | 0 | 0.455 | 0.5 | 120 | -0.045 | 0 | 0.5 | 0.045 | 0.045 | 110/10
5 | No. 38 | 2.5 | 0.327 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.473 | 0.473 |  |  |  | 5 | No. 38 | 2.5 | 0 | 0.327 | 0.8 | 120 | -0.473 | 0 | 0.8 | 0.473 | 0.473 | 35/10
6 | No. 46 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 6 | No. 46 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35/6
7 | Istobnoe | 4 | 0.342 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.018 | 0.018 |  |  |  | 7 | Istobnoe | 4 | 0.01 | 0.352 | 0.36 | 120 | -0.008 | 0 | 0.36 | 0.008 | 0.008 | 35/10
8 | Rodina | 2.5 | 0.549 | 2.2 | 120 | 2.2 | 0 | 2.2 | 1.651 | 1.651 |  |  |  | 8 | Rodina | 2.5 | 1.63 | 2.179 | 2.2 | 120 | -0.021 | 0 | 2.2 | 0.021 | 0.021 | 35/10
9 | Vyaznovatovka | 2.5 | 0.352 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.148 | 1.148 |  |  |  | 9 | Vyaznovatovka | 2.5 | 1.02 | 1.372 | 1.5 | 120 | -0.128 | 0 | 1.5 | 0.128 | 0.128 | 35/10
10 | V.Turovo-1 | 3.2 | 0.927 | 1.4 | 120 | 1.4 | 0 | 1.4 | 0.473 | 0.473 |  |  |  | 10 | V.Turovo-1 | 3.2 | 0.02 | 0.947 | 1.4 | 120 | -0.453 | 0 | 1.4 | 0.453 | 0.453 | 35/10
11 | Semidesyatnoe | 2.5 | 0.69 | 0 | 0 | 0 | 0 | 0 | -0.69 | -0.69 |  |  |  | 11 | Semidesyatnoe | 2.5 | 0.07 | 0.76 | 0 | 0 | 0.76 | 0 | 0 | -0.76 | -0.76 | 35/10
12 | Arkhangelskoe SPS | 2.5 | 0.872 | 0 | 0 | 0 | 0 | 0 | -0.872 | -0.872 |  |  |  | 12 | Arkhangelskoe SPS | 2.5 | 0.07 | 0.942 | 0 | 0 | 0.942 | 0 | 0 | -0.942 | -0.942 | 35/10
13 | Khokhol-2 | 2.5 | 1.362 | 0 | 0 | 0 | 0 | 0 | -1.362 | -1.362 |  |  |  | 13 | Khokhol-2 | 2.5 | 0.11 | 1.472 | 0 | 0 | 1.472 | 0 | 0 | -1.472 | -1.472 | 35/10
14 | N.Olshanka | 4 | 0.697 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | 0.0604 | 0.0604 |  |  |  | 14 | N.Olshanka | 4 | 0.03 | 0.727 | 0.7574 | 120 | -0.0304 | 0 | 0.7574 | 0.0304 | 0.0304 | 35/10
15 | Troitskoe | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 |  |  |  | 15 | Troitskoe | 2.5 | 0.01 | 0.43 | 0 | 0 | 0.43 | 0 | 0 | -0.43 | -0.43 | 35/10
16 | Zemlyansk | 4 | 1.007 | 0 | 0 | 0 | 0 | 0 | -1.007 | -1.007 |  |  |  | 16 | Zemlyansk | 4 | 0.01 | 1.017 | 0 | 0 | 1.017 | 0 | 0 | -1.017 | -1.017 | 35/10
17 | Losevo SPS | 2.5 | 0.708 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.2456 | 0.2456 |  |  |  | 17 | Losevo SPS | 2.5 | 0 | 0.708 | 0.9536 | 120 | -0.2456 | 0 | 0.9536 | 0.2456 | 0.2456 | 35/10
18 | Verny | 2.5 | 2.089 | 2.15 | 120 | 2.15 | 0 | 2.15 | 0.061 | 0.061 |  |  |  | 18 | Verny | 2.5 | 0.04 | 2.129 | 2.15 | 120 | -0.021 | 0 | 2.15 | 0.021 | 0.021 | 35/10
19 | Elevator | 2.5 | 1 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.1 | 0.1 |  |  |  | 19 | Elevator | 2.5 | 0.03 | 1.03 | 1.1 | 120 | -0.07 | 0 | 1.1 | 0.07 | 0.07 | 35/10
20 | Yubileynaya | 4 | 0.999 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.601 | 0.601 |  |  |  | 20 | Yubileynaya | 4 | 0.07 | 1.069 | 1.6 | 120 | -0.531 | 0 | 1.6 | 0.531 | 0.531 | 35/10
21 | Parusnoe | 4 | 2.672 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.4864 | 0.4864 |  |  |  | 21 | Parusnoe | 4 | 0.05 | 2.722 | 3.1584 | 120 | -0.4364 | 0 | 3.1584 | 0.4364 | 0.4364 | 35/10
22 | Rogachyovka | 4 | 1.958 | 2.05 | 120 | 2.05 | 0 | 2.05 | 0.092 | 0.092 |  |  |  | 22 | Rogachyovka | 4 | 0.05 | 2.008 | 2.05 | 120 | -0.042 | 0 | 2.05 | 0.042 | 0.042 | 35/10
23 | Poultry farm Rassvet | 2.5 | 0.262 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.038 | 0.038 |  |  |  | 23 | Poultry farm Rassvet | 2.5 | 0 | 0.262 | 0.3 | 120 | -0.038 | 0 | 0.3 | 0.038 | 0.038 | 35/10
24 | Dankovo | 2.5 | 0.641 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.258 | 0.258 |  |  |  | 24 | Dankovo | 2.5 | 0.02 | 0.661 | 0.899 | 120 | -0.238 | 0 | 0.899 | 0.238 | 0.238 | 35/10
| LPS | [12 empty] | 2: LPS
25 | Bugaevka | 16 | 7.04 | 14 | 90 | 14 | 0 | 14 | 6.96 | 1.86 |  |  |  | 25 | Bugaevka | 16 | 0.2 | 7.24 | 14 | 90 | -6.76 | 0 | 14 | 6.76 | 1.66
| Sн. MV, МVА | 16 | 4.9 | 10 | 90 | 10 | 0 | 10 | 5.1 | [5 empty] | Sн. MV, МVА | 16 | 0 | 4.9 | 10 | 90 | -5.1 | 0 | 10 | 5.1 |  | 110/35/10
| Sн. LV, МVА | 16 | 2.14 | 4 | 90 | 4 | 0 | 4 | 1.86 | [5 empty] | Sн. LV, МVА | 16 | 0.2 | 2.34 | 4 | 90 | -1.66 | 0 | 4 | 1.66
26 | Dobrino | 10 | 1.22 | 6.6 | 90 | 6.6 | 0 | 6.6 | 5.38 | 1.96 |  |  |  | 26 | Dobrino | 10 | 0.13 | 1.35 | 6.6 | 90 | -5.25 | 0 | 6.6 | 5.25 | 1.83
| Sн. MV, МVА | 10 | 0.06 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.74 | [5 empty] | Sн. MV, МVА | 10 | 0 | 0.06 | 5.8 | 90 | -5.74 | 0 | 5.8 | 5.74 |  | 110/35/10
| Sн. LV, МVА | 10 | 1.16 | 3.12 | 90 | 3.12 | 0 | 3.12 | 1.96 | [5 empty] | Sн. LV, МVА | 10 | 0.13 | 1.29 | 3.12 | 90 | -1.83 | 0 | 3.12 | 1.83
27 | N. Kalitva | 6.3 | 1.64 | 2 | 240 | 2 | 0 | 2 | 0.36 | 0.36 |  |  |  | 27 | N. Kalitva | 6.3 | 0.28 | 1.92 | 2 | 240 | -0.08 | 0 | 2 | 0.08 | 0.08 | 110/10
28 | Shishovka | 6.3 | 0.64 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.7 | 1.7 |  |  |  | 28 | Shishovka | 6.3 | 0.25 | 0.89 | 2.34 | 180 | -1.45 | 0 | 2.34 | 1.45 | 1.45 | 110/10
29 | Azovka | 10 | 1.51 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.61 | 1.61 |  |  |  | 29 | Azovka | 10 | 1.2 | 2.71 | 3.12 | 180 | -0.41 | 0 | 3.12 | 0.41 | 0.41 | 110/10
30 | Yurasovka | 2.5 | 0.63 | 1.56 | 120 | 1.56 | 0 | 1.56 | 0.93 | 0.93 |  |  |  | 30 | Yurasovka | 2.5 | 0.02 | 0.65 | 1.56 | 120 | -0.91 | 0 | 1.56 | 0.91 | 0.91 | 35/10
31 | Nerovnovka | 2.5 | 0.29 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.49 | 0.49 |  |  |  | 31 | Nerovnovka | 2.5 | 0.02 | 0.31 | 0.78 | 240 | -0.47 | 0 | 0.78 | 0.47 | 0.47 | 35/10
32 | Saprino | 1.8 | 0.3 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.5 | 1.5 |  |  |  | 32 | Saprino | 1.8 | 0.01 | 0.31 | 1.8 | 120 | -1.49 | 0 | 1.8 | 1.49 | 1.49 | 35/10
33 | Sergeevka | 4 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 |  |  |  | 33 | Sergeevka | 4 | 0.06 | 0.41 | 0 | 0 | 0.41 | 0 | 0 | -0.41 | -0.41 | 35/10
34 | Stepanovka | 4 | 0.3 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.26 | 1.26 |  |  |  | 34 | Stepanovka | 4 | 0.02 | 0.32 | 1.56 | 240 | -1.24 | 0 | 1.56 | 1.24 | 1.24 | 35/10
35 | Kolodezhanskaya | 2.5 | 0.29 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.49 | 0.49 |  |  |  | 35 | Kolodezhanskaya | 2.5 | 0.05 | 0.34 | 0.78 | 180 | -0.44 | 0 | 0.78 | 0.44 | 0.44 | 35/10
36 | Andreevka | 2.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.1 |  |  |  | 36 | Andreevka | 2.5 | 0.02 | 0.12 | 0 | 0 | 0.12 | 0 | 0 | -0.12 | -0.12 | 35/10
37 | Kulikovka | 4 | 1.63 | 0 | 0 | 0 | 0 | 0 | -1.63 | -1.63 |  |  |  | 37 | Kulikovka | 4 | 0.23 | 1.86 | 0 | 0 | 1.86 | 0 | 0 | -1.86 | -1.86 | 35/10
38 | Lizinovka | 2.5 | 0.94 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.56 | 1.56 |  |  |  | 38 | Lizinovka | 2.5 | 0.05 | 0.99 | 2.5 | 240 | -1.51 | 0 | 2.5 | 1.51 | 1.51 | 35/10
39 | Sotnitskaya | 4 | 1.54 | 2.3 | 120 | 2.3 | 0 | 2.3 | 0.76 | 0.76 |  |  |  | 39 | Sotnitskaya | 4 | 0.04 | 1.58 | 2.3 | 120 | -0.72 | 0 | 2.3 | 0.72 | 0.72 | 35/10
40 | Kr. Polyana | 2.5 | 0.32 | 0 | 0 | 0 | 0 | 0 | -0.32 | -0.32 |  |  |  | 40 | Kr. Polyana | 2.5 | 0.04 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | -0.36 | -0.36 | 35/10
41 | Gumny | 4 | 0.83 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.73 | 0.73 |  |  |  | 41 | Gumny | 4 | 0.09 | 0.92 | 1.56 | 180 | -0.64 | 0 | 1.56 | 0.64 | 0.64 | 35/10
42 | Uryv | 2.5 | 0.71 | 0 | 0 | 0 | 0 | 0 | -0.71 | -0.71 |  |  |  | 42 | Uryv | 2.5 | 0.05 | 0.76 | 0 | 0 | 0.76 | 0 | 0 | -0.76 | -0.76 | 35/10
43 | Shubnoe | 2.5 | 0.82 | 1.17 | 180 | 1.17 | 0 | 1.17 | 0.35 | 0.35 |  |  |  | 43 | Shubnoe | 2.5 | 0.11 | 0.93 | 1.17 | 180 | -0.24 | 0 | 1.17 | 0.24 | 0.24 | 35/10
44 | Zaluzhnoe | 2.5 | 1.61 | 2 | 240 | 2 | 0 | 2 | 0.39 | 0.39 |  |  |  | 44 | Zaluzhnoe | 2.5 | 0.36 | 1.97 | 2 | 240 | -0.03 | 0 | 2 | 0.03 | 0.03 | 35/10
| BPS | [12 empty] | 2: BPS
46 | Anna-2 | 25 | 5.8 | 7.8 | 90 | 7.8 | 0 | 7.8 | 2 | 0.55 |  |  |  | 45 | Anna-2 | 25 | 0.03 | 5.83 | 7.8 | 90 | -1.97 | 0 | 7.8 | 1.97 | 0.55
| Sн. MV, МVА | 25 | 1.69 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.55 | [5 empty] | Sн. MV, МVА | 25 | 0 | 1.69 | 2.24 | 90 | -0.55 | 0 | 2.24 | 0.55 |  | 110/35/10
| Sн. LV, МVА | 25 | 4.11 | 5.56 | 90 | 5.56 | 0 | 5.56 | 1.45 | [5 empty] | Sн. LV, МVА | 25 | 0.03 | 4.14 | 5.56 | 90 | -1.42 | 0 | 5.56 | 1.42
47 | Vostochnaya | 10 | 3.42 | 4.8 | 30 | 4.8 | 0 | 4.8 | 1.38 | 1.38 |  |  |  | 46 | Vostochnaya | 10 | 0.93 | 4.35 | 4.8 | 30 | -0.45 | 0 | 4.8 | 0.45 | 0.45 | 35/6
48 | BolshevikBPS | 6.3 | 1.17 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.29 | 0.29 |  |  |  | 47 | BolshevikBPS | 6.3 | 0.01 | 1.18 | 1.46 | 60 | -0.28 | 0 | 1.46 | 0.28 | 0.28 | 110/10
49 | Rozhdestvo | 6.3 | 0.7 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.05 | 0.05 |  |  |  | 48 | Rozhdestvo | 6.3 | 0.02 | 0.72 | 0.75 | 60 | -0.03 | 0 | 0.75 | 0.03 | 0.03 | 110/10
50 | V. Toyda | 6.3 | 0.96 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.44 | 0.44 |  |  |  | 49 | V. Toyda | 6.3 | 0.01 | 0.97 | 1.4 | 90 | -0.43 | 0 | 1.4 | 0.43 | 0.43 | 110/10
51 | Vostochnaya-1 | 40 | 7.13 | 8.13 | 60 | 8.13 | 0 | 8.13 | 1 | 0.58 |  |  |  | 50 | Vostochnaya-1 | 40 | 0.92 | 8.05 | 8.13 | 60 | -0.08 | 0 | 8.13 | 0.08 | 0.08
| Sн. MV, МVА | 40 | 5.09 | 5.67 | 60 | 5.67 | 0 | 5.67 | 0.58 | [5 empty] | Sн. MV, МVА | 40 | 0 | 5.09 | 5.67 | 60 | -0.58 | 0 | 5.67 | 0.58 |  | 110/35/6
| Sн. LV, МVА | 40 | 2.04 | 3.1 | 60 | 3.1 | 0 | 3.1 | 1.06 | [5 empty] | Sн. LV, МVА | 40 | 0.92 | 2.96 | 3.1 | 60 | -0.14 | 0 | 3.1 | 0.14
52 | Makashevka | 2.5 | 0.34 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.14 | 0.14 |  |  |  | 51 | Makashevka | 2.5 | 0.02 | 0.36 | 0.48 | 180 | -0.12 | 0 | 0.48 | 0.12 | 0.12 | 35/10
53 | Mirolyubie | 4 | 0.4 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.1 | 0.1 |  |  |  | 52 | Mirolyubie | 4 | 0 | 0.4 | 0.5 | 60 | -0.1 | 0 | 0.5 | 0.1 | 0.1 | 35/10
54 | V. Zaton | 2.5 | 0 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0.01 | 0.01 |  |  |  | 53 | V. Zaton | 2.5 | 0 | 0 | 0.01 | 60 | -0.01 | 0 | 0.01 | 0.01 | 0.01 | 35/10
55 | Oktyabrskoe | 2.5 | 0.46 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.21 | 0.21 |  |  |  | 54 | Oktyabrskoe | 2.5 | 0.03 | 0.49 | 0.67 | 30 | -0.18 | 0 | 0.67 | 0.18 | 0.18 | 35/10
56 | Ilmen | 2.5 | 0.26 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.12 | 0.12 |  |  |  | 55 | Ilmen | 2.5 | 0.01 | 0.27 | 0.38 | 60 | -0.11 | 0 | 0.38 | 0.11 | 0.11 | 35/10
57 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 |  |  |  | 56 | Vikhlyaevka | 2.5 | 0 | 0.1 | 0.12 | 120 | -0.02 | 0 | 0.12 | 0.02 | 0.02 | 35/10
58 | N. Elan | 2.5 | 0.51 | 0 | 0 | 0 | 0 | 0 | -0.51 | -0.51 |  |  |  | 57 | N. Elan | 2.5 | 0 | 0.51 | 0 | 0 | 0.51 | 0 | 0 | -0.51 | -0.51 | 35/10
59 | B. Alabukhi | 2.5 | 0.77 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.16 | 0.16 |  |  |  | 58 | B. Alabukhi | 2.5 | 0.04 | 0.81 | 0.93 | 90 | -0.12 | 0 | 0.93 | 0.12 | 0.12 | 35/10
60 | Pykhovka | 2.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | -0.35 | -0.35 |  |  |  | 59 | Pykhovka | 2.5 | 0 | 0.35 | 0 | 0 | 0.35 | 0 | 0 | -0.35 | -0.35 | 35/10
61 | Е. Koleno | 4 | 2.48 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.85 | 0.85 |  |  |  | 60 | Е. Koleno | 4 | 0.03 | 2.51 | 3.33 | 120 | -0.82 | 0 | 3.33 | 0.82 | 0.82 | 35/10
62 | Podgornoe BPS | 2.5 | 0.35 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.11 | 0.11 |  |  |  | 61 | Podgornoe BPS | 2.5 | 0.01 | 0.36 | 0.46 | 180 | -0.1 | 0 | 0.46 | 0.1 | 0.1 | 35/10
63 | Mikhailovka-1 | 4 | 0.2 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.16 | 0.16 |  |  |  | 62 | Mikhailovka-1 | 4 | 0 | 0.2 | 0.36 | 60 | -0.16 | 0 | 0.36 | 0.16 | 0.16 | 35/10
64 | Mikhailovka | 2.5 | 0.32 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.18 | 0.18 |  |  |  | 63 | Mikhailovka | 2.5 | 0.01 | 0.33 | 0.5 | 60 | -0.17 | 0 | 0.5 | 0.17 | 0.17 | 35/10
65 | Gnilusha | 4 | 0.72 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.2 | 0.2 |  |  |  | 64 | Gnilusha | 4 | 0 | 0.72 | 0.92 | 180 | -0.2 | 0 | 0.92 | 0.2 | 0.2 | 35/10
66 | Mayskaya | 2.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | -0.6 | -0.6 |  |  |  | 65 | Mayskaya | 2.5 | 0 | 0.6 | 0 | 0 | 0.6 | 0 | 0 | -0.6 | -0.6 | 35/10
67 | Khleborodnoe | 2.5 | 0.42 | 0 | 0 | 0 | 0 | 0 | -0.42 | -0.42 |  |  |  | 66 | Khleborodnoe | 2.5 | 0.02 | 0.44 | 0 | 0 | 0.44 | 0 | 0 | -0.44 | -0.44 | 35/10
68 | N. Kurlak | 4 | 0.49 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.11 | 0.11 |  |  |  | 67 | N. Kurlak | 4 | 0 | 0.49 | 0.6 | 120 | -0.11 | 0 | 0.6 | 0.11 | 0.11 | 35/10
69 | Nikolaevka | 4 | 1.07 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.43 | 0.43 |  |  |  | 68 | Nikolaevka | 4 | 0 | 1.07 | 1.5 | 120 | -0.43 | 0 | 1.5 | 0.43 | 0.43 | 35/10
70 | Vasilyevka BPS | 2.5 | 0.37 | 0.39 | 180 | 0.39 | 0 | 0.39 | 0.02 | 0.02 |  |  |  | 69 | Vasilyevka BPS | 2.5 | 0.02 | 0.39 | 0.39 | 180 | 0 | 0 | 0.39 | 0 | 0 | 35/10
71 | Avangard | 2.5 | 0.7 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.21 | 0.21 |  |  |  | 70 | Avangard | 2.5 | 0.01 | 0.71 | 0.91 | 120 | -0.2 | 0 | 0.91 | 0.2 | 0.2 | 35/10
72 | Orlovka | 2.5 | 0.4 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.08 | 0.08 |  |  |  | 71 | Orlovka | 2.5 | 0 | 0.4 | 0.48 | 90 | -0.08 | 0 | 0.48 | 0.08 | 0.08 | 35/10
73 | N. Chigla | 2.5 | 0.6 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.3 | 0.3 |  |  |  | 72 | N. Chigla | 2.5 | 0.15 | 0.75 | 0.9 | 120 | -0.15 | 0 | 0.9 | 0.15 | 0.15 | 35/10
74 | Troitskoe-1 | 1.6 | 0.1 | 0.11 | 120 | 0.11 | 0 | 0.11 | 0.01 | 0.01 |  |  |  | 73 | Troitskoe-1 | 1.6 | 0 | 0.1 | 0.11 | 120 | -0.01 | 0 | 0.11 | 0.01 | 0.01 | 35/10
75 | Tishanka | 2.5 | 1.1 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.41 | 0.41 |  |  |  | 74 | Tishanka | 2.5 | 0.03 | 1.13 | 1.51 | 120 | -0.38 | 0 | 1.51 | 0.38 | 0.38 | 35/10
| KPS | [12 empty] | 2: KPS
76 | Kalacheevskaya | 6.3 | 0.62 | 1 | 24 hours | 1 | 0 | 1 | 0.38 | 0.38 |  |  |  | 75 | Kalacheevskaya | 6.3 | 0 | 0.62 | 1 | 24 hours | -0.38 | 0 | 1 | 0.38 | 0.38 | 110/10
77 | B.Kazinka | 6.3 | 0.47 | 0 | 0 | 0 | 0 | 0 | -0.47 | -0.47 |  |  |  | 76 | B.Kazinka | 6.3 | 3.09 | 3.56 | 0 | 0 | 3.56 | 0 | 0 | -3.56 | -3.56
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110/35/10
| Sн. LV, МVА | 6.3 | 0.47 | 0 | 0 | 0 | 0 | 0 | -0.47 | [5 empty] | Sн. LV, МVА | 6.3 | 3.09 | 3.56 | 0 | 0 | 3.56 | 0 | 0 | -3.56
78 | Derezovka | 6.3 | 0.33 | 0 | 0 | 0 | 0 | 0 | -0.33 | -0.33 |  |  |  | 77 | Derezovka | 6.3 | 0.07 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | -0.4 | -0.4 | 110/10
79 | Osetrovka | 6.3 | 0.35 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.15 | 1.15 |  |  |  | 78 | Osetrovka | 6.3 | 2.21 | 2.56 | 1.5 | 24 hours | 1.06 | 0 | 1.5 | -1.06 | -1.06 | 110/10
80 | sovkhoz Radchensky | 10 | 1.27 | 2 | 24 hours | 2 | 0 | 2 | 0.73 | -1.13 |  |  |  | 79 | sovkhoz Radchensky | 10 | 0.01 | 1.28 | 2 | 24 hours | -0.72 | 0 | 2 | 0.72 | -1.13
| Sн. MV, МVА | 10 | 1.13 | 0 | 24 hours | 0 | 0 | 0 | -1.13 | [5 empty] | Sн. MV, МVА | 10 | 0 | 1.13 | 0 | 0 | 1.13 | 0 | 0 | -1.13 |  | 110/35/10
| Sн. LV, МVА | 10 | 0.14 | 2 | 24 hours | 2 | 0 | 2 | 1.86 | [5 empty] | Sн. LV, МVА | 10 | 0.01 | 0.15 | 2 | 24 hours | -1.85 | 0 | 2 | 1.85
81 | Klepovka | 4 | 1.4 | 1.6 | 120 | 1.6 | 0 | 1.6 | 0.2 | 0.2 |  |  |  | 80 | Klepovka | 4 | 0.12 | 1.52 | 1.6 | 120 | -0.08 | 0 | 1.6 | 0.08 | 0.08 | 35/10
82 | Krasnopolye | 4 | 0.28 | 1 | 120 | 1 | 0 | 1 | 0.72 | 0.72 |  |  |  | 81 | Krasnopolye | 4 | 0.02 | 0.3 | 1 | 120 | -0.7 | 0 | 1 | 0.7 | 0.7 | 35/10
83 | Nikolskoe | 2.5 | 0.4 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.1 | 1.1 |  |  |  | 82 | Nikolskoe | 2.5 | 0 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
84 | N. Liman | 2.5 | 0.39 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.11 | 1.11 |  |  |  | 83 | N. Liman | 2.5 | 0.01 | 0.4 | 1.5 | 45 | -1.1 | 0 | 1.5 | 1.1 | 1.1 | 35/10
85 | Bereznyagi | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 |  |  |  | 84 | Bereznyagi | 2.5 | 0.03 | 0.33 | 1.5 | 45 | -1.17 | 0 | 1.5 | 1.17 | 1.17 | 35/10
86 | Kr.Flot | 2.5 | 0.3 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.2 | 1.2 |  |  |  | 85 | Kr.Flot | 2.5 | 0.08 | 0.38 | 1.5 | 45 | -1.12 | 0 | 1.5 | 1.12 | 1.12 | 35/10
87 | R. Zhuravka | 2.5 | 0.77 | 0 | 0 | 0 | 0 | 0 | -0.77 | -0.77 |  |  |  | 86 | R. Zhuravka | 2.5 | 0.08 | 0.85 | 0 | 0 | 0.85 | 0 | 0 | -0.85 | -0.85 | 35/10
88 | Gorokhovka | 2.5 | 0.47 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.03 | 1.03 |  |  |  | 87 | Gorokhovka | 2.5 | 0.04 | 0.51 | 1.5 | 45 | -0.99 | 0 | 1.5 | 0.99 | 0.99 | 35/10
89 | Livenka | 2.5 | 0.45 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0.05 | 0.05 |  |  |  | 88 | Livenka | 2.5 | 0.05 | 0.5 | 0.5 | 24 hours | 0 | 0 | 0.5 | 0 | 0 | 35/10
90 | R.Buylovka | 2.5 | 0.49 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.01 | 1.01 |  |  |  | 89 | R.Buylovka | 2.5 | 0.05 | 0.54 | 1.5 | 45 | -0.96 | 0 | 1.5 | 0.96 | 0.96 | 35/10
91 | Shurinovka | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 |  |  |  | 90 | Shurinovka | 2.5 | 0 | 0.29 | 0 | 0 | 0.29 | 0 | 0 | -0.29 | -0.29 | 35/10
92 | Tvyordokhlebovka | 4 | 0.28 | 0 | 0 | 0 | 0 | 0 | -0.28 | -0.28 |  |  |  | 91 | Tvyordokhlebovka | 4 | 0.03 | 0.31 | 0 | 0 | 0.31 | 0 | 0 | -0.31 | -0.31 | 35/10
93 | Krinitsa | 2.5 | 0.26 | 0 | 0 | 0 | 0 | 0 | -0.26 | -0.26 |  |  |  | 92 | Krinitsa | 2.5 | 0 | 0.26 | 0 | 0 | 0.26 | 0 | 0 | -0.26 | -0.26 | 35/10
94 | Krasnogorovka | 2.5 | 0.09 | 0 | 0 | 0 | 0 | 0 | -0.09 | -0.09 |  |  |  | 93 | Krasnogorovka | 2.5 | 0.01 | 0.1 | 0 | 0 | 0.1 | 0 | 0 | -0.1 | -0.1 | 35/10
| Two- and more transformer substations | [12 empty] | 2: Two- and more transformer substations
| SPS | [12 empty] | 2: SPS
95 | No. 2 | 25+25 | 19.31 | 4.8 | 120 | 14.51 | 0 | 26.25 | 11.74 | 11.74 |  | 1.05 | 25 | 95 | No. 2 | 25+25 | 11.69 | 31 | 4.8 | 120 | 26.2 | 0 | 26.25 | 0.05 | 0.05 | 110/6
96 | No.3 | 6,3 + 10 | 9.426 | 2.5 | 120 | 6.926 | 0 | 6.615 | -0.311 | -0.311 |  | 1.05 | 6.3 | 96 | No.3 | 6,3 + 10 | 0.39 | 9.816 | 2.5 | 120 | 7.316 | 0 | 6.615 | -0.701 | -0.701 | 35/6
97 | No. 4 | 10+10+15 | 13.41 | 0 | 0 | 13.41 | 0 | 21 | 7.59 | 7.59 |  | 1.05 | 20 | 97 | No. 4 | 10+10+15 | 0 | 13.41 | 0 | 0 | 13.41 | 0 | 21 | 7.59 | 7.59 | 35/6
98 | No. 6 | 25+32 | 19.125 | 1.6 | 120 | 17.525 | 0 | 26.25 | 8.725 | 8.725 |  | 1.05 | 25 | 98 | No. 6 | 25+32 | 3.3 | 22.425 | 1.6 | 120 | 20.825 | 0 | 26.25 | 5.425 | 5.425 | 110/6
99 | No. 8 | 4+4+4 | 5.285 | 0 | 0 | 5.285 | 0 | 8.4 | 3.115 | 3.115 |  | 1.05 | 8 | 99 | No. 8 | 4+4+4 | 0.34 | 5.625 | 0 | 0 | 5.625 | 0 | 8.4 | 2.775 | 2.775 | 35/6
100 | No. 9 | 16+25 | 23.02 | 3.3 | 120 | 19.72 | 0 | 16.8 | -2.92 | -2.92 |  | 1.05 | 16 | 100 | No. 9 | 16+25 | 10.19 | 33.21 | 3.3 | 120 | 29.91 | 0 | 16.8 | -13.11 | -13.11 | 110/6
101 | No. 10 | 20+20 | 29.97 | 13.3 | 120 | 16.67 | 0 | 21 | 4.33 | 4.33 |  | 1.05 | 20 | 101 | No. 10 | 20+20 | 7.38 | 37.35 | 13.3 | 120 | 24.05 | 0 | 21 | -3.05 | -3.05 | 35/6
102 | No. 13 | 6,3+6,3 | 7.047 | 3.7 | 120 | 3.347 | 0 | 6.615 | 3.268 | 3.268 |  | 1.05 | 6.3 | 102 | No. 13 | 6,3+6,3 | 4.41 | 11.457 | 3.7 | 120 | 7.757 | 0 | 6.615 | -1.142 | -1.142 | 35/10
103 | No. 14 | 31,5+31,5 | 16.649 | 1.3 | 120 | 15.349 | 0 | 33.075 | 17.726 | 17.726 |  | 1.05 | 31.5 | 103 | No. 14 | 31,5+31,5 | 0.54 | 17.189 | 1.3 | 120 | 15.889 | 0 | 33.075 | 17.186 | 17.186
| Sн. MV, МVА | 31,5+31,5 | 2.811 | 0 | 0 | 2.811 | 0 | 33.075 | 30.264 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 2.811 | 0 | 0 | 2.811 | 0 | 33.075 | 30.264 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5 | 13.838 | 1.3 | 120 | 12.538 | 0 | 33.075 | 20.537 |  |  | 1.05 | 31.5 |  | Sн. LV, МVА | 31,5+31,5 | 0.54 | 14.378 | 1.3 | 120 | 13.078 | 0 | 33.075 | 19.997
104 | No. 15 | 40,5+40,5+63,0 | 34.14 | 44.01 | 120 | -9.87 | 0 | 85.05 | 94.92 | 85.05 |  | 1.05 | 81 | 104 | No. 15 | 40,5+40,5+63,0 | 0.59 | 34.73 | 44.01 | 120 | -9.28 | 0 | 85.05 | 94.33 | 84.46
| Sн. MV, МVА | 40,5+40,5+63,0 | 34.14 | 44.01 | 120 | -9.87 | 0 | 85.05 | 94.92 |  |  | 1.05 | 81 |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 34.14 | 44.01 | 120 | -9.87 | 0 | 85.05 | 94.92 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  | 1.05 | 81 |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0.59 | 0.59 | 0 | 0 | 0.59 | 0 | 85.05 | 84.46
105 | No. 16 | 31,5+31,5+40,0 | 54.651 | 4 | 120 | 50.651 | 0 | 66.15 | 15.499 | 15.499 |  | 1.05 | 63 | 105 | No. 16 | 31,5+31,5+40,0 | 7.41 | 62.061 | 4 | 120 | 58.061 | 0 | 66.15 | 8.089 | 8.089
| Sн. MV, МVА | 31,5+31,5 | 4.419 | 0 | 0 | 4.419 | 0 | 33.075 | 28.656 |  |  | 1.05 | 31.5 |  | Sн. MV, МVА | 31,5+31,5 | 0 | 4.419 | 0 | 0 | 4.419 | 0 | 33.075 | 28.656 |  | 110/35/6
| Sн. LV, МVА | 31,5+31,5+40,0 | 50.232 | 4 | 120 | 46.232 | 0 | 66.15 | 19.918 |  |  | 1.05 | 63 |  | Sн. LV, МVА | 31,5+31,5+40,0 | 7.41 | 57.642 | 4 | 120 | 53.642 | 0 | 66.15 | 12.508
106 | No. 18 | 6,3+6,3 | 2.641 | 0 | 0 | 2.641 | 0 | 6.615 | 3.974 | 3.974 |  | 1.05 | 6.3 | 106 | No. 18 | 6,3+6,3 | 0.13 | 2.771 | 0 | 0 | 2.771 | 0 | 6.615 | 3.844 | 3.844 | 110/10
107 | No. 20 | 25,0+6,3+16 | 27.687 | 5.6 | 120 | 22.087 | 0 | 26.25 | 4.163 | -7.811 |  | 1.05 | 25 | 107 | No. 20 | 25,0+6,3+16 | 2.22 | 29.907 | 5.6 | 120 | 24.307 | 0 | 26.25 | 1.943 | -10.031
| Sн. MV, МVА | 25,0+16,0 | 7.661 | 0 | 0 | 7.661 | 0 | 26.25 | 18.589 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+16 | 0 | 7.661 | 0 | 0 | 7.661 | 0 | 26.25 | 18.589 |  | 110/10/6
| Sн. LV, МVА | 25,0+6,3 | 20.026 | 5.6 | 120 | 14.426 | 0 | 6.615 | -7.811 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 25+6,3 | 2.22 | 22.246 | 5.6 | 120 | 16.646 | 0 | 6.615 | -10.031
108 | No. 21 | 25,0+20,0+40,0 | 36.77 | 4.6 | 120 | 32.17 | 0 | 47.25 | 15.08 | 15.08 |  | 1.05 | 45 | 108 | No. 21 | 25,0+20,0+40,0 | 20.03 | 56.8 | 4.6 | 180 | 52.2 | 0 | 49.6125 | -2.5875 | -2.5875 | 110/35/6
109 | No. 22 | 10+10 | 4.364 | 1.4 | 120 | 2.964 | 0 | 10.5 | 7.536 | 7.536 |  | 1.05 | 10 | 109 | No. 22 | 10+10 | 2.69 | 7.054 | 1.4 | 120 | 5.654 | 0 | 10.5 | 4.846 | 4.846 | 35/6
110 | No. 23 | 7,5+6,3 | 6.974 | 0.8 | 120 | 6.174 | 0 | 6.615 | 0.441 | 0.441 |  | 1.05 | 6.3 | 110 | No. 23 | 7,5+6,3 | 0.75 | 7.724 | 0.8 | 120 | 6.924 | 0 | 6.615 | -0.309 | -0.309 | 35/6
111 | No. 24 | 3,2+4,0 | 2.157 | 0 | 0 | 2.157 | 0 | 3.36 | 1.203 | 1.203 |  | 1.05 | 3.2 | 111 | No. 24 | 3,2+4,0 | 0.04 | 2.197 | 0 | 0 | 2.197 | 0 | 3.36 | 1.163 | 1.163 | 35/6
112 | No. 25 | 40+25 | 34.163 | 3.8 | 120 | 30.363 | 0 | 26.25 | -4.113 | -4.113 |  | 1.05 | 25 | 112 | No. 25 | 40+25 | 8.26 | 42.423 | 3.8 | 120 | 38.623 | 0 | 26.25 | -12.373 | -12.373 | 110/6
113 | No. 27 | 32,0+32,0+32,0 | 39.88 | 3.3 | 180 | 36.58 | 0 | 67.2 | 30.62 | 30.62 |  | 1.05 | 64 | 113 | No. 27 | 32,0+32,0+32,0 | 17.48 | 57.36 | 3.3 | 180 | 54.06 | 0 | 67.2 | 13.14 | 13.14 | 110/6
114 | No. 28 | 10+10 | 10.897 | 0 | 0 | 10.897 | 0 | 10.5 | -0.397 | -0.397 |  | 1.05 | 10 | 114 | No. 28 | 10+10 | 3.45 | 14.347 | 0 | 0 | 14.347 | 0 | 10.5 | -3.847 | -3.847 | 110/10
115 | No.29 | 25+25 | 27.462 | 8.4 | 120 | 19.062 | 0 | 26.25 | 7.188 | 7.188 |  | 1.05 | 25 | 115 | No.29 | 25+25 | 3.8 | 31.262 | 8.4 | 120 | 22.862 | 0 | 26.25 | 3.388 | 3.388
| Sн. MV, МVА | 25+25 | 10.862 | 4.2 | 120 | 6.662 | 0 | 26.25 | 19.588 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 10.862 | 4.2 | 120 | 6.662 | 0 | 26.25 | 19.588 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 16.606 | 4.2 | 120 | 12.406 | 0 | 26.25 | 13.844 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 3.8 | 20.406 | 4.2 | 120 | 16.206 | 0 | 26.25 | 10.044
116 | No. 30 | 40+40 | 71.691 | 5.1 | 120 | 66.591 | 0 | 42 | -24.591 | -24.591 |  | 1.05 | 40 | 116 | No. 30 | 40+40 | 16.52 | 88.211 | 5.1 | 120 | 83.111 | 0 | 42 | -41.111 | -41.111
| Sн. MV, МVА | 40+40 | 13.35 | 0 | 0 | 13.35 | 0 | 42 | 28.65 |  |  | 1.05 | 40 |  | Sн. MV, МVА | 40+40 | 0 | 13.35 | 0 | 0 | 13.35 | 0 | 42 | 28.65 |  | 110/35/10
| Sн. LV, МVА | 40+40 | 58.341 | 5.1 | 120 | 53.241 | 0 | 42 | -11.241 |  |  | 1.05 | 40 |  | Sн. LV, МVА | 40+40 | 16.52 | 74.861 | 5.1 | 120 | 69.761 | 0 | 42 | -27.761
117 | No. 32 | 10+16 | 19.754 | 8 | 120 | 11.754 | 0 | 10.5 | -1.254 | -1.254 |  | 1.05 | 10 | 117 | No. 32 | 10+16 | 0.96 | 20.714 | 8 | 120 | 12.714 | 0 | 10.5 | -2.214 | -2.214
| Sн. MV, МVА | 10+16 | 16.65 | 8 | 120 | 8.65 | 0 | 10.5 | 1.85 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 16.65 | 8 | 120 | 8.65 | 0 | 10.5 | 1.85 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 3.104 | 0 | 0 | 3.104 | 0 | 10.5 | 7.396 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 0.96 | 4.064 | 0 | 0 | 4.064 | 0 | 10.5 | 6.436
118 | No. 33 | 4,0+4,0 | 1.318 | 0 | 0 | 1.318 | 0 | 4.2 | 2.882 | 2.882 |  | 1.05 | 4 | 118 | No. 33 | 4,0+4,0 | 0.3 | 1.618 | 0 | 0 | 1.618 | 0 | 4.2 | 2.582 | 2.582 | 35/10
119 | No. 34 | 2,5+1,8 | 1.95 | 0 | 0 | 1.95 | 0 | 1.89 | -0.06 | -0.06 |  | 1.05 | 1.8 | 119 | No. 34 | 2,5+1,8 | 0 | 1.95 | 0 | 0 | 1.95 | 0 | 1.89 | -0.06 | -0.06 | 35/6
120 | No.35 | 10+10 | 14.045 | 2.4 | 120 | 11.645 | 0 | 10.5 | -1.145 | -1.145 |  | 1.05 | 10 | 120 | No.35 | 10+10 | 0 | 14.045 | 2.4 | 120 | 11.645 | 0 | 10.5 | -1.145 | -1.145 | 35/6
121 | No. 36 | 6,3+10 | 1.259 | 0 | 0 | 1.259 | 0 | 6.615 | 5.356 | 5.356 |  | 1.05 | 6.3 | 121 | No. 36 | 6,3+10 | 3.5 | 4.759 | 0 | 0 | 4.759 | 0 | 6.615 | 1.856 | 1.856 | 110/35/10
122 | No. 39 | 25+25 | 25.936 | 4.1 | 120 | 21.836 | 0 | 26.25 | 4.414 | 4.414 |  | 1.05 | 25 | 122 | No. 39 | 25+25 | 1.95 | 27.886 | 4.1 | 120 | 23.786 | 0 | 26.25 | 2.464 | 2.464 | 110/6
123 | No. 41 | 10+10 | 10.654 | 0 | 0 | 10.654 | 0 | 10.5 | -0.154 | -0.154 |  | 1.05 | 10 | 123 | No. 41 | 10+10 | 0 | 10.654 | 0 | 0 | 10.654 | 0 | 10.5 | -0.154 | -0.154 | 35/6
124 | No. 42 | 25+40 | 19.65 | 1.6 | 120 | 18.05 | 0 | 26.25 | 8.2 | 8.2 |  | 1.05 | 25 | 124 | No. 42 | 25+40 | 9.01 | 28.66 | 1.6 | 120 | 27.06 | 0 | 26.25 | -0.81 | -0.81 | 110/6
125 | No. 43 | 63+63 | 18.602 | 1.6 | 60 | 17.002 | 0 | 66.15 | 49.148 | 49.148 |  | 1.05 | 63 | 125 | No. 43 | 63+63 | 8.24 | 26.842 | 1.6 | 60 | 25.242 | 0 | 66.15 | 40.908 | 40.908 | 110/6
126 | No. 45 | 63+63 | 30.741 | 7.1 | 120 | 23.641 | 0 | 66.15 | 42.509 | 42.509 |  | 1.05 | 63 | 126 | No. 45 | 63+63 | 28.71 | 59.451 | 7.1 | 120 | 52.351 | 0 | 66.15 | 13.799 | 13.799 | 110/6
127 | No. 47 | 25+25 | 13.35 | 0 | 0 | 13.35 | 0 | 26.25 | 12.9 | 12.9 |  | 1.05 | 25 | 127 | No. 47 | 25+25 | 0.03 | 13.38 | 0 | 0 | 13.38 | 0 | 26.25 | 12.87 | 12.87
| Sн. MV, МVА | 25+25 | 7.04 | 0 | 0 | 7.04 | 0 | 26.25 | 19.21 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 7.04 | 0 | 0 | 7.04 | 0 | 26.25 | 19.21 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.31 | 0 | 0 | 6.31 | 0 | 26.25 | 19.94 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.03 | 6.34 | 0 | 0 | 6.34 | 0 | 26.25 | 19.91
128 | Panino | 16+16 | 12.431 | 5.2 | 120 | 7.231 | 0 | 16.8 | 9.569 | 9.569 |  | 1.05 | 16 | 128 | Panino | 16+16 | 0.22 | 12.651 | 5.2 | 120 | 7.451 | 0 | 16.8 | 9.349 | 9.349
| Sн. MV, МVА | 16+16 | 6.236 | 5 | 120 | 1.236 | 0 | 16.8 | 15.564 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 6.236 | 5 | 120 | 1.236 | 0 | 16.8 | 15.564 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 6.195 | 0.2 | 120 | 5.995 | 0 | 16.8 | 10.805 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.22 | 6.415 | 0.2 | 120 | 6.215 | 0 | 16.8 | 10.585
129 | Kriusha | 2,5+2,5 | 1.013 | 0 | 0 | 1.013 | 0 | 2.625 | 1.612 | 1.612 |  | 1.05 | 2.5 | 129 | Kriusha | 2,5+2,5 | 0.03 | 1.043 | 0 | 0 | 1.043 | 0 | 2.625 | 1.582 | 1.582 | 35/10
130 | Seed plant | 4+4 | 2.446 | 0 | 0 | 2.446 | 0 | 4.2 | 1.754 | 1.754 |  | 1.05 | 4 | 130 | Seed plant | 4+4 | 0.02 | 2.466 | 0 | 0 | 2.466 | 0 | 4.2 | 1.734 | 1.734 | 35/10
131 | Progress | 2,5+10 | 0.534 | 0.5315 | 120 | 0.0025 | 0 | 2.625 | 2.6225 | 2.6225 |  | 1.05 | 2.5 | 131 | Progress | 2,5+10 | 0.01 | 0.544 | 0.5315 | 120 | 0.0125 | 0 | 2.625 | 2.6125 | 2.6125 | 110/35/10
132 | Katukhovka | 2,5+2,5 | 0.784 | 0.385 | 120 | 0.399 | 0 | 2.625 | 2.226 | 2.226 |  | 1.05 | 2.5 | 132 | Katukhovka | 2,5+2,5 | 0.01 | 0.794 | 0.385 | 120 | 0.409 | 0 | 2.625 | 2.216 | 2.216 | 35/10
133 | Kr.Liman | 2,5+4,0 | 1.035 | 0 | 0 | 1.035 | 0 | 2.625 | 1.59 | 1.59 |  | 1.05 | 2.5 | 133 | Kr.Liman | 2,5+4,0 | 0.01 | 1.045 | 0 | 0 | 1.045 | 0 | 2.625 | 1.58 | 1.58 | 35/10
134 | Ivanovka | 1,8+1,6 | 0.327 | 0.36 | 120 | -0.033 | 0 | 1.68 | 1.713 | 1.713 |  | 1.05 | 1.6 | 134 | Ivanovka | 1,8+1,6 | 0 | 0.327 | 0.36 | 120 | -0.033 | 0 | 1.68 | 1.713 | 1.713 | 35/10
135 | Don | 2,5+2,5 | 2.96 | 0 | 0 | 2.96 | 0 | 2.625 | -0.335 | -0.335 |  | 1.05 | 2.5 | 135 | Don | 2,5+2,5 | 0.39 | 3.35 | 0 | 0 | 3.35 | 0 | 2.625 | -0.725 | -0.725 | 35/10
136 | Yablochnoe | 4+4 | 0.363 | 0 | 0 | 0.363 | 0 | 4.2 | 3.837 | 3.837 |  | 1.05 | 4 | 136 | Yablochnoe | 4+4 | 0.01 | 0.373 | 0 | 0 | 0.373 | 0 | 4.2 | 3.827 | 3.827 | 35/10
137 | St.Nikolskoe | 2,5+2,5 | 0.944 | 1.227 | 120 | -0.283 | 0 | 2.625 | 2.908 | 2.908 |  | 1.05 | 2.5 | 137 | St.Nikolskoe | 2,5+2,5 | 0.3 | 1.244 | 1.227 | 120 | 0.017 | 0 | 2.625 | 2.608 | 2.608 | 35/10
138 | Rudkino | 4,0+4,0 | 2.761 | 0 | 0 | 2.761 | 0 | 4.2 | 1.439 | 1.439 |  | 1.05 | 4 | 138 | Rudkino | 4,0+4,0 | 0.08 | 2.841 | 0 | 0 | 2.841 | 0 | 4.2 | 1.359 | 1.359 | 35/10
139 | Khokhol-1 | 6,3+6,3 | 5.449 | 0 | 0 | 5.449 | 0 | 6.615 | 1.166 | 1.166 |  | 1.05 | 6.3 | 139 | Khokhol-1 | 6,3+6,3 | 1.22 | 6.669 | 0 | 0 | 6.669 | 0 | 6.615 | -0.054 | -0.054 | 35/6
140 | No. 11 | 5,6+6,3 | 3.013 | 0.5 | 120 | 2.513 | 0 | 5.88 | 3.367 | 2.931 |  | 1.05 | 5.6 | 140 | No. 11 | 5,6+6,3 | 0 | 3.013 | 0.5 | 120 | 2.513 | 0 | 5.88 | 3.367 | 2.931
| Sн. MV, МVА | 5,6+6,3 | 0.064 | 0.5 | 120 | -0.436 | 0 | 5.88 | 6.316 |  |  | 1.05 | 5.6 |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.064 | 0.5 | 120 | -0.436 | 0 | 5.88 | 6.316 |  | 110/35/6
| Sн. LV, МVА | 5,6+6,3 | 2.949 | 0 | 0 | 2.949 | 0 | 5.88 | 2.931 |  |  | 1.05 | 5.6 |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.949 | 0 | 0 | 2.949 | 0 | 5.88 | 2.931
141 | Beryozovka | 4+4 | 3.283 | 0 | 0 | 3.283 | 0 | 4.2 | 0.917 | 0.917 |  | 1.05 | 4 | 141 | Beryozovka | 4+4 | 0.09 | 3.373 | 0 | 0 | 3.373 | 0 | 4.2 | 0.827 | 0.827 | 35/10
142 | N.Zhivotinnoe | 6,3+6,3 | 5.152 | 1 | 120 | 4.152 | 0 | 6.615 | 2.463 | 2.463 |  | 1.05 | 6.3 | 142 | N.Zhivotinnoe | 6,3+6,3 | 1.52 | 6.672 | 1 | 120 | 5.672 | 0 | 6.615 | 0.943 | 0.943 | 35/10
143 | Ramon-1 | 4+4+4 | 5.43 | 6.85 | 120 | -1.42 | 0 | 8.4 | 9.82 | 9.82 |  | 1.05 | 8 | 143 | Ramon-1 | 4+4+4 | 0.86 | 6.29 | 6.85 | 120 | -0.56 | 0 | 8.4 | 8.96 | 8.96 | 35/10/6
144 | Ramon-2 | 16,0+16,0 | 19.859 | 10.48 | 120 | 9.379 | 0 | 16.8 | 7.421 | 7.421 |  | 1.05 | 16 | 144 | Ramon-2 | 16,0+16,0 | 4.87 | 24.729 | 10.48 | 120 | 14.249 | 0 | 16.8 | 2.551 | 2.551
| Sн. MV, МVА | 16,0+16,0 | 15.632 | 6.85 | 0 | 8.782 | 0 | 16.8 | 8.018 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 15.632 | 6.85 | 0 | 8.782 | 0 | 16.8 | 8.018 |  | 110/35/10
| Sн. LV, МVА | 16,0+16,0 | 4.227 | 3.63 | 120 | 0.597 | 0 | 16.8 | 16.203 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 4.87 | 9.097 | 3.63 | 120 | 5.467 | 0 | 16.8 | 11.333
145 | Vereyka | 2,5+2,5 | 1.283 | 0 | 0 | 1.283 | 0 | 2.625 | 1.342 | 1.342 |  | 1.05 | 2.5 | 145 | Vereyka | 2,5+2,5 | 0.01 | 1.293 | 0 | 0 | 1.293 | 0 | 2.625 | 1.332 | 1.332 | 35/10
146 | Complex | 10+10 | 6.05 | 3.4 | 180 | 2.65 | 0 | 10.5 | 7.85 | 7.85 |  | 1.05 | 10 | 146 | Complex | 10+10 | 0 | 6.05 | 3.4 | 180 | 2.65 | 0 | 10.5 | 7.85 | 7.85
| Sн. MV, МVА | 10+10 | 4.05 | 3.1 | 180 | 0.95 | 0 | 10.5 | 9.55 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 4.05 | 3.1 | 180 | 0.95 | 0 | 10.5 | 9.55 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.996 | 0.3 | 180 | 1.696 | 0 | 10.5 | 8.804 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0 | 1.996 | 0.3 | 180 | 1.696 | 0 | 10.5 | 8.804
147 | N.Veduga | 16+16 | 6.996 | 2.9 | 120 | 4.096 | 0 | 16.8 | 12.704 | 12.704 |  | 1.05 | 16 | 147 | N.Veduga | 16+16 | 0 | 6.996 | 2.9 | 120 | 4.096 | 0 | 16.8 | 12.704 | 12.704
| Sн. MV, МVА | 16+16 | 5.47 | 2.9 | 120 | 2.57 | 0 | 16.8 | 14.23 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 5.47 | 2.9 | 120 | 2.57 | 0 | 16.8 | 14.23 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.526 | 0 | 0 | 1.526 | 0 | 16.8 | 15.274 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0 | 1.526 | 0 | 0 | 1.526 | 0 | 16.8 | 15.274
148 | Golosnovka | 2,5+2,5 | 0.499 | 0.512 | 120 | -0.013 | 0 | 2.625 | 2.638 | 2.638 |  | 1.05 | 2.5 | 148 | Golosnovka | 2,5+2,5 | 0.02 | 0.519 | 0.512 | 120 | 0.007 | 0 | 2.625 | 2.618 | 2.618 | 35/10
149 | Medvezhye | 3,2+4,0 | 0.762 | 0 | 0 | 0.762 | 0 | 3.36 | 2.598 | 2.598 |  | 1.05 | 3.2 | 149 | Medvezhye | 3,2+4,0 | 0.11 | 0.872 | 0 | 0 | 0.872 | 0 | 3.36 | 2.488 | 2.488 | 35/10
150 | St.Veduga | 4+4 | 0.968 | 0 | 0 | 0.968 | 0 | 4.2 | 3.232 | 3.232 |  | 1.05 | 4 | 150 | St.Veduga | 4+4 | 0.03 | 0.998 | 0 | 0 | 0.998 | 0 | 4.2 | 3.202 | 3.202 | 35/10
151 | M.Pokrovka | 2,5+2,5 | 0.587 | 0 | 0 | 0.587 | 0 | 2.625 | 2.038 | 2.038 |  | 1.05 | 2.5 | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.597 | 0 | 0 | 0.597 | 0 | 2.625 | 2.028 | 2.028 | 35/10
152 | V.Turovo-2 | 2,5+2,5 | 1.299 | 0.7 | 120 | 0.599 | 0 | 2.625 | 2.026 | 2.026 |  | 1.05 | 2.5 | 152 | V.Turovo-2 | 2,5+2,5 | 0.06 | 1.359 | 0.7 | 120 | 0.659 | 0 | 2.625 | 1.966 | 1.966 | 35/10
153 | S.Lipyagi | 3,2+2,5 | 1.679 | 2.9638 | 120 | -1.2848 | 0 | 2.625 | 3.9098 | 3.9098 |  | 1.05 | 2.5 | 153 | S.Lipyagi | 3,2+2,5 | 1.69 | 3.369 | 2.9638 | 120 | 0.4052 | 0 | 2.625 | 2.2198 | 2.2198 | 35/10
154 | N.Devitsk | 25+16 | 7.436 | 8.2225 | 180 | -0.7865 | 0 | 16.8 | 17.5865 | 15.001 |  | 1.05 | 16 | 154 | N.Devitsk | 25+16 | 2.66 | 10.096 | 8.2225 | 180 | 1.8735 | 0 | 16.8 | 14.9265 | 14.9265
| Sн. MV, МVА | 25+16 | 4.599 | 2.8 | 180 | 1.799 | 0 | 16.8 | 15.001 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 25+16 | 0 | 4.599 | 2.8 | 180 | 1.799 | 0 | 16.8 | 15.001 |  | 110/35/10
| Sн. LV, МVА | 25+16 | 2.837 | 5.393 | 180 | -2.556 | 0 | 16.8 | 19.356 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 25+16 | 2.66 | 5.497 | 5.393 | 180 | 0.104 | 0 | 16.8 | 16.696
155 | Repyevka | 4+4 | 2.561 | 0.5 | 120 | 2.061 | 0 | 4.2 | 2.139 | 2.139 |  | 1.05 | 4 | 155 | Repyevka | 4+4 | 0.02 | 2.581 | 0.5 | 120 | 2.081 | 0 | 4.2 | 2.119 | 2.119 | 35/10
156 | Krasnolipye | 16+16 | 18.983 | 2.9 | 120 | 16.083 | 0 | 16.8 | 0.717 | 0.717 |  | 1.05 | 16 | 156 | Krasnolipye | 16+16 | 0.03 | 19.013 | 2.9 | 120 | 16.113 | 0 | 16.8 | 0.687 | 0.687
| Sн. MV, МVА | 16+16 | 17.639 | 2.7 | 120 | 14.939 | 0 | 16.8 | 1.861 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 17.639 | 2.7 | 120 | 14.939 | 0 | 16.8 | 1.861 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.344 | 0.2 | 120 | 1.144 | 0 | 16.8 | 15.656 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.03 | 1.374 | 0.2 | 120 | 1.174 | 0 | 16.8 | 15.626
157 | Ulyanovka | 6,3+6,3 | 0.392 | 0.04 | 60 | 0.352 | 0 | 6.615 | 6.263 | 6.263 |  | 1.05 | 6.3 | 157 | Ulyanovka | 6,3+6,3 | 0.03 | 0.422 | 0.04 | 60 | 0.382 | 0 | 6.615 | 6.233 | 6.233 | 110/10
158 | МОB | 4+2,5 | 1.325 | 0.6 | 60 | 0.725 | 0 | 2.625 | 1.9 | 1.9 |  | 1.05 | 2.5 | 158 | МОB | 4+2,5 | 0.08 | 1.405 | 0.6 | 60 | 0.805 | 0 | 2.625 | 1.82 | 1.82 | 35/10
159 | L.Rossosh | 6,3+6,3 | 5.81 | 0 | 0 | 5.81 | 0 | 6.615 | 0.805 | 0.805 |  | 1.05 | 6.3 | 159 | L.Rossosh | 6,3+6,3 | 0.24 | 6.05 | 0 | 0 | 6.05 | 0 | 6.615 | 0.565 | 0.565 | 35/10
160 | Kashirskoe | 2,5+2,5 | 0.761 | 0 | 0 | 0.761 | 0 | 2.625 | 1.864 | 1.864 |  | 1.05 | 2.5 | 160 | Kashirskoe | 2,5+2,5 | 0.05 | 0.811 | 0 | 0 | 0.811 | 0 | 2.625 | 1.814 | 1.814 | 35/10
161 | Zaprudskoe | 2,5+2,5 | 1.809 | 0 | 0 | 1.809 | 0 | 2.625 | 0.816 | 0.816 |  | 1.05 | 2.5 | 161 | Zaprudskoe | 2,5+2,5 | 0.13 | 1.939 | 0 | 0 | 1.939 | 0 | 2.625 | 0.686 | 0.686 | 35/10
162 | Moskovskoe | 10+10 | 10.512 | 1.8 | 120 | 8.712 | 0 | 10.5 | 1.788 | 0.773 |  | 1.05 | 10 | 162 | Moskovskoe | 10+10 | 0.02 | 10.532 | 1.8 | 120 | 8.732 | 0 | 10.5 | 1.768 | 0.773
| Sн. MV, МVА | 10+10 | 9.727 | 0 | 0 | 9.727 | 0 | 10.5 | 0.773 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 9.727 | 0 | 0 | 9.727 | 0 | 10.5 | 0.773 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.785 | 1.8 | 120 | -1.015 | 0 | 10.5 | 11.515 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.02 | 0.805 | 1.8 | 120 | -0.995 | 0 | 10.5 | 11.495
163 | SemenovkaSPS | 2,5+4,0 | 1.468 | 0 | 0 | 1.468 | 0 | 2.625 | 1.157 | 1.157 |  | 1.05 | 2.5 | 163 | SemenovkaSPS | 2,5+4,0 | 0.01 | 1.478 | 0 | 0 | 1.478 | 0 | 2.625 | 1.147 | 1.147 | 35/10
164 | N. Baygora | 2,5+2,5 | 1.137 | 1.03 | 60 | 0.107 | 0 | 2.625 | 2.518 | 2.518 |  | 1.05 | 2.5 | 164 | N. Baygora | 2,5+2,5 | 0.02 | 1.157 | 1.03 | 60 | 0.127 | 0 | 2.625 | 2.498 | 2.498 | 35/10
165 | Shukavka | 2,5+2,5 | 1.1 | 0.1 | 120 | 1 | 0 | 2.625 | 1.625 | 1.625 |  | 1.05 | 2.5 | 165 | Shukavka | 2,5+2,5 | 0.03 | 1.13 | 0.1 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | 35/10
166 | Uglyanets | 4+2,5 | 2.896 | 0.8 | 120 | 2.096 | 0 | 2.625 | 0.529 | 0.529 |  | 1.05 | 2.5 | 166 | Uglyanets | 4+2,5 | 0.11 | 3.006 | 0.8 | 120 | 2.206 | 0 | 2.625 | 0.419 | 0.419 | 35/10
167 | V.Khava | 16+16 | 11.982 | 0.4 | 120 | 11.582 | 0 | 16.8 | 5.218 | 5.218 |  | 1.05 | 16 | 167 | V.Khava | 16+16 | 0.27 | 12.252 | 0.4 | 120 | 11.852 | 0 | 16.8 | 4.948 | 4.948
| Sн. MV, МVА | 16+16 | 4.546 | 0 | 0 | 4.546 | 0 | 16.8 | 12.254 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 4.546 | 0 | 0 | 4.546 | 0 | 16.8 | 12.254 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 7.436 | 0.4 | 120 | 7.036 | 0 | 16.8 | 9.764 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.27 | 7.706 | 0.4 | 120 | 7.306 | 0 | 16.8 | 9.494
168 | Usman-1 | 10,0+6,3 | 9.058 | 0 | 0 | 9.058 | 0 | 6.615 | -2.443 | -2.443 |  | 1.05 | 6.3 | 168 | Usman-1 | 10,0+6,3 | 5.14 | 14.198 | 0 | 0 | 14.198 | 0 | 6.615 | -7.583 | -7.583 | 35/10
169 | Usman-2 | 6,3+6,3 | 10.456 | 0 | 0 | 10.456 | 0 | 6.615 | -3.841 | -3.841 |  | 1.05 | 6.3 | 169 | Usman-2 | 6,3+6,3 | 1.71 | 12.166 | 0 | 0 | 12.166 | 0 | 6.615 | -5.551 | -5.551 | 35/10
170 | R.Khava | 4+4 | 4.235 | 0.2 | 120 | 4.035 | 0 | 4.2 | 0.165 | 0.165 |  | 1.05 | 4 | 170 | R.Khava | 4+4 | 0.08 | 4.315 | 0.2 | 120 | 4.115 | 0 | 4.2 | 0.085 | 0.085 | 35/10
171 | No. 31 | 16+25 | 24.566 | 5.6 | 120 | 18.966 | 0 | 16.8 | -2.166 | -2.166 |  | 1.05 | 16 | 171 | No. 31 | 16+25 | 0.18 | 24.746 | 5.6 | 120 | 19.146 | 0 | 16.8 | -2.346 | -2.346
| Sн. MV, МVА | 16+25 | 16.429 | 5.6 | 120 | 10.829 | 0 | 16.8 | 5.971 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+25 | 0 | 16.429 | 5.6 | 120 | 10.829 | 0 | 16.8 | 5.971 |  | 110/35/10
| Sн. LV, МVА | 16+25 | 8.137 | 0 | 0 | 8.137 | 0 | 16.8 | 8.663 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+25 | 0.18 | 8.317 | 0 | 0 | 8.317 | 0 | 16.8 | 8.483
172 | Maslovka | 2,5+4,0 | 3.578 | 0 | 0 | 3.578 | 0 | 2.625 | -0.953 | -0.953 |  | 1.05 | 2.5 | 172 | Maslovka | 2,5+4,0 | 0.43 | 4.008 | 0 | 0 | 4.008 | 0 | 2.625 | -1.383 | -1.383 | 35/10
| LPS | [12 empty] | 2: LPS
173 | Podgornaya - district Line Maintenance Service | 16+16 | 7.07 | 1.6 | 180 | 5.47 | 0 | 16.8 | 11.33 | 11.33 |  | 1.05 | 16 | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 2.42 | 9.49 | 1.6 | 180 | 7.89 | 0 | 16.8 | 8.91 | 8.91
| Sн. MV, МVА | 16+16 | 3.1 | 1.05 | 180 | 2.05 | 0 | 16.8 | 14.75 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.1 | 1.05 | 180 | 2.05 | 0 | 16.8 | 14.75 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 3.97 | 0.55 | 180 | 3.42 | 0 | 16.8 | 13.38 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.42 | 6.39 | 0.55 | 180 | 5.84 | 0 | 16.8 | 10.96
174 | Kantemirovka | 10+10 | 9.1 | 1.6 | 60 | 7.5 | 0 | 10.5 | 3 | 3 |  | 1.05 | 10 | 174 | Kantemirovka | 10+10 | 1 | 10.1 | 1.6 | 60 | 8.5 | 0 | 10.5 | 2 | 2
| Sн. MV, МVА | 10+10 | 6.28 | 1.4 | 60 | 4.88 | 0 | 10.5 | 5.62 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 6.28 | 1.4 | 60 | 4.88 | 0 | 10.5 | 5.62 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.82 | 0.2 | 60 | 2.62 | 0 | 10.5 | 7.88 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 1 | 3.82 | 0.2 | 60 | 3.62 | 0 | 10.5 | 6.88
175 | Rossosh | 16+16+40 | 24.02 | 2.68 | 120 | 21.34 | 0 | 33.6 | 12.26 | 12.26 |  | 1.05 | 32 | 175 | Rossosh | 16+16+40 | 0.39 | 24.41 | 2.68 | 120 | 21.73 | 0 | 33.6 | 11.87 | 11.87
| Sн. MV, МVА | 16+16+40 | 4.17 | 1.9 | 120 | 2.27 | 0 | 33.6 | 31.33 |  |  | 1.05 | 32 |  | Sн. MV, МVА | 16+16+40 | 0 | 4.17 | 1.9 | 120 | 2.27 | 0 | 33.6 | 31.33 |  | 110/35/10/6
| Sн. LV, МVА | 16+16+40 | 19.85 | 0.78 | 120 | 19.07 | 0 | 33.6 | 14.53 |  |  | 1.05 | 32 |  | Sн. LV, МVА | 16+16+40 | 0.39 | 20.24 | 0.78 | 120 | 19.46 | 0 | 33.6 | 14.14
176 | Kamenka r-naya LPS | 16+16 | 3.31 | 0.97 | 120 | 2.34 | 0 | 16.8 | 14.46 | 14.46 |  | 1.05 | 16 | 176 | Kamenka r-naya LPS | 16+16 | 0.41 | 3.72 | 0.97 | 120 | 2.75 | 0 | 16.8 | 14.05 | 14.05
| Sн. MV, МVА | 16+16 | 0.56 | 0 | 120 | 0.56 | 0 | 16.8 | 16.24 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0.56 | 0 | 120 | 0.56 | 0 | 16.8 | 16.24 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.75 | 0.97 | 120 | 1.78 | 0 | 16.8 | 15.02 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.41 | 3.16 | 0.97 | 120 | 2.19 | 0 | 16.8 | 14.61
177 | Korotoyak | 6,3+10 | 4.23 | 0.47 | 180 | 3.76 | 0 | 6.615 | 2.855 | 2.855 |  | 1.05 | 6.3 | 177 | Korotoyak | 6,3+10 | 0.4 | 4.63 | 0.47 | 180 | 4.16 | 0 | 6.615 | 2.455 | 2.455
| Sн. MV, МVА | 6,3+10 | 1.34 | 0 | 180 | 1.34 | 0 | 6.615 | 5.275 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+10 | 0 | 1.34 | 0 | 180 | 1.34 | 0 | 6.615 | 5.275 |  | 110/35/10
| Sн. LV, МVА | 6,3+10 | 2.89 | 0.47 | 180 | 2.42 | 0 | 6.615 | 4.195 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+10 | 0.4 | 3.29 | 0.47 | 180 | 2.82 | 0 | 6.615 | 3.795
178 | Ostrogozhsk | 40,5+40,5 | 16.8 | 2.4 | 60 | 14.4 | 0 | 42.525 | 28.125 | 28.125 |  | 1.05 | 40.5 | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 16.8 | 2.4 | 60 | 14.4 | 0 | 42.525 | 28.125 | 28.125
| Sн. MV, МVА | 40,5+40,5 | 14.5 | 2.4 | 60 | 12.1 | 0 | 42.525 | 30.425 |  |  | 1.05 | 40.5 |  | Sн. MV, МVА | 40,5+40,5 | 0 | 14.5 | 2.4 | 60 | 12.1 | 0 | 42.525 | 30.425 |  | 110/35/6
| Sн. LV, МVА | 40,5+40,5 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225 |  |  | 1.05 | 40.5 |  | Sн. LV, МVА | 40,5+40,5 | 0 | 2.3 | 0 | 60 | 2.3 | 0 | 42.525 | 40.225
179 | Khrenovoe | 16+6,3 | 4.22 | 0 | 0 | 4.22 | 0 | 6.615 | 2.395 | 2.395 |  | 1.05 | 6.3 | 179 | Khrenovoe | 16+6,3 | 0.05 | 4.27 | 0 | 0 | 4.27 | 0 | 6.615 | 2.345 | 2.345
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  | 110/35/10
| Sн. LV, МVА | 16+6,3 | 4.22 | 0 | 0 | 4.22 | 0 | 6.615 | 2.395 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 16+6,3 | 0.05 | 4.27 | 0 | 0 | 4.27 | 0 | 6.615 | 2.345
180 | Oil extraction plant | 25+25 | 18.9 | 7.9 | 120 | 11 | 0 | 26.25 | 15.25 | 12.35 |  | 1.05 | 25 | 180 | Oil extraction plant | 25+25 | 0.09 | 18.99 | 7.9 | 120 | 11.09 | 0 | 26.25 | 15.16 | 12.26
| Sн. MV, МVА | 25+25 | 5 | 7.9 | 120 | -2.9 | 0 | 26.25 | 29.15 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 5 | 7.9 | 120 | -2.9 | 0 | 26.25 | 29.15 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 13.9 | 0 | 0 | 13.9 | 0 | 26.25 | 12.35 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.09 | 13.99 | 0 | 0 | 13.99 | 0 | 26.25 | 12.26
181 | ANP | 6,3+6,3 | 2.49 | 0.39 | 120 | 2.1 | 0 | 6.615 | 4.515 | 4.515 |  | 1.05 | 6.3 | 181 | ANP | 6,3+6,3 | 2.84 | 5.33 | 0.39 | 120 | 4.94 | 0 | 6.615 | 1.675 | 1.675 | 110/6
182 | St. Kalitva | 6,3+6,3 | 1.16 | 0.86 | 240 | 0.3 | 0 | 6.615 | 6.315 | 6.315 |  | 1.05 | 6.3 | 182 | St. Kalitva | 6,3+6,3 | 0.08 | 1.24 | 0.86 | 240 | 0.38 | 0 | 6.615 | 6.235 | 6.235 | 110/10
183 | Nikanorovka | 2,5+6,3 | 0.43 | 0.5 | 240 | -0.07 | 0 | 2.625 | 2.695 | 2.695 |  | 1.05 | 2.5 | 183 | Nikanorovka | 2,5+6,3 | 0.09 | 0.52 | 0.5 | 240 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | 110/10
184 | Poultry plant | 10+10 | 2.44 | 1 | 120 | 1.44 | 0 | 10.5 | 9.06 | 9.06 |  | 1.05 | 10 | 184 | Poultry plant | 10+10 | 0.65 | 3.09 | 1 | 120 | 2.09 | 0 | 10.5 | 8.41 | 8.41 | 110/10
185 | Korshevo | 6,3+6,3 | 0.64 | 0.56 | 120 | 0.08 | 0 | 6.615 | 6.535 | 6.535 |  | 1.05 | 6.3 | 185 | Korshevo | 6,3+6,3 | 0.8 | 1.44 | 0.56 | 120 | 0.88 | 0 | 6.615 | 5.735 | 5.735 | 110/10
186 | Davydovka | 6,3+6,3 | 6.27 | 2.11 | 240 | 4.16 | 0 | 6.615 | 2.455 | 2.455 |  | 1.05 | 6.3 | 186 | Davydovka | 6,3+6,3 | 0.72 | 6.99 | 2.11 | 240 | 4.88 | 0 | 6.615 | 1.735 | 1.735 | 110/10
187 | the 2nd Pyatiletka | 6,3+6,3 | 1 | 0.66 | 120 | 0.34 | 0 | 6.615 | 6.275 | 6.275 |  | 1.05 | 6.3 | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.1 | 1.1 | 0.66 | 120 | 0.44 | 0 | 6.615 | 6.175 | 6.175 | 110/10
188 | Liskinskaya | 10+16 | 2.23 | 0.72 | 120 | 1.51 | 0 | 10.5 | 8.99 | 8.99 |  | 1.05 | 10 | 188 | Liskinskaya | 10+16 | 4.28 | 6.51 | 0.72 | 120 | 5.79 | 0 | 10.5 | 4.71 | 4.71 | 110/6
189 | Olkhovatka | 4+4 | 3.64 | 2.55 | 180 | 1.09 | 0 | 4.2 | 3.11 | 3.11 |  | 1.05 | 4 | 189 | Olkhovatka | 4+4 | 0.95 | 4.59 | 2.55 | 180 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | 35/10
190 | Shaposhnikovka | 2,5+2,5 | 0.95 | 0.86 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 |  | 1.05 | 2.5 | 190 | Shaposhnikovka | 2,5+2,5 | 0.18 | 1.13 | 0.86 | 180 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | 35/10
191 | Karayashnik | 2,5+2,5 | 0.35 | 0.2875 | 180 | 0.0625 | 0 | 2.625 | 2.5625 | 2.5625 |  | 1.05 | 2.5 | 191 | Karayashnik | 2,5+2,5 | 0.05 | 0.4 | 0.2875 | 180 | 0.1125 | 0 | 2.625 | 2.5125 | 2.5125 | 35/10
192 | Saguny | 2,5+2,5 | 0.97 | 0.91 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 2.5 | 192 | Saguny | 2,5+2,5 | 0.09 | 1.06 | 0.91 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | 35/10
193 | Belogorye | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 |  | 1.05 | 2.5 | 193 | Belogorye | 2,5+2,5 | 0.15 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | 35/10
194 | Taly | 4+4 | 1.16 | 0 | 0 | 1.16 | 0 | 4.2 | 3.04 | 3.04 |  | 1.05 | 4 | 194 | Taly | 4+4 | 0.12 | 1.28 | 0 | 0 | 1.28 | 0 | 4.2 | 2.92 | 2.92 | 35/10
195 | Titarevka | 2,5+2,5 | 0.79 | 0 | 0 | 0.79 | 0 | 2.625 | 1.835 | 1.835 |  | 1.05 | 2.5 | 195 | Titarevka | 2,5+2,5 | 0.13 | 0.92 | 0 | 0 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | 35/10
196 | Mitrofanovka | 4+4 | 2.1 | 0 | 0 | 2.1 | 0 | 4.2 | 2.1 | 2.1 |  | 1.05 | 4 | 196 | Mitrofanovka | 4+4 | 0.28 | 2.38 | 0 | 0 | 2.38 | 0 | 4.2 | 1.82 | 1.82 | 35/10
197 | Druzhba | 4+4 | 1.72 | 0.44 | 150 | 1.28 | 0 | 4.2 | 2.92 | 2.92 |  | 1.05 | 4 | 197 | Druzhba | 4+4 | 0.18 | 1.9 | 0.44 | 150 | 1.46 | 0 | 4.2 | 2.74 | 2.74 | 35/10
198 | AlexandrovkaLPS | 4+4 | 1.94 | 0 | 0 | 1.94 | 0 | 4.2 | 2.26 | 2.26 |  | 1.05 | 4 | 198 | AlexandrovkaLPS | 4+4 | 0.1 | 2.04 | 0 | 0 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | 35/10
199 | Tkhorevka | 4+4 | 0.94 | 0.78 | 180 | 0.16 | 0 | 4.2 | 4.04 | 4.04 |  | 1.05 | 4 | 199 | Tkhorevka | 4+4 | 0.11 | 1.05 | 0.78 | 180 | 0.27 | 0 | 4.2 | 3.93 | 3.93 | 35/10
200 | Marki | 2,5+2,5 | 0.33 | 0.27 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 2.5 | 200 | Marki | 2,5+2,5 | 0 | 0.33 | 0.27 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
201 | Olkhov Log | 2,5+2,5 | 0.64 | 0.58 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 |  | 1.05 | 2.5 | 201 | Olkhov Log | 2,5+2,5 | 0 | 0.64 | 0.58 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
202 | Boldyrevka | 2,5+2,5 | 1.02 | 0 | 0 | 1.02 | 0 | 2.625 | 1.605 | 1.605 |  | 1.05 | 2.5 | 202 | Boldyrevka | 2,5+2,5 | 0.23 | 1.25 | 0 | 0 | 1.25 | 0 | 2.625 | 1.375 | 1.375 | 35/10
203 | Pobeda | 4+4 | 0.36 | 0 | 0 | 0.36 | 0 | 4.2 | 3.84 | 3.84 |  | 1.05 | 4 | 203 | Pobeda | 4+4 | 0.05 | 0.41 | 0 | 0 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | 35/10
204 | Lipovka | 4+4 | 1.43 | 0 | 0 | 1.43 | 0 | 4.2 | 2.77 | 2.77 |  | 1.05 | 4 | 204 | Lipovka | 4+4 | 0.19 | 1.62 | 0 | 0 | 1.62 | 0 | 4.2 | 2.58 | 2.58 | 35/10
205 | Yudanovka | 2,5+2,5 | 0.9 | 0.81 | 180 | 0.09 | 0 | 2.625 | 2.535 | 2.535 |  | 1.05 | 2.5 | 205 | Yudanovka | 2,5+2,5 | 0.12 | 1.02 | 0.81 | 180 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | 35/10
206 | Mechetka | 2,5+1,6 | 0.42 | 0 | 0 | 0.42 | 0 | 1.68 | 1.26 | 1.26 |  | 1.05 | 1.6 | 206 | Mechetka | 2,5+1,6 | 0.04 | 0.46 | 0 | 0 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | 35/10
207 | Petrovskaya | 4+4 | 1.75 | 0.03 | 180 | 1.72 | 0 | 4.2 | 2.48 | 2.48 |  | 1.05 | 4 | 207 | Petrovskaya | 4+4 | 0.96 | 2.71 | 0.03 | 180 | 2.68 | 0 | 4.2 | 1.52 | 1.52 | 35/10
208 | Sr. Ikorets | 4+4 | 3.27 | 0.06 | 120 | 3.21 | 0 | 4.2 | 0.99 | 0.99 |  | 1.05 | 4 | 208 | Sr. Ikorets | 4+4 | 0.9 | 4.17 | 0.06 | 120 | 4.11 | 0 | 4.2 | 0.09 | 0.09 | 35/10
209 | the 2nd Storozhevoe | 2,5+2,5 | 0.25 | 0 | 0 | 0.25 | 0 | 2.625 | 2.375 | 2.375 |  | 1.05 | 2.5 | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.35 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | 35/10
210 | Purification facilities | 2,5+2,5 | 2.71 | 0.42 | 120 | 2.29 | 0 | 2.625 | 0.335 | 0.335 |  | 1.05 | 2.5 | 210 | Purification facilities | 2,5+2,5 | 0.97 | 3.68 | 0.6 | 120 | 3.08 | 0 | 2.625 | -0.455 | -0.455 | 35/6
| BPS | [12 empty] | 2: BPS
211 | Borisoglebsk | 25+25 | 18.66 | 15.05 | 240 | 3.61 | 0 | 26.25 | 22.64 | 22.64 |  | 1.05 | 25 | 211 | Borisoglebsk | 25+25 | 0 | 18.66 | 24.9 | 240 | -6.24 | 0 | 26.25 | 32.49 | 27.69
| Sн. MV, МVА | 25+25 | 11.7 | 10.9 | 240 | 0.8 | 0 | 26.25 | 25.45 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 11.7 | 16.5 | 240 | -4.8 | 0 | 26.25 | 31.05 |  | 110/35/6
| Sн. LV, МVА | 25+25 | 6.96 | 4.15 | 240 | 2.81 | 0 | 26.25 | 23.44 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0 | 6.96 | 8.4 | 240 | -1.44 | 0 | 26.25 | 27.69
212 | KamenkaBPS | 10+10 | 4.22 | 2.79 | 180 | 1.43 | 0 | 10.5 | 9.07 | 9.07 |  | 1.05 | 10 | 212 | KamenkaBPS | 10+10 | 0.01 | 4.23 | 6.01 | 180 | -1.78 | 0 | 10.5 | 12.28 | 10.73
| Sн. MV, МVА | 10+10 | 3.8 | 2.54 | 180 | 1.26 | 0 | 10.5 | 9.24 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 3.8 | 5.35 | 180 | -1.55 | 0 | 10.5 | 12.05 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 0.42 | 0.25 | 180 | 0.17 | 0 | 10.5 | 10.33 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.01 | 0.43 | 0.66 | 180 | -0.23 | 0 | 10.5 | 10.73
213 | Talovaya | 16+16 | 5.59 | 3.6 | 180 | 1.99 | 0 | 16.8 | 14.81 | 14.81 |  | 1.05 | 16 | 213 | Talovaya | 16+16 | 0.08 | 5.67 | 6.39 | 180 | -0.72 | 0 | 16.8 | 17.52 | 15.95
| Sн. MV, МVА | 16+16 | 4.82 | 3.6 | 180 | 1.22 | 0 | 16.8 | 15.58 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 4.82 | 6.39 | 180 | -1.57 | 0 | 16.8 | 18.37 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.08 | 0.85 | 0 | 0 | 0.85 | 0 | 16.8 | 15.95
214 | Anna | 25+25 | 10.28 | 7.8 | 150 | 2.48 | 0 | 26.25 | 23.77 | 23.77 |  | 1.05 | 25 | 214 | Anna | 25+25 | 0.14 | 10.42 | 14.11 | 150 | -3.69 | 0 | 26.25 | 29.94 | 27.75
| Sн. MV, МVА | 25+25 | 3.87 | 2.39 | 150 | 1.48 | 0 | 26.25 | 24.77 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 3.87 | 5.37 | 150 | -1.5 | 0 | 26.25 | 27.75 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 6.41 | 5.4 | 150 | 1.01 | 0 | 26.25 | 25.24 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.14 | 6.55 | 8.74 | 150 | -2.19 | 0 | 26.25 | 28.44
215 | ArkhangelskoeBPS | 10+10 | 5.95 | 0.88 | 90 | 5.07 | 0 | 10.5 | 5.43 | 5.43 |  | 1.05 | 10 | 215 | ArkhangelskoeBPS | 10+10 | 0.01 | 5.96 | 3.02 | 90 | 2.94 | 0 | 10.5 | 7.56 | 7.43
| Sн. MV, МVА | 10+10 | 2.89 | 0.88 | 90 | 2.01 | 0 | 10.5 | 8.49 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.89 | 3.02 | 90 | -0.13 | 0 | 10.5 | 10.63 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.06 | 0 | 0 | 3.06 | 0 | 10.5 | 7.44 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.01 | 3.07 | 0 | 0 | 3.07 | 0 | 10.5 | 7.43
216 | Listopadovka | 10+10 | 3.43 | 1.63 | 90 | 1.8 | 0 | 10.5 | 8.7 | 8.7 |  | 1.05 | 10 | 216 | Listopadovka | 10+10 | 0.03 | 3.46 | 3.08 | 90 | 0.38 | 0 | 10.5 | 10.12 | 9.4
| Sн. MV, МVА | 10+10 | 2.36 | 1.63 | 90 | 0.73 | 0 | 10.5 | 9.77 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.36 | 3.08 | 90 | -0.72 | 0 | 10.5 | 11.22 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.07 | 0 | 0 | 1.07 | 0 | 10.5 | 9.43 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.03 | 1.1 | 0 | 0 | 1.1 | 0 | 10.5 | 9.4
217 | V. Karachan | 10+10 | 2.49 | 0.81 | 90 | 1.68 | 0 | 10.5 | 8.82 | 8.82 |  | 1.05 | 10 | 217 | V. Karachan | 10+10 | 0.01 | 2.5 | 1.18 | 90 | 1.32 | 0 | 10.5 | 9.18 | 8.92
| Sн. MV, МVА | 10+10 | 0.92 | 0.81 | 90 | 0.11 | 0 | 10.5 | 10.39 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 0.92 | 1.18 | 90 | -0.26 | 0 | 10.5 | 10.76 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 1.57 | 0 | 0 | 1.57 | 0 | 10.5 | 8.93 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.01 | 1.58 | 0 | 0 | 1.58 | 0 | 10.5 | 8.92
218 | Ternovka | 10+10 | 3.56 | 0.66 | 60 | 2.9 | 0 | 10.5 | 7.6 | 7.6 |  | 1.05 | 10 | 218 | Ternovka | 10+10 | 0.06 | 3.62 | 1.03 | 60 | 2.59 | 0 | 10.5 | 7.91 | 7.91
| Sн. MV, МVА | 10+10 | 1.21 | 0.66 | 60 | 0.55 | 0 | 10.5 | 9.95 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 1.21 | 1.03 | 60 | 0.18 | 0 | 10.5 | 10.32 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.35 | 0 | 0 | 2.35 | 0 | 10.5 | 8.15 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.06 | 2.41 | 0 | 0 | 2.41 | 0 | 10.5 | 8.09
219 | Narodnoe | 16+10 | 2.98 | 0.6 | 90 | 2.38 | 0 | 10.5 | 8.12 | 8.12 |  | 1.05 | 10 | 219 | Narodnoe | 16+10 | 0.06 | 3.04 | 0.93 | 90 | 2.11 | 0 | 10.5 | 8.39 | 8.23
| Sн. MV, МVА | 16+10 | 0.77 | 0.6 | 90 | 0.17 | 0 | 10.5 | 10.33 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 0.77 | 0.93 | 90 | -0.16 | 0 | 10.5 | 10.66 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 2.21 | 0 | 0 | 2.21 | 0 | 10.5 | 8.29 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 0.06 | 2.27 | 0 | 0 | 2.27 | 0 | 10.5 | 8.23
220 | N. Khopersk | 10+16 | 7.84 | 1.7 | 120 | 6.14 | 0 | 10.5 | 4.36 | 4.36 |  | 1.05 | 10 | 220 | N. Khopersk | 10+16 | 0.29 | 8.13 | 1.95 | 120 | 6.18 | 0 | 10.5 | 4.32 | 4.32
| Sн. MV, МVА | 10+16 | 2.2 | 1.7 | 120 | 0.5 | 0 | 10.5 | 10 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 2.2 | 1.95 | 120 | 0.25 | 0 | 10.5 | 10.25 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 5.64 | 0 | 0 | 5.64 | 0 | 10.5 | 4.86 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 0.29 | 5.93 | 0 | 0 | 5.93 | 0 | 10.5 | 4.57
221 | Ertil | 10+16 | 6.72 | 2.92 | 180 | 3.8 | 0 | 10.5 | 6.7 | 6.7 |  | 1.05 | 10 | 221 | Ertil | 10+16 | 0.08 | 6.8 | 1.4 | 180 | 5.4 | 0 | 10.5 | 5.1 | 5.1
| Sн. MV, МVА | 10+16 | 4.62 | 2.92 | 180 | 1.7 | 0 | 10.5 | 8.8 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+16 | 0 | 4.62 | 1.4 | 180 | 3.22 | 0 | 10.5 | 7.28 |  | 110/35/10
| Sн. LV, МVА | 10+16 | 2.1 | 0.08 | 0 | 2.02 | 0 | 10.5 | 8.48 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+16 | 0.08 | 2.18 | 0 | 0 | 2.18 | 0 | 10.5 | 8.32
222 | Shchuchye | 6,3+6,3 | 2.03 | 1.09 | 180 | 0.94 | 0 | 6.615 | 5.675 | 5.635 |  | 1.05 | 6.3 | 222 | Shchuchye | 6,3+6,3 | 0.08 | 2.11 | 2.33 | 180 | -0.22 | 0 | 6.615 | 6.835 | 5.825
| Sн. MV, МVА | 6,3+6,3 | 0.8 | 0.84 | 180 | -0.04 | 0 | 6.615 | 6.655 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 0.8 | 1.81 | 180 | -1.01 | 0 | 6.615 | 7.625 |  | 110/35/10
| Sн.LV, МVА | 6,3+6,3 | 1.23 | 0.25 | 180 | 0.98 | 0 | 6.615 | 5.635 |  |  | 1.05 | 6.3 |  | Sн.LV, МVА | 6,3+6,3 | 0.08 | 1.31 | 0.52 | 180 | 0.79 | 0 | 6.615 | 5.825
223 | Dokuchaevo | 10+10 | 1.8 | 0.12 | 120 | 1.68 | 0 | 10.5 | 8.82 | 8.82 |  | 1.05 | 10 | 223 | Dokuchaevo | 10+10 | 0.03 | 1.83 | 0.45 | 120 | 1.38 | 0 | 10.5 | 9.12 | 9.12 | 110/10
224 | B. Gribanovka | 16+16 | 6.2 | 0.11 | 30 | 6.09 | 0 | 16.8 | 10.71 | 10.71 |  | 1.05 | 16 | 224 | B. Gribanovka | 16+16 | 0.15 | 6.35 | 0.24 | 30 | 6.11 | 0 | 16.8 | 10.69 | 10.69 | 110/10
225 | Khimmash | 16+16 | 4.4 | 4.47 | 240 | -0.07 | 0 | 16.8 | 16.87 | 16.87 |  | 1.05 | 16 | 225 | Khimmash | 16+16 | 0 | 4.4 | 7.1 | 240 | -2.7 | 0 | 16.8 | 19.5 | 19.5 | 110/6
226 | Chigorak | 2,5+4 | 0.7 | 0.74 | 90 | -0.04 | 0 | 2.625 | 2.665 | 2.665 |  | 1.05 | 2.5 | 226 | Chigorak | 2,5+4 | 0.11 | 0.81 | 0.96 | 90 | -0.15 | 0 | 2.625 | 2.775 | 2.775 | 35/10
227 | Tretyaki | 4+4 | 0.83 | 0 | 0 | 0.83 | 0 | 4.2 | 3.37 | 3.37 |  | 1.05 | 4 | 227 | Tretyaki | 4+4 | 0.03 | 0.86 | 0 | 0 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | 35/10
228 | Gubari | 2,5+2,5 | 0.27 | 0.06 | 180 | 0.21 | 0 | 2.625 | 2.415 | 2.415 |  | 1.05 | 2.5 | 228 | Gubari | 2,5+2,5 | 0.05 | 0.32 | 0.43 | 180 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | 35/10
229 | Tantsyrey | 2,5+2,5 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 |  | 1.05 | 2.5 | 229 | Tantsyrey | 2,5+2,5 | 0.04 | 0.9 | 0 | 0 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | 35/10
230 | Peski | 4+4 | 3.34 | 0 | 0 | 3.34 | 0 | 4.2 | 0.86 | 0.86 |  | 1.05 | 4 | 230 | Peski | 4+4 | 0.12 | 3.46 | 0 | 0 | 3.46 | 0 | 4.2 | 0.74 | 0.74 | 35/10
231 | M. Gribanovka | 1,6+1,6 | 0.32 | 0.31 | 30 | 0.01 | 0 | 1.68 | 1.67 | 1.67 |  | 1.05 | 1.6 | 231 | M. Gribanovka | 1,6+1,6 | 0.02 | 0.34 | 0.87 | 30 | -0.53 | 0 | 1.68 | 2.21 | 2.21 | 35/10
232 | N. Karachan | 2,5+2,5 | 0.5 | 0 | 0 | 0.5 | 0 | 2.625 | 2.125 | 2.125 |  | 1.05 | 2.5 | 232 | N. Karachan | 2,5+2,5 | 0 | 0.5 | 0 | 0 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | 35/10
233 | Kozlovka BPS | 4+2,5 | 1.13 | 0 | 0 | 1.13 | 0 | 2.625 | 1.495 | 1.495 |  | 1.05 | 2.5 | 233 | Kozlovka BPS | 4+2,5 | 0.03 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 | 35/10
234 | K. Otdelets | 2,5+2,5 | 0.46 | 0 | 30 | 0.46 | 0 | 2.625 | 2.165 | 2.165 |  | 1.05 | 2.5 | 234 | K. Otdelets | 2,5+2,5 | 0 | 0.46 | 0.63 | 30 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | 35/10
235 | Esipovo | 2,5+2,5 | 0.67 | 0 | 0 | 0.67 | 0 | 2.625 | 1.955 | 1.955 |  | 1.05 | 2.5 | 235 | Esipovo | 2,5+2,5 | 0.02 | 0.69 | 0 | 0 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | 35/10
236 | Kiselnov | 2,5+2,5 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 |  | 1.05 | 2.5 | 236 | Kiselnov | 2,5+2,5 | 0 | 0.45 | 0 | 0 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | 35/10
237 | Krasnoe | 6,3+6,3 | 1.85 | 0 | 0 | 1.85 | 0 | 6.615 | 4.765 | 4.765 |  | 1.05 | 6.3 | 237 | Krasnoe | 6,3+6,3 | 0.01 | 1.86 | 0 | 0 | 1.86 | 0 | 6.615 | 4.755 | 4.755 | 35/10
238 | Troitskoe | 2,5+2,5 | 0.42 | 0 | 0 | 0.42 | 0 | 2.625 | 2.205 | 2.205 |  | 1.05 | 2.5 | 238 | Troitskoe | 2,5+2,5 | 0.01 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | 35/10
239 | Ertil-gorod | 6,3+6,3 | 3.55 | 2.45 | 240 | 1.1 | 0 | 6.615 | 5.515 | 5.515 |  | 1.05 | 6.3 | 239 | Ertil-gorod | 6,3+6,3 | 0.06 | 3.61 | 5 | 240 | -1.39 | 0 | 6.615 | 8.005 | 8.005 | 35/10
240 | Rostoshi | 4+4 | 1.47 | 0 | 0 | 1.47 | 0 | 4.2 | 2.73 | 2.73 |  | 1.05 | 4 | 240 | Rostoshi | 4+4 | 0 | 1.47 | 0 | 0 | 1.47 | 0 | 4.2 | 2.73 | 2.73 | 35/10
241 | Vvedenka | 2,5+2,5 | 0.35 | 0 | 60 | 0.35 | 0 | 2.625 | 2.275 | 2.275 |  | 1.05 | 2.5 | 241 | Vvedenka | 2,5+2,5 | 0 | 0.35 | 0.48 | 60 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | 35/10
242 | Sadovoe | 4+4 | 1.92 | 0 | 0 | 1.92 | 0 | 4.2 | 2.28 | 2.28 |  | 1.05 | 4 | 242 | Sadovoe | 4+4 | 0.03 | 1.95 | 0 | 0 | 1.95 | 0 | 4.2 | 2.25 | 2.25 | 35/10
243 | Rubashevka | 2,5+2,5 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 |  | 1.05 | 2.5 | 243 | Rubashevka | 2,5+2,5 | 0 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | 35/10
244 | N. Nadezhdenka | 2,5+2,5 | 0.46 | 0.22 | 180 | 0.24 | 0 | 2.625 | 2.385 | 2.385 |  | 1.05 | 2.5 | 244 | N. Nadezhdenka | 2,5+2,5 | 0 | 0.46 | 0.75 | 180 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | 35/10
245 | Abramovka | 6,3+4 | 3.4 | 0.29 | 120 | 3.11 | 0 | 4.2 | 1.09 | 1.09 |  | 1.05 | 4 | 245 | Abramovka | 6,3+4 | 0.04 | 3.44 | 0.52 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | 35/10
246 | Alexandrovka BPS | 2,5+2,5 | 0.9 | 0.64 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 |  | 1.05 | 2.5 | 246 | Alexandrovka BPS | 2,5+2,5 | 0.01 | 0.91 | 1.17 | 120 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | 35/10
247 | N. Troitskaya | 4+4 | 0.3 | 0.2 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 |  | 1.05 | 4 | 247 | N. Troitskaya | 4+4 | 0 | 0.3 | 0.34 | 120 | -0.04 | 0 | 4.2 | 4.24 | 4.24 | 35/10
| KPS | [12 empty] | 2: KPS
248 | Kalach-1 | 25+25 | 14.75 | 2.2 | 120 | 12.55 | 0 | 26.25 | 13.7 | 13.7 |  | 1.05 | 25 | 248 | Kalach-1 | 25+25 | 0.52 | 15.27 | 2.2 | 120 | 13.07 | 0 | 26.25 | 13.18 | 13.18
| Sн. MV, МVА | 25+25 | 6.2 | 1 | 120 | 5.2 | 0 | 26.25 | 21.05 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 6.2 | 1 | 120 | 5.2 | 0 | 26.25 | 21.05 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 8.55 | 1.2 | 120 | 7.35 | 0 | 26.25 | 18.9 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.52 | 9.07 | 1.2 | 120 | 7.87 | 0 | 26.25 | 18.38
249 | Kalach-2 | 16+16 | 7.13 | 2 | 24 hours | 5.13 | 0 | 16.8 | 11.67 | 11.67 |  | 1.05 | 16 | 249 | Kalach-2 | 16+16 | 0.54 | 7.67 | 2 | 24 hours | 5.67 | 0 | 16.8 | 11.13 | 11.13 | 110/10
250 | Buturlinovka-1 | 16+16 | 12.94 | 2 | 120 | 10.94 | 0 | 16.8 | 5.86 | 5.86 |  | 1.05 | 16 | 250 | Buturlinovka-1 | 16+16 | 0.1 | 13.04 | 2 | 120 | 11.04 | 0 | 16.8 | 5.76 | 5.76
| Sн. MV, МVА | 16+16 | 2.89 | 0 | 0 | 2.89 | 0 | 16.8 | 13.91 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 2.89 | 0 | 0 | 2.89 | 0 | 16.8 | 13.91 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 10.05 | 2 | 120 | 8.05 | 0 | 16.8 | 8.75 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.1 | 10.15 | 2 | 120 | 8.15 | 0 | 16.8 | 8.65
251 | Buturlinovka-2 | 16+6,3 | 5.36 | 1.5 | 120 | 3.86 | 0 | 6.615 | 2.755 | 2.755 |  | 1.05 | 6.3 | 251 | Buturlinovka-2 | 16+6,3 | 0.01 | 5.37 | 1.5 | 120 | 3.87 | 0 | 6.615 | 2.745 | 2.745 | 110/10
252 | N.Kislyai | 10+10 | 6.28 | 1.5 | 120 | 4.78 | 0 | 10.5 | 5.72 | 5.72 |  | 1.05 | 10 | 252 | N.Kislyai | 10+10 | 0.4 | 6.68 | 1.5 | 120 | 5.18 | 0 | 10.5 | 5.32 | 5.32
| Sн. MV, МVА | 10+10 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2.92 | 0 | 0 | 2.92 | 0 | 10.5 | 7.58 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 3.36 | 1.5 | 120 | 1.86 | 0 | 10.5 | 8.64 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.4 | 3.76 | 1.5 | 120 | 2.26 | 0 | 10.5 | 8.24
253 | Kozlovka CPS | 2,5+6,3 | 1.14 | 1.5 | 45 | -0.36 | 0 | 2.625 | 2.985 | 2.985 |  | 1.05 | 2.5 | 253 | Kozlovka CPS | 2,5+6,3 | 0.18 | 1.32 | 1.5 | 45 | -0.18 | 0 | 2.625 | 2.805 | 2.805 | 110/10
254 | Filippenkovo | 6,3+6,3 | 1.12 | 1.5 | 120 | -0.38 | 0 | 6.615 | 6.995 | 6.995 |  | 1.05 | 6.3 | 254 | Filippenkovo | 6,3+6,3 | 0.05 | 1.17 | 1.5 | 120 | -0.33 | 0 | 6.615 | 6.945 | 6.945 | 110/10
255 | Vorobyovka | 16+16 | 5.85 | 1.5 | 120 | 4.35 | 0 | 16.8 | 12.45 | 12.45 |  | 1.05 | 16 | 255 | Vorobyovka | 16+16 | 0.41 | 6.26 | 1.5 | 120 | 4.76 | 0 | 16.8 | 12.04 | 12.04
| Sн. MV, МVА | 16+16 | 3.3 | 0.5 | 120 | 2.8 | 0 | 16.8 | 14 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.3 | 0.5 | 120 | 2.8 | 0 | 16.8 | 14 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 2.55 | 1 | 120 | 1.55 | 0 | 16.8 | 15.25 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.41 | 2.96 | 1 | 120 | 1.96 | 0 | 16.8 | 14.84
256 | Solontsy | 6,3+6,3 | 2.61 | 1 | 24 hours | 1.61 | 0 | 6.615 | 5.005 | 5.005 |  | 1.05 | 6.3 | 256 | Solontsy | 6,3+6,3 | 0.03 | 2.64 | 1 | 24 hours | 1.64 | 0 | 6.615 | 4.975 | 4.975
| Sн. MV, МVА | 6,3+6,3 | 1.71 | 1 | 24 hours | 0.71 | 0 | 6.615 | 5.905 |  |  | 1.05 | 6.3 |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.71 | 1 | 24 hours | 0.71 | 0 | 6.615 | 5.905 |  | 110/35/10
| Sн. LV, МVА | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 |  |  | 1.05 | 6.3 |  | Sн. LV, МVА | 6,3+6,3 | 0.03 | 0.93 | 0 | 0 | 0.93 | 0 | 6.615 | 5.685
257 | Manino | 16+16 | 2.05 | 1.5 | 24 hours | 0.55 | 0 | 16.8 | 16.25 | 16.25 |  | 1.05 | 16 | 257 | Manino | 16+16 | 0.03 | 2.08 | 1.5 | 24 hours | 0.58 | 0 | 16.8 | 16.22 | 16.22
| Sн. MV, МVА | 16+16 | 0.74 | 0.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 0.74 | 0.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 1.31 | 1 | 24 hours | 0.31 | 0 | 16.8 | 16.49 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 0.03 | 1.34 | 1 | 24 hours | 0.34 | 0 | 16.8 | 16.46
258 | Petropavlovka | 10+10 | 4.59 | 2 | 120 | 2.59 | 0 | 10.5 | 7.91 | 7.91 |  | 1.05 | 10 | 258 | Petropavlovka | 10+10 | 0.22 | 4.81 | 2 | 120 | 2.81 | 0 | 10.5 | 7.69 | 7.69
| Sн. MV, МVА | 10+10 | 2.01 | 1 | 120 | 1.01 | 0 | 10.5 | 9.49 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 10+10 | 0 | 2 | 1 | 120 | 1 | 0 | 10.5 | 9.5 |  | 110/35/10
| Sн. LV, МVА | 10+10 | 2.58 | 1 | 120 | 1.58 | 0 | 10.5 | 8.92 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 10+10 | 0.22 | 2.8 | 1 | 120 | 1.8 | 0 | 10.5 | 8.7
259 | V.Mamon | 16+10 | 5.87 | 2 | 120 | 3.87 | 0 | 10.5 | 6.63 | 6.63 |  | 1.05 | 10 | 259 | V.Mamon | 16+10 | 0.62 | 6.49 | 2 | 120 | 4.49 | 0 | 10.5 | 6.01 | 6.01
| Sн. MV, МVА | 16+10 | 2.13 | 0 | 0 | 2.13 | 0 | 10.5 | 8.37 |  |  | 1.05 | 10 |  | Sн. MV, МVА | 16+10 | 0 | 2.13 | 0 | 0 | 2.13 | 0 | 10.5 | 8.37 |  | 110/35/10
| Sн. LV, МVА | 16+10 | 3.74 | 2 | 120 | 1.74 | 0 | 10.5 | 8.76 |  |  | 1.05 | 10 |  | Sн. LV, МVА | 16+10 | 0.62 | 4.36 | 2 | 120 | 2.36 | 0 | 10.5 | 8.14
260 | N.Mamon | 2,5+6,3 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 |  | 1.05 | 2.5 | 260 | N.Mamon | 2,5+6,3 | 0.08 | 1.24 | 0 | 0 | 1.24 | 0 | 2.625 | 1.385 | 1.385 | 110/10
261 | Pavlovsk-2 | 25+25 | 19.63 | 1.5 | 120 | 18.13 | 0 | 26.25 | 8.12 | 8.12 |  | 1.05 | 25 | 261 | Pavlovsk-2 | 25+25 | 0.08 | 19.71 | 1.5 | 120 | 18.21 | 0 | 26.25 | 8.04 | 8.04
| Sн. MV, МVА | 25+25 | 9.94 | 1.5 | 120 | 8.44 | 0 | 26.25 | 17.81 |  |  | 1.05 | 25 |  | Sн. MV, МVА | 25+25 | 0 | 9.94 | 1.5 | 120 | 8.44 | 0 | 26.25 | 17.81 |  | 110/35/10
| Sн. LV, МVА | 25+25 | 9.69 | 0 | 0 | 9.69 | 0 | 26.25 | 16.56 |  |  | 1.05 | 25 |  | Sн. LV, МVА | 25+25 | 0.08 | 9.77 | 0 | 0 | 9.77 | 0 | 26.25 | 16.48
262 | Bogucharskaya | 16+16 | 9.16 | 2 | 120 | 7.16 | 0 | 16.8 | 9.64 | 9.64 |  | 1.05 | 16 | 262 | Bogucharskaya | 16+16 | 2.18 | 11.34 | 2 | 120 | 9.34 | 0 | 16.8 | 7.46 | 7.46
| Sн. MV, МVА | 16+16 | 3.65 | 1 | 120 | 2.65 | 0 | 16.8 | 14.15 |  |  | 1.05 | 16 |  | Sн. MV, МVА | 16+16 | 0 | 3.65 | 1 | 120 | 2.65 | 0 | 16.8 | 14.15 |  | 110/35/10
| Sн. LV, МVА | 16+16 | 5.51 | 1 | 120 | 4.51 | 0 | 16.8 | 12.29 |  |  | 1.05 | 16 |  | Sн. LV, МVА | 16+16 | 2.18 | 7.69 | 1 | 120 | 6.69 | 0 | 16.8 | 10.11
263 | Opornaya | 6,3+6,3 | 1.13 | 1.5 | 120 | -0.37 | 0 | 6.615 | 6.985 | 6.985 |  | 1.05 | 6.3 | 263 | Opornaya | 6,3+6,3 | 1.43 | 2.56 | 1.5 | 120 | 1.06 | 0 | 6.615 | 5.555 | 5.555 | 110/10
264 | Podgornaya KPS | 2,5+2,5 | 0.95 | 1 | 120 | -0.05 | 0 | 2.625 | 2.675 | 2.675 |  | 1.05 | 2.5 | 264 | Podgornaya KPS | 2,5+2,5 | 0.02 | 0.97 | 1 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | 35/10
265 | Bolshevik KPS | 4+2,5 | 2.24 | 1.5 | 45 | 0.74 | 0 | 2.625 | 1.885 | 1.885 |  | 1.05 | 2.5 | 265 | Bolshevik KPS | 4+2,5 | 0.22 | 2.46 | 1.5 | 45 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | 35/10
266 | Semenovka KPS | 2,5+1,8 | 0.84 | 1 | 80 | -0.16 | 0 | 1.89 | 2.05 | 2.05 |  | 1.05 | 1.8 | 266 | Semenovka KPS | 2,5+1,8 | 0.03 | 0.87 | 1 | 80 | -0.13 | 0 | 1.89 | 2.02 | 2.02 | 35/10
267 | Popasnoe | 4+4 | 0.31 | 1.5 | 120 | -1.19 | 0 | 4.2 | 5.39 | 5.39 |  | 1.05 | 4 | 267 | Popasnoe | 4+4 | 0.02 | 0.33 | 1.5 | 120 | -1.17 | 0 | 4.2 | 5.37 | 5.37 | 35/10
268 | N.Kriusha | 2,5+2,5 | 1.05 | 1.5 | 45 | -0.45 | 0 | 2.625 | 3.075 | 3.075 |  | 1.05 | 2.5 | 268 | N.Kriusha | 2,5+2,5 | 0.03 | 1.08 | 1.5 | 45 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | 35/10
269 | N.Melovatka | 2,5+2,5 | 1.49 | 1.5 | 45 | -0.01 | 0 | 2.625 | 2.635 | 2.635 |  | 1.05 | 2.5 | 269 | N.Melovatka | 2,5+2,5 | 0.07 | 1.56 | 1.5 | 45 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | 35/10
270 | Vasilyevka KPS | 4+4 | 0.91 | 1.5 | 120 | -0.59 | 0 | 4.2 | 4.79 | 4.79 |  | 1.05 | 4 | 270 | Vasilyevka KPS | 4+4 | 0.06 | 0.97 | 1.5 | 120 | -0.53 | 0 | 4.2 | 4.73 | 4.73 | 35/10
271 | V.Oktyabr | 4+4 | 1.22 | 1.5 | 120 | -0.28 | 0 | 4.2 | 4.48 | 4.48 |  | 1.05 | 4 | 271 | V.Oktyabr | 4+4 | 0.19 | 1.41 | 1.5 | 120 | -0.09 | 0 | 4.2 | 4.29 | 4.29 | 35/10
272 | V.Arkhangelskoe | 2,5+2,5 | 0.48 | 1.5 | 45 | -1.02 | 0 | 2.625 | 3.645 | 3.645 |  | 1.05 | 2.5 | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.07 | 0.55 | 1.5 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | 35/10
273 | Leshchanaya | 2,5+2,5 | 1.63 | 1.5 | 45 | 0.13 | 0 | 2.625 | 2.495 | 2.495 |  | 1.05 | 2.5 | 273 | Leshchanaya | 2,5+2,5 | 0.18 | 1.81 | 1.5 | 45 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | 35/10
274 | Muzhichye | 4+2,5 | 0.53 | 1.5 | 45 | -0.97 | 0 | 2.625 | 3.595 | 3.595 |  | 1.05 | 2.5 | 274 | Muzhichye | 4+2,5 | 0.11 | 0.64 | 1.5 | 45 | -0.86 | 0 | 2.625 | 3.485 | 3.485 | 35/10
275 | Rudnya | 4+4 | 0.44 | 1.5 | 120 | -1.06 | 0 | 4.2 | 5.26 | 5.26 |  | 1.05 | 4 | 275 | Rudnya | 4+4 | 0.03 | 0.47 | 1.5 | 120 | -1.03 | 0 | 4.2 | 5.23 | 5.23 | 35/10
276 | St. Melovaya | 4+4 | 0.85 | 0 | 0 | 0.85 | 0 | 4.2 | 3.35 | 3.35 |  | 1.05 | 4 | 276 | St. Melovaya | 4+4 | 0.07 | 0.92 | 0 | 0 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | 35/10
277 | St. Kriusha | 2,5+4 | 1.15 | 0 | 0 | 1.15 | 0 | 2.625 | 1.475 | 1.475 |  | 1.05 | 2.5 | 277 | St. Kriusha | 2,5+4 | 0.04 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | 35/10
278 | Lozovaya | 4+4 | 0.73 | 0 | 0 | 0.73 | 0 | 4.2 | 3.47 | 3.47 |  | 1.05 | 4 | 278 | Lozovaya | 4+4 | 0.3 | 1.03 | 0 | 0 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | 35/10
279 | Pavlovsk-1 | 4+4 | 2.17 | 1 | 120 | 1.17 | 0 | 4.2 | 3.03 | 3.03 |  | 1.05 | 4 | 279 | Pavlovsk-1 | 4+4 | 0.23 | 2.4 | 1 | 120 | 1.4 | 0 | 4.2 | 2.8 | 2.8 | 35/10
280 | Losevo KPS | 4+4 | 3.42 | 0 | 0 | 3.42 | 0 | 4.2 | 0.78 | 0.78 |  | 1.05 | 4 | 280 | Losevo KPS | 4+4 | 0.05 | 3.47 | 0 | 0 | 3.47 | 0 | 4.2 | 0.73 | 0.73 | 35/10
281 | Gavrilsk | 4+4 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 |  | 1.05 | 4 | 281 | Gavrilsk | 4+4 | 0.03 | 0.65 | 0 | 0 | 0.65 | 0 | 4.2 | 3.55 | 3.55 | 35/10
282 | Pokrovka | 4+2,5 | 0.98 | 0 | 0 | 0.98 | 0 | 2.625 | 1.645 | 1.645 |  | 1.05 | 2.5 | 282 | Pokrovka | 4+2,5 | 0.02 | 1 | 0 | 0 | 1 | 0 | 2.625 | 1.625 | 1.625 | 35/10
283 | Vorontsovka | 4+4 | 2.57 | 1.5 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 |  | 1.05 | 4 | 283 | Vorontsovka | 4+4 | 0.62 | 3.19 | 1.5 | 120 | 1.69 | 0 | 4.2 | 2.51 | 2.51 | 35/10
284 | А.Donskaya | 2,5+2,5 | 1.15 | 1.5 | 45 | -0.35 | 0 | 2.625 | 2.975 | 2.975 |  | 1.05 | 2.5 | 284 | А.Donskaya | 2,5+2,5 | 0.06 | 1.21 | 1.5 | 45 | -0.29 | 0 | 2.625 | 2.915 | 2.915 | 35/10
285 | Petrovka | 2,5+4 | 1.54 | 1.5 | 45 | 0.04 | 0 | 2.625 | 2.585 | 2.585 |  | 1.05 | 2.5 | 285 | Petrovka | 2,5+4 | 0.04 | 1.58 | 1.5 | 45 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | 35/10
286 | Monastyrshchina | 4+4 | 0.9 | 1.5 | 120 | -0.6 | 0 | 4.2 | 4.8 | 4.8 |  | 1.05 | 4 | 286 | Monastyrshchina | 4+4 | 0.1 | 1 | 1.5 | 120 | -0.5 | 0 | 4.2 | 4.7 | 4.7 | 35/10
287 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 |  | 1.05 | 1.8 | 287 | Zhuravka | 1,8+2,5 | 0 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | 35/10
288 | Dyachenkovo | 2,5+2,5 | 1.63 | 1.5 | 45 | 0.13 | 0 | 2.625 | 2.495 | 2.495 |  | 1.05 | 2.5 | 288 | Dyachenkovo | 2,5+2,5 | 0.46 | 2.09 | 1.5 | 45 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | 35/10
289 | Radchenskaya | 1,6+2,5 | 0.74 | 0 | 0 | 0.74 | 0 | 1.68 | 0.94 | 0.94 |  | 1.05 | 1.6 | 289 | Radchenskaya | 1,6+2,5 | 0.2 | 0.94 | 0 | 0 | 0.94 | 0 | 1.68 | 0.74 | 0.74 | 35/10
290 | Rossiya | 4+4 | 1.39 | 1.5 | 120 | -0.11 | 0 | 4.2 | 4.31 | 4.31 |  | 1.05 | 4 | 290 | Rossiya | 4+4 | 0.08 | 1.47 | 1.5 | 120 | -0.03 | 0 | 4.2 | 4.23 | 4.23 | 35/10
291 | Pervomayskaya | 4+4 | 0.42 | 1.5 | 120 | -1.08 | 0 | 4.2 | 5.28 | 5.28 |  | 1.05 | 4 | 291 | Pervomayskaya | 4+4 | 0.01 | 0.43 | 1.5 | 120 | -1.07 | 0 | 4.2 | 5.27 | 5.27 | 35/10
292 | Podkolodnovka | 2,5+3,2 | 1.09 | 0 | 0 | 1.09 | 0 | 2.625 | 1.535 | 1.535 |  | 1.05 | 2.5 | 292 | Podkolodnovka | 2,5+3,2 | 0.07 | 1.16 | 0 | 0 | 1.16 | 0 | 2.625 | 1.465 | 1.465 | 35/10
293 | Yuzhny | 2,5+2,5 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 |  | 1.05 | 2.5 | 293 | Yuzhny | 2,5+2,5 | 0 | 0.089683 | 0 | 0 | 0.089683 | 0 | 2.625 | 2.5353 | 2.5353 | 35/10
| TOTAL: |  | 1322.3557 | [6 empty] | 1074.694 |  |  |  | 2: TOTAL:; min. 12: 854.302
| deficit | [8 empty] | 63.665 |  |  |  | 2: deficit; min. 12: 132.2425
| proficit | [8 empty] | 1011.029 |  |  |  | 2: proficit; min. 12: 722.0595
Note on S7: не нашел
Note on S32: не нашел
Note on S57: не нашел
Note on S117: не нашел
Note on S232: не нашел
Note on S287: не нашел
Note on S349: не нашел
Note on S415: не нашел
Note on S416: не нашел
Note on S417: не нашел
Note on S418: не нашел
Note on S419: не нашел
Note on Z153: Ivanov_MA:
Note on AF415: не нашел