## Орел
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kV Almazovo | 2.5 | 0.49 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.34 | 0.34 | open | 1 | SS 35/10 kV Almazovo | 2.5 | 0.041 | 0.531 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.299 | 0.299 | open
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | open | 2 | SS 35/10 kV Voronets | 2.5 | 0 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | open
3 | SS 35/10 kV Gostoml | 2.5 | 0.79 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.81 | 0.81 | open | 3 | SS 35/10 kV Gostoml | 2.5 | 0.059 | 0.849 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.751 | 0.751 | open
4 | SS 35/10 kV Gubkino | 3.2 | 0.39 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.17 | 1.17 | open | 4 | SS 35/10 kV Gubkino | 3.2 | 0.014 | 0.404 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.156 | 1.156 | open
5 | SS 35/10 kV Devyatino | 1.6 | 0.21 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.5 | 0.5 | open | 5 | SS 35/10 kV Devyatino | 1.6 | 0.012 | 0.222 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.488 | 0.488 | open
6 | SS 35/10 kV Kamenka | 2.5 | 0.89 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.71 | 0.71 | open | 6 | SS 35/10 kV Kamenka | 2.5 | 0.025 | 0.915 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.685 | 0.685 | open
7 | SS 35/10 kV Kozminskaya | 2.5 | 0.33 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.96 | 0.96 | open | 7 | SS 35/10 kV Kozminskaya | 2.5 | 0.053 | 0.383 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.907 | 0.907 | open
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.23 | 6.14 | 60 | 1.91 | 0 | 6.14 | 1.91 | 0.04 | open | 8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 3.051 | 7.281 | 6.14 | 60 | 6.14 | 0 | 6.14 | -1.141 | -1.141 | closed
| Nom. capacity MV, MVA | 10 | 1.9 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.04 |  |  |  | Nom. capacity MV, MVA | 10 | 0.057 | 1.957 | 1.94 | 60 | 1.94 | 0 | 1.94 | -0.017
| Nom. capacity LV, MVA | 10 | 2.33 | 4.2 | 60 | 1.87 | 0 | 4.2 | 1.87 |  |  |  | Nom. capacity LV, MVA | 10 | 2.994 | 5.324 | 4.2 | 60 | 4.2 | 0 | 4.2 | -1.124
9 | SS 110/35/10 kV Novopolevo | 16 | 4.5 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.79 | -0.79 | closed | 9 | SS 110/35/10 kV Novopolevo | 16 | 0.728 | 5.228 | 3.71 | 30 | 3.71 | 0 | 3.71 | -1.518 | -1.518 | closed
| Nom. capacity MV, MVA | 16 | 3.2 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.295 | 3.495 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.895
| Nom. capacity LV, MVA | 16 | 1.3 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.19 |  |  |  | Nom. capacity LV, MVA | 16 | 0.433 | 1.733 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.623
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.51 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.82 | 0.82 | open | 10 | SS 35/10 kV Nikolskaya | 2.5 | 0.088 | 0.598 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.732 | 0.732 | open
11 | SS 35/10 kV Paramonovo | 1.8 | 0.34 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.14 | 0.14 | open | 11 | SS 35/10 kV Paramonovo | 1.8 | 0.127 | 0.467 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.013 | 0.013 | open
12 | SS 35/10 kV Senkovo | 1.6 | 0.42 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.87 | 0.87 | open | 12 | SS 35/10 kV Senkovo | 1.6 | 0.127 | 0.547 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.743 | 0.743 | open
13 | SS 35/10 kV Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | open | 13 | SS 35/10 kV Somovo | 2.5 | 0.021 | 0.361 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.599 | 0.599 | open
14 | SS 110/35/10 kV Trosna | 16 | 3.74 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.42 | -0.3 | closed | 14 | SS 110/35/10 kV Trosna | 16 | 0.879 | 4.619 | 4.16 | 45 | 4.16 | 0 | 4.16 | -0.459 | -0.459 | closed
| Nom. capacity MV, MVA | 16 | 2.66 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.065 | 2.725 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.365
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.814 | 1.894 | 1.8 | 45 | 1.8 | 0 | 1.8 | -0.094
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | open | 15 | SS 35/10 kV Shablykino | 5.6 | 0 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | open
16 | SS 35/10 kV Yuryevo | 2.5 | 0.17 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.9 | 0.9 | open | 16 | SS 35/10 kV Yuryevo | 2.5 | 0.029 | 0.199 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.871 | 0.871 | open
17 | SS 110/35/10 kV Region V | 10 | 4.48 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.92 | 0 | open | 17 | SS 110/35/10 kV Region V | 10 | 0.2 | 4.605 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.795 | 0.795 | open
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 |  |  |  | Nom. capacity LV, MVA | 10 | 0.565 | 4.605 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.795
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.79 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.085 | 0.085 | open | 18 | SS 110/10 kV Pishchevaya | 6.3 | 2.588 | 4.378 | 1.875 | 60 | 1.875 | 0 | 1.875 | -2.503 | -2.503 | closed
19 | SS 110/10 kV Telchye | 3.2 | 1.56 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.1 | -0.1 | closed | 19 | SS 110/10 kV Telchye | 3.2 | 0.054 | 1.614 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.154 | -0.154 | closed
20 | SS 110/10 kV B.Chern | 2.5 | 0.43 | 1 | 120 | 1 | 0 | 1 | 0.57 | 0.57 | open | 20 | SS 110/10 kV B.Chern | 2.5 | 0.272 | 0.702 | 1 | 120 | 1 | 0 | 1 | 0.298 | 0.298 | open
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.46 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.34 | 0.34 | open | 21 | SS 35/10 kV Bashkatovo | 1.6 | 0.018 | 0.478 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.322 | 0.322 | open
22 | SS 35/10 kV Vysokoe | 1.6 | 0.2 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.04 | 1.04 | open | 22 | SS 35/10 kV Vysokoe | 1.6 | 0.016 | 0.216 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.024 | 1.024 | open
23 | SS 35/10 kV Gladkoe | 2.5 | 0.32 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.14 | 1.14 | open | 23 | SS 35/10 kV Gladkoe | 2.5 | 0.024 | 0.344 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.116 | 1.116 | open
24 | SS 35/10 kV Lykovo | 2.5 | 0.72 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.52 | 0.52 | open | 24 | SS 35/10 kV Lykovo | 2.5 | 0.169 | 0.889 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.351 | 0.351 | open
25 | SS 35/6 kV Sugar mill | 4 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | open | 25 | SS 35/6 kV Sugar mill | 4 | 0 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | open
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.38 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.3 | 0.3 | open | 26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.014 | 0.394 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.286 | 0.286 | open
27 | SS 35/10 kV Koptevo | 2.5 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | open | 27 | SS 35/10 kV Koptevo | 2.5 | 0 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | open
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 | 0 | open | 28 | SS 110/35/10/6 kV Meat processing factory | 10 | 0.012 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221 | 0.221 | open
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 |  |  |  | Nom. capacity LV, MVA | 10 | 0.019 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221
29 | SS 110/35/10 kV Shatilovo | 10 | 1.21 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.52 | -0.52 | closed | 29 | SS 110/35/10 kV Shatilovo | 10 | 0.005 | 1.28 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.59 | -0.59 | closed
| Nom. capacity MV, MVA | 10 | 0.52 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.36 |  |  |  | Nom. capacity MV, MVA | 10 | 0.027 | 0.547 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.387
| Nom. capacity LV, MVA | 10 | 0.68 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.15 |  |  |  | Nom. capacity LV, MVA | 10 | 0.053 | 0.733 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.203
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.33 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.63 | 1.06 | open | 30 | SS 110/35/10 kV Sovkhoznaya | 10 | 2.017 | 5.357 | 8.96 | 120 | 8.96 | 0 | 8.96 | 3.603 | 0.985 | open
| Nom. capacity MV, MVA | 10 | 2.06 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.56 |  |  |  | Nom. capacity MV, MVA | 10 | 1.942 | 4.002 | 6.62 | 120 | 6.62 | 0 | 6.62 | 2.618
| Nom. capacity LV, MVA | 10 | 1.28 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.06 |  |  |  | Nom. capacity LV, MVA | 10 | 0.075 | 1.355 | 2.34 | 120 | 2.34 | 0 | 2.34 | 0.985
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | open | 31 | SS 35/10 kV Danilovskaya | 1.6 | 0 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | open
32 | SS 35/10 kV Korseevo | 1.8 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | open | 32 | SS 35/10 kV Korseevo | 1.8 | 0 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | open
33 | SS 35/10 kV Lipovets | 2.5 | 0.74 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.65 | 0.65 | open | 33 | SS 35/10 kV Lipovets | 2.5 | 0.316 | 1.056 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.334 | 0.334 | open
34 | SS 35/10 kV Misaylovo | 1.6 | 0.3 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.3 | 1.3 | open | 34 | SS 35/10 kV Misaylovo | 1.6 | 0 | 0.3 | 1.6 |  | 1.6 | 0 | 1.6 | 1.3 | 1.3 | open
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | open | 35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.009 | 0.269 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.041 | 0.041 | open
36 | SS 35/10 kV Pankovo | 1.8 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open | 36 | SS 35/10 kV Pankovo | 1.8 | 0.027 | 0.547 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.053 | 1.053 | open
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.65 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.95 | 0.95 | open | 37 | SS 35/10 kV Sudbishchi | 2.5 | 0.015 | 0.665 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.935 | 0.935 | open
38 | SS 35/10 kV Tim | 1.6 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | open | 38 | SS 35/10 kV Tim | 1.6 | 0.006 | 0.526 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.074 | 1.074 | open
39 | SS 35/10 kV Topki | 1 | 0.19 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.41 | 1.41 | open | 39 | SS 35/10 kV Topki | 1 | 0.041 | 0.231 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.369 | 1.369 | open
40 | SS 35/10 kV Yarishche | 2.5 | 0.29 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.31 | 1.31 | open | 40 | SS 35/10 kV Yarishche | 2.5 | 0.032 | 0.322 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.278 | 1.278 | open
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.06 | 3.88 | 30 | 0.18 | 0 | 10.5 | 10.32 | 10.32 | open | 41 | SS 110/10 kV Alshanskaya | 10+10 | 0.504 | 4.564 | 3.88 | 30 | 0.684 | 0 | 10.5 | 9.816 | 9.816 | open
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | open | 42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.018 | 0.418 | 0.93 | 90 | -0.512 | 0 | 2.625 | 3.137 | 3.137 | open
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | open | 43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.376 | 1.076 | 0 |  | 1.076 | 0 | 1.68 | 0.604 | 0.604 | open
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.64 | 3.06 | 90 | -0.42 | 0 | 10.5 | 10.92 | 10.51 | open | 44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 0.763 | 3.403 | 3.06 | 90 | 0.343 | 0 | 10.5 | 10.157 | 10.157 | open
| Nom. capacity MV, MVA | 10+10 | 2.42 | 2.43 | 90 | -0.01 | 0 | 10.5 | 10.51 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.763 | 3.183 | 2.43 | 90 | 0.753 | 0 | 10.5 | 9.747
| Nom. capacity LV, MVA | 10+10 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 1.01 | 0.64 | 60 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | open | 45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.066 | 1.076 | 0.64 | 60 | 0.436 | 0 | 1.68 | 1.244 | 1.244 | open
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.07 | 2.05 | 90 | 1.02 | 0 | 6.615 | 5.595 | 5.595 | open | 46 | SS 35/10 kV Biofactory | 6,3+6,3 | 0.892 | 3.962 | 2.05 | 90 | 1.912 | 0 | 6.615 | 4.703 | 4.703 | open
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.19 | 1.46 | 30 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | open | 47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.773 | 6.963 | 1.46 | 30 | 5.503 | 0 | 2.625 | -2.878 | -2.878 | closed
48 | SS 110/10 kV Vostochnaya | 15+15 | 13.63 | 5.87 | 120 | 7.76 | 0 | 15.75 | 7.99 | 7.99 | open | 48 | SS 110/10 kV Vostochnaya | 15+15 | 0.471 | 14.101 | 5.87 | 120 | 8.231 |  | 15.75 | 7.519 | 7.519 | open
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.26 | 0.45 | 60 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | open | 49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 0.214 | 3.474 | 0.45 | 60 | 3.024 | 0 | 10.5 | 7.476 | 7.476 | open
| Nom. capacity MV, MVA | 10+10 | 0.25 | 0 | 0 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.012 | 0.262 | 0 |  | 0.262 | 0 | 10.5 | 10.238
| Nom. capacity LV, MVA | 10+10 | 3.01 | 0.45 | 60 | 2.56 | 0 | 10.5 | 7.94 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.202 | 3.212 | 0.45 | 60 | 2.762 | 0 | 10.5 | 7.738
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.84 | 3.98 | 180 | 7.86 | 0 | 16.8 | 8.94 | 8.94 | open | 50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 0.341 | 12.181 | 3.98 | 180 | 8.201 | 0 | 16.8 | 8.599 | 8.599 | open
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.98 | 0.64 | 60 | 0.34 | 0 | 1.89 | 1.55 | 1.55 | open | 51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.019 | 0.999 | 0.64 | 60 | 0.359 | 0 | 1.89 | 1.531 | 1.531 | open
52 | SS 110/6 kV Zavodskaya | 40+25 | 11.83 | 4.39 | 150 | 7.44 | 0 | 26.25 | 18.81 | 18.81 | open | 52 | SS 110/6 kV Zavodskaya | 40+25 | 1.612 | 13.442 | 4.39 | 150 | 9.052 | 0 | 26.25 | 17.198 | 17.198 | open
53 | SS 110/6 kV Zapadnaya | 63+63 | 25.39 | 5.37 | 120 | 20.02 | 19 | 66.15 | 27.13 | 27.13 | open | 53 | SS 110/6 kV Zapadnaya | 63+63 | 15.235 | 40.625 | 5.37 | 120 | 35.255 | 19 | 66.15 | 11.895 | 11.895 | open
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.87 | 1.48 | 60 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | open | 54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.105 | 2.975 | 1.48 | 60 | 1.495 | 0 | 2.625 | 1.13 | 1.13 | open
55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.84 | 1.18 | 30 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | open | 55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.082 | 0.922 | 1.18 | 30 | -0.258 | 0 | 1.68 | 1.938 | 1.938 | open
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 5.59 | 1.44 | 90 | 4.15 | 0 | 10.5 | 6.35 | 6.35 | open | 56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 6.049 | 11.639 | 1.44 | 90 | 10.199 | 0 | 10.5 | 0.301 | 0.301 | open
| Nom. capacity MV, MVA | 10+10 | 1.76 | 1 | 90 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.338 | 2.098 | 1 | 90 | 1.098 | 0 | 10.5 | 9.402
| Nom. capacity LV, MVA | 10+10 | 3.83 | 0.44 | 90 | 3.39 | 0 | 10.5 | 7.11 |  |  |  | Nom. capacity LV, MVA | 10+10 | 5.711 | 9.541 | 0.44 | 90 | 9.101 | 0 | 10.5 | 1.399
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.68 | 6.83 | 45 | -0.15 | 0 | 16.8 | 16.95 | 15.28 | open | 57 | SS 110/35/10 kV Kromskaya | 16+16 | 7.026 | 13.706 | 6.83 | 45 | 6.876 | 0 | 16.8 | 9.924 | 9.924 | open
| Nom. capacity MV, MVA | 16+16 | 3.33 | 5 | 45 | -1.67 | 0 | 16.8 | 18.47 |  |  |  | Nom. capacity MV, MVA | 16+16 | 6.445 | 9.775 | 5 | 45 | 4.775 | 0 | 16.8 | 12.025
| Nom. capacity LV, MVA | 16+16 | 3.35 | 1.83 | 45 | 1.52 | 0 | 16.8 | 15.28 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.581 | 3.931 | 1.83 | 45 | 2.101 | 0 | 16.8 | 14.699
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.63 | 0.95 | 30 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | open | 58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 0.065 | 1.695 | 0.95 | 30 | 0.745 | 0 | 2.625 | 1.88 | 1.88 | open
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | open | 59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.02 | 0.58 | 0 |  | 0.58 | 0 | 1.68 | 1.1 | 1.1 | open
60 | SS 35/10 kV Kutafino | 1,6+1,6 | 0.66 | 0.83 | 30 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | open | 60 | SS 35/10 kV Kutafino | 1,6+1,6 | 5.905 | 6.565 | 0.83 | 30 | 5.735 | 0 | 1.68 | -4.055 | -4.055 | closed
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.89 | 1.59 | 30 | -0.7 | 0 | 2.625 | 3.325 | 3.325 | open | 61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.127 | 1.017 | 1.59 | 30 | -0.573 | 0 | 2.625 | 3.198 | 3.198 | open
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.48 | 0.47 | 60 | 0.01 | 0 | 1.05 | 1.04 | 1.04 | open | 62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.02 | 0.5 | 0.47 | 60 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | open
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.33 | 0.99 | 90 | -0.66 | 0 | 1.89 | 2.55 | 2.55 | open | 63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.018 | 0.348 | 0.99 | 90 | -0.642 | 0 | 1.89 | 2.532 | 2.532 | open
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.47 | 1.7 | 30 | -1.23 | 0 | 5.88 | 7.11 | 7.11 | open | 64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 1.082 | 1.552 | 1.7 | 30 | -0.148 | 0 | 5.88 | 6.028 | 6.028 | open
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 9.2 | 1.41 | 90 | 7.79 | 0 | 10.5 | 2.71 | 2.71 | open | 65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 1.003 | 10.203 | 1.41 | 90 | 8.793 | 0 | 10.5 | 1.707 | 1.707 | open
| Nom. capacity MV, MVA | 10+10 | 2.76 | 0.86 | 90 | 1.9 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.123 | 2.883 | 0.86 | 90 | 2.023 | 0 | 10.5 | 8.477
| Nom. capacity LV, MVA | 10+10 | 6.44 | 0.55 | 90 | 5.89 | 0 | 10.5 | 4.61 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.88 | 7.32 | 0.55 | 90 | 6.77 | 0 | 10.5 | 3.73
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.68 | 1.63 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | open | 66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.021 | 0.701 | 1.63 | 45 | -0.929 | 0 | 2.625 | 3.554 | 3.554 | open
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.52 | 0.73 | 60 | -0.21 | 0 | 1.68 | 1.89 | 1.89 | open | 67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.066 | 0.586 | 0.73 | 60 | -0.144 | 0 | 1.68 | 1.824 | 1.824 | open
68 | SS 35/10 kV Putimets | 2,5+2,5 | 1.31 | 1.53 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.175 | 1.485 | 1.53 | 90 | -0.045 | 0 | 2.625 | 2.67 | 2.67 | open
69 | SS 110/10 kV Pishchevaya* | 40+25 | 5.38 | 2.22 | 60 | 3.16 | 0 | 26.25 | 23.09 | 23.09 | open | 69 | SS 110/10 kV Pishchevaya* | 40+25 | 0.268 | 5.648 | 2.22 | 60 | 3.428 | 0 | 26.25 | 22.822 | 22.822 | open
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.43 | 0.65 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open | 70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.036 | 0.466 | 0.65 | 90 | -0.184 | 0 | 2.625 | 2.809 | 2.809 | open
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.69 | 1.98 | 45 | 0.71 | 0 | 10.5 | 9.79 | 9.74 | open | 71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 0.829 | 3.519 | 1.98 | 45 | 1.539 | 0 | 10.5 | 8.961 | 8.961 | open
| Nom. capacity MV, MVA | 10+10 | 1.36 | 1.41 | 45 | -0.05 | 0 | 10.5 | 10.55 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.207 | 1.567 | 1.41 | 45 | 0.157 | 0 | 10.5 | 10.343
| Nom. capacity LV, MVA | 10+10 | 1.33 | 0.57 | 45 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.622 | 1.952 | 0.57 | 45 | 1.382 | 0 | 10.5 | 9.118
72 | SS 35/10 kV Streletskaya | 4+4 | 1.66 | 0.91 | 90 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | open | 72 | SS 35/10 kV Streletskaya | 4+4 | 1.622 | 3.282 | 0.91 | 90 | 2.372 | 0 | 4.2 | 1.828 | 1.828 | open
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 27.61 | 3.86 | 180 | 23.75 | 0 | 68.25 | 44.5 | 19.36 | open | 73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 9.084 | 29.364 | 3.86 | 180 | 25.504 | 0 | 68.25 | 42.746 | 16.634 | open
| Nom. capacity MV -35kV; MVA | 20+20 | 6.74 | 5.1 | 90 | 1.64 | 0 | 21 | 19.36 |  |  |  | Nom. capacity MV -35kV; MVA | 20+20 | 2.726 | 9.466 | 5.1 | 90 | 4.366 | 0 | 21 | 16.634
| Nom. capacity LV-10kV; MVA | 25+40 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72 |  |  |  | Nom. capacity LV-10kV; MVA | 25+40 | 0 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72
| Nom. capacity LV-6kV; MVA | 20+20+40 | 13.54 | 3.86 | 180 | 9.68 | 0 | 42 | 32.32 |  |  |  | Nom. capacity LV-6kV; MVA | 20+20+40 | 6.358 | 19.898 | 3.86 | 180 | 16.038 | 0 | 42 | 25.962
74 | SS 35/10 kV Soskovskaya | 4+3,2 | 1.13 | 0.64 | 90 | 0.49 | 0 | 3.36 | 2.87 | 2.87 | open | 74 | SS 35/10 kV Soskovskaya | 4+3,2 | 0.049 | 1.179 | 0.64 | 90 | 0.539 | 0 | 3.36 | 2.821 | 2.821 | open
75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.69 | 1.76 | 30 | -1.07 | 0 | 3.36 | 4.43 | 4.43 | open | 75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.045 | 0.735 | 1.76 | 30 | -1.025 | 0 | 3.36 | 4.385 | 4.385 | open
76 | SS 110/10 kV Khimmash | 25+25 | 6.32 | 1.51 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | open | 76 | SS 110/10 kV Khimmash | 25+25 | 7.694 | 14.014 | 1.51 | 120 | 12.504 | 0 | 26.25 | 13.746 | 13.746 | open
77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.97 | 0 | - | 0.97 | 0 | 5.88 | 4.91 | 4.91 | open | 77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0 | 0.97 | 0 |  | 0.97 | 0 | 5.88 | 4.91 | 4.91 | open
78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 2.2 | 1.49 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | open | 78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 0.734 | 2.934 | 1.49 | 80 | 1.444 | 0 | 2.625 | 1.181 | 1.181 | open
79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.58 | 1.03 | 80 | -0.45 | 0 | 1.68 | 2.13 | 2.13 | open | 79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.064 | 0.644 | 1.03 | 80 | -0.386 | 0 | 1.68 | 2.066 | 2.066 | open
80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | open | 80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 0 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | open
81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 2.68 | 1.36 | 30 | 1.32 | 0 | 6.615 | 5.295 | 5.295 | open | 81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 0.103 | 2.783 | 1.36 | 30 | 1.423 | 0 | 6.615 | 5.192 | 5.192 | open
| Nom. capacity MV, MVA | 6,3+6,3 | 1.08 | 0.54 | 30 | 0.54 | 0 | 6.615 | 6.075 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.085 | 1.165 | 0.54 | 30 | 0.625 | 0 | 6.615 | 5.99
| Nom. capacity LV, MVA | 6,3+6,3 | 1.6 | 0.82 | 30 | 0.78 | 0 | 6.615 | 5.835 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.018 | 1.618 | 0.82 | 30 | 0.798 | 0 | 6.615 | 5.817
82 | SS 110/35/10 kV Shakhovo | 10+10 | 4.21 | 2.55 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | open | 82 | SS 110/35/10 kV Shakhovo | 10+10 | 4.319 | 8.529 | 2.55 | 120 | 5.979 | 0 | 10.5 | 4.521 | 4.521 | open
| Nom. capacity MV, MVA | 10+10 | 1.33 | 0.39 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.175 | 1.505 | 0.39 | 120 | 1.115 | 0 | 10.5 | 9.385
| Nom. capacity LV, MVA | 10+10 | 2.88 | 2.16 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. capacity LV, MVA | 10+10 | 4.144 | 7.024 | 2.16 | 120 | 4.864 | 0 | 10.5 | 5.636
83 | SS 35/10 kV Shepino | 2,5+1,6 | 1.6 | 1.1 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 83 | SS 35/10 kV Shepino | 2,5+1,6 | 0.338 | 1.938 | 1.1 | 120 | 0.838 | 0 | 1.68 | 0.842 | 0.842 | open
84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 9.8 | 0.74 | 60 | 9.06 | 0 | 26.25 | 17.19 | 17.19 | open | 84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 1.176 | 10.976 | 0.74 | 60 | 10.236 | 0 | 26.25 | 16.014 | 16.014 | open
85 | SS 110/10 kV Yuzhnaya | 10+10 | 7.42 | 1.05 | 90 | 6.37 | 0 | 10.5 | 4.13 | 4.13 | open | 85 | SS 110/10 kV Yuzhnaya | 10+10 | 1.67 | 9.09 | 1.05 | 90 | 8.04 | 0 | 10.5 | 2.46 | 2.46 | open
86 | SS 220/110/10 kV Mtsensk | 40+40 | 9.57 | 0 | - | 9.57 | 0 | 42 | 32.43 | 32.43 | open | 86 | SS 220/110/10 kV Mtsensk | 40+40 | 0.46 | 10.03 | 0 |  | 10.03 | 0 | 42 | 31.97 | 31.97 | open
87 | SS 110/35/10 kV Kommash | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 | 4.89 | open | 87 | SS 110/35/10 kV Kommash | 10+16 | 3.984 | 14.244 | 4.65 | 90 | 9.594 | 0 | 10.5 | 0.906 | 0.906 | open
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 |  |  |  | Nom. capacity LV, MVA | 10+16 | 3.984 | 14.244 | 4.65 | 90 | 9.594 | 0 | 10.5 | 0.906
88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 1.84 | 4.13 | 120 | -2.29 | 0 | 6.615 | 8.905 | 7.365 | open | 88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 0.292 | 2.102 | 4.13 | 120 | -2.028 | 0 | 6.615 | 8.643 | 7.073 | open
| Nom. capacity MV, MVA | 6,3+10 | 1.65 | 2.4 | 120 | -0.75 | 0 | 6.615 | 7.365 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.292 | 1.942 | 2.4 | 120 | -0.458 | 0 | 6.615 | 7.073
| Nom. capacity LV, MVA | 6,3+10 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185
89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 2.52 | 1.83 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | open | 89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 0.094 | 2.614 | 1.83 | 120 | 0.784 | 0 | 6.615 | 5.831 | 5.831 | open
90 | SS 110/35/10 kV Zalegoshch | 10+16 | 6 | 3.95 | 120 | 2.05 | 0 | 10.5 | 8.45 | 8.45 | open | 90 | SS 110/35/10 kV Zalegoshch | 10+16 | 0.191 | 6.191 | 3.95 | 120 | 2.241 | 0 | 10.5 | 8.259 | 8.259 | open
| Nom. capacity MV, MVA | 10+16 | 2.71 | 2.39 | 120 | 0.32 | 0 | 10.5 | 10.18 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.09 | 2.8 | 2.39 | 120 | 0.41 | 0 | 10.5 | 10.09
| Nom. capacity LV, MVA | 10+16 | 3.29 | 1.56 | 120 | 1.73 | 0 | 10.5 | 8.77 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.101 | 3.391 | 1.56 | 120 | 1.831 | 0 | 10.5 | 8.669
91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.26 | 0.66 | 120 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | open | 91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.029 | 0.289 | 0.66 | 120 | -0.371 | 0 | 2.625 | 2.996 | 2.996 | open
92 | SS 110/35/10 kV Bolkhov | 10+10 | 7.69 | 4.1 | 120 | 3.59 | 0 | 10.5 | 6.91 | 6.88 | open | 92 | SS 110/35/10 kV Bolkhov | 10+10 | 0.382 | 8.062 | 4.1 | 120 | 3.962 | 0 | 10.5 | 6.538 | 6.538 | open
| Nom. capacity MV, MVA | 10+10 | 2.41 | 2.45 | 120 | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.297 | 2.707 | 2.45 | 120 | 0.257 | 0 | 10.5 | 10.243
| Nom. capacity LV, MVA | 10+10 | 5.27 | 1.65 | 120 | 3.62 | 0 | 10.5 | 6.88 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.085 | 5.355 | 1.65 | 120 | 3.705 | 0 | 10.5 | 6.795
93 | SS 110/35/10 kV Novosil | 10+10 | 4.98 | 2.98 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | open | 93 | SS 110/35/10 kV Novosil | 10+10 | 0.175 | 5.195 | 2.98 | 120 | 2.215 | 0 | 10.5 | 8.285 | 8.285 | open
| Nom. capacity MV, MVA | 10+10 | 2.53 | 1.46 | 120 | 1.07 | 0 | 10.5 | 9.43 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.095 | 2.625 | 1.46 | 120 | 1.165 | 0 | 10.5 | 9.335
| Nom. capacity LV, MVA | 10+10 | 2.49 | 1.52 | 120 | 0.97 | 0 | 10.5 | 9.53 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.08 | 2.57 | 1.52 | 120 | 1.05 | 0 | 10.5 | 9.45
94 | SS 110/35/10 kV Znamenskaya | 10+10 | 2.14 | 1.78 | 120 | 0.36 | 0 | 10.5 | 10.14 | 10.14 | open | 94 | SS 110/35/10 kV Znamenskaya | 10+10 | 0.098 | 2.198 | 1.78 | 120 | 0.418 | 0 | 10.5 | 10.082 | 10.082 | open
| Nom. capacity MV, MVA | 10+10 | 0.39 | 0.34 | 120 | 0.05 | 0 | 10.5 | 10.45 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.016 | 0.406 | 0.34 | 120 | 0.066 | 0 | 10.5 | 10.434
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.082 | 1.792 | 1.44 | 120 | 0.352 | 0 | 10.5 | 10.148
95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.29 | 0.48 | 120 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | open | 95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.021 | 0.311 | 0.48 | 120 | -0.169 | 0 | 1.89 | 2.059 | 2.059 | open
96 | SS 35/10 kV Podberyozovo | 4+1 | 0.14 | 0.59 | 120 | -0.45 | 0 | 1.05 | 1.5 | 1.5 | open | 96 | SS 35/10 kV Podberyozovo | 4+1 | 0.016 | 0.156 | 0.59 | 120 | -0.434 | 0 | 1.05 | 1.484 | 1.484 | open
97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0.54 | 0 |  | 0.54 | 0 | 1.68 | 1.14 | 1.14 | open | 97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0.018 | 0.558 | 0 |  | 0.558 | 0 | 1.68 | 1.122 | 1.122 | open
98 | SS 35/10 kV Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | open | 98 | SS 35/10 kV Alyoshnya | 1+1 | 0.034 | 0.374 | 0.24 | 120 | 0.134 | 0 | 1.05 | 0.916 | 0.916 | open
99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 1.25 | 0 | - | 1.25 | 0 | 2.625 | 1.375 | 1.375 | open | 99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0.029 | 1.279 | 0 |  | 1.279 | 0 | 2.625 | 1.346 | 1.346 | open
100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.89 | 0.63 | 120 | 0.26 |  | 2.625 | 2.365 | 2.365 | open | 100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.027 | 0.917 | 0.63 | 120 | 0.287 | 0 | 2.625 | 2.338 | 2.338 | open
101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | open | 101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | open
102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.33 | 0 | - | 0.33 | 0 | 2.625 | 2.295 | 2.295 | open | 102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.042 | 0.372 | 0 |  | 0.372 | 0 | 2.625 | 2.253 | 2.253 | open
103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.66 | 0.67 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | open | 103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.169 | 0.829 | 0.67 | 120 | 0.159 | 0 | 2.625 | 2.466 | 2.466 | open
104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.59 | 0.37 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open | 104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.033 | 0.623 | 0.37 | 120 | 0.253 | 0 | 1.68 | 1.427 | 1.427 | open
105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open | 105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | open
106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.36 | 0 | - | 0.36 | 0 | 1.68 | 1.32 | 1.32 | open | 106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.039 | 0.399 | 0 |  | 0.399 | 0 | 1.68 | 1.281 | 1.281 | open
107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | open | 107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.016 | 0.196 | 0.25 | 120 | -0.054 | 0 | 1.05 | 1.104 | 1.104 | open
108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | open | 108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.091 | 0.851 | 0.69 | 120 | 0.161 | 0 | 2.625 | 2.464 | 2.464 | open
109 | SS 35/10 kV Paramonovo | 4+2,5 | 1.06 | 0.76 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | open | 109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.056 | 1.116 | 0.76 | 120 | 0.356 | 0 | 2.625 | 2.269 | 2.269 | open
110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.067 | 0.257 | 0 |  | 0.257 | 0 | 1.68 | 1.423 | 1.423 | open
111 | SS 110/35/10 kV Verkhovye I | 16+10 | 7.34 | 3.65 | 120 | 3.69 | 0 | 10.5 | 6.81 | 6.81 | open | 111 | SS 110/35/10 kV Verkhovye I | 16+10 | 0.203 | 7.543 | 3.65 | 120 | 3.893 | 0 | 10.5 | 6.607 | 6.607 | open
| Nom. capacity MV, MVA | 16+10 | 2.25 | 2.05 | 120 | 0.2 | 0 | 10.5 | 10.3 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.025 | 2.275 | 2.05 | 120 | 0.225 | 0 | 10.5 | 10.275
| Nom. capacity LV, MVA | 16+10 | 5.09 | 1.6 | 120 | 3.49 | 0 | 10.5 | 7.01 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.178 | 5.268 | 1.6 | 120 | 3.668 | 0 | 10.5 | 6.832
112 | SS 110/35/10 kV Verkhovye II | 40+40 | 7.05 | 0.3 | - | 6.75 | 0 | 42 | 35.25 | 35.25 | open | 112 | SS 110/35/10 kV Verkhovye II | 40+40 | 0.009 | 7.099 | 0.3 |  | 6.799 | 0 | 42 | 35.201 | 35.201 | open
| Nom. capacity MV, MVA | 40+40 | 0.37 | 0.3 | - | 0.07 | 0 | 42 | 41.93 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.009 | 0.379 | 0.3 |  | 0.079 | 0 | 42 | 41.921
| Nom. capacity LV, MVA | 40+40 | 6.72 | 0 | - | 6.72 | 0 | 42 | 35.28 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 6.72 | 0 |  | 6.72 | 0 | 42 | 35.28
113 | SS 110/35/10 kV Dolgoe | 16+10 | 4.82 | 3.38 | 120 | 1.44 | 0 | 10.5 | 9.06 | 8.55 | open | 113 | SS 110/35/10 kV Dolgoe | 16+10 | 0.076 | 4.896 | 3.38 | 120 | 1.516 | 0 | 10.5 | 8.984 | 8.492 | open
| Nom. capacity MV, MVA | 16+10 | 1.87 | 2.38 | 120 | -0.51 | 0 | 10.5 | 11.01 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.018 | 1.888 | 2.38 | 120 | -0.492 | 0 | 10.5 | 10.992
| Nom. capacity LV, MVA | 16+10 | 2.95 | 1 | 120 | 1.95 | 0 | 10.5 | 8.55 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.058 | 3.008 | 1 | 120 | 2.008 | 0 | 10.5 | 8.492
114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 3.73 | 2.79 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.35 | open | 114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 0.236 | 3.966 | 2.79 | 120 | 1.176 | 0 | 10.5 | 9.324 | 9.225 | open
| Nom. capacity MV, MVA | 10+16 | 2.25 | 2.46 | 120 | -0.21 | 0 | 10.5 | 10.71 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.111 | 2.361 | 2.46 | 120 | -0.099 | 0 | 10.5 | 10.599
| Nom. capacity LV, MVA | 10+16 | 1.48 | 0.33 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.125 | 1.605 | 0.33 | 120 | 1.275 | 0 | 10.5 | 9.225
115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 3.69 | 1.54 | 120 | 2.15 | 0 | 10.5 | 8.35 | 8.35 | open | 115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 0.07 | 3.78 | 1.54 | 120 | 2.24 | 0 | 10.5 | 8.26 | 8.26 | open
| Nom. capacity MV, MVA | 10+10 | 1.6 | 1.29 | 120 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.024 | 1.624 | 1.29 | 120 | 0.334 | 0 | 10.5 | 10.166
| Nom. capacity LV, MVA | 10+10 | 2.11 | 0.25 | 120 | 1.86 | 0 | 10.5 | 8.64 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.046 | 2.156 | 0.25 | 120 | 1.906 | 0 | 10.5 | 8.594
116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 5.36 | 2.84 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | open | 116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 0.626 | 5.996 | 2.84 | 120 | 3.156 | 0 | 10.5 | 7.344 | 7.344 | open
| Nom. capacity MV, MVA | 10+10 | 2.47 | 2.12 | 120 | 0.35 | 0 | 10.5 | 10.15 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.206 | 2.676 | 2.12 | 120 | 0.556 | 0 | 10.5 | 9.944
| Nom. capacity LV, MVA | 10+10 | 2.9 | 0.72 | 120 | 2.18 | 0 | 10.5 | 8.32 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.42 | 3.32 | 0.72 | 120 | 2.6 | 0 | 10.5 | 7.9
117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 21.65 | 13.39 | 120 | 8.26 | 0 | 26.25 | 17.99 | 17.99 | open | 117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 3.782 | 25.452 | 13.39 | 120 | 12.062 | 0 | 26.25 | 14.188 | 14.188 | open
| Nom. capacity MV, MVA | 40+25 | 15.2 | 10.84 | 120 | 4.36 | 0 | 26.25 | 21.89 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.788 | 17.988 | 10.84 | 120 | 7.148 | 0 | 26.25 | 19.102
| Nom. capacity LV, MVA | 40+25 | 6.47 | 2.55 | 120 | 3.92 | 0 | 26.25 | 22.33 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0.994 | 7.464 | 2.55 | 120 | 4.914 | 0 | 26.25 | 21.336
118 | SS 110/6 kV Plastmass | 16+16 | 9.77 | 0 | - | 9.77 | 0 | 16.8 | 7.03 | 7.03 | open | 118 | SS 110/6 kV Plastmass | 16+16 | 0 | 9.77 | 0 |  | 9.77 | 0 | 16.8 | 7.03 | 7.03 | open
119 | SS 110/10 kV PM | 10+10 | 3.48 | 0 | - | 3.48 | 0 | 10.5 | 7.02 | 7.02 | open | 119 | SS 110/10 kV PM | 10+10 | 0 | 3.48 | 0 |  | 3.48 | 0 | 10.5 | 7.02 | 7.02 | open
120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.95 | 1.85 | 120 | -0.9 | 0 | 6.615 | 7.515 | 7.515 | open | 120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.033 | 0.983 | 1.85 | 120 | -0.867 | 0 | 6.615 | 7.482 | 7.482 | open
121 | SS 110/10 kV R.Brod | 5,6+10 | 1.6 | 0.29 | 120 | 1.31 | 0 | 5.88 | 4.57 | 4.57 | open | 121 | SS 110/10 kV R.Brod | 5,6+10 | 0.135 | 1.735 | 0.29 | 120 | 1.445 | 0 | 5.88 | 4.435 | 4.435 | open
122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.63 | 0.13 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | open | 122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.098 | 0.728 | 0.13 | 120 | 0.598 | 0 | 1.68 | 1.082 | 1.082 | open
123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.85 | 0.65 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | open | 123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.061 | 0.911 | 0.65 | 120 | 0.261 | 0 | 2.625 | 2.364 | 2.364 | open
124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open | 124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | open
125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.68 | 0.56 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open | 125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.027 | 0.707 | 0.56 | 120 | 0.147 | 0 | 1.68 | 1.533 | 1.533 | open
126 | SS 35/10 kV Droskovo | 4+2,5 | 1.57 | 0 | - | 1.57 | 0 | 2.625 | 1.055 | 1.055 | open | 126 | SS 35/10 kV Droskovo | 4+2,5 | 0.108 | 1.678 | 0 |  | 1.678 | 0 | 2.625 | 0.947 | 0.947 | open
127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.96 | 0.39 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | open | 127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.035 | 0.995 | 0.39 | 120 | 0.605 | 0 | 6.615 | 6.01 | 6.01 | open
128 | SS 35/10 kV Krutoe | 2,5+2,5 | 1.41 | 0.87 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open | 128 | SS 35/10 kV Krutoe | 2,5+2,5 | 0.173 | 1.583 | 0.87 | 120 | 0.713 | 0 | 2.625 | 1.912 | 1.912 | open
129 | SS 35/10 kV Mezentsevo | 4+6,3 | 1.66 | 1.11 | 80 | 0.55 | 0 | 4.2 | 3.65 | 3.65 | open | 129 | SS 35/10 kV Mezentsevo | 4+6,3 | 0.271 | 1.931 | 1.11 | 80 | 0.821 | 0 | 4.2 | 3.379 | 3.379 | open
130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.008 | 0.198 | 0 |  | 0.198 | 0 | 1.68 | 1.482 | 1.482 | open
131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.55 | 0.39 | - | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0 | 0.55 | 0.39 |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 1.14 | 0.54 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | open | 132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 0.066 | 1.206 | 0.54 | 80 | 0.666 | 0 | 2.625 | 1.959 | 1.959 | open
133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.37 | 1.67 | 120 | -1.3 | 0 | 3.36 | 4.66 | 4.66 | open | 133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.009 | 0.379 | 1.67 | 120 | -1.291 | 0 | 3.36 | 4.651 | 4.651 | open
134 | SS 35/6 kV Pushkarskaya | 4+4 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | closed | 134 | SS 35/6 kV Pushkarskaya | 4+4 | 0 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | closed
135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open | 135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | open
136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.97 | 0.7 | 80 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open | 136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.188 | 1.158 | 0.7 | 80 | 0.458 | 0 | 2.625 | 2.167 | 2.167 | open
137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.31 | 1.5 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | open | 137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.626 | 2.936 | 1.5 | 120 | 1.436 | 0 | 2.625 | 1.189 | 1.189 | open
138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.3 | 0.33 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | open | 138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.025 | 0.325 | 0.33 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | open
139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.25 | 0 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | open | 139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.035 | 0.285 | 0 |  | 0.285 | 0 | 1.68 | 1.395 | 1.395 | open
140 | SS 35/10 kV SSK | 1,6+1,6 | 0.07 | 0 |  | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 140 | SS 35/10 kV SSK | 1,6+1,6 | 0.012 | 0.082 | 0 |  | 0.082 | 0 | 1.68 | 1.598 | 1.598 | open
141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.84 | 0.52 | 20 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.012 | 0.852 | 0.52 | 20 | 0.332 | 0 | 1.68 | 1.348 | 1.348 | open
142 | SS 35/10 kV Khomutovo | 4+4 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | open | 142 | SS 35/10 kV Khomutovo | 4+4 | 0 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | open
| Total: | [10 empty] | 2: Total:; 4: 147.308; 5: 700.295
| deficit | [8 empty] | -2.51 |  | 2: deficit; Min 12: -14.098
| proficit | [8 empty] | 618.475 |  | 2: proficit; Min 12: 477.483
* | Subsstations do not belong to the division, but IDGC of Center - Orelenergo provides technical requirements to connect customers.
SWG-10kV SS Mtsensk is in sublease, and SS Pischevaya is actually ownerless.