## Тамбовэнерго
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Current deficit/ proficit, MVA
|  |  |  | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | SS 110/35/6 Tambovskaya No.2 | 40 + 25 | 19.2 |  |  | 19.2 | 0 | 26.25 | 7.05 | 7.05 | opened
2 | SS 110/6 Tambovskaya No.3 | 2*25 | 18.44 |  |  | 18.44 | 0 | 26.25 | 7.81 | 7.81 | opened
3 | SS 110/6 Tambovskaya No.5 | 16 + 25 | 16.45 |  |  | 16.45 | 12.5 | 13.125 | -3.32 | -3.32 | closed
4 | SS 110/6 Tambovskaya No.7 | 2*25 | 21.18 |  |  | 21.18 | 0 | 26.25 | 5.07 | 5.07 | opened
5 | SS 110/35/6 Pigment | 2*63 | 33.98 | 27.68 | 80 | 6.3 | 0 | 66.15 | 59.85 | 59.85 | opened
6 | SS 110/6 Tambovskaya No.8 | 40+16 | 13.09 |  |  | 13.09 | 20 | 16.8 | 3.71 | 3.71 | opened
7 | SS 110/35/6 Malinovskaya | 2*40 | 12.73 | 4.75 | 120 | 7.98 | 0 | 42 | 34.02 | 34.02 | opened
8 | SS 110/35/10 Tambovskaya No.6 | 2*10 | 9.59 | 1.25 | 120 | 8.34 | 0 | 10.5 | 2.16 | 2.16 | opened
9 | SS 110/10 N.Lyadinskaya | 10+6,3 | 5.08 | 1.62 | 120 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | opened
10 | SS 110/35/10 Komsomolskaya | 2*10 | 8.81 | 4 | 80 | 4.81 | 0 | 10.5 | 5.69 | 5.69 | opened
11 | SS 110/10 М.Talinskaya | 10 | 0.68 | 0.52 | 24 hours | 0.16 | 0 | 10.5 | 10.34 | 10.34 | opened
12 | SS 110/35/10 Promyshlennaya | 2*40 | 25.61 | 10.2 | 120 | 15.41 | 0 | 42 | 26.59 | 26.59 | opened
13 | SS 110/35/10 Arzhenskaya | 2*10 | 5.46 | 3.92 | 80 | 1.54 | 0 | 10.5 | 8.96 | 8.96 | opened
14 | SS 110/10 Teleshovskaya | 2*2,5 | 0.45 |  |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
15 | SS 110/6 Oktyabrskaya | 2*25 | 7.83 |  |  | 7.83 | 0 | 26.25 | 18.42 | 18.42 | opened
16 | SS 110/10 Spasskaya | 2*6,3 | 2.43 |  |  | 2.43 | 0 | 6.615 | 4.185 | 4.185 | opened
17 | SS 110/35/10 Kuzminskaya | 16+10 | 7.41 | 5.02 | 45 | 2.39 | 0 | 10.5 | 8.11 | 8.11 | opened
18 | SS 110/35/10 Sampurskaya | 10+16 | 6.73 | 4.33 | 80 | 2.4 | 0 | 10.5 | 8.1 | 8.1 | opened
19 | SS 110/6 Leather plant | 2*10 | 1.37 |  |  | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened
20 | SS 110/35/6 Rasskazovskaya | 25+20 | 17.49 | 3.04 | 120 | 14.45 | 0 | 21 | 6.55 | 6.55 | opened
21 | SS 110/35/10 Volchkovskaya | 2*10 | 3.5 | 0.95 | 120 | 2.55 | 0 | 10.5 | 7.95 | 7.95 | opened
22 | SS 110/35/10 Staroyuryevskaya | 6,3+16 | 2.89 | 1.66 | 120 | 1.23 | 0 | 6.615 | 5.385 | 5.385 | opened
23 | SS 110/35/10 Khmelevskaya | 2*10 | 3.83 | 0.92 | 120 | 2.91 | 0 | 10.5 | 7.59 | 7.59 | opened
24 | SS 110/35/10 Khobotovskaya | 2*6,3 | 5.93 | 2.84 | 80 | 3.09 | 0 | 6.615 | 3.525 | 3.525 | opened
25 | SS 110/35/10 Nikiforovskaya | 10+16 | 5.07 | 2.81 | 120 | 2.26 | 0 | 10.5 | 8.24 | 8.24 | opened
26 | SS 110/10 N.Seslavinskaya | 2.5 | 0.41 | 0.47 | 24 hours | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
27 | SS 110/10 N. Arkhangelskaya | 2.5 | 0.39 | 0.19 | 24 hours | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
28 | SS 110/10 Ilovayskaya | 2*2,5 | 0.02 |  |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
29 | SS 110/35/10 Yuzhnaya | 16 | 9.72 | 8.51 | 24 hours | 1.21 | 0 | 16.8 | 15.59 | 15.59 | opened
30 | SS 110/27,5/6 Pervomayskaya | 2*31,5 | 23.36 | 9.45 | 120 | 13.91 | 0 | 33.075 | 19.165 | 19.165 | opened
31 | SS 110/35/10 Sosnovskaya | 2*16 | 7.19 | 6.6 | 80 | 0.59 | 0 | 16.8 | 16.21 | 16.21 | opened
32 | SS 110/35/10 Pichaevskaya | 2*10 | 3.68 | 4.19 | 80 | -0.51 | 0 | 10.5 | 11.01 | 11.01 | opened
33 | SS 110/35/10 Algasovskaya | 2*40 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened
34 | SS 110/35/6 Morshanskaya | 40+25 | 16.96 | 7.2005 | 120 | 9.7595 | 0 | 26.25 | 16.4905 | 16.4905 | opened
35 | SS 110/35/6 Kamvolnaya | 16+25 | 8.19 | 7.2 | 80 | 0.99 | 0 | 16.8 | 15.81 | 15.81 | opened
36 | SS 110/35/10 Grazhdanovskaya | 2*10 | 1.4 | 0.63 | 120 | 0.77 | 0 | 10.5 | 9.73 | 9.73 | opened
37 | SS 110/35/10 Nashchekinskaya | 2*10 | 5.21 | 2.05 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened
38 | SS 110/10 Shachinskaya | 2.5 | 0.61 | 0.054495 | 24 hours | 0.55551 | 0 | 2.625 | 2.0695 | 2.0695 | opened
39 | SS 110/35/10/6 Uvarovskaya | 16+16 | 9.88 | 9.027 | 45 | 0.85301 | 0 | 16.8 | 15.947 | 15.947 | opened
40 | SS 110/35/10 Muchkapskaya | 2*10 | 3.68 | 1.3519 | 120 | 2.3281 | 0 | 10.5 | 8.1719 | 8.1719 | opened
41 | SS 110/10 M.Alabushskaya | 2*2,5 | 0.88 | 0.66667 | 120 | 0.21333 | 0 | 2.625 | 2.4117 | 2.4117 | opened
42 | SS 110/35/10 M.Gorkovskaya | 10+16 | 1.94 | 1.2921 | 120 | 0.64795 | 0 | 10.5 | 9.8521 | 9.8521 | opened
43 | SS 110/10 Shpikulovskaya | 2*2,5 | 0.68 | 0.61404 | 120 | 0.065965 | 0 | 2.625 | 2.559 | 2.559 | opened
44 | SS 110/35/10 Zherdevskaya | 2*16 | 8.1 | 5.6533 | 80 | 2.4467 | 0 | 16.8 | 14.3533 | 14.3533 | opened
45 | SS 110/35/10 Rzhaksinskaya | 2*10 | 4.95 | 0.58824 | 120 | 4.3618 | 0 | 10.5 | 6.1382 | 6.1382 | opened
46 | SS 110/10 Bogdanovskaya | 2*2,5 | 0.86 | 0.42105 | 120 | 0.43895 | 0 | 2.625 | 2.1861 | 2.1861 | opened
47 | SS 110/35/10 Tokarevskaya | 2*25 | 8.34 | 6.0846 | 120 | 2.2554 | 0 | 26.25 | 23.9946 | 23.9946 | opened
48 | SS 110/35/10 Zveryaevskaya | 6,3+10 | 1.13 | 0.90918 | 120 | 0.22082 | 0 | 6.615 | 6.3942 | 6.3942 | opened
49 | SS 110/35/10 Mordovskaya | 2*10 | 3.44 | 1.8937 | 120 | 1.5463 | 0 | 10.5 | 8.9537 | 8.9537 | opened
50 | SS 110/35/10 Pavlovskaya | 10 | 1.58 | 1.56 | 24 hours | 0.02 | 0 | 10.5 | 10.48 | 10.48 | opened
51 | SS 110/35/10 Kirsanovskaya | 2*25 | 13.32 | 5.989 | 120 | 7.331 | 0 | 26.25 | 18.919 | 18.919 | opened
52 | SS 110/35/10 Inzhavinskaya | 2*16 | 8.38 | 3.41 | 120 | 4.97 | 0 | 16.8 | 11.83 | 11.83 | opened
53 | SS 110/35/10 Umyotskaya | 2*10 | 1.03 | 4.5 | 80 | -3.47 | 0 | 10.5 | 13.97 | 13.97 | opened
54 | SS 110/35/10 Kovylskaya | 2*10 | 1.27 | 1.347 | 120 | -0.077 | 0 | 10.5 | 10.577 | 10.577 | opened
55 | SS 110/10 Inokovskaya | 2.5 | 0.16 | 0.184 | 24 hours | -0.024 | 0 | 2.625 | 2.649 | 2.649 | opened
SS of 35 kv
56 | SS 35/6 Pervomayskaya | 2*2,5 | 1.64 |  |  | 1.64 | 0 | 2.625 | 0.985 | 0.985 | opened
57 | SS 35/10 Picherskaya | 2*2,5 | 0.68 |  |  | 0.68 | 0 | 2.625 | 1.945 | 1.945 | opened
58 | SS 35/10 Osinovskaya | 2*2,5 | 1.01 |  |  | 1.01 | 0 | 2.625 | 1.615 | 1.615 | opened
59 | SS 35/10 Koptevskaya | 2*2,5 | 0.18 |  |  | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
60 | SS 35/10 Sayukinskaya | 2,5+4 | 0.6 | 0.5 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
61 | SS 35/10 Zelyonaya-1 | 2*4 | 2.68 |  |  | 2.68 | 0 | 4.2 | 1.52 | 1.52 | opened
62 | SS 35/10 Pyatiletka | 2*4 | 0.29 |  |  | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
63 | SS 35/10 Yaroslavskaya | 2*2,5 | 0.81 |  |  | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened
64 | SS 35/10 Platonovskaya | 2*6,3 | 2.71 | 0.24 | 120 | 2.47 | 0 | 6.615 | 4.145 | 4.145 | opened
65 | SS 35/10 Znamenskaya | 2*4 | 3.53 | 1.54 | 120 | 1.99 | 0 | 4.2 | 2.21 | 2.21 | opened
66 | SS 35/10 Sukhotinskaya | 2.5 | 0.3 | 0 | 24 hours | 0.3 | 0 | 0 | -0.3 | -0.3 | closed
67 | SS 35/10 P.Marfinskaya | 2,5+1,6 | 0.91 |  |  | 0.91 | 0 | 1.68 | 0.77 | 0.77 | opened
68 | SS 35/10 Aleksandrovskaya | 1,6+2,5 | 0.45 | 0.29 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
69 | SS 35/10 Stepnaya | 2*4 | 1.82 | 1.7 | 80 | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
70 | SS 35/10 Ivanovskaya (ТPS) | 2*4 | 1.16 | 0.97 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened
71 | SS 35/10 Verkhotsenskaya | 2,5+1,6 | 0.39 | 0.47 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened
72 | SS 35/10 Gorelskaya | 4+6,3 | 2.09 | 1.71 | 80 | 0.38 | 0 | 4.2 | 3.82 | 3.82 | opened
73 | SS 35/10 B.Dvoynyovskaya | 2*2,5 | 0.72 |  |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
74 | SS 35/10 Avangardskaya | 2*2,5 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened
75 | SS 35/10 Suravskaya | 1,6+2,5 | 0.54 | 0.45 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
76 | SS 35/10 Seleznzyovskaya | 2*4 | 3.78 |  |  | 3.78 | 0 | 4.2 | 0.42 | 0.42 | opened
77 | SS 35/10 Chernyanskaya | 1,6+2,5 | 1.77 | 0.68 | 80 | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened
78 | SS 35/10 Viktorskaya | 2.5 | 0.62 |  |  | 0.62 | 0 | 0 | -0.62 | -0.62 | closed
79 | SS 35/10 Novoseltsevskaya | 2*1,6 | 0.7 |  |  | 0.7 | 0 | 1.68 | 0.98 | 0.98 | opened
80 | SS 35/10 Avdeevskaya | 2*2,5 | 0.83 |  |  | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened
81 | SS 35/10 Tatanovskaya | 2*2,5 | 2.49 |  |  | 2.49 | 0 | 2.625 | 0.135 | 0.135 | opened
82 | SS 35/10 Timiryazevskaya | 2,5+2,5+4 | 3.35 | 0.63 | 60 | 2.72 | 0 | 5.25 | 2.53 | 2.53 | opened
83 | SS 35/10 P.Prigorodnaya | 2*6,3 | 5.07 |  |  | 5.07 | 0 | 6.615 | 1.545 | 1.545 | opened
84 | SS 35/10 Bokinskaya | 2*6,3 | 2.19 | 0.92 | 30 | 1.27 | 0 | 6.615 | 5.345 | 5.345 | opened
85 | SS 35/10 Stolovskaya | 4 | 0.64 | 0.52 | 24 hours | 0.12 | 0 | 4.2 | 4.08 | 4.08 | opened
86 | SS 35/10 Tulinovskaya | 2*2,5 | 1.41 |  |  | 1.41 | 0 | 2.625 | 1.215 | 1.215 | opened
87 | SS 35/6 Macaroni factory | 1.6 | 0.16 |  |  | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
88 | SS 35/10 Serebryakovskaya | 2*1,6 | 1.27 |  |  | 1.27 | 0 | 1.68 | 0.41 | 0.41 | opened
89 | SS 35/10 B.Doroga | 2*1,6 | 0.39 | 0.34 | 60 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened
90 | SS 35/10 B.Izberdeevskaya | 2*2,5 | 0.64 |  |  | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
91 | SS 35/10 Vishnevskaya | 2*2,5 | 0.51 | 0.26 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened
92 | SS 35/10 Vyrubovskaya | 2*2,5 | 0.4 | 0.32 | 50 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
93 | SS 35/10 Glazkovskaya | 2*4 | 0.97 | 0.71 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened
94 | SS 35/10 Dmitirievskaya | 2*2,5 | 0.08 |  |  | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
95 | SS 35/6 Donskaya | 6,3+10 | 4.59 | 3.65 | 24 hours | 0.94 | 0 | 6.615 | 5.675 | 5.675 | opened
96 | SS 35/10 Druzhba | 2.5 | 0.16 | 0.16 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
97 | SS 35/10 Ekaterininskaya | 2*2,5 | 0.2 | 0.23 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
98 | SS 35/10 Zhidilovskaya | 2,5+1,6 | 0.66 | 0.25 | 120 | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened
99 | SS 35/10 Izosimovskaya | 6,3+2,5 | 1.58 | 1.08 | 80 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
100 | SS 35/10 KIM | 2,5+4 | 0.6 | 0.74 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened
101 | SS 35/10 Klenskaya | 2*2,5 | 0.24 | 0.22 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
102 | SS 35/10 Kozmodemyanovskaya | 2*2,5 | 0.57 | 0.6 | 120 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
103 | SS 35/10 Komintern | 2*2,5 | 0.42 | 0.22 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
104 | SS 35/10 Kochetovskaya | 6.3 | 0.32 | 0.2 | 24 hours | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened
105 | SS 35/10 Nov.Vasilyevskaya | 2*2,5 | 0.15 | 0.14 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
106 | SS 35/10 Nov.Tarbeevskaya | 2.5 | 1.06 | 0.66 | 24 hours | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
107 | SS 35/10 Nov.Yuryevskaya | 2*1,6 | 0.39 | 0.28 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
108 | SS 35/10 Petrovskaya | 2*4 | 2.9 | 1.2 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened
109 | SS 35/10 Prigorodnaya | 2*5,6 | 0.9 | 0.62 | 120 | 0.28 | 0 | 5.88 | 5.6 | 5.6 | opened
110 | SS 35/6 Progress | 2*10 | 11.35 |  |  | 11.35 | 0 | 10.5 | -0.85 | -0.85 | closed
111 | SS 35/10 Raninskaya | 1.6 | 0.27 | 0.32 | 24 hours | -0.05 | 0 | 1.68 | 1.73 | 1.73 | opened
112 | SS 35/10 Rakhmaninskaya | 2*1,6 | 0.21 |  |  | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
113 | SS 35/10 Saburovskaya | 2*2,5 | 1.65 |  |  | 1.65 | 0 | 2.625 | 0.975 | 0.975 | opened
114 | SS 35/10 Sestryonskaya | 1.6 | 0.11 |  |  | 0.11 | 0 | 0 | -0.11 | -0.11 | closed
115 | SS 35/10 Sitovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
116 | SS 35/10 Skobelevskaya | 1.6 | 0.27 | 0.24 | 24 hours | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
117 | SS 35/10 Ustyinskaya | 2.5 | 1.25 | 1.06 | 24 hours | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
118 | SS 35/10 Yurlovskaya | 2*2,5 | 0.54 |  |  | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened
119 | SS 35/10 Yablonovetskaya | 2*2,5 | 0.63 |  |  | 0.63 | 0 | 2.625 | 1.995 | 1.995 | opened
120 | SS 35/10 Agroprom | 2*4 | 1.22 |  |  | 1.22 | 0 | 4.2 | 2.98 | 2.98 | opened
121 | SS 35/10 Alekseevskaya | 1,6+2,5 | 0.28 |  |  | 0.28 | 0 | 1.68 | 1.4 | 1.4 | opened
122 | SS 35/10 Vanovskaya | 2*2,5 | 0.1 | 0.07 | 80 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
123 | SS 35/10 Vyazhlinskaya | 1.8 | 0.72 | 0.81 | 24 hours | -0.09 | 0 | 1.89 | 1.98 | 1.98 | opened
124 | SS 35/10 Zarechnaya | 2*2,5 | 1.25 |  |  | 1.25 | 0 | 2.625 | 1.375 | 1.375 | opened
125 | SS 35/10 Kryukovskaya | 2*2,5 | 0.55 | 0.6593 | 120 | -0.1093 | 0 | 2.625 | 2.7343 | 2.7343 | opened
126 | SS 35/6 Korshunovskaya | 2*2,5 | 0.43 |  |  | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
127 | SS 35/6 Lugovaya | 4 | 0.43 | 0.94977 | 24 hours | -0.51977 | 0 | 4.2 | 4.7198 | 4.7198 | opened
128 | SS 35/10 Lyubvinskaya | 2*2,5 | 0.11 | 0.1467 | 120 | -0.036704 | 0 | 2.625 | 2.6617 | 2.6617 | opened
129 | SS 35/10 Morshanskaya | 2*4 | 2.66 |  |  | 2.66 | 0 | 4.2 | 1.54 | 1.54 | opened
130 | SS 35/10 Piterskaya | 2.5 | 1.05 | 0.93 | 24 hours | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
131 | SS 35/10 Rakshinskaya | 2*4 | 1.95 | 1.6137 | 80 | 0.33626 | 0 | 4.2 | 3.8637 | 3.8637 | opened
132 | SS 35/10 Rybinskaya | 2*2,5 | 0.92 | 1.0536 | 80 | -0.13357 | 0 | 2.625 | 2.7586 | 2.7586 | opened
133 | SS 35/10 Serpovskaya | 2*2,5 | 0.84 | 0.7 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
134 | SS 35/10 St.Tomnikovskaya | 1 | 0.1 | 0.092555 | 24 hours | 0.007445 | 0 | 1.05 | 1.0426 | 1.0426 | opened
135 | SS 35/10 Chernitovskaya | 2.5 | 0.54 | 0.39963 | 24 hours | 0.14037 | 0 | 2.625 | 2.4846 | 2.4846 | opened
136 | SS 35/10 Bondarskaya | 2*2,5 | 1.53 | 0.93 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
137 | SS 35/10 Vernadovskaya | 2,5+1,6 | 0.5 | 0.53457 | 80 | -0.03457 | 0 | 1.68 | 1.7146 | 1.7146 | opened
138 | SS 35/10 Gagarinskaya | 2,5+1,6 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened
139 | SS 35/10 Egorovskaya | 2,5+3,2 | 0.44 | 0.71276 | 120 | -0.27276 | 0 | 2.625 | 2.8978 | 2.8978 | opened
140 | SS 35/10 Kershinskaya | 1,6+2,5 | 0.24 |  |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
141 | SS 35/10 Kurovshchinskaya | 2*1,6 | 0.39 | 0.054495 | 120 | 0.3355 | 0 | 1.68 | 1.3445 | 1.3445 | opened
142 | SS 35/10 Lipovskaya | 2.5 | 0.25 | 0.26988 | 24 hours | -0.01988 | 0 | 2.625 | 2.6449 | 2.6449 | opened
143 | SS 35/10 Lomovisskaya | 3,2+2,5 | 0.13 | 0.11 | 120 | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
144 | SS 35/10 Mitropolskaya | 2.5 | 0.2 | 0.28 | 24 hours | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened
145 | SS 35/10 P.Uglovskaya | 1.6 | 0.36 | 0.35292 | 24 hours | 0.00708 | 0 | 1.68 | 1.6729 | 1.6729 | opened
146 | SS 35/10 Rudovskaya | 2*2,5 | 0.29 |  |  | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
147 | SS 35/10 V.Yaroslavskaya | 2.5 | 0.31 | 0.23 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
148 | SS 35/10 Degtyanskaya | 2.5 | 1.16 | 0.9 | 24 hours | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened
149 | SS 35/10 Zelenaya-2 | 1.6 | 0.27 | 0.17992 | 24 hours | 0.09008 | 0 | 1.68 | 1.5899 | 1.5899 | opened
150 | SS 35/10 Kulevatovskaya | 2*4 | 1.99 | 1.81 | 80 | 0.18 | 0 | 4.2 | 4.02 | 4.02 | opened
151 | SS 35/10 Lamskaya | 4+2,5 | 0.46 | 0.20362 | 120 | 0.25638 | 0 | 2.625 | 2.3686 | 2.3686 | opened
152 | SS 35/10 Gryaznovskaya | 2*2,5 | 0.07 |  |  | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
153 | SS 35/10 Otyasskaya | 2*2,5 | 0.51 | 0.39963 | 120 | 0.11037 | 0 | 2.625 | 2.5146 | 2.5146 | opened
154 | SS 35/10 P.Vasilyevskaya | 1.6 | 0.09 | 0.1903 | 24 hours | -0.1003 | 0 | 1.68 | 1.7803 | 1.7803 | opened
155 | SS 35/10 Podlesnaya | 2*2,5 | 0.45 | 0.41935 | 120 | 0.030648 | 0 | 2.625 | 2.5944 | 2.5944 | opened
156 | SS 35/10 Tr.Roslyayskaya (Moscow region power grid company) | 2*2,5 | 0.33 | 0.38146 | 120 | -0.051465 | 0 | 2.625 | 2.6765 | 2.6765 | opened
157 | SS 35/10 Zherdevskaya | 10 | 2.75 | 2.25 | 24 hours | 0.5 | 0 | 10.5 | 10 | 10 | opened
158 | SS 35/10 Sukmanovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
159 | SS 35/10 Tugolukovskaya | 2,5+4 | 0.49 | 0.29 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
160 | SS 35/10 Artemovskaya | 2*2,5 | 0.54 | 0.35 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
161 | SS 35/10 RSKhO | 2,5+4 | 1.24 | 1.16 | 80 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
162 | SS 35/10 Maksimovskaya | 2*1,6 | 0.16 | 0.18 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
163 | SS 35/10 Burnakskaya | 5,6+6,3 | 3.44 |  |  | 3.44 | 0 | 5.88 | 2.44 | 2.44 | opened
164 | SS 35/10 Poletaevskaya | 2*4 | 0.29 | 0.19 | 120 | 0.1 | 2.18 | 4.2 | 1.92 | 1.92 | opened
165 | SS 35/10 T.Roslyayskaya (Housing and Utilities System) | 4+2,5 | 0.71 |  |  | 0.71 | 0 | 4.2 | 3.49 | 3.49 | opened
166 | SS 35/10 Pioner | 1,6+2,5 | 1.16 | 0.72 | 60 | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened
167 | SS 35/10 Lvovskaya | 2*2,5 | 0.6 | 0.47 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
168 | SS 35/10 Nadezhdinskaya | 1.6 | 0.39 | 0.28 | 24 hours | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
169 | SS 35/10 Kuleshovskaya | 2.5 | 0.42 | 0.26 | 24 hours | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
170 | SS 35/10 Chernyaevskaya | 4+2,5 | 1.51 |  |  | 1.51 | 0 | 2.625 | 1.115 | 1.115 | opened
171 | SS 35/10 Ivanovskaya (Housing and Utilities System) | 2*2,5 | 0.62 |  |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
172 | SS 35/10 Shulginskaya | 2*4 | 0.77 | 0.02 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened
173 | SS 35/10 Lavrovskaya | 2*2,5 | 0.13 |  |  | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
174 | SS 35/10 N.Sergievskaya | 3.2 | 0.58 | 0.49 | 24 hours | 0.09 | 0 | 3.36 | 3.27 | 3.27 | opened
175 | SS 35/10 Kamenskaya | 2*2,5 | 0.44 |  |  | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened
176 | SS 35/10 Protasovskaya | 4+2,5 | 0.38 |  |  | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
177 | SS 35/10 Chakinskaya | 4 | 0.72 |  |  | 0.72 | 0 | 0 | -0.72 | -0.72 | closed
178 | SS 35/10 Lukinskaya | 2.5 | 0.26 | 0.22 | 24 hours | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
179 | SS 35/10 Zolotovskaya | 2.5 | 0.38 | 0.37 | 24 hours | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
180 | SS 35/10 Mozdokskaya | 2.5 | 0.2 |  |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed
181 | SS 35/10 Oblovskaya | 2*2,5 | 0.37 | 0.65 | 120 | -0.28 | 0 | 2.625 | 2.905 | 2.905 | opened
182 | SS 35/10 V.Vershinskaya | 2,5+4 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
183 | SS 35/10 Luchevskaya | 2,5+1,6 | 0.13 |  |  | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
184 | SS 35/10 Olshanskaya | 4+2,5 | 1.28 | 0.32 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
185 | SS 35/10 Pavlodarskaya | 2.5 | 0.41 | 0.1 | 24 hours | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
186 | SS 35/10 Berezovskaya | 2*2,5 | 0.21 |  |  | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
187 | SS 35/10 K.Zvezdinskaya | 2*1,6 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
188 | SS 35/10 Prudkovskaya | 1,6+2,5 | 0.3 |  |  | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
189 | SS 35/10 Shapkinskaya | 2*4 | 0.51 |  |  | 0.51 | 0 | 4.2 | 3.69 | 3.69 | opened
190 | SS 35/10 Maryinskaya | 2*1,6 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
191 | SS 35/10 Irskaya | 1,6+2,5 | 0.34 | 0.345 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | opened
192 | SS 35/10 Zavodskaya | 2*4 | 0.73 | 1.25 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | opened
193 | SS 35/10 Kalaisskaya | 2.5 | 0.5 | 0.58 | 24 hours | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened
194 | SS 35/10 Sokolovskaya | 2*2,5 | 1.71 | 1.02 | 80 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened
195 | SS 35/10 Veterinarnaya | 2.5 | 0.13 | 0.13 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
196 | SS 35/10 Glukhovskaya | 2.5 | 0.08 | 0.09 | 24 hours | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened
197 | SS 35/10 Orzhevskaya | 2.5 | 0.55 | 0.47 | 24 hours | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
198 | SS 35/10 Umyotskaya | 2*4 | 1.64 | 1.54 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
199 | SS 35/10 Gavrilovskaya | 2*4 | 1.37 | 0.996 | 120 | 0.374 | 0 | 4.2 | 3.826 | 3.826 | opened
200 | SS 35/10 Peresypkinskaya | 2*2,5 | 0.73 | 0.76 | 80 | -0.03 | 0 | 2.625 | 2.655 | 2.655 | opened
201 | SS 35/10 Annenskaya | 2*2,5 | 1.18 | 0.806 | 80 | 0.374 | 0 | 2.625 | 2.251 | 2.251 | opened
202 | SS 35/10 Filatovskaya | 2*2,5 | 0.5 | 0.33 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
203 | SS 35/10 Nikitinskaya | 2,5+1,6 | 0.21 | 0.135 | 120 | 0.075 | 0 | 1.68 | 1.605 | 1.605 | opened
204 | SS 35/10 Balykleyskaya | 2*2,5 | 1.28 | 0.414 | 120 | 0.866 | 0 | 2.625 | 1.759 | 1.759 | opened
205 | SS 35/10 Karavainskaya | 2*1,6 | 0.54 | 0.548 | 80 | -0.008 | 0 | 1.68 | 1.688 | 1.688 | opened
206 | SS 35/10 Poultry plant | 2*2,5 |  |  |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
207 | SS 35/10 Pavlovskaya | 3.2 | 0.28 | 0.28 | 24 hours | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
| Total: | 2441.2 | 544.36
| deficit | [8 empty] | -6.12
| proficit | [8 empty] | 949.557