## Курск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications | Expected load at main substation | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | MVA | Мin. | [11 empty] | МVА | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.68 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.62 | 1.01 | opened | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.006 | 1.686 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.614 | 1.004 | opened
| Nom. capacity MV, MVA | 6.3 | 1.29 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.01 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.006 | 1.296 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.004
| Nom. capacity MV, MVA | 6.3 | 0.39 | 4 | 24 hours | 4 | 0 | 4 | 3.61 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.39 | 4 | 24 hours | 4 | 0 | 4 | 3.61
2 | SS 110/10 Beketovo | 1*6,3 | 0.3 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.85 | 1.85 | opened | 2 | SS 110/10 Beketovo | 1*6,3 | 0.1711 | 0.4711 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.6789 | 1.6789 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.2 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.1 | 0.3 | opened | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.077 | 2.277 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.023 | 0.232 | opened
| Nom. capacity MV, MVA | 6.3 | 0.4 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.8 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.009 | 0.409 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.791
| Nom. capacity LV, MVA | 6.3 | 1.8 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.3 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.068 | 1.868 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.232
4 | SS 110/10 Voskhod | 1*10,0 | 0.2 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.3 | 2.3 | opened | 4 | SS 110/10 Voskhod | 1*10,0 | 0.0153 | 0.2153 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.2847 | 2.2847 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.57 | 6 | 24 hours | 6 | 0 | 6 | 5.43 | 1.73 | opened | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.015 | 0.585 | 6 | 24 hours | 6 | 0 | 6 | 5.415 | 1.715 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.57 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.73 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.015 | 0.585 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.715
6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.45 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.71 | 0.62 | opened | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.0075 | 0.4575 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.7025 | 0.62 | opened
| Nom. capacity MV, MVA | 10 | 0.41 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 4.09 |  |  |  | Nom. capacity MV, MVA | 10 | 0.0075 | 0.4175 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 4.0825
| Nom. capacity LV, MVA | 10 | 0.04 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.62 |  |  |  | Nom. capacity LV, MVA | 10 | 0 | 0.04 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.62
7 | SS 110/10 Zabelye | 1*2,5 | 0.38 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.77 | 1.77 | opened | 7 | SS 110/10 Zabelye | 1*2,5 | 0.003 | 0.383 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.767 | 1.767 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.16 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened | 8 | SS 110/10 Ivnitsa | 1*6,3 | 0 | 0.16 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened
9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.95 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 4.18 | 1.12 | opened | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.464 | 1.414 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.716 | 0.656 | opened
| Nom. capacity MV, MVA | 10 | 0.54 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 3.06 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.54 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 3.06
| Nom. capacity LV, MVA | 10 | 0.41 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1.12 |  |  |  | Nom. capacity LV, MVA | 10 | 0.464 | 0.874 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.656
10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.73 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.48 | 0.48 | opened | 10 | SS 110/10 Malaya Loknya | 1*10,0 | 0.008 | 0.738 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.472 | 0.472 | opened
11 | SS 110/35/10 Maritsa | 1*6,3 | 0.71 | 6.24 | 24 hours | 6.24 | 0 | 6.24 | 5.53 | 1.21 | opened | 11 | SS 110/35/10 Maritsa | 1*6,3 | 0.01 | 0.72 | 6.24 | 24 hours | 6.24 | 0 | 6.24 | 5.52 | 1.2 | opened
| Nom. capacity MV, MVA | 6.3 |  | 4.32 | 24 hours | 4.32 | 0 | 4.32 | 4.32 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0 | 4.32 | 24 hours | 4.32 | 0 | 4.32 | 4.32
| Nom. capacity LV, MVA | 6.3 | 0.71 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 1.21 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.01 | 0.72 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 1.2
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 1.21 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 4.68 | 1.21 | opened | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0 | 1.21 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 4.68 | 1.21 | opened
| Nom. capacity MV, MVA | 6.3 | 0.27 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.47 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.27 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.47
| Nom. capacity LV, MVA | 6.3 | 0.94 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.21 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.94 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.21
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.303 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.097 | 1.097 | opened
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened | 14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.75 | 9.85 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | -3.21 | -3.21 | closed
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 2.94 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.56 | 0.45 | opened | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 0.331 | 3.271 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.229 | 0.446 | opened
| Nom. capacity MV, MVA | 10 | 2.29 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 4.11 |  |  |  | Nom. capacity MV, MVA | 10 | 0.327 | 2.617 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.783
| Nom. capacity LV, MVA | 10 | 0.65 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.45 |  |  |  | Nom. capacity LV, MVA | 10 | 0.004 | 0.654 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.446
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.09 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.71 | 0.71 | opened | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.009 | 0.099 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.701 | 0.701 | opened
17 | SS 35/10 Agronom | 1 х 1,8 | 0.5 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.06 | 0.06 | opened | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.015 | 0.515 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.045 | 0.045 | opened
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened | 18 | SS 35/10 Akimovka | 1 х 2,5 | 0 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.41 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.02 | 1.02 | opened | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0 | 0.41 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.02 | 1.02 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 1.17 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.17 | 0.17 | opened | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.02 | 1.19 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.15 | 0.15 | opened
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.001 | 0.701 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.259 | 0.259 | opened
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.88 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.95 | 1.95 | opened | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0 | 0.88 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.95 | 1.95 | opened
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.21 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.43 | 0.43 | opened | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.0065 | 0.2165 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.4235 | 0.4235 | opened
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.0577 | 0.4077 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.0223 | 1.0223 | opened
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.0277 | 0.6277 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.1323 | 1.1323 | opened
27 | SS 35/10 Biryukovka | 1х1,6 | 0.16 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.4 | 0.4 | opened | 27 | SS 35/10 Biryukovka | 1х1,6 | 0 | 0.16 | 0.56 | 24 hours | 0.56 | 0 | 0.56 | 0.4 | 0.4 | opened
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.19 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.48 | 0.48 | opened | 28 | SS 35/10 Bobrovka | 1 х 1,6 | 0 | 0.19 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.48 | 0.48 | opened
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.37 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.39 | 0.39 | opened | 29 | SS 35/10 Bobrovo | 1 х 2,5 | 0 | 0.37 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.39 | 0.39 | opened
30 | SS 35/10 Budki | 1 х 1,0 | 0.12 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.52 | 0.52 | opened | 30 | SS 35/10 Budki | 1 х 1,0 | 0 | 0.12 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.52 | 0.52 | opened
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.35 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.25 | 1.25 | opened | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0 | 0.35 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.25 | 1.25 | opened
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.24 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.19 | 1.19 | opened | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.018 | 0.258 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.172 | 1.172 | opened
34 | SS 35/10 Bykovo | 1 х 4,0 | 0.76 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.67 | 0.67 | opened | 34 | SS 35/10 Bykovo | 1 х 4,0 | 0.006 | 0.766 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.664 | 0.664 | opened
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.097 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.053 | 2.053 | opened | 35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0 | 0.097 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.053 | 2.053 | opened
36 | SS 35/10 Vanino | 1 х 2,5 | 0.36 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.44 | 0.44 | opened | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.021 | 0.381 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.419 | 0.419 | opened
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.48 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.57 | 0.57 | opened | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.006 | 0.486 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.564 | 0.564 | opened
38 | SS 35/10 Water storage | 1 х 4,0 | 0.09 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 2.63 | 2.63 | opened | 38 | SS 35/10 Water storage | 1 х 4,0 | 3.509 | 3.599 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | -0.879 | -0.879 | closed
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened | 39 | SS 35/10 Volokonsk | 1 х 2,5 | 0 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.24 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.66 | 0.66 | opened | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0 | 0.24 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.66 | 0.66 | opened
41 | SS 35/10 Voronok | 1 х 4,0 | 1 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.1 | 1.1 | opened | 41 | SS 35/10 Voronok | 1 х 4,0 | 0 | 1 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.1 | 1.1 | opened
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.475 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.675 | 1.675 | opened | 42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.013 | 0.488 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.662 | 1.662 | opened
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.005 | 0.215 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.585 | 1.585 | opened
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.13 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.37 | 1.37 | opened | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.021 | 0.151 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.349 | 1.349 | opened
45 | SS 35/10 Glazovo | 1 х 2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 45 | SS 35/10 Glazovo | 1 х 2,5 | 0 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.37 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.03 | 1.03 | opened | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.019 | 0.389 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.011 | 1.011 | opened
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened | 47 | SS 35/10 Gordeevka | 1 х 1,6 | 0 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.51 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.25 | 0.25 | opened | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.029 | 0.539 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.221 | 0.221 | opened
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.36 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.74 | 0.74 | opened | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.0268 | 0.3868 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.7132 | 0.7132 | opened
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.47 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.96 | 0.96 | opened | 50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0 | 0.47 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.96 | 0.96 | opened
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.016 | 0.406 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.024 | 1.024 | opened
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.23 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.62 | 2.62 | opened | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0 | 0.23 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.62 | 2.62 | opened
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.28 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.66 | 0.66 | opened | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.006 | 0.286 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.654 | 0.654 | opened
54 | SS 35/10 Daryino | 1 х 2,5 | 0.24 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.56 | 1.56 | opened | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.0151 | 0.2551 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.5449 | 1.5449 | opened
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.53 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.27 | 0.27 | opened | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.021 | 0.551 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.249 | 0.249 | opened
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.36 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.71 | 0.71 | opened | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.073 | 0.433 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.637 | 0.637 | opened
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.3 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.55 | 0.55 | opened | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.023 | 0.323 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.527 | 0.527 | opened
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.054 | 0.324 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.826 | 1.826 | opened
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.001 | 0.601 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.239 | 0.239 | opened
60 | SS 35/10 Znamenka | 1 х 1,8 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened | 60 | SS 35/10 Znamenka | 1 х 1,8 | 0 | 0.37 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.78 | 1.78 | opened
61 | SS 35/10 Iskra | 1 х 2,5 | 0.35 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.23 | 0.23 | opened | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.009 | 0.359 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.221 | 0.221 | opened
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.35 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.45 | 0.45 | opened | 62 | SS 35/10 Kazanka | 1 х 4,0 | 0 | 0.35 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.45 | 0.45 | opened
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.13 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.67 | 1.67 | opened | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.002 | 0.132 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.668 | 1.668 | opened
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.4 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.24 | 0.24 | opened | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.001 | 0.401 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.239 | 0.239 | opened
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.48 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.26 | 0.26 | opened | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.207 | 0.687 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.053 | 0.053 | opened
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.95 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.58 | 0.58 | opened | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.196 | 1.146 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.384 | 0.384 | opened
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.36 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.48 | 0.48 | opened | 67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0 | 0.36 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.48 | 0.48 | opened
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.3 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 1.12 | 1.12 | opened | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0 | 0.3 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 1.12 | 1.12 | opened
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.4 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.36 | 0.36 | opened | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.0124 | 0.4124 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.3476 | 0.3476 | opened
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.106 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.324 | 1.324 | opened | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0 | 0.106 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.324 | 1.324 | opened
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.59 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.14 | 0.14 | opened | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.001 | 0.591 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.139 | 0.139 | opened
72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.94 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.15 | 0.15 | opened | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.006 | 0.946 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.144 | 0.144 | opened
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.6 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.69 | 0.69 | opened | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.001 | 0.601 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.689 | 0.689 | opened
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.38 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.77 | 0.77 | opened | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0 | 0.38 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.77 | 0.77 | opened
75 | SS 35/10 lyubimovka-1 | 1 х 3,2 | 0.1 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.86 | 0.86 | opened | 75 | SS 35/10 lyubimovka-1 | 1 х 3,2 | 0 | 0.1 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.86 | 0.86 | opened
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.62 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.48 | 0.48 | opened | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.105 | 0.725 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.375 | 0.375 | opened
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.61 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.67 | 0.67 | opened | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.001 | 0.611 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.669 | 0.669 | opened
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.24 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.95 | 0.95 | opened | 78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0 | 0.24 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.95 | 0.95 | opened
79 | SS 35/10 Markovo | 1 х 2,5 | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 | opened | 79 | SS 35/10 Markovo | 1 х 2,5 | 0 | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 | opened
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 1.01 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 0.32 | 0.32 | opened | 80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.005 | 1.015 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 0.315 | 0.315 | opened
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.58 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.57 | 1.57 | opened | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.024 | 0.604 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.546 | 1.546 | opened
82 | SS 35/10 Mokva | 1 х 4,0 | 0.59 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.56 | 1.56 | opened | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.016 | 0.606 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.544 | 1.544 | opened
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.006 | 0.206 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.894 | 0.894 | opened
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.18 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.72 | 0.72 | opened | 84 | SS 35/10 Molotychi | 1 х 2,5 | 0 | 0.18 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.72 | 0.72 | opened
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.015 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.055 | 1.055 | opened | 85 | SS 35/10 Mochaki | 1 х 2,5 | 0 | 0.015 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.055 | 1.055 | opened
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.107 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.193 | 4.193 | opened | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0 | 0.107 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.193 | 4.193 | opened
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.008 | 0.508 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.642 | 1.642 | opened
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.07 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.33 | 1.33 | opened | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0 | 0.07 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.33 | 1.33 | opened
89 | SS 35/10 Niva | 1 х 2,5 | 0.26 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.3 | 1.3 | opened | 89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.275 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.285 | 1.285 | opened
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.75 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.22 | 0.22 | opened | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0 | 0.75 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.22 | 0.22 | opened
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.36 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.28 | 0.28 | opened | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.0075 | 0.3675 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.2725 | 0.2725 | opened
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 2.19 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 0.78 | 0.78 | opened | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.3976 | 2.5876 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 0.3824 | 0.3824 | opened
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.2 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 2.12 | 2.12 | opened | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.5 | 0.7 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.62 | 1.62 | opened
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.13 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.27 | 1.27 | opened | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0 | 0.13 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.27 | 1.27 | opened
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.33 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.07 | 1.07 | opened | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0 | 0.33 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.07 | 1.07 | opened
96 | SS 35/10 Petrovo | 1 х 6,3 | 0.74 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.41 | 1.41 | opened | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0 | 0.74 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.41 | 1.41 | opened
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.02 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.72 | 0.72 | opened | 97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0 | 0.02 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.72 | 0.72 | opened
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.208 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.942 | 1.942 | opened | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0 | 0.208 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.942 | 1.942 | opened
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.43 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.72 | 1.72 | opened | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0 | 0.43 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.72 | 1.72 | opened
100 | SS 35/10 Pristen | 1 х 4,0 | 1.1 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 2.2 | 2.2 | opened | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.034 | 1.134 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 2.166 | 2.166 | opened
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.2 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.54 | 0.54 | opened | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.024 | 0.224 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.516 | 0.516 | opened
102 | SS 35/10 Reut | 1 х 2,5 | 0.15 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.71 | 0.71 | opened | 102 | SS 35/10 Reut | 1 х 2,5 | 0.11 | 0.26 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.6 | 0.6 | opened
103 | SS 35/10 Rovenka | 1 х 1,6 | 0.068 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.362 | 1.362 | opened | 103 | SS 35/10 Rovenka | 1 х 1,6 | 0 | 0.068 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.362 | 1.362 | opened
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.09 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.61 | 0.61 | opened | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.016 | 0.106 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.594 | 0.594 | opened
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.318 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.982 | 1.982 | opened | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0 | 0.318 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.982 | 1.982 | opened
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.33 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.98 | 0.98 | opened | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.653 | 0.983 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.327 | 0.327 | opened
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.289 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.141 | 1.141 | opened | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0 | 0.289 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.141 | 1.141 | opened
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.34 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.6 | 0.6 | opened | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.022 | 0.362 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.578 | 0.578 | opened
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.51 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.64 | 0.64 | opened | 109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.006 | 0.516 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.634 | 0.634 | opened
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.16 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 1.09 | 1.09 | opened | 110 | SS 35/10 Sazanovka | 1 х 2,5 | 0 | 0.16 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 1.09 | 1.09 | opened
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.18 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.52 | 2.52 | opened | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0 | 0.18 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.52 | 2.52 | opened
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.346 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.084 | 1.084 | opened | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.054 | 0.4 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.03 | 1.03 | opened
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.048 | 0.648 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.112 | 1.112 | opened
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened | 114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.069 | 0.309 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.791 | 0.791 | opened
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.15 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.25 | 1.25 | opened | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0 | 0.15 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.25 | 1.25 | opened
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.41 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.89 | 0.89 | opened | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.0165 | 0.4265 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.8735 | 0.8735 | opened
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.23 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 1.11 | 1.11 | opened | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.005 | 0.235 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 1.105 | 1.105 | opened
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.47 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.24 | 0.24 | opened | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.002 | 0.472 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.238 | 0.238 | opened
119 | SS 35/10 Telmana | 1 х 2,5 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.409 | 0.989 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.161 | 0.161 | opened
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.37 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.06 | 1.06 | opened | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.057 | 0.427 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.003 | 1.003 | opened
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 | opened | 121 | SS 35/10 Fateevka | 1 х 2,5 | 0 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 | opened
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.15 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.57 | 1.57 | opened | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0 | 0.15 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.57 | 1.57 | opened
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0 | 0.24 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.86 | 0.86 | opened
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.11 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.74 | 0.74 | opened | 124 | SS 35/10 Chemerki | 1 х 1,6 | 0 | 0.11 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.74 | 0.74 | opened
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.003 | 0.283 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.147 | 1.147 | opened
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.23 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.2 | 1.2 | opened | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0 | 0.23 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.2 | 1.2 | opened
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.5 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.97 | 0.97 | opened | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.018 | 0.518 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.952 | 0.952 | opened
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.14 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.71 | 0.71 | opened | 128 | SS 35/10 Shuklino | 1 х 2,5 | 0 | 0.14 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.71 | 0.71 | opened
129 | SS 35/10 Elevator | 1х6,3 | 0.23 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.37 | 0.37 | opened | 129 | SS 35/10 Elevator | 1х6,3 | 0.025 | 0.255 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.345 | 0.345 | opened
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.2 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.44 | 0.44 | opened | 130 | SS 35/10 Yankovo | 1 х 1,6 | 0.003 | 0.203 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.437 | 0.437 | opened
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened | 131 | SS 35/10 Yasenki | 1 х 2,5 | 0.008 | 0.488 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.662 | 1.662 | opened
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
132 | SS 110/6 Akkumulyatornaya | 2*25 | 24.23 | 0 | 0 | 24.23 | 0 | 26.25 | 2.02 | 2.02 | opened | 132 | SS 110/6 Akkumulyatornaya | 2*25 | 0 | 24.23 | 0 | 0 | 24.23 | 0 | 26.25 | 2.02 | 2.02 | opened
133 | SS 110/10 ARZ | 6,3+10,0 | 3.15 | 0.9 | 45 | 2.25 | 0 | 6.62 | 4.37 | 4.37 | opened | 133 | SS 110/10 ARZ | 6,3+10,0 | 0 | 3.15 | 0.9 | 45 | 2.25 | 0 | 6.62 | 4.37 | 4.37 | opened
134 | SS 110/35/10 Atomgrad | 2*25 | 13.35 | 20.2 | 120 | -6.85 | 0 | 26.25 | 33.1 | 23.5 | opened | 134 | SS 110/35/10 Atomgrad | 2*25 | 0.19118 | 13.5412 | 20.2 | 120 | -6.6588 | 0 | 26.25 | 32.9088 | 23.4395 | opened
| Nom. capacity MV, MVA | 25 | 1 | 10.6 | 120 | -9.6 | 0 | 26.25 | 35.85 |  |  |  | Nom. capacity MV, MVA | 25 | 0.13068 | 1.1307 | 10.6 | 120 | -9.4693 | 0 | 26.25 | 35.7193
| Nom. capacity lV, MVA | 25 | 12.35 | 9.6 | 120 | 2.75 | 0 | 26.25 | 23.5 |  |  |  | Nom. capacity lV, MVA | 25 | 0.0605 | 12.4105 | 9.6 | 120 | 2.8105 | 0 | 26.25 | 23.4395
135 | SS 110/10 B. Zhirovo | 2*6,3 | 0.44 | 0.6 | 120 | -0.16 | 0 | 6.62 | 6.78 | 6.78 | opened | 135 | SS 110/10 B. Zhirovo | 2*6,3 | 0.027 | 0.467 | 0.6 | 120 | -0.133 | 0 | 6.62 | 6.753 | 6.753 | opened
136 | SS 110/35/10 Basovo | 5,6+10,0 | 0.96 | 6.19 | 15 | -5.23 | 0 | 5.88 | 11.11 | 5.43 | opened | 136 | SS 110/35/10 Basovo | 5,6+10,0 | 0.058 | 1.018 | 6.19 | 15 | -5.172 | 0 | 5.88 | 11.052 | 5.426 | opened
| Ном. Мощность СН, МВА | 5,6+10,0 | 0.32 | 6 |  | -5.68 | 0 | 5.88 | 11.56 |  |  |  | Ном. Мощность СН, МВА | 5,6+10,0 | 0.054 | 0.374 | 6 | 0 | -5.626 | 0 | 5.88 | 11.506
| Nom. capacity LV, MVA | 5,6+10,0 | 0.64 | 0.19 | 120 | 0.45 | 0 | 5.88 | 5.43 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.004 | 0.644 | 0.19 | 120 | 0.454 | 0 | 5.88 | 5.426
137 | SS 110/35/10 Belaya | 2*16,0 | 6 | 12 | 120 | -6 | 0 | 16.8 | 22.8 | 13 | opened | 137 | SS 110/35/10 Belaya | 2*16,0 | 0.7298 | 6.7298 | 12 | 120 | -5.2702 | 0 | 16.8 | 22.0702 | 12.4663 | opened
| Nom. capacity MV, MVA | 16 | 3.8 | 0 |  | 3.8 | 0 | 16.8 | 13 |  |  |  | Nom. capacity MV, MVA | 16 | 0.5337 | 4.3337 | 0 | 0 | 4.3337 | 0 | 16.8 | 12.4663
| Nom. capacity LV, MVA | 16 | 2.2 | 12 | 120 | -9.8 | 0 | 16.8 | 26.6 |  |  |  | Nom. capacity LV, MVA | 16 | 0.1961 | 2.3961 | 12 | 120 | -9.6039 | 0 | 16.8 | 26.4039
138 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.03 | 1.3 | 120 | -0.27 | 0 | 6.62 | 6.89 | 6.39 | opened | 138 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.026 | 1.056 | 1.3 | 120 | -0.244 | 0 | 6.62 | 6.864 | 6.39 | opened
| Nom. capacity MV, MVA | 6.3 | 0.23 |  |  | 0.23 | 0 | 6.62 | 6.39 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.23 | 0 | 0 | 0.23 | 0 | 6.62 | 6.39
| Nom. capacity LV, MVA | 6.3 | 0.8 | 1.3 | 120 | -0.5 | 0 | 6.62 | 7.12 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.026 | 0.826 | 1.3 | 120 | -0.474 | 0 | 6.62 | 7.094
139 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.22 | 1.17 | 45 | 1.05 | 0 | 2.63 | 1.58 | 1.58 | opened | 139 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.032 | 2.252 | 1.17 | 45 | 1.082 | 0 | 2.63 | 1.548 | 1.548 | opened
140 | SS 110/35/6 Volokno | 40,0+2*40,5 | 52.92 | 16.8 | 0 | 36.12 | 0 | 84.53 | 48.41 | 48.41 | opened | 140 | SS 110/35/6 Volokno | 40,0+2*40,5 | 0.5495 | 53.4695 | 16.8 | 0 | 36.6695 | 0 | 84.53 | 47.8605 | 47.8605 | opened
| Nom. capacity MV, MVA | 40,0+2*40,5 | 23.81 | 16.8 | 0 | 7.01 | 0 | 84.53 | 77.52 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.4885 | 24.2985 | 16.8 | 0 | 7.4985 | 0 | 84.53 | 77.0315
| Nom. capacity MV, MVA | 40,0+2*40,5 | 29.11 | 0 | 0 | 29.11 | 0 | 84.53 | 55.42 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.061 | 29.171 | 0 | 0 | 29.171 | 0 | 84.53 | 55.359
141 | SS 110/10 Vysokaya | 2*16,0 | 19.46 | 3.2 | 15 | 16.26 | 0 | 16.8 | 0.54 | 0.54 | opened | 141 | SS 110/10 Vysokaya | 2*16,0 | 0 | 19.46 | 3.2 | 15 | 16.26 | 0 | 16.8 | 0.54 | 0.54 | opened
142 | SS 110/35/10 Glushkovo | 2*10,0 | 7.95 | 8.04 | 120 | -0.09 | 0 | 10.5 | 10.59 | 7.59 | opened | 142 | SS 110/35/10 Glushkovo | 2*10,0 | 0.88 | 8.83 | 8.04 | 120 | 0.79 | 0 | 10.5 | 9.71 | 7.57 | opened
| Nom. capacity MV, MVA | 10 | 3.6 | 6.6 | 120 | -3 | 0 | 10.5 | 13.5 |  |  |  | Nom. capacity MV, MVA | 10 | 0.86 | 4.46 | 6.6 | 120 | -2.14 | 0 | 10.5 | 12.64
| Nom. capacity LV, MVA | 10 | 4.35 | 1.44 | 80 | 2.91 | 0 | 10.5 | 7.59 |  |  |  | Nom. capacity LV, MVA | 10 | 0.02 | 4.37 | 1.44 | 80 | 2.93 | 0 | 10.5 | 7.57
143 | SS 110/10 Gorodskaya | 2*25,0 | 10.05 | 0 | 0 | 10.05 | 0 | 26.25 | 16.2 | 16.2 | opened | 143 | SS 110/10 Gorodskaya | 2*25,0 | 0.394 | 10.444 | 0 | 0 | 10.444 | 0 | 26.25 | 15.806 | 15.806 | opened
144 | SS 110/35/10 Gorshechnoe | 10+16,0 | 9.52 | 6.52 | 120 | 3 | 0 | 10.5 | 7.5 | 4.86 | opened | 144 | SS 110/35/10 Gorshechnoe | 10+16,0 | 0.4938 | 10.0138 | 6.52 | 120 | 3.4938 | 0 | 10.5 | 7.0062 | 4.407 | opened
| Nom. capacity MV, MVA | 10+16,0 | 3.42 | 6.06 |  | -2.64 | 0 | 10.5 | 13.14 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 0.0408 | 3.4608 | 6.06 | 0 | -2.5992 | 0 | 10.5 | 13.0992
| Nom. capacity LV, MVA | 10+16,0 | 6.1 | 0.46 | 120 | 5.64 | 0 | 10.5 | 4.86 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.453 | 6.553 | 0.46 | 120 | 6.093 | 0 | 10.5 | 4.407
145 | SS 110/35/10 Dmitriev | 2*10,0 | 7.85 | 10.4 | 120 | -2.55 | 0 | 10.5 | 13.05 | 8.01 | opened | 145 | SS 110/35/10 Dmitriev | 2*10,0 | 0.3835 | 8.2335 | 10.4 | 120 | -2.1665 | 0 | 10.5 | 12.6665 | 7.6625 | opened
| Nom. capacity MV, MVA | 10 | 2.36 | 7.4 |  | -5.04 | 0 | 10.5 | 15.54 |  |  |  | Nom. capacity MV, MVA | 10 | 0.036 | 2.396 | 7.4 | 0 | -5.004 | 0 | 10.5 | 15.504
| Nom. capacity LV, MVA | 10 | 5.49 | 3 | 80 | 2.49 | 0 | 10.5 | 8.01 |  |  |  | Nom. capacity LV, MVA | 10 | 0.3475 | 5.8375 | 3 | 80 | 2.8375 | 0 | 10.5 | 7.6625
146 | SS 110/6 Dolgie Budy | 2*10,0 | 0.36 | 0.5 | 120 | -0.14 | 0 | 10.5 | 10.64 | 10.64 | opened | 146 | SS 110/6 Dolgie Budy | 2*10,0 | 0.048 | 0.408 | 0.5 | 120 | -0.092 | 0 | 10.5 | 10.592 | 10.592 | opened
147 | SS 110/35/10 Zolotukhino | 2*25,0 | 5.2 | 22.1 | 80 | -16.9 | 0 | 26.25 | 43.15 | 27.99 | opened | 147 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.2147 | 5.4147 | 22.1 | 80 | -16.6853 | 0 | 26.25 | 42.9353 | 27.7963 | opened
| Nom. capacity MV, MVA | 25 | 3.64 | 18.8 |  | -15.16 | 0 | 26.25 | 41.41 |  |  |  | Nom. capacity MV, MVA | 25 | 0.021 | 3.661 | 18.8 | 0 | -15.139 | 0 | 26.25 | 41.389
| Nom. capacity LV, MVA | 25 | 1.56 | 3.3 | 120 | -1.74 | 0 | 26.25 | 27.99 |  |  |  | Nom. capacity LV, MVA | 25 | 0.1937 | 1.7537 | 3.3 | 120 | -1.5463 | 0 | 26.25 | 27.7963
148 | SS 110/35/10 Kamyshi | 2*6,3 | 7.87 | 6.45 | 20 | 1.42 | 0 | 6.62 | 5.2 | 4.36 | opened | 148 | SS 110/35/10 Kamyshi | 2*6,3 | 6.2977 | 14.1677 | 6.45 | 20 | 7.7177 | 0 | 6.62 | -1.0977 | -1.9377 | closed
| Nom. capacity MV, MVA | 6.3 | 6.71 | 4.45 |  | 2.26 | 0 | 6.62 | 4.36 |  |  |  | Nom. capacity MV, MVA | 6.3 | 6.2977 | 13.0077 | 4.45 | 0 | 8.5577 | 0 | 6.62 | -1.9377
| Nom. capacity LV, MVA | 6.3 | 1.16 | 2 | 20 | -0.84 | 0 | 6.62 | 7.46 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 1.16 | 2 | 20 | 2 | 0 | 6.62 | 4.62
149 | SS 110/35/10 Kastornoe | 15,0+16,0 | 11.37 | 6.97 | 120 | 4.4 | 0 | 15.75 | 11.35 | 11.35 | opened | 149 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.3589 | 11.7289 | 6.97 | 120 | 4.7589 | 0 | 15.75 | 10.9911 | 10.9911 | opened
| Nom. capacity MV, MVA | 15,0+16,0 | 10.12 | 6.6 |  | 3.52 | 0 | 15.75 | 12.23 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.2426 | 10.3626 | 6.6 | 0 | 3.7626 | 0 | 15.75 | 11.9874
| Nom. capacity LV, MVA | 15,0+16,0 | 1.25 | 0.37 | 120 | 0.88 | 0 | 15.75 | 14.87 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.1163 | 1.3663 | 0.37 | 120 | 0.9963 | 0 | 15.75 | 14.7537
150 | SS 110/35/10 Kilikino | 2*16,0 | 2.59 | 6.9 | 120 | -4.31 | 0 | 16.8 | 21.11 | 18.62 | opened | 150 | SS 110/35/10 Kilikino | 2*16,0 | 0.045 | 2.635 | 6.9 | 120 | -4.265 | 0 | 16.8 | 21.065 | 18.62 | opened
| Nom. capacity MV, MVA | 16 | 2.51 | 5 |  | -2.49 | 0 | 16.8 | 19.29 |  |  |  | Nom. capacity MV, MVA | 16 | 0.045 | 2.555 | 5 | 0 | -2.445 | 0 | 16.8 | 19.245
| Nom. capacity LV, MVA | 16 | 0.08 | 1.9 | 120 | -1.82 | 0 | 16.8 | 18.62 |  |  |  | Nom. capacity LV, MVA | 16 | 0 | 0.08 | 1.9 | 120 | -1.82 | 0 | 16.8 | 18.62
151 | SS 110/35/6 Kirovskaya | 2*40,0 | 55.32 | 14.86 | 120 | 40.46 | 0 | 42 | 1.54 | 1.54 | opened | 151 | SS 110/35/6 Kirovskaya | 2*40,0 | 0.55 | 55.87 | 14.86 | 120 | 41.01 | 0 | 42 | 0.99 | 0.99 | opened
| Nom. capacity MV, MVA | 40 | 27.08 | 11.56 | 120 | 15.52 | 0 | 42 | 26.48 |  |  |  | Nom. capacity MV, MVA | 40 |  | 27.08 | 11.56 | 120 | 15.52 | 0 | 42 | 26.48
| Nom. capacity LV, MVA | 40 | 28.24 | 3.3 | 120 | 24.94 | 0 | 42 | 17.06 |  |  |  | Nom. capacity LV, MVA | 40 | 0.55 | 28.79 | 3.3 | 120 | 25.49 | 0 | 42 | 16.51
152 | SS 110/35/10 Klyukva | 2*16,0 | 2.59 | 1.2 | 120 | 1.39 | 0 | 16.8 | 15.41 | 15.41 | opened | 152 | SS 110/35/10 Klyukva | 2*16,0 | 0.268 | 2.858 | 1.2 | 120 | 1.658 | 0 | 16.8 | 15.142 | 15.142 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16 |  | 0 | 0 | 0 | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 2.59 | 1.2 | 120 | 1.39 | 0 | 16.8 | 15.41 |  |  |  | Nom. capacity LV, MVA | 16 | 0.268 | 2.858 | 1.2 | 120 | 1.658 | 0 | 16.8 | 15.142
153 | SS 110/10 Kompressornaya | 2*40,0 | 1.02 | 0 | 0 | 1.02 | 0 | 42 | 40.98 | 40.98 | opened | 153 | SS 110/10 Kompressornaya | 2*40,0 | 0 | 1.02 | 0 | 0 | 1.02 | 0 | 42 | 40.98 | 40.98 | opened
154 | SS 110/35/10 Konyshevka | 10,0+16,0 | 7.32 | 8 | 120 | -0.68 | 0 | 10.5 | 11.18 | 10.58 | opened | 154 | SS 110/35/10 Konyshevka | 10,0+16,0 | 0.0425 | 7.3625 | 8 | 120 | -0.6375 | 0 | 10.5 | 11.1375 | 10.5425 | opened
| Nom. capacity MV, MVA | 10,0+16,0 | 5.82 | 5.9 |  | -0.08 | 0 | 10.5 | 10.58 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.0375 | 5.8575 | 5.9 | 0 | -0.0425 | 0 | 10.5 | 10.5425
| Nom. capacity LV, MVA | 10,0+16,0 | 1.5 | 2.1 |  | -0.6 | 0 | 10.5 | 11.1 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.005 | 1.505 | 2.1 | 0 | -0.595 | 0 | 10.5 | 11.095
155 | SS 110/10 Kotelnaya | 10,0+25,0 | 7.14 | 0 | 0 | 7.14 | 0 | 10.5 | 3.36 | 3.36 | opened | 155 | SS 110/10 Kotelnaya | 10,0+25,0 | 0.605 | 7.745 | 0 | 0 | 7.745 | 0 | 10.5 | 2.755 | 2.755 | opened
156 | SS 110/35/10 Kshen | 2*10,0 | 8.84 | 6.63 | 10 | 2.21 | 0 | 10.5 | 8.29 | 6.13 | opened | 156 | SS 110/35/10 Kshen | 2*10,0 | 0.2875 | 9.1275 | 6.63 | 10 | 2.4975 | 0 | 10.5 | 8.0025 | 5.9532 | opened
| Nom. capacity MV, MVA | 10 | 3.9 | 6.06 |  | -2.16 | 0 | 10.5 | 12.66 |  |  |  | Nom. capacity MV, MVA | 10 | 0.1107 | 4.0107 | 6.06 | 0 | -2.0493 | 0 | 10.5 | 12.5493
| Nom. capacity LV, MVA | 10 | 4.94 | 0.57 | 120 | 4.37 | 0 | 10.5 | 6.13 |  |  |  | Nom. capacity LV, MVA | 10 | 0.1768 | 5.1168 | 0.57 | 120 | 4.5468 | 0 | 10.5 | 5.9532
157 | SS 110/6 Lesnaya | 2*40,0 | 1.99 | 0 | 0 | 1.99 | 0 | 42 | 40.01 | 40.01 | opened | 157 | SS 110/6 Lesnaya | 2*40,0 | 0 | 1.99 | 0 | 0 | 1.99 | 0 | 42 | 40.01 | 40.01 | opened
158 | SS 110/35/10 Lgov | 2*25,0 | 12.32 | 4 | 120 | 8.32 | 0 | 26.25 | 17.93 | 3.19 | opened | 158 | SS 110/35/10 Lgov | 2*25,0 | 0.2665 | 12.5865 | 4 | 120 | 8.5865 | 0 | 26.25 | 17.6635 | 2.9315 | opened
| Nom. capacity MV, MVA | 25 | 1.01 |  |  | 1.01 | 0 | 10.5 | 9.49 |  |  |  | Nom. capacity MV, MVA | 25 | 0.008 | 1.018 | 0 | 0 | 1.018 | 0 | 10.5 | 9.482
| Nom. capacity LV, MVA | 25 | 11.31 | 4 | 120 | 7.31 | 0 | 10.5 | 3.19 |  |  |  | Nom. capacity LV, MVA | 25 | 0.2585 | 11.5685 | 4 | 120 | 7.5685 | 0 | 10.5 | 2.9315
159 | SS 110/35/10 Lukashevka | 2*16,0 | 7.38 | 10.6 | 120 | -3.22 | 0 | 16.8 | 20.02 | 16.12 | opened | 159 | SS 110/35/10 Lukashevka | 2*16,0 | 0.039 | 7.419 | 10.6 | 120 | -3.181 | 0 | 16.8 | 19.981 | 16.12 | opened
| Nom. capacity MV, MVA | 16 | 1.4 | 5.3 |  | -3.9 | 0 | 16.8 | 20.7 |  |  |  | Nom. capacity MV, MVA | 16 | 0.039 | 1.439 | 5.3 | 0 | -3.861 | 0 | 16.8 | 20.661
| Nom. capacity LV, MVA | 16 | 5.98 | 5.3 | 120 | 0.68 | 0 | 16.8 | 16.12 |  |  |  | Nom. capacity LV, MVA | 16 | 0 | 5.98 | 5.3 | 120 | 0.68 | 0 | 16.8 | 16.12
160 | SS 110/35/10 Lyubostan | 6,3+10,0 | 3.24 | 13.1 | 120 | -9.86 | 0 | 6.62 | 16.48 | 7.18 | opened | 160 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.1151 | 3.3551 | 13.1 | 120 | -9.7449 | 0 | 6.62 | 16.3649 | 7.1755 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 2.5 | 11.8 |  | -9.3 | 0 | 6.62 | 15.92 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.1106 | 2.6106 | 11.8 | 0 | -9.1894 | 0 | 6.62 | 15.8094
| Nom. capacity LV, MVA | 6,3+10,0 | 0.74 | 1.3 |  | -0.56 | 0 | 6.62 | 7.18 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.0045 | 0.7445 | 1.3 | 0 | -0.5555 | 0 | 6.62 | 7.1755
161 | SS 110/35/6 Manturovo | 2*16,0 | 6.88 | 9.35 | 10 | -2.47 | 0 | 16.8 | 19.27 | 16.77 | opened | 161 | SS 110/35/6 Manturovo | 2*16,0 | 0.1775 | 7.0575 | 9.35 | 10 | -2.2925 | 0 | 16.8 | 19.0925 | 16.7655 | opened
| Nom. capacity MV, MVA | 16 | 6.59 | 9.09 |  | -2.5 | 0 | 16.8 | 19.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.173 | 6.763 | 9.09 | 0 | -2.327 | 0 | 16.8 | 19.127
| Nom. capacity LV, MVA | 16 | 0.29 | 0.26 | 120 | 0.03 | 0 | 16.8 | 16.77 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0045 | 0.2945 | 0.26 | 120 | 0.0345 | 0 | 16.8 | 16.7655
162 | SS 110/35/10 8th Marta | 6,3+10,0 | 6.39 | 9.6 | 120 | -3.21 | 0 | 6.62 | 9.83 | 7.68 | opened | 162 | SS 110/35/10 8th Marta | 6,3+10,0 | 0.247 | 6.637 | 9.6 | 120 | -2.963 | 0 | 6.62 | 9.583 | 7.437 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 5.54 | 6.6 | 120 | -1.06 | 0 | 6.62 | 7.68 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.243 | 5.783 | 6.6 | 120 | -0.817 | 0 | 6.62 | 7.437
| Nom. capacity LV, MVA | 6,3+10,0 | 0.85 | 3 | 45 | -2.15 | 0 | 6.62 | 8.77 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.004 | 0.854 | 3 | 45 | -2.146 | 0 | 6.62 | 8.766
163 | SS 110/10 Martovskaya | 2*6,3 | 0.63 | 0.55 | 120 | 0.08 | 0 | 6.62 | 6.54 | 6.54 | opened | 163 | SS 110/10 Martovskaya | 2*6,3 | 0.269 | 0.899 | 0.55 | 120 | 0.349 | 0 | 6.62 | 6.271 | 6.271 | opened
164 | SS 110/35/10 Maryino | 10,0+25,0 | 7.16 | 8.11 | 120 | -0.95 | 0 | 10.5 | 11.45 | 10.06 | opened | 164 | SS 110/35/10 Maryino | 10,0+25,0 | 0.457 | 7.617 | 8.11 | 120 | -0.493 | 0 | 10.5 | 10.993 | 10.051 | opened
| Nom. capacity MV, MVA | 10,0+25,0 | 3.51 | 4.9 |  | -1.39 | 0 | 10.5 | 11.89 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.448 | 3.958 | 4.9 | 0 | -0.942 | 0 | 10.5 | 11.442
| Nom. capacity LV, MVA | 10,0+25,0 | 3.65 | 3.21 |  | 0.44 | 0 | 10.5 | 10.06 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.009 | 3.659 | 3.21 | 0 | 0.449 | 0 | 10.5 | 10.051
165 | SS 110/35/10 Medvenka | 2*10,0 | 6.19 | 19.22 | 120 | -13.03 | 0 | 10.5 | 23.53 | 8.89 | opened | 165 | SS 110/35/10 Medvenka | 2*10,0 | 0.333 | 6.523 | 19.22 | 120 | -12.697 | 0 | 10.5 | 23.197 | 8.851 | opened
| Nom. capacity MV, MVA | 10 | 2.46 | 17.1 |  | -14.64 | 0 | 10.5 | 25.14 |  |  |  | Nom. capacity MV, MVA | 10 | 0.294 | 2.754 | 17.1 | 0 | -14.346 | 0 | 10.5 | 24.846
| Nom. capacity LV, MVA | 10 | 3.73 | 2.12 | 120 | 1.61 | 0 | 10.5 | 8.89 |  |  |  | Nom. capacity LV, MVA | 10 | 0.039 | 3.769 | 2.12 | 120 | 1.649 | 0 | 10.5 | 8.851
166 | SS 110/6 Neftyanaya | 2*10,0 | 0.144 |  |  | 0.144 | 0 | 10.5 | 10.356 | 10.356 | opened | 166 | SS 110/6 Neftyanaya | 2*10,0 | 0 | 0.144 | 0 | 0 | 0.144 | 0 | 10.5 | 10.356 | 10.356 | opened
167 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 9.8 | 26.86 | 120 | -17.06 | 0 | 16.8 | 33.86 | 17.86 | opened | 167 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 0.4631 | 10.2631 | 26.86 | 120 | -16.5969 | 0 | 16.8 | 33.3969 | 17.4237 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 1.4 | 17.4 | 0 | -16 | 0 | 16.8 | 32.8 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.0268 | 1.4268 | 17.4 | 0 | -15.9732 | 0 | 16.8 | 32.7732
| Nom. capacity LV, MVA | 16,0 + 25,0 | 8.4 | 9.46 |  | -1.06 | 0 | 16.8 | 17.86 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.4363 | 8.8363 | 9.46 | 0 | -0.6237 | 0 | 16.8 | 17.4237
168 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 9.58 | 15.5 | 120 | -5.92 | 0 | 16.8 | 22.72 | 14.11 | opened | 168 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.113 | 9.693 | 15.5 | 120 | -5.807 | 0 | 16.8 | 22.607 | 14.019 | opened
| Nom. capacity MV, MVA | 16 | 5.88 | 14.5 |  | -8.62 | 0 | 16.8 | 25.42 |  |  |  | Nom. capacity MV, MVA | 16 | 0.022 | 5.902 | 14.5 | 0 | -8.598 | 0 | 16.8 | 25.398
| Nom. capacity LV, MVA | 16 | 3.69 | 1 | 120 | 2.69 | 0 | 16.8 | 14.11 |  |  |  | Nom. capacity LV, MVA | 16 | 0.091 | 3.781 | 1 | 120 | 2.781 | 0 | 16.8 | 14.019
169 | SS 110/35/10 Olkhovatka | 2 х 6,3 | 1.48 | 6.31 | 120 | -4.83 | 0 | 6.62 | 11.45 | 7.76 | opened | 169 | SS 110/35/10 Olkhovatka | 2 х 6,3 | 0.02 | 1.5 | 6.31 | 120 | -4.81 | 0 | 6.62 | 11.43 | 7.744 | opened
| Nom. capacity MV, MVA | 6.3 | 1.31 | 5 | 120 | -3.69 | 0 | 6.62 | 10.31 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.004 | 1.314 | 5 | 120 | -3.686 | 0 | 6.62 | 10.306
| Nom. capacity LV, MVA | 6.3 | 0.17 | 1.31 | 120 | -1.14 | 0 | 6.62 | 7.76 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.016 | 0.186 | 1.31 | 120 | -1.124 | 0 | 6.62 | 7.744
170 | SS 110/10 Paniki | 2 х 2,5 | 0.47 | 0.1 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened | 170 | SS 110/10 Paniki | 2 х 2,5 | 0 | 0.47 | 0.1 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened
171 | SS 110/35/10 Peny | 2 х 16,0 | 7.67 | 6.9 | 120 | 0.77 | 0 | 16.8 | 16.03 | 14.48 | opened | 171 | SS 110/35/10 Peny | 2 х 16,0 | 0.0506 | 7.7206 | 6.9 | 120 | 0.8206 | 0 | 16.8 | 15.9794 | 14.48 | opened
| Nom. capacity MV, MVA | 16 | 1.95 | 3.5 |  | -1.55 | 0 | 16.8 | 18.35 |  |  |  | Nom. capacity MV, MVA | 16 | 0.0506 | 2.0006 | 3.5 | 0 | -1.4994 | 0 | 16.8 | 18.2994
| Nom. capacity LV, MVA | 16 | 5.72 | 3.4 | 120 | 2.32 | 0 | 16.8 | 14.48 |  |  |  | Nom. capacity LV, MVA | 16 | 0 | 5.72 | 3.4 | 120 | 2.32 | 0 | 16.8 | 14.48
172 | SS 110/35/10 Pribor | 2 х 25,0 | 25.53 | 2.46 | 0 | 23.07 | 0 | 26.25 | 3.18 | 3.18 | opened | 172 | SS 110/35/10 Pribor | 2 х 25,0 | 2.4 | 27.93 | 2.46 | 0 | 25.47 | 0 | 26.25 | 0.78 | 0.78 | opened
| Nom. capacity MV, MVA | 25 |  |  |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 25 |  | 0 | 0 | 0 | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 25.53 | 2.46 | 0 | 23.07 | 0 | 26.25 | 3.18 |  |  |  | Nom. capacity LV, MVA | 25 | 2.4 | 27.93 | 2.46 | 0 | 25.47 | 0 | 26.25 | 0.78
173 | SS 110/10 Progress | 2 х 63,0 | 28.16 | 0 | 0 | 28.16 | 0 | 66.2 | 38.04 | 38.04 | opened | 173 | SS 110/10 Progress | 2 х 63,0 | 0 | 28.16 | 0 | 0 | 28.16 | 0 | 66.2 | 38.04 | 38.04 | opened
174 | SS 110/10 PTF | 6,3 + 10,0 | 6.27 | 0 | 0 | 6.27 | 0 | 6.62 | 0.35 | 0.35 | opened | 174 | SS 110/10 PTF | 6,3 + 10,0 | 0.08 | 6.35 | 0 | 0 | 6.35 | 0 | 6.62 | 0.27 | 0.27 | opened
175 | SS 110/35/10 R. Budy | 2 х 10,0 | 1.25 | 15.7 | 120 | -14.45 | 0 | 10.5 | 24.95 | 16 | opened | 175 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.024 | 1.274 | 15.7 | 120 | -14.426 | 0 | 10.5 | 24.926 | 15.976 | opened
| Nom. capacity MV, MVA | 10 | 0.35 | 9.3 |  | -8.95 | 0 | 10.5 | 19.45 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.35 | 9.3 | 0 | -8.95 | 0 | 10.5 | 19.45
| Nom. capacity LV, MVA | 10 | 0.9 | 6.4 |  | -5.5 | 0 | 10.5 | 16 |  |  |  | Nom. capacity LV, MVA | 10 | 0.024 | 0.924 | 6.4 | 0 | -5.476 | 0 | 10.5 | 15.976
176 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.08 | 21.4 | 45 | -19.32 | 0 | 6.62 | 25.94 | 9.56 | opened | 176 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 0.302 | 2.382 | 21.4 | 45 | -19.018 | 0 | 6.62 | 25.638 | 9.56 | opened
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.42 | 17.8 |  | -16.38 | 0 | 6.62 | 23 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 0.302 | 1.722 | 17.8 | 0 | -16.078 | 0 | 6.62 | 22.698
| Nom. capacity LV, MVA | 6,3 + 10,0 | 0.66 | 3.6 | 45 | -2.94 | 0 | 6.62 | 9.56 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0 | 0.66 | 3.6 | 45 | -2.94 | 0 | 6.62 | 9.56
177 | SS 110/35/10 Rudnaya | 2 х 31,5 | 16.99 | 3.25 | 10 | 13.74 | 0 | 33.1 | 19.36 | 19.36 | opened | 177 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.3 | 17.29 | 3.25 | 10 | 14.04 | 0 | 33.1 | 19.06 | 19.06 | opened
| Nom. capacity MV, MVA | 31.5 | 11.46 | 1.7 |  | 9.76 | 0 | 33.1 | 23.34 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.3 | 11.76 | 1.7 | 0 | 10.06 | 0 | 33.1 | 23.04
| Nom. capacity LV, MVA | 31.5 | 5.53 | 1.55 | 120 | 3.98 | 0 | 33.1 | 29.12 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0 | 5.53 | 1.55 | 120 | 3.98 | 0 | 33.1 | 29.12
178 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 16.47 | 11 | 120 | 5.47 | 0 | 16.8 | 11.33 | 11.33 | opened | 178 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 0.3328 | 16.8028 | 11 | 120 | 5.8028 | 0 | 16.8 | 10.9972 | 10.9972 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 9.76 | 7 |  | 2.76 | 0 | 16.8 | 14.04 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.1988 | 9.9588 | 7 | 0 | 2.9588 | 0 | 16.8 | 13.8412
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.71 | 4 | 120 | 2.71 | 0 | 16.8 | 14.09 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.134 | 6.844 | 4 | 120 | 2.844 | 0 | 16.8 | 13.956
179 | SS 110/10 Solovyinaya | 2 х 25,0 | 17.32 | 0 | 0 | 17.32 | 0 | 26.25 | 8.93 | 8.93 | opened | 179 | SS 110/10 Solovyinaya | 2 х 25,0 | 0 | 17.32 | 0 | 0 | 17.32 | 0 | 26.25 | 8.93 | 8.93 | opened
180 | SS 110/10 STK | 2 х 10,0 | 2.34 | 0 | 0 | 2.34 | 0 | 10.5 | 8.16 | 8.16 | opened | 180 | SS 110/10 STK | 2 х 10,0 | 0 | 2.34 | 0 | 0 | 2.34 | 0 | 10.5 | 8.16 | 8.16 | opened
181 | SS 110/10 Studenok | 2 х 6,3 | 2.89 | 0.7 | 120 | 2.19 | 0 | 6.62 | 4.43 | 4.43 | opened | 181 | SS 110/10 Studenok | 2 х 6,3 | 0.071 | 2.961 | 0.7 | 120 | 2.261 | 0 | 6.62 | 4.359 | 4.359 | opened
182 | SS 110/35/10 Sudzha | 2 х 25,0 | 12.77 | 29 | 120 | -16.23 | 0 | 26.25 | 42.48 | 31.45 | opened | 182 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.1984 | 13.9683 | 29 | 120 | -15.0317 | 0 | 26.25 | 41.2816 | 31.0398 | opened
| Nom. capacity MV, MVA | 25 | 6.07 | 17.1 |  | -11.03 | 0 | 26.25 | 37.28 |  |  |  | Nom. capacity MV, MVA | 25 | 0.7881 | 6.8581 | 17.1 | 0 | -10.2419 | 0 | 26.25 | 36.4919
| Nom. capacity LV, MVA | 25 | 6.7 | 11.9 |  | -5.2 | 0 | 26.25 | 31.45 |  |  |  | Nom. capacity LV, MVA | 25 | 0.41025 | 7.1102 | 11.9 | 0 | -4.7897 | 0 | 26.25 | 31.0398
183 | SS 110/35/10 Schyotmash | 2 х 25,0 | 12.53 | 0 | 0 | 12.53 | 0 | 26.25 | 13.72 | 13.72 | opened | 183 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.0431 | 18.5731 | 0 | 0 | 18.5731 | 0 | 26.25 | 7.6769 | 7.6769 | opened
| Nom. capacity MV, MVA | 25 | 4.18 |  |  | 4.18 | 0 | 26.25 | 22.07 |  |  |  | Nom. capacity MV, MVA | 25 | 0.6431 | 4.8231 | 0 | 0 | 4.8231 | 0 | 26.25 | 21.4269
| Nom. capacity LV, MVA | 25 | 8.35 | 0 | 0 | 8.35 | 0 | 26.25 | 17.9 |  |  |  | Nom. capacity LV, MVA | 25 | 5.4 | 13.75 | 0 | 0 | 13.75 | 0 | 26.25 | 12.5
184 | SS 110/35/10 Tyotkino | 2 х 10,0 | 3.9 | 3.44 | 120 | 0.46 | 0 | 10.5 | 10.04 | 9.04 | opened | 184 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.0189 | 3.9189 | 3.44 | 120 | 0.4789 | 0 | 10.5 | 10.0211 | 9.0335 | opened
| Nom. capacity MV, MVA | 10 | 1 | 2 |  | -1 | 0 | 10.5 | 11.5 |  |  |  | Nom. capacity MV, MVA | 10 | 0.0124 | 1.0124 | 2 | 0 | -0.9876 | 0 | 10.5 | 11.4876
| Nom. capacity LV, MVA | 10 | 2.9 | 1.44 |  | 1.46 | 0 | 10.5 | 9.04 |  |  |  | Nom. capacity LV, MVA | 10 | 0.0065 | 2.9065 | 1.44 | 0 | 1.4665 | 0 | 10.5 | 9.0335
185 | SS 110/35/10 Tim | 6,3 + 16,0 | 3.13 | 9.59 | 120 | -6.46 | 0 | 6.62 | 13.08 | 6.5 | opened | 185 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.1713 | 3.3013 | 9.59 | 120 | -6.2887 | 0 | 6.62 | 12.9087 | 6.4627 | opened
| Nom. capacity MV, MVA | 6,3 + 16,0 | 2.51 | 9.09 |  | -6.58 | 0 | 6.62 | 13.2 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.134 | 2.644 | 9.09 | 0 | -6.446 | 0 | 6.62 | 13.066
| Nom. capacity LV, MVA | 6,3 + 16,0 | 0.62 | 0.5 | 120 | 0.12 | 0 | 6.62 | 6.5 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.0373 | 0.6573 | 0.5 | 120 | 0.1573 | 0 | 6.62 | 6.4627
186 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.67 | 0.5 | 120 | 0.17 | 0 | 10.5 | 10.33 | 10 | opened | 186 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.01 | 0.68 | 0.5 | 120 | 0.18 | 0 | 10.5 | 10.32 | 10 | opened
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.5 |  |  | 0.5 | 0 | 10.5 | 10 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0 | 0.5 | 0 | 0 | 0.5 | 0 | 10.5 | 10
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.17 | 0.5 | 120 | -0.33 | 0 | 10.5 | 10.83 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.01 | 0.18 | 0.5 | 120 | -0.32 | 0 | 10.5 | 10.82
187 | SS 110/35/10 Fatezh | 2 х 16,0 | 5.99 | 17.4 | 120 | -11.41 | 0 | 16.8 | 28.21 | 17.12 | opened | 187 | SS 110/35/10 Fatezh | 2 х 16,0 | 0.1665 | 6.1565 | 17.4 | 120 | -11.2435 | 0 | 16.8 | 28.0435 | 17.0555 | opened
| Nom. capacity MV, MVA | 16 | 1.71 | 12.8 |  | -11.09 | 0 | 16.8 | 27.89 |  |  |  | Nom. capacity MV, MVA | 16 | 0.102 | 1.812 | 12.8 | 0 | -10.988 | 0 | 16.8 | 27.788
| Nom. capacity LV, MVA | 16 | 4.28 | 4.6 | 120 | -0.32 | 0 | 16.8 | 17.12 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0645 | 4.3445 | 4.6 | 120 | -0.2555 | 0 | 16.8 | 17.0555
188 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 4.025 | 12.34 | 120 | -8.315 | 0 | 26.25 | 34.565 | 24.905 | opened | 188 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.0469 | 4.0719 | 12.34 | 120 | -8.2681 | 0 | 26.25 | 34.5181 | 24.9031 | opened
| Nom. capacity MV, MVA | 25 | 2.45 | 12.12 |  | -9.67 | 0 | 26.25 | 35.92 |  |  |  | Nom. capacity MV, MVA | 25 | 0.045 | 2.495 | 12.12 | 0 | -9.625 | 0 | 26.25 | 35.875
| Nom. capacity LV, MVA | 25 | 1.565 | 0.22 | 10 | 1.345 | 0 | 26.25 | 24.905 |  |  |  | Nom. capacity LV, MVA | 25 | 0.0019 | 1.5669 | 0.22 | 10 | 1.3469 | 0 | 26.25 | 24.9031
189 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 2.61 | 6.3 | 80 | -3.69 | 0 | 7.88 | 11.57 | 8.3 | opened | 189 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.043 | 2.653 | 6.3 | 80 | -3.647 | 0 | 7.88 | 11.527 | 8.259 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.63 | 3.9 |  | -3.27 | 0 | 7.88 | 11.15 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.002 | 0.632 | 3.9 | 0 | -3.268 | 0 | 7.88 | 11.148
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.98 | 2.4 | 80 | -0.42 | 0 | 7.88 | 8.3 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.041 | 2.021 | 2.4 | 80 | -0.379 | 0 | 7.88 | 8.259
190 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 6.09 | 9.38 | 10 | -3.29 | 0 | 16.8 | 20.09 | 15.72 | opened | 190 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.17525 | 6.2652 | 9.38 | 10 | -3.1147 | 0 | 16.8 | 19.9148 | 15.5448 | opened
| Nom. capacity MV, MVA | 16 | 4.72 | 9.09 |  | -4.37 | 0 | 16.8 | 21.17 |  |  |  | Nom. capacity MV, MVA | 16 | 0 | 4.72 | 9.09 | 0 | -4.37 | 0 | 16.8 | 21.17
| Nom. capacity LV, MVA | 16 | 1.37 | 0.29 | 120 | 1.08 | 0 | 16.8 | 15.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.17525 | 1.5453 | 0.29 | 120 | 1.2552 | 0 | 16.8 | 15.5448
191 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 3.13 | 8.25 | 120 | -5.12 | 0 | 6.62 | 11.74 | 6.67 | opened | 191 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.4325 | 3.5625 | 8.25 | 120 | -4.6875 | 0 | 6.62 | 11.3075 | 6.6645 | opened
| Nom. capacity MV, MVA | 6.3 | 1.93 | 7 |  | -5.07 | 0 | 6.62 | 11.69 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.427 | 2.357 | 7 | 0 | -4.643 | 0 | 6.62 | 11.263
| Nom. capacity LV, MVA | 6.3 | 1.2 | 1.25 | 129 | -0.05 | 0 | 6.62 | 6.67 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.0055 | 1.2055 | 1.25 | 129 | -0.0445 | 0 | 6.62 | 6.6645
192 | SS 110/35/10 Shumakovo | 2 х 10,0 | 3.75 | 13.73 | 120 | -9.98 | 0 | 10.5 | 20.48 | 12.58 | opened | 192 | SS 110/35/10 Shumakovo | 2 х 10,0 | 1.612 | 5.362 | 13.73 | 120 | -8.368 | 0 | 10.5 | 18.868 | 11.1182 | opened
| Nom. capacity MV, MVA | 10 | 3.3 | 11.2 |  | -7.9 | 0 | 10.5 | 18.4 |  |  |  | Nom. capacity MV, MVA | 10 | 0.1502 | 3.4502 | 11.2 | 0 | -7.7498 | 0 | 10.5 | 18.2498
| Nom. capacity LV, MVA | 10 | 0.45 | 2.53 | 120 | -2.08 | 0 | 10.5 | 12.58 |  |  |  | Nom. capacity LV, MVA | 10 | 1.4618 | 1.9118 | 2.53 | 120 | -0.6182 | 0 | 10.5 | 11.1182
193 | SS 110/35/10 Shchigry | 2 х 25,0 | 9.15 | 12.9 | 120 | -3.75 | 0 | 26.5 | 30.25 | 21.27 | opened | 193 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.262 | 9.412 | 12.9 | 120 | -3.488 | 0 | 26.5 | 29.988 | 21.161 | opened
| Nom. capacity MV, MVA | 25 | 3.14 | 12.12 |  | -8.98 | 0 | 26.5 | 35.48 |  |  |  | Nom. capacity MV, MVA | 25 | 0.153 | 3.293 | 12.12 | 0 | -8.827 | 0 | 26.5 | 35.327
| Nom. capacity LV, MVA | 25 | 6.01 | 0.78 | 120 | 5.23 | 0 | 26.5 | 21.27 |  |  |  | Nom. capacity LV, MVA | 25 | 0.109 | 6.119 | 0.78 | 120 | 5.339 | 0 | 26.5 | 21.161
194 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.45 | 6.31 | 10 | -3.86 | 0 | 7.88 | 11.74 | 7.09 | opened | 194 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.1732 | 2.6232 | 6.31 | 10 | -3.6868 | 0 | 7.88 | 11.5668 | 7.0655 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.41 | 6.06 |  | -4.65 | 0 | 7.88 | 12.53 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.1487 | 1.5587 | 6.06 | 0 | -4.5013 | 0 | 7.88 | 12.3813
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.04 | 0.25 | 10 | 0.79 | 0 | 7.88 | 7.09 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.0245 | 1.0645 | 0.25 | 10 | 0.8145 | 0 | 7.88 | 7.0655
195 | SS 35/10 Amosovka | 2 х 2,5 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened | 195 | SS 35/10 Amosovka | 2 х 2,5 | 0 | 0.39 | 0.2 | 120 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened
196 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.2 | 0.37 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened | 196 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0 | 0.2 | 0.37 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened
197 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 197 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 0 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
198 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.06 | 1.43 | 120 | -1.37 | 0 | 1.68 | 3.05 | 3.05 | opened | 198 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0 | 0.06 | 1.43 | 120 | -1.37 | 0 | 1.68 | 3.05 | 3.05 | opened
199 | SS 35/10 Bezlesnaya | 2 х 4,0 | 1.51 | 6.1 | 0 | -4.59 | 0 | 4.2 | 8.79 | 8.79 | opened | 199 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.148 | 1.658 | 6.1 | 0 | -4.442 | 0 | 4.2 | 8.642 | 8.642 | opened
200 | SS 35/10 Bereza | 1,0 + 2,5 | 0.15 | 0.15 | 120 | 0 | 0 | 1.05 | 1.05 | 1.05 | opened | 200 | SS 35/10 Bereza | 1,0 + 2,5 | 0.016 | 0.166 | 0.15 | 120 | 0.016 | 0 | 1.05 | 1.034 | 1.034 | opened
201 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.96 | 0.29 | 120 | 0.67 | 0 | 2.63 | 1.96 | 1.96 | opened | 201 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.018 | 0.978 | 0.29 | 120 | 0.688 | 0 | 2.63 | 1.942 | 1.942 | opened
202 | SS 35/10 Bykanovo | 2 х 2,5 | 0.35 | 0.41 | 120 | -0.06 | 0 | 2.63 | 2.69 | 2.69 | opened | 202 | SS 35/10 Bykanovo | 2 х 2,5 | 0.014 | 0.364 | 0.41 | 120 | -0.046 | 0 | 2.63 | 2.676 | 2.676 | opened
203 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.67 | 0.4 | 120 | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened | 203 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.034 | 0.704 | 0.4 | 120 | 0.304 | 0 | 4.2 | 3.896 | 3.896 | opened
204 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.36 | 0.22 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 204 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.45 | 0.81 | 0.22 | 120 | 0.59 | 0 | 1.68 | 1.09 | 1.09 | opened
205 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.5 | 0.46 | 120 | 0.04 | 0 | 2.63 | 2.59 | 2.59 | opened | 205 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.019 | 0.519 | 0.46 | 120 | 0.059 | 0 | 2.63 | 2.571 | 2.571 | opened
206 | SS 35/10 Voropaevo | 2 х 4,0 | 0.42 | 0 | 0 | 0.42 | 0 | 4.2 | 3.78 | 3.78 | opened | 206 | SS 35/10 Voropaevo | 2 х 4,0 | 0.045 | 0.465 | 0 | 0 | 0.465 | 0 | 4.2 | 3.735 | 3.735 | opened
207 | SS 35/10 Vostochnaya | 2 х 6,3 | 2.52 | 0.46 | 120 | 2.06 | 0 | 6.62 | 4.56 | 4.56 | opened | 207 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.1973 | 2.7173 | 0.46 | 120 | 2.2573 | 0 | 6.62 | 4.3627 | 4.3627 | opened
208 | SS 35/10 Vygornoe | 2 х 2,5 | 1.28 | 0.51 | 120 | 0.77 | 0 | 2.63 | 1.86 | 1.86 | opened | 208 | SS 35/10 Vygornoe | 2 х 2,5 | 0.044 | 1.324 | 0.51 | 120 | 0.814 | 0 | 2.63 | 1.816 | 1.816 | opened
209 | SS 35/10 Gastomlya | 2 х 1,6 |  | 0.17 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened | 209 | SS 35/10 Gastomlya | 2 х 1,6 | 0.013 | 0.013 | 0.17 | 120 | -0.157 | 0 | 1.68 | 1.837 | 1.837 | opened
210 | SS 35/10 Gorodok | 2 х 4,0 | 1.62 | 0.7 | 45 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened | 210 | SS 35/10 Gorodok | 2 х 4,0 | 0 | 1.62 | 0.7 | 45 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened
211 | SS 35/10 Guevo | 2 х 2,5 | 1.14 | 1.69 | 20 | -0.55 | 0 | 2.63 | 3.18 | 3.18 | opened | 211 | SS 35/10 Guevo | 2 х 2,5 | 0.105 | 1.245 | 1.69 | 20 | -0.445 | 0 | 2.63 | 3.075 | 3.075 | opened
212 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.12 | 0.38 | 120 | -0.26 | 0 | 1.68 | 1.94 | 1.94 | opened | 212 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0 | 0.12 | 0.38 | 120 | -0.26 | 0 | 1.68 | 1.94 | 1.94 | opened
213 | SS 35/6 Dukhovets | 2,5 + 4,0 | 2.38 | 3.5 | 0 | -1.12 | 0 | 2.63 | 3.75 | 3.75 | opened | 213 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0 | 2.38 | 3.5 | 0 | -1.12 | 0 | 2.63 | 3.75 | 3.75 | opened
214 | SS 35/10 Zhernovets | 2 х 2,5 | 0.28 | 0.26 | 120 | 0.02 | 0 | 2.63 | 2.61 | 2.61 | opened | 214 | SS 35/10 Zhernovets | 2 х 2,5 | 0.007 | 0.287 | 0.26 | 120 | 0.027 | 0 | 2.63 | 2.603 | 2.603 | opened
215 | SS 35/6 Zapadnaya | 2 х 10,0 | 8.14 | 0 | 0 | 8.14 | 0 | 10.5 | 2.36 | 2.36 | opened | 215 | SS 35/6 Zapadnaya | 2 х 10,0 | 0 | 8.14 | 0 | 0 | 8.14 | 0 | 10.5 | 2.36 | 2.36 | opened
216 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 1.11 | 1.67 | 0 | -0.56 | 0 | 4.2 | 4.76 | 4.76 | opened | 216 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0 | 1.11 | 1.67 | 0 | -0.56 | 0 | 4.2 | 4.76 | 4.76 | opened
217 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.75 | 0.93 | 45 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened | 217 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.047 | 0.797 | 0.93 | 45 | -0.133 | 0 | 1.68 | 1.813 | 1.813 | opened
218 | SS 35/10 Ivanino | 2 х 6,3 | 4.31 | 2.69 | 80 | 1.62 | 0 | 6.62 | 5 | 5 | opened | 218 | SS 35/10 Ivanino | 2 х 6,3 | 0.01 | 4.32 | 2.69 | 80 | 1.63 | 0 | 6.62 | 4.99 | 4.99 | opened
219 | ПС 35/10 Калиновка | 1,8 + 2,5 | 0.64 | 0.5 | 120 | 0.14 | 0 | 1.89 | 1.75 | 1.75 | opened | 219 | ПС 35/10 Калиновка | 1,8 + 2,5 | 0.002 | 0.642 | 0.5 | 120 | 0.142 | 0 | 1.89 | 1.748 | 1.748 | opened
220 | SS 35/10 Kirilovka | 2 х 1,6 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | opened | 220 | SS 35/10 Kirilovka | 2 х 1,6 | 0 | 0.22 | 0.52 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | opened
221 | SS 35/6 Kislinskaya | 2 х 10,0 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened | 221 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.315 | 17.015 | 6.25 | 20 | 10.765 | 0 | 10.5 | -0.265 | -0.265 | opened
222 | SS 35/10 Fodder plant | 4,0+6,3 | 0.71 | 0 | 0 | 0.71 | 0 | 4.2 | 3.49 | 3.49 | opened | 222 | SS 35/10 Fodder plant | 4,0+6,3 | 0.008 | 0.718 | 0 | 0 | 0.718 | 0 | 4.2 | 3.482 | 3.482 | opened
223 | SS 35/10 Fodder plant | 2 х 6,3 | 2.65 | 0.21 | 120 | 2.44 | 0 | 6.62 | 4.18 | 4.18 | opened | 223 | SS 35/10 Fodder plant | 2 х 6,3 | 0.032 | 2.682 | 0.21 | 120 | 2.472 | 0 | 6.62 | 4.148 | 4.148 | opened
224 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 1.83 | 1.14 | 80 | 0.69 | 0 | 3.36 | 2.67 | 2.67 | opened | 224 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 0 | 1.83 | 1.14 | 80 | 0.69 | 0 | 3.36 | 2.67 | 2.67 | opened
225 | SS 35/10 Korenevo | 4,0 + 6,3 | 2.51 | 1.56 | 80 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened | 225 | SS 35/10 Korenevo | 4,0 + 6,3 | 0.003 | 2.513 | 1.56 | 80 | 0.953 | 0 | 4.2 | 3.247 | 3.247 | opened
226 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.42 | 0.24 | 120 | 0.18 | 0 | 2.63 | 2.45 | 2.45 | opened | 226 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0 | 0.42 | 0.24 | 120 | 0.18 | 0 | 2.63 | 2.45 | 2.45 | opened
227 | SS 35/10 Krupets | 1,8 + 2,5 | 1.19 | 0.42 | 120 | 0.77 | 0 | 1.89 | 1.12 | 1.12 | opened | 227 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.354 | 0.42 | 120 | 0.934 | 0 | 1.89 | 0.956 | 0.956 | opened
228 | SS 35/10 Kulbaki | 2 х 2,5 | 0.84 | 0.6 | 120 | 0.24 | 0 | 2.63 | 2.39 | 2.39 | opened | 228 | SS 35/10 Kulbaki | 2 х 2,5 | 0.212 | 1.052 | 0.6 | 120 | 0.452 | 0 | 2.63 | 2.178 | 2.178 | opened
229 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened | 229 | SS 35/10 Kultprosvet | 2 х 2,5 | 0 | 0.13 | 0.17 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened
230 | SS 35/10 Kurchatov | 2 х 10,0 | 6.62 | 4.5 | 80 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened | 230 | SS 35/10 Kurchatov | 2 х 10,0 | 0 | 6.62 | 4.5 | 80 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened
231 | SS 35/10 Kutok | 2 х 2,5 | 0.08 | 0.05 | 120 | 0.03 | 0 | 2.63 | 2.6 | 2.6 | opened | 231 | SS 35/10 Kutok | 2 х 2,5 | 0.011 | 0.091 | 0.05 | 120 | 0.041 | 0 | 2.63 | 2.589 | 2.589 | opened
232 | SS 35/10 Linets | 2 х 2,5 | 0.34 | 0.25 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened | 232 | SS 35/10 Linets | 2 х 2,5 | 0.026 | 0.366 | 0.25 | 120 | 0.116 | 0 | 2.63 | 2.514 | 2.514 | opened
233 | SS 35/10 Luch | 2 х 6,3 | 2.39 | 0.23 | 120 | 2.16 | 0 | 6.62 | 4.46 | 4.46 | opened | 233 | SS 35/10 Luch | 2 х 6,3 | 0.137 | 2.527 | 0.23 | 120 | 2.297 | 0 | 6.62 | 4.323 | 4.323 | opened
234 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.57 | 1.59 | 80 | -1.02 | 0 | 4.2 | 5.22 | 5.22 | opened | 234 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.0056 | 0.5756 | 1.59 | 80 | -1.0144 | 0 | 4.2 | 5.2144 | 5.2144 | opened
235 | SS 35/10 Matveevka | 2 х 2,5 | 0.45 | 0.08 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened | 235 | SS 35/10 Matveevka | 2 х 2,5 | 0 | 0.45 | 0.08 | 120 | 0.37 | 0 | 2.63 | 2.26 | 2.26 | opened
236 | SS 35/10 Mayak | 2 х 2,5 | 0.26 | 0.3 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened | 236 | SS 35/10 Mayak | 2 х 2,5 | 0 | 0.26 | 0.3 | 120 | -0.04 | 0 | 2.63 | 2.67 | 2.67 | opened
237 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 1.6 | 1.7 | 80 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened | 237 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.116 | 1.716 | 1.7 | 80 | 0.016 | 0 | 4.2 | 4.184 | 4.184 | opened
238 | SS 35/10 Murynovka | 2 х 4,0 | 0.71 | 0.3 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 238 | SS 35/10 Murynovka | 2 х 4,0 | 0.2927 | 1.0027 | 0.3 | 120 | 0.7027 | 0 | 4.2 | 3.4973 | 3.4973 | opened
239 | SS 35/10 N. Borki | 2 х 2,5 | 0.36 | 0.63 | 120 | -0.27 | 0 | 2.63 | 2.9 | 2.9 | opened | 239 | SS 35/10 N. Borki | 2 х 2,5 | 0.0028 | 0.3628 | 0.63 | 120 | -0.2672 | 0 | 2.63 | 2.8972 | 2.8972 | opened
240 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.32 | 0.03 | 80 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened | 240 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0 | 0.32 | 0.03 | 80 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
241 | SS 35/10 Novaya | 2 х 2,5 | 1.18 | 0.4 | 120 | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 241 | SS 35/10 Novaya | 2 х 2,5 | 0.2295 | 1.4095 | 0.4 | 120 | 1.0095 | 0 | 2.63 | 1.6205 | 1.6205 | opened
242 | SS 35/10 Orekhovo | 2 х 2,5 | 0.44 | 0.19 | 120 | 0.25 | 0 | 2.63 | 2.38 | 2.38 | opened | 242 | SS 35/10 Orekhovo | 2 х 2,5 | 0.027 | 0.467 | 0.19 | 120 | 0.277 | 0 | 2.63 | 2.353 | 2.353 | opened
243 | SS 35/10 Orlovka | 2 х 2,5 | 0.23 | 0.52 | 120 | -0.29 | 0 | 2.63 | 2.92 | 2.92 | opened | 243 | SS 35/10 Orlovka | 2 х 2,5 | 0 | 0.23 | 0.52 | 120 | -0.29 | 0 | 2.63 | 2.92 | 2.92 | opened
244 | SS 35/10 Osotskoe | 2 х 2,5 | 0.25 | 0.2 | 120 | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened | 244 | SS 35/10 Osotskoe | 2 х 2,5 | 0 | 0.25 | 0.2 | 120 | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened
245 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.13 | 0.74 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | opened | 245 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.04 | 1.17 | 0.74 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened
246 | SS 35/10 Panino | 2 х 2,5 | 0.27 | 0.11 | 80 | 0.16 | 0 | 2.63 | 2.47 | 2.47 | opened | 246 | SS 35/10 Panino | 2 х 2,5 | 0.008 | 0.278 | 0.11 | 80 | 0.168 | 0 | 2.63 | 2.462 | 2.462 | opened
247 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.61 | 0.52 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened | 247 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.008 | 0.618 | 0.52 | 120 | 0.098 | 0 | 2.63 | 2.532 | 2.532 | opened
248 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.18 | 0.3 | 120 | 0.88 | 0 | 2.63 | 1.75 | 1.75 | opened | 248 | SS 35/10 Petrinka | 2,5 + 4,0 | 0 | 1.18 | 0.3 | 120 | 0.88 | 0 | 2.63 | 1.75 | 1.75 | opened
249 | SS 35/10 Platava | 2 х 2,5 | 0.86 | 0.26 | 120 | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 249 | SS 35/10 Platava | 2 х 2,5 | 0.012 | 0.872 | 0.26 | 120 | 0.612 | 0 | 2.63 | 2.018 | 2.018 | opened
250 | SS 35/10 Pogozhee | 2 х 1,6 | 0.21 | 0.46 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | opened | 250 | SS 35/10 Pogozhee | 2 х 1,6 | 0.012 | 0.222 | 0.46 | 120 | -0.238 | 0 | 1.68 | 1.918 | 1.918 | opened
251 | SS 35/10 Porechnoe | 2 х 4,0 | 0.53 | 1.16 | 120 | -0.63 | 0 | 4.2 | 4.83 | 4.83 | opened | 251 | SS 35/10 Porechnoe | 2 х 4,0 | 0 | 0.53 | 1.16 | 120 | -0.63 | 0 | 4.2 | 4.83 | 4.83 | opened
252 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened | 252 | SS 35/10 Pochepnoe | 2 х 6,3 | 0 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened
253 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.45 | 0.3 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened | 253 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.26 | 0.71 | 0.3 | 80 | 0.41 | 0 | 2.63 | 2.22 | 2.22 | opened
254 | SS 35/10 Pselets | 2 х 1,6 | 0.11 | 0.24 | 120 | -0.13 | 0 | 1.68 | 1.81 | 1.81 | opened | 254 | SS 35/10 Pselets | 2 х 1,6 | 0.0032 | 0.1132 | 0.24 | 120 | -0.1268 | 0 | 1.68 | 1.8068 | 1.8068 | opened
255 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.59 | 0.43 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened | 255 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.012 | 0.602 | 0.43 | 120 | 0.172 | 0 | 1.68 | 1.508 | 1.508 | opened
256 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.6 | 0.32 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 256 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.0238 | 0.6238 | 0.32 | 120 | 0.3038 | 0 | 2.625 | 2.3212 | 2.3212 | opened
257 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.54 | 0.44 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 257 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.0547 | 0.5947 | 0.44 | 120 | 0.1547 | 0 | 2.625 | 2.4703 | 2.4703 | opened
258 | SS 35/10 Razvetye | 2 х 4,0 | 1.35 | 1.03 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | opened | 258 | SS 35/10 Razvetye | 2 х 4,0 | 0.184 | 1.534 | 1.03 | 120 | 0.504 | 0 | 4.2 | 3.696 | 3.696 | opened
259 | SS 35/10 V. Reutets | 2 х 4,0 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | opened | 259 | SS 35/10 V. Reutets | 2 х 4,0 | 0 | 0.18 | 0.11 | 120 | 0.07 | 0 | 4.2 | 4.13 | 4.13 | opened
260 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 260 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.005 | 0.305 | 0.29 | 120 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | opened
261 | SS 35/10 Rubilnik | 2 х 2,5 | 1.4 | 1.18 | 80 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 261 | SS 35/10 Rubilnik | 2 х 2,5 | 0.016 | 1.416 | 1.18 | 80 | 0.236 | 0 | 2.625 | 2.389 | 2.389 | opened
262 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.28 | 0.08 | 20 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 262 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.0065 | 0.2865 | 0.08 | 20 | 0.2065 | 0 | 1.68 | 1.4735 | 1.4735 | opened
263 | SS 35/10 Sapogovo | 2 х 2,5 | 1.73 | 0.6 | 20 | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 263 | SS 35/10 Sapogovo | 2 х 2,5 | 0 | 1.73 | 0.6 | 20 | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened
264 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 3.65 | 2.25 | 80 | 1.4 | 0 | 6.615 | 5.215 | 5.215 | opened | 264 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 2.496 | 6.146 | 2.25 | 80 | 3.896 | 0 | 6.615 | 2.719 | 2.719 | opened
265 | SS 35/10 Selektsionnaya | 2 х 4,0 | 2.75 | 1.4 | 45 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 265 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.0145 | 2.7645 | 1.4 | 45 | 1.3645 | 0 | 4.2 | 2.8355 | 2.8355 | opened
266 | SS 35/10 Semyonovka | 2 х 2,5 | 0.29 | 0 | - | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened | 266 | SS 35/10 Semyonovka | 2 х 2,5 | 0.0003 | 0.2903 | 0 | - | 0.2903 | 0 | 2.625 | 2.3347 | 2.3347 | opened
267 | SS 35/10 Seed plant | 2 х 2,5 | 0.35 | 0.6 | 120 | -0.25 | 0 | 2.63 | 2.88 | 2.88 | opened | 267 | SS 35/10 Seed plant | 2 х 2,5 | 0.047 | 0.397 | 0.6 | 120 | -0.203 | 0 | 2.63 | 2.833 | 2.833 | opened
268 | SS 35/10 Snagost | 2 х 4,0 | 0.88 | 0.05 | 10 | 0.83 | 0 | 4.2 | 3.37 | 3.37 | opened | 268 | SS 35/10 Snagost | 2 х 4,0 | 0.012 | 0.892 | 0.05 | 10 | 0.842 | 0 | 4.2 | 3.358 | 3.358 | opened
269 | SS 35/10 SOM | 1,6 + 4,0 | 1.15 | 0.08 | 10 | 1.07 | 0 | 1.68 | 0.61 | 0.61 | opened | 269 | SS 35/10 SOM | 1,6 + 4,0 | 0.024 | 1.174 | 0.08 | 10 | 1.094 | 0 | 1.68 | 0.586 | 0.586 | opened
270 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.49 | 0.69 | 120 | -0.2 | 0 | 3.36 | 3.56 | 3.56 | opened | 270 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.08668 | 0.57668 | 0.69 | 120 | -0.11332 | 0 | 3.36 | 3.4733 | 3.4733 | opened
271 | SS 35/10 Stakanovo | 2 х 2,5 | 0.84 | 0.58 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened | 271 | SS 35/10 Stakanovo | 2 х 2,5 | 0 | 0.84 | 0.58 | 80 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | opened
272 | SS 35/10 Starkovo | 2 х 1,6 | 0.41 | 0.2 | 80 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 272 | SS 35/10 Starkovo | 2 х 1,6 | 0 | 0.41 | 0.2 | 80 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
273 | CC 35/10 Starshee | 2 х 1,6 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened | 273 | CC 35/10 Starshee | 2 х 1,6 | 0 | 0.24 | 0.2 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | opened
274 | SS 35/10 Teplitsy | 2 х 4,0 | 2.2 | 1.08 | 45 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | opened | 274 | SS 35/10 Teplitsy | 2 х 4,0 | 0.039 | 2.239 | 1.08 | 45 | 1.159 | 0 | 4.2 | 3.041 | 3.041 | opened
275 | SS 35/10 Turovka | 2 х 2,5 | 0.5 | 0.6 | 120 | -0.1 | 0 | 2.63 | 2.73 | 2.73 | opened | 275 | SS 35/10 Turovka | 2 х 2,5 | 0 | 0.5 | 0.6 | 120 | -0.1 | 0 | 2.63 | 2.73 | 2.73 | opened
276 | SS 35/10 Uspenka | 2 х 2,5 | 1.28 | 1 | 80 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened | 276 | SS 35/10 Uspenka | 2 х 2,5 | 0.005 | 1.285 | 1 | 80 | 0.285 | 0 | 2.63 | 2.345 | 2.345 | opened
277 | SS 35/6 Tsentralnaya | 2 х 25,0 | 27.41 | 5 | 10 | 22.41 | 0 | 26.25 | 3.84 | 3.84 | opened | 277 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0 | 27.41 | 5 | 10 | 22.41 | 0 | 26.25 | 3.84 | 3.84 | opened
278 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.3 | 0.5 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | opened | 278 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0 | 0.3 | 0.5 | 120 | -0.2 | 0 | 4.2 | 4.4 | 4.4 | opened
279 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.32 | 0.21 | 80 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 279 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.021 | 0.341 | 0.21 | 80 | 0.131 | 0 | 2.625 | 2.494 | 2.494 | opened
280 | SS 35/10 Shipy | 2 х 2,5 | 0.18 | 0.3 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | opened | 280 | SS 35/10 Shipy | 2 х 2,5 | 0 | 0.18 | 0.3 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | opened
281 | SS 35/10 Elevator | 4,0 + 6,3 | 1.7 | 0.6 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | opened | 281 | SS 35/10 Elevator | 4,0 + 6,3 | 0.025 | 1.725 | 0.6 | 120 | 1.125 | 0 | 4.2 | 3.075 | 3.075 | opened
282 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 8.46 | 4.7 | 80 | 3.76 | 0 | 10.5 | 6.74 | 6.74 | opened | 282 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 0 | 8.46 | 4.7 | 80 | 3.76 | 0 | 10.5 | 6.74 | 6.74 | opened
| TOTAL: | 3188.5 | 741.028 | 772.71 | [5 empty] | 1177.962 |  | 2: TOTAL:; 3: 3188.5; 4: 49.046; 5: 790.074; МVА 6: 772.71
| deficit | [8 empty] | 0 |  | 2: deficit; Min. 12: -6.2917
| proficit | [8 empty] | 1177.962 |  | 2: proficit; Min. 12: 1140.5309

## Орел
No. | Object of main substation, voltage class | Current deficit | [9 empty] | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit /proficit of main substation, MVA |  | Note |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc.; МVА for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 7 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
Production association Orlovskie power networks | [11 empty] | 1: Production association Orlovskie power networks
1 | SS 35/10 kv Almazovo | 2.5 | 0.33 | 0.83333 | 30 | 0.83333 | 0 | 0.83333 | 0.50333 | 0.50333 | opened | 1 | SS 35/10 kv Almazovo | 2.5 | 0.0058824 | 0.33588 | 0.83333 | 30 | 0.83333 | 0 | 0.83333 | 0.49745 | 0.49745 | opened
2 | SS 35/10 kv Voronets | 2.5 | 0.25 | 0.90909 | 90 | 0.90909 | 0 | 0.90909 | 0.65909 | 0.65909 | opened | 2 | SS 35/10 kv Voronets | 2.5 | 0 | 0.25 | 0.90909 | 90 | 0.90909 | 0 | 0.90909 | 0.65909 | 0.65909 | opened
3 | SS 35/10 kv Gostoml | 2.5 | 0.62 | 0.65854 | 120 | 0.65854 | 0 | 0.65854 | 0.038537 | 0.038537 | opened | 3 | SS 35/10 kv Gostoml | 2.5 | 0.017647 | 0.63765 | 0.65854 | 120 | 0.65854 | 0 | 0.65854 | 0.02089 | 0.02089 | opened
4 | SS 35/10 kv Gubkino | 3.2 | 0.51 | 1.5584 | 30 | 1.5584 | 0 | 1.5584 | 1.0484 | 1.0484 | opened | 4 | SS 35/10 kv Gubkino | 3.2 | 0 | 0.51 | 1.5584 | 30 | 1.5584 | 0 | 1.5584 | 1.0484 | 1.0484 | opened
5 | SS 35/10 kv Devyatino | 1.6 | 0.3 | 0.71429 | 45 | 0.71429 | 0 | 0.71429 | 0.41429 | 0.41429 | opened | 5 | SS 35/10 kv Devyatino | 1.6 | 0.011765 | 0.31176 | 0.71429 | 45 | 0.71429 | 0 | 0.71429 | 0.40252 | 0.40252 | opened
6 | SS 35/10 kv Kamenka | 2.5 | 0.61 | 0.62921 | 30 | 0.62921 | 0 | 0.62921 | 0.019213 | 0.019213 | opened | 6 | SS 35/10 kv Kamenka | 2.5 | 0 | 0.61 | 0.62921 | 30 | 0.62921 | 0 | 0.62921 | 0.019213 | 0.019213 | opened
7 | SS 35/10 kv Kozminskaya | 2.5 | 0.33 | 1.2941 | 45 | 1.2941 | 0 | 1.2941 | 0.96412 | 0.96412 | opened | 7 | SS 35/10 kv Kozminskaya | 2.5 | 0.0094118 | 0.33941 | 1.2941 | 45 | 1.2941 | 0 | 1.2941 | 0.95471 | 0.95471 | opened
8 | SS 110/35/10 kv Malorkhangelskaya | 10 | 4.26 | 6.1445 | 60 | 6.1445 | 0 | 6.1445 | 1.8845 | 1.88 | opened | 8 | SS 110/35/10 kv Malorkhangelskaya | 10 | 2.9588 | 7.2188 | 10.5536 | 60 | 10.5536 | 0 | 10.5536 | 3.3348 | 1 | opened
| Nom. capacity MV, MVA | 10 | 1.94 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0 |  | opened |  | Nom. capacity MV, MVA | 10 | 0 | 1.94 | 2.94 | 60 | 2.94 | 0 | 2.94 | 1 |  | opened
| Nom. capacity LV, MVA | 10 | 2.32 | 4.2045 | 60 | 4.2045 | 0 | 4.2045 | 1.8845 |  | opened |  | Nom. capacity LV, MVA | 10 | 2.9588 | 5.2788 | 7.6136 | 60 | 7.6136 | 0 | 7.6136 | 2.3348 |  | opened
9 | SS 110/35/10 kv Novopolevo | 16 | 3.87 | 3.7136 | 30 | 3.7136 | 0 | 3.7136 | -0.15636 | -0.16 | closed | 9 | SS 110/35/10 kv Novopolevo | 16+16 | 0.030588 | 3.9006 | 3.7136 | 30 | 20.5136 | 0 | 20.5136 | 16.613 | 16.613 | opened (installation of the second transformer)
| Nom. capacity MV, MVA | 16 | 2.6 | 2.6 | 30 | 2.6 | 0 | 2.6 | 0 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0 | 2.6 | 2.6 | 30 | 19.4 | 0 | 19.4 | 16.8
| Nom. capacity LV, MVA | 16 | 1.27 | 1.1136 | 30 | 1.1136 | 0 | 1.1136 | -0.15636 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.030588 | 1.3006 | 1.1136 | 30 | 17.9136 | 0 | 17.9136 | 16.613
10 | SS 35/10 kv Nikolskaya | 2.5 | 0.52 | 1.3253 | 45 | 1.3253 | 0 | 1.3253 | 0.8053 | 0.8053 | opened | 10 | SS 35/10 kv Nikolskaya | 2.5 | 0.0047059 | 0.52471 | 1.3253 | 45 | 1.3253 | 0 | 1.3253 | 0.8006 | 0.8006 | opened
11 | SS 35/10 kv Paramonovo | 1.8 | 0.28 | 0.48193 | 90 | 0.48193 | 0 | 0.48193 | 0.20193 | 0.20193 | opened | 11 | SS 35/10 kv Paramonovo | 1.8 | 0 | 0.28 | 0.48193 | 90 | 0.48193 | 0 | 0.48193 | 0.20193 | 0.20193 | opened
12 | SS 35/10 kv Senkovo | 1.6 | 0.29 | 1.2941 | 30 | 1.2941 | 0 | 1.2941 | 1.0041 | 1.0041 | opened | 12 | SS 35/10 kv Senkovo | 1.6 | 0.014118 | 0.30412 | 1.2941 | 30 | 1.2941 | 0 | 1.2941 | 0.99 | 0.99 | opened
13 | SS 35/10 kv Somovo | 2.5 | 0.27 | 0.96386 | 60 | 0.96386 | 0 | 0.96386 | 0.69386 | 0.69386 | opened | 13 | SS 35/10 kv Somovo | 2.5 | 0 | 0.27 | 0.96386 | 60 | 0.96386 | 0 | 0.96386 | 0.69386 | 0.69386 | opened
14 | SS 110/35/10 kv Trosna | 16 | 3.61 | 4.1621 | 45 | 4.1621 | 0 | 4.1621 | 0.55208 | 0.55 | opened | 14 | SS 110/35/10 kv Trosna | 16 | 0.021176 | 3.6312 | 4.1621 | 45 | 4.1621 | 0 | 4.1621 | 0.53091 | 0.53091 | opened
| Nom. capacity MV, MVA | 16 | 2.36 | 2.36 | 45 | 2.36 | 0 | 2.36 | 0 |  |  |  | Nom. capacity MV, MVA | 16 | 0 | 2.36 | 2.36 | 45 | 2.36 | 0 | 2.36 | 0 | 0
| Nom. capacity LV, MVA | 16 | 1.25 | 1.8021 | 45 | 1.8021 | 0 | 1.8021 | 0.55208 |  |  |  | Nom. capacity LV, MVA | 16 | 0.021176 | 1.2712 | 1.8021 | 45 | 1.8021 | 0 | 1.8021 | 0.53091 | 0.53091
15 | SS 35/10 kv Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | opened | 15 | SS 35/10 kv Shablykino | 5.6 | 0.0035294 | 0.10353 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.69647 | 0.69647 | opened
16 | SS 35/10 kv Yuryevo | 2.5 | 0.12 | 1.0732 | 60 | 1.0732 | 0 | 1.0732 | 0.95317 | 0.95317 | opened | 16 | SS 35/10 kv Yuryevo | 2.5 | 0 | 0.12 | 1.0732 | 60 | 1.0732 | 0 | 1.0732 | 0.95317 | 0.95317 | opened
| Total: | 75.8 | 16.27 | [8 empty] | 2: Total:; 3: 91.8; 4: 3.0776
| deficit | [8 empty] | -0.16 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 10.4354 |  | 2: proficit; Мin. 12: 26.6132
Production association Mtsenskie power networks | [11 empty] | 1: Production association Mtsenskie power networks
17 | SS 110/35/10 kv Region V | 10 | 4.04 | 5.3961 | 120 | 5.3961 | 0 | 5.3961 | 1.3561 | 1.36 | opened | 17 | SS 110/35/10 kv Region V | 10 | 0 | 4.04 | 5.3961 | 120 | 5.3961 | 0 | 5.3961 | 1.3561 | 0 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.3961 | 120 | 5.3961 | 0 | 5.3961 | 1.3561 |  |  |  | Nom. capacity LV, MVA | 10 | 0 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36
18 | SS 110/10 kv Pishchevaya | 6.3 | 2.45 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.575 | -0.575 | closed | 18 | SS 110/10 kv Pishchevaya | 6.3 | 2.3529 | 4.8029 | 7.7647 | 60 | 7.7647 | 0 | 7.7647 | 2.9618 | 2.9618 | opened ( at construction of HV line)
19 | SS 110/10 kv Telchye | 3.2 | 2.08 | 1.4607 | 120 | 1.4607 | 0 | 1.4607 | -0.61933 | -0.61933 | closed | 19 | SS 110/10 kv Telchye | 3.2 | 0.35647 | 2.4365 | 3.0337 | 120 | 3.0337 | 0 | 3.0337 | 0.59724 | 0.59724 | opened ( at construction of HV line)
20 | SS 110/10 kv B.Chern | 2.5 | 0.22 | 1 | 120 | 1 | 0 | 1 | 0.78 | 0.78 | opened | 20 | SS 110/10 kv B.Chern | 2.5 | 0.0023529 | 0.22235 | 1 | 120 | 1 | 0 | 1 | 0.77765 | 0.77765 | opened
21 | SS 35/10 kv Bashkatovo | 1.6 | 0.31 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.49 | 0.49 | opened | 21 | SS 35/10 kv Bashkatovo | 1.6 | 0.011765 | 0.32176 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.47824 | 0.47824 | opened
22 | SS 35/10 kv Vysokoe | 1.6 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | opened | 22 | SS 35/10 kv Vysokoe | 1.6 | 0 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | opened
23 | SS 35/10 kv Gladkoe | 2.5 | 0.27 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.19 | 1.19 | opened | 23 | SS 35/10 kv Gladkoe | 2.5 | 0 | 0.27 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.19 | 1.19 | opened
24 | SS 35/10 kv Lykovo | 2.5 | 0.7 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.54 | 0.54 | opened | 24 | SS 35/10 kv Lykovo | 2.5 | 0.043529 | 0.74353 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.49647 | 0.49647 | opened
25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened | 25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.27 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.41 | 0.41 | opened | 26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.0070588 | 0.27706 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.40294 | 0.40294 | opened
27 | SS 35/10 kv Koptevo | 2.5 | 0.22 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.22 | 0.22 | opened | 27 | SS 35/10 kv Koptevo | 2.5 | 0 | 0.22 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.22 | 0.22 | opened
| Total: | 38.3 | 10.74 | [8 empty] | 2: Total:; 3: 38.3; 4: 2.7741; 5: 13.5141
| deficit | [8 empty] | -1.1943 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 6.05 |  | 2: proficit; Мin. 12: 8.1843
Production association Livenskie power networks | [11 empty] | 2: Production association Livenskie power networks
28 | SS 110/35/10/6 kv Meat processing factory | 10 | 2.11 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.02 | 0.02 | opened | 28 | SS 110/35/10/6 kv Meat processing factory | 10 | 0.011765 | 2.1218 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.0082353 | 0.02 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 6.3 | 2.11 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.02 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.011765 | 2.1218 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.0082353
29 | SS 110/35/10 kv Shatilovo | 10 | 1.11 | 0.52969 | 120 | 0.52969 | 0 | 0.52969 | -0.58031 | -0.58 | closed | 29 | SS 110/35/10 kv Shatilovo | 10 | 0.016471 | 1.1265 | 1.16 | 120 | 1.16 | 0 | 1.16 | 0.033529 | 0.013529 | opened (construction of HV line)
| Nom. capacity MV, MVA | 10 | 0.48 | 0.16 | 180 | 0.16 | 0 | 0 | -0.48 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.48 | 0.5 | 180 | 0.5 | 0 | 0.5 | 0.02
| Nom. capacity LV, MVA | 10 | 0.63 | 0.52969 | 120 | 0.52969 | 0 | 0.53 | -0.1 |  |  |  | Nom. capacity LV, MVA | 10 | 0.016471 | 0.64647 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.013529
30 | SS 110/35/10 kv Sovkhoznaya | 10 | 5.23 | 6.66 | 120 | 6.66 | 0 | 6.66 | 1.43 | 1.43 | opened | 30 | SS 110/35/10 kv Sovkhoznaya | 10 | 0.082353 | 5.3124 | 6.66 | 120 | 6.66 | 0 | 6.66 | 1.3476 | 1.43 | opened
| Nom. capacity MV, MVA | 10 | 4.32 | 4.32 | 120 | 4.32 | 0 | 4.32 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 4.32 | 4.32 | 120 | 4.32 | 0 | 4.32 | 0
| Nom. capacity LV, MVA | 10 | 0.91 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.43 |  |  |  | Nom. capacity LV, MVA | 10 | 0.082353 | 0.99235 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.43
31 | SS 35/10 kv Danilovskaya | 1.6 | 0.11 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.43 | 0.43 | opened | 31 | SS 35/10 kv Danilovskaya | 1.6 | 0 | 0.11 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.43 | 0.43 | opened
32 | SS 35/10 kv Korseevo | 1.8 | 0.07 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.81 | 0.81 | opened | 32 | SS 35/10 kv Korseevo | 1.8 | 0 | 0.07 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.81 | 0.81 | opened
33 | SS 35/10 kv Lipovets | 2.5 | 0.66 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.73 | 0.73 | opened | 33 | SS 35/10 kv Lipovets | 2.5 | 0 | 0.66 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.73 | 0.73 | opened
34 | SS 35/10 kv Misaylovo | 1.6 | 0.32 | 0 | - | 0 | 0 | 0 | -0.32 | -0.32 | closed | 34 | SS 35/10 kv Misaylovo | 1,6+(2,5) | 0.0044706 | 0.32447 | 0 | - | 1.12 | 0 | 1.12 | 0.79553 | 0.79553 | opened
35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.25 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.06 | 0.06 | opened | 35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.0094118 | 0.25941 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.050588 | 0.06 | opened
36 | SS 35/10 kv Pankovo | 1.8 | 0.48 | 0.16 | 120 | 0.16 | 0 | 0.16 | -0.32 | -0.32 | closed | 36 | SS 35/10 kv Pankovo | 1,8+(2,5) | 0 | 0.48 | 0.16 | 120 | 1.42 | 0 | 1.42 | 0.94 | 0.94 | opened
37 | SS 35/10 kv SSK | 1.6 | 0.1 | 0 | - | 0 | 0 | 0 | -0.1 | -0.1 | closed | 37 | SS 35/10 kv SSK | 1,6+(2,5) | 0 | 0.1 | 0 | - | 1.12 | 0 | 1.12 | 1.02 | 1.02 | opened
38 | SS 35/10 kv Sudbishchi | 2.5 | 0.54 | 0.36 | 120 | 0.36 | 0 | 0.36 | -0.18 | -0.18 | closed | 38 | SS 35/10 kv Sudbishchi | 2,5+(2,5) | 0.034118 | 0.57412 | 0.36 | 120 | 2.11 | 0 | 2.11 | 1.5359 | 1.5359 | opened
39 | SS 35/10 kv Tim | 1.6 | 0.6 | 0.43 | 120 | 0.43 | 0 | 0.43 | -0.17 | -0.17 | closed | 39 | SS 35/10 kv Tim | 1,6+(2,5) | 0.012941 | 0.61294 | 0.43 | 120 | 1.55 | 0 | 1.55 | 0.93706 | 0.93706 | opened
40 | SS 35/10 kv Topki | 1 | 0.3 | 0.16 | 120 | 0.16 | 0 | 0.16 | -0.14 | -0.14 | closed | 40 | SS 35/10 kv Topki | 1+(2,5) | 0.0058824 | 0.30588 | 0.16 | 120 | 0.86 | 0 | 0.86 | 0.55412 | 0.55412 | opened
41 | SS 35/10 kv Yarishche | 2.5 | 0.37 | 0.17 | 120 | 0.17 | 0 | 0.17 | -0.2 | -0.2 | closed | 41 | SS 35/10 kv Yarishche | 2,5+(2,5) | 0.028 | 0.398 | 0.17 | 120 | 1.92 | 0 | 1.92 | 1.522 | 1.522 | opened
| Total: | 51 | 12.25 | [8 empty] | 2: Total:; 3: 51; 4: 0.20541
| deficit | [8 empty] | -2.01 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 3.48 |  | 2: proficit; Мin. 12: 10.7981
Two- and more transformer substations | [11 empty] | 2: Two- and more transformer substations
Production association Orlovskie power networks | [11 empty] | 2: Production association Orlovskie power networks
42 | SS 110/10 kv Alshanskaya | 10+10 | 4.45 | 3.8824 | 30 | 0.56765 | 0 | 10.5 | 9.9324 | 9.9324 | opened | 42 | SS 110/10 kv Alshanskaya | 10+10 | 0.14588 | 4.5959 | 3.8824 | 30 | 0.71353 | 0 | 10.5 | 9.7865 | 9.7865 | opened
43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.52 | 0.93023 | 90 | -0.41023 | 0 | 2.625 | 3.0352 | 3.0352 | opened | 43 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.022353 | 0.54235 | 0.93023 | 90 | -0.38788 | 0 | 2.625 | 3.0129 | 3.0129 | opened
44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.73 | 0 | - | 0.73 | 0 | 1.68 | 0.95 | 0.95 | opened | 44 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0 | 0.73 | 0 | - | 0.73 | 0 | 1.68 | 0.95 | 0.95 | opened
45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.61 | 3.0629 | 90 | -0.45291 | 0 | 10.5 | 10.9529 | 8.07 | opened | 45 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 0 | 2.61 | 3.0629 | 90 | -0.45291 | 0 | 10.5 | 10.9529 | 8.07 | opened
| Nom. capacity MV, MVA | 10+10 | 2.43 | 2.43 | 90 | 0 |  | 10.5 | 8.07 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.43 | 2.43 | 90 | 0 | 0 | 10.5 | 8.07
| Nom. capacity LV, MVA | 10+10 | 0.18 | 0.63291 | 90 | -0.45291 |  | 10.5 | 10.9529 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 0.18 | 0.63291 | 90 | -0.45291 | 0 | 10.5 | 10.9529
46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.86 | 0.63636 | 60 | 0.22364 | 0 | 1.68 | 1.4564 | 1.4564 | opened | 46 | SS 35/10 kv Baklanovo | 1,6+1,6 | 0.011765 | 0.87176 | 0.63636 | 60 | 0.2354 | 0 | 1.68 | 1.4446 | 1.4446 | opened
47 | SS 35/10 kv Biofactory | 6,3+6,3 | 2.22 | 2.0455 | 90 | 0.17455 | 0 | 6.615 | 6.4405 | 6.4405 | opened | 47 | SS 35/10 kv Biofactory | 6,3+6,3 | 0.28824 | 2.5082 | 2.0455 | 90 | 0.46278 | 0 | 6.615 | 6.1522 | 6.1522 | opened
48 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.89 | 1.4607 | 30 | 2.4293 | 0 | 2.625 | 0.19567 | 0.19567 | opened | 48 | SS 110/10 kv Volodarskaya | 6,3+6,3 | 4.0376 | 7.9276 | 1.4607 | 30 | 6.467 | 0 | 6.615 | 0.14803 | 0.14803 | opened
49 | SS 110/10 kv Vostochnaya | 15+15 | 14.1 | 5.8696 | 120 | 8.2304 | 0 | 15.75 | 7.5196 | 7.5196 | opened | 49 | SS 110/10 kv Vostochnaya | 15+15 | 0.29412 | 14.3941 | 5.8696 | 120 | 8.5246 | 0 | 15.75 | 7.2254 | 7.2254 | opened
50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 3.49 | 0.45455 | 60 | 3.0355 | 0 | 10.5 | 7.4645 | 7.4645 | opened | 50 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 0.056471 | 3.49 | 0.45455 | 60 | 3.0355 | 0 | 10.5 | 7.4645 | 7.4645 | opened
| Nom. capacity MV, MVA | 10+10 | 0.3 | 0 | 0 | 0.3 |  | 10.5 | 10.2 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.3 | 0 | 0 | 0.3 | 0 | 10.5 | 10.2
| Nom. capacity LV, MVA | 10+10 | 3.19 | 0.45455 | 60 | 2.7355 |  | 10.5 | 7.7645 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 3.19 | 0.45455 | 60 | 2.7355 | 0 | 10.5 | 7.7645
51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 11.89 | 3.9785 | 180 | 7.9115 | 0 | 16.8 | 8.8885 | 8.8885 | opened | 51 | SS 110/10 kv Zheleznodorozhnaya | 16+16 | 0.31294 | 12.2029 | 3.9785 | 180 | 8.2244 | 0 | 16.8 | 8.5756 | 8.5756 | opened
52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 1.08 | 0.64368 | 60 | 0.43632 | 0 | 1.89 | 1.4537 | 1.4537 | opened | 52 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 0.017647 | 1.0976 | 0.64368 | 60 | 0.45397 | 0 | 1.89 | 1.436 | 1.436 | opened
53 | SS 110/6 kv Zavodskaya | 40+25 | 11.48 | 4.3913 | 150 | 7.0887 | 0 | 26.25 | 19.1613 | 19.1613 | opened | 53 | SS 110/6 kv Zavodskaya | 40+25 | 5.4118 | 16.8918 | 4.3913 | 150 | 12.5005 | 0 | 26.25 | 13.7495 | 13.7495 | opened
54 | SS 110/6 kv Zapadnaya | 25+25 | 26.59 | 0 | 120 | 26.59 | 0 | 26.25 | -0.34 | -0.34 | closed | 54 | SS 110/6 kv Zapadnaya | 63+63 | 19.1176 | 45.7076 | 5.3684 | 120 | 40.3392 | 0 | 66.15 | 25.8108 | 25.8108 | opened
55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 1.81 | 1.4815 | 60 | 0.32852 | 0 | 2.625 | 2.2965 | 2.2965 | opened | 55 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 0.32588 | 2.1359 | 1.4815 | 60 | 0.6544 | 0 | 2.625 | 1.9706 | 1.9706 | opened
56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 1.06 | 1.1828 | 30 | -0.1228 | 0 | 1.68 | 1.8028 | 1.8028 | opened | 56 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 0.029412 | 1.0894 | 1.1828 | 30 | -0.093384 | 0 | 1.68 | 1.7734 | 1.7734 | opened
57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 6.85 | 1.4396 | 90 | 5.4104 | 0 | 10.5 | 5.0896 | 5.0896 | opened | 57 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.1553 | 6.85 | 1.4396 | 90 | 5.4104 | 0 | 10.5 | 5.0896 | 5.0896 | opened
| Nom. capacity MV, MVA | 10+10 | 3.58 | 1 | 90 | 2.58 |  | 10.5 | 6.92 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 3.58 | 1 | 90 | 2.58 | 0 | 10.5 | 6.92
| Nom. capacity LV, MVA | 10+10 | 3.27 | 0.43956 | 90 | 2.8304 |  | 10.5 | 7.6696 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 3.27 | 0.43956 | 90 | 2.8304 | 0 | 10.5 | 7.6696
58 | SS 110/35/10 kv Kromskaya | 16+16 | 8.4 | 6.828 | 45 | 1.572 | 0 | 16.8 | 15.228 | 11.8 | opened | 58 | SS 110/35/10 kv Kromskaya | 16+16 | 0.044706 | 8.4 | 6.828 | 45 | 1.572 | 0 | 16.8 | 15.228 | 11.8 | opened
| Nom. capacity MV, MVA | 16+16 | 5 | 5 | 45 | 0 |  | 16.8 | 11.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0 | 5 | 5 | 45 | 0 | 0 | 16.8 | 11.8
| Nom. capacity LV, MVA | 16+16 | 3.4 | 1.828 | 45 | 1.572 |  | 16.8 | 15.228 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 3.4 | 1.828 | 45 | 1.572 | 0 | 16.8 | 15.228
59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 1.15 | 0.95238 | 30 | 0.19762 | 0 | 2.625 | 2.4274 | 2.4274 | opened | 59 | SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 0.055294 | 1.2053 | 0.95238 | 30 | 0.25291 | 0 | 2.625 | 2.3721 | 2.3721 | opened
60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | opened | 60 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.012941 | 0.71294 | 0 | - | 0.71294 | 0 | 1.68 | 0.96706 | 0.96706 | opened
61 | SS 35/10 kv Kutafino | 1,6+1,6 | 0.57 | 0.83333 | 30 | -0.26333 | 0 | 1.68 | 1.9433 | 1.9433 | opened | 61 | SS 35/10 kv Kutafino | 6,3+6,3 | 6.0647 | 6.6347 | 0.83333 | 30 | 5.8014 | 0 | 6.615 | 0.81363 | 0.81363 | opened
62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.69 | 1.5909 | 30 | -0.90091 | 0 | 2.625 | 3.5259 | 3.5259 | opened | 62 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.015294 | 0.70529 | 1.5909 | 30 | -0.88561 | 0 | 2.625 | 3.5106 | 3.5106 | opened
63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.44 | 0.46512 | 60 | -0.025116 | 0 | 1.05 | 1.0751 | 1.0751 | opened | 63 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0 | 0.44 | 0.46512 | 60 | -0.025116 | 0 | 1.05 | 1.0751 | 1.0751 | opened
64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.41 | 0.98765 | 90 | -0.57765 | 0 | 1.89 | 2.4677 | 2.4677 | opened | 64 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.0070588 | 0.41706 | 0.98765 | 90 | -0.5706 | 0 | 1.89 | 2.4606 | 2.4606 | opened
65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.41 | 1.7045 | 30 | -1.2945 | 0 | 5.88 | 7.1745 | 7.1745 | opened | 65 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0 | 0.41 | 1.7045 | 30 | -1.2945 | 0 | 5.88 | 7.1745 | 7.1745 | opened
64 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 6.89 | 1.4055 | 90 | 5.4845 | 0 | 10.5 | 5.0155 | 5.0155 | opened | 64 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 0.43882 | 6.89 | 1.4055 | 90 | 5.4845 | 0 | 10.5 | 5.0155 | 5.0155 | opened
| Nom. capacity MV, MVA | 10+10 | 0.86 | 0.86 | 90 | 0 |  | 10.5 | 9.64 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.86 | 0.86 | 90 | 0 | 0 | 10.5 | 9.64
| Nom. capacity LV, MVA | 10+10 | 6.03 | 0.54545 | 90 | 5.4845 |  | 10.5 | 5.0155 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 6.03 | 0.54545 | 90 | 5.4845 | 0 | 10.5 | 5.0155
65 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.93 | 1.6292 | 45 | -0.69921 | 0 | 2.625 | 3.3242 | 3.3242 | opened | 65 | SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.0070588 | 0.93706 | 1.6292 | 45 | -0.69215 | 0 | 2.625 | 3.3172 | 3.3172 | opened
66 | SS 35/10 kv N.Petrovka | 2,5+1,6 | 0.57 | 0.72727 | 60 | -0.15727 | 0 | 1.68 | 1.8373 | 1.8373 | opened | 66 | SS 35/10 kv N.Petrovka | 2,5+1,6 | 0 | 0.57 | 0.72727 | 60 | -0.15727 | 0 | 1.68 | 1.8373 | 1.8373 | opened
67 | SS 35/10 kv Putimets | 2,5+2,5 | 0.39 | 1.5281 | 90 | -1.1381 | 0 | 2.625 | 3.7631 | 3.7631 | opened | 67 | SS 35/10 kv Putimets | 2,5+2,5 | 0.0047059 | 0.39471 | 1.5281 | 90 | -1.1334 | 0 | 2.625 | 3.7584 | 3.7584 | opened
68 | SS 110/10 kv Pishchevaya | 40+25 | 6.42 | 2.2222 | 60 | 4.1978 | 0 | 26.25 | 22.0522 | 22.0522 | opened | 68 | SS 110/10 kv Pishchevaya | 40+25 | 1.2718 | 7.6918 | 2.2222 | 60 | 5.4695 | 0 | 26.25 | 20.7805 | 20.7805 | opened
69 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.44 | 0.65116 | 90 | -0.21116 | 0 | 2.625 | 2.8362 | 2.8362 | opened | 69 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0 | 0.44 | 0.65116 | 90 | -0.21116 | 0 | 2.625 | 2.8362 | 2.8362 | opened
68 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 3.94 | 1.9782 | 45 | 1.9618 | 0 | 10.5 | 8.5382 | 8.5382 | opened | 68 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 0.24235 | 3.94 | 1.9782 | 45 | 1.9618 | 0 | 10.5 | 8.5382 | 8.5382 | opened
| Nom. capacity MV, MVA | 10+10 | 1.41 | 1.41 | 45 | 0 |  | 10.5 | 9.09 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.41 | 1.41 | 45 | 0 | 0 | 10.5 | 9.09
| Nom. capacity LV, MVA | 10+10 | 2.53 | 0.56818 | 45 | 1.9618 |  | 10.5 | 8.5382 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.53 | 0.56818 | 45 | 1.9618 | 0 | 10.5 | 8.5382
69 | SS 35/10 kv Streletskaya | 4+4 | 2.33 | 0.90909 | 90 | 1.4209 | 0 | 4.2 | 2.7791 | 2.7791 | opened | 69 | SS 35/10 kv Streletskaya | 4+4 | 0.034706 | 2.3647 | 0.90909 | 90 | 1.4556 | 0 | 4.2 | 2.7444 | 2.7444 | opened
70 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 28.03 | 3.8617 | 180 | 24.1683 | 0 | 68.25 | 44.0817 | 44.0817 | opened | 70 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 2.8941 | 30.9241 | 3.8617 | 180 | 27.0624 | 0 | 68.25 | 41.1876 | 41.1876 | opened
71 | SS 35/10 kv Soskovskaya | 4+3,2 | 1.25 | 0.63636 | 90 | 0.61364 | 0 | 3.36 | 2.7464 | 2.7464 | opened | 71 | SS 35/10 kv Soskovskaya | 4+3,2 | 0.018824 | 1.2688 | 0.63636 | 90 | 0.63246 | 0 | 3.36 | 2.7275 | 2.7275 | opened
72 | SS 35/10 kv Trosna | 5,6+3,2 | 0.98 | 1.7582 | 30 | -0.77824 | 0 | 3.36 | 4.1382 | 4.1382 | opened | 72 | SS 35/10 kv Trosna | 5,6+3,2 | 0.011765 | 0.99176 | 1.7582 | 30 | -0.76648 | 0 | 3.36 | 4.1265 | 4.1265 | opened
73 | SS 110/10 kv Khimmash | 25+25 | 5.6 | 1.5054 | 120 | 4.0946 | 0 | 26.25 | 22.1554 | 22.1554 | opened | 73 | SS 110/10 kv Khimmash | 25+25 | 7.3871 | 12.9871 | 1.5054 | 120 | 11.4817 | 0 | 26.25 | 14.7683 | 14.7683 | opened
74 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0.93 | 0 | - | 0.93 | 0 | 5.88 | 4.95 | 4.95 | opened | 74 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 0 | 0.93 | 0 | - | 0.93 | 0 | 5.88 | 4.95 | 4.95 | opened
75 | SS 35/10 kv Khotynetskaya | 4+2,5 | 2.31 | 1.4943 | 80 | 0.81575 | 0 | 2.625 | 1.8093 | 1.8093 | opened | 75 | SS 35/10 kv Khotynetskaya | 4+2,5 | 0.036471 | 2.3465 | 1.4943 | 80 | 0.85222 | 0 | 2.625 | 1.7728 | 1.7728 | opened
76 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.55 | 1.0256 | 80 | -0.47564 | 0 | 1.68 | 2.1556 | 2.1556 | opened | 76 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.0047059 | 0.55471 | 1.0256 | 80 | -0.47094 | 0 | 1.68 | 2.1509 | 2.1509 | opened
77 | SS 110/10/6 kv Tsentralnaya | 25+25 | 14.12 | 3.4632 | 135 | 10.6568 | 0 | 26.25 | 15.5932 | 15.5932 | opened | 77 | SS 110/10/6 kv Tsentralnaya | 25+25 | 0 | 14.12 | 3.4632 | 135 | 10.6568 | 0 | 26.25 | 15.5932 | 15.5932 | opened
76 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 2.5 | 1.3635 | 30 | 1.1365 | 0 | 6.615 | 5.4785 | 5.4785 | opened | 76 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 0.014118 | 2.5 | 1.3635 | 30 | 1.1365 | 0 | 6.615 | 5.4785 | 5.4785 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 0.81 | 0.54 | 30 | 0.27 |  | 6.615 | 5.805 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0.81 | 0.54 | 30 | 0.27 | 0 | 6.615 | 5.805
| Nom. capacity LV, MVA | 6,3+6,3 | 1.69 | 0.82353 | 30 | 0.86647 |  | 6.615 | 5.7485 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 1.69 | 0.82353 | 30 | 0.86647 | 0 | 6.615 | 5.7485
77 | SS 110/35/10 kv Shakhovo | 10+10 | 2.12 | 2.5491 | 120 | -0.42909 | 0 | 10.5 | 10.9291 | 10.11 | opened | 77 | SS 110/35/10 kv Shakhovo | 10+10 | 0.45294 | 2.12 | 2.5491 | 120 | -0.42909 | 0 | 10.5 | 10.9291 | 10.11 | opened
| Nom. capacity MV, MVA | 10+10 | 0.39 | 0.39 | 120 | 0 |  | 10.5 | 10.11 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.39 | 0.39 | 120 | 0 | 0 | 10.5 | 10.11
| Nom. capacity LV, MVA | 10+10 | 1.73 | 2.1591 | 120 | -0.42909 |  | 10.5 | 10.9291 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 1.73 | 2.1591 | 120 | -0.42909 | 0 | 10.5 | 10.9291
78 | SS 35/10 kv Shepino | 2,5+1,6 | 1.57 | 1.0989 | 120 | 0.4711 | 0 | 1.68 | 1.2089 | 1.2089 | opened | 78 | SS 35/10 kv Shepino | 2,5+1,6 | 0.054118 | 1.6241 | 1.0989 | 120 | 0.52522 | 0 | 1.68 | 1.1548 | 1.1548 | opened
79 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 8.59 | 0.7449 | 60 | 7.8451 | 0 | 26.25 | 18.4049 | 18.4049 | opened | 79 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 0 | 8.59 | 0.7449 | 60 | 7.8451 | 0 | 26.25 | 18.4049 | 18.4049 | opened
80 | SS 110/10 kv Yuzhnaya | 10+10 | 5.86 | 1.0518 | 90 | 4.8082 | 0 | 10.5 | 5.6918 | 5.6918 | opened | 80 | SS 110/10 kv Yuzhnaya | 10+10 | 1.6976 | 7.5576 | 1.0518 | 90 | 6.5059 | 0 | 10.5 | 3.9941 | 3.9941 | opened
| Total: | 785.3 | 202.72 | [8 empty] | 2: Total:; 3: 859.5; 4: 49.5935
| deficit | [8 empty] | -0.34 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 303.82 |  | 2: proficit; Мin. 12: 308.0799
Production association Mtsenskie power networks | [11 empty] | 2: Production association Mtsenskie power networks
81 | SS 220/110/10 kv Mtsensk | 40+40 | 9.73 | 0 | - | 9.73 | 0 | 42 | 32.27 | 32.27 | opened | 81 | SS 220/110/10 kv Mtsensk | 40+40 | 0.063529 | 9.7935 | 0 | - | 9.7935 | 0 | 42 | 32.2065 | 32.2065 | opened
82 | SS 110/35/10 kv Kommash | 10+16 | 9.42 | 4.6512 | 90 | 4.7688 | 0 | 10.5 | 5.7312 | 5.7312 | opened | 82 | SS 110/35/10 kv Kommash | 16+16 | 0.056471 | 9.4765 | 4.6512 | 90 | 4.8253 | 0 | 16.8 | 11.9747 | 11.9747 | opened
82 | Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  | 82 | Nom. capacity MV, MVA | 16+16 | 0 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8
83 | Nom. capacity LV, MVA | 10+16 | 9.42 | 4.6512 | 90 | 4.7688 | 0 | 10.5 | 5.7312 |  |  | 83 | Nom. capacity LV, MVA | 16+16 | 0.056471 | 9.4765 | 4.6512 | 90 | 4.8253 | 0 | 16.8 | 11.9747
83 | SS 110/35/10 kv Novosergievka | 6,3+10 | 2.57 | 4.1284 | 120 | -1.5584 | 0 | 6.615 | 8.1734 | 4.215 | opened | 83 | SS 110/35/10 kv Novosergievka | 6,3+10 | 0 | 2.57 | 4.1284 | 120 | -1.5584 | 0 | 6.615 | 8.1734 | 4.215 | opened
84 | Nom. capacity MV, MVA | 6,3+10 | 2.4 | 2.4 | 120 | 0 | 0 | 6.615 | 4.215 |  |  | 84 | Nom. capacity MV, MVA | 6,3+10 | 0 | 2.4 | 2.4 | 120 | 0 | 0 | 6.615 | 4.215
84 | Nom. capacity LV, MVA | 6,3+10 | 0.17 | 1.7284 | 120 | -1.5584 | 0 | 6.615 | 8.1734 |  |  | 84 | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.17 | 1.7284 | 120 | -1.5584 | 0 | 6.615 | 8.1734
84 | SS 110/10 kv 1 Voin | 6,3+6,3 | 0.98 | 1.828 | 120 | -0.84796 | 0 | 6.615 | 7.463 | 7.463 | opened | 84 | SS 110/10 kv 1 Voin | 6,3+6,3 | 0.0082353 | 0.98824 | 1.828 | 120 | -0.83972 | 0 | 6.615 | 7.4547 | 7.4547 | opened
85 | SS 110/35/10 kv Zalegoshch | 10+16 | 5.31 | 3.9456 | 120 | 1.3644 | 0 | 10.5 | 9.1356 | 8.11 | opened | 85 | SS 110/35/10 kv Zalegoshch | 16+16 | 0.04 | 5.35 | 3.9456 | 120 | 1.4044 | 0 | 16.8 | 15.3956 | 14.41 | opened
85 | Nom. capacity MV, MVA | 10+16 | 2.39 | 2.39 | 120 | 0 | 0 | 10.5 | 8.11 |  |  | 85 | Nom. capacity MV, MVA | 16+16 | 0 | 2.39 | 2.39 | 120 | 0 | 0 | 16.8 | 14.41
86 | Nom. capacity LV, MVA | 10+16 | 2.92 | 1.5556 | 120 | 1.3644 | 0 | 10.5 | 9.1356 |  |  | 86 | Nom. capacity LV, MVA | 16+16 | 0.04 | 2.96 | 1.5556 | 120 | 1.4044 | 0 | 16.8 | 15.3956
86 | SS 110/10 kv Kochety | 2,5+2,5 | 0.46 | 0.65934 | 120 | -0.19934 | 0 | 2.625 | 2.8243 | 2.8243 | opened | 86 | SS 110/10 kv Kochety | 2,5+2,5 | 0 | 0.46 | 0.65934 | 120 | -0.19934 | 0 | 2.625 | 2.8243 | 2.8243 | opened
87 | SS 110/35/10 kv Bolkhov | 10+10 | 7.33 | 4.0971 | 120 | 3.2329 | 0 | 10.5 | 7.2671 | 7.2671 | opened | 87 | SS 110/35/10 kv Bolkhov | 10+10 | 0.0094118 | 7.3394 | 4.0971 | 120 | 3.2424 | 0 | 10.5 | 7.2576 | 7.2576 | opened
87 | Nom. capacity MV, MVA | 10+10 | 2.45 | 2.45 | 120 | 0 | 0 | 10.5 | 8.05 |  |  | 87 | Nom. capacity MV, MVA | 10+10 | 0 | 2.45 | 2.45 | 120 | 0 | 0 | 10.5 | 8.05
88 | Nom. capacity LV, MVA | 10+10 | 4.88 | 1.6471 | 120 | 3.2329 | 0 | 10.5 | 7.2671 |  |  | 88 | Nom. capacity LV, MVA | 10+10 | 0.0094118 | 4.8894 | 1.6471 | 120 | 3.2424 | 0 | 10.5 | 7.2576
88 | SS 110/35/10 kv Novosil | 10+10 | 3.45 | 2.9817 | 120 | 0.46826 | 0 | 10.5 | 10.0317 | 9.04 | opened | 88 | SS 110/35/10 kv Novosil | 10+10 | 0.0076471 | 3.4576 | 2.9817 | 120 | 0.47591 | 0 | 10.5 | 10.0241 | 9.04 | opened
89 | Nom. capacity MV, MVA | 10+10 | 1.46 | 1.46 | 120 | 0 | 0 | 10.5 | 9.04 |  |  | 89 | Nom. capacity MV, MVA | 10+10 | 0 | 1.46 | 1.46 | 120 | 0 | 0 | 10.5 | 9.04
89 | Nom. capacity LV, MVA | 10+10 | 1.99 | 1.5217 | 120 | 0.46826 | 0 | 10.5 | 10.0317 |  |  | 89 | Nom. capacity LV, MVA | 10+10 | 0.0076471 | 1.9976 | 1.5217 | 120 | 0.47591 | 0 | 10.5 | 10.0241
89 | SS 110/35/10 kv Znamenskaya | 10+10 | 1.56 | 1.7833 | 120 | -0.2233 | 0 | 10.5 | 10.7233 | 10.16 | opened | 89 | SS 110/35/10 kv Znamenskaya | 10+10 | 0.031765 | 1.5918 | 1.7833 | 120 | -0.19153 | 0 | 10.5 | 10.6915 | 10.16 | opened
90 | Nom. capacity MV, MVA | 10+10 | 0.34 | 0.34 | 120 | 0 | 0 | 10.5 | 10.16 |  |  | 90 | Nom. capacity MV, MVA | 10+10 | 0 | 0.34 | 0.34 | 120 | 0 | 0 | 10.5 | 10.16
90 | Nom. capacity LV, MVA | 10+10 | 1.22 | 1.4433 | 120 | -0.2233 | 0 | 10.5 | 10.7233 |  |  | 90 | Nom. capacity LV, MVA | 10+10 | 0.031765 | 1.2518 | 1.4433 | 120 | -0.19153 | 0 | 10.5 | 10.6915
90 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0.48 | 0.47619 | 120 | 0.0038095 | 0 | 1.89 | 1.8862 | 1.8862 | opened | 90 | SS 35/10 kv Apalkovo | 1,8+1,8 | 0 | 0.48 | 0.47619 | 120 | 0.0038095 | 0 | 1.89 | 1.8862 | 1.8862 | opened
91 | SS 35/10 kv Podberyozovo | 4+1 | 0.23 | 0.59302 | 120 | -0.36302 | 0 | 1.05 | 1.413 | 1.413 | opened | 91 | SS 35/10 kv Podberyozovo | 4+1 | 0 | 0.23 | 0.59302 | 120 | -0.36302 | 0 | 1.05 | 1.413 | 1.413 | opened
92 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.5 | 0 | - | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 92 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.018824 | 0.51882 | 0 | - | 0.51882 | 0 | 1.68 | 1.1612 | 1.1612 | opened
93 | SS 35/10 kv Alyoshnya | 1+1 | 0.44 | 0.2439 | 120 | 0.1961 | 0 | 1.05 | 0.8539 | 0.8539 | opened | 93 | SS 35/10 kv Alyoshnya | 1+1 | 0.0035294 | 0.44353 | 0.2439 | 120 | 0.19963 | 0 | 1.05 | 0.85037 | 0.85037 | opened
94 | SS 35/10 kv Lomovoe | 2,5+2,5 | 1.03 | 0 | - | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 94 | SS 35/10 kv Lomovoe | 2,5+2,5 | 0 | 1.03 | 0 | - | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened
95 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.72 | 0.625 | 120 | 0.095 | 0 | 2.625 | 2.53 | 2.53 | opened | 95 | SS 35/10 kv Mokhovoe | 2,5+4 | 0 | 0.72 | 0.625 | 120 | 0.095 | 0 | 2.625 | 2.53 | 2.53 | opened
96 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.22 | 0.47059 | 120 | -0.25059 | 0 | 1.68 | 1.9306 | 1.9306 | opened | 96 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.0035294 | 0.22353 | 0.47059 | 120 | -0.24706 | 0 | 1.68 | 1.9271 | 1.9271 | opened
97 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.17 | 0 | - | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 97 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.0035294 | 0.17353 | 0 | - | 0.17353 | 0 | 2.625 | 2.4515 | 2.4515 | opened
98 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.69 | 0.67416 | 120 | 0.015843 | 0 | 2.625 | 2.6092 | 2.6092 | opened | 98 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 0.021176 | 0.71118 | 0.67416 | 120 | 0.037019 | 0 | 2.625 | 2.588 | 2.588 | opened
99 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.43 | 0.36585 | 120 | 0.064146 | 0 | 1.68 | 1.6159 | 1.6159 | opened | 99 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.0011765 | 0.43118 | 0.36585 | 120 | 0.065323 | 0 | 1.68 | 1.6147 | 1.6147 | opened
100 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.32 | 0.68966 | 120 | -0.36966 | 0 | 2.625 | 2.9947 | 2.9947 | opened | 100 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.024706 | 0.34471 | 0.68966 | 120 | -0.34495 | 0 | 2.625 | 2.9699 | 2.9699 | opened
101 | SS 35/10 kv Odinok | 1,6+1,6 | 0.44 | 0 | - | 0.44 | 0 | 1.68 | 1.24 | 1.24 | opened | 101 | SS 35/10 kv Odinok | 1,6+1,6 | 0.024706 | 0.46471 | 0 | - | 0.46471 | 0 | 1.68 | 1.2153 | 1.2153 | opened
102 | SS 35/10 kv Uzkoe | 1,6+1 | 0.15 | 0.25 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened | 102 | SS 35/10 kv Uzkoe | 1,6+1 | 0 | 0.15 | 0.25 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened
103 | SS 35/10 kv Korsakovo | 2,5+4 | 0.83 | 0.68966 | 120 | 0.14034 | 0 | 2.625 | 2.4847 | 2.4847 | opened | 103 | SS 35/10 kv Korsakovo | 2,5+4 | 0.0023529 | 0.83235 | 0.68966 | 120 | 0.1427 | 0 | 2.625 | 2.4823 | 2.4823 | opened
104 | SS 35/10 kv Paramonovo | 4+2,5 | 0.71 | 0.75949 | 120 | -0.049494 | 0 | 2.625 | 2.6745 | 2.6745 | opened | 104 | SS 35/10 kv Paramonovo | 4+2,5 | 0.0058824 | 0.71588 | 0.75949 | 120 | -0.043611 | 0 | 2.625 | 2.6686 | 2.6686 | opened
105 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.21 | 0 | - | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 105 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.0058824 | 0.21588 | 0 | - | 0.21588 | 0 | 1.68 | 1.4641 | 1.4641 | opened
| Total: | 295.5 | 48.38 | [8 empty] | 2: Total:; 3: 352.7; 5: 90.7741
| deficit | [8 empty] | 0 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 117.163 |  | 2: proficit; Мin. 12: 193.1193
| Production association Livenskie power networks | [10 empty] | 2: Production association Livenskie power networks
106 | SS 110/35/10 kv Verkhovye I | 16+10 | 6.25 | 3.65 | 120 | 2.5978 | 0 | 10.5 | 7.9 | 7.9 | opened | 106 | SS 110/35/10 kv Verkhovye I | 16+10 | 0 | 7.1653 | 3.65 | 120 | 3.5153 | 0 | 10.5 | 6.9847 | 7.9 | opened
1 | Nom. capacity MV, MVA | 16+10 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 |  |  | 1 | Nom. capacity MV, MVA | 16+10 | 0 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5
107 | Nom. capacity LV, MVA | 16+10 | 4.2 | 1.6 | 120 | 2.5978 | 0 | 10.5 | 7.9 |  |  | 107 | Nom. capacity LV, MVA | 16+10 | 0.91529 | 5.1153 | 1.6 | 120 | 3.5153 | 0 | 10.5 | 6.9847
107 | SS 110/35/10 kv Verkhovye II | 40+40 | 10.2 | 0.3 | - | 9.9 | 0 | 42 | 32.1 | 32.1 | opened | 107 | SS 110/35/10 kv Verkhovye II | 40+40 | 0 | 10.2 | 0.3 | - | 9.9 | 0 | 42 | 32.1 | 32.1 | opened
108 | Nom. capacity MV, MVA | 40+40 | 0.3 | 0.3 | - | 0 | 0 | 42 | 42 |  |  | 108 | Nom. capacity MV, MVA | 40+40 | 0 | 0.3 | 0.3 | - | 0 | 0 | 42 | 42
108 | Nom. capacity LV, MVA | 40+40 | 9.9 | 0 | - | 9.9 | 0 | 42 | 32.1 |  |  | 108 | Nom. capacity LV, MVA | 40+40 | 0 | 9.9 | 0 | - | 9.9 | 0 | 42 | 32.1
108 | SS 110/35/10 kv Dolgoe | 16+10 | 5.84 | 3.3773 | 120 | 2.46 | 0 | 10.5 | 8.0373 | 8.04 | opened | 108 | SS 110/35/10 kv Dolgoe | 16+10 | 0 | 5.8447 | 3.3773 | 120 | 2.4674 | 0 | 10.5 | 8.0326 | 8.04 | opened
109 | Nom. capacity MV, MVA | 16+10 | 2.38 | 2.38 | 120 | 0 | 0 | 10.5 | 10.5 |  |  | 109 | Nom. capacity MV, MVA | 16+10 | 0 | 2.38 | 2.38 | 120 | 0 | 0 | 10.5 | 10.5
109 | Nom. capacity LV, MVA | 16+10 | 3.46 | 0.99726 | 120 | 2.46 | 0 | 10.5 | 8.0373 |  |  | 109 | Nom. capacity LV, MVA | 16+10 | 0.0047059 | 3.4647 | 0.99726 | 120 | 2.4674 | 0 | 10.5 | 8.0326
109 | SS 110/35/10 kv Kolpny-110 | 10+16 | 4.03 | 2.787 | 120 | 1.243 | 0 | 10.5 | 9.257 | 9.26 | opened | 109 | SS 110/35/10 kv Kolpny-110 | 10+16 | 0 | 4.0488 | 2.787 | 120 | 1.2619 | 0 | 10.5 | 9.2381 | 9.26 | opened
110 | Nom. capacity MV, MVA | 10+16 | 2.46 | 2.46 | 120 | 0 | 0 | 10.5 | 10.5 |  |  | 110 | Nom. capacity MV, MVA | 10+16 | 0 | 2.46 | 2.46 | 120 | 0 | 0 | 10.5 | 10.5
110 | Nom. capacity LV, MVA | 10+16 | 1.57 | 0.32697 | 120 | 1.243 | 0 | 10.5 | 9.257 |  |  | 110 | Nom. capacity LV, MVA | 10+16 | 0.018824 | 1.5888 | 0.32697 | 120 | 1.2619 | 0 | 10.5 | 9.2381
110 | SS 110/35/10 kv Kr. Zarya | 10+10 | 4.51 | 1.5352 | 120 | 2.9748 | 0 | 10.5 | 7.5252 | 7.53 | opened | 110 | SS 110/35/10 kv Kr. Zarya | 10+10 | 0 | 4.5218 | 1.5352 | 120 | 2.9865 | 0 | 10.5 | 7.5135 | 7.53 | opened
111 | Nom. capacity MV, MVA | 10+10 | 1.29 | 1.29 | 120 | 0 | 0 | 10.5 | 10.5 |  |  | 111 | Nom. capacity MV, MVA | 10+10 | 0 | 1.29 | 1.29 | 120 | 0 | 0 | 10.5 | 10.5
111 | Nom. capacity LV, MVA | 10+10 | 3.22 | 0.24523 | 120 | 2.9748 | 0 | 10.5 | 7.5252 |  |  | 111 | Nom. capacity LV, MVA | 10+10 | 0.011765 | 3.2318 | 0.24523 | 120 | 2.9865 | 0 | 10.5 | 7.5135
111 | SS 110/35/10 kv Pokrovskaya | 10+10 | 5.3 | 2.8393 | 120 | 2.4607 | 0 | 10.5 | 8.0393 | 8.04 | opened | 111 | SS 110/35/10 kv Pokrovskaya | 10+10 | 0 | 5.8847 | 2.8393 | 120 | 3.0454 | 0 | 10.5 | 7.4546 | 8.04 | opened
112 | Nom. capacity MV, MVA | 10+10 | 2.12 | 2.12 | 120 | 0 | 0 | 10.5 | 10.5 |  |  | 112 | Nom. capacity MV, MVA | 10+10 | 0 | 2.12 | 2.12 | 120 | 0 | 0 | 10.5 | 10.5
112 | Nom. capacity LV, MVA | 10+10 | 3.18 | 0.71933 | 120 | 2.4607 | 0 | 10.5 | 8.0393 |  |  | 112 | Nom. capacity LV, MVA | 10+10 | 0.58471 | 3.7647 | 0.71933 | 120 | 3.0454 | 0 | 10.5 | 7.4546
112 | SS 110/35/6 kv Cherkasskaya | 40+25 | 19.17 | 13.3904 | 120 | 5.7796 | 0 | 26.25 | 20.4704 | 20.47 | opened | 112 | SS 110/35/6 kv Cherkasskaya | 40+25 | 0 | 19.1759 | 13.3904 | 120 | 5.7855 | 0 | 26.25 | 20.4645 | 20.47 | opened
113 | Nom. capacity MV, MVA | 40+25 | 10.84 | 10.84 | 120 | 0 | 0 | 26.25 | 26.25 |  |  | 113 | Nom. capacity MV, MVA | 40+25 | 0 | 10.84 | 10.84 | 120 | 0 | 0 | 26.25 | 26.25
113 | Nom. capacity LV, MVA | 40+25 | 8.33 | 2.5504 | 120 | 5.7796 | 0 | 26.25 | 20.4704 |  |  | 113 | Nom. capacity LV, MVA | 40+25 | 0.0058824 | 8.3359 | 2.5504 | 120 | 5.7855 | 0 | 26.25 | 20.4645
113 | SS 110/6 kv Plastmass | 16+16 | 10.6 | 0 | - | 10.6 | 0 | 16.8 | 6.2 | 6.2 | opened | 113 | SS 110/6 kv Plastmass | 16+16 | 0 | 10.6 | 0 | - | 10.6 | 0 | 16.8 | 6.2 | 6.2 | opened
114 | SS 110/10 kv PM | 10+10 | 4.3 | 0 | - | 4.3 | 0 | 10.5 | 6.2 | 6.2 | opened | 114 | SS 110/10 kv PM | 10+10 | 0 | 4.3 | 0 | - | 4.3 | 0 | 10.5 | 6.2 | 6.2 | opened
115 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.92 | 1.8474 | 120 | -0.92738 | 0 | 6.615 | 7.5424 | 7.5424 | opened | 115 | SS 110/10 kv Rechitsa | 6,3+6,3 | 0.6 | 1.52 | 1.8474 | 120 | -0.32738 | 0 | 6.615 | 6.9424 | 6.9424 | opened
116 | SS 110/10 kv R.Brod | 5,6+10 | 1.89 | 0.29427 | 120 | 1.5957 | 0 | 5.88 | 4.2843 | 4.2843 | opened | 116 | SS 110/10 kv R.Brod | 5,6+10 | 0.37294 | 2.2629 | 0.29427 | 120 | 1.9687 | 0 | 5.88 | 3.9113 | 3.9113 | opened
117 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.4 | 0.13079 | 120 | 0.26921 | 0 | 1.68 | 1.4108 | 1.4108 | opened | 117 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.015882 | 0.41588 | 0.13079 | 120 | 0.28509 | 0 | 1.68 | 1.3949 | 1.3949 | opened
118 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 1.04 | 0.65394 | 120 | 0.38606 | 0 | 2.625 | 2.2389 | 2.2389 | opened | 118 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 0.047059 | 1.0871 | 0.65394 | 120 | 0.43312 | 0 | 2.625 | 2.1919 | 2.1919 | opened
119 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0.78 | 0.42506 | 120 | 0.35494 | 0 | 2.625 | 2.2701 | 2.2701 | opened | 119 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0 | 0.78 | 0.42506 | 120 | 0.35494 | 0 | 2.625 | 2.2701 | 2.2701 | opened
120 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.85 | 0.55585 | 120 | 0.29415 | 0 | 1.68 | 1.3858 | 1.3858 | opened | 120 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 0.017647 | 0.86765 | 0.55585 | 120 | 0.3118 | 0 | 1.68 | 1.3682 | 1.3682 | opened
121 | SS 35/10 kv Droskovo | 4+2,5 | 1.53 | 0 | - | 1.53 | 0 | 2.625 | 1.095 | 1.095 | opened | 121 | SS 35/10 kv Droskovo | 4+2,5 | 0.016118 | 1.5461 | 0 | - | 1.5461 | 0 | 2.625 | 1.0789 | 1.0789 | opened
122 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 1.26 | 0.39236 | 120 | 0.86764 | 0 | 6.615 | 5.7474 | 5.7474 | opened | 122 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 0 | 1.26 | 0.39236 | 120 | 0.86764 | 0 | 6.615 | 5.7474 | 5.7474 | opened
123 | SS 35/10 kv Krutoe | 2,5+1,6 | 1.33 | 0.86647 | 120 | 0.46353 | 0 | 1.68 | 1.2165 | 1.2165 | opened | 123 | SS 35/10 kv Krutoe | 2,5+1,6 | 0.12941 | 1.4594 | 0.86647 | 120 | 0.59294 | 0 | 1.68 | 1.0871 | 1.0871 | opened
124 | SS 35/10 kv Mezentsevo | 4+6,3 | 2.1 | 1.1117 | 80 | 0.9883 | 0 | 4.2 | 3.2117 | 3.2117 | opened | 124 | SS 35/10 kv Mezentsevo | 4+6,3 | 0.1 | 2.2 | 1.1117 | 80 | 1.0883 | 0 | 4.2 | 3.1117 | 3.1117 | opened
125 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.14 | 0 | - | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 125 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0 | 0.14 | 0 | - | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
126 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0.28 | 0.39236 | - | -0.11236 | 0 | 2.625 | 2.7374 | 2.7374 | opened | 126 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0 | 0.28 | 0.39236 | - | -0.11236 | 0 | 2.625 | 2.7374 | 2.7374 | opened
127 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 1.14 | 0.5395 | 80 | 0.6005 | 0 | 2.625 | 2.0245 | 2.0245 | opened | 127 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 0.075294 | 1.2153 | 0.5395 | 80 | 0.67579 | 0 | 2.625 | 1.9492 | 1.9492 | opened
128 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.3 | 1.6675 | - | -1.3675 | 0 | 3.36 | 4.7275 | 4.7275 | opened | 128 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.0035294 | 0.30353 | 1.6675 | - | -1.364 | 0 | 3.36 | 4.724 | 4.724 | opened
129 | SS 35/6 kv Pushkarskaya | 4+4 | 5.16 | 0 | 120 | 5.16 | 0 | 4.2 | -0.96 | -0.96 | closed | 129 | SS 35/6 kv Pushkarskaya | 10+10 | 0 | 5.16 | 0 | 120 | 5.16 | 0 | 10.5 | 5.34 | 5.34 | opened
130 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0.44 | 0.24523 | 120 | 0.19477 | 0 | 2.625 | 2.4302 | 2.4302 | opened | 130 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0 | 0.44 | 0.24523 | 120 | 0.19477 | 0 | 2.625 | 2.4302 | 2.4302 | opened
131 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.94 | 0.70299 | 80 | 0.23701 | 0 | 2.625 | 2.388 | 2.388 | opened | 131 | SS 35/10 kv Rosstani | 2,5+2,5 | 0.076471 | 1.0165 | 0.70299 | 80 | 0.31349 | 0 | 2.625 | 2.3115 | 2.3115 | opened
132 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.09 | 1.5041 | 120 | -0.41406 | 0 | 2.625 | 3.0391 | 3.0391 | opened | 132 | SS 35/10 kv Sergievskaya | 4+2,5 | 0.97059 | 2.0606 | 1.5041 | 120 | 0.55653 | 0 | 2.625 | 2.0685 | 2.0685 | opened
133 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.39 | 0.32697 | 120 | 0.06303 | 0 | 1.68 | 1.617 | 1.617 | opened | 133 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0 | 0.39 | 0.32697 | 120 | 0.06303 | 0 | 1.68 | 1.617 | 1.617 | opened
134 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0.3 | 0 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 134 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0 | 0.3 | 0 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
135 | SS 35/10 kv Urynok | 1,6+1,6 | 0.99 | 0.52315 | 20 | 0.46685 | 0 | 1.68 | 1.2132 | 1.2132 | opened | 135 | SS 35/10 kv Urynok | 1,6+1,6 | 0.0011765 | 0.99118 | 0.52315 | 20 | 0.46802 | 0 | 1.68 | 1.212 | 1.212 | opened
136 | SS 35/10 kv Khomutovo | 4+4 | 1.66 | 0.31062 | 80 | 1.3494 | 0 | 4.2 | 2.8506 | 2.8506 | opened | 136 | SS 35/10 kv Khomutovo | 4+4 | 0 | 1.66 | 0.31062 | 80 | 1.3494 | 0 | 4.2 | 2.8506 | 2.8506 | opened
| Total: | 438.1 | 149.2 | [8 empty] | 2: Total:; 3: 450.1; 4: 2.5155
| deficit | [8 empty] | -0.96 |  | 2: deficit; Мin. 12: 0
| proficit | [8 empty] | 162.0903 |  | 2: proficit; Мin. 12: 165.0041
| Total as per PS: | 1684 | 439.56 | [8 empty] | 2: Total as per PS:; 3: 1662.3; 4: 52.1091
| deficit of PS | [8 empty] | -4.6643 |  | 2: deficit of PS; Мin. 12: 0
| proficit of PS | [8 empty] | 603.0386 |  | 2: proficit of PS; Мin. 12: 711.7989
Note on E35: Автор: Первое слагаемое-полная мощность перераспределяемая на ПС "Коммаш" по потребительскому фидеру ОАО "Мужгосметиз-Мценск"; второе слагаемое полная мощность перераспределяемая по городской электросети; третье слагаемое полная мощность перераспределяемая по кольцевой связи 10 кВ ПС"Район"В" с ПС"Подберёзово"(проверена расчётом по потере напряжения-не более 0,96кВ).
Note on E40: Автор: Определена расчётом по допустимой потере напряжения.
Note on E41: Автор: Определена расчётом по допустимой потере напряжения.
Note on E42: Автор: Определена расчётом по допустимой потере напряжения.
Note on E43: Автор: Определена расчётом по допустимой потере напряжения.
Note on E44: Автор: Определена расчётом по допустимой потере напряжения.
Note on E46: Автор: Определена расчётом по допустимой потере напряжения.
Note on E47: Автор: Определена расчётом по допустимой потере напряжения.
Note on S35: Автор: Первое слагаемое-полная мощность перераспределяемая на ПС "Коммаш" по потребительскому фидеру ОАО "Мужгосметиз-Мценск"; второе слагаемое полная мощность перераспределяемая по городской электросети; третье слагаемое полная мощность перераспределяемая по кольцевой связи 10 кВ ПС"Район"В" с ПС"Подберёзово"(проверена расчётом по потере напряжения-не более 0,96кВ).
Note on S38: Автор: Строительство связи с ПС "Район "В". ВЛ-10кВ проводом АС-95 на передачу до 6,0МВА в аварийном режиме. В перспективе планируется установка Т-2 мощностью 6,3МВА.
Note on S164: Автор: Подтверждено расчётом по связи фид.№5 с фид.№2 ПС"Район"В".
Note on S165: Автор: Подстанция не имеет связей с другими ПС на низшем напряжении.
Note on S167: Автор: Подстанция не имеет связей с другими ПС на низшем напряжении.
Note on S170: Автор: Подстанция не имеет связей с другими ПС на низшем напряжении.
Note on S174: Автор: Подстанция не имеет связей с другими ПС на низшем напряжении.
Note on S178: Автор: Подстанция не имеет связей с другими ПС на низшем напряжении.

## воронеж
[11 empty] | Table 1 | [12 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1mode, MVA | Deficit / proficit of main substation, MVA
|  |  | МVА | МVА | Мin. | [11 empty] | МVА | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| Power supply system | [10 empty] | 2: Power supply system
1 | No. 44 | 10 | 0.06 | 0 | 0 | 0 | 0 | 0 | -0.06 | -0.06 | closed | 1 | No. 44 | 10 | 2.065 | 2.125 | 0 | 0 | 2.125 | 0 | 0 | -2.125 | -2.125 | closed
2 | No. 7 | 2.5 | 0.22 | 0 | 0 | 0 | 0 | 0 | -0.22 | -0.22 | closed | 2 | No. 7 | 2.5 | 3.212 | 3.432 | 3.5 | 0 | -0.068 | 0 | 3.5 | 0.068 | 0.068 | opened
3 | Stupino | 6.3 | 0.95 | 1.0375 | 120 | 1.0375 | 0 | 1.0375 | 0.0875 | 0.0875 | opened | 3 | Stupino | 6.3 | 0.0875 | 1.0375 | 1.0375 | 120 | 0 | 0 | 1.0375 | 0 | 0 | opened
4 | P.Kommuna | 6.3 | 0.41 | 0.413 | 120 | 0.413 | 0 | 0.413 | 0.003 | 0.003 | opened | 4 | P.Kommuna | 6.3 | 0.003 | 0.413 | 0.413 | 120 | 0 | 0 | 0.413 | 0 | 0 | opened
5 | No. 38 | 2.5 | 0.8 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0 | 0 | opened | 5 | No. 38 | 2.5 | 0 | 0.8 | 0.8 | 120 | 0 | 0 | 0.8 | 0 | 0 | opened
6 | No. 46 | 4 | 0.03 | 0 | 0 | 0 | 0 | 0 | -0.03 | -0.03 | opened | 6 | No. 46 | 4 | 0 | 0.03 | 0 | 0 | 0.03 | 0 | 0 | -0.03 | -0.03 | opened
7 | Istobnoe | 4 | 0.35 | 0.36 | 120 | 0.36 | 0 | 0.36 | 0.01 | 0.01 | opened | 7 | Istobnoe | 4 | 0.01 | 0.36 | 0.36 | 120 | 0 | 0 | 0.36 | 0 | 0 | opened
8 | Rodina | 2.5 | 0.15 | 1.6525 | 120 | 1.6525 | 0 | 1.6525 | 1.5025 | 1.5025 | opened | 8 | Rodina | 2.5 | 1.5025 | 1.6525 | 1.6525 | 120 | 0 | 0 | 1.6525 | 0 | 0 | opened
9 | Vyaznovatovka | 2.5 | 0.45 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.94 | 0.94 | opened | 9 | Vyaznovatovka | 2.5 | 0.94 | 1.39 | 1.39 | 120 | 0 | 0 | 1.39 | 0 | 0 | opened
10 | Turovo-1 | 3.2 | 1.31 | 1.3433 | 120 | 1.3433 | 0 | 1.3433 | 0.0333 | 0.0333 | opened | 10 | Turovo-1 | 3.2 | 0.0333 | 1.3433 | 1.3433 | 120 | 0 | 0 | 1.3433 | 0 | 0 | opened
11 | Semidesyatnoe | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 | closed | 11 | Semidesyatnoe | 2.5 | 0.089 | 0.379 | 0 | 0 | 0.379 | 0 | 0 | -0.379 | -0.379 | closed
12 | Arkhangelskoe | 3.2 | 0.58 | 0 | 0 | 0 | 0 | 0 | -0.58 | -0.58 | closed | 12 | Arkhangelskoe | 3.2 | 0.06139 | 0.64139 | 0 | 0 | 0.64139 | 0 | 0 | -0.64139 | -0.64139 | closed
13 | Khokhol-2 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | closed | 13 | Khokhol-2 | 2.5 | 0.1 | 1.1 | 0 | 0 | 1.1 | 0 | 0 | -1.1 | -1.1 | closed
14 | N.Olshanka | 4 | 0.73 | 0.7574 | 120 | 0.7574 | 0 | 0.7574 | 0.0274 | 0.0274 | opened | 14 | N.Olshanka | 4 | 0.0274 | 0.7574 | 0.7574 | 120 | 0 | 0 | 0.7574 | 0 | 0 | opened
15 | Troitskoe | 2.5 | 0.31 | 0 | 0 | 0 | 0 | 0 | -0.31 | -0.31 | closed | 15 | Troitskoe | 2.5 | 0.0105 | 0.3205 | 0 | 0 | 0.3205 | 0 | 0 | -0.3205 | -0.3205 | closed
16 | Zemlyansk | 4 | 0.91 | 0 | 0 | 0 | 0 | 0 | -0.91 | -0.91 | closed | 16 | Zemlyansk | 4 | 0.012 | 0.922 | 0 | 0 | 0.922 | 0 | 0 | -0.922 | -0.922 | closed
17 | Losevo | 2.5 | 0.95 | 0.9536 | 120 | 0.9536 | 0 | 0.9536 | 0.0036 | 0.0036 | opened | 17 | Losevo | 2.5 | 0.0036 | 0.9536 | 0.9536 | 120 | 0 | 0 | 0.9536 | 0 | 0 | opened
18 | Verny | 2.5 | 1.66 | 1.706 | 120 | 1.706 | 0 | 1.706 | 0.046 | 0.046 | opened | 18 | Verny | 2.5 | 0.046 | 1.706 | 1.706 | 120 | 0 | 0 | 1.706 | 0 | 0 | opened
19 | Elevator | 2.5 | 0.81 | 0.848 | 120 | 0.848 | 0 | 0.848 | 0.038 | 0.038 | opened | 19 | Elevator | 2.5 | 0.038 | 0.848 | 0.848 | 120 | 0 | 0 | 0.848 | 0 | 0 | opened
20 | Yubileynaya | 4 | 1.45 | 1.5145 | 120 | 1.5145 | 0 | 1.5145 | 0.0645 | 0.0645 | opened | 20 | Yubileynaya | 4 | 0.0645 | 1.5145 | 1.5145 | 120 | 0 | 0 | 1.5145 | 0 | 0 | opened
21 | Parusnoe | 4 | 3.07 | 3.1584 | 120 | 3.1584 | 0 | 3.1584 | 0.0884 | 0.0884 | opened | 21 | Parusnoe | 4 | 0.0884 | 3.1584 | 3.1584 | 120 | 0 | 0 | 3.1584 | 0 | 0 | opened
22 | Rogachyovka | 4 | 1.91 | 1.9643 | 120 | 1.9643 | 0 | 1.9643 | 0.0543 | 0.0543 | opened | 22 | Rogachyovka | 4 | 0.0543 | 1.9643 | 1.9643 | 120 | 0 | 0 | 1.9643 | 0 | 0 | opened
23 | Rassvet | 2.5 | 0.2 | 0.2 | 120 | 0.2 | 0 | 0.2 | 0 | 0 | opened | 23 | Rassvet | 2.5 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 0.2 | 0 | 0 | opened
24 | Dankovo | 2.5 | 0.87 | 0.899 | 120 | 0.899 | 0 | 0.899 | 0.029 | 0.029 | opened | 24 | Dankovo | 2.5 | 0.029 | 0.899 | 0.899 | 120 | 0 | 0 | 0.899 | 0 | 0 | opened
25 | Bugaevka | 16 | 5.26 | 14 | 90 | 14 | 0 | 14 | 8.74 | 2.41 | opened | 25 | Bugaevka | 16 | 0.1128 | 5.3728 | 14 | 90 | -8.6272 | 0 | 14 | 8.6272 | 2.2972 | opened
| Sн. MV, МVА | 16 | 3.67 | 10 | 90 | 10 | 0 | 10 | 6.33 |  |  |  | Sн. MV, МVА | 16 | 0 | 3.67 | 10 | 90 | -6.33 | 0 | 10 | 6.33
| Sн. LV, МVА | 16 | 1.59 | 4 | 90 | 4 | 0 | 4 | 2.41 |  |  |  | Sн. LV, МVА | 16 | 0.1128 | 1.7028 | 4 | 90 | -2.2972 | 0 | 4 | 2.2972
26 | Dobrino | 10 | 1.03 | 6.6 | 90 | 6.6 | 0 | 6.6 | 5.57 | 2.31 | opened | 26 | Dobrino | 10 | 0.095012 | 1.125 | 6.6 | 90 | -5.475 | 0 | 6.6 | 5.475 | 2.215 | opened
| Sн. MV, МVА | 10 | 0.22 | 5.8 | 90 | 5.8 | 0 | 5.8 | 5.58 |  |  |  | Sн. MV, МVА | 10 | 0 | 0.22 | 5.8 | 90 | -5.58 | 0 | 5.8 | 5.58
| Sн. LV, МVА | 10 | 0.81 | 3.12 | 90 | 3.12 | 0 | 3.12 | 2.31 |  |  |  | Sн. LV, МVА | 10 | 0.095012 | 0.90501 | 3.12 | 90 | -2.215 | 0 | 3.12 | 2.215
27 | N. Kalitva | 6.3 | 1.55 | 0.78 | 240 | 0.78 | 0 | 0.78 | -0.77 | -0.77 | closed | 27 | N. Kalitva | 6.3 | 0.034048 | 1.584 | 0.78 | 240 | 0.80405 | 0 | 0.78 | -0.80405 | -0.80405 | closed
28 | Shishovka | 6.3 | 0.68 | 2.34 | 180 | 2.34 | 0 | 2.34 | 1.66 | 1.66 | opened | 28 | Shishovka | 6.3 | 0.0185 | 0.6985 | 2.34 | 180 | -1.6415 | 0 | 2.34 | 1.6415 | 1.6415 | opened
29 | Azovka | 10 | 1.47 | 3.12 | 180 | 3.12 | 0 | 3.12 | 1.65 | 1.65 | opened | 29 | Azovka | 10 | 2.13 | 3.6 | 3.12 | 180 | 0.47996 | 0 | 3.12 | -0.47996 | -0.47996 | closed
30 | Yurasovka | 2.5 | 0.56 | 1.56 | 120 | 1.56 | 0 | 1.56 | 1 | 1 | opened | 30 | Yurasovka | 2.5 | 0.014036 | 0.57404 | 1.56 | 120 | -0.98596 | 0 | 1.56 | 0.98596 | 0.98596 | opened
31 | Nerovnovka | 2.5 | 0.25 | 0.78 | 240 | 0.78 | 0 | 0.78 | 0.53 | 0.53 | opened | 31 | Nerovnovka | 2.5 | 0.003512 | 0.25351 | 0.78 | 240 | -0.52649 | 0 | 0.78 | 0.52649 | 0.52649 | opened
32 | Saprino | 1.8 | 0.34 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.46 | 1.46 | opened | 32 | Saprino | 1.8 | 0.009848 | 0.34985 | 1.8 | 120 | -1.4502 | 0 | 1.8 | 1.4502 | 1.4502 | opened
33 | Sergeevka | 4 | 0.31 | 0 | 0 | 0 | 0 | 0 | -0.31 | -0.31 | closed | 33 | Sergeevka | 4 | 0.040324 | 0.35032 | 0 | 0 | 0.35032 | 0 | 0 | -0.35032 | -0.35032 | closed
34 | Stepanovka | 4 | 0.31 | 1.56 | 240 | 1.56 | 0 | 1.56 | 1.25 | 1.25 | opened | 34 | Stepanovka | 4 | 0.020036 | 0.33004 | 1.56 | 240 | -1.23 | 0 | 1.56 | 1.23 | 1.23 | opened
35 | Kolodezhanskaya | 2.5 | 0.23 | 0.78 | 180 | 0.78 | 0 | 0.78 | 0.55 | 0.55 | opened | 35 | Kolodezhanskaya | 2.5 | 0.042 | 0.272 | 0.78 | 180 | -0.508 | 0 | 0.78 | 0.508 | 0.508 | opened
36 | Andreevka | 2.5 | 0.09 | 0 | 0 | 0 | 0 | 0 | -0.09 | -0.09 | opened | 36 | Andreevka | 2.5 | 0.017125 | 0.10712 | 0 | 0 | 0.10712 | 0 | 0 | -0.10712 | -0.10712 | closed
37 | Kulikovka | 4 | 1.27 | 0 | 0 | 0 | 0 | 0 | -1.27 | -1.27 | closed | 37 | Kulikovka | 4 | 0.18075 | 1.4507 | 0 | 0 | 1.4507 | 0 | 0 | -1.4507 | -1.4507 | closed
38 | Lizinovka | 2.5 | 0.56 | 2.5 | 240 | 2.5 | 0 | 2.5 | 1.94 | 1.94 | opened | 38 | Lizinovka | 2.5 | 0.006012 | 0.56601 | 2.5 | 240 | -1.934 | 0 | 2.5 | 1.934 | 1.934 | opened
39 | Sotnitskaya | 4 | 1.09 | 2.3 | 120 | 2.3 | 0 | 2.3 | 1.21 | 1.21 | opened | 39 | Sotnitskaya | 4 | 0.018 | 1.108 | 2.3 | 120 | -1.192 | 0 | 2.3 | 1.192 | 1.192 | opened
40 | Kr. Polyana | 2.5 | 0.22 | 0 | 0 | 0 | 0 | 0 | -0.22 | -0.22 | closed | 40 | Kr. Polyana | 2.5 | 0.010524 | 0.23052 | 0 | 0 | 0.23052 | 0 | 0 | -0.23052 | -0.23052 | closed
41 | Gumny | 4 | 0.66 | 1.56 | 180 | 1.56 | 0 | 1.56 | 0.9 | 0.9 | opened | 41 | Gumny | 4 | 0.069612 | 0.72961 | 1.56 | 180 | -0.83039 | 0 | 1.56 | 0.83039 | 0.83039 | opened
42 | Uryv | 2.5 | 0.55 | 0 | 0 | 0 | 0 | 0 | -0.55 | -0.55 | closed | 42 | Uryv | 2.5 | 0.044 | 0.594 | 0 | 0 | 0.594 | 0 | 0 | -0.594 | -0.594 | closed
43 | Shubnov | 2.5 | 0.56 | 1.17 | 180 | 1.17 | 0 | 1.17 | 0.61 | 0.61 | opened | 43 | Shubnov | 2.5 | 0.080124 | 0.64012 | 1.17 | 180 | -0.52988 | 0 | 1.17 | 0.52988 | 0.52988 | opened
44 | Zaluzhnoe | 2.5 | 1.41 | 1.56 | 240 | 1.56 | 0 | 1.56 | 0.15 | 0.15 | opened | 44 | Zaluzhnoe | 2.5 | 0.23352 | 1.6435 | 1.56 | 240 | 0.083524 | 0 | 1.56 | -0.083524 | -0.083524 | closed
46 | Anna-2 | 25 | 6.51 | 7.8 | 90 | 7.8 | 0 | 7.8 | 1.29 | 0.37 | opened | 46 | Anna-2 | 25 | 0.2338 | 6.7438 | 7.8 | 90 | -1.0562 | 0 | 7.8 | 1.0562 | 0.37 | opened
| Sн. MV, МVА | 25 | 1.87 | 2.24 | 90 | 2.24 | 0 | 2.24 | 0.37 |  |  |  | Sн. MV, МVА | 25 | 0 | 1.87 | 2.24 | 90 | -0.37 | 0 | 2.24 | 0.37
| Sн. LV, МVА | 25 | 4.64 | 5.56 | 90 | 5.56 | 0 | 5.56 | 0.92 |  |  |  | Sн. LV, МVА | 25 | 0.2338 | 4.8738 | 5.56 | 90 | -0.6862 | 0 | 5.56 | 0.6862
47 | Vostochnaya | 10 | 3.69 | 4.42 | 30 | 4.42 | 0 | 4.42 | 0.73 | 0.73 | opened | 47 | Vostochnaya | 10 | 0 | 3.69 | 4.42 | 30 | -0.73 | 0 | 4.42 | 0.73 | 0.73 | opened
48 | Bolshevik | 6.3 | 1.22 | 1.46 | 60 | 1.46 | 0 | 1.46 | 0.24 | 0.24 | opened | 48 | Bolshevik | 6.3 | 0.11522 | 1.3352 | 1.46 | 60 | -0.12478 | 0 | 1.46 | 0.12478 | 0.12478 | opened
49 | Rozhdestvo | 6.3 | 0.59 | 0.7 | 60 | 0.7 | 0 | 0.7 | 0.11 | 0.11 | opened | 49 | Rozhdestvo | 6.3 | 0.059783 | 0.64978 | 0.7 | 60 | -0.050217 | 0 | 0.7 | 0.050217 | 0.050217 | opened
50 | V. Toyda | 6.3 | 1.16 | 1.4 | 90 | 1.4 | 0 | 1.4 | 0.24 | 0.24 | opened | 50 | V. Toyda | 6.3 | 0.15043 | 1.3104 | 1.4 | 90 | -0.089565 | 0 | 1.4 | 0.089565 | 0.089565 | opened
51 | Vostochnaya-1 | 40 | 6.78 | 8.13 | 60 | 8.13 | 0 | 8.13 | 1.35 | 0.41 | opened | 51 | Vostochnaya-1 | 40 | 0.0032609 | 6.7833 | 8.13 | 60 | -1.3467 | 0 | 8.13 | 1.3467 | 0.40674 | opened
| Sн. MV, МVА | 40 | 4.73 | 5.67 | 60 | 5.67 | 0 | 5.67 | 0.94 |  |  |  | Sн. MV, МVА | 40 | 0 | 4.73 | 5.67 | 60 | -0.94 | 0 | 5.67 | 0.94
| Sн. LV, МVА | 40 | 2.05 | 2.46 | 60 | 2.46 | 0 | 2.46 | 0.41 |  |  |  | Sн. LV, МVА | 40 | 0.0032609 | 2.0533 | 2.46 | 60 | -0.40674 | 0 | 2.46 | 0.40674
52 | Makashevka | 2.5 | 0.4 | 0.48 | 180 | 0.48 | 0 | 0.48 | 0.08 | 0.08 | opened | 52 | Makashevka | 2.5 | 0.046739 | 0.44674 | 0.48 | 180 | -0.033261 | 0 | 0.48 | 0.033261 | 0.033261 | opened
53 | Mirolyubie | 4 | 0.42 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.08 | 0.08 | opened | 53 | Mirolyubie | 4 | 0.018478 | 0.43848 | 0.5 | 60 | -0.061522 | 0 | 0.5 | 0.061522 | 0.061522 | opened
54 | V. Zaton | 2.5 | 0.01 | 0.01 | 60 | 0.01 | 0 | 0.01 | 0 | 0 | opened | 54 | V. Zaton | 2.5 | 0 | 0.01 | 0.01 | 60 | 0 | 0 | 0.01 | 0 | 0 | opened
55 | Oktyabrskoe | 2.5 | 0.56 | 0.67 | 30 | 0.67 | 0 | 0.67 | 0.11 | 0.11 | opened | 55 | Oktyabrskoe | 2.5 | 0.068478 | 0.62848 | 0.67 | 30 | -0.041522 | 0 | 0.67 | 0.041522 | 0.041522 | opened
56 | Ilmen | 2.5 | 0.26 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.12 | 0.12 | opened | 56 | Ilmen | 2.5 | 0.063559 | 0.32356 | 0.38 | 60 | -0.056441 | 0 | 0.38 | 0.056441 | 0.056441 | opened
57 | Vikhlyaevka | 2.5 | 0.1 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.02 | 0.02 | opened | 57 | Vikhlyaevka | 2.5 | 0 | 0.1 | 0.12 | 120 | -0.02 | 0 | 0.12 | 0.02 | 0.02 | opened
58 | N. Elan | 2.5 | 0.41 | 0 | 0 | 0 | 0 | 0 | -0.41 | -0.41 | closed | 58 | N. Elan | 2.5 | 0.027174 | 0.43717 | 0 | 0 | 0.43717 | 0 | 0 | -0.43717 | -0.43717 | closed
59 | B. Alabukhi | 2.5 | 0.78 | 0.93 | 90 | 0.93 | 0 | 0.93 | 0.15 | 0.15 | opened | 59 | B. Alabukhi | 2.5 | 0.083696 | 0.8637 | 0.93 | 90 | -0.066305 | 0 | 0.93 | 0.066305 | 0.066305 | opened
60 | Pykhovka | 2.5 | 0.29 | 0 | 0 | 0 | 0 | 0 | -0.29 | -0.29 | closed | 60 | Pykhovka | 2.5 | 0.044565 | 0.33457 | 0 | 0 | 0.33457 | 0 | 0 | -0.33457 | -0.33457 | closed
61 | Е. Koleno | 4 | 2.78 | 3.33 | 120 | 3.33 | 0 | 3.33 | 0.55 | 0.55 | opened | 61 | Е. Koleno | 4 | 0.05788 | 2.8379 | 3.33 | 120 | -0.49212 | 0 | 3.33 | 0.49212 | 0.49212 | opened
62 | Podgornoe | 2.5 | 0.39 | 0.46 | 180 | 0.46 | 0 | 0.46 | 0.07 | 0.07 | opened | 62 | Podgornoe | 2.5 | 0.044565 | 0.43457 | 0.46 | 180 | -0.025435 | 0 | 0.46 | 0.025435 | 0.025435 | opened
63 | Mikhailovka-1 | 4 | 0.3 | 0.36 | 60 | 0.36 | 0 | 0.36 | 0.06 | 0.06 | opened | 63 | Mikhailovka-1 | 4 | 0.052174 | 0.35217 | 0.36 | 60 | -0.0078261 | 0 | 0.36 | 0.0078261 | 0.0078261 | opened
64 | Mikhailovka | 2.5 | 0.42 | 0.5 | 60 | 0.5 | 0 | 0.5 | 0.08 | 0.08 | opened | 64 | Mikhailovka | 2.5 | 0.067935 | 0.48794 | 0.5 | 60 | -0.012065 | 0 | 0.5 | 0.012065 | 0.012065 | opened
65 | Gnilusha | 4 | 0.77 | 0.92 | 180 | 0.92 | 0 | 0.92 | 0.15 | 0.15 | opened | 65 | Gnilusha | 4 | 0.096196 | 0.8662 | 0.92 | 180 | -0.053804 | 0 | 0.92 | 0.053804 | 0.053804 | opened
66 | Mayskaya | 2.5 | 0.64 | 0 | 0 | 0 | 0 | 0 | -0.64 | -0.64 | closed | 66 | Mayskaya | 2.5 | 0.016304 | 0.6563 | 0 | 0 | 0.6563 | 0 | 0 | -0.6563 | -0.6563 | closed
67 | Khleborodnoe | 2.5 | 0.48 | 0 | 0 | 0 | 0 | 0 | -0.48 | -0.48 | closed | 67 | Khleborodnoe | 2.5 | 0.058696 | 0.5387 | 0 | 0 | 0.5387 | 0 | 0 | -0.5387 | -0.5387 | closed
68 | N. Kurlak | 4 | 0.5 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.1 | 0.1 | opened | 68 | N. Kurlak | 4 | 0.015217 | 0.51522 | 0.6 | 120 | -0.084783 | 0 | 0.6 | 0.084783 | 0.084783 | opened
69 | Nikolaevka | 4 | 1.46 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.04 | 0.04 | opened | 69 | Nikolaevka | 4 | 0.0032609 | 1.4633 | 1.5 | 120 | -0.036739 | 0 | 1.5 | 0.036739 | 0.036739 | opened
70 | Vasilyevka | 2.5 | 0.33 | 0.39 | 180 | 0.39 | 0 | 0.39 | 0.06 | 0.06 | opened | 70 | Vasilyevka | 2.5 | 0.030109 | 0.36011 | 0.39 | 180 | -0.029891 | 0 | 0.39 | 0.029891 | 0.029891 | opened
71 | Avangard | 2.5 | 0.76 | 0.91 | 120 | 0.91 | 0 | 0.91 | 0.15 | 0.15 | opened | 71 | Avangard | 2.5 | 0.11783 | 0.87783 | 0.91 | 120 | -0.032174 | 0 | 0.91 | 0.032174 | 0.032174 | opened
72 | Orlovka | 2.5 | 0.4 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.08 | 0.08 | opened | 72 | Orlovka | 2.5 | 0.0097826 | 0.40978 | 0.48 | 90 | -0.070217 | 0 | 0.48 | 0.070217 | 0.070217 | opened
73 | N. Chigla | 2.5 | 0.66 | 0.79 | 120 | 0.79 | 0 | 0.79 | 0.13 | 0.13 | opened | 73 | N. Chigla | 2.5 | 0.092391 | 0.75239 | 0.79 | 120 | -0.037609 | 0 | 0.79 | 0.037609 | 0.037609 | opened
74 | Troitskoe-1 | 1.6 | 0.11 | 0.11 | 120 | 0.11 | 0 | 0.11 | 0 | 0 | opened | 74 | Troitskoe-1 | 1.6 | 0 | 0.11 | 0.11 | 120 | 0 | 0 | 0.11 | 0 | 0 | opened
75 | Tishanka | 2.5 | 1.26 | 1.51 | 120 | 1.51 | 0 | 1.51 | 0.25 | 0.25 | opened | 75 | Tishanka | 2.5 | 0.1163 | 1.3763 | 1.51 | 120 | -0.1337 | 0 | 1.51 | 0.1337 | 0.1337 | opened
76 | Kalacheevskaya | 6.3 | 0.59 | 1 | 24 hours | 1 | 0 | 1 | 0.41 | 0.41 | opened | 76 | Kalacheevskaya | 6.3 | 0 | 0.59 | 1 | 24 hours | -0.41 | 0 | 1 | 0.41 | 0.41 | opened
77 | B.Kazinka | 6.3 | 0.52 | 0 | 0 | 0 | 0 | 0 | -0.52 | -0.52 | closed | 77 | B.Kazinka | 6.3 | 5.9887 | 6.5088 | 0 | 0 | 6.5088 | 0 | 0 | -6.5088 | -6.5088 | closed
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 0.52 | 0 | 0 | 0 | 0 | 0 | -0.52 |  |  |  | Sн. LV, МVА | 6.3 | 5.9887 | 6.5088 | 0 | 0 | 6.5088 | 0 | 0 | -6.5088
78 | Derezovka | 6.3 | 0.34 | 0 | 0 | 0 | 0 | 0 | -0.34 | -0.34 | closed | 78 | Derezovka | 6.3 | 0.017 | 0.357 | 0 | 0 | 0.357 | 0 | 0 | -0.357 | -0.357 | closed
79 | Osetrovka | 6.3 | 0 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.5 | 1.5 | opened | 79 | Osetrovka | 6.3 | 2.6424 | 2.6424 | 1.5 | 24 hours | 1.1424 | 0 | 1.5 | -1.1424 | -1.1424 | closed
80 | sovkhoz Radchensky | 10 | 1.27 | 2 | 24 hours | 2 | 0 | 2 | 0.73 | -1.14 | closed | 80 | sovkhoz Radchensky | 10 | 0.01325 | 1.2833 | 2 | 24 hours | -0.71675 | 0 | 2 | 0.71675 | -1.14 | closed
| Sн. MV, МVА | 10 | 1.14 | 0 | 24 hours | 0 | 0 | 0 | -1.14 |  |  |  | Sн. MV, МVА | 10 | 0 | 1.14 | 0 | 24 hours | 1.14 | 0 | 0 | -1.14
| Sн. LV, МVА | 10 | 0.13 | 2 | 24 hours | 2 | 0 | 2 | 1.87 |  |  |  | Sн. LV, МVА | 10 | 0.01325 | 0.14325 | 2 | 24 hours | -1.8567 | 0 | 2 | 1.8567
81 | Klepovka | 4 | 1.37 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0.13 | 0.13 | opened | 81 | Klepovka | 4 | 0.056 | 1.426 | 1.5 | 120 | -0.074 | 0 | 1.5 | 0.074 | 0.074 | opened
82 | Krasnopolye | 4 | 0.36 | 1 | 120 | 1 | 0 | 1 | 0.64 | 0.64 | opened | 82 | Krasnopolye | 4 | 0.008 | 0.368 | 1 | 120 | -0.632 | 0 | 1 | 0.632 | 0.632 | opened
83 | Nikolskoe | 2.5 | 0.46 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.04 | 1.04 | opened | 83 | Nikolskoe | 2.5 | 0.004 | 0.464 | 1.5 | 45 | -1.036 | 0 | 1.5 | 1.036 | 1.036 | opened
84 | N. Liman | 2.5 | 0.39 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.11 | 1.11 | opened | 84 | N. Liman | 2.5 | 0.012 | 0.402 | 1.5 | 45 | -1.098 | 0 | 1.5 | 1.098 | 1.098 | opened
85 | Bereznyagi | 2.5 | 0.25 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 85 | Bereznyagi | 2.5 | 0.014 | 0.264 | 1.5 | 45 | -1.236 | 0 | 1.5 | 1.236 | 1.236 | opened
86 | Kr.Flot | 2.5 | 0.26 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1.24 | 1.24 | opened | 86 | Kr.Flot | 2.5 | 0.0877 | 0.3477 | 1.5 | 45 | -1.1523 | 0 | 1.5 | 1.1523 | 1.1523 | opened
87 | R. Zhuravka | 2.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | -0.7 | -0.7 | closed | 87 | R. Zhuravka | 2.5 | 0.014 | 0.714 | 0 | 0 | 0.714 | 0 | 0 | -0.714 | -0.714 | closed
88 | Gorokhovka | 2.5 | 0.54 | 1.5 | 45 | 1.5 | 0 | 1.5 | 0.96 | 0.96 | opened | 88 | Gorokhovka | 2.5 | 0.0483 | 0.5883 | 1.5 | 45 | -0.9117 | 0 | 1.5 | 0.9117 | 0.9117 | closed
89 | Livenka | 2.5 | 0.44 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0.06 | 0.06 | opened | 89 | Livenka | 2.5 | 0.0085 | 0.4485 | 0.5 | 24 hours | -0.0515 | 0 | 0.5 | 0.0515 | 0.0515 | opened
90 | R.Buylovka | 2.5 | 0.5 | 1.5 | 45 | 1.5 | 0 | 1.5 | 1 | 1 | opened | 90 | R.Buylovka | 2.5 | 0.0795 | 0.5795 | 1.5 | 45 | -0.9205 | 0 | 1.5 | 0.9205 | 0.9205 | opened
91 | Shurinovka | 2.5 | 0.31 | 0 | 0 | 0 | 0 | 0 | -0.31 | -0.31 | closed | 91 | Shurinovka | 2.5 | 0.002 | 0.312 | 0 | 0 | 0.312 | 0 | 0 | -0.312 | -0.312 | closed
92 | Tvyordokhlebovka | 4 | 0.27 | 0 | 0 | 0 | 0 | 0 | -0.27 | -0.27 | closed | 92 | Tvyordokhlebovka | 4 | 0.004 | 0.274 | 0 | 0 | 0.274 | 0 | 0 | -0.274 | -0.274 | closed
93 | Krinitsa | 2.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | -0.25 | -0.25 | closed | 93 | Krinitsa | 2.5 | 0.00596 | 0.25596 | 0 | 0 | 0.25596 | 0 | 0 | -0.25596 | -0.25596 | closed
94 | Krasnogorovka | 2.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.1 | closed | 94 | Krasnogorovka | 2.5 | 0.0114 | 0.1114 | 0 | 0 | 0.1114 | 0 | 0 | -0.1114 | -0.1114 | closed
| Two- and more transformer SS | [10 empty] | 2: Two- and more transformer SS
95 | No.2 | 25+25 | 18.72 | 4.8 | 120 | 13.92 | 0 | 26.25 | 12.33 | 12.33 | opened | 95 | No.2 | 25+25 | 18.007 | 36.727 | 4.8 | 120 | 31.927 | 0 | 26.25 | -5.677 | -5.677 | opened
96 | No.3 | 6,3 + 10 | 8.89 | 2.5 | 120 | 6.39 | 0 | 6.615 | 0.225 | 0.225 | opened | 96 | No.3 | 6,3 + 10 | 0.458 | 9.348 | 2.5 | 120 | 6.848 | 0 | 6.615 | -0.233 | -0.233 | opened
97 | No. 4 | 10+10+15 | 14.72 | 0 | 0 | 14.72 | 0 | 21 | 6.28 | 6.28 | opened | 97 | No. 4 | 10+10+15 | 0 | 14.72 | 0 | 0 | 14.72 | 0 | 21 | 6.28 | 6.28 | opened
98 | No. 6 | 25+32 | 15.85 | 1.6 | 120 | 14.25 | 0 | 26.25 | 12 | 12 | opened | 98 | No. 6 | 25+32 | 4.919 | 20.769 | 1.6 | 120 | 19.169 | 0 | 26.25 | 7.081 | 7.081 | opened
99 | No. 8 | 4+4+4 | 6.88 | 0 | 0 | 6.88 | 0 | 8.4 | 1.52 | 1.52 | opened | 99 | No. 8 | 4+4+4 | 0.3475 | 7.2275 | 0 | 0 | 7.2275 | 0 | 8.4 | 1.1725 | 1.1725 | opened
100 | No. 9 | 16+25 | 23.6 | 3.3 | 120 | 20.3 | 0 | 16.8 | -3.5 | -3.5 | closed | 100 | No. 9 | 16+25 | 10.927 | 34.527 | 3.3 | 120 | 31.227 | 0 | 16.8 | -14.427 | -14.427 | Change of transformers is provided
101 | No. 10 | 20+20 | 30.4 | 13.3 | 120 | 17.1 | 0 | 21 | 3.9 | 3.9 | opened | 101 | No. 10 | 20+20 | 14.678 | 45.078 | 13.3 | 120 | 31.778 | 0 | 21 | -10.778 | -10.778 | Reconstruction is provided
102 | No. 13 | 6,3+6,3 | 9.52 | 1 | 120 | 8.52 | 0 | 6.615 | -1.905 | -1.905 | closed | 102 | No. 13 | 6,3+6,3 | 3.591 | 13.111 | 4.2 | 120 | 8.911 | 0 | 6.615 | -2.296 | -2.296 | Change of transformers is provided
103 | No. 14 | 31,5+31,5 | 16.06 | 1.3 | 120 | 14.76 | 0 | 33.075 | 18.315 | 18.315 | opened | 103 | No. 14 | 31,5+31,5 | 0.486 | 16.546 | 1.3 | 120 | 15.246 | 0 | 33.075 | 17.829 | 17.829 | opened
| Sн. MV, МVА | 31,5+31,5 | 1.34 | 0 | 0 | 1.34 | 0 | 33.075 | 31.735 |  |  |  | Sн. MV, МVА | 31,5+31,5 | 0 | 1.34 | 0 | 0 | 1.34 | 0 | 33.075 | 31.735
| Sн. LV, МVА | 31,5+31,5 | 14.72 | 1.3 | 120 | 13.42 | 0 | 33.075 | 19.655 |  |  |  | Sн. LV, МVА | 31,5+31,5 | 0.486 | 15.206 | 1.3 | 120 | 13.906 | 0 | 33.075 | 19.169
104 | No. 15 | 40,5+40,5+63,0 | 44.01 | 44.01 | 120 | 0 | 0 | 85.05 | 85.05 | 85.05 | opened | 104 | No. 15 | 40,5+40,5+63,0 | 0 | 44.01 | 44.01 | 120 | 0 | 0 | 85.05 | 85.05 | 85.05 | opened
| Sн. MV, МVА | 40,5+40,5+63,0 | 44.01 | 44.01 | 120 | 0 | 0 | 85.05 | 85.05 |  |  |  | Sн. MV, МVА | 40,5+40,5+63,0 | 0 | 44.01 | 44.01 | 120 | 0 | 0 | 85.05 | 85.05
| Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05 |  |  |  | Sн. LV, МVА | 40,5+40,5+63,0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.05 | 85.05
105 | No. 16 | 31,5+31,5+40,0 | 59.26 | 4 | 120 | 55.26 | 0 | 66.15 | 10.89 | 10.89 | opened | 105 | No. 16 | 31,5+31,5+40,0 | 5.338 | 64.598 | 4 | 120 | 60.598 | 0 | 66.15 | 5.552 | 5.552 | opened
| Sн. MV, МVА | 31,5+31,5 | 10 | 0 | 0 | 10 | 0 | 33.075 | 23.075 |  |  |  | Sн. MV, МVА | 31,5+31,5 | 0 | 10 | 0 | 0 | 10 | 0 | 33.075 | 23.075
| Sн. LV, МVА | 31,5+31,5+40,0 | 49.26 | 4 | 120 | 45.26 | 0 | 66.15 | 20.89 |  |  |  | Sн. LV, МVА | 31,5+31,5+40,0 | 5.338 | 54.598 | 4 | 120 | 50.598 | 0 | 66.15 | 15.552
106 | No. 18 | 6,3+6,3 | 2.19 | 0 | 0 | 2.19 | 0 | 6.615 | 4.425 | 4.425 | opened | 106 | No. 18 | 6,3+6,3 | 2.2775 | 4.4675 | 0 | 0 | 4.4675 | 0 | 6.615 | 2.1475 | 2.1475 | opened
107 | No. 20 | 25,0+25,0 | 15.24 | 5.6 | 120 | 9.64 | 0 | 26.25 | 16.61 | 16.61 | opened | 107 | No. 20 | 25,0+25,0 | 1.752 | 16.992 | 5.6 | 120 | 11.392 | 0 | 26.25 | 14.858 | 14.858 | opened
| Sн. MV, МVА | 25,0+25,0 | 3.5 | 0 | 0 | 3.5 | 0 | 26.25 | 22.75 |  |  |  | Sн. MV, МVА | 25+25 | 0.191 | 3.691 | 0 | 0 | 3.691 | 0 | 26.25 | 22.559
| Sн. LV, МVА | 25,0+25,0 | 15.24 | 5.6 | 120 | 9.64 | 0 | 26.25 | 16.61 |  |  |  | Sн. LV, МVА | 25+25 | 1.561 | 16.801 | 5.6 | 120 | 11.201 | 0 | 26.25 | 15.049
108 | No. 21 | 25,0+20,0+40,0 | 37.18 | 4.6 | 180 | 32.58 | 0 | 47.25 | 14.67 | 14.67 | opened | 108 | No. 21 | 25,0+20,0+40,0 | 25.844 | 63.024 | 4.6 | 180 | 58.424 | 0 | 47.25 | -11.174 | -11.174 | Reconstruction is provided
109 | No. 22 | 10+10 | 4.7 | 1.4 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | opened | 109 | No. 22 | 10+10 | 0.709 | 5.409 | 1.4 | 120 | 4.009 | 0 | 10.5 | 6.491 | 6.491 | opened
110 | No. 23 | 7,5+6,3 | 6.82 | 0.8 | 120 | 6.02 | 0 | 6.615 | 0.595 | 0.595 | opened | 110 | No. 23 | 7,5+6,3 | 0.792 | 7.612 | 0.8 | 120 | 6.812 | 0 | 6.615 | -0.197 | -0.197 | Change of transformers is provided
111 | No. 24 | 3,2+4,0 | 1.97 | 0 | 0 | 1.97 | 0 | 3.36 | 1.39 | 1.39 | opened | 111 | No. 24 | 3,2+4,0 | 0 | 1.97 | 0 | 0 | 1.97 | 0 | 3.36 | 1.39 | 1.39 | opened
112 | No. 25 | 40+40+40 | 39.18 | 3.8 | 120 | 35.38 | 0 | 84 | 48.62 | 48.62 | opened | 112 | No. 25 | 40+40 | 12.259 | 51.439 | 3.8 | 120 | 47.639 | 0 | 84 | 36.361 | 36.361 | opened
113 | No. 27 | 32,0+32,0+32,0 | 38.9 | 3.3 | 180 | 35.6 | 0 | 67.2 | 31.6 | 31.6 | opened | 113 | No. 27 | 32,0+32,0+32,0 | 5.576 | 44.476 | 3.3 | 180 | 41.176 | 0 | 67.2 | 26.024 | 26.024 | opened
114 | No. 28 | 10+10 | 12 | 0 | 0 | 12 | 0 | 10.5 | -1.5 | -1.5 | closed | 114 | No. 28 | 10+10 | 3.6057 | 15.6057 | 0 | 0 | 15.6057 | 0 | 10.5 | -5.1057 | -5.1057 | Change of transformers is provided
115 | No.29 | 25+25 | 27.75 | 8.4 | 120 | 19.35 | 0 | 26.25 | 6.9 | 6.9 | opened | 115 | No.29 | 25+25 | 5.913 | 33.663 | 8.4 | 120 | 25.263 | 0 | 26.25 | 0.987 | 0.987 | opened
| Sн. MV, МVА | 25+25 | 11.7 | 4.2 | 120 | 7.5 | 0 | 26.25 | 18.75 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 11.7 | 4.2 | 120 | 7.5 | 0 | 26.25 | 18.75
| Sн. LV, МVА | 25+25 | 16.05 | 4.2 | 120 | 11.85 | 0 | 26.25 | 14.4 |  |  |  | Sн. LV, МVА | 25+25 | 5.913 | 21.963 | 4.2 | 120 | 17.763 | 0 | 26.25 | 8.487
116 | No. 30 | 40+40+63,0 | 70.53 | 5.1 | 120 | 65.43 | 0 | 84 | 18.57 | 18.57 | opened | 116 | No. 30 | 40+40+63,0 | 17.731 | 88.261 | 5.1 | 120 | 83.161 | 0 | 84 | 0.839 | 0.839 | opened
| Sн. MV, МVА | 40+40 | 12 | 0 | 0 | 12 | 0 | 42 | 30 |  |  |  | Sн. MV, МVА | 40+40+63 | 2.174 | 14.174 | 0 | 0 | 14.174 | 0 | 42 | 27.826
| Sн. LV, МVА | 40+40+63 | 58.53 | 5.1 | 120 | 53.43 | 0 | 84 | 30.57 |  |  |  | Sн. LV, МVА | 40+40+63 | 15.557 | 74.087 | 5.1 | 120 | 68.987 | 0 | 84 | 15.013
117 | No. 32 | 10+16 | 18.27 | 8 | 120 | 10.27 | 0 | 10.5 | 0.23 | 0.23 | opened | 117 | No. 32 | 10+16 | 0.0032 | 18.2732 | 8 | 120 | 10.2732 | 0 | 10.5 | 0.2268 | 0.2268 | opened
| Sн. MV, МVА | 10+16 | 15.6 | 8 | 120 | 7.6 | 0 | 10.5 | 2.9 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 15.6 | 8 | 120 | 7.6 | 0 | 10.5 | 2.9
| Sн. LV, МVА | 10+16 | 2.67 | 0 | 0 | 2.67 | 0 | 10.5 | 7.83 |  |  |  | Sн. LV, МVА | 10+16 | 0.0032 | 2.6732 | 0 | 0 | 2.6732 | 0 | 10.5 | 7.8268
118 | No. 33 | 4,0+4,0 | 1.55 | 0 | 0 | 1.55 | 0 | 4.2 | 2.65 | 2.65 | opened | 118 | No. 33 | 4,0+4,0 | 0.3106 | 1.8606 | 0 | 0 | 1.8606 | 0 | 4.2 | 2.3394 | 2.3394 | opened
119 | No. 34 | 2,5+1,8 | 2.32 | 0 | 0 | 2.32 | 0 | 1.89 | -0.43 | -0.43 | closed | 119 | No. 34 | 2,5+1,8 | 0 | 2.32 | 0 | 0 | 2.32 | 0 | 1.89 | -0.43 | -0.43 | closed
120 | No.35 | 10+10 | 13.1 | 2.4 | 120 | 10.7 | 0 | 10.5 | -0.2 | -0.2 | cс | 120 | No.35 | 10+10 | 0.012 | 13.112 | 2.4 | 120 | 10.712 | 0 | 10.5 | -0.212 | -0.212 | Reconstruction is provided
121 | No. 36 | 6,3+10 | 1.33 | 0 | 0 | 1.33 | 0 | 6.615 | 5.285 | 5.285 | opened | 121 | No. 36 | 6,3+10 | 0.0173 | 1.3473 | 0 | 0 | 1.3473 | 0 | 6.615 | 5.2677 | 5.2677 | opened
122 | No. 39 | 25+25 | 27.82 | 7.1 | 120 | 20.72 | 0 | 26.25 | 5.53 | 5.53 | opened | 122 | No. 39 | 25+25 | 3 | 30.82 | 4.1 | 120 | 26.72 | 0 | 26.25 | -0.47 | -0.47 | Change of transformers is provided
123 | No. 41 | 10+10 | 10.4 | 0 | 0 | 10.4 | 0 | 10.5 | 0.1 | 0.1 | opened | 123 | No. 41 | 10+10 | 0 | 10.4 | 0 | 0 | 10.4 | 0 | 10.5 | 0.1 | 0.1 | opened
124 | No. 42 | 25+40 | 16.59 | 1.6 | 120 | 14.99 | 0 | 26.25 | 11.26 | 11.26 | opened | 124 | No. 42 | 25+40 | 9.55 | 26.14 | 1.6 | 120 | 24.54 | 0 | 26.25 | 1.71 | 1.71 | opened
125 | No. 43 | 63+63 | 18.63 | 1.6 | 60 | 17.03 | 0 | 66.15 | 49.12 | 49.12 | opened | 125 | No. 43 | 63+63 | 9.962 | 28.592 | 1.6 | 60 | 26.992 | 0 | 66.15 | 39.158 | 39.158 | opened
126 | No. 45 | 63+63 | 27.28 | 7.1 | 120 | 20.18 | 0 | 66.15 | 45.97 | 45.97 | opened | 126 | No. 45 | 63+63 | 34.146 | 61.426 | 7.1 | 120 | 54.326 | 0 | 66.15 | 11.824 | 11.824 | opened
127 | No. 47 | 25+25 | 13.46 | 0 | 0 | 13.46 | 0 | 26.25 | 12.79 | 12.79 | opened | 127 | No. 47 | 25+25 | 0.032 | 13.492 | 0 | 0 | 13.492 | 0 | 26.25 | 12.758 | 12.758 | opened
| Sн. MV, МVА | 25+25 | 8.1 | 0 | 0 | 8.1 | 0 | 26.25 | 18.15 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 8.1 | 0 | 0 | 8.1 | 0 | 26.25 | 18.15
| Sн. LV, МVА | 25+25 | 5.36 | 0 | 0 | 5.36 | 0 | 26.25 | 20.89 |  |  |  | Sн. LV, МVА | 25+25 | 0.032 | 5.392 | 0 | 0 | 5.392 | 0 | 26.25 | 20.858
128 | Panino | 16+16 | 10.72 | 5.2 | 120 | 5.52 | 0 | 16.8 | 11.28 | 10.68 | opened | 128 | Panino | 16+16 | 0.2765 | 10.9965 | 5.2 | 120 | 5.7965 | 0 | 16.8 | 11.0035 | 10.4035 | opened
| Sн. MV, МVА | 16+16 | 4.4 | 5 | 120 | -0.6 | 0 | 16.8 | 17.4 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.4 | 5 | 120 | -0.6 | 0 | 16.8 | 17.4
| Sн. LV, МVА | 16+16 | 6.32 | 0.2 | 120 | 6.12 | 0 | 16.8 | 10.68 |  |  |  | Sн. LV, МVА | 16+16 | 0.2765 | 6.5965 | 0.2 | 120 | 6.3965 | 0 | 16.8 | 10.4035
129 | Kriusha | 2,5+2,5 | 0.97 | 0 | 0 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | opened | 129 | Kriusha | 2,5+2,5 | 0.0263 | 0.9963 | 0 | 0 | 0.9963 | 0 | 2.625 | 1.6287 | 1.6287 | opened
130 | Seed plant | 4+4 | 1.65 | 0 | 0 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | opened | 130 | Seed plant | 4+4 | 0.023 | 1.673 | 0 | 0 | 1.673 | 0 | 4.2 | 2.527 | 2.527 | opened
131 | Progress | 2,5+10 | 0.51 | 0.5315 | 120 | -0.0215 | 0 | 2.625 | 2.6465 | 2.6465 | opened | 131 | Progress | 2,5+10 | 0.0215 | 0.5315 | 0.5315 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
132 | Katukhovka | 2,5+2,5 | 0.38 | 0.385 | 120 | -0.005 | 0 | 2.625 | 2.63 | 2.63 | opened | 132 | Katukhovka | 2,5+2,5 | 0.005 | 0.385 | 0.385 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
133 | Kr.Liman | 2,5+4,0 | 0.88 | 0 | 0 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 133 | Kr.Liman | 2,5+4,0 | 0.017 | 0.897 | 0 | 0 | 0.897 | 0 | 2.625 | 1.728 | 1.728 | opened
134 | Ivanovka | 1,8+1,6 | 0.36 | 0.36 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 134 | Ivanovka | 1,8+1,6 | 0 | 0.36 | 0.36 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
135 | Don | 2,5+2,5 | 2.85 | 0 | 0 | 2.85 | 0 | 2.625 | -0.225 | -0.225 | closed | 135 | Don | 2,5+2,5 | 0.4687 | 3.3187 | 0 | 0 | 3.3187 | 0 | 2.625 | -0.6937 | -0.6937 | closed
136 | Yablochnoe | 4+4 | 0.27 | 0 | 0 | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened | 136 | Yablochnoe | 4+4 | 0.01 | 0.28 | 0 | 0 | 0.28 | 0 | 4.2 | 3.92 | 3.92 | opened
137 | St.Nikolskoe | 2,5+2,5 | 0.95 | 1.227 | 120 | -0.277 | 0 | 2.625 | 2.902 | 2.902 | opened | 137 | St.Nikolskoe | 2,5+2,5 | 0.277 | 1.227 | 1.227 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
138 | Rudkino | 4,0+4,0 | 2.27 | 0 | 0 | 2.27 | 0 | 4.2 | 1.93 | 1.93 | opened | 138 | Rudkino | 4,0+4,0 | 0.0945 | 2.3645 | 0 | 0 | 2.3645 | 0 | 4.2 | 1.8355 | 1.8355 | opened
139 | Khokhol-1 | 6,3+6,3 | 4.96 | 0 | 0 | 4.96 | 0 | 6.615 | 1.655 | 1.655 | opened | 139 | Khokhol-1 | 6,3+6,3 | 1.147 | 6.107 | 0 | 0 | 6.107 | 0 | 6.615 | 0.508 | 0.508 | opened
140 | No. 11 | 5,6+6,3 | 2.53 | 0.5 | 120 | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened | 140 | No. 11 | 5,6+6,3 | 0 | 2.53 | 0.5 | 120 | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened
| Sн. MV, МVА | 5,6+6,3 | 0.5 | 0.5 | 120 | 0 | 0 | 5.88 | 5.88 |  |  |  | Sн. MV, МVА | 5,6+6,3 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 5.88 | 5.88
| Sн. LV, МVА | 5,6+6,3 | 2.03 | 0 | 0 | 2.03 | 0 | 5.88 | 3.85 |  |  |  | Sн. LV, МVА | 5,6+6,3 | 0 | 2.03 | 0 | 0 | 2.03 | 0 | 5.88 | 3.85
141 | Beryozovka | 4+4 | 3.22 | 0 | 0 | 3.22 | 0 | 4.2 | 0.98 | 0.98 | opened | 141 | Beryozovka | 4+4 | 0.0945 | 3.3145 | 0 | 0 | 3.3145 | 0 | 4.2 | 0.8855 | 0.8855 | opened
142 | N.Zhivotinnoe | 4+6,3 | 3.54 | 1 | 120 | 2.54 | 0 | 4.2 | 1.66 | 1.66 | opened | 142 | N.Zhivotinnoe | 4+6,3 | 1.461 | 5.001 | 1 | 120 | 4.001 | 0 | 4.2 | 0.199 | 0.199 | opened
143 | Ramon-1 | 4+4+4 | 5.95 | 6.85 | 120 | -0.9 | 0 | 8.4 | 9.3 | 9.3 | opened | 143 | Ramon-1 | 4+4+4 | 0.9 | 6.85 | 6.85 | 120 | 0 | 0 | 8.4 | 8.4 | 8.4 | opened
144 | Ramon-2 | 16,0+16,0 | 17.43 | 10.48 | 120 | 6.95 | 0 | 16.8 | 9.85 | 9.85 | opened | 144 | Ramon-2 | 16,0+16,0 | 4.8406 | 22.2706 | 10.48 | 120 | 11.7906 | 0 | 16.8 | 5.0094 | 5.0094 | opened
| Sн. MV, МVА | 16,0+16,0 | 13.8 | 6.85 | 0 | 6.95 | 0 | 16.8 | 9.85 |  |  |  | Sн. MV, МVА | 16+16 | 4.348 | 18.148 | 6.85 | 0 | 11.298 | 0 | 16.8 | 5.502
| Sн. LV, МVА | 16,0+16,0 | 3.63 | 3.63 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. LV, МVА | 16+16 | 0.4926 | 4.1226 | 3.63 | 120 | 0.4926 | 0 | 16.8 | 16.3074
145 | Vereyka | 2,5+2,5 | 1.26 | 0 | 0 | 1.26 | 0 | 2.625 | 1.365 | 1.365 | opened | 145 | Vereyka | 2,5+2,5 | 0.018 | 1.278 | 0 | 0 | 1.278 | 0 | 2.625 | 1.347 | 1.347 | opened
146 | Complex | 10+10 | 5.24 | 3.4 | 180 | 1.84 | 0 | 10.5 | 8.66 | 8.36 | opened | 146 | Complex | 10+10 | 0.016 | 5.256 | 3.4 | 180 | 1.856 | 0 | 10.5 | 8.644 | 8.344 | opened
| Sн. MV, МVА | 10+10 | 2.8 | 3.1 | 180 | -0.3 | 0 | 10.5 | 10.8 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.8 | 3.1 | 180 | -0.3 | 0 | 10.5 | 10.8
| Sн. LV, МVА | 10+10 | 2.44 | 0.3 | 180 | 2.14 | 0 | 10.5 | 8.36 |  |  |  | Sн. LV, МVА | 10+10 | 0.016 | 2.456 | 0.3 | 180 | 2.156 | 0 | 10.5 | 8.344
147 | N.Veduga | 16+16 | 4.54 | 2.9 | 120 | 1.64 | 0 | 16.8 | 15.16 | 15.16 | opened | 147 | N.Veduga | 16+16 | 0 | 4.54 | 2.9 | 120 | 1.64 | 0 | 16.8 | 15.16 | 15.16 | opened
| Sн. MV, МVА | 16+16 | 2.9 | 2.9 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 2.9 | 2.9 | 120 | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 1.64 | 0 | 0 | 1.64 | 0 | 16.8 | 15.16 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 1.64 | 0 | 0 | 1.64 | 0 | 16.8 | 15.16
148 | Golosnovka | 2,5+2,5 | 0.49 | 0.512 | 120 | -0.022 | 0 | 2.625 | 2.647 | 2.647 | opened | 148 | Golosnovka | 2,5+2,5 | 0.022 | 0.512 | 0.512 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
149 | Medvezhye | 3,2+4,0 | 1.11 | 0 | 0 | 1.11 | 0 | 3.36 | 2.25 | 2.25 | opened | 149 | Medvezhye | 3,2+4,0 | 0.097 | 1.207 | 0 | 0 | 1.207 | 0 | 3.36 | 2.153 | 2.153 | opened
150 | St.Veduga | 4+4 | 1.22 | 0 | 0 | 1.22 | 0 | 4.2 | 2.98 | 2.98 | opened | 150 | St.Veduga | 4+4 | 0.034 | 1.254 | 0 | 0 | 1.254 | 0 | 4.2 | 2.946 | 2.946 | opened
151 | M.Pokrovka | 2,5+2,5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 151 | M.Pokrovka | 2,5+2,5 | 0.01 | 0.57 | 0 | 0 | 0.57 | 0 | 2.625 | 2.055 | 2.055 | opened
152 | Turovo-2 | 2,5+2,5 | 1.2 | 0.7 | 120 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 152 | Turovo-2 | 2,5+2,5 | 0.0625 | 1.2625 | 0.7 | 120 | 0.5625 | 0 | 2.625 | 2.0625 | 2.0625 | opened
153 | S.Lipyagi | 3,2+2,5 | 1.4 | 2.9638 | 120 | -1.5638 | 0 | 2.625 | 4.1888 | 4.1888 | opened | 153 | S.Lipyagi | 3,2+2,5 | 1.5638 | 2.9638 | 2.9638 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
154 | N.Devitsk | 25+16 | 5.77 | 8.2225 | 180 | -2.4525 | 0 | 16.8 | 19.2525 | 16.8 | opened | 154 | N.Devitsk | 25+16 | 2.4525 | 8.2225 | 8.2225 | 180 | 0 | 0 | 16.8 | 16.8 | 16.7705 | opened
| Sн. MV, МVА | 25+16 | 2.8 | 2.8 | 180 | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 25+16 | 0 | 2.8 | 2.8 | 180 | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 25+16 | 2.97 | 5.393 | 180 | -2.423 | 0 | 16.8 | 19.223 |  |  |  | Sн. LV, МVА | 25+16 | 2.4525 | 5.4225 | 5.393 | 180 | 0.0295 | 0 | 16.8 | 16.7705
155 | Repyevka | 4+4 | 2.68 | 0.5 | 120 | 2.18 | 0 | 4.2 | 2.02 | 2.02 | opened | 155 | Repyevka | 4+4 | 0.0192 | 2.6992 | 0.5 | 120 | 2.1992 | 0 | 4.2 | 2.0008 | 2.0008 | opened
156 | Kr.Lipye | 16+16 | 11.22 | 2.9 | 120 | 8.32 | 0 | 16.8 | 8.48 | 8.48 | opened | 156 | Kr.Lipye | 16+16 | 0.0525 | 11.2725 | 2.9 | 120 | 8.3725 | 0 | 16.8 | 8.4275 | 8.4275 | opened
| Sн. MV, МVА | 16+16 | 9.7 | 2.7 | 120 | 7 | 0 | 16.8 | 9.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 9.7 | 2.7 | 120 | 7 | 0 | 16.8 | 9.8
| Sн. LV, МVА | 16+16 | 1.52 | 0.2 | 120 | 1.32 | 0 | 16.8 | 15.48 |  |  |  | Sн. LV, МVА | 16+16 | 0.0525 | 1.5725 | 0.2 | 120 | 1.3725 | 0 | 16.8 | 15.4275
157 | Ulyanovka | 6,3+6,3 | 0.44 | 0.04 | 60 | 0.4 | 0 | 6.615 | 6.215 | 6.215 | opened | 157 | Ulyanovka | 6,3+6,3 | 0.025 | 0.465 | 0.04 | 60 | 0.425 | 0 | 6.615 | 6.19 | 6.19 | opened
158 | МОB | 4+2,5 | 1.16 | 0.6 | 60 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 158 | МОB | 4+2,5 | 0.077 | 1.237 | 0.6 | 60 | 0.637 | 0 | 2.625 | 1.988 | 1.988 | opened
159 | L.Rossosh | 6,3+4,0 | 4.34 | 0 | 0 | 4.34 | 0 | 4.2 | -0.14 | -0.14 | opened | 159 | L.Rossosh | 6,3+4,0 | 0.2976 | 4.6376 | 0 | 0 | 4.6376 | 0 | 4.2 | -0.4376 | -0.4376 | opened
160 | Kashira | 2,5+2,5 | 0.67 | 0 | 0 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | opened | 160 | Kashira | 2,5+2,5 | 0.042 | 0.712 | 0 | 0 | 0.712 | 0 | 2.625 | 1.913 | 1.913 | opened
161 | Zaprudskoe | 2,5+2,5 | 1.62 | 0 | 0 | 1.62 | 0 | 2.625 | 1.005 | 1.005 | opened | 161 | Zaprudskoe | 2,5+2,5 | 0.247 | 1.867 | 0 | 0 | 1.867 | 0 | 2.625 | 0.758 | 0.758 | opened
162 | Moskovskoe | 10+10 | 11.48 | 1.8 | 120 | 9.68 | 0 | 10.5 | 0.82 | -0.1 | closed | 162 | Moskovskoe | 10+10 | 0.039 | 11.519 | 1.8 | 120 | 9.719 | 0 | 10.5 | 0.781 | -0.1 | closed
| Sн. MV, МVА | 10+10 | 10.6 | 0 | 0 | 10.6 | 0 | 10.5 | -0.1 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 10.6 | 0 | 0 | 10.6 | 0 | 10.5 | -0.1
| Sн. LV, МVА | 10+10 | 0.88 | 1.8 | 120 | -0.92 | 0 | 10.5 | 11.42 |  |  |  | Sн. LV, МVА | 10+10 | 0.039 | 0.919 | 1.8 | 120 | -0.881 | 0 | 10.5 | 11.381
163 | Semenovka | 2,5+4,0 | 0.84 | 0 | 0 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 163 | Semenovka | 2,5+4,0 | 0.0128 | 0.8528 | 0 | 0 | 0.8528 | 0 | 2.625 | 1.7722 | 1.7722 | opened
164 | Baygora | 2,5+2,5 | 1.01 | 1.03 | 60 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | opened | 164 | Baygora | 2,5+2,5 | 0.02 | 1.03 | 1.03 | 60 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
165 | Shukaevka | 2,5+2,5 | 0.9 | 0.1 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 165 | Shukaevka | 2,5+2,5 | 0.0245 | 0.9245 | 0.1 | 120 | 0.8245 | 0 | 2.625 | 1.8005 | 1.8005 | opened
166 | Uglyanets | 4+2,5 | 2.91 | 0.8 | 120 | 2.11 | 0 | 2.625 | 0.515 | 0.515 | opened | 166 | Uglyanets | 4+2,5 | 0.108 | 3.018 | 0.8 | 120 | 2.218 | 0 | 2.625 | 0.407 | 0.407 | opened
167 | V.Khava | 16+16 | 12.88 | 0.4 | 120 | 12.48 | 0 | 16.8 | 4.32 | 4.32 | opened | 167 | V.Khava | 16+16 | 0.274 | 13.154 | 0.4 | 120 | 12.754 | 0 | 16.8 | 4.046 | 4.046 | opened
| Sн. MV, МVА | 16+16 | 5.7 | 0 | 0 | 5.7 | 0 | 16.8 | 11.1 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 5.7 | 0 | 0 | 5.7 | 0 | 16.8 | 11.1
| Sн. LV, МVА | 16+16 | 7.18 | 0.4 | 120 | 6.78 | 0 | 16.8 | 10.02 |  |  |  | Sн. LV, МVА | 16+16 | 0.274 | 7.454 | 0.4 | 120 | 7.054 | 0 | 16.8 | 9.746
168 | Usman-1 | 10,0+6,3 | 11.25 | 0 | 0 | 11.25 | 0 | 6.615 | -4.635 | -4.635 | closed | 168 | Usman-1 | 10,0+6,3 | 5.1182 | 16.3682 | 0 | 0 | 16.3682 | 0 | 6.615 | -9.7532 | -9.7532 | Transition to 110 kv and reconstruction of SS are planned
169 | Usman-2 | 4+6,3 | 9.35 | 0 | 0 | 9.35 | 0 | 4.2 | -5.15 | -5.15 | closed | 169 | Usman-2 | 4+6,3 | 0.6936 | 10.0436 | 0 | 0 | 10.0436 | 0 | 4.2 | -5.8436 | -5.8436 | Transition to 110 kv and reconstruction of SS are planned
170 | R.Khava | 4+4 | 3.01 | 0.2 | 120 | 2.81 | 0 | 4.2 | 1.39 | 1.39 | opened | 170 | R.Khava | 4+4 | 0.7692 | 3.7792 | 0.2 | 120 | 3.5792 | 0 | 4.2 | 0.6208 | 0.6208 | opened
| Sн. MV, МVА | 4+4 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2 |  |  |  | Sн. MV, МVА | 4+4 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2
| Sн. LV, МVА | 4+4 | 3.01 | 0.2 | 120 | 2.81 | 0 | 4.2 | 1.39 |  |  |  | Sн. LV, МVА | 4+4 | 0.7692 | 3.7792 | 0.2 | 120 | 3.5792 | 0 | 4.2 | 0.6208
171 | No. 31 | 16+25 | 23.15 | 5.6 | 120 | 17.55 | 0 | 16.8 | -0.75 | -0.75 | closed | 171 | No. 31 | 16+25 | 0 | 23.15 | 5.6 | 120 | 17.55 | 0 | 16.8 | -0.75 | -0.75 | closed
| Sн. MV, МVА | 16+25 | 15 | 5.6 | 120 | 9.4 | 0 | 16.8 | 7.4 |  |  |  | Sн. MV, МVА | 16+25 | 0 | 15 | 5.6 | 120 | 9.4 | 0 | 16.8 | 7.4
| Sн. LV, МVА | 16+25 | 8.15 | 0 | 0 | 8.15 | 0 | 16.8 | 8.65 |  |  |  | Sн. LV, МVА | 16+25 | 0 | 8.15 | 0 | 0 | 8.15 | 0 | 16.8 | 8.65
172 | Maslovka | 2,5+4,0 | 2.25 | 0 | 0 | 2.25 | 0 | 2.625 | 0.375 | 0.375 | opened | 172 | Maslovka | 2,5+4,0 | 0.4032 | 2.6532 | 0 | 0 | 2.6532 | 0 | 2.625 | -0.0282 | -0.0282 | opened
173 | Podgornaya - district Line Maintenance Service | 16+16 | 3.91 | 1.6 | 180 | 2.31 | 0 | 16.8 | 14.49 | 14.49 | opened | 173 | Podgornaya - district Line Maintenance Service | 16+16 | 0.37973 | 4.2897 | 1.6 | 180 | 2.6897 | 0 | 16.8 | 14.1103 | 14.1103 | opened
| Sн. MV, МVА | 16+16 | 2 | 1.05 | 180 | 0.95 | 0 | 16.8 | 15.85 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 2 | 1.05 | 180 | 0.95 | 0 | 16.8 | 15.85
| Sн. LV, МVА | 16+16 | 1.91 | 0.55 | 180 | 1.36 | 0 | 16.8 | 15.44 |  |  |  | Sн. LV, МVА | 16+16 | 0.37973 | 2.2897 | 0.55 | 180 | 1.7397 | 0 | 16.8 | 15.0603
174 | Kantemirovka | 10+10 | 8.11 | 1.6 | 60 | 6.51 | 0 | 10.5 | 3.99 | 3.99 | opened | 174 | Kantemirovka | 10+10 | 0.8982 | 9.0082 | 1.6 | 60 | 7.4082 | 0 | 10.5 | 3.0918 | 3.0918 | opened
| Sн. MV, МVА | 10+10 | 5.4 | 1.4 | 60 | 4 | 0 | 10.5 | 6.5 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.4 | 1.4 | 60 | 4 | 0 | 10.5 | 6.5
| Sн. LV, МVА | 10+10 | 2.71 | 0.2 | 60 | 2.51 | 0 | 10.5 | 7.99 |  |  |  | Sн. LV, МVА | 10+10 | 0.8982 | 3.6082 | 0.2 | 60 | 3.4082 | 0 | 10.5 | 7.0918
175 | Rossosh | 16+16+40 | 21.3 | 2.68 | 120 | 18.62 | 0 | 33.6 | 14.98 | 14.98 | opened | 175 | Rossosh | 16+16+40 | 0.20251 | 21.5025 | 2.68 | 120 | 18.8225 | 0 | 33.6 | 14.7775 | 14.7775 | opened
| Sн. MV, МVА | 16+16+40 | 3.2 | 1.9 | 120 | 1.3 | 0 | 33.6 | 32.3 |  |  |  | Sн. MV, МVА | 16+16+40 | 0.05 | 3.25 | 1.9 | 120 | 1.35 | 0 | 33.6 | 32.25
| Sн. LV, МVА | 16+16+40 | 18.1 | 0.78 | 120 | 17.32 | 0 | 33.6 | 16.28 |  |  |  | Sн. LV, МVА | 16+16+40 | 0.1525 | 18.2525 | 0.78 | 120 | 17.4725 | 0 | 33.6 | 16.1275
176 | Kamenka r-naya | 16+16 | 3.25 | 0.97 | 120 | 2.28 | 0 | 16.8 | 14.52 | 14.52 | opened | 176 | Kamenka r-naya | 16+16 | 0.14596 | 3.396 | 0.97 | 120 | 2.426 | 0 | 16.8 | 14.374 | 14.374 | opened
| Sн. MV, МVА | 16+16 | 0.61 | 0 | 120 | 0.61 | 0 | 16.8 | 16.19 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 0.61 | 0 | 120 | 0.61 | 0 | 16.8 | 16.19
| Sн. LV, МVА | 16+16 | 2.64 | 0.97 | 120 | 1.67 | 0 | 16.8 | 15.13 |  |  |  | Sн. LV, МVА | 16+16 | 0.14596 | 2.786 | 0.97 | 120 | 1.816 | 0 | 16.8 | 14.984
177 | Korotoyak | 6,3+10 | 3.35 | 0.47 | 180 | 2.88 | 0 | 6.615 | 3.735 | 3.735 | opened | 177 | Korotoyak | 6,3+10 | 0.26913 | 3.6191 | 0.47 | 180 | 3.1491 | 0 | 6.615 | 3.4659 | 3.4659 | opened
| Sн. MV, МVА | 6,3+10 | 1.44 | 0 | 180 | 1.44 | 0 | 6.615 | 5.175 |  |  |  | Sн. MV, МVА | 6,3+10 | 0 | 1.44 | 0 | 180 | 1.44 | 0 | 6.615 | 5.175
| Sн. LV, МVА | 6,3+10 | 1.91 | 0.47 | 180 | 1.44 | 0 | 6.615 | 5.175 |  |  |  | Sн. LV, МVА | 6,3+10 | 0.26913 | 2.1791 | 0.47 | 180 | 1.7091 | 0 | 6.615 | 4.9059
178 | Ostrogozhsk | 40,5+40,5 | 12.84 | 2.4 | 60 | 10.44 | 0 | 42.525 | 32.085 | 32.085 | opened | 178 | Ostrogozhsk | 40,5+40,5 | 0 | 12.84 | 2.4 | 60 | 10.44 | 0 | 42.525 | 32.085 | 32.085 | opened
| Sн. MV, МVА | 40,5+40,5 | 12.63 | 2.4 | 60 | 10.23 | 0 | 42.525 | 32.295 |  |  |  | Sн. MV, МVА | 40,5+40,5 | 0 | 12.63 | 2.4 | 60 | 10.23 | 0 | 42.525 | 32.295
| Sн. LV, МVА | 40,5+40,5 | 0.21 | 0 | 60 | 0.21 | 0 | 42.525 | 42.315 |  |  |  | Sн. LV, МVА | 40,5+40,5 | 0 | 0.21 | 0 | 60 | 0.21 | 0 | 42.525 | 42.315
179 | Khrenovoe | 16+6,3 | 3.91 | 0 | 0 | 3.91 | 0 | 6.615 | 2.705 | 2.705 | opened | 179 | Khrenovoe | 16+6,3 | 0.0292 | 3.9392 | 0 | 0 | 3.9392 | 0 | 6.615 | 2.6758 | 2.6758 | opened
| Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615 |  |  |  | Sн. MV, МVА | 16+6,3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.615 | 6.615
| Sн. LV, МVА | 16+6,3 | 3.91 | 0 | 0 | 3.91 | 0 | 6.615 | 2.705 |  |  |  | Sн. LV, МVА | 16+6,3 | 0.0292 | 3.9392 | 0 | 0 | 3.9392 | 0 | 6.615 | 2.6758
180 | Oil extraction plant | 25+25 | 20 | 7.9 | 120 | 12.1 | 0 | 26.25 | 14.15 | 14.15 | opened | 180 | Oil extraction plant | 25+25 | 0.007 | 20.007 | 7.9 | 120 | 12.107 | 0 | 26.25 | 14.143 | 14.143 | opened
| Sн. MV, МVА | 25+25 | 7.9 | 7.9 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 7.9 | 7.9 | 120 | 0 | 0 | 26.25 | 26.25
| Sн. LV, МVА | 25+25 | 12.1 | 0 | 0 | 12.1 | 0 | 26.25 | 14.15 |  |  |  | Sн. LV, МVА | 25+25 | 0.007 | 12.107 | 0 | 0 | 12.107 | 0 | 26.25 | 14.143
181 | ANP | 6,3+6,3 | 1.35 | 0.39 | 120 | 0.96 | 0 | 6.615 | 5.655 | 5.655 | opened | 181 | ANP | 6,3+6,3 | 2.7682 | 4.1182 | 0.39 | 120 | 3.7282 | 0 | 6.615 | 2.8868 | 2.8868 | opened
182 | St. Kalitva | 6,3+6,3 | 0.86 | 0.86 | 240 | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 182 | St. Kalitva | 6,3+6,3 | 0.03415 | 0.89415 | 0.86 | 240 | 0.03415 | 0 | 6.615 | 6.5808 | 6.5808 | opened
183 | Nikanorovka | 2,5+6,3 | 0.5 | 0.5 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 183 | Nikanorovka | 2,5+6,3 | 0.031548 | 0.53155 | 0.5 | 240 | 0.031548 | 0 | 2.625 | 2.5935 | 2.5935 | opened
184 | PTF | 10+10 | 1.97 | 1 | 120 | 0.97 | 0 | 10.5 | 9.53 | 9.53 | opened | 184 | PTF | 10+10 | 0.06 | 2.03 | 1 | 120 | 1.03 | 0 | 10.5 | 9.47 | 9.47 | opened
185 | Korshevo | 6,3+6,3 | 0.56 | 0.56 | 120 | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 185 | Korshevo | 6,3+6,3 | 0.6755 | 1.2355 | 0.56 | 120 | 0.6755 | 0 | 6.615 | 5.9395 | 5.9395 | opened
186 | Davydovka | 6,3+6,3 | 5.39 | 2.11 | 240 | 3.28 | 0 | 6.615 | 3.335 | 3.335 | opened | 186 | Davydovka | 6,3+6,3 | 0.341 | 5.731 | 2.11 | 240 | 3.621 | 0 | 6.615 | 2.994 | 2.994 | opened
187 | the 2nd Pyatiletka | 6,3+6,3 | 1 | 0.66 | 120 | 0.34 | 0 | 6.615 | 6.275 | 6.275 | opened | 187 | the 2nd Pyatiletka | 6,3+6,3 | 0.084012 | 1.084 | 0.66 | 120 | 0.42401 | 0 | 6.615 | 6.191 | 6.191 | opened
188 | Liskinskaya | 10+16 | 0.93 | 0.72 | 120 | 0.21 | 0 | 10.5 | 10.29 | 10.29 | opened | 188 | Liskinskaya | 10+16 | 4.2265 | 5.1565 | 0.72 | 120 | 4.4365 | 0 | 10.5 | 6.0635 | 6.0635 | opened
189 | Olkhovatka | 4+4 | 2.55 | 2.55 | 180 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 189 | Olkhovatka | 4+4 | 0.56354 | 3.1135 | 2.55 | 180 | 0.56354 | 0 | 4.2 | 3.6365 | 3.6365 | opened
190 | Shaposhnikovka | 2,5+2,5 | 0.86 | 0.86 | 180 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 190 | Shaposhnikovka | 2,5+2,5 | 0.067036 | 0.92704 | 0.86 | 180 | 0.067036 | 0 | 2.625 | 2.558 | 2.558 | opened
191 | Karayashnik | 2,5+2,5 | 0.29 | 0.2875 | 180 | 0.0025 | 0 | 2.625 | 2.6225 | 2.6225 | opened | 191 | Karayashnik | 2,5+2,5 | 0.0105 | 0.3005 | 0.2875 | 180 | 0.013 | 0 | 2.625 | 2.612 | 2.612 | opened
192 | Saguny | 2,5+2,5 | 0.91 | 0.91 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 192 | Saguny | 2,5+2,5 | 0.038624 | 0.94862 | 0.91 | 120 | 0.038624 | 0 | 2.625 | 2.5864 | 2.5864 | opened
193 | Belogorye | 2,5+2,5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 193 | Belogorye | 2,5+2,5 | 0.081208 | 0.64121 | 0 | 0 | 0.64121 | 0 | 2.625 | 1.9838 | 1.9838 | opened
194 | Taly | 4+4 | 1.11 | 0 | 0 | 1.11 | 0 | 4.2 | 3.09 | 3.09 | opened | 194 | Taly | 4+4 | 0.08875 | 1.1987 | 0 | 0 | 1.1987 | 0 | 4.2 | 3.0013 | 3.0013 | opened
195 | Titarevka | 2,5+2,5 | 0.66 | 0 | 0 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | opened | 195 | Titarevka | 2,5+2,5 | 0.11355 | 0.77355 | 0 | 0 | 0.77355 | 0 | 2.625 | 1.8515 | 1.8515 | opened
196 | Mitrofanovka | 4+4 | 2.06 | 0 | 0 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | opened | 196 | Mitrofanovka | 4+4 | 0.20555 | 2.2656 | 0 | 0 | 2.2656 | 0 | 4.2 | 1.9345 | 1.9345 | opened
197 | Druzhba | 4+4 | 1.33 | 0.44 | 150 | 0.89 | 0 | 4.2 | 3.31 | 3.31 | opened | 197 | Druzhba | 4+4 | 0.1135 | 1.4435 | 0.44 | 150 | 1.0035 | 0 | 4.2 | 3.1965 | 3.1965 | opened
198 | Alexandrovka | 4+4 | 1.88 | 0 | 0 | 1.88 | 0 | 4.2 | 2.32 | 2.32 | opened | 198 | Alexandrovka | 4+4 | 0.0455 | 1.9255 | 0 | 0 | 1.9255 | 0 | 4.2 | 2.2745 | 2.2745 | opened
199 | Tkhorevka | 4+4 | 0.78 | 0.78 | 180 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 199 | Tkhorevka | 4+4 | 0.075272 | 0.85527 | 0.78 | 180 | 0.075272 | 0 | 4.2 | 4.1247 | 4.1247 | opened
200 | Marki | 2,5+2,5 | 0.27 | 0.27 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 200 | Marki | 2,5+2,5 | 0.00226 | 0.27226 | 0.27 | 120 | 0.00226 | 0 | 2.625 | 2.6227 | 2.6227 | opened
201 | Olkhov Log | 2,5+2,5 | 0.58 | 0.58 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 201 | Olkhov Log | 2,5+2,5 | 0.003036 | 0.58304 | 0.58 | 120 | 0.003036 | 0 | 2.625 | 2.622 | 2.622 | opened
202 | Boldyrevka | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 202 | Boldyrevka | 2,5+2,5 | 0.17966 | 0.89966 | 0 | 0 | 0.89966 | 0 | 2.625 | 1.7253 | 1.7253 | opened
203 | Pobeda | 4+4 | 0.5 | 0 | 0 | 0.5 | 0 | 4.2 | 3.7 | 3.7 | opened | 203 | Pobeda | 4+4 | 0.029736 | 0.52974 | 0 | 0 | 0.52974 | 0 | 4.2 | 3.6703 | 3.6703 | opened
204 | Lipovka | 4+4 | 1.34 | 0 | 0 | 1.34 | 0 | 4.2 | 2.86 | 2.86 | opened | 204 | Lipovka | 4+4 | 0.10866 | 1.4487 | 0 | 0 | 1.4487 | 0 | 4.2 | 2.7513 | 2.7513 | opened
205 | Yudanovka | 2,5+2,5 | 0.81 | 0.81 | 180 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 205 | Yudanovka | 2,5+2,5 | 0.049524 | 0.85952 | 0.81 | 180 | 0.049524 | 0 | 2.625 | 2.5755 | 2.5755 | opened
206 | Mechetka | 2,5+1,6 | 0.38 | 0 | 0 | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened | 206 | Mechetka | 2,5+1,6 | 0.01106 | 0.39106 | 0 | 0 | 0.39106 | 0 | 1.68 | 1.2889 | 1.2889 | opened
207 | Petrovskaya | 4+4 | 1.23 | 0.03 | 180 | 1.2 | 0 | 4.2 | 3 | 3 | opened | 207 | Petrovskaya | 4+4 | 0.71815 | 1.9482 | 0.03 | 180 | 1.9182 | 0 | 4.2 | 2.2818 | 2.2818 | opened
208 | Sr. Ikorets | 4+4 | 2.68 | 0.06 | 120 | 2.62 | 0 | 4.2 | 1.58 | 1.58 | opened | 208 | Sr. Ikorets | 4+4 | 0.73908 | 3.4191 | 0.06 | 120 | 3.3591 | 0 | 4.2 | 0.84092 | 0.84092 | opened
209 | the 2nd Storozhevoe | 2,5+2,5 | 0.22 | 0 | 0 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 209 | the 2nd Storozhevoe | 2,5+2,5 | 0.005 | 0.225 | 0 | 0 | 0.225 | 0 | 2.625 | 2.4 | 2.4 | opened
210 | Och. Sooruzheniya | 2,5+2,5 | 1.52 | 0.42 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 210 | Och. Sooruzheniya | 2,5+2,5 | 0.9128 | 2.4328 | 0.42 | 120 | 2.0128 | 0 | 2.625 | 0.6122 | 0.6122 | opened
211 | Borisoglebsk | 25+25 | 23.35 | 24.9 | 240 | -1.55 | 0 | 26.25 | 27.8 | 26.6 | opened | 211 | Borisoglebsk | 25+25 | 0 | 23.35 | 24.9 | 240 | -1.55 | 0 | 26.25 | 27.8 | 26.6 | opened
| Sн. MV, МVА | 25+25 | 16.15 | 16.5 | 240 | -0.35 | 0 | 26.25 | 26.6 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 16.15 | 16.5 | 240 | -0.35 | 0 | 26.25 | 26.6
| Sн. LV, МVА | 25+25 | 7.2 | 8.4 | 240 | -1.2 | 0 | 26.25 | 27.45 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 7.2 | 8.4 | 240 | -1.2 | 0 | 26.25 | 27.45
212 | Kamenka | 10+10 | 5.01 | 6.01 | 180 | -1 | 0 | 10.5 | 11.5 | 10.61 | opened | 212 | Kamenka | 10+10 | 0.028043 | 5.038 | 6.01 | 180 | -0.97196 | 0 | 10.5 | 11.472 | 10.582 | opened
| Sн. MV, МVА | 10+10 | 4.46 | 5.35 | 180 | -0.89 | 0 | 10.5 | 11.39 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 4.46 | 5.35 | 180 | -0.89 | 0 | 10.5 | 11.39
| Sн. LV, МVА | 10+10 | 0.55 | 0.66 | 180 | -0.11 | 0 | 10.5 | 10.61 |  |  |  | Sн. LV, МVА | 10+10 | 0.028043 | 0.57804 | 0.66 | 180 | -0.081957 | 0 | 10.5 | 10.582
213 | Talovaya | 16+16 | 6.39 | 6.39 | 180 | 0 | 0 | 16.8 | 16.8 | 15.74 | opened | 213 | Talovaya | 16+16 | 0.38946 | 6.7795 | 6.39 | 180 | 0.38946 | 0 | 16.8 | 16.4105 | 15.3505 | opened
| Sн. MV, МVА | 16+16 | 5.33 | 6.39 | 180 | -1.06 | 0 | 16.8 | 17.86 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 5.33 | 6.39 | 180 | -1.06 | 0 | 16.8 | 17.86
| Sн. LV, МVА | 16+16 | 1.06 | 0 | 0 | 1.06 | 0 | 16.8 | 15.74 |  |  |  | Sн. LV, МVА | 16+16 | 0.38946 | 1.4495 | 0 | 0 | 1.4495 | 0 | 16.8 | 15.3505
214 | Anna | 25+25 | 11.77 | 14.11 | 150 | -2.34 | 0 | 26.25 | 28.59 | 27.14 | opened | 214 | Anna | 25+25 | 0.31163 | 12.0816 | 14.11 | 150 | -2.0284 | 0 | 26.25 | 28.2784 | 27.14 | opened
| Sн. MV, МVА | 25+25 | 4.48 | 5.37 | 150 | -0.89 | 0 | 26.25 | 27.14 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 4.48 | 5.37 | 150 | -0.89 | 0 | 26.25 | 27.14
| Sн. LV, МVА | 25+25 | 7.29 | 8.74 | 150 | -1.45 | 0 | 26.25 | 27.7 |  |  |  | Sн. LV, МVА | 25+25 | 0.31163 | 7.6016 | 8.74 | 150 | -1.1384 | 0 | 26.25 | 27.3884
215 | Arkhangelskoe | 10+10 | 5.42 | 3.02 | 90 | 2.4 | 0 | 10.5 | 8.1 | 7.59 | opened | 215 | Arkhangelskoe | 10+10 | 0.24837 | 5.6684 | 3.02 | 90 | 2.6484 | 0 | 10.5 | 7.8516 | 7.3416 | opened
| Sн. MV, МVА | 10+10 | 2.52 | 3.02 | 90 | -0.5 | 0 | 10.5 | 11 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.52 | 3.02 | 90 | -0.5 | 0 | 10.5 | 11
| Sн. LV, МVА | 10+10 | 2.91 | 0 | 0 | 2.91 | 0 | 10.5 | 7.59 |  |  |  | Sн. LV, МVА | 10+10 | 0.24837 | 3.1584 | 0 | 0 | 3.1584 | 0 | 10.5 | 7.3416
216 | Listopadovka | 10+10 | 3.54 | 3.08 | 90 | 0.46 | 0 | 10.5 | 10.04 | 9.53 | opened | 216 | Listopadovka | 10+10 | 0.053804 | 3.5938 | 3.08 | 90 | 0.5138 | 0 | 10.5 | 9.9862 | 9.4762 | opened
| Sн. MV, МVА | 10+10 | 2.57 | 3.08 | 90 | -0.51 | 0 | 10.5 | 11.01 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 2.57 | 3.08 | 90 | -0.51 | 0 | 10.5 | 11.01
| Sн. LV, МVА | 10+10 | 0.97 | 0 | 0 | 0.97 | 0 | 10.5 | 9.53 |  |  |  | Sн. LV, МVА | 10+10 | 0.053804 | 1.0238 | 0 | 0 | 1.0238 | 0 | 10.5 | 9.4762
217 | V. Karachan | 10+10 | 2.49 | 1.18 | 90 | 1.31 | 0 | 10.5 | 9.19 | 9 | opened | 217 | V. Karachan | 10+10 | 0.16772 | 2.6577 | 1.18 | 90 | 1.4777 | 0 | 10.5 | 9.0223 | 8.8323 | opened
| Sн. MV, МVА | 10+10 | 0.99 | 1.18 | 90 | -0.19 | 0 | 10.5 | 10.69 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 0.99 | 1.18 | 90 | -0.19 | 0 | 10.5 | 10.69
| Sн. LV, МVА | 10+10 | 1.5 | 0 | 0 | 1.5 | 0 | 10.5 | 9 |  |  |  | Sн. LV, МVА | 10+10 | 0.16772 | 1.6677 | 0 | 0 | 1.6677 | 0 | 10.5 | 8.8323
218 | Ternovka | 10+10 | 3.6 | 1.03 | 60 | 2.57 | 0 | 10.5 | 7.93 | 7.76 | opened | 218 | Ternovka | 10+10 | 0.21587 | 3.8159 | 1.03 | 60 | 2.7859 | 0 | 10.5 | 7.7141 | 7.5441 | opened
| Sн. MV, МVА | 10+10 | 0.86 | 1.03 | 60 | -0.17 | 0 | 10.5 | 10.67 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 0.86 | 1.03 | 60 | -0.17 | 0 | 10.5 | 10.67
| Sн. LV, МVА | 10+10 | 2.74 | 0 | 0 | 2.74 | 0 | 10.5 | 7.76 |  |  |  | Sн. LV, МVА | 10+10 | 0.21587 | 2.9559 | 0 | 0 | 2.9559 | 0 | 10.5 | 7.5441
219 | Narodnoe | 16+10 | 2.85 | 0.93 | 90 | 1.92 | 0 | 10.5 | 8.58 | 8.43 | opened | 219 | Narodnoe | 16+10 | 0.39913 | 3.2491 | 0.93 | 90 | 2.3191 | 0 | 10.5 | 8.1809 | 8.0309 | opened
| Sн. MV, МVА | 16+10 | 0.78 | 0.93 | 90 | -0.15 | 0 | 10.5 | 10.65 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 0.78 | 0.93 | 90 | -0.15 | 0 | 10.5 | 10.65
| Sн. LV, МVА | 16+10 | 2.07 | 0 | 0 | 2.07 | 0 | 10.5 | 8.43 |  |  |  | Sн. LV, МVА | 16+10 | 0.39913 | 2.4691 | 0 | 0 | 2.4691 | 0 | 10.5 | 8.0309
220 | N. Khopersk | 10+16 | 7.62 | 1.95 | 120 | 5.67 | 0 | 10.5 | 4.83 | 4.61 | opened | 220 | N. Khopersk | 10+16 | 0.71772 | 8.3377 | 1.95 | 120 | 6.3877 | 0 | 10.5 | 4.1123 | 3.8923 | opened
| Sн. MV, МVА | 10+16 | 1.63 | 1.95 | 120 | -0.32 | 0 | 10.5 | 10.82 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 1.63 | 1.95 | 120 | -0.32 | 0 | 10.5 | 10.82
| Sн. LV, МVА | 10+16 | 5.89 | 0 | 0 | 5.89 | 0 | 10.5 | 4.61 |  |  |  | Sн. LV, МVА | 10+16 | 0.71772 | 6.6077 | 0 | 0 | 6.6077 | 0 | 10.5 | 3.8923
221 | Ertil | 10+16 | 8.91 | 1.4 | 180 | 7.51 | 0 | 10.5 | 2.99 | 2.99 | opened | 221 | Ertil | 10+16 | 0.43935 | 9.3493 | 1.4 | 180 | 7.9493 | 0 | 10.5 | 2.5507 | 2.5507 | opened
| Sн. MV, МVА | 10+16 | 5.9 | 1.4 | 180 | 4.5 | 0 | 10.5 | 6 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 5.9 | 1.4 | 180 | 4.5 | 0 | 10.5 | 6
| Sн. LV, МVА | 10+16 | 3.01 | 0 | 0 | 3.01 | 0 | 10.5 | 7.49 |  |  |  | Sн. LV, МVА | 10+16 | 0.43935 | 3.4493 | 0 | 0 | 3.4493 | 0 | 10.5 | 7.0507
222 | Shchuchye | 6,3+6,3 | 3.15 | 2.33 | 180 | 0.82 | 0 | 6.615 | 5.795 | 5.495 | opened | 222 | Shchuchye | 6,3+6,3 | 0.12717 | 3.2772 | 2.33 | 180 | 0.94717 | 0 | 6.615 | 5.6678 | 5.3678 | opened
| Sн. MV, МVА | 6,3+6,3 | 1.51 | 1.81 | 180 | -0.3 | 0 | 6.615 | 6.915 |  |  |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.51 | 1.81 | 180 | -0.3 | 0 | 6.615 | 6.915
| Sн.LV, МVА | 6,3+6,3 | 1.64 | 0.52 | 180 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Sн.LV, МVА | 6,3+6,3 | 0.12717 | 1.7672 | 0.52 | 180 | 1.2472 | 0 | 6.615 | 5.3678
223 | Dokuchaevo | 10+10 | 2.1 | 0.45 | 120 | 1.65 | 0 | 10.5 | 8.85 | 8.85 | opened | 223 | Dokuchaevo | 10+10 | 0.2063 | 2.3063 | 0.45 | 120 | 1.8563 | 0 | 10.5 | 8.6437 | 8.6437 | opened
224 | B. Gribanovka | 16+16 | 6.54 | 0.24 | 30 | 6.3 | 0 | 16.8 | 10.5 | 10.5 | opened | 224 | B. Gribanovka | 16+16 | 0.48049 | 7.0205 | 0.24 | 30 | 6.7805 | 0 | 16.8 | 10.0195 | 10.0195 | opened
225 | Khimmash | 16+16 | 5.93 | 7.1 | 240 | -1.17 | 0 | 16.8 | 17.97 | 17.97 | opened | 225 | Khimmash | 16+16 | 0 | 5.93 | 7.1 | 240 | -1.17 | 0 | 16.8 | 17.97 | 17.97 | opened
226 | Chigorak | 2,5+4 | 0.8 | 0.96 | 90 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | opened | 226 | Chigorak | 2,5+4 | 0.16924 | 0.96924 | 0.96 | 90 | 0.0092391 | 0 | 2.625 | 2.6158 | 2.6158 | opened
227 | Tretyaki | 4+4 | 0.97 | 0 | 0 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | opened | 227 | Tretyaki | 4+4 | 0.085652 | 1.0557 | 0 | 0 | 1.0557 | 0 | 4.2 | 3.1443 | 3.1443 | opened
228 | Gubari | 2,5+2,5 | 0.36 | 0.43 | 180 | -0.07 | 0 | 2.625 | 2.695 | 2.695 | opened | 228 | Gubari | 2,5+2,5 | 0.24924 | 0.60924 | 0.43 | 180 | 0.17924 | 0 | 2.625 | 2.4458 | 2.4458 | opened
229 | Tantsyrey | 2,5+2,5 | 0.89 | 0 | 0 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened | 229 | Tantsyrey | 2,5+2,5 | 0.015217 | 0.90522 | 0 | 0 | 0.90522 | 0 | 2.625 | 1.7198 | 1.7198 | opened
230 | Peski | 4+4 | 3.86 | 0 | 0 | 3.86 | 0 | 4.2 | 0.34 | 0.34 | opened | 230 | Peski | 4+4 | 0.28587 | 4.1459 | 0 | 0 | 4.1459 | 0 | 4.2 | 0.05413 | 0.05413 | opened
231 | M. Gribanovka | 1,6+1,6 | 0.72 | 0.87 | 30 | -0.15 | 0 | 1.68 | 1.83 | 1.83 | opened | 231 | M. Gribanovka | 1,6+1,6 | 0.06413 | 0.78413 | 0.87 | 30 | -0.08587 | 0 | 1.68 | 1.7659 | 1.7659 | opened
232 | N. Karachan | 2,5+2,5 | 0.56 | 0 | 0 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 232 | N. Karachan | 2,5+2,5 | 0.048478 | 0.60848 | 0 | 0 | 0.60848 | 0 | 2.625 | 2.0165 | 2.0165 | opened
233 | Kozlovka | 4+2,5 | 0.78 | 0 | 0 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | opened | 233 | Kozlovka | 4+2,5 | 0.08125 | 0.86125 | 0 | 0 | 0.86125 | 0 | 2.625 | 1.7638 | 1.7638 | opened
234 | K. Otdelets | 2,5+2,5 | 0.53 | 0.63 | 30 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 234 | K. Otdelets | 2,5+2,5 | 0.034239 | 0.56424 | 0.63 | 30 | -0.065761 | 0 | 2.625 | 2.6908 | 2.6908 | opened
235 | Esipovo | 2,5+2,5 | 0.86 | 0 | 0 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | opened | 235 | Esipovo | 2,5+2,5 | 0.34788 | 1.2079 | 0 | 0 | 1.2079 | 0 | 2.625 | 1.4171 | 1.4171 | opened
236 | Kiselnov | 2,5+2,5 | 0.46 | 0 | 0 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened | 236 | Kiselnov | 2,5+2,5 | 0.013315 | 0.47332 | 0 | 0 | 0.47332 | 0 | 2.625 | 2.1517 | 2.1517 | opened
237 | Krasnoe | 6,3+6,3 | 1.34 | 0 | 0 | 1.34 | 0 | 6.615 | 5.275 | 5.275 | opened | 237 | Krasnoe | 6,3+6,3 | 0.078804 | 1.4188 | 0 | 0 | 1.4188 | 0 | 6.615 | 5.1962 | 5.1962 | opened
238 | Troitskoe | 2,5+2,5 | 0.43 | 0 | 0 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 238 | Troitskoe | 2,5+2,5 | 0.05 | 0.48 | 0 | 0 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
239 | Ertil-gorod | 6,3+6,3 | 4.73 | 5 | 240 | -0.27 | 0 | 6.615 | 6.885 | 6.885 | opened | 239 | Ertil-gorod | 6,3+6,3 | 0.24315 | 4.9732 | 5 | 240 | -0.026848 | 0 | 6.615 | 6.6418 | 6.6418 | opened
240 | Rostoshi | 4+4 | 1.34 | 0 | 0 | 1.34 | 0 | 4.2 | 2.86 | 2.86 | opened | 240 | Rostoshi | 4+4 | 0.079891 | 1.4199 | 0 | 0 | 1.4199 | 0 | 4.2 | 2.7801 | 2.7801 | opened
241 | Vvedenka | 2,5+2,5 | 0.4 | 0.48 | 60 | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened | 241 | Vvedenka | 2,5+2,5 | 0 | 0.4 | 0.48 | 60 | -0.08 | 0 | 2.625 | 2.705 | 2.705 | opened
242 | Sadovoe | 4+4 | 2.06 | 0 | 0 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | opened | 242 | Sadovoe | 4+4 | 0.077174 | 2.1372 | 0 | 0 | 2.1372 | 0 | 4.2 | 2.0628 | 2.0628 | opened
243 | Rubashevka | 2,5+2,5 | 0.87 | 0 | 0 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | opened | 243 | Rubashevka | 2,5+2,5 | 0.013804 | 0.8838 | 0 | 0 | 0.8838 | 0 | 2.625 | 1.7412 | 1.7412 | opened
244 | N. Nadezhdenka | 2,5+2,5 | 0.63 | 0.75 | 180 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | opened | 244 | N. Nadezhdenka | 2,5+2,5 | 0.0043478 | 0.63435 | 0.75 | 180 | -0.11565 | 0 | 2.625 | 2.7407 | 2.7407 | opened
245 | Abramovka | 6,3+4 | 3.81 | 0.52 | 120 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | opened | 245 | Abramovka | 6,3+4 | 0.10679 | 3.9168 | 0.52 | 120 | 3.3968 | 0 | 4.2 | 0.80321 | 0.80321 | opened
246 | Alexandrovka | 2,5+2,5 | 0.98 | 1.17 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 246 | Alexandrovka | 2,5+2,5 | 0.059783 | 1.0398 | 1.17 | 120 | -0.13022 | 0 | 2.625 | 2.7552 | 2.7552 | opened
247 | N. Troitskaya | 4+4 | 0.29 | 0.34 | 120 | -0.05 | 0 | 4.2 | 4.25 | 4.25 | opened | 247 | N. Troitskaya | 4+4 | 0.0032609 | 0.29326 | 0.34 | 120 | -0.046739 | 0 | 4.2 | 4.2467 | 4.2467 | opened
248 | Kalach-1 | 25+25 | 13.07 | 2.2 | 120 | 10.87 | 0 | 26.25 | 15.38 | 15.38 | opened | 248 | Kalach-1 | 25+25 | 0.6238 | 13.6938 | 2.2 | 120 | 11.4938 | 0 | 26.25 | 14.7562 | 14.7562 | opened
| Sн. MV, МVА | 25+25 | 6.56 | 1 | 120 | 5.56 | 0 | 26.25 | 20.69 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 6.56 | 1 | 120 | 5.56 | 0 | 26.25 | 20.69
| Sн. LV, МVА | 25+25 | 6.51 | 1.2 | 120 | 5.31 | 0 | 26.25 | 20.94 |  |  |  | Sн. LV, МVА | 25+25 | 0.6238 | 7.1338 | 1.2 | 120 | 5.9338 | 0 | 26.25 | 20.3162
249 | Kalach-2 | 16+16 | 7.2 | 2 | 24 hours | 5.2 | 0 | 16.8 | 11.6 | 11.6 | opened | 249 | Kalach-2 | 16+16 | 0.5215 | 7.7215 | 2 | 24 hours | 5.7215 | 0 | 16.8 | 11.0785 | 11.0785 | opened
250 | Buturlinovka-1 | 16+16 | 14.37 | 2 | 120 | 12.37 | 0 | 16.8 | 4.43 | 4.43 | opened | 250 | Buturlinovka-1 | 16+16 | 0.017 | 14.387 | 2 | 120 | 12.387 | 0 | 16.8 | 4.413 | 4.413 | opened
| Sн. MV, МVА | 16+16 | 5.09 | 0 | 0 | 5.09 | 0 | 16.8 | 11.71 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 5.09 | 0 | 0 | 5.09 | 0 | 16.8 | 11.71
| Sн. LV, МVА | 16+16 | 9.28 | 2 | 120 | 7.28 | 0 | 16.8 | 9.52 |  |  |  | Sн. LV, МVА | 16+16 | 0.017 | 9.297 | 2 | 120 | 7.297 | 0 | 16.8 | 9.503
251 | Buturlinovka-2 | 16+6,3 | 5.27 | 1.5 | 120 | 3.77 | 0 | 6.615 | 2.845 | 2.845 | opened | 251 | Buturlinovka-2 | 16+6,3 | 0.0717 | 5.3417 | 1.5 | 120 | 3.8417 | 0 | 6.615 | 2.7733 | 2.7733 | opened
252 | N.Kislyai | 10+10 | 6.32 | 1.5 | 120 | 4.82 | 0 | 10.5 | 5.68 | 5.68 | opened | 252 | N.Kislyai | 10+10 | 0.3485 | 6.6685 | 1.5 | 120 | 5.1685 | 0 | 10.5 | 5.3315 | 5.3315 | opened
| Sн. MV, МVА | 10+10 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 3.29 | 0 | 0 | 3.29 | 0 | 10.5 | 7.21
| Sн. LV, МVА | 10+10 | 3.03 | 1.5 | 120 | 1.53 | 0 | 10.5 | 8.97 |  |  |  | Sн. LV, МVА | 10+10 | 0.3485 | 3.3785 | 1.5 | 120 | 1.8785 | 0 | 10.5 | 8.6215
253 | Kozlovka | 2,5+6,3 | 1.15 | 1.5 | 45 | -0.35 | 0 | 2.625 | 2.975 | 2.975 | opened | 253 | Kozlovka | 2,5+6,3 | 0.271 | 1.421 | 1.5 | 45 | -0.079 | 0 | 2.625 | 2.704 | 2.704 | opened
254 | Filippenkovo | 6,3+6,3 | 0.92 | 1.5 | 120 | -0.58 | 0 | 6.615 | 7.195 | 7.195 | opened | 254 | Filippenkovo | 6,3+6,3 | 0.0275 | 0.9475 | 1.5 | 120 | -0.5525 | 0 | 6.615 | 7.1675 | 7.1675 | opened
255 | Vorobyovka | 16+16 | 5.17 | 1.5 | 120 | 3.67 | 0 | 16.8 | 13.13 | 13.13 | opened | 255 | Vorobyovka | 16+16 | 0.40091 | 5.5709 | 1.5 | 120 | 4.0709 | 0 | 16.8 | 12.7291 | 12.7291 | opened
| Sн. MV, МVА | 16+16 | 3.33 | 0.5 | 120 | 2.83 | 0 | 16.8 | 13.97 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 3.33 | 0.5 | 120 | 2.83 | 0 | 16.8 | 13.97
| Sн. LV, МVА | 16+16 | 1.84 | 1 | 120 | 0.84 | 0 | 16.8 | 15.96 |  |  |  | Sн. LV, МVА | 16+16 | 0.40091 | 2.2409 | 1 | 120 | 1.2409 | 0 | 16.8 | 15.5591
256 | Solontsy | 6,3+6,3 | 1.98 | 1 | 24 hours | 0.98 | 0 | 6.615 | 5.635 | 5.635 | opened | 256 | Solontsy | 6,3+6,3 | 0.063 | 2.043 | 1 | 24 hours | 1.043 | 0 | 6.615 | 5.572 | 5.572 | opened
| Sн. MV, МVА | 6,3+6,3 | 1.05 | 1 | 24 hours | 0.05 | 0 | 6.615 | 6.565 |  |  |  | Sн. MV, МVА | 6,3+6,3 | 0 | 1.05 | 1 | 24 hours | 0.05 | 0 | 6.615 | 6.565
| Sн. LV, МVА | 6,3+6,3 | 0.93 | 0 | 0 | 0.93 | 0 | 6.615 | 5.685 |  |  |  | Sн. LV, МVА | 6,3+6,3 | 0.063 | 0.993 | 0 | 0 | 0.993 | 0 | 6.615 | 5.622
257 | Manino | 16+16 | 1.74 | 1.5 | 24 hours | 0.24 | 0 | 16.8 | 16.56 | 16.56 | opened | 257 | Manino | 16+16 | 0.01015 | 1.7502 | 1.5 | 24 hours | 0.25015 | 0 | 16.8 | 16.5498 | 16.5498 | opened
| Sн. MV, МVА | 16+16 | 0.59 | 0.5 | 24 hours | 0.09 | 0 | 16.8 | 16.71 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 0.59 | 0.5 | 24 hours | 0.09 | 0 | 16.8 | 16.71
| Sн. LV, МVА | 16+16 | 1.15 | 1 | 24 hours | 0.15 | 0 | 16.8 | 16.65 |  |  |  | Sн. LV, МVА | 16+16 | 0.01015 | 1.1602 | 1 | 24 hours | 0.16015 | 0 | 16.8 | 16.6398
258 | Petropavlovka | 10+10 | 4.13 | 2 | 120 | 2.13 | 0 | 10.5 | 8.37 | 8.37 | opened | 258 | Petropavlovka | 10+10 | 0.22806 | 4.3581 | 2 | 120 | 2.3581 | 0 | 10.5 | 8.1419 | 8.1419 | opened
| Sн. MV, МVА | 10+10 | 1.78 | 1 | 120 | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 1.78 | 1 | 120 | 0.78 | 0 | 10.5 | 9.72
| Sн. LV, МVА | 10+10 | 2.35 | 1 | 120 | 1.35 | 0 | 10.5 | 9.15 |  |  |  | Sн. LV, МVА | 10+10 | 0.22806 | 2.5781 | 1 | 120 | 1.5781 | 0 | 10.5 | 8.9219
259 | V.Mamon | 16+10 | 6.08 | 2 | 120 | 4.08 | 0 | 10.5 | 6.42 | 6.42 | opened | 259 | V.Mamon | 16+10 | 1.2184 | 7.2984 | 2 | 120 | 5.2984 | 0 | 10.5 | 5.2016 | 5.2016 | opened
| Sн. MV, МVА | 16+10 | 1.94 | 0 | 0 | 1.94 | 0 | 10.5 | 8.56 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 1.94 | 0 | 0 | 1.94 | 0 | 10.5 | 8.56
| Sн. LV, МVА | 16+10 | 4.14 | 2 | 120 | 2.14 | 0 | 10.5 | 8.36 |  |  |  | Sн. LV, МVА | 16+10 | 1.2184 | 5.3584 | 2 | 120 | 3.3584 | 0 | 10.5 | 7.1416
260 | N.Mamon | 2,5+6,3 | 1.09 | 0 | 0 | 1.09 | 0 | 2.625 | 1.535 | 1.535 | opened | 260 | N.Mamon | 2,5+6,3 | 0.0326 | 1.1226 | 0 | 0 | 1.1226 | 0 | 2.625 | 1.5024 | 1.5024 | opened
261 | Pavlovsk-2 | 25+25 | 17.6 | 1.5 | 120 | 16.1 | 0 | 26.25 | 10.15 | 10.15 | opened | 261 | Pavlovsk-2 | 25+25 | 0.0925 | 17.6925 | 1.5 | 120 | 16.1925 | 0 | 26.25 | 10.0575 | 10.0575 | opened
| Sн. MV, МVА | 25+25 | 9.62 | 1.5 | 120 | 8.12 | 0 | 26.25 | 18.13 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 9.62 | 1.5 | 120 | 8.12 | 0 | 26.25 | 18.13
| Sн. LV, МVА | 25+25 | 7.98 | 0 | 0 | 7.98 | 0 | 26.25 | 18.27 |  |  |  | Sн. LV, МVА | 25+25 | 0.0925 | 8.0725 | 0 | 0 | 8.0725 | 0 | 26.25 | 18.1775
262 | Bogucharskaya | 16+16 | 10.8 | 2 | 120 | 8.8 | 0 | 16.8 | 8 | 8 | opened | 262 | Bogucharskaya | 16+16 | 4.0441 | 14.8441 | 2 | 120 | 12.8441 | 0 | 16.8 | 3.9559 | 3.9559 | opened
| Sн. MV, МVА | 16+16 | 5.42 | 1 | 120 | 4.42 | 0 | 16.8 | 12.38 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 5.42 | 1 | 120 | 4.42 | 0 | 16.8 | 12.38
| Sн. LV, МVА | 16+16 | 5.38 | 1 | 120 | 4.38 | 0 | 16.8 | 12.42 |  |  |  | Sн. LV, МVА | 16+16 | 4.0441 | 9.4241 | 1 | 120 | 8.4241 | 0 | 16.8 | 8.3759
263 | Opornaya | 6,3+6,3 | 2.12 | 1.5 | 120 | 0.62 | 0 | 6.615 | 5.995 | 5.995 | opened | 263 | Opornaya | 6,3+6,3 | 1.378 | 3.498 | 1.5 | 120 | 1.998 | 0 | 6.615 | 4.617 | 4.617 | opened
264 | Podgornoe | 2,5+2,5 | 0.81 | 1 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 264 | Podgornoe | 2,5+2,5 | 0.018 | 0.828 | 1 | 120 | -0.172 | 0 | 2.625 | 2.797 | 2.797 | opened
265 | Bolshevik | 4+2,5 | 2 | 1.5 | 45 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 265 | Bolshevik | 4+2,5 | 0.1403 | 2.1403 | 1.5 | 45 | 0.6403 | 0 | 2.625 | 1.9847 | 1.9847 | opened
266 | Semenovka | 2,5+1,8 | 0.77 | 1 | 80 | -0.23 | 0 | 1.89 | 2.12 | 2.12 | opened | 266 | Semenovka | 2,5+1,8 | 0.0315 | 0.8015 | 1 | 80 | -0.1985 | 0 | 1.89 | 2.0885 | 2.0885 | opened
267 | Popasnoe | 4+4 | 0.32 | 1.5 | 120 | -1.18 | 0 | 4.2 | 5.38 | 5.38 | opened | 267 | Popasnoe | 4+4 | 0.0056 | 0.3256 | 1.5 | 120 | -1.1744 | 0 | 4.2 | 5.3744 | 5.3744 | opened
268 | N.Kriusha | 2,5+2,5 | 1.09 | 1.5 | 45 | -0.41 | 0 | 2.625 | 3.035 | 3.035 | opened | 268 | N.Kriusha | 2,5+2,5 | 0.02 | 1.11 | 1.5 | 45 | -0.39 | 0 | 2.625 | 3.015 | 3.015 | opened
269 | N.Melovatka | 2,5+2,5 | 1.53 | 1.5 | 45 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 269 | N.Melovatka | 2,5+2,5 | 0.056 | 1.586 | 1.5 | 45 | 0.086 | 0 | 2.625 | 2.539 | 2.539 | opened
270 | Vasilyevka | 4+4 | 0.77 | 1.5 | 120 | -0.73 | 0 | 4.2 | 4.93 | 4.93 | opened | 270 | Vasilyevka | 4+4 | 0.105 | 0.875 | 1.5 | 120 | -0.625 | 0 | 4.2 | 4.825 | 4.825 | opened
271 | V.Oktyabr | 4+4 | 0.96 | 1.5 | 120 | -0.54 | 0 | 4.2 | 4.74 | 4.74 | opened | 271 | V.Oktyabr | 4+4 | 0.133 | 1.093 | 1.5 | 120 | -0.407 | 0 | 4.2 | 4.607 | 4.607 | opened
272 | V.Arkhangelskoe | 2,5+2,5 | 0.5 | 1.5 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 | opened | 272 | V.Arkhangelskoe | 2,5+2,5 | 0.088 | 0.588 | 1.5 | 45 | -0.912 | 0 | 2.625 | 3.537 | 3.537 | opened
273 | Leshchanaya | 2,5+2,5 | 1.5 | 1.5 | 45 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 273 | Leshchanaya | 2,5+2,5 | 0.2222 | 1.7222 | 1.5 | 45 | 0.2222 | 0 | 2.625 | 2.4028 | 2.4028 | opened
274 | Muzhichye | 4+2,5 | 0.54 | 1.5 | 45 | -0.96 | 0 | 2.625 | 3.585 | 3.585 | opened | 274 | Muzhichye | 4+2,5 | 0.1305 | 0.6705 | 1.5 | 45 | -0.8295 | 0 | 2.625 | 3.4545 | 3.4545 | opened
275 | Rudnya | 4+4 | 0.46 | 1.5 | 120 | -1.04 | 0 | 4.2 | 5.24 | 5.24 | opened | 275 | Rudnya | 4+4 | 0.0255 | 0.4855 | 1.5 | 120 | -1.0145 | 0 | 4.2 | 5.2145 | 5.2145 | opened
276 | St. Melovaya | 4+4 | 0.89 | 0 | 0 | 0.89 | 0 | 4.2 | 3.31 | 3.31 | opened | 276 | St. Melovaya | 4+4 | 0.0506 | 0.9406 | 0 | 0 | 0.9406 | 0 | 4.2 | 3.2594 | 3.2594 | opened
277 | St. Kriusha | 2,5+4 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 277 | St. Kriusha | 2,5+4 | 0.04955 | 1.1496 | 0 | 0 | 1.1496 | 0 | 2.625 | 1.4754 | 1.4754 | opened
278 | Lozovaya | 4+4 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | opened | 278 | Lozovaya | 4+4 | 0.0155 | 0.6355 | 0 | 0 | 0.6355 | 0 | 4.2 | 3.5645 | 3.5645 | opened
279 | Pavlovsk-1 | 4+4 | 3.21 | 1 | 120 | 2.21 | 0 | 4.2 | 1.99 | 1.99 | opened | 279 | Pavlovsk-1 | 4+4 | 0.2015 | 3.4115 | 1 | 120 | 2.4115 | 0 | 4.2 | 1.7885 | 1.7885 | opened
280 | Losevo | 4+4 | 2.5 | 0 | 0 | 2.5 | 0 | 4.2 | 1.7 | 1.7 | opened | 280 | Losevo | 4+4 | 0.0951 | 2.5951 | 0 | 0 | 2.5951 | 0 | 4.2 | 1.6049 | 1.6049 | opened
281 | Gavrilsk | 4+4 | 0.53 | 0 | 0 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 281 | Gavrilsk | 4+4 | 0.019 | 0.549 | 0 | 0 | 0.549 | 0 | 4.2 | 3.651 | 3.651 | opened
282 | Pokrovka | 4+2,5 | 0.83 | 0 | 0 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | opened | 282 | Pokrovka | 4+2,5 | 0.036 | 0.866 | 0 | 0 | 0.866 | 0 | 2.625 | 1.759 | 1.759 | opened
283 | Vorontsovka | 4+4 | 2.44 | 1.5 | 120 | 0.94 | 0 | 4.2 | 3.26 | 3.26 | opened | 283 | Vorontsovka | 4+4 | 0.51173 | 2.9517 | 1.5 | 120 | 1.4517 | 0 | 4.2 | 2.7483 | 2.7483 | opened
284 | А.Donskaya | 2,5+2,5 | 1.09 | 1.5 | 45 | -0.41 | 0 | 2.625 | 3.035 | 3.035 | opened | 284 | А.Donskaya | 2,5+2,5 | 0.0515 | 1.1415 | 1.5 | 45 | -0.3585 | 0 | 2.625 | 2.9835 | 2.9835 | opened
285 | Petrovka | 2,5+4 | 1.36 | 1.5 | 45 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened | 285 | Petrovka | 2,5+4 | 0.1175 | 1.4775 | 1.5 | 45 | -0.0225 | 0 | 2.625 | 2.6475 | 2.6475 | opened
286 | Monastyrshchina | 4+4 | 0.88 | 1.5 | 120 | -0.62 | 0 | 4.2 | 4.82 | 4.82 | opened | 286 | Monastyrshchina | 4+4 | 0.063 | 0.943 | 1.5 | 120 | -0.557 | 0 | 4.2 | 4.757 | 4.757 | opened
287 | Zhuravka | 1,8+2,5 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | opened | 287 | Zhuravka | 1,8+2,5 | 0 | 0.15 | 0 | 0 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | opened
288 | Dyachenkovo | 2,5+2,5 | 1.48 | 1.5 | 45 | -0.02 | 0 | 2.625 | 2.645 | 2.645 | opened | 288 | Dyachenkovo | 2,5+2,5 | 0.0735 | 1.5535 | 1.5 | 45 | 0.0535 | 0 | 2.625 | 2.5715 | 2.5715 | opened
289 | Radchenskaya | 1,6+2,5 | 0.83 | 0 | 0 | 0.83 | 0 | 1.68 | 0.85 | 0.85 | opened | 289 | Radchenskaya | 1,6+2,5 | 0.07105 | 0.90105 | 0 | 0 | 0.90105 | 0 | 1.68 | 0.77895 | 0.77895 | opened
290 | Rossiya | 4+4 | 1.07 | 1.5 | 120 | -0.43 | 0 | 4.2 | 4.63 | 4.63 | opened | 290 | Rossiya | 4+4 | 0.0876 | 1.1576 | 1.5 | 120 | -0.3424 | 0 | 4.2 | 4.5424 | 4.5424 | opened
291 | Pervomayskaya | 4+4 | 0.35 | 1.5 | 120 | -1.15 | 0 | 4.2 | 5.35 | 5.35 | opened | 291 | Pervomayskaya | 4+4 | 0.038 | 0.388 | 1.5 | 120 | -1.112 | 0 | 4.2 | 5.312 | 5.312 | opened
292 | Podkolodnovka | 2,5+3,2 | 0.91 | 0 | 0 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | opened | 292 | Podkolodnovka | 2,5+3,2 | 0.2959 | 1.2059 | 0 | 0 | 1.2059 | 0 | 2.625 | 1.4191 | 1.4191 | opened
293 | Yuzhny | 2,5+2,5 | 0.16 | 0 | 0 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 293 | Yuzhny | 2,5+2,5 | 0.0101 | 0.1701 | 0 | 0 | 0.1701 | 0 | 2.625 | 2.4549 | 2.4549 | opened
| TOTAL: |  | 1348.47 | 487.9668 |  | 1012.8082 | [5 empty] | 2: TOTAL:; 4: 274.4333; 5: 1622.9033; МVА 6: 491.6668; min. 8: 1131.2365
| deficit | [8 empty] | -30.6 |  | 2: deficit; min. 12: -90.5364
| proficit | [8 empty] | 1279.48 |  | 2: proficit; min. 12: 1077.0461

## тверь
table 1 | [11 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS Alekseykovo 35/10 kv | 1.6 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened | 1 | SS Alekseykovo 35/10 kv | 1.6 | 0 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened
2 | SS Belyznitsy 35/10 kv | 2.5 | 0.7 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 0.8 | 0.8 | opened | 2 | SS Belyznitsy 35/10 kv | 2.5 | 0 | 0.7 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 0.8 | 0.8 | opened
3 | SS Borisovskoe 35/10 kv | 1 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 3 | SS Borisovskoe 35/10 kv | 1 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed
4 | SS Vysokusha 35/10 kv | 2.5 | 0.1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.2 | 1.2 | opened | 4 | SS Vysokusha 35/10 kv | 2.5 | 0 | 0.1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.2 | 1.2 | opened
5 | SS Hotel 35/10 kv | 1.6 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 | opened | 5 | SS Hotel 35/10 kv | 1.6 | 0 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 | opened
6 | SS Grigorovo 35/10 kv | 2.5 | 0.1 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.8 | 0.8 | opened | 6 | SS Grigorovo 35/10 kv | 2.5 | 0.015 | 0.115 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.785 | 0.785 | opened
7 | SS Deledino 35/10 kv | 4 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 | opened | 7 | SS Deledino 35/10 kv | 4 | 0 | 0.2 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.5 | 0.5 | opened
8 | SS Zaramenye 35/10 kv | 1.6 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 8 | SS Zaramenye 35/10 kv | 1.6 | 0 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
9 | SS Zoby 35/10 kv | 4 | 0.1 | 3 | 24 hours | 3 | 0 | 3 | 2.9 | 2.9 | opened | 9 | SS Zoby 35/10 kv | 4 | 0 | 0.1 | 3 | 24 hours | 3 | 0 | 3 | 2.9 | 2.9 | opened
10 | SS Koy 35/10 kv | 1.6 | 0.1 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.6 | 0.6 | opened | 10 | SS Koy 35/10 kv | 1.6 | 0.03 | 0.13 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.57 | 0.57 | opened
11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.1 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1.1 | 1.1 | opened | 11 | SS Ladozhskoe 35/10 kv | 1.6 | 0.125 | 0.225 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.975 | 0.975 | opened
12 | SS Litvinovo 35/10 kv | 4 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened | 12 | SS Litvinovo 35/10 kv | 4 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened
13 | SS Loshchemlya 35/10 kv | 2.5 | 0.6 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.2 | 0.2 | opened | 13 | SS Loshchemlya 35/10 kv | 2.5 | 0.015 | 0.615 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.185 | 0.185 | opened
14 | SS Lyubegoshchi 35/10 kv | 4 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened | 14 | SS Lyubegoshchi 35/10 kv | 4 | 0 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened
15 | SS Martynovo 35/10 kv | 1.6 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 | opened | 15 | SS Martynovo 35/10 kv | 1.6 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 | opened
16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 | opened | 16 | SS Mikhailovskoe 35/10 kv | 2.5 | 0 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 | opened
17 | SS Morozovo 35/10 kv | 2.5 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened | 17 | SS Morozovo 35/10 kv | 2.5 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened
18 | SS Popovka 35/10 kv | 1 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 | opened | 18 | SS Popovka 35/10 kv | 1 | 0 | 0.1 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 1 | 1 | opened
19 | SS Romantsevo 35/10 kv | 4 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened | 19 | SS Romantsevo 35/10 kv | 4 | 0 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened
20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0.6 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.3 | 0.3 | opened | 20 | SS Staroe Sandovo 35/10 kv | 2.5 | 0 | 0.6 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.3 | 0.3 | opened
21 | SS Sukromny 35/10 kv | 1.6 | 0.5 | 1.7 | 24 hours | 1.7 | 0 | 1.7 | 1.2 | 1.2 | opened | 21 | SS Sukromny 35/10 kv | 1.6 | 0 | 0.5 | 1.7 | 24 hours | 1.7 | 0 | 1.7 | 1.2 | 1.2 | opened
22 | SS tebleshi 35/10 kv | 2.5 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 | 1.6 | opened | 22 | SS tebleshi 35/10 kv | 2.5 | 0 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 | 1.6 | opened
23 | SS Trestna 35/10 kv | 2.5 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 | opened | 23 | SS Trestna 35/10 kv | 2.5 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 | 1.1 | opened
24 | SS Fralyovo 35/10 kv | 4 | 0.8 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1 | 1 | opened | 24 | SS Fralyovo 35/10 kv | 4 | 0 | 0.8 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1 | 1 | opened
25 | SS Chamerovo 35/10 kv | 1.8 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6 | 0.6 | opened | 25 | SS Chamerovo 35/10 kv | 1.8 | 0.3363 | 1.1363 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.2637 | 0.2637 | opened
26 | SS Akhmatovo 110/10 kv | 2.5 | 0.4 | 1 | 24 hours | 1 | 0 | 1 | 0.6 | 0.6 | opened | 26 | SS Akhmatovo 110/10 kv | 2.5 | 0 | 0.4 | 1 | 24 hours | 1 | 0 | 1 | 0.6 | 0.6 | opened
27 | SS Kladovo 110/10 kv | 6.3 | 1 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 0.8 | 0.8 | opened | 27 | SS Kladovo 110/10 kv | 6.3 | 0 | 1 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 0.8 | 0.8 | opened
28 | SS Laptikha 110/10 kv | 2.5 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | 0.7 | opened | 28 | SS Laptikha 110/10 kv | 2.5 | 0 | 0.5 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.7 | 0.7 | opened
29 | SS Malyshevo 110/10 kv | 2.5 | 0.8 | 1 | 24 hours | 1 | 0 | 1 | 0.2 | 0.2 | opened | 29 | SS Malyshevo 110/10 kv | 2.5 | 0.0443 | 0.8443 | 1 | 24 hours | 1 | 0 | 1 | 0.1557 | 0.1557 | opened
30 | SS Start 10/10 kv | 16 | 1.6 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0 | 0 | opened | 30 | SS Start 10/10 kv | 16 | 0 | 1.6 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0 | 0 | opened
31 | SS Rassvet 110/35 kv | 10 | 4.5 | 5 | 24 hours | 5 | 0 | 5 | 0.5 | 0.5 | opened | 31 | SS Rassvet 110/35 kv | 10 | 0.03 | 4.53 | 5 | 24 hours | 5 | 0 | 5 | 0.47 | 0.47 | opened
32 | SS Ivanovo 110/35/10 kv | 6.3 | 1 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.3 | -0.8 | MS is closed | 32 | SS Ivanovo 110/35/10 kv | 6.3 | 0.3363 | 1.3363 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | -0.0363 | -1.1363 | MS is closed
| Nom. capacity MV, MVA | 6.3 | 0.8 | 0 | 24 hours | 0 | 0 | 0 | -0.8 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.3363 | 1.1363 | 0 | 24 hours | 0 | 0 | 0 | -1.1363
| Nom. capacity LV, MVA | 6.3 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.2 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.1
33 | SS Kesma 110/35/10 kv | 6.3 | 1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.4 | -0.2 | MS is closed | 33 | SS Kesma 110/35/10 kv | 6.3 | 0 | 1 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.4 | -0.2 | MS is closed
| Nom. capacity MV, MVA | 6.3 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2
| Nom. capacity LV, MVA | 6.3 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.8 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.6
34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0.4 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.8 | -0.2 | MS is closed | 34 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0 | 0.4 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 0.8 | -0.2 | MS is closed
| Nom. capacity MV, MVA | 5.6 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2 |  |  |  | Nom. capacity MV, MVA | 5.6 | 0 | 0.2 | 0 | 24 hours | 0 | 0 | 0 | -0.2
| Nom. capacity LV, MVA | 5.6 | 0.2 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1 |  |  |  | Nom. capacity LV, MVA | 5.6 | 0 | 0.2 | 1.2 | 24 hours | 1.2 | 0 | 1.2 | 1
35 | SS Topalki 110/35/10 kv | 6.3 | 2.1 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 1.6 | 0 | opened | 35 | SS Topalki 110/35/10 kv | 6.3 | 0 | 2.1 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 1.6 | 0 | opened
| Nom. capacity MV, MVA | 6.3 | 1.9 | 1.9 | 24 hours | 1.9 | 0 | 1.9 | 0 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 1.9 | 1.9 | 24 hours | 1.9 | 0 | 1.9 | 0
| Nom. capacity LV, MVA | 6.3 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0 | 0.2 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.6
36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0.1 | 1 | 24 hours | -0.9 | 0 | 1.05 | 1.95 | 1.95 | opened | 36 | SS Berezyo 35/10 kv | 1,0+1,0 | 0 | 0.1 | 1 | 24 hours | -0.9 | 0 | 1.05 | 1.95 | 1.95 | opened
37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 1.8 | 1.4 | 24 hours | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened | 37 | SS Lesnoe 35/10 kv | 1,6+4,0 | 0 | 1.8 | 1.4 | 24 hours | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened
38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 4.3 | 1.9 | 24 hours | 2.4 | 0 | 4.2 | 1.8 | 1.8 | opened | 38 | SS Maksatikha 35/10 kv | 4,0+6,3 | 0.02 | 4.32 | 1.9 | 24 hours | 2.42 | 0 | 4.2 | 1.78 | 1.78 | opened
39 | SS Molokovo 35/10 kv | 2,5+4,0 | 1.2 | 1.5 | 24 hours | -0.3 | 0 | 2.63 | 2.93 | 2.93 | opened | 39 | SS Molokovo 35/10 kv | 2,5+4,0 | 0 | 1.2 | 1.5 | 24 hours | -0.3 | 0 | 2.63 | 2.93 | 2.93 | opened
40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 | opened | 40 | SS Novokotovo 35/10 kv | 2,5+2,5 | 0 | 0.3 | 0 |  | 0.3 | 0 | 2.63 | 2.33 | 2.33 | opened
41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 1.2 | 1.4 | 24 hours | -0.2 | 0 | 1.68 | 1.88 | 1.88 | opened | 41 | SS Rivzavod 35/10 kv | 1,6+2,5 | 0.0162 | 1.2162 | 1.4 | 24 hours | -0.1838 | 0 | 1.68 | 1.8638 | 1.8638 | opened
42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 3.8 | 1.4 | 24 hours | 2.4 | 0 | 3.4 | 1 | 1 | opened | 42 | SS Sonkovo 35/10 kv | 4,0+3,2 | 0 | 3.8 | 1.4 | 24 hours | 2.4 | 0 | 3.4 | 1 | 1 | opened
43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0.4 | 0.8 | 24 hours | -0.4 | 0 | 1.68 | 2.08 | 2.08 | opened | 43 | SS Sulezhsky Borok 35/10 kv | 1,6+2,5 | 0 | 0.4 | 0.8 | 24 hours | -0.4 | 0 | 1.68 | 2.08 | 2.08 | opened
44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0.9 | 1.8 | 24 hours | -0.9 | 0 | 6.62 | 7.52 | 7.52 | opened | 44 | SS Shishkovo Dubrovo 110/10 kv | 6,3+6,3 | 0.027 | 0.927 | 1.8 | 24 hours | -0.873 | 0 | 6.62 | 7.493 | 7.493 | opened
45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 4.2 | 0 |  | 4.2 | 0 | 6.62 | 2.42 | 2.42 | opened | 45 | SS Vesyegonsk 110/35/10 kv | 6,3+6,3 | 0.058 | 4.258 | 0 |  | 4.258 | 0 | 6.62 | 2.362 | 2.362 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.015 | 0.015 | 0 |  | 0.015 | 0 | 6.62 | 6.605
| Nom. capacity LV, MVA | 6,3+6,3 | 4.2 | 0 |  | 4.2 | 0 | 6.62 | 2.42 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.043 | 4.243 | 0 |  | 4.243 | 0 | 6.62 | 2.377
46 | SS DVP 110/35/10 kv | 25,0+25,0 | 11.7 | 2.5 | 24 hours | 9.2 | 0 | 26.3 | 17.1 | 17.1 | opened | 46 | SS DVP 110/35/10 kv | 25,0+25,0 | 0 | 11.7 | 2.5 | 24 hours | 9.2 | 0 | 26.3 | 17.1 | 17.1 | opened
| Nom. capacity MV, MVA | 25,0+25,0 | 4.6 | 2.5 | 24 hours | 2.1 | 0 | 26.3 | 24.2 |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0 | 4.6 | 2.5 | 24 hours | 2.1 | 0 | 26.3 | 24.2
| Nom. capacity LV, MVA | 25,0+25,0 | 7.1 | 0 |  | 7.1 | 0 | 26.3 | 19.2 |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0 | 7.1 | 0 |  | 7.1 | 0 | 26.3 | 19.2
47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 5.4 | 2 | 24 hours | 3.4 | 0 | 10.5 | 7.1 | 5.3 | opened | 47 | SS Krasny Kholm 110/35/10 kv | 10,0+10,0 | 0 | 5.4 | 2 | 24 hours | 3.4 | 0 | 10.5 | 7.1 | 5.3 | opened
| Nom. capacity MV, MVA | 10,0+10,0 | 0.2 | 2 | 24 hours | -1.8 | 0 | 10.5 | 12.3 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.2 | 2 | 24 hours | -1.8 | 0 | 10.5 | 12.3
| Nom. capacity LV, MVA | 10,0+10,0 | 5.2 | 0 |  | 5.2 | 0 | 10.5 | 5.3 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 5.2 | 0 |  | 5.2 | 0 | 10.5 | 5.3
48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 2.4 | 2.2 | 24 hours | 0.2 | 0 | 6.62 | 6.42 | 6.42 | opened | 48 | SS Porechye 110/35/10 кВ | 6,3+6,3 | 0 | 2.4 | 2.2 | 24 hours | 0.2 | 0 | 6.62 | 6.42 | 6.42 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 2.2 | 2.2 | 24 hours | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 2.2 | 2.2 | 24 hours | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, MVA | 6,3+6,3 | 0.2 | 0 |  | 0.2 | 0 | 6.62 | 6.42 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.2 | 0 |  | 0.2 | 0 | 6.62 | 6.42
49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 5.4 | 7.5 | 24 hours | -2.1 | 0 | 10.5 | 12.6 | 9.9 | opened | 49 | SS Sandovo 110/35/10 kv | 10,0+10,0 | 0.125 | 5.525 | 7.5 | 24 hours | -1.975 | 0 | 10.5 | 12.475 | 9.9 | opened
| Nom. capacity MV, MVA | 10,0+10,0 | 3.3 | 6 | 24 hours | -2.7 | 0 | 10.5 | 13.2 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0.125 | 3.425 | 6 | 24 hours | -2.575 | 0 | 10.5 | 13.075
| Nom. capacity LV, MVA | 10,0+10,0 | 2.1 | 1.5 | 24 hours | 0.6 | 0 | 10.5 | 9.9 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0 | 2.1 | 1.5 | 24 hours | 0.6 | 0 | 10.5 | 9.9
50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 17.1 | 5 | 24 hours | 12.1 | 0 | 26.3 | 14.2 | 14.2 | opened | 50 | SS Sholmino 110/35/10 kv | 25,0+25,0 | 0 | 17.1 | 5 | 24 hours | 12.1 | 0 | 26.3 | 14.2 | 14.2 | opened
| Nom. capacity MV, MVA | 25,0+25,0 | 5.9 | 5 | 24 hours | 0.9 | 0 | 26.3 | 25.4 |  |  |  | Nom. capacity MV, MVA | 25,0+25,0 | 0 | 5.9 | 5 | 24 hours | 0.9 | 0 | 26.3 | 25.4
| Nom. capacity LV, MVA | 25,0+25,0 | 11.2 | 0 |  | 11.2 | 0 | 26.3 | 15.1 |  |  |  | Nom. capacity LV, MVA | 25,0+25,0 | 0 | 11.2 | 0 |  | 11.2 | 0 | 26.3 | 15.1
51 | SS Belsky Karyer 35/6 kv | 4 | 0.08 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.07 | -0.07 | MS is closed | 51 | SS Belsky Karyer 35/6 kv | 4 | 0 | 0.08 | 0.01 | 24 hours | 0.01 | 0 | 0.01 | -0.07 | -0.07 | MS is closed
52 | SS Dubrovka 35/10 kv | 1.6 | 0.17 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0.07 | 0.07 | opened | 52 | SS Dubrovka 35/10 kv | 1.6 | 0 | 0.17 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0.07 | 0.07 | opened
53 | SS Zhilotkovo 35/10 kv | 1.8 | 0.19 | 0 |  | 0 | 0 | 0 | -0.19 | -0.19 | MS is closed | 53 | SS Zhilotkovo 35/10 kv | 1.8 | 0 | 0.19 | 0 |  | 0 | 0 | 0 | -0.19 | -0.19 | MS is closed
54 | SS Kopachevo 35/10 kv | 1.6 | 0.47 | 0.47 | 24 hours | 0.47 | 0 | 0.47 | 0 | 0 | opened | 54 | SS Kopachevo 35/10 kv | 1.6 | 0 | 0.47 | 0.47 | 24 hours | 0.47 | 0 | 0.47 | 0 | 0 | opened
55 | SS Kuznetsovo 35/10 kv | 1.6 | 0.51 | 0.51 | 24 hours | 0.51 | 0 | 0.51 | 0 | 0 | opened | 55 | SS Kuznetsovo 35/10 kv | 1.6 | 0 | 0.51 | 0.51 | 24 hours | 0.51 | 0 | 0.51 | 0 | 0 | opened
56 | SS Luzhnikovo 35/10 kv | 2.5 | 0.102 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | -0.002 | -0.002 | MS is closed | 56 | SS Luzhnikovo 35/10 kv | 2.5 | 0 | 0.102 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | -0.002 | -0.002 | MS is closed
57 | SS Nasakino 35/10 kv | 0.56 | 0.05 | 0 |  | 0 | 0 | 0 | -0.05 | -0.05 | MS is closed | 57 | SS Nasakino 35/10 kv | 0.56 | 0 | 0.05 | 0 |  | 0 | 0 | 0 | -0.05 | -0.05 | MS is closed
58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 1.32 | 1.32 | 24 hours | 1.32 | 0 | 1.32 | 0 | 0 | opened | 58 | SS Oktyabrsky Karyer 110/35 kv | 25 | 0 | 1.32 | 1.32 | 24 hours | 1.32 | 0 | 1.32 | 0 | 0 | opened
59 | SS Porozhki 35/10 kv | 1 | 0.43 | 0.43 | 24 hours | 0.43 | 0 | 0.43 | 0 | 0 | opened | 59 | SS Porozhki 35/10 kv | 1 | 0.0491 | 0.4791 | 0.43 | 24 hours | 0.43 | 0 | 0.43 | -0.0491 | -0.0491 | MS is closed
60 | SS Kh.B.K. 35/6 kv | 4 | 2.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -1.8 | -1.8 | MS is closed | 60 | SS Kh.B.K. 35/6 kv | 4 | 0 | 2.7 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | -1.8 | -1.8 | MS is closed
61 | SS no.5 35/6 kv | 1.0+1.6 | 0.65 | 0 |  | 0.65 | 0 | 1.05 | 0.4 | 0.4 | opened | 61 | SS no.5 35/6 kv | 1.0+1.6 | 0 | 0.65 | 0 |  | 0.65 | 0 | 1.05 | 0.4 | 0.4 | opened
62 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0.05 | 0 |  | 0.05 | 0 | 1.05 | 1 | 1 | opened | 62 | SS Afanasovo 35/6 kv | 1.0+1.8 | 0 | 0.05 | 0 |  | 0.05 | 0 | 1.05 | 1 | 1 | opened
63 | SS Borisovo 35/6 kv | 3.2+3.2 | 2.67 | 0 |  | 2.67 | 0 | 3.36 | 0.69 | 0.69 | opened | 63 | SS Borisovo 35/6 kv | 3.2+3.2 | 0 | 2.67 | 0 |  | 2.67 | 0 | 3.36 | 0.69 | 0.69 | opened
64 | SS Borovno 35/10 kv | 2.5+2.5 | 0.58 | 0.2 | 120 | 0.38 | 0 | 2.63 | 2.25 | 2.25 | opened | 64 | SS Borovno 35/10 kv | 2.5+2.5 | 0 | 0.58 | 0.2 | 120 | 0.38 | 0 | 2.63 | 2.25 | 2.25 | opened
65 | SS Bushevets 110/10 kv | 6.3+6.3 | 0.51 | 0 |  | 0.51 | 0 | 6.62 | 6.11 | 6.11 | opened | 65 | SS Bushevets 110/10 kv | 6.3+6.3 | 0 | 0.51 | 0 |  | 0.51 | 0 | 6.62 | 6.11 | 6.11 | opened
66 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 3.7 | 0 |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 | opened | 66 | SS Veliky Oktyabr 35/6 kv | 6.3+6.3 | 0 | 3.7 | 0 |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 | opened
67 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0.425 | 0 |  | 0.425 | 0 | 1.68 | 1.255 | 1.255 | opened | 67 | SS Vydropuzhsk 35/10 kv | 2.5+1.6 | 0 | 0.425 | 0 |  | 0.425 | 0 | 1.68 | 1.255 | 1.255 | opened
68 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0.663 | 0.4 | 120 | 0.263 | 0 | 1.68 | 1.417 | 1.417 | opened | 68 | SS Golubye Ozyora 35/10 kv | 2.5+1.6 | 0 | 0.663 | 0.4 | 120 | 0.263 | 0 | 1.68 | 1.417 | 1.417 | opened
69 | SS Gorodok 35/10 kv | 1.6+1.6 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 | opened | 69 | SS Gorodok 35/10 kv | 1.6+1.6 | 0 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 | opened
70 | SS DOZ 35/10 kv | 4+4 | 6.205 | 0 |  | 6.205 | 0 | 4.2 | -2.005 | -2.005 | MS is closed | 70 | SS DOZ 35/10 kv | 4+4 | 0 | 6.205 | 0 |  | 6.205 | 0 | 4.2 | -2.005 | -2.005 | MS is closed
71 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.48 | 0 |  | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened | 71 | SS Dyatlovo 35/10 kv | 1.6+1.6 | 0.02 | 0.5 | 0 |  | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened
72 | SS Esenovichi 35/10 kv | 1.8+2.5 | 0.969 | 0 |  | 0.969 | 0 | 1.89 | 0.921 | 0.921 | opened | 72 | SS Esenovichi 35/10 kv | 1.8+2.5 | 0 | 0.969 | 0 |  | 0.969 | 0 | 1.89 | 0.921 | 0.921 | opened
73 | SS CG 35/10 kv | 6.3+6.3 | 0.204 | 0 |  | 0.204 | 0 | 6.62 | 6.416 | 6.416 | opened | 73 | SS CG 35/10 kv | 6.3+6.3 | 0 | 0.204 | 0 |  | 0.204 | 0 | 6.62 | 6.416 | 6.416 | opened
74 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0.59 | 0.2 | 120 | 0.39 | 0 | 6.62 | 6.23 | 6.23 | opened | 74 | SS Zaozyornaya 35/10 kv | 6.3+6.3 | 0 | 0.59 | 0.2 | 120 | 0.39 | 0 | 6.62 | 6.23 | 6.23 | opened
75 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0.66 | 0.2 | 120 | 0.46 | 0 | 2.63 | 2.17 | 2.17 | opened | 75 | SS Knyashchiny 35/10 kv | 2.5+2.5 | 0 | 0.66 | 0.2 | 120 | 0.46 | 0 | 2.63 | 2.17 | 2.17 | opened
76 | SS Kozlovo 35/10 kv | 1.8+4 | 0.68 | 0 |  | 0.68 | 0 | 1.89 | 1.21 | 1.21 | opened | 76 | SS Kozlovo 35/10 kv | 1.8+4 | 0 | 0.68 | 0 |  | 0.68 | 0 | 1.89 | 1.21 | 1.21 | opened
77 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened | 77 | SS Krasnoe Znamya 35/10 kv | 1.6+1.8 | 0 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened
78 | SS Krasny May 35/6 kv | 10+10 | 2.25 | 0 |  | 2.25 | 0 | 10.5 | 8.25 | 8.25 | opened | 78 | SS Krasny May 35/6 kv | 10+10 | 0.025 | 2.275 | 0 |  | 2.275 | 0 | 10.5 | 8.225 | 8.225 | opened
79 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 1.96 | 0.2 | 120 | 1.76 | 0 | 3.36 | 1.6 | 1.6 | opened | 79 | SS Kuzhenkino 35/10 kv | 3.2+3.2 | 0 | 1.96 | 0.2 | 120 | 1.76 | 0 | 3.36 | 1.6 | 1.6 | opened
80 | SS Lukino 35/10 kv | 2.5+1.6 | 0.22 | 0 |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 80 | SS Lukino 35/10 kv | 2.5+1.6 | 0 | 0.22 | 0 |  | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
81 | SS Makarovo 35/6 kv | 4+4 | 0.85 | 0.1 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened | 81 | SS Makarovo 35/6 kv | 4+4 | 0 | 0.85 | 0.1 | 120 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened
82 | SS Mankhino 110/10 kv | 2.5+2.5 | 0.26 | 0 |  | 0.26 | 0 | 2.63 | 2.37 | 2.37 | opened | 82 | SS Mankhino 110/10 kv | 2.5+2.5 | 0 | 0.26 | 0 |  | 0.26 | 0 | 2.63 | 2.37 | 2.37 | opened
83 | SS Moldino 35/10 kv | 1+1 | 0.85 | 0.2 | 120 | 0.65 | 0 | 1.05 | 0.4 | 0.4 | opened | 83 | SS Moldino 35/10 kv | 1+1 | 0.025 | 0.875 | 0.2 | 120 | 0.675 | 0 | 1.05 | 0.375 | 0.375 | opened
84 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0.697 | 0.5 | 120 | 0.197 | 0 | 1.05 | 0.853 | 0.853 | opened | 84 | SS Novo-Kuzminskaya 35/10 kv | 1+1 | 0.0358 | 0.7328 | 0.5 | 120 | 0.2328 | 0 | 1.05 | 0.8172 | 0.8172 | opened
85 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened | 85 | SS Ovsishche 35/10 kv | 2.5+1.6 | 0 | 0.41 | 0 |  | 0.41 | 0 | 1.68 | 1.27 | 1.27 | opened
86 | SS OEZ 35/6 kv | 2.5+5.6 | 1.6 | 1.25 | 120 | 0.35 | 0 | 2.63 | 2.28 | 2.28 | opened | 86 | SS OEZ 35/6 kv | 2.5+5.6 | 0 | 1.6 | 1.25 | 120 | 0.35 | 0 | 2.63 | 2.28 | 2.28 | opened
87 | SS Plotichno 35/10 kv | 1.8+1.6 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 | opened | 87 | SS Plotichno 35/10 kv | 1.8+1.6 | 0 | 0.289 | 0 |  | 0.289 | 0 | 1.68 | 1.391 | 1.391 | opened
88 | SS Popovo 35/10 kv | 1+1 | 0.66 | 0 |  | 0.66 | 0 | 1.05 | 0.39 | 0.39 | opened | 88 | SS Popovo 35/10 kv | 1+1 | 0 | 0.66 | 0 |  | 0.66 | 0 | 1.05 | 0.39 | 0.39 | opened
89 | SS Proletary 35/10 kv | 2.5+2.5 | 2.13 | 0.7 | 120 | 1.43 | 0 | 2.63 | 1.2 | 1.2 | opened | 89 | SS Proletary 35/10 kv | 2.5+2.5 | 0.03 | 2.16 | 0.7 | 120 | 1.46 | 0 | 2.63 | 1.17 | 1.17 | opened
90 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0.34 | 0 |  | 0.34 | 0 | 2.63 | 2.29 | 2.29 | opened | 90 | SS Rozhdestvo 35/10 kv | 2.5+2.5 | 0.015 | 0.355 | 0 |  | 0.355 | 0 | 2.63 | 2.275 | 2.275 | opened
91 | SS Ryad 35/10 kv | 2.5+2.5 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.63 | 2.4 | 2.4 | opened | 91 | SS Ryad 35/10 kv | 2.5+2.5 | 0 | 0.43 | 0.2 | 120 | 0.23 | 0 | 2.63 | 2.4 | 2.4 | opened
92 | Ss Seglino 35/10 kv | 1.6+1.6 | 0.68 | 0 |  | 0.68 | 0 | 1.68 | 1 | 1 | opened | 92 | Ss Seglino 35/10 kv | 1.6+1.6 | 0 | 0.68 | 0 |  | 0.68 | 0 | 1.68 | 1 | 1 | opened
93 | SS Soroki 35/10 kv | 2.5+2.5 | 0.595 | 0 |  | 0.595 | 0 | 2.63 | 2.035 | 2.035 | opened | 93 | SS Soroki 35/10 kv | 2.5+2.5 | 0 | 0.595 | 0 |  | 0.595 | 0 | 2.63 | 2.035 | 2.035 | opened
94 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0.7 | 0.4 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened | 94 | SS Terelesovo 35/10 kv | 1.6+1.6 | 0 | 0.7 | 0.4 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
95 | SS Timkovo 35/10 kv | 1.6+1.6 | 1.003 | 0 |  | 1.003 | 0 | 1.68 | 0.677 | 0.677 | opened | 95 | SS Timkovo 35/10 kv | 1.6+1.6 | 0.1013 | 1.1043 | 0 |  | 1.1043 | 0 | 1.68 | 0.5757 | 0.5757 | opened
96 | SS Firovo 35/10 kv | 2.5+2.5 | 1.785 | 1.35 | 120 | 0.435 | 0 | 2.63 | 2.195 | 2.195 | opened | 96 | SS Firovo 35/10 kv | 2.5+2.5 | 0 | 1.785 | 1.35 | 120 | 0.435 | 0 | 2.63 | 2.195 | 2.195 | opened
97 | SS Yubileynaya 35/6 kv | 7.5+10 | 4.8 | 0.9 | 120 | 3.9 | 0 | 8.17 | 4.27 | 4.27 | opened | 97 | SS Yubileynaya 35/6 kv | 7.5+10 | 0.375 | 5.175 | 0.9 | 120 | 4.275 | 0 | 8.17 | 3.895 | 3.895 | opened
98 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0.204 | 0.17 | 120 | 0.034 | 0 | 2.63 | 2.596 | 2.596 | opened | 98 | SS Yakonovo 35/10 kv | 2.5+2.5 | 0 | 0.204 | 0.17 | 120 | 0.034 | 0 | 2.63 | 2.596 | 2.596 | opened
99 | SS Brusovo 110/35/10 kv | 10+10 | 2.58 | 3.9 | 120 | -1.32 | 0 | 10.5 | 11.82 | 10.5 | opened | 99 | SS Brusovo 110/35/10 kv | 10+10 | 0.314 | 2.894 | 3.9 | 120 | -1.006 | 0 | 10.5 | 11.506 | 10.5 | opened
| Nom. capacity MV, MVA | 10+10 | 2.1 | 2.1 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 2.1 | 2.1 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 0.48 | 1.8 | 120 | -1.32 | 0 | 10.5 | 11.82 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.314 | 0.794 | 1.8 | 120 | -1.006 | 0 | 10.5 | 11.506
100 | SS Vypozovo 110/35/6 kv | 10+10 | 5.4 | 6.88 | 120 | -1.48 | 0 | 10.5 | 11.98 | 10.5 | opened | 100 | SS Vypozovo 110/35/6 kv | 10+10 | 0 | 5.4 | 6.88 | 120 | -1.48 | 0 | 10.5 | 11.98 | 10.5 | opened
| Nom. capacity MV, MVA | 10+10 | 3.18 | 3.18 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 3.18 | 3.18 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+10 | 2.22 | 3.7 | 120 | -1.48 | 0 | 10.5 | 11.98 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.22 | 3.7 | 120 | -1.48 | 0 | 10.5 | 11.98
101 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 28.7 | 19.6 | 120 | 9.1 | 0 | 42 | 32.9 | 30 | opened | 101 | SS Vyshny Volochek 110/35/6 kv | 40+40 | 0.45 | 29.15 | 19.6 | 120 | 9.55 | 0 | 42 | 32.45 | 29.55 | opened
| Nom. capacity MV, MVA | 40+40 | 22.8 | 10.8 | 120 | 12 | 0 | 42 | 30 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.45 | 23.25 | 10.8 | 120 | 12.45 | 0 | 42 | 29.55
| Nom. capacity LV, MVA | 40+40 | 5.9 | 8.8 | 120 | -2.9 | 0 | 42 | 44.9 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 5.9 | 8.8 | 120 | -2.9 | 0 | 42 | 44.9
102 | SS Kasharovo 110/35/10-6 kv | 25+20 | 11.99 | 11.5 | 120 | 0.49 | 0 | 21 | 20.51 | 20.51 | opened | 102 | SS Kasharovo 110/35/10-6 kv | 25+20 | 0.0313 | 12.0213 | 11.5 | 120 | 0.5213 | 0 | 21 | 20.4787 | 20.4787 | opened
| Nom. capacity MV, MVA | 25+20 | 7.2 | 7.2 | 120 | 0 | 0 | 21 | 21 |  |  |  | Nom. capacity MV, MVA | 25+20 | 0 | 7.2 | 7.2 | 120 | 0 | 0 | 21 | 21
| Nom. capacity LV, MVA | 25+20 | 4.79 | 4.3 | 120 | 0.49 | 0 | 21 | 20.51 |  |  |  | Nom. capacity LV, MVA | 25+20 | 0.0313 | 4.8213 | 4.3 | 120 | 0.5213 | 0 | 21 | 20.4787
103 | SS Spirovo 110/35/10 kv | 16+16 | 3.32 | 1.2 | 120 | 2.12 | 0 | 16.8 | 14.68 | 14.68 | opened | 103 | SS Spirovo 110/35/10 kv | 16+16 | 0 | 3.32 | 1.2 | 120 | 2.12 | 0 | 16.8 | 14.68 | 14.68 | opened
| Nom. capacity MV, MVA | 16+16 | 0.6 | 0.6 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0 | 0.6 | 0.6 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16+16 | 2.72 | 0.6 | 120 | 2.12 | 0 | 16.8 | 14.68 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 2.72 | 0.6 | 120 | 2.12 | 0 | 16.8 | 14.68
104 | SS Trud 110/35/10 kv | 16+16 | 4.11 | 4.02 | 120 | 0.09 | 0 | 16.8 | 16.71 | 16.71 | opened | 104 | SS Trud 110/35/10 kv | 16+16 | 0.015 | 4.125 | 4.02 | 120 | 0.105 | 0 | 16.8 | 16.695 | 16.695 | opened
| Nom. capacity MV, MVA | 16+16 | 4.02 | 4.02 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.015 | 4.035 | 4.02 | 120 | 0.015 | 0 | 16.8 | 16.785
| Nom. capacity LV, MVA | 16+16 | 0.09 | 0 |  | 0.09 | 0 | 16.8 | 16.71 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0 | 0.09 | 0 |  | 0.09 | 0 | 16.8 | 16.71
105 | SS Udomlya 110/35/10 kv | 25+25 | 9.06 | 11.16 | 120 | -2.1 | 0 | 26.25 | 28.35 | 26.25 | opened | 105 | SS Udomlya 110/35/10 kv | 25+25 | 4.9351 | 13.9951 | 11.16 | 120 | 2.8351 | 0 | 26.25 | 23.4149 | 21.7219 | opened
| Nom. capacity MV, MVA | 25+25 | 3.96 | 3.96 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 25+25 | 4.5281 | 8.4881 | 3.96 | 120 | 4.5281 | 0 | 26.25 | 21.7219
| Nom. capacity LV, MVA | 25+25 | 5.1 | 7.2 | 120 | -2.1 | 0 | 26.25 | 28.35 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.407 | 5.507 | 7.2 | 120 | -1.693 | 0 | 26.25 | 27.943
106 | SS kholokholenka 110/35/10 kv | 6.3+6.3 | 3.35 | 2.16 | 120 | 1.19 | 0 | 6.62 | 5.43 | 5.43 | opened | 106 | SS kholokholenka 110/35/10 kv | 6.3+6.3 | 3.5 | 6.85 | 2.16 | 120 | 4.69 | 0 | 6.62 | 1.93 | 1.93 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 2.16 | 2.16 | 120 | 0 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 2.16 | 2.16 | 120 | 0 | 0 | 6.62 | 6.62
| Nom. capacity LV, MVA | 6,3+6,3 | 1.19 | 0 |  | 1.19 | 0 | 6.62 | 5.43 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 3.5 | 4.69 | 0 |  | 4.69 | 0 | 6.62 | 1.93
107 | 35/6 kv Mikrorayonnaya | 6.3 | 2.2689 | 2.2689 | 24 hours | 2.2689 | 0 | 2.2689 | 0 | 0 | opened | 107 | 35/6 kv Mikrorayonnaya | 6.3 | 0 | 2.2689 | 2.2689 | 24 hours | 2.2689 | 0 | 2.2689 | 0 | 0 | opened
108 | 35/10 kv Barykovo | 2,5 +2,5 | 0.94458 | 0 |  | 0.94458 | 0 | 2.625 | 1.6804 | 1.6804 | opened | 108 | 35/10 kv Barykovo | 2,5 +2,5 | 0.1495 | 1.0941 | 0 |  | 1.0941 | 0 | 2.625 | 1.5309 | 1.5309 | opened
109 | 35/10 kv B.Gorodok | 5,6 +4,0 | 3.5074 | 0 |  | 3.5074 | 0 | 4.2 | 0.6926 | 0.6926 | opened | 109 | 35/10 kv B.Gorodok | 6,3+6,3 (according to TS) | 2.6515 | 6.1589 | 0 |  | 6.1589 | 0 | 6.62 | 0.4611 | 0.4611 | opened
110 | 35/10 kv Vega | 2,5 +2,5 | 0.7266 | 0 |  | 0.7266 | 0 | 2.625 | 1.8984 | 1.8984 | opened | 110 | 35/10 kv Vega | 2,5 +2,5 | 0.2393 | 0.9659 | 0 |  | 0.9659 | 0 | 2.625 | 1.6591 | 1.6591 | opened
111 | 35/10 kv Volga | 6,3+6,3 | 4.2324 | 0 |  | 4.2324 | 0 | 6.615 | 2.3826 | 2.3826 | opened | 111 | 35/10 kv Volga | 6,3+6,3 | 0.029 | 4.2614 | 0 |  | 4.2614 | 0 | 6.615 | 2.3536 | 2.3536 | opened
112 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 1.9245 | 0 |  | 1.9245 | 0 | 2.625 | 0.70055 | 0.70055 | opened | 112 | 35/10 kv Ilyinskoe | 4,0 +2,5 | 0.1368 | 2.0613 | 0 |  | 2.0613 | 0 | 2.625 | 0.56375 | 0.56375 | opened
113 | 35/10 kv Kalyazin | 6,3 +6,3 | 7.1478 | 0 |  | 7.1478 | 0 | 6.615 | -0.53284 | -0.53284 | MS is closed | 113 | 35/10 kv Kalyazin | 6,3 +6,3 | 0.1363 | 7.2841 | 0 |  | 7.2841 | 0 | 6.615 | -0.66914 | -0.66914 | MS is closed
114 | 35/10 kv Kimry | 16,0+16,0 | 8.1169 | 0 |  | 8.1169 | 0 | 16.8 | 8.6831 | 8.6831 | opened | 114 | 35/10 kv Kimry | 16,0+16,0 | 0.053 | 8.1699 | 0 |  | 8.1699 | 0 | 16.8 | 8.6301 | 8.6301 | opened
115 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0.85376 | 0 |  | 0.85376 | 0 | 2.625 | 1.7712 | 1.7712 | opened | 115 | 35/10 kv Kozmodemyanovskaya | 2,5 +2,5 | 0.018 | 0.87175 | 0 |  | 0.87175 | 0 | 2.625 | 1.7532 | 1.7532 | opened
116 | 35/10 kv Kurortnaya | 4,0 +4,0 | 1.4532 | 0 |  | 1.4532 | 0 | 4.2 | 2.7468 | 2.7468 | opened | 116 | 35/10 kv Kurortnaya | 4,0 +4,0 | 0.097 | 1.5502 | 0 |  | 1.5502 | 0 | 4.2 | 2.6498 | 2.6498 | opened
117 | 35/10 kv Mayak | 6,3 +6,3 | 3.4695 | 0 |  | 3.4695 | 0 | 6.615 | 3.1455 | 3.1455 | opened | 117 | 35/10 kv Mayak | 6,3 +6,3 | 3.467 | 6.9365 | 0 |  | 6.9365 | 0 | 6.615 | -0.32151 | -0.32151 | MS is closed
118 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 2.2706 | 0 |  | 2.2706 | 0 | 4.2 | 1.9294 | 1.9294 | opened | 118 | 35/10 kv Mikrorayonnaya | 4,0+4,0 | 0.1135 | 2.3841 | 0 |  | 2.3841 | 0 | 4.2 | 1.8159 | 1.8159 | opened
119 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0.52177 | 0 |  | 0.52177 | 0 | 1.89 | 1.3682 | 1.3682 | opened | 119 | 35/10 kv Nagorskoe | 2,5 +1,8 | 0 | 0.52177 | 0 |  | 0.52177 | 0 | 1.89 | 1.3682 | 1.3682 | opened
120 | 35/10 kv Neklyudovo | 1,6 +1,6 | 1.1807 | 0 |  | 1.1807 | 0 | 1.68 | 0.49928 | 0.49928 | opened | 120 | 35/10 kv Neklyudovo | 1,6 +1,6 | 0.143 | 1.3237 | 0 |  | 1.3237 | 0 | 1.68 | 0.35628 | 0.35628 | opened
121 | 35/10 kv Nerl | 4,0 +2,5 | 1.3987 | 0 |  | 1.3987 | 0 | 2.625 | 1.2263 | 1.2263 | opened | 121 | 35/10 kv Nerl | 4,0 +2,5 | 0.3828 | 1.7815 | 0 |  | 1.7815 | 0 | 2.625 | 0.84349 | 0.84349 | opened
122 | 35/10 kv Plutkovo | 2,5 +2,5 | 0.89009 | 0 |  | 0.89009 | 0 | 2.625 | 1.7349 | 1.7349 | opened | 122 | 35/10 kv Plutkovo | 2,5 +2,5 | 0.047 | 0.93708 | 0 |  | 0.93708 | 0 | 2.625 | 1.6879 | 1.6879 | opened
123 | 35/10 kv Savtsino | 2,5 +2,5 | 0.23615 | 0 |  | 0.23615 | 0 | 2.625 | 2.3889 | 2.3889 | opened | 123 | 35/10 kv Savtsino | 2,5 +2,5 | 0 | 0.23615 | 0 |  | 0.23615 | 0 | 2.625 | 2.3889 | 2.3889 | opened
124 | 35/10 kv Sotskoe | 1,6 +2,5 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 | opened | 124 | 35/10 kv Sotskoe | 1,6 +2,5 | 0 | 0.45413 | 0 |  | 0.45413 | 0 | 1.68 | 1.2259 | 1.2259 | opened
125 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0.19981 | 0 |  | 0.19981 | 0 | 2.625 | 2.4252 | 2.4252 | opened | 125 | 35/10 kv Stoyantsy | 2,5 +2,5 | 0 | 0.19981 | 0 |  | 0.19981 | 0 | 2.625 | 2.4252 | 2.4252 | opened
126 | 35/10 kv Ulanovo | 1,6 +1,6 | 1.2055 | 0 |  | 1.2055 | 0 | 1.68 | 0.47454 | 0.47454 | opened | 126 | 35/10 kv Ulanovo | 1,6 +1,6 | 0.034 | 1.2395 | 0 |  | 1.2395 | 0 | 1.68 | 0.44054 | 0.44054 | opened
127 | 35/10 kv Unitsy | 4,0 +4,0 | 0.2159 | 0 |  | 0.2159 | 0 | 4.2 | 3.9841 | 3.9841 | opened | 127 | 35/10 kv Unitsy | 4,0 +4,0 | 0 | 0.2159 | 0 |  | 0.2159 | 0 | 4.2 | 3.9841 | 3.9841 | opened
128 | 35/10 kv Fenevo | 2,5 +2,5 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 | opened | 128 | 35/10 kv Fenevo | 2,5 +2,5 | 0 | 0.25725 | 0 |  | 0.25725 | 0 | 2.625 | 2.3677 | 2.3677 | opened
129 | 35/10 kv Frolovo | 2,5 +2,5 | 0.84562 | 0 |  | 0.84562 | 0 | 2.625 | 1.7794 | 1.7794 | opened | 129 | 35/10 kv Frolovo | 2,5 +2,5 | 0.0908 | 0.93642 | 0 |  | 0.93642 | 0 | 2.625 | 1.6886 | 1.6886 | opened
130 | 110/10 kv Zarnitsa | 10,0+10,0 | 0.10899 | 0 |  | 0.10899 | 0 | 10.5 | 10.391 | 10.391 | opened | 130 | 110/10 kv Zarnitsa | 10,0+10,0 | 0.017 | 0.12599 | 0 |  | 0.12599 | 0 | 10.5 | 10.374 | 10.374 | opened
131 | 110/10 kv Zobnino | 2,5 +2,5 | 0.78084 | 0 |  | 0.78084 | 0 | 2.625 | 1.8442 | 1.8442 | opened | 131 | 110/10 kv Zobnino | 2,5 +2,5 | 0 | 0.78084 | 0 |  | 0.78084 | 0 | 2.625 | 1.8442 | 1.8442 | opened
132 | 110/10 kv Inyakino | 25,0+25,0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 | opened | 132 | 110/10 kv Inyakino | 25,0+25,0 | 0 | 0.23269 | 0 |  | 0.23269 | 0 | 26.25 | 26.0173 | 26.0173 | opened
133 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 | opened | 133 | 110/35/10 kv Vasilevo | 6,3 +6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 | 6.4738 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3+6,3 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0 | 0.14117 | 0 |  | 0.14117 | 0 | 6.615 | 6.4738
134 | 110/35/10 kv Borki | 40,0+25,0 | 21.0011 | 0 |  | 21.0011 | 0 | 26.25 | 5.2489 | 5.2489 | opened | 134 | 110/35/10 kv Borki | 40,0+40,0( according to IP) | 6.4075 | 27.4086 | 0 |  | 27.4086 | 0 | 42 | 14.5914 | 14.5914 | opened
| Nom. capacity MV, MVA | 40,0+25,0 | 17.1797 | 0 |  | 17.1797 | 0 | 26.25 | 9.0703 |  |  |  | Nom. capacity MV, MVA | 40,0+40,0( according to IP) | 6.1475 | 23.3272 | 0 |  | 23.3272 | 0 | 42 | 18.6728
| Nom. capacity LV, MVA | 40,0+25,0 | 3.8214 | 0 |  | 3.8214 | 0 | 26.25 | 22.4286 |  |  |  | Nom. capacity LV, MVA | 40,0+40,0( according to IP) | 0.26 | 4.0814 | 0 |  | 4.0814 | 0 | 42 | 37.9186
135 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 3.9329 | 0.83421 | 24 hours | 3.0986 | 0 | 6.615 | 3.5164 | 3.5164 | opened | 135 | 110/35/10 kv Verkhnyaya Troitsa | 6,3 +6,3 | 0.2193 | 4.1522 | 0.83421 | 24 hours | 3.3179 | 0 | 6.615 | 3.2971 | 3.2971 | opened
| Nom. capacity MV, MVA | 6,3 +6,3 | 2.2383 | 0.83421 | 24 hours | 1.4041 | 0 | 6.615 | 5.2109 |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0.143 | 2.3813 | 0.83421 | 24 hours | 1.5471 | 0 | 6.615 | 5.0679
| Nom. capacity LV, MVA | 6,3 +6,3 | 1.6945 | 0 |  | 1.6945 | 0 | 6.615 | 4.9205 |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0.0763 | 1.7708 | 0 |  | 1.7708 | 0 | 6.615 | 4.8442
136 | 110/35/10 kv Goritsy | 6,3 +6,3 | 1.9018 | 0.13131 | 24 hours | 1.7705 | 0 | 6.615 | 4.8445 | 4.8445 | opened | 136 | 110/35/10 kv Goritsy | 6,3 +6,3 | 0.025 | 1.9268 | 0.13131 | 24 hours | 1.7955 | 0 | 6.615 | 4.8195 | 4.8195 | opened
| Nom. capacity MV, MVA | 6,3 +6,3 | 0.13131 | 0.13131 | 24 hours | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, MVA | 6,3 +6,3 | 0 | 0.13131 | 0.13131 | 24 hours | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, MVA | 6,3 +6,3 | 1.7705 | 0 |  | 1.7705 | 0 | 6.615 | 4.8445 |  |  |  | Nom. capacity LV, MVA | 6,3 +6,3 | 0.025 | 1.7955 | 0 |  | 1.7955 | 0 | 6.615 | 4.8195
137 | 110/35/10 kv Luch | 16,0+16,0 | 16.7201 | 0 |  | 16.7201 | 0 | 16.8 | 0.079858 | 0.079858 | opened | 137 | 110/35/10 kv Luch | 16,0+16,0 | 1.5431 | 18.2632 | 0 |  | 18.2632 | 0 | 16.8 | -1.4632 | -1.4632 | MS is closed
| Nom. capacity MV, MVA | 16,0+16,0 | 12.994 | 0 |  | 12.994 | 0 | 16.8 | 3.806 |  |  |  | Nom. capacity MV, MVA | 16,0+16,0 | 0.4566 | 13.4506 | 0 |  | 13.4506 | 0 | 16.8 | 3.3494
| Nom. capacity LV, MVA | 16,0+16,0 | 3.7261 | 0 |  | 3.7261 | 0 | 16.8 | 13.0739 |  |  |  | Nom. capacity LV, MVA | 16,0+16,0 | 1.0865 | 4.8126 | 0 |  | 4.8126 | 0 | 16.8 | 11.9874
138 | 110/35/10 kv Prostor | 25,0+16,0 | 12.8011 | 0.45413 | 24 hours | 12.347 | 0 | 16.8 | 4.453 | 4.453 | opened | 138 | 110/35/10 kv Prostor | 25,0+16,0 | 0.8308 | 13.6319 | 0.45413 | 24 hours | 13.1778 | 0 | 16.8 | 3.6222 | 3.6222 | opened
| Nom. capacity MV, MVA | 25,0+16,0 | 4.2514 | 0.45413 | 24 hours | 3.7973 | 0 | 16.8 | 13.0027 |  |  |  | Nom. capacity MV, MVA | 25,0+16,0 | 0.3553 | 4.6067 | 0.45413 | 24 hours | 4.1526 | 0 | 16.8 | 12.6474
| Nom. capacity LV, MVA | 25,0+16,0 | 8.5497 | 0 |  | 8.5497 | 0 | 16.8 | 8.2503 |  |  |  | Nom. capacity LV, MVA | 25,0+16,0 | 0.4755 | 9.0252 | 0 |  | 9.0252 | 0 | 16.8 | 7.7748
139 | 110/35/10 kv Raduga | 40,0+25,0 | 25.7398 | 0.13 | 24 hours | 25.6098 | 0 | 26.25 | 0.64022 | 0.64022 | opened | 139 | 110/35/10 kv Raduga | 40,0+40,0( according to IP) | 0.3766 | 26.1164 | 0.13 | 24 hours | 25.9864 | 0 | 42 | 16.0136 | 16.0136 | opened
| Nom. capacity MV, MVA | 40,0+25,0 | 17.9833 | 0.13 | 24 hours | 17.8533 | 0 | 26.25 | 8.3967 |  |  |  | Nom. capacity MV, MVA | 40,0+40,0( according to IP) | 0.1898 | 18.1731 | 0.13 | 24 hours | 18.0431 | 0 | 42 | 23.9569
| Nom. capacity LV, MVA | 40,0+25,0 | 7.7565 | 0 |  | 7.7565 | 0 | 26.25 | 18.4935 |  |  |  | Nom. capacity LV, MVA | 40,0+40,0( according to IP) | 0.1868 | 7.9433 | 0 |  | 7.9433 | 0 | 42 | 34.0567
140 | 110/35/10 kv Roshcha | 10,0+10,0 | 4.2683 | 0.39963 | 24 hours | 3.8686 | 0 | 10.5 | 6.6314 | 6.6314 | opened | 140 | 110/35/10 kv Roshcha | 10,0+10,0 | 0.9585 | 5.2268 | 0.39963 | 24 hours | 4.8271 | 0 | 10.5 | 5.6729 | 5.6729 | opened
| Nom. capacity MV, MVA | 10,0+10,0 | 0.8657 | 0.39963 | 24 hours | 0.46607 | 0 | 10.5 | 10.0339 |  |  |  | Nom. capacity MV, MVA | 10,0+10,0 | 0 | 0.8657 | 0.39963 | 24 hours | 0.46607 | 0 | 10.5 | 10.0339
| Nom. capacity LV, MVA | 10,0+10,0 | 3.4026 | 0 |  | 3.4026 | 0 | 10.5 | 7.0974 |  |  |  | Nom. capacity LV, MVA | 10,0+10,0 | 0.9585 | 4.3611 | 0 |  | 4.3611 | 0 | 10.5 | 6.1389
141 | SS 110/10 kv Bibirevo | 2.5 | 0.1 | 1 | 24 hours | 1 | 0 | 1 | 0.9 | 0.9 | opened | 141 | SS 110/10 kv Bibirevo | 2.5 | 0 | 0.1 | 1 | 24 hours | 1 | 0 | 1 | 0.9 | 0.9 | opened
142 | SS 35/10 kv Bor | 1.6 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened | 142 | SS 35/10 kv Bor | 1.6 | 0 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened
143 | SS 110/10 kv Vorobyi | 2.5 | 0.3 | 1 | 24 hours | 1 | 0 | 1 | 0.7 | 0.7 | opened | 143 | SS 110/10 kv Vorobyi | 2.5 | 0 | 0.3 | 1 | 24 hours | 1 | 0 | 1 | 0.7 | 0.7 | opened
144 | SS 35/10 kv Glazomichi | 2.5 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed | 144 | SS 35/10 kv Glazomichi | 2.5 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed
145 | SS 35/10 kv Zharki | 10 | 2.2 | 0 |  | 0 | 0 | 0 | -2.2 | -2.2 | MS is closed | 145 | SS 35/10 kv Zharki | 10 | 0.138 | 2.338 | 0 |  | 0 | 0 | 0 | -2.338 | -2.338 | MS is closed
146 | SS 35/10 kv Zemtsy | 2.5 | 0.5 | 1 | 24 hours | 1 | 0 | 1 | 0.5 | 0.5 | opened | 146 | SS 35/10 kv Zemtsy | 2.5 | 0 | 0.5 | 1 | 24 hours | 1 | 0 | 1 | 0.5 | 0.5 | opened
147 | SS 35/10 kv Kovalevo | 2.5 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened | 147 | SS 35/10 kv Kovalevo | 2.5 | 0 | 0.2 | 1 | 24 hours | 1 | 0 | 1 | 0.8 | 0.8 | opened
148 | SS 35/10 kv Korotyshi | 1.6 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened | 148 | SS 35/10 kv Korotyshi | 1.6 | 0 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened
149 | SS 110/10 kv Monino | 6.3 | 1.3 | 1 | 24 hours | 1 | 0 | 1 | -0.3 | -0.3 | MS is closed | 149 | SS 110/10 kv Monino | 6.3 | 0.165 | 1.465 | 1 | 24 hours | 1 | 0 | 1 | -0.465 | -0.465 | MS is closed
150 | SS 35/10 kv Ozerets | 1.6 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed | 150 | SS 35/10 kv Ozerets | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed
151 | SS 35/10 kv Pozhnya | 1.6 | 0.2 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.4 | 0.4 | opened | 151 | SS 35/10 kv Pozhnya | 1.6 | 0.035 | 0.235 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.365 | 0.365 | opened
152 | SS 35/10 kv Polovtsovo | 1.6 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 152 | SS 35/10 kv Polovtsovo | 1.6 | 0 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
153 | SS 110/10 kv Ponizovye | 2.5 | 0.3 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.4 | 0.4 | opened | 153 | SS 110/10 kv Ponizovye | 2.5 | 0.056 | 0.356 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.344 | 0.344 | opened
154 | SS 35/10 kv Sinkovo | 1 | 0.2 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0.1 | 0.1 | opened | 154 | SS 35/10 kv Sinkovo | 1 | 0.029 | 0.229 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0.071 | 0.071 | opened
155 | SS 35/10 kv Ulin | 1.6 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed | 155 | SS 35/10 kv Ulin | 1.6 | 0 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed
156 | SS 35/10 kv Kavelshchino | 2.5 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened | 156 | SS 35/10 kv Kavelshchino | 2.5 | 0 | 0.2 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.7 | 0.7 | opened
157 | SS 35/10 kv Bologovo | 1,6+2,5 | 0.3 | 0.7 | 120 | -0.4 | 0 | 1.68 | 2.08 | 2.08 | opened | 157 | SS 35/10 kv Bologovo | 1,6+2,5 | 0.2925 | 0.5925 | 0.7 | 120 | -0.1075 | 0 | 1.68 | 1.7875 | 1.7875 | opened
158 | SS 35/10 kv Verkhovye | 1+2,5 | 0.2 | 1 | 120 | -0.8 | 0 | 1.05 | 1.85 | 1.85 | opened | 158 | SS 35/10 kv Verkhovye | 1+2,5 | 0 | 0.2 | 1 | 120 | -0.8 | 0 | 1.05 | 1.85 | 1.85 | opened
159 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0.3 | 0.7 | 120 | -0.4 | 0 | 1.68 | 2.08 | 2.08 | opened | 159 | SS 35/10 kv Voskresenskoe | 1,6+1,6 | 0.073 | 0.373 | 0.7 | 120 | -0.327 | 0 | 1.68 | 2.007 | 2.007 | opened
160 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0.5 | 1 | 120 | -0.5 | 0 | 2.65 | 3.15 | 3.15 | opened | 160 | SS 35/10 kv Dashkovo | 2,5+2,5 | 0 | 0.5 | 1 | 120 | -0.5 | 0 | 2.65 | 3.15 | 3.15 | opened
161 | SS 35/10 kv Ilyino | 1,6+1,6 | 0.6 | 0.9 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | opened | 161 | SS 35/10 kv Ilyino | 1,6+1,6 | 0 | 0.6 | 0.9 | 120 | -0.3 | 0 | 1.68 | 1.98 | 1.98 | opened
162 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0.6 | 0.7 | 120 | -0.1 | 0 | 1.68 | 1.78 | 1.78 | opened | 162 | SS 35/10 kv Ploskosh | 1,6+1,6 | 0.065 | 0.665 | 0.7 | 120 | -0.035 | 0 | 1.68 | 1.715 | 1.715 | opened
163 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 3.4 | 1.5 | 120 | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened | 163 | SS 35/6 kv Polovtsovo | 5,6+5,6 | 0 | 3.4 | 1.5 | 120 | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened
164 | SS 35/10 kv St. Toropa | 4+4 | 1.8 | 0 |  | 1.8 | 0 | 4.5 | 2.7 | 2.7 | opened | 164 | SS 35/10 kv St. Toropa | 4+4 | 0.05 | 1.85 | 0 |  | 1.85 | 0 | 4.5 | 2.65 | 2.65 | opened
165 | SS 110/35/10 kv Andreapol | 10+10 | 6.95 | 0.7 | 120 | 6.25 | 0 | 10.5 | 4.25 | 4.25 | opened | 165 | SS 110/35/10 kv Andreapol | 10+10 | 5.2542 | 12.2042 | 0.7 | 120 | 11.5042 | 0 | 10.5 | -1.0042 | -1.0042 | MS is closed
| Nom. capacity MV, MVA | 10+10 | 0.75 | 0 |  | 0.75 | 0 | 10.5 | 9.75 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.39 | 1.14 | 0 |  | 1.14 | 0 | 10.5 | 9.36
| Nom. capacity LV, MVA | 10+10 | 6.2 | 0.7 | 120 | 5.5 | 0 | 10.5 | 5 |  |  |  | Nom. capacity LV, MVA | 10+10 | 4.8642 | 11.0642 | 0.7 | 120 | 10.3642 | 0 | 10.5 | 0.1358
166 | SS 110/35/10 kv Bely | 16+10 | 5.7 | 1 | 120 | 4.7 | 0 | 10.5 | 5.8 | 5.8 | opened | 166 | SS 110/35/10 kv Bely | 16+10 | 0.2343 | 5.9343 | 1 | 120 | 4.9343 | 0 | 10.5 | 5.5657 | 5.5657 | opened
| Nom. capacity MV, MVA | 16+10 | 3.1 | 0 |  | 3.1 | 0 | 10.5 | 7.4 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.138 | 3.238 | 0 |  | 3.238 | 0 | 10.5 | 7.262
| Nom. capacity LV, MVA | 16+10 | 2.6 | 1 | 120 | 1.6 | 0 | 10.5 | 8.9 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.0963 | 2.6963 | 1 | 120 | 1.6963 | 0 | 10.5 | 8.8037
167 | SS 110/35/10 kv Zapadnaya Dvina | 10+10 | 9.7 | 1 | 120 | 8.7 | 0 | 10.5 | 1.8 | 1.8 | opened | 167 | SS 110/35/10 kv Zapadnaya Dvina | 16+16 (according to IP) | 0.1588 | 9.8588 | 1 | 120 | 8.8588 | 0 | 16.8 | 7.9412 | 7.9412 | opened
| Nom. capacity MV, MVA | 10+10 | 1.7 | 1 | 120 | 0.7 | 0 | 10.5 | 9.8 |  |  |  | Nom. capacity MV, MVA | 16+16 (according to IP) | 0.05 | 1.75 | 1 | 120 | 0.75 | 0 | 16.8 | 16.05
| Nom. capacity LV, MVA | 10+10 | 8 | 0 |  | 8 | 0 | 10.5 | 2.5 |  |  |  | Nom. capacity LV, MVA | 16+16 (according to IP) | 0.1088 | 8.1088 | 0 |  | 8.1088 | 0 | 16.8 | 8.6912
168 | SS 110/35/10 kv Toropets | 16+25 | 16.8 | 2.2 | 120 | 14.6 | 0 | 16.8 | 2.2 | 2.2 | opened | 168 | SS 110/35/10 kv Toropets | 25(according to IP)+25 | 3.0475 | 19.8475 | 2.2 | 120 | 17.6475 | 0 | 26.25 | 8.6025 | 8.6025 | opened
| Nom. capacity MV, MVA | 16+25 | 4.9 | 1.2 | 120 | 3.7 | 0 | 16.8 | 13.1 |  |  |  | Nom. capacity MV, MVA | 25(according to IP)+25 | 0.173 | 5.073 | 1.2 | 120 | 3.873 | 0 | 26.25 | 22.377
| Nom. capacity LV, MVA | 16+25 | 11.9 | 1 | 120 | 10.9 | 0 | 16.8 | 5.9 |  |  |  | Nom. capacity LV, MVA | 25(according to IP)+25 | 2.8745 | 14.7745 | 1 | 120 | 13.7745 | 0 | 26.25 | 12.4755
169 | SS Bakhmutovo 35/10 kv | 2.5 | 0.50862 | 0.50862 | 120 | 0.50862 | 0 | 0.50862 | 0 | 0 | opened | 169 | SS Bakhmutovo 35/10 kv | 2.5 | 0 | 0.50862 | 0.50862 | 120 | 0.50862 | 0 | 0.50862 | 0 | 0 | opened
170 | SS Pyatnitskoe 35/10kv | 2.5 | 0.18165 | 0.18165 | 240 | 0.18165 | 0 | 0.18165 | 0 | 0 | opened | 170 | SS Pyatnitskoe 35/10kv | 2.5 | 0.03 | 0.21165 | 0.18165 | 240 | 0.18165 | 0 | 0.18165 | -0.03 | -0.03 | MS is closed
171 | SS Karamzino 35/10kv | 1.6 | 0.3633 | 0 |  | 0 | 0 | 0 | -0.3633 | -0.3633 | MS is closed | 171 | SS Karamzino 35/10kv | 1.6 | 0 | 0.3633 | 0 |  | 0 | 0 | 0 | -0.3633 | -0.3633 | MS is closed
172 | SS Kn. Gory 35/10kv | 2.5 | 1.2715 | 0.23333 | 240 | 0.23333 | 0 | 0.23333 | -1.0382 | -1.0382 | MS is closed | 172 | SS Kn. Gory 35/10kv | 2.5 | 0.5 | 1.7715 | 0.23333 | 240 | 0.23333 | 0 | 0.23333 | -1.5382 | -1.5382 | MS is closed
173 | SS Salino 35/10kv | 2.5 | 0.4498 | 0 |  | 0 | 0 | 0 | -0.4498 | -0.4498 | MS is closed | 173 | SS Salino 35/10kv | 2.5 | 0.25 | 0.6998 | 0 |  | 0 | 0 | 0 | -0.6998 | -0.6998 | MS is closed
174 | SS Gusevo 35/10kv | 2.5 | 0.30448 | 0.30448 | 120 | 0.30448 | 0 | 0.30448 | 0 | 0 | opened | 174 | SS Gusevo 35/10kv | 2.5 | 0 | 0.30448 | 0.30448 | 120 | 0.30448 | 0 | 0.30448 | 0 | 0 | opened
175 | SS Mol.Tud 35/10kv | 2.5 | 0.45413 | 0.45413 | 120 | 0.45413 | 0 | 0.45413 | 0 | 0 | opened | 175 | SS Mol.Tud 35/10kv | 2.5 | 0.015 | 0.46913 | 0.45413 | 120 | 0.45413 | 0 | 0.45413 | -0.015 | -0.015 | MS is closed
176 | SS Ilyenki 35/10kv | 2.5 | 0.1429 | 0.1429 | 120 | 0.1429 | 0 | 0.1429 | 0 | 0 | opened | 176 | SS Ilyenki 35/10kv | 2.5 | 0 | 0.1429 | 0.1429 | 120 | 0.1429 | 0 | 0.1429 | 0 | 0 | opened
177 | SS Kadenka 35/10kv | 1 | 0.23614 | 0.23614 | 120 | 0.23614 | 0 | 0.23614 | 0 | 0 | opened | 177 | SS Kadenka 35/10kv | 1 | 0 | 0.23614 | 0.23614 | 120 | 0.23614 | 0 | 0.23614 | 0 | 0 | opened
178 | SS Rodnya 35/10kv | 2.5 | 0.4588 | 0.4588 | 120 | 0.4588 | 0 | 0.4588 | 0 | 0 | opened | 178 | SS Rodnya 35/10kv | 2.5 | 0.022 | 0.4808 | 0.4588 | 120 | 0.4588 | 0 | 0.4588 | -0.022 | -0.022 | MS is closed
179 | SS Bernovo 35/10kv | 1.6 | 0.5792 | 0 |  | 0 | 0 | 0 | -0.5792 | -0.5792 | MS is closed | 179 | SS Bernovo 35/10kv | 1.6 | 0 | 0.5792 | 0 |  | 0 | 0 | 0 | -0.5792 | -0.5792 | MS is closed
180 | SS RMK 35/10kv | 10+10 | 13.67 | 8.1167 | 240 | 5.5533 | 0 | 10.5 | 4.9467 | 4.9467 | opened | 180 | SS RMK 35/10kv | 10+10 | 0.088 | 13.758 | 8.1167 | 240 | 5.6413 | 0 | 10.5 | 4.8587 | 4.8587 | opened
181 | SS Osuga 35/10kv | 2,5+2,5 | 0.23 | 0 |  | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened | 181 | SS Osuga 35/10kv | 2,5+2,5 | 0 | 0.23 | 0 |  | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened
182 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.58 | 0 |  | 1.58 | 0 | 2.625 | 1.045 | 1.045 | opened | 182 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.5415 | 3.1215 | 0 |  | 3.1215 | 0 | 2.625 | -0.4965 | -0.4965 | MS is closed
183 | SS Kleshnevo 35/10kv | 4+4 | 0.88 | 0 |  | 0.88 | 0 | 4.2 | 3.32 | 3.32 | opened | 183 | SS Kleshnevo 35/10kv | 4+4 | 0 | 0.88 | 0 |  | 0.88 | 0 | 4.2 | 3.32 | 3.32 | opened
184 | SS Zubtsov 35/10kv | 6,3+6,3 | 10.08 | 1.2167 | 120 | 8.8633 | 0 | 6.615 | -2.2483 | -2.2483 | MS is closed | 184 | SS Zubtsov 35/10kv | 6,3+6,3 | 1.884 | 11.964 | 1.2167 | 120 | 10.7473 | 0 | 6.615 | -4.1323 | -4.1323 | MS is closed
185 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 2.6 | 1.2 | 240 | 1.4 | 0 | 5.88 | 4.48 | 4.48 | opened | 185 | SS P.Gorodishche 35/10kv | 5,6+5,6 | 0 | 2.6 | 1.2 | 240 | 1.4 | 0 | 5.88 | 4.48 | 4.48 | opened
186 | SS Stepurino 35/10kv | 4+4 | 1.28 | 0 |  | 1.28 | 0 | 4.2 | 2.92 | 2.92 | opened | 186 | SS Stepurino 35/10kv | 4+4 | 0 | 1.28 | 0 |  | 1.28 | 0 | 4.2 | 2.92 | 2.92 | opened
187 | SS Maksimovo 35/10kv | 2,5+2,5 | 0.42 | 0.42 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 187 | SS Maksimovo 35/10kv | 2,5+2,5 | 0 | 0.42 | 0.42 | 240 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
188 | SS Lukovnikovo 35/10kv | 4+2,5 | 1.02 | 0 |  | 1.02 | 0 | 2.625 | 1.605 | 1.605 | opened | 188 | SS Lukovnikovo 35/10kv | 4+2,5 | 0.04 | 1.06 | 0 |  | 1.06 | 0 | 2.625 | 1.565 | 1.565 | opened
189 | SS NTPF 110/10kv | 6,3+6,3 | 1.33 | 0 |  | 1.33 | 0 | 6.615 | 5.285 | 5.285 | opened | 189 | SS NTPF 110/10kv | 6,3+6,3 | 0.75 | 2.08 | 0 |  | 2.08 | 0 | 6.615 | 4.535 | 4.535 | opened
190 | SS Mostovaya 110/10kv | 6,3+6,3 | 1.7 | 0.46667 | 240 | 1.2333 | 0 | 6.615 | 5.3817 | 5.3817 | opened | 190 | SS Mostovaya 110/10kv | 6,3+6,3 | 0.4375 | 2.1375 | 0.46667 | 240 | 1.6708 | 0 | 6.615 | 4.9442 | 4.9442 | opened
191 | SS Rzhev 110/35/10kv | 40.5+40 | 48.2 | 5.1851 | 24 hours | 43.0149 | 0 | 42 | -1.0149 | -1.0149 | MS is closed | 191 | SS Rzhev 110/35/10kv | 40.5+40 | 4.3885 | 52.5885 | 5.1851 | 24 hours | 47.4034 | 0 | 42 | -5.4034 | -5.4034 | MS is closed
| Nom. capacity MV, MVA | 40.5+40 | 38.57 | 2.7684 | 24 hours | 35.8016 | 0 | 42 | 6.1984 |  |  |  | Nom. capacity MV, MVA | 40.5+40 | 4.2635 | 42.8335 | 2.7684 | 24 hours | 40.0651 | 0 | 42 | 1.9349
| Nom. capacity LV, MVA | 40.5+40 | 9.63 | 2.4167 | 120 | 7.2133 | 0 | 42 | 34.7867 |  |  |  | Nom. capacity LV, MVA | 40.5+40 | 0.125 | 9.755 | 2.4167 | 120 | 7.3383 | 0 | 42 | 34.6617
192 | SS Chertolino 110/35/10kv | 5,6+6,3 | 1.27 | 0.1 | 240 | 1.17 | 0 | 5.88 | 4.71 | 4.71 | opened | 192 | SS Chertolino 110/35/10kv | 5,6+6,3 | 0.03 | 1.3 | 0.1 | 240 | 1.2 | 0 | 5.88 | 4.68 | 4.68 | opened
| Nom. capacity MV, MVA | 5,6+6,3 | 0.1 | 0.1 | 240 | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, MVA | 5,6+6,3 | 0.03 | 0.13 | 0.1 | 240 | 0.03 | 0 | 5.88 | 5.85
| Nom. capacity LV, MVA | 5,6+6,3 | 1.17 | 0 |  | 1.17 | 0 | 5.88 | 4.71 |  |  |  | Nom. capacity LV, MVA | 5,6+6,3 | 0 | 1.17 | 0 |  | 1.17 | 0 | 5.88 | 4.71
193 | SS Olenino 110/35/10 | 16+10 | 4.36 | 0 |  | 4.36 | 0 | 10.5 | 6.14 | 6.14 | opened | 193 | SS Olenino 110/35/10 | 16+10 | 0.0275 | 4.3875 | 0 |  | 4.3875 | 0 | 10.5 | 6.1125 | 6.1125 | opened
| Nom. capacity MV, MVA | 16+10 | 0.97 | 0 |  | 0.97 | 0 | 10.5 | 9.53 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.015 | 0.985 | 0 |  | 0.985 | 0 | 10.5 | 9.515
| Nom. capacity LV, MVA | 16+10 | 3.39 | 0 |  | 3.39 | 0 | 10.5 | 7.11 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.0125 | 3.4025 | 0 |  | 3.4025 | 0 | 10.5 | 7.0975
194 | SS Staritsa 110/35/10kv | 16+16 | 12.39 | 4.2325 |  | 8.1575 | 0 | 16.8 | 8.6425 | 8.6425 | opened | 194 | SS Staritsa 110/35/10kv | 16+16 | 1.3223 | 13.7123 | 4.2325 | 24 hours | 9.4798 | 0 | 16.8 | 7.3202 | 7.3202 | opened
| Nom. capacity MV, MVA | 16+16 | 3.76 | 3.2992 |  | 0.4608 | 0 | 16.8 | 16.3392 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.062 | 3.822 | 3.2992 | 24 hours | 0.5228 | 0 | 16.8 | 16.2772
| Nom. capacity LV, MVA | 16+16 | 8.63 | 0.93333 | 240 | 7.6967 | 0 | 16.8 | 9.1033 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.2603 | 9.8903 | 0.93333 | 240 | 8.957 | 0 | 16.8 | 7.843
195 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515 | 3.515 | opened | 195 | SS Z.Pole 110/35/10kv | 6,3+6,3 | 0 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515 | 3.515 | opened
| Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity MV, MVA | 6,3+6,3 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0 | 3.1 | 0 |  | 3.1 | 0 | 6.615 | 3.515
196 | SS Zolootval 110/10 | 2.5 | 0.42 | 0.42 | 24 hours | 0.42 | 0 | 0.42 | 0 | 0 | opened | 196 | SS Zolootval 110/10 | 2.5 | 3.375 | 3.795 | 3.795 | 24 hours | 3.795 | 0 | 3.795 | 0 | 0 | opened
197 | SS Krasnogorskaya 35/10 | 1.6 | 0.83 | 0 |  | 0 | 0 | 0 | -0.83 | -0.83 | MS is closed | 197 | SS Krasnogorskaya 35/10 | 1.6 | 0.10625 | 0.93625 | 0 |  | 0 | 0 | 0 | -0.93625 | -0.93625 | MS is closed
198 | SS Lisitsky Bor 35/10 | 2.5 | 1.37 | 0 |  | 0 | 0 | 0 | -1.37 | -1.37 | MS is closed | 198 | SS Lisitsky Bor 35/10 | 2.5 | 0.032 | 1.402 | 0 |  | 0 | 0 | 0 | -1.402 | -1.402 | MS is closed
199 | SS Danilovskaya 35/10 | 2.5 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed | 199 | SS Danilovskaya 35/10 | 6,3+6,3 (according to IP) | 0.86775 | 1.0108 | 0 |  | 1.0108 | 0 | 6.62 | 5.6093 | 5.6093 | opened
200 | SS No.6 35/10 | 1 | 0.03 | 0 |  | 0 | 0 | 0 | -0.03 | -0.03 | MS is closed | 200 | SS No.6 35/10 | 1 | 0 | 0.03 | 0 |  | 0 | 0 | 0 | -0.03 | -0.03 | MS is closed
201 | SS No.1 35/6 | 1 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed | 201 | SS No.1 35/6 | 1 | 0 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed
| SS No.1 35/10 | 2.5 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed |  | SS No.1 35/10 | 2.5 | 1.1027 | 2.6827 | 0 |  | 0 | 0 | 0 | -2.6827 | -2.6827 | MS is closed
202 | SS No.16 35/6 | 1 | 0.12 | 0 |  | 0 | 0 | 0 | -0.12 | -0.12 | MS is closed | 202 | SS No.16 35/6 | 1 | 0 | 0.12 | 0 |  | 0 | 0 | 0 | -0.12 | -0.12 | MS is closed
| SS No.16 35/10 | 2.5 | 0.85 | 0 |  | 0 | 0 | 0 | -0.85 | -0.85 | MS is closed |  | SS No.16 35/10 | 2.5 | 0 | 0.85 | 0 |  | 0 | 0 | 0 | -0.85 | -0.85 | MS is closed
203 | SS No.17 35/10 | 4 | 0.62 | 0 |  | 0 | 0 | 0 | -0.62 | -0.62 | MS is closed | 203 | SS No.17 35/10 | 4 | 0 | 0.62 | 0 |  | 0 | 0 | 0 | -0.62 | -0.62 | MS is closed
204 | SS Zolotikha 35/10 | 2.5 | 0.8 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0 | 0 | opened | 204 | SS Zolotikha 35/10 | 2.5 | 0 | 0.8 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0 | 0 | opened
205 | SS Novy Stan 35/10 | 2.5 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 | opened | 205 | SS Novy Stan 35/10 | 2.5 | 0 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 | opened
206 | SS Romanovo 35/10 | 2.5 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 | opened | 206 | SS Romanovo 35/10 | 2.5 | 0 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 | opened
207 | SS Pervitino 35/10 | 1.6 | 0.34 | 0 |  | 0 | 0 | 0 | -0.34 | -0.34 | MS is closed | 207 | SS Pervitino 35/10 | 1.6 | 0 | 0.34 | 0 |  | 0 | 0 | 0 | -0.34 | -0.34 | MS is closed
208 | SS No. 8 35/10 | 2.5 | 1.53 | 0 |  | 0 | 0 | 0 | -1.53 | -1.53 | MS is closed | 208 | SS No. 8 35/10 | 2.5 | 0.04125 | 1.5713 | 0 |  | 0 | 0 | 0 | -1.5713 | -1.5713 | MS is closed
209 | SS Aleksino 35/6 | 2.5 | 1.02 | 0 |  | 0 | 0 | 0 | -1.02 | -1.02 | MS is closed | 209 | SS Aleksino 35/6 | 2.5 | 0.324 | 1.344 | 0 |  | 0 | 0 | 0 | -1.344 | -1.344 | MS is closed
210 | SS Bezborodovo 35/10 | 2.5 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed | 210 | SS Bezborodovo 35/10 | 2.5 | 0 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed
211 | SS Medvedikha 110/10 | 2.5 | 0.57 | 0.57 | 24 hours | 0.57 | 0 | 0.57 | 0 | 0 | opened | 211 | SS Medvedikha 110/10 | 2.5 | 0.026 | 0.596 | 0.57 | 24 hours | 0.57 | 0 | 0.57 | -0.026 | -0.026 | MS is closed
212 | SS Kivirichi 35/10 | 2.5 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 | -0.7 | MS is closed | 212 | SS Kivirichi 35/10 | 2.5 | 0 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 | -0.7 | MS is closed
213 | SS Dievo 35/10 | 2.5 | 0.22 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.03 | 0.03 | opened | 213 | SS Dievo 35/10 | 2.5 | 0 | 0.22 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | 0.03 | 0.03 | opened
214 | SS Kushalino 35/10 | 2,5+2,5 | 1.81 | 0 |  | 1.81 | 0 | 2.63 | 0.82 | 0.82 | opened | 214 | SS Kushalino 35/10 | 2,5+2,5 | 0.13275 | 1.9427 | 0 |  | 1.9427 | 0 | 2.63 | 0.68725 | 0.68725 | opened
215 | SS No.4 35/6 | 5,6+5,6 | 1.9 | 0 |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened | 215 | SS No.4 35/6 | 5,6+5,6 | 0.965 | 2.865 | 0 |  | 2.865 | 0 | 5.88 | 3.015 | 3.015 | opened
216 | SS No.13 35/10/6 | 3,2+3,2 | 1.42 | 0 |  | 1.42 | 0 | 3.36 | 1.94 | 1.94 | opened | 216 | SS No.13 35/10/6 | 3,2+3,2 | 0 | 1.42 | 0 |  | 1.42 | 0 | 3.36 | 1.94 | 1.94 | opened
217 | SS No.27 35/6 | 10+10 | 13.45 | 0 |  | 13.45 | 0 | 10.5 | -2.95 | -2.95 | MS is closed | 217 | SS No.27 35/6 | 10+10 | 0.06375 | 13.5137 | 0 |  | 13.5137 | 0 | 10.5 | -3.0137 | -3.0137 | MS is closed
218 | SS Vagzhanovskaya 35/6 | 16+16 | 20.44 | 0 |  | 20.44 | 0 | 16.8 | -3.64 | -3.64 | MS is closed | 218 | SS Vagzhanovskaya 35/6 | 16+16 | 0.1125 | 20.5525 | 0 |  | 20.5525 | 0 | 16.8 | -3.7525 | -3.7525 | MS is closed
219 | SS Plant 1Maya 35/6 | 10+10 | 5.95 | 0 |  | 5.95 | 0 | 10.5 | 4.55 | 4.55 | opened | 219 | SS Plant 1Maya 35/6 | 10+10 | 2.5882 | 8.5382 | 0 |  | 8.5382 | 0 | 10.5 | 1.9618 | 1.9618 | opened
220 | SS Steklovolokno 35/6 | 10+10 | 6.05 | 0 |  | 6.05 | 0 | 10.5 | 4.45 | 4.45 | opened | 220 | SS Steklovolokno 35/6 | 10+10 | 0.31625 | 6.3662 | 0 |  | 6.3662 | 0 | 10.5 | 4.1338 | 4.1338 | opened
221 | SS Sominka 35/10 | 16+16 | 14.05 | 0 |  | 14.05 | 0 | 16.8 | 2.75 | 2.75 | opened | 221 | SS Sominka 35/10 | 16+16 | 0.01325 | 14.0633 | 0 |  | 14.0633 | 0 | 16.8 | 2.7367 | 2.7367 | opened
222 | SS Zavolzhskaya 35/6 | 7,5+10 | 7.83 | 0 |  | 7.83 | 0 | 7.88 | 0.05 | 0.05 | opened | 222 | SS Zavolzhskaya 35/6 | 7,5+10 | 0 | 7.83 | 0 |  | 7.83 | 0 | 7.88 | 0.05 | 0.05 | opened
223 | SS Kaloshvar 35/10 | 10+10 | 9.66 | 0 |  | 9.66 | 0 | 10.5 | 0.84 | 0.84 | opened | 223 | SS Kaloshvar 35/10 | 10+10 | 3.875 | 13.535 | 0 |  | 13.535 | 0 | 10.5 | -3.035 | -3.035 | MS is closed
224 | SS Mamulino 110/10 | 6,3+6,3 | 1.27 | 0 |  | 1.27 | 0 | 6.62 | 5.35 | 5.35 | opened | 224 | SS Mamulino 110/10 | 6,3+6,3 | 5.8825 | 7.1525 | 0 |  | 7.1525 | 0 | 6.62 | -0.5325 | -0.5325 | MS is closed
225 | SS Glazkovo 110/10 | 6,3+6,3 | 5.07 | 0 |  | 5.07 | 0 | 6.62 | 1.55 | 1.55 | opened | 225 | SS Glazkovo 110/10 | 6,3+6,3 | 0.6135 | 5.6835 | 0 |  | 5.6835 | 0 | 6.62 | 0.9365 | 0.9365 | opened
226 | SS Proletarskaya 110/10 | 16+16 | 8.7 | 0 |  | 8.7 | 0 | 16.8 | 8.1 | 8.1 | opened | 226 | SS Proletarskaya 110/10 | 16+16 | 1.0688 | 9.7688 | 0 |  | 9.7688 | 0 | 16.8 | 7.0312 | 7.0312 | opened
227 | SS Turginovo 35/10 | 6,3+6,3 | 3.5 | 0 |  | 3.5 | 0 | 6.62 | 3.12 | 3.12 | opened | 227 | SS Turginovo 35/10 | 6,3+6,3 | 0.7171 | 4.2171 | 0 |  | 4.2171 | 0 | 6.62 | 2.4029 | 2.4029 | opened
228 | SS Sakharovo 35/10 | 2,5+2,5 | 2.25 | 0 |  | 2.25 | 0 | 2.62 | 0.37 | 0.37 | opened | 228 | SS Sakharovo 35/10 | 2,5+2,5 | 0.8139 | 3.0639 | 0 |  | 3.0639 | 0 | 2.62 | -0.4439 | -0.4439 | MS is closed
229 | SS Golovino 35/10 | 2,5+2,5 | 0.73 | 0 |  | 0.73 | 0 | 2.62 | 1.89 | 1.89 | opened | 229 | SS Golovino 35/10 | 2,5+2,5 | 0.2335 | 0.9635 | 0 |  | 0.9635 | 0 | 2.62 | 1.6565 | 1.6565 | opened
230 | SS Kalikino 35/10 | 2+3,2 | 1.99 | 0 |  | 1.99 | 0 | 2.1 | 0.11 | 0.11 | opened | 230 | SS Kalikino 35/10 | 2+3,2 | 0.075 | 2.065 | 0 |  | 2.065 | 0 | 2.1 | 0.035 | 0.035 | opened
231 | SS Kvakshino 35/10 | 4+4 | 0.92 | 0 |  | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened | 231 | SS Kvakshino 35/10 | 4+4 | 0.025 | 0.945 | 0 |  | 0.945 | 0 | 4.2 | 3.255 | 3.255 | opened
232 | SS Gorodnya 35/10 | 4+6,3 | 2.59 | 0 |  | 2.59 | 0 | 4.2 | 1.61 | 1.61 | opened | 232 | SS Gorodnya 35/10 | 4+6,3 | 0.17932 | 2.7693 | 0 |  | 2.7693 | 0 | 4.2 | 1.4307 | 1.4307 | opened
233 | SS Ryazanovo 35/10 | 4+4 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 | opened | 233 | SS Ryazanovo 35/10 | 4+4 | 0 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 | opened
234 | SS Savvatyevo 35/10 | 1,6+2,5 | 0.55 | 0 |  | 0.55 | 0 | 1.68 | 1.13 | 1.13 | opened | 234 | SS Savvatyevo 35/10 | 1,6+2,5 | 0.0715 | 0.6215 | 0 |  | 0.6215 | 0 | 1.68 | 1.0585 | 1.0585 | opened
235 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0.5 | 0 |  | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 235 | SS Bele-Kushal 35/10 | 1,6+2,5 | 0.0425 | 0.5425 | 0 |  | 0.5425 | 0 | 1.68 | 1.1375 | 1.1375 | opened
236 | SS Glass plant 35/10 | 2,5+2,5 | 0.28 | 0 |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened | 236 | SS Glass plant 35/10 | 2,5+2,5 | 0 | 0.28 | 0 |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened
237 | SS Grishkino 35/10 | 4+4 | 2.92 | 0 |  | 2.92 | 0 | 4.2 | 1.28 | 1.28 | opened | 237 | SS Grishkino 35/10 | 10+6,3 (according to TS) | 5.4356 | 8.3556 | 0 |  | 8.3556 | 0 | 6.6 | -1.7556 | -1.7556 | MS is closed
238 | SS No.2 35/3 | 1+1 | 0.32 | 0 |  | 0.32 | 0 | 1.05 | 0.73 | 0.73 | opened | 238 | SS No.2 35/3 | 1+1 | 0 | 0.32 | 0 |  | 0.32 | 0 | 1.05 | 0.73 | 0.73 | opened
239 | SS No.15 35/10 | 4+4 | 2.08 | 0 |  | 2.08 | 0 | 4.2 | 2.12 | 2.12 | opened | 239 | SS No.15 35/10 | 4+4 | 0.037 | 2.117 | 0 |  | 2.117 | 0 | 4.2 | 2.083 | 2.083 | opened
240 | SS Mednoe 35/10 | 6,3+4 | 2.83 | 0 |  | 2.83 | 0 | 4.2 | 1.37 | 1.37 | opened | 240 | SS Mednoe 35/10 | 6,3+4 | 0.45 | 3.28 | 0 |  | 3.28 | 0 | 4.2 | 0.92 | 0.92 | opened
241 | SS Tolmachi 35/10 | 2,5+1,8 | 1.08 | 0 |  | 1.08 | 0 | 1.89 | 0.81 | 0.81 | opened | 241 | SS Tolmachi 35/10 | 2,5+1,8 | 0.0395 | 1.1195 | 0 |  | 1.1195 | 0 | 1.89 | 0.7705 | 0.7705 | opened
242 | SS No. 7 35/10 | 1,8+2,5 | 0.47 | 0 |  | 0.47 | 0 | 1.89 | 1.42 | 1.42 | opened | 242 | SS No. 7 35/10 | 1,8+2,5 | 0.0375 | 0.5075 | 0 |  | 0.5075 | 0 | 1.89 | 1.3825 | 1.3825 | opened
243 | SS No. 5 35/6 | 5,6+4 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 | opened | 243 | SS No. 5 35/6 | 5,6+4 | 0 | 1.8 | 0 |  | 1.8 | 0 | 4.2 | 2.4 | 2.4 | opened
244 | SS No. 9 35/6 | 5,6+7,5 | 4.5 | 0 |  | 4.5 | 0 | 5.88 | 1.38 | 1.38 | opened | 244 | SS No. 9 35/6 | 5,6+7,5 | 0.1805 | 4.6805 | 0 |  | 4.6805 | 0 | 5.88 | 1.1995 | 1.1995 | opened
245 | SS No. 9 35/10 | 4+6,3 | 2.43 | 0 |  | 2.43 | 0 | 4.2 | 1.77 | 1.77 | opened | 245 | SS No. 9 35/10 | 4+6,3 | 0 | 2.43 | 0 |  | 2.43 | 0 | 4.2 | 1.77 | 1.77 | opened
246 | SS No. 10 35/6 | 1,8+1,8 | 1.42 | 0 |  | 1.42 | 0 | 1.89 | 0.47 | 0.47 | opened | 246 | SS No. 10 35/6 | 1,8+1,8 | 0.225 | 1.645 | 0 |  | 1.645 | 0 | 1.89 | 0.245 | 0.245 | opened
247 | SS No. 11 35/10 kv | 10+6,3 | 4.517 | 0 |  | 4.517 | 0 | 6.62 | 2.103 | 2.103 | opened | 247 | SS No. 11 35/10 kv | 10+6,3 | 0.14375 | 4.6608 | 0 |  | 4.6608 | 0 | 6.62 | 1.9592 | 1.9592 | opened
248 | SS Dm.Gora 35/10 | 2,5+4 | 4.7 | 0 |  | 4.7 | 0 | 2.63 | -2.07 | -2.07 | MS is closed | 248 | SS Dm.Gora 35/10 | 6,3 (according to IP) +6,3 (according to TS) | 0.099 | 4.799 | 0 |  | 4.799 | 0 | 6.6 | 1.801 | 1.801 | opened
249 | SS ZMI 35/6 | 10+16 | 2.6 | 0 |  | 2.6 | 0 | 10.5 | 7.9 | 7.9 | opened | 249 | SS ZMI 35/6 | 10+16 | 0.4475 | 3.0475 | 0 |  | 3.0475 | 0 | 10.5 | 7.4525 | 7.4525 | opened
250 | SS Izoplit 35/10 | 6,3+6,3 | 0.67 | 0 |  | 0.67 | 0 | 6.62 | 5.95 | 5.95 | opened | 250 | SS Izoplit 35/10 | 6,3+6,3 | 0 | 0.67 | 0 |  | 0.67 | 0 | 6.62 | 5.95 | 5.95 | opened
251 | SS Karacharovo 35/10 | 4+6,3 | 1.4 | 0 |  | 1.4 | 0 | 4.2 | 2.8 | 2.8 | opened | 251 | SS Karacharovo 35/10 | 4+6,3 | 0.14 | 1.54 | 0 |  | 1.54 | 0 | 4.2 | 2.66 | 2.66 | opened
252 | SS Kr. Luch 35/6 | 2,5+3,2 | 2.25 | 0 |  | 2.25 | 0 | 2.63 | 0.38 | 0.38 | opened | 252 | SS Kr. Luch 35/6 | 2,5+3,2 | 0.1095 | 2.3595 | 0 |  | 2.3595 | 0 | 2.63 | 0.2705 | 0.2705 | opened
253 | SS Melkovo 35/6 | 1,6+2,5 | 0.98 | 0 |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened | 253 | SS Melkovo 35/6 | 1,6+2,5 | 0.0125 | 0.9925 | 0 |  | 0.9925 | 0 | 1.68 | 0.6875 | 0.6875 | opened
254 | SS Selikhovo 35/6 | 2,5+2,5 | 0.93 | 0 |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | opened | 254 | SS Selikhovo 35/6 | 2,5+2,5 | 0.025 | 0.955 | 0 |  | 0.955 | 0 | 2.63 | 1.675 | 1.675 | opened
255 | SS Mokshino 35/10 | 6,3+6,3 | 2.73 | 0 |  | 2.73 | 0 | 6.62 | 3.89 | 3.89 | opened | 255 | SS Mokshino 35/10 | 6,3+6,3 | 0.0567 | 2.7867 | 0 |  | 2.7867 | 0 | 6.62 | 3.8333 | 3.8333 | opened
256 | SS Energetik 35/10 | 4+2,5 | 1.25 | 0 |  | 1.25 | 0 | 2.63 | 1.38 | 1.38 | opened | 256 | SS Energetik 35/10 | 4+2,5 | 0.032 | 1.282 | 0 |  | 1.282 | 0 | 2.63 | 1.348 | 1.348 | opened
257 | SS Emmaus 35/10 | 2,5+4 | 2.17 | 0 |  | 2.17 | 0 | 2.63 | 0.46 | 0.46 | opened | 257 | SS Emmaus 35/10 | 2,5+4 | 0.218 | 2.388 | 0 |  | 2.388 | 0 | 2.63 | 0.242 | 0.242 | opened
258 | SS Yu.-Devichye 35/10 | 4+4 | 2.19 | 1.095 | 120 | 1.095 | 0 | 4.2 | 3.105 | 3.105 | opened | 258 | SS Yu.-Devichye 35/10 | 4+4 | 0.094 | 2.284 | 1.142 | 120 | 1.142 | 0 | 4.2 | 3.058 | 3.058 | opened
259 | SS No.18 35/6 | 10+10+10 | 19.49 | 0 |  | 19.49 | 0 | 21 | 1.51 | 1.51 | opened | 259 | SS No.18 35/6 | 10+10+10 | 0.06875 | 19.5587 | 0 |  | 19.5587 | 0 | 21 | 1.4412 | 1.4412 | opened
260 | SS Zatveretskaya 35/6 | 10+10+10 | 12.95 | 0 |  | 12.95 | 0 | 21 | 8.05 | 8.05 | opened | 260 | SS Zatveretskaya 35/6 | 10+10+10 | 0.85 | 13.8 | 0 |  | 13.8 | 0 | 21 | 7.2 | 7.2 | opened
261 | SS Pushkino 110/35/10 | 10 | 4.82 | 4.82 | 24 hours | 4.82 | 0 | 4.82 | 0 | 0 | opened | 261 | SS Pushkino 110/35/10 | 10 | 0.7171 | 5.5371 | 4.82 | 24 hours | 4.82 | 0 | 4.82 | -0.7171 | -0.7171 | MS is closed
| Nom. capacity MV, MVA | 8.83 | 4.65 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0 |  |  |  | Nom. capacity MV, MVA | 8.83 | 0.7171 | 5.3671 | 4.65 | 24 hours | 4.65 | 0 | 4.65 | 0
| Nom. capacity LV, MVA | 8.75 | 0.17 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | 0 |  |  |  | Nom. capacity LV, MVA | 8.75 | 0 | 0.17 | 0.17 | 24 hours | 0.17 | 0 | 0.17 | 0
262 | SS Mechanical plant 110/10/6 | 40+40 | 21.2262 | 0 |  | 21.2262 | 0 | 42 | 20.7738 | 9.6555 | opened | 262 | SS Mechanical plant 110/10/6 | 40+40 | 0.317 | 21.5432 | 0 |  | 21.5432 | 0 | 42 | 20.4568 | 9.3765 | opened
| Nom. capacity MV, MVA | 20+20 | 9.8818 | 0 |  | 9.8818 | 0 | 21 | 11.1182 |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.038 | 9.9198 | 0 |  | 9.9198 | 0 | 21 | 11.0802
| Nom. capacity LV, MVA | 20+20 | 11.3445 | 0 |  | 11.3445 | 0 | 21 | 9.6555 |  |  |  | Nom. capacity LV, MVA | 20+20 | 0.279 | 11.6235 | 0 |  | 11.6235 | 0 | 21 | 9.3765
263 | SS Yuzhnaya 110/35/10 | 40+40 | 45.69 | 15.9 | 120 | 29.79 | 0 | 42 | 12.21 | 12.21 | opened | 263 | SS Yuzhnaya 110/35/10 | 40+40 | 1.9115 | 47.6015 | 15.9 | 120 | 31.7015 | 0 | 42 | 10.2985 | 10.2985 | opened
| Nom. capacity MV, MVA | 40+40 | 27.39 | 13.9 | 120 | 13.49 | 0 | 42 | 28.51 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.974 | 28.364 | 13.9 | 120 | 14.464 | 0 | 42 | 27.536
| Nom. capacity LV, MVA | 40+40 | 18.3 | 2 | 120 | 16.3 | 0 | 42 | 25.7 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.9375 | 19.2375 | 2 | 120 | 17.2375 | 0 | 42 | 24.7625
264 | SS Severnaya 110/35/10 | 40+40 | 44.6817 | 18.165 | 120 | 26.5167 | 0 | 42 | 15.4833 | 15.4833 | opened | 264 | SS Severnaya 110/35/10 | 40+40 | 8.7583 | 53.44 | 18.165 | 120 | 35.275 | 0 | 42 | 6.725 | 6.725 | opened
| Nom. capacity MV, MVA | 40+40 | 18.165 | 18.165 | 120 | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.3295 | 18.4945 | 18.165 | 120 | 0.3295 | 0 | 42 | 41.6705
| Nom. capacity LV, MVA | 40+40 | 26.5167 | 0 |  | 26.5167 | 0 | 42 | 15.4833 |  |  |  | Nom. capacity LV, MVA | 40+40 | 8.4288 | 34.9455 | 0 |  | 34.9455 | 0 | 42 | 7.0545
265 | SS Lazurnaya 110/35/10 | 40+40 | 19.7 | 6.47 | 120 | 13.23 | 0 | 42 | 28.77 | 28.77 | opened | 265 | SS Lazurnaya 110/35/10 | 40+40 | 14.8274 | 34.5274 | 6.47 | 120 | 28.0574 | 0 | 42 | 13.9426 | 13.9426 | opened
| Nom. capacity MV, MVA | 40+40 | 15.46 | 6.47 | 120 | 8.99 | 0 | 42 | 33.01 |  |  |  | Nom. capacity MV, MVA | 40+40 | 6.6436 | 22.1036 | 6.47 | 120 | 15.6336 | 0 | 42 | 26.3664
| Nom. capacity LV, MVA | 40+40 | 4.24 | 0 |  | 4.24 | 0 | 42 | 37.76 |  |  |  | Nom. capacity LV, MVA | 40+40 | 8.1838 | 12.4238 | 0 |  | 12.4238 | 0 | 42 | 29.5762
266 | SS Earthmoving machine plant 110/10/6 | 40+40 | 13.6916 | 0 |  | 13.6916 | 0 | 42 | 28.3084 | 9.5246 | opened | 266 | SS Earthmoving machine plant 110/10/6 | 40+40 | 3.0579 | 16.7495 | 0 |  | 16.7495 | 0 | 42 | 25.2505 | 8.9777 | opened
| Nom. capacity MV, MVA | 20+20 | 11.4754 | 0 |  | 11.4754 | 0 | 21 | 9.5246 |  |  |  | Nom. capacity MV, MVA | 20+20 | 0.5469 | 12.0223 | 0 |  | 12.0223 | 0 | 21 | 8.9777
| Nom. capacity LV, MVA | 20+20 | 2.2161 | 0 |  | 2.2161 | 0 | 21 | 18.7839 |  |  |  | Nom. capacity LV, MVA | 20+20 | 2.511 | 4.7271 | 0 |  | 4.7271 | 0 | 21 | 16.2729
267 | SS Mednovsky v-or 110/35/10 | 10+10 | 4.4271 | 4.43 | 120 | -0.00293 | 0 | 10.5 | 10.5029 | 10.498 | opened | 267 | SS Mednovsky v-or 110/35/10 | 10+10 | 0.74432 | 5.1714 | 4.43 | 120 | 0.74139 | 0 | 10.5 | 9.7586 | 9.7586 | opened
| Nom. capacity MV, MVA | 10+10 | 2.505 | 2.51 | 120 | -0.00496 | 0 | 10.5 | 10.505 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.70432 | 3.2094 | 2.51 | 120 | 0.69936 | 0 | 10.5 | 9.8006
| Nom. capacity LV, MVA | 10+10 | 1.922 | 1.92 | 120 | 0.00203 | 0 | 10.5 | 10.498 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.04 | 1.962 | 1.92 | 120 | 0.04203 | 0 | 10.5 | 10.458
268 | SS Likhoslavl 110/35/10 | 25+25 | 15.06 | 6.3 | 120 | 8.76 | 0 | 26.25 | 17.49 | 17.49 | opened | 268 | SS Likhoslavl 110/35/10 | 25+25 | 0.1967 | 15.2567 | 6.3 | 120 | 8.9567 | 0 | 26.25 | 17.2933 | 17.2933 | opened
| Nom. capacity MV, MVA | 25+25 | 6.3 | 6.3 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, MVA | 25+25 | 0.0375 | 6.3375 | 6.3 | 120 | 0.0375 | 0 | 26.25 | 26.2125
| Nom. capacity LV, MVA | 25+25 | 8.76 | 0 |  | 8.76 | 0 | 26.25 | 17.49 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.1592 | 8.9192 | 0 |  | 8.9192 | 0 | 26.25 | 17.3308
269 | SS Bezborodovo 110/35/6 | 16+16 | 13.63 | 4.25 | 120 | 9.38 | 0 | 16.8 | 7.42 | 7.42 | opened | 269 | SS Bezborodovo 110/35/6 | 16+16 | 0.71295 | 14.343 | 4.25 | 120 | 10.093 | 0 | 16.8 | 6.707 | 6.707 | opened
| Nom. capacity MV, MVA | 16+16 | 13.63 | 4.25 | 120 | 9.38 | 0 | 16.8 | 7.42 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.21295 | 13.843 | 4.25 | 120 | 9.593 | 0 | 16.8 | 7.207
| Nom. capacity LV, MVA | 16+16 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.5 | 0.5 | 0 |  | 0.5 | 0 | 16.8 | 16.3
270 | SS Redkino 110/35/6 | 40+40,5 | 25.27 | 8.53 | 120 | 16.74 | 0 | 42 | 25.26 | 25.26 | opened | 270 | SS Redkino 110/35/6 | 40+40,5 | 4.589 | 29.859 | 8.53 | 120 | 21.329 | 0 | 42 | 20.671 | 20.671 | opened
| Nom. capacity MV, MVA | 40+40 | 19 | 8.53 | 120 | 10.47 | 0 | 42 | 31.53 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.839 | 19.839 | 8.53 | 120 | 11.309 | 0 | 42 | 30.691
| Nom. capacity LV, MVA | 40+40 | 6.27 | 0 |  | 6.27 | 0 | 42 | 35.73 |  |  |  | Nom. capacity LV, MVA | 40+40 | 3.75 | 10.02 | 0 |  | 10.02 | 0 | 42 | 31.98
271 | SS Rameshki 110/35/10 | 25+10 | 5.32 | 3.59 | 120 | 1.73 | 0 | 10.5 | 8.77 | 8.77 | opened | 271 | SS Rameshki 110/35/10 | 25+10 | 0.1315 | 5.4515 | 3.59 | 120 | 1.8615 | 0 | 10.5 | 8.6385 | 8.6385 | opened
| Nom. capacity MV, MVA | 25+10 | 2.59 | 2.59 | 120 | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 25+10 | 0.0395 | 2.6295 | 2.59 | 120 | 0.0395 | 0 | 10.5 | 10.4605
| Nom. capacity MV, MVA | 25+10 | 2.73 | 1 | 120 | 1.73 | 0 | 10.5 | 8.77 |  |  |  | Nom. capacity MV, MVA | 25+10 | 0.092 | 2.822 | 1 | 120 | 1.822 | 0 | 10.5 | 8.678
272 | SS Tuchevo 110/35/10 | 25+25 | 0.33 | 0.29 | 120 | 0.04 | 0 | 26.25 | 26.21 | 22.94 | opened | 272 | SS Tuchevo 110/35/10 | 25+25 | 0 | 0.33 | 0.29 | 120 | 0.04 | 0 | 26.25 | 26.21 | 22.94 | opened
| Nom. capacity MV, MVA | 22,06+22,06 | 0.29 | 0.29 | 120 | 0 | 0 | 23.17 | 23.17 |  |  |  | Nom. capacity MV, MVA | 22,06+22,06 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 23.17 | 23.17
| Nom. capacity MV, MVA | 21,89+21,89 | 0.04 | 0 |  | 0.04 | 0 | 22.98 | 22.94 |  |  |  | Nom. capacity MV, MVA | 21,89+21,89 | 0 | 0.04 | 0 |  | 0.04 | 0 | 22.98 | 22.94
273 | SS Strashevichi 35/10 kv | 4 | 0.74 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0 | 0 | opened | 273 | SS Strashevichi 35/10 kv | 4 | 0 | 0.74 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0 | 0 | opened
274 | SS Sukromlya 35/10 kv | 2.5 | 0.31 | 0.31 | 24 hours | 0.31 | 0 | 0.31 | 0 | 0 | opened | 274 | SS Sukromlya 35/10 kv | 2.5 | 0 | 0.31 | 0.31 | 24 hours | 0.31 | 0 | 0.31 | 0 | 0 | opened
275 | SS Kr. Gorodok 35/10 kv | 0.56 | 0.02 | 0 |  | 0 | 0 | 0 | -0.02 | -0.02 | MS is closed | 275 | SS Kr. Gorodok 35/10 kv | 0.56 | 0 | 0.02 | 0 |  | 0 | 0 | 0 | -0.02 | -0.02 | MS is closed
276 | SS Pryamukhino 35/10 kv | 2.5 | 0.52 | 0.52 | 24 hours | 0.52 | 0 | 0.52 | 0 | 0 | opened | 276 | SS Pryamukhino 35/10 kv | 2.5 | 0 | 0.52 | 0.52 | 24 hours | 0.52 | 0 | 0.52 | 0 | 0 | opened
277 | SS Pen 35/10 kv | 1.6 | 0.16 | 0 |  | 0 | 0 | 0 | -0.16 | -0.16 | MS is closed | 277 | SS Pen 35/10 kv | 1.6 | 0 | 0.16 | 0 |  | 0 | 0 | 0 | -0.16 | -0.16 | MS is closed
278 | SS Pechnikovo 35/10 kv | 2.5 | 0.09 | 0.09 | 24 hours | 0.09 | 0 | 0.09 | 0 | 0 | opened | 278 | SS Pechnikovo 35/10 kv | 2.5 | 0 | 0.09 | 0.09 | 24 hours | 0.09 | 0 | 0.09 | 0 | 0 | opened
279 | SS Maksimkovo 35/10 kv | 4 | 0.58 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0 | 0 | opened | 279 | SS Maksimkovo 35/10 kv | 4 | 0.035 | 0.615 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | -0.035 | -0.035 | MS is closed
280 | SS Filistovo 35/10 kv | 1.6 | 0.16 | 0.16 | 24 hours | 0.16 | 0 | 0.16 | 0 | 0 | opened | 280 | SS Filistovo 35/10 kv | 1.6 | 0 | 0.16 | 0.16 | 24 hours | 0.16 | 0 | 0.16 | 0 | 0 | opened
281 | SS Okovtsy 35/10 kv | 1 | 0.59 | 0.59 | 24 hours | 0.59 | 0 | 0.59 | 0 | 0 | opened | 281 | SS Okovtsy 35/10 kv | 1 | 0.025 | 0.615 | 0.59 | 24 hours | 0.59 | 0 | 0.59 | -0.025 | -0.025 | MS is closed
282 | SS Seliger 35/10 kv | 4 | 3.33 | 0 |  | 0 | 0 | 0 | -3.33 | -3.33 | MS is closed | 282 | SS Seliger 35/10 kv | 4 | 1.69 | 5.02 | 0 |  | 0 | 0 | 0 | -5.02 | -5.02 | MS is closed
283 | SS Moshary 35/10 kv | 1.6 | 0.26 | 0 |  | 0 | 0 | 0 | -0.26 | -0.26 | MS is closed | 283 | SS Moshary 35/10 kv | 1.6 | 0 | 0.26 | 0 |  | 0 | 0 | 0 | -0.26 | -0.26 | MS is closed
284 | SS Voroshilovo 35/10 kv | 1 | 0.39 | 0 |  | 0 | 0 | 0 | -0.39 | -0.39 | MS is closed | 284 | SS Voroshilovo 35/10 kv | 1 | 0 | 0.39 | 0 |  | 0 | 0 | 0 | -0.39 | -0.39 | MS is closed
285 | SS Salutino 35/10 kv | 1.6 | 0.47 | 0 |  | 0 | 0 | 0 | -0.47 | -0.47 | MS is closed | 285 | SS Salutino 35/10 kv | 1.6 | 0.0685 | 0.5385 | 0 |  | 0 | 0 | 0 | -0.5385 | -0.5385 | MS is closed
286 | SS Moshki 35/10 kv | 2,5+2,5 | 2.77 | 0 |  | 2.77 | 0 | 2.63 | -0.14 | -0.14 | MS is closed | 286 | SS Moshki 35/10 kv | 2,5+2,5 | 0.0805 | 2.8505 | 0 |  | 2.8505 | 0 | 2.63 | -0.2205 | -0.2205 | MS is closed
287 | SS Eltsy 35/10 kv | 4+2,5 | 0.81 | 0 |  | 0.81 | 0 | 2.63 | 1.82 | 1.82 | opened | 287 | SS Eltsy 35/10 kv | 4+2,5 | 0.02 | 0.83 | 0 |  | 0.83 | 0 | 2.63 | 1.8 | 1.8 | opened
288 | SS Selishche 35/10 kv | 4+4 | 2.82 | 0 |  | 2.82 | 0 | 4.2 | 1.38 | 1.38 | opened | 288 | SS Selishche 35/10 kv | 4+4 | 0.1885 | 3.0085 | 0 |  | 3.0085 | 0 | 4.2 | 1.1915 | 1.1915 | opened
289 | SS Svyatoe 35/10 kv | 2,5+2,5 | 0.91 | 0 |  | 0.91 | 0 | 2.63 | 1.72 | 1.72 | opened | 289 | SS Svyatoe 35/10 kv | 2,5+2,5 | 0 | 0.91 | 0 |  | 0.91 | 0 | 2.63 | 1.72 | 1.72 | opened
290 | SS Budovo 35/10 kv | 2,5+2,5 | 1.77 | 0 |  | 1.77 | 0 | 2.63 | 0.86 | 0.86 | opened | 290 | SS Budovo 35/10 kv | 2,5+2,5 | 0.059 | 1.829 | 0 |  | 1.829 | 0 | 2.63 | 0.801 | 0.801 | opened
291 | SS Eltsy 35/10 kv | 4+4 | 0.84 | 0 |  | 0.84 | 0 | 4.2 | 3.36 | 3.36 | opened | 291 | SS Eltsy 35/10 kv | 4+4 | 0.015 | 0.855 | 0 |  | 0.855 | 0 | 4.2 | 3.345 | 3.345 | opened
292 | SS Selishche 35/10 kv | 6,3+4 | 1.37 | 0 |  | 1.37 | 0 | 4.2 | 2.83 | 2.83 | opened | 292 | SS Selishche 35/10 kv | 6,3+4 | 1.5665 | 2.9365 | 0 |  | 2.9365 | 0 | 4.2 | 1.2635 | 1.2635 | opened
293 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.59 | 0 |  | 0.59 | 0 | 1.68 | 1.09 | 1.09 | opened | 293 | SS Svyatoe 35/10 kv | 2,5+1,6 | 0.044 | 0.634 | 0 |  | 0.634 | 0 | 1.68 | 1.046 | 1.046 | opened
294 | SS Krapivnaya 35/10 kv | 2,5+2,5 | 0.49 | 0 |  | 0.49 | 0 | 2.63 | 2.14 | 2.14 | opened | 294 | SS Krapivnaya 35/10 kv | 2,5+2,5 | 0 | 0.49 | 0 |  | 0.49 | 0 | 2.63 | 2.14 | 2.14 | opened
295 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 1.66 | 0 |  | 1.66 | 0 | 2.63 | 0.97 | 0.97 | opened | 295 | SS Svetlitsa 35/10 kv | 2,5+2,5 | 0.3605 | 2.0205 | 0 |  | 2.0205 | 0 | 2.63 | 0.6095 | 0.6095 | opened
296 | SS KS-20 110/6 kv | 63+63 | 16.36 | 0 |  | 16.36 | 0 | 66.15 | 49.79 | 49.79 | opened | 296 | SS KS-20 110/6 kv | 63+63 | 0 | 16.36 | 0 |  | 16.36 | 0 | 66.15 | 49.79 | 49.79 | opened
297 | SS Poligrafkraski 110/10 kv | 10+10 | 6.08 | 0 |  | 6.08 | 0 | 10.5 | 4.42 | 4.42 | opened | 297 | SS Poligrafkraski 110/10 kv | 10+10 | 0.023 | 6.103 | 0 |  | 6.103 | 0 | 10.5 | 4.397 | 4.397 | opened
298 | SS NPS Torzhok 110/10 kv | 25+25 | 0.01 | 0 |  | 0.01 | 0 | 26.25 | 26.24 | 26.24 | opened | 298 | SS NPS Torzhok 110/10 kv | 25+25 | 0 | 0.01 | 0 |  | 0.01 | 0 | 26.25 | 26.24 | 26.24 | opened
299 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0.5 | 0 |  | 0.5 | 0 | 2.63 | 2.13 | 2.13 | opened | 299 | SS Selikhovo 110/10 kv | 2,5+2,5 | 0 | 0.5 | 0 |  | 0.5 | 0 | 2.63 | 2.13 | 2.13 | opened
300 | SS Peno 110/10 kv | 6,3+6,3 | 4.05 | 0 |  | 4.05 | 0 | 6.62 | 2.57 | 2.57 | opened | 300 | SS Peno 110/10 kv | 6,3+6,3 | 0.1953 | 4.2453 | 0 |  | 4.2453 | 0 | 6.62 | 2.3747 | 2.3747 | opened
301 | SS Torzhok 110/35/10 kv | 25+40 | 23.54 | 7.38 | 120 | 16.16 | 0 | 26.25 | 10.09 | 10.09 | opened | 301 | SS Torzhok 110/35/10 kv | 40 (according to TS)+40 | 6.1965 | 29.7365 | 7.38 | 120 | 22.3565 | 0 | 42 | 19.6435 | 19.6435 | opened
| Nom. Capacity MV, MVA | 25+40 | 7.38 | 7.38 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, MVA | 40 (according to TS)+40 | 0.348 | 7.728 | 7.38 | 120 | 0.348 | 0 | 42 | 41.652
| Nom. Capacity LV, MVA | 25+40 | 16.16 | 0 |  | 16.16 | 0 | 26.25 | 10.09 |  |  |  | Nom. Capacity LV, MVA | 40 (according to TS)+40 | 5.8485 | 22.0085 | 0 |  | 22.0085 | 0 | 42 | 19.9915
302 | SS Stroyindustriya 110/35/10 kv | 25+25 | 5.45 | 0.32 | 120 | 5.13 | 0 | 26.25 | 21.12 | 21.12 | opened | 302 | SS Stroyindustriya 110/35/10 kv | 25+25 | 0.033 | 5.483 | 0.32 | 120 | 5.163 | 0 | 26.25 | 21.087 | 21.087 | opened
| Nom. Capacity MV, MVA | 25+25 | 0.32 | 0.32 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 0.32 | 0.32 | 120 | 0 | 0 | 26.25 | 26.25
| Nom. Capacity LV, MVA | 25+25 | 5.13 | 0 |  | 5.13 | 0 | 26.25 | 21.12 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.033 | 5.163 | 0 |  | 5.163 | 0 | 26.25 | 21.087
303 | SS Kuvshinovo 110/35/10 kv | 25+25 | 18.92 | 1.8 | 120 | 17.12 | 0 | 26.25 | 9.13 | 9.13 | opened | 303 | SS Kuvshinovo 110/35/10 kv | 25+25 | 0.06 | 18.98 | 1.8 | 120 | 17.18 | 0 | 26.25 | 9.07 | 9.07 | opened
| Nom. Capacity MV, MVA | 25+25 | 1.8 | 1.8 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 1.8 | 1.8 | 120 | 0 | 0 | 26.25 | 26.25
| Nom. Capacity LV, MVA | 25+25 | 17.12 | 0 |  | 17.12 | 0 | 26.25 | 9.13 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.06 | 17.18 | 0 |  | 17.18 | 0 | 26.25 | 9.07
304 | SS Selizharovo 110/35/10 kv | 16+10 | 8.79 | 0 |  | 8.79 | 0 | 10.5 | 1.71 | 1.71 | opened | 304 | SS Selizharovo 110/35/10 kv | 16+10 | 2.2761 | 11.0661 | 0 |  | 11.0661 | 0 | 10.5 | -0.5661 | -0.5661 | MS is closed
| Nom. Capacity MV, MVA | 16+10 | 2.13 | 0 |  | 2.13 | 0 | 10.5 | 8.37 |  |  |  | Nom. Capacity MV, MVA | 16+10 | 0 | 2.13 | 0 |  | 2.13 | 0 | 10.5 | 8.37
| Nom. Capacity LV, MVA | 16+10 | 6.66 | 0 |  | 6.66 | 0 | 10.5 | 3.84 |  |  |  | Nom. Capacity LV, MVA | 16+10 | 2.2761 | 8.9361 | 0 |  | 8.9361 | 0 | 10.5 | 1.5639
305 | SS NPS Borisovo 110/35/10 kv | 25+25 | 1.95 | 1.59 | 120 | 0.36 | 0 | 26.25 | 25.89 | 25.89 | opened | 305 | SS NPS Borisovo 110/35/10 kv | 25+25 | 0.04 | 1.99 | 1.59 | 120 | 0.4 | 0 | 26.25 | 25.85 | 25.85 | opened
| Nom. Capacity MV, MVA | 25+25 | 1.59 | 1.59 | 120 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0.04 | 1.63 | 1.59 | 120 | 0.04 | 0 | 26.25 | 26.21
| Nom. Capacity LV, MVA | 25+25 | 0.36 | 0 |  | 0.36 | 0 | 26.25 | 25.89 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0 | 0.36 | 0 |  | 0.36 | 0 | 26.25 | 25.89
306 | SS Ostashkov 110/35/10 kv | 25+25 | 16.88 | 0 |  | 16.88 | 0 | 26.25 | 9.37 | 9.37 | opened | 306 | SS Ostashkov 110/35/10 kv | 25+25 | 0.8418 | 17.7218 | 0 |  | 17.7218 | 0 | 26.25 | 8.5282 | 8.5282 | opened
| Nom. Capacity MV, MVA | 25+25 | 1.79 | 0 |  | 1.79 | 0 | 26.25 | 24.46 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0.3605 | 2.1505 | 0 |  | 2.1505 | 0 | 26.25 | 24.0995
| Nom. Capacity LV, MVA | 25+25 | 15.09 | 0 |  | 15.09 | 0 | 26.25 | 11.16 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.4813 | 15.5713 | 0 |  | 15.5713 | 0 | 26.25 | 10.6787
307 | SS N. Rozhok 110/35/10 kv | 10+10 | 15.57 | 0 |  | 15.57 | 0 | 10.5 | -5.07 | -5.07 | MS is closed | 307 | SS N. Rozhok 110/35/10 kv | 10+10 | 1.85 | 17.42 | 0 |  | 17.42 | 0 | 10.5 | -6.92 | -6.92 | MS is closed
| Nom. Capacity MV, MVA | 10+10 | 2.4 | 0 |  | 2.4 | 0 | 10.5 | 8.1 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 1.69 | 4.09 | 0 |  | 4.09 | 0 | 10.5 | 6.41
| Nom. Capacity LV, MVA | 10+10 | 13.17 | 0 |  | 13.17 | 0 | 10.5 | -2.67 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.16 | 13.33 | 0 |  | 13.33 | 0 | 10.5 | -2.83
Total: |  | 3931.32 | 1052.0948 | [8 empty] | 1: Total:; 3: 4028.82; 4: 133.9543; 5: 1185.9263
deficit | [9 empty] | -44.8136 |  | 1: deficit; Мin. 12: -66.051
proficit | [9 empty] | 982.4526 |  | 1: proficit; Мin. 12: 955.09
профицит | [10 empty] | 955.0903
Note on E149: Перевод нагрузки по 6 кВ на ПС Кимры
Note on E182: перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on E185: Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on E191: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on E194: Перевод нагрузки Т-1 ПС Стоянцы
Note on E197: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская
Note on S149: Перевод нагрузки по 6 кВ на ПС Кимры
Note on S182: перевод питания Т-2 35 кВ с ПС В.Троица на ПС Роща( ПС Уницы Т-1 + Савцино Т-1 Т-2) + перевод питания Т-1 35 кВ с ПС В.Троица на ПС Ильинское
Note on S185: Перевод нагрузки Т-1 ПС Стоянцы с ПС Горицы на ПС 35 кВ Ильиское
Note on S191: Перевод нагрузки Т-1 ПС К.Демьяновская на ПС Роща по ВЛ 35 кВ Роща-К.Демьяновская
Note on S194: Перевод нагрузки Т-1 ПС Стоянцы
Note on S197: Перевод нагрузки Т-2 ПС К.Демьяновская на ПС Простор по ВЛ 35 кВ Простор-К.Демьяновская

## смоленск
[9 empty] | table 1 | [13 empty] | table2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the mode n-1, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.18 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.52 | 0.52 | opened | 1 | Gerchiki 35/10 | 2.5 | 0.5 | 0.68 | 0.7 | 24 hours | -0.02 | 0 | 0.7 | 0.02 | 0.02 | opened
2 | Verkhovye 35/10 | 4 | 0.6 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.76 | 0.76 | opened | 2 | Verkhovye 35/10 | 4 | 0 | 0.6 | 1.36 | 24 hours | -0.76 | 0 | 1.36 | 0.76 | 0.76 | opened
3 | Neykovo 35/10 | 2.5 | 0.22 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.51 | 1.51 | opened | 3 | Neykovo 35/10 | 2.5 | 0 | 0.22 | 1.73 | 24 hours | -1.51 | 0 | 1.73 | 1.51 | 1.51 | opened
4 | Merlino 110/35/10 | 6.3 | 0.38 | 0.25 | 24 hours | 0.25 | 0 | 0.25 | -0.13 | -0.15 | closed | 4 | Merlino 110/35/10 | 6.3 | 0.47 | 0.85 | 0.54 | 24 hours | 0.31 | 0 | 0.54 | -0.31 | -0.31 | closed
| Nom. capacity MV, МVА | 6.3 | 0.15 | 0.15 |  | 0.15 | 0 | 0.15 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0.44 | 0.44 | 0.44 |  | 0 | 0 | 0.44 | 0
| Nom. capacity LV, МVА | 6.3 | 0.25 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | -0.15 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.03 | 0.28 | 0.1 | 24 hours | 0.18 | 0 | 0.1 | -0.18
5 | Belyaevo 35/10 | 1.6 | 0.21 | 2.11 | 24 hours | 2.11 | 0 | 2.11 | 1.9 | 1.9 | opened | 5 | Belyaevo 35/10 | 1.6 | 0 | 0.21 | 2.11 | 24 hours | -1.9 | 0 | 2.11 | 1.9 | 1.9 | opened
6 | Zaozerye 35/10 | 1.6 | 0.16 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.69 | 0.69 | opened | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.16 | 0.85 | 24 hours | -0.69 | 0 | 0.85 | 0.69 | 0.69 | opened
7 | Selezni 35/10 | 2.5 | 0.48 | 2.21 | 24 hours | 2.21 | 0 | 2.21 | 1.73 | 1.73 | opened | 7 | Selezni 35/10 | 2.5 | 0 | 0.48 | 2.21 | 24 hours | -1.73 | 0 | 2.21 | 1.73 | 1.73 | opened
8 | Logovo 110/10 | 6.3 | 0.4 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.96 | 0.96 | opened | 8 | Logovo 110/10 | 6.3 | 0 | 0.4 | 1.36 | 24 hours | -0.96 | 0 | 1.36 | 0.96 | 0.96 | opened
9 | Dubrovka 35/10 | 2.5 | 0.24 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 1.12 | 1.12 | opened | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.34 | 1.36 | 24 hours | -1.02 | 0 | 1.36 | 1.02 | 1.02 | opened
10 | Svistovichi 35/10 | 2.5 | 0.12 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.73 | 0.73 | opened | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.12 | 0.85 | 24 hours | -0.73 | 0 | 0.85 | 0.73 | 0.73 | opened
11 | Elsha 35/10 | 1.6 | 0.03 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.82 | 0.82 | opened | 11 | Elsha 35/10 | 1.6 | 0 | 0.03 | 0.85 | 24 hours | -0.82 | 0 | 0.85 | 0.82 | 0.82 | opened
12 | Sapsho 35/10 | 4 | 0.82 | 2.12 | 24 hours | 2.12 | 0 | 2.12 | 1.3 | 1.3 | opened | 12 | Sapsho 35/10 | 4 | 0 | 0.82 | 2.12 | 24 hours | -1.3 | 0 | 2.12 | 1.3 | 1.3 | opened
13 | Divo 110/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened | 13 | Divo 110/10 | 2.5 | 0 | 0.22 | 0.85 | 24 hours | -0.63 | 0 | 0.85 | 0.63 | 0.63 | opened
14 | Vachkovo 35/10 | 2.5 | 0.61 | 1.02 | 24 hours | 1.02 | 0 | 1.02 | 0.41 | 0.41 | opened | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.61 | 1.02 | 24 hours | -0.41 | 0 | 1.02 | 0.41 | 0.41 | opened
15 | Zamoshye 35/10 | 2.5 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
16 | Loino 35/10 | 2.5 | 0.12 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.73 | 0.73 | opened | 16 | Loino 35/10 | 2.5 | 0 | 0.12 | 0.85 | 24 hours | -0.73 | 0 | 0.85 | 0.73 | 0.73 | opened
17 | Rokot 35/10 | 2.5 | 0.25 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.05 | 1.05 | opened | 17 | Rokot 35/10 | 2.5 | 0 | 0.25 | 1.3 | 24 hours | -1.05 | 0 | 1.3 | 1.05 | 1.05 | opened
18 | Nikontsy 35/10 | 2.5 | 0.07 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.78 | 0.78 | opened | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.07 | 0.85 | 24 hours | -0.78 | 0 | 0.85 | 0.78 | 0.78 | opened
19 | Batishchevo 35/10 | 2.5 | 0.21 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.52 | 1.52 | opened | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.21 | 1.73 | 24 hours | -1.52 | 0 | 1.73 | 1.52 | 1.52 | opened
20 | Vasino 35/10 | 2.5 | 0.34 | 0 | 24 hours | 0 | 0 | 0 | -0.34 | -0.34 | closed | 20 | Vasino 35/10 | 2.5 | 0 | 0.34 | 0 | 24 hours | 0.34 | 0 | 0 | -0.34 | -0.34 | closed
21 | Bulgakovo 35/10 | 2.5 | 0.19 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.54 | 1.54 | opened | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.19 | 1.73 | 24 hours | -1.54 | 0 | 1.73 | 1.54 | 1.54 | opened
22 | Spas-Ugly 35/10 | 1.6 | 0.19 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.49 | 0.49 | opened | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.19 | 0.68 | 24 hours | -0.49 | 0 | 0.68 | 0.49 | 0.49 | opened
23 | Tretyakovo 35/10 | 4 | 0.34 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.21 | 2.21 | opened | 23 | Tretyakovo 35/10 | 4 | 0 | 0.34 | 2.55 | 24 hours | -2.21 | 0 | 2.55 | 2.21 | 2.21 | opened
24 | Velisto 35/10 | 2.5 | 0.06 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.24 | 1.24 | opened | 24 | Velisto 35/10 | 2.5 | 0 | 0.06 | 1.3 | 24 hours | -1.24 | 0 | 1.3 | 1.24 | 1.24 | opened
25 | Baturino 35/10 | 1.6 | 0.09 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.76 | 0.76 | opened | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.27 | 0.85 | 24 hours | -0.58 | 0 | 0.85 | 0.58 | 0.58 | opened
26 | Pechatniki 35/10 | 2.5 | 0.6 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.86 | 2.86 | opened | 26 | Pechatniki 35/10 | 2.5 | 2 | 2.6 | 3.46 | 24 hours | -0.86 | 0 | 3.46 | 0.86 | 0.86 | opened
27 | Garistovo 35/10 | 1.6 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened | 27 | Garistovo 35/10 | 1.6 | 0 | 0.23 | 0.85 | 24 hours | -0.62 | 0 | 0.85 | 0.62 | 0.62 | opened
28 | Bezzaboty 35/10 | 2.5 | 0.17 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.56 | 1.56 | opened | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.17 | 1.73 | 24 hours | -1.56 | 0 | 1.73 | 1.56 | 1.56 | opened
29 | Vysokoe 35/10 | 2.5 | 0.13 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.42 | 2.42 | opened | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.13 | 2.55 | 24 hours | -2.42 | 0 | 2.55 | 2.42 | 2.42 | opened
30 | Zaytsevo 35/10 | 1.6 | 0.3 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.55 | 0.55 | opened | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.3 | 0.85 | 24 hours | -0.55 | 0 | 0.85 | 0.55 | 0.55 | opened
31 | Saveevo 35/10 | 2.5 | 0.6 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.25 | 0.25 | opened | 31 | Saveevo 35/10 | 2.5 | 0 | 0.6 | 0.85 | 24 hours | -0.25 | 0 | 0.85 | 0.25 | 0.25 | opened
32 | Gorenovo 35/10 | 1.6 | 0.16 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.39 | 2.39 | opened | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.16 | 2.55 | 24 hours | -2.39 | 0 | 2.55 | 2.39 | 2.39 | opened
33 | Shpunty 35/10 | 2.5 | 0.27 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.58 | 0.58 | opened | 33 | Shpunty 35/10 | 2.5 | 0.38 | 0.65 | 0.85 | 24 hours | -0.2 | 0 | 0.85 | 0.2 | 0.2 | opened
34 | Kadino 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 34 | Kadino 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
35 | Stegrimovo 35/10 | 2.5 | 0.21 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.68 | 2.68 | opened | 35 | Stegrimovo 35/10 | 2.5 | 0 | 0.21 | 2.89 | 24 hours | -2.68 | 0 | 2.89 | 2.68 | 2.68 | opened
36 | Zhukovo 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.13 | 1.73 | 24 hours | -1.6 | 0 | 1.73 | 1.6 | 1.6 | opened
37 | Mikshino 35/10 | 2.5 | 0.11 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.62 | 1.62 | opened | 37 | Mikshino 35/10 | 2.5 | 0 | 0.11 | 1.73 | 24 hours | -1.62 | 0 | 1.73 | 1.62 | 1.62 | opened
38 | Petrovichi 35/10 | 2.5 | 0.17 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.38 | 2.38 | opened | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.17 | 2.55 | 24 hours | -2.38 | 0 | 2.55 | 2.38 | 2.38 | opened
39 | Mikulichi 35/10 | 2.5 | 0.4 | 4.59 | 24 hours | 4.59 | 0 | 4.59 | 4.19 | 4.19 | opened | 39 | Mikulichi 35/10 | 2.5 | 0 | 0.4 | 4.59 | 24 hours | -4.19 | 0 | 4.59 | 4.19 | 4.19 | opened
40 | Nedeykovichi 35/10 | 2.5 | 0.24 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.61 | 0.61 | opened | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.24 | 0.85 | 24 hours | -0.61 | 0 | 0.85 | 0.61 | 0.61 | opened
41 | Posyolki 110/35/10 | 6.3 | 0.54 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.4 | 0.4 | opened | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.54 | 0.94 | 24 hours | -0.4 | 0 | 0.94 | 0.4 | 0.4 | opened
42 | Kuzmichi 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.2 | 1.73 | 24 hours | -1.53 | 0 | 1.73 | 1.53 | 1.53 | opened
43 | Putkovo 35/10 | 1.8 | 0.16 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.69 | 0.69 | opened | 43 | Putkovo 35/10 | 1.8 | 0 | 0.16 | 0.85 | 24 hours | -0.69 | 0 | 0.85 | 0.69 | 0.69 | opened
44 | Uspenskoe 35/10 | 2.5 | 0.4 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.15 | 2.15 | opened | 44 | Uspenskoe 35/10 | 2.5 | 0 | 0.4 | 2.55 | 24 hours | -2.15 | 0 | 2.55 | 2.15 | 2.15 | opened
45 | Kalpita 35/10 | 1.6 | 0.056 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.794 | 0.794 | opened | 45 | Kalpita 35/10 | 1.6 | 0 | 0.056 | 0.85 | 24 hours | -0.794 | 0 | 0.85 | 0.794 | 0.794 | opened
46 | Kasnya 110/10 | 2.5 | 0.5 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.96 | 2.96 | opened | 46 | Kasnya 110/10 | 2.5 | 0 | 0.5 | 3.46 | 24 hours | -2.96 | 0 | 3.46 | 2.96 | 2.96 | opened
47 | Akatovo 35/10 | 1.6 | 0.94 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 1.95 | 1.95 | opened | 47 | Akatovo 35/10 | 1.6 | 0.69 | 1.63 | 2.89 | 24 hours | -1.26 | 0 | 2.89 | 1.26 | 1.26 | opened
48 | Gorki 35/10 | 1.6 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened | 48 | Gorki 35/10 | 1.6 | 0 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
49 | Druzhba 35/10 | 2.5 | 0.81 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.04 | 0.04 | opened | 49 | Druzhba 35/10 | 2.5 | 0 | 0.81 | 0.85 | 24 hours | -0.04 | 0 | 0.85 | 0.04 | 0.04 | opened
50 | NS-21 110/10 | 16 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened | 50 | NS-21 110/10 | 16 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened
51 | NS-22 110/35/10 | 25 | 2.76 | 2.76 | 24 hours | 2.76 | 0 | 2.76 | 0 | 0 | opened | 51 | NS-22 110/35/10 | 25 | 0.99 | 3.75 | 3.75 | 24 hours | 0 | 0 | 3.75 | 0 | 0 | opened
| Nom. capacity MV, МVА | 25 | 2.76 | 2.76 | 24 hours | 2.76 | 0 | 2.76 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 0.99 | 3.75 | 3.75 | 24 hours | 0 | 0 | 3.75 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0
52 | Shuyskoe 35/10 | 2.5 | 0.4 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.06 | 3.06 | opened | 52 | Shuyskoe 35/10 | 2.5 | 0 | 0.4 | 3.46 | 24 hours | -3.06 | 0 | 3.46 | 3.06 | 3.06 | opened
53 | Torbeevo 110/10 | 6.3 | 0.28 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.61 | 2.61 | opened | 53 | Torbeevo 110/10 | 6.3 | 0 | 0.28 | 2.89 | 24 hours | -2.61 | 0 | 2.89 | 2.61 | 2.61 | opened
54 | Leuzdovo 35/10 | 1 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 54 | Leuzdovo 35/10 | 1 | 0.3 | 0.42 | 0.68 | 24 hours | -0.26 | 0 | 0.68 | 0.26 | 0.26 | opened
55 | Maltsevo 35/10 | 2.5 | 0.16 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.57 | 1.57 | opened | 55 | Maltsevo 35/10 | 2.5 | 0 | 0.16 | 1.73 | 24 hours | -1.57 | 0 | 1.73 | 1.57 | 1.57 | opened
56 | Avrora 35/10 | 2.5 | 0.14 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.54 | 0.54 | opened | 56 | Avrora 35/10 | 2.5 | 2 | 2.14 | 0.68 | 24 hours | 1.46 | 0 | 0.68 | -1.46 | -1.46 | closed
57 | Bekhteevo 35/10 | 2.5 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened | 57 | Bekhteevo 35/10 | 2.5 | 0.06 | 0.18 | 0.68 | 24 hours | -0.5 | 0 | 0.68 | 0.5 | 0.5 | opened
58 | Sereda 35/10 | 2.5 | 0.11 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.57 | 0.57 | opened | 58 | Sereda 35/10 | 2.5 | 0 | 0.11 | 0.68 | 24 hours | -0.57 | 0 | 0.68 | 0.57 | 0.57 | opened
59 | Mikhali 35/10 | 2.5 | 0.08 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.77 | 0.77 | opened | 59 | Mikhali 35/10 | 2.5 | 0 | 0.08 | 0.85 | 24 hours | -0.77 | 0 | 0.85 | 0.77 | 0.77 | opened
60 | Mytishino 35/10 | 1.6 | 0.09 | 0 | 24 hours | 0 | 0 | 0 | -0.09 | -0.09 | closed | 60 | Mytishino 35/10 | 1.6 | 0 | 0.09 | 0 | 24 hours | 0.09 | 0 | 0 | -0.09 | -0.09 | closed
61 | Zakharyevskoe 35/10 | 1.6 | 0.017 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.833 | 0.833 | opened | 61 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.017 | 0.85 | 24 hours | -0.833 | 0 | 0.85 | 0.833 | 0.833 | opened
62 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 62 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 24 hours | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
63 | Baskakovka 35/10 | 4 | 0.25 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.48 | 1.48 | opened | 63 | Baskakovka 35/10 | 4 | 0 | 0.25 | 1.73 | 24 hours | -1.48 | 0 | 1.73 | 1.48 | 1.48 | opened
64 | Ekimtsevo 110/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened | 64 | Ekimtsevo 110/10 | 2.5 | 2.22 | 2.42 | 1.73 | 24 hours | 0.69 | 0 | 1.73 | -0.69 | -0.69 | closed
Two-transformer SS | [11 empty] | 1: Two-transformer SS
65 | Smolensk 1 110/35/6 | 40+40 | 41.67 | 6.82 | 120 | 34.85 | 0 | 42 | 7.15 | 7.15 | opened | 65 | Smolensk 1 110/35/6 | 40+40 | 9.53 | 51.2 | 11.64 | 120 | 39.56 | 0 | 42 | 2.44 | 2.44 | opened
| Nom. capavity MV, МVА | 40+40 | 4.9 | 4.9 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capavity MV, МVА | 40+40 | 4.82 | 9.72 | 9.72 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 36.77 | 1.92 | 120 | 34.85 | 0 | 42 | 7.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 4.71 | 41.48 | 1.92 | 120 | 39.56 | 0 | 42 | 2.44
66 | Water intake 35/6 | 4+4 | 3.35 | 1.2 | 120 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | opened | 66 | Water intake 35/6 | 4+4 | 4.62 | 7.97 | 1.2 | 120 | 6.77 | 0 | 4.2 | -2.57 | -2.57 | closed
67 | Tychinino 35/10 | 4+4 | 0.9 | 0.91 | 120 | -0.01 | 0 | 4.2 | 4.21 | 4.21 | opened | 67 | Tychinino 35/10 | 4+4 | 0 | 0.9 | 0.91 | 120 | -0.01 | 0 | 4.2 | 4.21 | 4.21 | opened
68 | Ryaиtsevo 35/10 | 4+4 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | opened | 68 | Ryaиtsevo 35/10 | 4+4 | 0.2 | 2.07 | 0 | 120 | 2.07 | 0 | 4.2 | 2.13 | 2.13 | opened
69 | Smolensk 2 110/6 | 40+40 | 14.64 | 6.41 | 120 | 8.23 | 0 | 42 | 33.77 | 33.77 | opened | 69 | Smolensk 2 110/6 | 40+40 | 6.33 | 20.97 | 6.41 | 120 | 14.56 | 0 | 42 | 27.44 | 27.44 | opened
70 | Vostochnaya 110/6 | 25+16 | 10.14 | 0 | 120 | 10.14 | 0 | 16.8 | 6.66 | 6.66 | opened | 70 | Vostochnaya 110/6 | 25+16 | 0.09 | 10.23 | 0 | 120 | 10.23 | 0 | 16.8 | 6.57 | 6.57 | opened
71 | Diffuzion 110/6 | 25+25 | 14.1 | 1.06 | 120 | 13.04 | 0 | 26.25 | 13.21 | 13.21 | opened | 71 | Diffuzion 110/6 | 25+25 | 16.87 | 30.97 | 1.06 | 120 | 29.91 | 0 | 26.25 | -3.66 | -3.66 | closed
72 | Zavodskaya 110/35/10 | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 | 16.8 | in repairs, load is transferred to SS Yuzhnaya | 72 | Заводская 110/35/10 | 16+16 | 11.8 | 11.8 | 2.04 | 120 | 9.76 | 0 | 16.8 | 7.04 | 7.04 | in repairs, load is transferred to SS Yuzhnaya
| Nom. capacity MV, МVА | 16+16 | 0 | 0 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 2.04 | 2.04 | 2.04 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capcity LV, МVА | 16+16 | 9.76 | 9.76 | 0 | 120 | 9.76 | 0 | 16.8 | 7.04
73 | Yasennaya 35/6 | 6,3+10 | 11.21 | 0 | 120 | 11.21 | 0 | 6.615 | -4.595 | -4.595 | closed | 73 | Yasennaya 35/6 | 6,3+10 | 0.98 | 12.19 | 0 | 120 | 12.19 | 0 | 6.615 | -5.575 | -5.575 | closed
74 | Gnezodovo 35/6 | 7,5+7,5 | 6.2 | 0.42 | 120 | 5.78 | 0 | 7.875 | 2.095 | 2.095 | opened | 74 | Птуявщмщ 35/6 | 7,5+7,5 | 1.06 | 7.26 | 0.42 | 120 | 6.84 | 0 | 7.875 | 1.035 | 1.035 | opened
75 | Zapadnaya 110/6 | 25+16 | 12.99 | 0.63 | 120 | 12.36 | 0 | 16.8 | 4.44 | 4.44 | opened | 75 | Zapadnaya 110/6 | 25+16 | 9.71 | 22.7 | 0.63 | 120 | 22.07 | 0 | 16.8 | -5.27 | -5.27 | closed
76 | Katyn 2 110/35/10 | 10+16 | 4.24 | 2.24 | 120 | 2 | 0 | 10.5 | 8.5 | 8.4 | opened | 76 | Katyn 2 110/35/10 | 10+16 | 9.22 | 13.46 | 3.15 | 120 | 10.31 | 0 | 10.5 | 0.19 | 0.19 | opened
| Nom. capacity MV, МVА | 10+16 | 4.24 | 2.24 |  | 2 | 0 | 10.5 | 8.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 3.71 | 7.95 | 3.15 |  | 4.8 | 0 | 10.5 | 5.7
| Nom. capacity LV, МVА | 10+16 | 2.1 | 0 | 120 | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.51 | 7.61 | 0 | 120 | 7.61 | 0 | 10.5 | 2.89
77 | Katyn 1 35/10 | 4+4 | 1.63 | 0.05 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | opened | 77 | Katyn 1 35/10 | 4+4 | 2.81 | 4.44 | 0.05 | 120 | 4.39 | 0 | 4.2 | -0.19 | -0.19 | closed
78 | Lubnya 35/10 | 4+4 | 1.45 | 0.13 | 120 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | opened | 78 | Lubnya 35/10 | 4+4 | 0.4 | 1.85 | 0.13 | 120 | 1.72 | 0 | 4.2 | 2.48 | 2.48 | opened
79 | Kozino 110/35/10 | 10+10 | 9.28 | 1.48 | 120 | 7.8 | 0 | 10.5 | 2.7 | 2.7 | opened | 79 | Kozino 110/35/10 | 10+10 | 4.71 | 13.99 | 3.22 | 120 | 10.77 | 0 | 10.5 | -0.27 | -0.27 | closed
| Nom. capacity MV, МVА | 10+10 | 6.27 | 1.47 |  | 4.8 | 0 | 10.5 | 5.7 |  |  |  | Nom. capacity MV, МVА | 10+10 | 3.6 | 9.87 | 3.21 |  | 6.66 | 0 | 10.5 | 3.84
| Nom. capacity LV, МVА | 10+10 | 3.01 | 0.01 | 120 | 3 | 0 | 10.5 | 7.5 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.11 | 4.12 | 0.01 | 120 | 4.11 | 0 | 10.5 | 6.39
80 | Odintsovo 35/10 | 6,3+6,3 | 4.28 | 2.15 | 120 | 2.13 | 0 | 6.615 | 4.485 | 4.485 | opened | 80 | Odintsovo 35/10 | 6,3+6,3 | 2.47 | 6.75 | 2.15 | 120 | 4.6 | 0 | 6.615 | 2.015 | 2.015 | opened
81 | Trudilovo 35/10 | 2,5+2,5 | 1.18 | 0.08 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 81 | Trudilovo 35/10 | 2,5+2,5 | 1.13 | 2.31 | 0.08 | 120 | 2.23 | 0 | 2.625 | 0.395 | 0.395 | opened
82 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 | 120 | 0 | 0 | 42 | 42 | 42 | opened | 82 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 | 0 | 120 | 0 | 0 | 42 | 42 | 42 | opened
83 | Pronino 110/35/6 | 10+10 | 5.95 | 1.4 | 120 | 4.55 | 0 | 10.5 | 5.95 | 5.95 | opened | 83 | Pronino 110/35/6 | 10+10 | 2.09 | 8.04 | 2.5 | 120 | 5.54 | 0 | 10.5 | 4.96 | 4.96 | opened
| Nom. capacity MV, МVА | 10+10 | 3.27 | 0.21 |  | 3.06 | 0 | 10.5 | 7.44 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.04 | 5.31 | 1.31 |  | 4 | 0 | 10.5 | 6.5
| Nom. capacity LV, МVА | 10+10 | 2.68 | 1.19 | 120 | 1.49 | 0 | 10.5 | 9.01 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 2.68 | 1.19 | 120 | 1.49 | 0 | 10.5 | 9.01
84 | Olsha 35/10 | 2,5+2,5 | 0.72 | 0 | 120 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 84 | Olsha 35/10 | 2,5+2,5 | 1.29 | 2.01 | 0 | 120 | 2.01 | 0 | 2.625 | 0.615 | 0.615 | opened
85 | Krasny bor 35/6 | 4+4 | 2.39 | 0 | 120 | 2.39 | 0 | 4.2 | 1.81 | 1.81 | opened | 85 | Krasny bor 35/6 | 4+4 | 0.75 | 3.14 | 0 | 120 | 3.14 | 0 | 4.2 | 1.06 | 1.06 | opened
86 | Severnaya 110/35/6 | 25+25 | 24 | 9.53 | 120 | 14.47 | 0 | 26.25 | 11.78 | 11.78 | opened | 86 | Severnaya 110/35/6 | 25+25 | 11.57 | 35.57 | 11.96 | 120 | 23.61 | 0 | 26.25 | 2.64 | 2.64 | opened
| Nom. capacity MV, МVА | 25+25 | 6.94 | 6.94 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 2.43 | 9.37 | 9.37 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 17.06 | 2.59 | 120 | 14.47 | 0 | 26.25 | 11.78 |  |  |  | Nom. capacity LV, МVА | 25+25 | 9.14 | 26.2 | 2.59 | 120 | 23.61 | 0 | 26.25 | 2.64
87 | Peсhersk 35/6 | 4+4 | 2.54 | 0.34 | 120 | 2.2 | 0 | 4.2 | 2 | 2 | opened | 87 | Peсhersk 35/6 | 4+4 | 1.82 | 4.36 | 0.34 | 120 | 4.02 | 0 | 4.2 | 0.18 | 0.18 | opened
88 | Kolodnya 35/6 | 6,3+4 | 3.68 | 0 | 120 | 3.68 | 0 | 4.2 | 0.52 | 0.52 | opened | 88 | Kolodnya 35/6 | 6,3+4 | 0.61 | 4.29 | 0 | 120 | 4.29 | 0 | 4.2 | -0.09 | -0.09 | closed
89 | Tsentralnaya 110/10/6 | 25+25 | 18.8 | 5.76 | 120 | 13.04 | 0 | 26.25 | 13.21 | 13.21 | opened | 89 | Tsentralnaya 110/10/6 | 25+25 | 5.82 | 24.62 | 5.76 | 120 | 18.86 | 0 | 26.25 | 7.39 | 7.39 | opened
| Nom. capacity MV, МVА | 25+25 | 0.03 | 0 |  | 0.03 | 0 | 26.25 | 26.22 |  |  |  | Nom. capacity MV, МVА | 25+25 | 3 | 3.03 | 0 |  | 3.03 | 0 | 26.25 | 23.22
| Nom. capacity LV, МVА | 25+25 | 18.77 | 5.76 | 120 | 13.01 | 0 | 26.25 | 13.24 |  |  |  | Nom. capacity LV, МVА | 25+25 | 2.82 | 21.59 | 5.76 | 120 | 15.83 | 0 | 26.25 | 10.42
90 | Chernushki 110/10/6 | 25+25 | 21 | 2.12 | 120 | 18.88 | 0 | 26.25 | 7.37 | 7.37 | opened | 90 | Cernushki 110/10/6 | 25+25 | 10.07 | 31.07 | 2.12 | 120 | 28.95 | 0 | 26.25 | -2.7 | -2.7 | closed
| Nom. capacity MV, МVА | 25+25 | 7.29 | 0 |  | 7.29 | 0 | 26.25 | 18.96 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.07 | 12.36 | 0 |  | 12.36 | 0 | 26.25 | 13.89
| Nom. Capacity LV, МVА | 25+25 | 13.71 | 2.12 | 120 | 11.59 | 0 | 26.25 | 14.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 5 | 18.71 | 2.12 | 120 | 16.59 | 0 | 26.25 | 9.66
91 | Yuzhnaya 110/35/6 | 40+40 | 46.58 | 7.52 | 120 | 39.06 | 0 | 42 | 2.94 | 2.94 | opened | 91 | Yuzhnaya 110/35/6 | 40+40 | 20.86 | 67.44 | 22.16 | 120 | 45.28 | 0 | 42 | -3.28 | -3.28 | closed
| Nom. capacity MV, МVА | 40+40 | 14.91 | 1.8 |  | 13.11 | 0 | 42 | 28.89 |  |  |  | Nom. capacity MV, МVА | 40+40 | 1.53 | 16.44 | 16.44 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 31.67 | 5.72 | 120 | 25.95 | 0 | 42 | 16.05 |  |  |  | Nom. Capacity LV, МVА | 40+40 | 19.33 | 51 | 5.72 | 120 | 45.28 | 0 | 42 | -3.28
92 | Karyernaya 110/35/6 | 16+16 | 9.15 | 1.05 | 120 | 8.1 | 0 | 16.8 | 8.7 | 8.7 | opened | 92 | Karyernaya 110/35/6 | 16+16 | 2.81 | 11.96 | 1.05 | 120 | 10.91 | 0 | 16.8 | 5.89 | 5.89 | opened
| Nom. capacity MV, МВА | 16+16 | 3.18 | 1.05 |  | 2.13 | 0 | 16.8 | 14.67 |  |  |  | Nom. capacity MV, МВА | 16+16 | 0.97 | 4.15 | 1.05 |  | 3.1 | 0 | 16.8 | 13.7
| Nom. capacity LV, МVА | 16+16 | 5.97 | 0 | 120 | 5.97 | 0 | 16.8 | 10.83 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.84 | 7.81 | 0 | 120 | 7.81 | 0 | 16.8 | 8.99
93 | Koshchino 35/10 | 4+4 | 0.72 | 0.11 | 120 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | opened | 93 | Koshchino 35/10 | 4+4 | 0 | 0.72 | 0.11 | 120 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | opened
94 | Kommunar 35/10 | 2,5+2,5 | 0.46 | 0.03 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened | 94 | Kommunar 35/10 | 2,5+2,5 | 0 | 0.46 | 0.03 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
95 | Kasplya 110/35/10 | 10+10 | 3.38 | 3.08 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened | 95 | Kasplya 110/35/10 | 10+10 | 5.22 | 8.6 | 6.73 | 120 | 1.87 | 0 | 10.5 | 8.63 | 8.63 | opened
| Nom. capacity MV, МVА | 10+10 | 2.22 | 2.22 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 3.65 | 5.87 | 5.87 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.16 | 0.86 | 120 | 0.3 | 0 | 10.5 | 10.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.57 | 2.73 | 0.86 | 120 | 1.87 | 0 | 10.5 | 8.63
96 | Apolye 35/10 | 2,5+2,5 | 0.57 | 0.17 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 96 | Apolye 35/10 | 2,5+2,5 | 0 | 0.57 | 0.17 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
97 | Zhukovskaya 35/10 | 4+4 | 2.04 | 0.19 | 120 | 1.85 | 0 | 4.2 | 2.35 | 2.35 | opened | 97 | Zhukovskaya 35/10 | 4+4 | 2.36 | 4.4 | 0.19 | 120 | 4.21 | 0 | 4.2 | -0.01 | -0.01 | closed
98 | Mazaltsevo 110/35/10 | 10+10 | 3.25 | 2.41 | 120 | 0.84 | 0 | 10.5 | 9.66 | 9.66 | opened | 98 | Mazaltsevo 110/35/10 | 10+10 | 4.5 | 7.75 | 6.46 | 120 | 1.29 | 0 | 10.5 | 9.21 | 9.21 | opened
| Nom. capacity MV, МVА | 10+10 | 2.31 | 2.15 |  | 0.16 | 0 | 10.5 | 10.34 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.1 | 6.41 | 6.2 |  | 0.21 | 0 | 10.5 | 10.29
| Nom. capacity LV, МVА | 10+10 | 0.94 | 0.26 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.4 | 1.34 | 0.26 | 120 | 1.08 | 0 | 10.5 | 9.42
99 | Krasny 110/35/10 | 10+10 | 2.69 | 0.77 | 120 | 1.92 | 0 | 10.5 | 8.58 | 8.58 | opened | 99 | Krasny 110/35/10 | 10+10 | 3.67 | 6.36 | 2.18 | 120 | 4.18 | 0 | 10.5 | 6.32 | 6.32 | opened
| Nom. capacity MV, МVА | 10+10 | 0.31 | 0.31 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.63 | 1.94 | 1.72 |  | 0.22 | 0 | 10.5 | 10.28
| Nom. capacity LV, МVА | 10+10 | 2.38 | 0.46 | 120 | 1.92 | 0 | 10.5 | 8.58 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.04 | 4.42 | 0.46 | 120 | 3.96 | 0 | 10.5 | 6.54
100 | Voloelovo 35/10 | 2,5+2,5 | 0.18 | 0.01 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 100 | Voloelovo 35/10 | 2,5+2,5 | 0 | 0.18 | 0.01 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
101 | Kryukovo 35/10 | 2,5+2,5 | 0.13 | 0.26 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | opened | 101 | Kryukovo 35/10 | 2,5+2,5 | 0.44 | 0.57 | 0.26 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
102 | Miganovo 35/10 | 2,5+2,5 | 1.11 | 0.49 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 102 | Miganovo 35/10 | 2,5+2,5 | 1.19 | 2.3 | 0.49 | 120 | 1.81 | 0 | 2.625 | 0.815 | 0.815 | opened
103 | Velizh 110/35/10 | 10+10 | 5.93 | 0.69 | 120 | 5.24 | 0 | 10.5 | 5.26 | 5.26 | opened | 103 | Velizh 110/35/10 | 10+10 | 0.71 | 6.64 | 0.69 | 120 | 5.95 | 0 | 10.5 | 4.55 | 4.55 | opened
| Nom. capacity MV, МVА | 10+10 | 0.02 | 0.02 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.02 | 0.02 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 5.91 | 0.67 | 120 | 5.24 | 0 | 10.5 | 5.26 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.71 | 6.62 | 0.67 | 120 | 5.95 | 0 | 10.5 | 4.55
104 | Chepli 35/10 | 2,5+2,5 | 0.32 | 0.09 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened | 104 | Chepli 35/10 | 2,5+2,5 | 0 | 0.32 | 0.09 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | opened
105 | Demidov 110/35/10 | 10+16 | 5.44 | 0.82 | 120 | 4.62 | 0 | 10.5 | 5.88 | 5.88 | opened | 105 | Demidov 110/35/10 | 10+16 | 2.9 | 8.34 | 0.88 | 120 | 7.46 | 0 | 10.5 | 3.04 | 3.04 | opened
| Nom. capacity MV, МVА | 10+16 | 0.85 | 0.64 |  | 0.21 | 0 | 10.5 | 10.29 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.1 | 0.95 | 0.7 |  | 0.25 | 0 | 10.5 | 10.25
| Nom. capacity LV, МVА | 10+16 | 4.59 | 0.18 | 120 | 4.41 | 0 | 10.5 | 6.09 |  |  |  | Nom. capacity LV, МVА | 10+16 | 2.8 | 7.39 | 0.18 | 120 | 7.21 | 0 | 10.5 | 3.29
106 | Staroe selo 35/10 | 2,5+2,5 | 0.38 | 0.17 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 106 | Staroe selo 35/10 | 2,5+2,5 | 0 | 0.38 | 0.17 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
107 | Zakrutye 35/10 | 2,5+2,5 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 107 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
108 | Zaborye 35/10 | 1,6+2,5 | 0.3 | 0.21 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 108 | Zaborye 35/10 | 1,6+2,5 | 0 | 0.3 | 0.21 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
109 | Mikhailovskoe 110/35/10 | 10+10 | 1.35 | 0.45 | 120 | 0.9 | 0 | 10.5 | 9.6 | 9.6 | opened | 109 | Mikhailovskoe 110/35/10 | 10+10 | 0 | 1.35 | 0.45 | 120 | 0.9 | 0 | 10.5 | 9.6 | 9.6 | opened
| Nom. capacity MV, МVА | 10+10 | 0.3 | 0.03 |  | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.3 | 0.03 | 120 | 0.27 | 0 | 10.5 | 10.23
| Nom. capacity LV, МVА | 10+10 | 1.05 | 0.42 | 120 | 0.63 | 0 | 10.5 | 9.87 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 1.05 | 0.42 | 120 | 0.63 | 0 | 10.5 | 9.87
110 | Kardymovo 110/35/10 | 10+16 | 4.83 | 2.09 | 120 | 2.74 | 0 | 10.5 | 7.76 | 7.76 | opened | 110 | Kardymovo 110/35/10 | 10+16 | 6.96 | 11.79 | 2.24 | 120 | 9.55 | 0 | 10.5 | 0.95 | 0.95 | opened
| Nom. capacity MV, МVА | 10+16 | 1.64 | 1.47 |  | 0.17 | 0 | 10.5 | 10.33 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.6 | 2.24 | 1.62 |  | 0.62 | 0 | 10.5 | 9.88
| Nom. capacity LV, МVА | 10+16 | 3.19 | 0.62 | 120 | 2.57 | 0 | 10.5 | 7.93 |  |  |  | Nom. capacity LV, МVА | 10+16 | 6.36 | 9.55 | 0.62 | 120 | 8.93 | 0 | 10.5 | 1.57
111 | Sinkovo 35/6 | 4+2,5 | 0.17 | 0.16 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 111 | Sinkovo 35/6 | 4+2,5 | 0 | 0.17 | 0.16 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened
112 | Kamenka 35/10 | 2,5+2,5 | 2.32 | 0.42 | 120 | 1.9 | 0 | 2.625 | 0.725 | 0.725 | opened | 112 | Kamenka 35/10 | 2,5+2,5 | 0.96 | 3.28 | 0.42 | 120 | 2.86 | 0 | 2.625 | -0.235 | -0.235 | closed
113 | Solovyevo 35/10 | 4+4 | 0.29 | 0.04 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 113 | Solovyevo 35/10 | 4+4 | 0.1 | 0.39 | 0.04 | 120 | 0.35 | 0 | 4.2 | 3.85 | 3.85 | opened
114 | Rudnya 110/35/10 | 10+16 | 8.34 | 1.64 | 120 | 6.7 | 0 | 10.5 | 3.8 | 3.8 | opened | 114 | Rudnya 110/35/10 | 10+16 | 1.56 | 9.9 | 2.05 | 120 | 7.85 | 0 | 10.5 | 2.65 | 2.65 | opened
| Nom. capacity MV, МVА | 10+16 | 0.71 | 0.71 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.41 | 1.12 | 1.12 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.63 | 0.93 | 120 | 6.7 | 0 | 10.5 | 3.8 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.15 | 8.78 | 0.93 | 120 | 7.85 | 0 | 10.5 | 2.65
115 | Zhichitsy 35/10 | 2,5+2,5 | 0.14 | 0.75 | 120 | -0.61 | 0 | 2.625 | 3.235 | 3.235 | opened | 115 | Zhichitsy 35/10 | 2,5+2,5 | 0 | 0.14 | 0.75 | 120 | -0.61 | 0 | 2.625 | 3.235 | 3.235 | opened
116 | Mikulino 35/10 | 6,3+6,3 | 0.72 | 1.1 | 120 | -0.38 | 0 | 6.615 | 6.995 | 6.995 | opened | 116 | Mikulino 35/10 | 6,3+6,3 | 0.15 | 0.87 | 1.1 | 120 | -0.23 | 0 | 6.615 | 6.845 | 6.845 | opened
117 | Lyubavichi 35/10 | 2,5+2,5 | 0.51 | 0.74 | 120 | -0.23 | 0 | 2.625 | 2.855 | 2.855 | opened | 117 | Lyubavichi 35/10 | 2,5+2,5 | 0.26 | 0.77 | 0.74 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
118 | Kazimirovo 35/10 | 4+4 | 0.28 | 0.02 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened | 118 | Kazimirovo 35/10 | 4+4 | 0 | 0.28 | 0.02 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | opened
119 | Golynki 110/35/6 | 25+25 | 5.16 | 2.88 | 120 | 2.28 | 0 | 26.25 | 23.97 | 23.97 | opened | 119 | Golynki 110/35/6 | 25+25 | 4.99 | 10.15 | 7.87 | 120 | 2.28 | 0 | 26.25 | 23.97 | 23.97 | opened
| Nom. Capacity MV, МVА | 25+25 | 2.72 | 2.72 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 4.99 | 7.71 | 7.71 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 2.44 | 0.16 | 120 | 2.28 | 0 | 26.25 | 23.97 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0 | 2.44 | 0.16 | 120 | 2.28 | 0 | 26.25 | 23.97
120 | Belei 35/10 | 2,5+2,5 | 1.77 | 0.75 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | opened | 120 | Belei 35/10 | 2,5+2,5 | 3.39 | 5.16 | 0.75 | 120 | 4.41 | 0 | 2.625 | -1.785 | -1.785 | closed
121 | Ponizovye 110/35/10 | 6,3+6,3 | 2.35 | 1.18 | 120 | 1.17 | 0 | 6.615 | 5.445 | 5.445 | opened | 121 | Ponizovye 110/35/10 | 6,3+6,3 | 0.15 | 2.5 | 1.33 | 120 | 1.17 | 0 | 6.615 | 5.445 | 5.445 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.12 | 1.12 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.15 | 1.27 | 1.27 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.23 | 0.06 | 120 | 1.17 | 0 | 6.615 | 5.445 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 1.23 | 0.06 | 120 | 1.17 | 0 | 6.615 | 5.445
122 | Klyarinovo 35/10 | 2,5+2,5 | 0.28 | 0.19 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 122 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0.19 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
123 | Safonovo 110/6 | 15+20 | 10.24 | 0.06 | 120 | 10.18 | 0 | 15.75 | 5.57 | 5.57 | opened | 123 | Safonovo 110/6 | 15+20 | 5.24 | 15.48 | 0.06 | 120 | 15.42 | 0 | 15.75 | 0.33 | 0.33 | opened
124 | Gornaya 110/35/6 | 25+25 | 11.43 | 9.29 | 120 | 2.14 | 0 | 26.25 | 24.11 | 24.11 | opened | 124 | Gornaya 110/35/6 | 25+25 | 5.79 | 17.22 | 13.17 | 120 | 4.05 | 0 | 26.25 | 22.2 | 22.2 | opened
| Nom. capacity MV, МVА | 25+25 | 5.81 | 4.62 |  | 1.19 | 0 | 26.25 | 25.06 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.66 | 11.47 | 8.5 |  | 2.97 | 0 | 26.25 | 23.28
| Nom. capacity LV, МVА | 25+25 | 5.62 | 4.67 | 120 | 0.95 | 0 | 26.25 | 25.3 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.13 | 5.75 | 4.67 | 120 | 1.08 | 0 | 26.25 | 25.17
125 | Water intake 35/6 | 6,3+4 | 1.67 | 0.69 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 125 | Water intake 35/6 | 6,3+4 | 2.82 | 4.49 | 0.69 | 120 | 3.8 | 0 | 4.2 | 0.4 | 0.4 | opened
126 | Vadino 35/10 | 4+4 | 1.36 | 0 | 120 | 1.36 | 0 | 4.2 | 2.84 | 2.84 | opened | 126 | Vadino 35/10 | 4+4 | 0.1 | 1.46 | 0 | 120 | 1.46 | 0 | 4.2 | 2.74 | 2.74 | opened
127 | ZSSK 35/6 | 4+4 | 1.66 | 0.75 | 120 | 0.91 | 0 | 4.2 | 3.29 | 3.29 | opened | 127 | ZSSK 35/6 | 4+4 | 1.31 | 2.97 | 0.75 | 120 | 2.22 | 0 | 4.2 | 1.98 | 1.98 | opened
128 | Yanovo 35/10 | 4+6,3 | 0.48 | 0.05 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened | 128 | Yanovo 35/10 | 4+6,3 | 0 | 0.48 | 0.05 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened
129 | Kapyrevshchina 35/10 | 4+4 | 1.25 | 0.22 | 120 | 1.03 | 0 | 4.2 | 3.17 | 3.17 | opened | 129 | Kapyrevshchina 35/10 | 4+4 | 1.92 | 3.17 | 0.22 | 120 | 2.95 | 0 | 4.2 | 1.25 | 1.25 | opened
130 | Miropolye 35/10 | 2,5+2,5 | 0.6 | 0 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 130 | Miropolye 35/10 | 2,5+2,5 | 0 | 0.6 | 0 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
131 | Izdeshkovo 110/35/10 | 5,6+6,3 | 3.78 | 1.23 | 120 | 2.55 | 0 | 5.88 | 3.33 | 1.69 | opened | 131 | Izdeshkovo 110/35/10 | 5,6+6,3 | 0.6 | 4.38 | 1.49 | 120 | 2.89 | 0 | 5.88 | 2.99 | 2.99 | opened
| Nom. capacity MV, МVА | 5,6+6,3 | 1.16 | 0.8 |  | 0.36 | 1 | 5.88 | 4.52 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 0.6 | 1.76 | 1.06 |  | 0.7 | 0 | 5.88 | 5.18
| Nom. capacity LV, МVА | 5,6+6,3 | 2.62 | 0.43 | 120 | 2.19 | 2 | 5.88 | 1.69 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 2.62 | 0.43 | 120 | 2.19 | 0 | 5.88 | 3.69
132 | Alferovo 35/10 | 2,5+2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 132 | Alferovo 35/10 | 2,5+2,5 | 0.34 | 0.7 | 0.2 | 120 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
133 | Kasulino 35/10 | 2,5+2,5 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 133 | Kasulino 35/10 | 2,5+2,5 | 0.18 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
134 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.32 | 0.15 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened | 134 | Bogdanovshchina 35/10 | 1,6+1,6 | 0 | 0.32 | 0.15 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened
135 | Glinka 110/35/10 | 10+6,3 | 1.49 | 0.34 | 120 | 1.15 | 0 | 6.615 | 5.465 | 3.465 | opened | 135 | Glinka 110/35/10 | 10+6,3 | 0.67 | 2.16 | 1.01 | 120 | 1.15 | 0 | 6.615 | 5.465 | 5.465 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.23 | 0.23 |  | 0 | 1 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.67 | 0.9 | 0.9 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.26 | 0.11 | 120 | 1.15 | 2 | 6.615 | 3.465 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0 | 1.26 | 0.11 | 120 | 1.15 | 0 | 6.615 | 5.465
136 | Dobromino 35/10 | 2,5+2,5 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 136 | Dobromino 35/10 | 2,5+2,5 | 0 | 0.21 | 0 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
137 | Bely kholm 35/10 | 1,6+1,6 | 0.03 | 0 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened | 137 | Bely kholm 35/10 | 1,6+1,6 | 0 | 0.03 | 0 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
138 | Dukhovshchina 110/35/10 | 10+10 | 3.24 | 0.88 | 120 | 2.36 | 0 | 10.5 | 8.14 | 8.14 | opened | 138 | Dukhovshchina 110/35/10 | 10+10 | 0.98 | 4.22 | 2.25 | 120 | 1.97 | 0 | 10.5 | 8.53 | 8.53 | opened
| Nom. capacity MV, МVА | 10+10 | 1.2 | 0.62 |  | 0.58 | 0 | 10.5 | 9.92 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.98 | 2.18 | 1.99 |  | 0.19 | 0 | 10.5 | 10.31
| Nom. capacity LV, МVА | 10+10 | 2.04 | 0.26 | 120 | 1.78 | 0 | 10.5 | 8.72 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 2.04 | 0.26 | 120 | 1.78 | 0 | 10.5 | 8.72
139 | Zimets 35/10 | 4+4 | 0.1 | 0.06 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened | 139 | Zimets 35/10 | 4+4 | 0 | 0.1 | 0.06 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened
140 | Beresnevo 35/10 | 1,6+1,6 | 0.22 | 0.01 | 120 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened | 140 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.22 | 0.01 | 120 | 0.21 | 0 | 1.68 | 1.47 | 1.47 | opened
141 | Prechistoe 110/35/10 | 6,3+6,3 | 0.57 | 0.14 | 120 | 0.43 | 0 | 6.615 | 6.185 | 6.185 | opened | 141 | Prechistoe 110/35/10 | 6,3+6,3 | 0 | 0.57 | 0.14 | 120 | 0.43 | 0 | 6.615 | 6.185 | 6.185 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.13 | 0 |  | 0.13 | 0 | 6.615 | 6.485 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.13 | 0 |  | 0.13 | 0 | 6.615 | 6.485
| Nom. capacity LV, МVА | 6,3+6,3 | 0.44 | 0.14 | 120 | 0.3 | 0 | 6.615 | 6.315 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.44 | 0.14 | 120 | 0.3 | 0 | 6.615 | 6.315
142 | Vorontsovo 35/10 | 2,5+2,5 | 0.14 | 0.07 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened | 142 | Vorontsovo 35/10 | 2,5+2,5 | 0 | 0.14 | 0.07 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
143 | Ozsyorny 35/10 | 6,3+6,3 | 1.08 | 0.01 | 120 | 1.07 | 0 | 6.615 | 5.545 | 5.545 | opened | 143 | Ozsyorny 35/10 | 6,3+6,3 | 0 | 1.08 | 0.01 | 120 | 1.07 | 0 | 6.615 | 5.545 | 5.545 | opened
144 | Igorevskaya 110/10 | 10+10 | 9.47 | 0 | 120 | 9.47 | 0 | 10.5 | 1.03 | 1.03 | opened | 144 | Igorevskaya 110/10 | 10+10 | 1.75 | 11.22 | 0 | 120 | 11.22 | 0 | 10.5 | -0.72 | -0.72 | closed
145 | Kanyutino 110/35/10 | 5,6+6,3 | 2.74 | 1.68 | 120 | 1.06 | 0 | 5.88 | 4.82 | 4.82 | opened | 145 | Kanyutino 110/35/10 | 5,6+6,3 | 2.83 | 5.57 | 5.57 | 120 | 0 | 0 | 5.88 | 5.88 | 5.88 | opened
| Nom. capacity LV, МVА | 5,6+6,3 | 2.53 | 2.53 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 2.83 | 5.36 | 5.36 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.21 | 0.21 | 120 | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.21 | 0.21 | 120 | 0 | 0 | 5.88 | 5.88
146 | Bogolyubovo 35/10 | 2,5+2,5 | 0.85 | 0.25 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 146 | Bogolyubovo 35/10 | 2,5+2,5 | 0 | 0.85 | 0.25 | 120 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
147 | Kholm-Zhirki 35/10 | 2,5+4 | 3.08 | 0.4 | 120 | 2.68 | 0 | 2.625 | -0.055 | -0.055 | closed | 147 | Kholm-Zhirki 35/10 | 2,5+4 | 0.52 | 3.6 | 0.4 | 120 | 3.2 | 0 | 2.625 | -0.575 | -0.575 | closed
148 | Dorogobuzh 1 110/35/10 | 16+16 | 5.64 | 2.19 | 120 | 3.45 | 0 | 16.8 | 13.35 | 13.35 | opened | 148 | Dorogobuzh 1 110/35/10 | 16+16 | 1.24 | 6.88 | 2.94 | 120 | 3.94 | 0 | 16.8 | 12.86 | 12.86 | opened
| Nom. capacity MV, МVА | 16+16 | 1.67 | 1.67 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.75 | 2.42 | 2.42 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 3.97 | 0.52 | 120 | 3.45 | 0 | 16.8 | 13.35 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.49 | 4.46 | 0.52 | 120 | 3.94 | 0 | 16.8 | 12.86
149 | Kaskovo 35/10 | 1,6+4 | 0.72 | 0.09 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened | 149 | Kaskovo 35/10 | 1,6+4 | 0 | 0.72 | 0.09 | 120 | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened
150 | Usvyatye 35/10 | 2,5+4 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 150 | Usvyatye 35/10 | 2,5+4 | 0.65 | 1.46 | 0 | 120 | 1.46 | 0 | 2.625 | 1.165 | 1.165 | opened
151 | Ushakovo 35/10 | 1,6+2,5 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 151 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
152 | Artek 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 152 | Artek 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
153 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.04 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened | 153 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0 | 0.04 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened
154 | Elnya 110/35/10 | 16+16 | 5.77 | 2.36 | 120 | 3.41 | 0 | 16.8 | 13.39 | 13.39 | opened | 154 | Elnya 110/35/10 | 16+16 | 0.21 | 5.98 | 2.36 | 120 | 3.62 | 0 | 16.8 | 13.18 | 13.18 | opened
| Nom. capacity MV, МVА | 16+16 | 1.82 | 1.82 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 1.82 | 1.82 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 3.95 | 0.54 | 10 | 3.41 | 0 | 16.8 | 13.39 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.21 | 4.16 | 0.54 | 120 | 3.62 | 0 | 16.8 | 13.18
155 | Pavlovo 35/10 | 2,5+2,5 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 155 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
156 | Sharapovo 35/10 | 4+4 | 0.63 | 1 | 120 | -0.37 | 0 | 4.2 | 4.57 | 4.57 | opened | 156 | Sharapovo 35/10 | 4+4 | 0 | 0.63 | 1 | 120 | -0.37 | 0 | 4.2 | 4.57 | 4.57 | opened
157 | Korobets 35/10 | 2,5+2,5 | 0.76 | 0.17 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 157 | Korobets 35/10 | 2,5+2,5 | 0 | 0.76 | 0.17 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
158 | Baltuty 35/10 | 2,5+2,5 | 0.42 | 0 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened | 158 | Baltuty 35/10 | 2,5+2,5 | 0 | 0.42 | 0 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened
159 | Lapino 110/35/10 | 5,6+5,6 | 0.89 | 0.48 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | opened | 159 | Lapino 110/35/10 | 5,6+5,6 | 0 | 0.89 | 0.48 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | opened
| Nom. capacity MV, МVА | 5,6+5,6 | 0.48 | 0.48 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0 | 0.48 | 0.48 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47
160 | Mutishche 35/10 | 1,6+2,5 | 0.17 | 0.08 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 160 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.17 | 0.08 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
161 | Suetovo 110/35/10 | 6,3+6,3 | 2.22 | 1.38 | 120 | 0.84 | 0 | 6.615 | 5.775 | 5.775 | opened | 161 | Suetovo 110/35/10 | 6,3+6,3 | 0 | 2.22 | 1.38 | 120 | 0.84 | 0 | 6.615 | 5.775 | 5.775 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.8 | 0.8 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.8 | 0.8 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.42 | 0.58 | 120 | 0.84 | 0 | 6.615 | 5.775 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 1.42 | 0.58 | 120 | 0.84 | 0 | 6.615 | 5.775
162 | Pushkino 35/10 | 2,5+2,5 | 0.44 | 0.04 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 162 | Pushkino 35/10 | 2,5+2,5 | 0 | 0.44 | 0.04 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
163 | Yartsevo 1 110/10 | 40+40 | 13.94 | 5.34 | 120 | 8.6 | 0 | 42 | 33.4 | 33.4 | opened | 163 | Yartsevo 1 110/10 | 40+40 | 3.85 | 17.79 | 5.34 | 120 | 12.45 | 0 | 42 | 29.55 | 29.55 | opened
164 | Yartsevo 2 110/10 | 16+16 | 12 | 0.75 | 120 | 11.25 | 0 | 16.8 | 5.55 | 5.55 | opened | 164 | Yartsevo 2 110/10 | 16+16 | 4.37 | 16.37 | 0.75 | 120 | 15.62 | 0 | 16.8 | 1.18 | 1.18 | opened
165 | Saprykino 110/35/10 | 6,3+6,3 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | opened | 165 | Saprykino 110/35/10 | 6,3+6,3 | 0 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.97 | 0.4 | 120 | 0.57 | 0 | 6.615 | 6.045
166 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.58 | 0 | 120 | 2.58 | 0 | 6.615 | 4.035 | 4.035 | opened | 166 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.69 | 3.27 | 0 | 120 | 3.27 | 0 | 6.615 | 3.345 | 3.345 | opened
167 | Egoryevo 35/10 | 6,3+6,3 | 4.55 | 0 | 120 | 4.55 | 0 | 6.615 | 2.065 | 2.065 | opened | 167 | Egoryevo 35/10 | 6,3+6,3 | 0 | 4.55 | 0 | 120 | 4.55 | 0 | 6.615 | 2.065 | 2.065 | opened
168 | Shalomino 35/10 | 1,6+2,5 | 0.75 | 0.13 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 168 | Shalomino 35/10 | 1,6+2,5 | 0.11 | 0.86 | 0.13 | 120 | 0.73 | 0 | 1.68 | 0.95 | 0.95 | opened
169 | Roslavl 110/35/6 | 25+40 | 22.72 | 1.4 | 120 | 21.32 | 0 | 26.25 | 4.93 | 4.93 | opened | 169 | Roslavl 110/35/6 | 25+40 | 0.61 | 23.33 | 1.4 | 120 | 21.93 | 0 | 26.25 | 4.32 | 4.32 | opened
| Nom. capacity MV, МVА | 25+40 | 9.05 | 1.4 |  | 7.65 | 0 | 26.25 | 18.6 |  |  |  | Nom. capacity MV, МVА | 25+40 | 0 | 9.05 | 1.4 |  | 7.65 | 0 | 26.25 | 18.6
| Nom. сapacity LV, МVА | 25+40 | 13.67 | 0 | 120 | 13.67 | 0 | 26.25 | 12.58 |  |  |  | Nom. capacity LV, МVА | 25+40 | 0.61 | 14.28 | 0 | 120 | 14.28 | 0 | 26.25 | 11.97
170 | Meet processing plant 35/6 | 6,3+6,3 | 0.73 | 0 | 120 | 0.73 | 0 | 6.615 | 5.885 | 5.885 | opened | 170 | Meet processing plant 35/6 | 6,3+6,3 | 0 | 0.73 | 0 | 120 | 0.73 | 0 | 6.615 | 5.885 | 5.885 | opened
171 | Perenka 35/10 | 4+4 | 0.37 | 0 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened | 171 | Perenka 35/10 | 4+4 | 0 | 0.37 | 0 | 120 | 0.37 | 0 | 4.2 | 3.83 | 3.83 | opened
172 | Khoroshevo 35/10 | 2,5+4 | 1.31 | 0 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened | 172 | Khoroshevo 35/10 | 2,5+4 | 0 | 1.31 | 0 | 120 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened
173 | Lipovka 35/10 | 2,5+2,5 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened | 173 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.51 | 0 | 120 | 0.51 | 0 | 2.625 | 2.115 | 2.115 | opened
174 | Kirilly 35/10 | 2,5+2,5 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 174 | Kirilly 35/10 | 2,5+2,5 | 0 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
175 | Desnogorsk 110/35/10 | 25+25 | 19.5 | 3.53 | 120 | 15.97 | 0 | 26.25 | 10.28 | 10.28 | opened | 175 | Desnogorsk 110/35/10 | 25+25 | 6.56 | 26.06 | 3.53 | 120 | 22.53 | 0 | 26.25 | 3.72 | 3.72 | opened
| Nom. capacity MV, МVА | 25+25 | 3.53 | 3.53 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0 | 3.53 | 3.53 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacidty LV, МVА | 25+25 | 15.97 | 0 | 120 | 15.97 | 0 | 26.25 | 10.28 |  |  |  | Nom. capacity LV, МVА | 25+25 | 6.56 | 22.53 | 0 | 120 | 22.53 | 0 | 26.25 | 3.72
176 | Ekimovichi 35/10 | 4+4 | 2.61 | 0.24 | 120 | 2.37 | 0 | 4.2 | 1.83 | 1.83 | opened | 176 | Ekimovichi 35/10 | 4+4 | 0 | 2.61 | 0.24 | 120 | 2.37 | 0 | 4.2 | 1.83 | 1.83 | opened
177 | Ivanovskaya 35/10 | 2,5+2,5 | 0.45 | 0.07 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened | 177 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.45 | 0.07 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | opened
178 | Kokhany 35/10 | 1,6+1,6 | 0.4 | 0.09 | 120 | 0.31 | 0 | 1.68 | 1.37 | 1.37 | opened | 178 | Kokhany 35/10 | 1,6+1,6 | 0 | 0.4 | 0.09 | 120 | 0.31 | 0 | 1.68 | 1.37 | 1.37 | opened
179 | Koski 35/10 | 4+4 | 0.92 | 0 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened | 179 | Koski 35/10 | 4+4 | 0 | 0.92 | 0 | 120 | 0.92 | 0 | 4.2 | 3.28 | 3.28 | opened
180 | Industrialnaya 110/35/6 | 16+16 | 4.85 | 0.51 | 120 | 4.34 | 0 | 16.8 | 12.46 | 4.565 | opened | 180 | Industrialnaya 110/35/6 | 16+16 | 10.93 | 15.78 | 0.51 | 120 | 15.27 | 0 | 16.8 | 1.53 | -4.035 | closed
| Nom. capacity MV, МVА | 16,3+5,3 | 0.51 | 0.51 |  | 0 | 1 | 5.565 | 4.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0 | 0.51 | 0.51 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 4.34 | 0 | 120 | 4.34 | 2 | 11.235 | 4.895 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 10.93 | 15.27 | 0 | 120 | 15.27 | 0 | 11.235 | -4.035
181 | Astapkovichi 35/10 | 2,5+2,5 | 0.74 | 0 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened | 181 | Astapkovichi 35/10 | 2,5+2,5 | 0 | 0.74 | 0 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened
182 | Barsuki 110/35/10 | 6,3+6,3 | 0.87 | 0.55 | 120 | 0.32 | 0 | 6.615 | 6.295 | 6.295 | opened | 182 | Astapkovichi 35/10 | 6,3+6,3 | 0 | 0.87 | 0.55 | 120 | 0.32 | 0 | 6.615 | 6.295 | 6.295 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.55 | 0.55 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.55 | 0.55 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.32 | 0 | 120 | 0.32 | 0 | 6.615 | 6.295 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.32 | 0 | 120 | 0.32 | 0 | 6.615 | 6.295
183 | Bogdanovo 35/10 | 4+4 | 0.41 | 0 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened | 183 | Bogdanovo 35/10 | 4+4 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened
184 | Prigorye 110/35/10 | 10+2,5 | 1.08 | 0.53 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened | 184 | Prigorye 110/35/10 | 10+2,5 | 0 | 1.08 | 0.53 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | opened
| Nom. capacity MV, МVА | 10+2,5 | 0.53 | 0.53 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0 | 0.53 | 0.53 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.55 | 0 | 120 | 0.55 | 0 | 2.625 | 2.075 |  |  |  | Nom. capacity LV, МVА | 10+2,5 | 0 | 0.55 | 0 | 120 | 0.55 | 0 | 2.625 | 2.075
185 | Bekhovo 35/10 | 2,5+2,5 | 0.34 | 0 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened | 185 | Bekhovo 35/10 | 2,5+2,5 | 0 | 0.34 | 0 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened
186 | Pochinok 110/35/10 | 10+16 | 7.46 | 1.53 | 120 | 5.93 | 0 | 10.5 | 4.57 | 4.57 | opened | 186 | Pochinok 110/35/10 | 10+16 | 1.26 | 8.72 | 1.53 | 120 | 7.19 | 0 | 10.5 | 3.31 | 3.31 | opened
| Nom. capacidty MV, МVА | 10+16 | 2.73 | 1.45 |  | 1.28 | 0 | 10.5 | 9.22 |  |  |  | Nom. capacity MV, МVА | 10+16 | 1.02 | 3.75 | 1.45 |  | 2.3 | 0 | 10.5 | 8.2
| Nom. capacity LV, МVА | 10+16 | 4.73 | 0.08 | 120 | 4.65 | 0 | 10.5 | 5.85 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.24 | 4.97 | 0.08 | 120 | 4.89 | 0 | 10.5 | 5.61
187 | Divinskaya 35/10 | 4+4 | 1.41 | 0.17 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened | 187 | Divinskaya 35/10 | 4+4 | 0 | 1.41 | 0.17 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened
188 | Shatalovo 35/10 | 2,5+2,5 | 1.95 | 0 | 120 | 1.95 | 0 | 2.625 | 0.675 | 0.675 | opened | 188 | Shatalovo 35/10 | 2,5+2,5 | 0.55 | 2.5 | 0 | 120 | 2.5 | 0 | 2.625 | 0.125 | 0.125 | opened
189 | Panskaya 35/10 | 6,3+6,3 | 0.95 | 0 | 120 | 0.95 | 0 | 6.615 | 5.665 | 5.665 | opened | 189 | Panskaya 35/10 | 6,3+6,3 | 0.47 | 1.42 | 0 | 120 | 1.42 | 0 | 6.615 | 5.195 | 5.195 | opened
190 | Stodolishche 110/35/10 | 6,3+6,3 | 2.98 | 1.65 | 120 | 1.33 | 0 | 6.615 | 5.285 | 5.285 | opened | 190 | Stodolishche 110/35/10 | 6,3+6,3 | 2.47 | 5.45 | 1.65 | 120 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.2 | 1.2 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 1.2 | 1.2 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.78 | 0.45 | 120 | 1.33 | 0 | 6.615 | 5.285 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.47 | 4.25 | 0.45 | 120 | 3.8 | 0 | 6.615 | 2.815
191 | Belik 35/10 | 2,5+2,5 | 0.14 | 0.33 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 191 | Belik 35/10 | 2,5+2,5 | 0 | 0.14 | 0.33 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened
192 | Pervomayskaya 35/10 | 4+4 | 1.24 | 0 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened | 192 | Pervomayskaya 35/10 | 4+4 | 0 | 1.24 | 0 | 120 | 1.24 | 0 | 4.2 | 2.96 | 2.96 | opened
193 | Vaskovo 110/35/10 | 6,3+6,3 | 2.53 | 2.07 | 120 | 0.46 | 0 | 6.615 | 6.155 | 6.155 | opened | 193 | Vaskovo 110/35/10 | 6,3+6,3 | 0.84 | 3.37 | 3.12 | 120 | 0.25 | 0 | 6.615 | 6.365 | 6.365 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 2.07 | 1.69 |  | 0.38 | 0 | 6.615 | 6.235 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.84 | 2.91 | 2.91 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.46 | 0.21 | 120 | 0.25 | 0 | 6.615 | 6.365 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.46 | 0.21 | 120 | 0.25 | 0 | 6.615 | 6.365
194 | Strigino 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 194 | Strigino 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
195 | Komintern 35/10 | 2,5+2,5 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened | 195 | Komintern 35/10 | 2,5+2,5 | 0 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
196 | Monastyrshchina 110/35/10 | 10+10 | 5.86 | 0.59 | 120 | 5.27 | 0 | 10.5 | 5.23 | 5.23 | opened | 196 | Monastyrshchina 110/35/10 | 10+10 | 0 | 5.86 | 0.59 | 120 | 5.27 | 0 | 10.5 | 5.23 | 5.23 | opened
| Nom. Capacity MV, МVА | 10+10 | 2.31 | 0.59 |  | 1.72 | 0 | 10.5 | 8.78 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 2.31 | 0.59 |  | 1.72 | 0 | 10.5 | 8.78
| Nom. capacity LV, МVА | 10+10 | 3.55 | 0 | 120 | 3.55 | 0 | 10.5 | 6.95 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 3.55 | 0 | 120 | 3.55 | 0 | 10.5 | 6.95
197 | N.Mikhailov 35/10 | 4+4 | 0.96 | 0 | 120 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | opened | 197 | N.Mikhailov 35/10 | 4+4 | 0 | 0.96 | 0 | 120 | 0.96 | 0 | 4.2 | 3.24 | 3.24 | opened
198 | Tatarsk 35/10 | 3,2+4 | 1.14 | 0 | 120 | 1.14 | 0 | 3.36 | 2.22 | 2.22 | opened | 198 | Tatarsk 35/10 | 3,2+4 | 0 | 1.14 | 0 | 120 | 1.14 | 0 | 3.36 | 2.22 | 2.22 | opened
199 | Turki 35/10 | 1,6+1,6 | 0.2 | 0 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 199 | Turki 35/10 | 1,6+1,6 | 0 | 0.2 | 0 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
200 | Sozh 35/10 | 4+4 | 0.35 | 0 | 120 | 0.35 | 0 | 4.2 | 3.85 | 3.85 | opened | 200 | Sozh 35/10 | 4+4 | 0 | 0.35 | 0 | 120 | 0.35 | 0 | 4.2 | 3.85 | 3.85 | opened
201 | Khislavichi 110/35/10 | 16+16 | 3.43 | 1.51 | 120 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened | 201 | Khislavichi 110/35/10 | 16+16 | 0.93 | 4.36 | 1.51 | 120 | 2.85 | 0 | 16.8 | 13.95 | 13.95 | opened
| Nom. capacity MV, МVА | 16+16 | 1.33 | 1.33 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0 | 1.33 | 1.33 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.1 | 0.18 | 120 | 1.92 | 0 | 16.8 | 14.88 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.93 | 3.03 | 0.18 | 120 | 2.85 | 0 | 16.8 | 13.95
202 | Gorodishche 35/10 | 1,8+2,5 | 0.99 | 0 | 120 | 0.99 | 0 | 1.89 | 0.9 | 0.9 | opened | 202 | Gorodishche 35/10 | 1,8+2,5 | 0 | 0.99 | 0 | 120 | 0.99 | 0 | 1.89 | 0.9 | 0.9 | opened
203 | Komarovka 35/10 | 4+4 | 0.31 | 0.02 | 120 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened | 203 | Komarovka 35/10 | 4+4 | 0 | 0.31 | 0.02 | 120 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
204 | Cherepovo 35/10 | 2,5+2,5 | 0.75 | 0 | 120 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened | 204 | Cherepovo 35/10 | 2,5+2,5 | 0 | 0.75 | 0 | 120 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened
205 | Studenets 35/10 | 1,6+2,5 | 0.37 | 0.01 | 120 | 0.36 | 0 | 1.68 | 1.32 | 1.32 | opened | 205 | Studenets 35/10 | 1,6+2,5 | 0 | 0.37 | 0.01 | 120 | 0.36 | 0 | 1.68 | 1.32 | 1.32 | opened
206 | Shumyachi 110/35/10 | 10+10 | 5.41 | 3.46 | 120 | 1.95 | 0 | 10.5 | 8.55 | 8.55 | opened | 206 | Shumyachi 110/35/10 | 10+10 | 0 | 5.41 | 3.46 | 120 | 1.95 | 0 | 10.5 | 8.55 | 8.55 | opened
| Nom. capacity MV, МVА | 10+10 | 2.82 | 2.82 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 2.82 | 2.82 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.59 | 0.64 | 120 | 1.95 | 0 | 10.5 | 8.55 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 2.59 | 0.64 | 120 | 1.95 | 0 | 10.5 | 8.55
207 | Ershichi 110/35/10 | 10+10 | 2.17 | 0.68 | 120 | 1.49 | 0 | 10.5 | 9.01 | 8.89 | opened | 207 | Ershichi 110/35/10 | 10+10 | 0.12 | 2.29 | 0.68 | 120 | 1.61 | 0 | 10.5 | 8.89 | 8.77 | opened
| Nom. capacity MV, МVА | 10+10 | 0.34 | 0.34 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.34 | 0.34 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.83 | 0.22 | 120 | 1.61 | 0 | 10.5 | 8.89 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.12 | 1.95 | 0.22 | 120 | 1.73 | 0 | 10.5 | 8.77
208 | Rukhan 35/10 | 2,5+2,5 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened | 208 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.29 | 0 | 120 | 0.29 | 0 | 2.625 | 2.335 | 2.335 | opened
209 | Vyazma 1 110/35/10 | 40+40 | 34.49 | 11.83 | 120 | 22.66 | 0 | 42 | 19.34 | 19.34 | opened | 209 | Vyazma 1 110/35/10 | 40+40 | 19.15 | 53.64 | 15.76 | 120 | 37.88 | 0 | 42 | 4.12 | 4.12 | opened
| Nom. capacity MV, МVА | 40+40 | 22.28 | 11.27 | 121 | 11.01 | 0 | 42 | 30.99 |  |  |  | Nom. capacity MV, МVА | 40+40 | 10.3 | 32.58 | 15.2 |  | 17.38 | 0 | 42 | 24.62
| Nom. capacity LV, МVА | 40+40 | 12.21 | 0.56 | 122 | 11.65 | 0 | 42 | 30.35 |  |  |  | Nom. capacity LV, МVА | 40+40 | 8.85 | 21.06 | 0.56 | 120 | 20.5 | 0 | 42 | 21.5
210 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2 | 0 | 120 | 2 | 0 | 6.615 | 4.615 | 4.615 | opened | 210 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 0.12 | 2.12 | 0 | 120 | 2.12 | 0 | 6.615 | 4.495 | 4.495 | opened
211 | Khmelita 35/10 | 1,6+2,5 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened | 211 | Khmelita 35/10 | 1,6+2,5 | 0 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened
212 | Isakovo 35/10 | 2,5+4 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 212 | Isakovo 35/10 | 2,5+4 | 0 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
213 | Rizskoe 35/10 | 2,5+2,5 | 0.67 | 0.01 | 120 | 0.66 | 0 | 2.625 | 1.965 | 1.965 | opened | 213 | Rizskoe 35/10 | 2,5+2,5 | 0.18 | 0.85 | 0.01 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
214 | Beryozka 35/10 | 4+4 | 0.61 | 0 | 120 | 0.61 | 0 | 4.2 | 3.59 | 3.59 | opened | 214 | Beryozka 35/10 | 4+4 | 3.93 | 4.54 | 0 | 120 | 4.54 | 0 | 4.2 | -0.34 | -0.34 | closed
215 | Shimanovo 35/10 | 1,8+4 | 0.51 | 0.32 | 120 | 0.19 | 0 | 1.89 | 1.7 | 1.7 | opened | 215 | Shimanovo 35/10 | 1,8+4 | 0 | 0.51 | 0.32 | 120 | 0.19 | 0 | 1.89 | 1.7 | 1.7 | opened
216 | Kaydakovo 35/10 | 4+4 | 1.17 | 0.2 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | opened | 216 | Kaydakovo 35/10 | 4+4 | 0 | 1.17 | 0.2 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | opened
217 | Flour mill 35/10 | 10+10 | 6.76 | 0.13 | 120 | 6.63 | 0 | 10.5 | 3.87 | 3.87 | opened | 217 | Flour mill 35/10 | 10+10 | 6.03 | 12.79 | 0.13 | 120 | 12.66 | 0 | 10.5 | -2.16 | -2.16 | closed
218 | Kikino 35/10 | 2,5+2,5 | 0.42 | 0.41 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 218 | Kikino 35/10 | 2,5+2,5 | 0.05 | 0.47 | 0.41 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
219 | Vyazma 2 110/10 | 16+16 | 13.39 | 0 | 120 | 13.39 | 0 | 16.8 | 3.41 | 3.41 | opened | 219 | Vyazma 2 110/10 | 16+16 | 4.47 | 17.86 | 0 | 120 | 17.86 | 0 | 16.8 | -1.06 | -1.06 | closed
220 | Tumanovo 110/35/10 | 6,3+6,3 | 2.32 | 0.73 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | opened | 220 | Tumanovo 110/35/10 | 6,3+6,3 | 0.31 | 2.63 | 0.73 | 120 | 1.9 | 0 | 6.615 | 4.715 | 4.715 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.82 | 0.39 |  | 0.43 | 0 | 6.615 | 6.185 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.82 | 0.39 |  | 0.43 | 0 | 6.615 | 6.185
| Nom. capacity LV, МVА | 6,3+6,3 | 1.5 | 0.34 | 120 | 1.16 | 0 | 6.615 | 5.455 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.31 | 1.81 | 0.34 | 120 | 1.47 | 0 | 6.615 | 5.145
221 | Rossiya 110/35/10 | 10+16 | 2.46 | 1.7 | 120 | 0.76 | 0 | 10.5 | 9.74 | 9.74 | opened | 221 | Rossiya 110/35/10 | 10+16 | 4.68 | 7.14 | 5.81 | 120 | 1.33 | 0 | 10.5 | 9.17 | 9.17 | opened
| Nom. capacity MV, МVА | 10+16 | 1.38 | 1.38 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 4.11 | 5.49 | 5.49 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.08 | 0.32 | 120 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.57 | 1.65 | 0.32 | 120 | 1.33 | 0 | 10.5 | 9.17
222 | Semlevo 35/10 | 2,5+4 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened | 222 | Semlevo 35/10 | 2,5+4 | 0 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
223 | Artyomovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 223 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
224 | Gagarin 110/35/10 | 25+25 | 25 | 4.78 | 120 | 20.22 | 0 | 26.25 | 6.03 | 6.03 | opened | 224 | Gagarin 110/35/10 | 25+25 | 8.57 | 33.57 | 6.82 | 120 | 26.75 | 0 | 26.25 | -0.5 | -0.5 | closed
| Nom. capacity MV, МVА | 25+25 | 4.95 | 3.06 |  | 1.89 | 0 | 26.25 | 24.36 |  |  |  | Nom. capacity MV, МVА | 25+25 | 2.74 | 7.69 | 5.1 |  | 2.59 | 0 | 26.25 | 23.66
| Nom. capacity LV, МVА | 25+25 | 20.05 | 1.72 | 120 | 18.33 | 0 | 26.25 | 7.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 5.83 | 25.88 | 1.72 | 120 | 24.16 | 0 | 26.25 | 2.09
225 | Rodomanovo 35/10 | 4+4 | 1.02 | 1.18 | 120 | -0.16 | 0 | 4.2 | 4.36 | 4.36 | opened | 225 | Rodomanovo 35/10 | 4+4 | 0 | 1.02 | 1.18 | 120 | -0.16 | 0 | 4.2 | 4.36 | 4.36 | opened
226 | Klushino 35/10 | 4+4 | 0.82 | 0.57 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened | 226 | Klushino 35/10 | 4+4 | 0.13 | 0.95 | 0.57 | 120 | 0.38 | 0 | 4.2 | 3.82 | 3.82 | opened
227 | Ivino 35/10 | 1,6+1,6 | 0.14 | 0 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 227 | Ivino 35/10 | 1,6+1,6 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
228 | Karmanovo 35/10 | 4+4 | 3.29 | 0.21 | 120 | 3.08 | 0 | 4.2 | 1.12 | 1.12 | opened | 228 | Karmanovo 35/10 | 4+4 | 1.03 | 4.32 | 0.21 | 120 | 4.11 | 0 | 4.2 | 0.09 | 0.09 | opened
229 | Sverchkovo 35/10 | 2,5+2,5 | 1.46 | 0.75 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened | 229 | Sverchkovo 35/10 | 2,5+2,5 | 0.46 | 1.92 | 0.75 | 120 | 1.17 | 0 | 2.625 | 1.455 | 1.455 | opened
230 | Lesnaya 35/10 | 4+4 | 1.01 | 0 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened | 230 | Lesnaya 35/10 | 4+4 | 0 | 1.01 | 0 | 120 | 1.01 | 0 | 4.2 | 3.19 | 3.19 | opened
231 | Tesovo 35/10 | 1,6+2,5 | 0.49 | 0.48 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 231 | Tesovo 35/10 | 1,6+2,5 | 0.44 | 0.93 | 0.48 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
232 | Svetotekhnika 110/10 | 16+16 | 4.05 | 0.97 | 120 | 3.08 | 0 | 16.8 | 13.72 | 13.72 | opened | 232 | Svetotekhnika 110/10 | 16+16 | 4.7 | 8.75 | 0.97 | 120 | 7.78 | 0 | 16.8 | 9.02 | 9.02 | opened
233 | Mishino 110/35/10 | 10+10 | 2.83 | 2.2 | 120 | 0.63 | 0 | 10.5 | 9.87 | 9.87 | opened | 233 | Mishino 110/35/10 | 10+10 | 0.63 | 3.46 | 2.76 | 120 | 0.7 | 0 | 10.5 | 9.8 | 9.78 | opened
| Nom. capacity MV, МVА | 10+10 | 1.66 | 1.66 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.46 | 2.12 | 2.12 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.17 | 0.64 | 120 | 0.53 | 0 | 10.5 | 9.97 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.19 | 1.36 | 0.64 | 120 | 0.72 | 0 | 10.5 | 9.78
234 | Nikolskoe 35/10 | 6,3+6,3 | 1.58 | 0.59 | 120 | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened | 234 | Nikolskoe 35/10 | 6,3+6,3 | 0 | 1.58 | 0.59 | 120 | 0.99 | 0 | 6.615 | 5.625 | 5.625 | opened
235 | Bekrino 35/10 | 2,5+2,5 | 0.53 | 0.09 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened | 235 | Bekrino 35/10 | 2,5+2,5 | 0 | 0.53 | 0.09 | 120 | 0.44 | 0 | 2.625 | 2.185 | 2.185 | opened
236 | Trubnaya 110/10 | 25+25 | 5.22 | 1.57 | 120 | 3.65 | 0 | 26.25 | 22.6 | 22.6 | opened | 236 | Trubnaya 110/10 | 25+25 | 1.84 | 7.06 | 1.57 | 120 | 5.49 | 0 | 26.25 | 20.76 | 20.76 | opened
237 | Temkino 110/35/10 | 10+10 | 3.23 | 0.71 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | opened | 237 | Temkino 110/35/10 | 10+10 | 1.31 | 4.54 | 0.97 | 120 | 3.57 | 0 | 10.5 | 6.93 | 6.93 | opened
| Nom. capacity MV, МVА | 10+10 | 0.46 | 0.46 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.26 | 0.72 | 0.72 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.77 | 0.25 | 120 | 2.52 | 0 | 10.5 | 7.98 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.05 | 3.82 | 0.25 | 120 | 3.57 | 0 | 10.5 | 6.93
238 | Narytka 35/10 | 2,5+2,5 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 238 | Narytka 35/10 | 2,5+2,5 | 0 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
239 | Novodugino 110/35/10 | 10+10 | 4.31 | 2.03 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.22 | opened | 239 | Novodugino 110/35/10 | 10+10 | 0.34 | 4.65 | 2.37 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.22 | opened
| Nom. capacity MV, МVА | 10+10 | 1.55 | 1.55 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.34 | 1.89 | 1.89 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.76 | 0.48 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0 | 2.76 | 0.48 | 120 | 2.28 | 0 | 10.5 | 8.22
240 | Khotkovo 35/10 | 4+4 | 0.74 | 0.26 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened | 240 | Khotkovo 35/10 | 4+4 | 0 | 0.74 | 0.26 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened
241 | Dneprovsk 110/35/10 | 10+10 | 2.89 | 2.77 | 120 | 0.12 | 0 | 10.5 | 10.38 | 10.38 | opened | 241 | Khotkovo 35/10 | 10+10 | 0.89 | 3.78 | 3.07 | 120 | 0.71 | 0 | 10.5 | 9.79 | 9.79 | opened
| Nom. capacity MV, МVА | 10+10 | 2.61 | 2.61 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.3 | 2.91 | 2.91 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.28 | 0.16 | 120 | 0.12 | 0 | 10.5 | 10.38 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.59 | 0.87 | 0.16 | 120 | 0.71 | 0 | 10.5 | 9.79
242 | Lipetsy 35/10 | 2,5+2,5 | 0.36 | 0.75 | 120 | -0.39 | 0 | 2.625 | 3.015 | 3.015 | opened | 242 | Lipetsy 35/10 | 2,5+2,5 | 0 | 0.36 | 0.75 | 120 | -0.39 | 0 | 2.625 | 3.015 | 3.015 | opened
243 | Sychevka 110/35/10 | 16+25 | 8.15 | 1.47 | 120 | 6.68 | 0 | 16.8 | 10.12 | 10.12 | opened | 243 | Sychevka 110/35/10 | 16+25 | 4.47 | 12.62 | 1.78 | 120 | 10.84 | 0 | 16.8 | 5.96 | 5.96 | opened
| Nom. capacity MV, МVА | 16+25 | 3.11 | 0.7 |  | 2.41 | 0 | 16.8 | 14.39 |  |  |  | Nom. capacity MV, МVА | 16+25 | 2.95 | 6.06 | 1.01 |  | 5.05 | 0 | 16.8 | 11.75
| Nom. capacfity LV, МVА | 16+25 | 5.04 | 0.77 | 120 | 4.27 | 0 | 16.8 | 12.53 |  |  |  | Nom. capacity LV, МVА | 16+25 | 1.52 | 6.56 | 0.77 | 120 | 5.79 | 0 | 16.8 | 11.01
244 | Sutormino 35/10 | 1,8+4 | 0.22 | 0.06 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened | 244 | Sutormino 35/10 | 1,8+4 | 0 | 0.22 | 0.06 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened
245 | Karavaevo 35/10 | 4+4 | 0.77 | 0.29 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | opened | 245 | Karavaevo 35/10 | 4+4 | 0.54 | 1.31 | 0.29 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened
246 | Lukino 35/10 | 4+1,6 | 0.01 | 0.51 | 120 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened | 246 | Lukino 35/10 | 4+1,6 | 0 | 0.01 | 0.51 | 120 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened
247 | Subbotniki 110/10 | 6,3+6,3 | 0.77 | 0 | 120 | 0.77 | 0 | 6.615 | 5.845 | 5.845 | opened | 247 | Subbotniki 110/10 | 6,3+6,3 | 0.17 | 0.94 | 0 | 120 | 0.94 | 0 | 6.615 | 5.675 | 5.675 | opened
248 | Ugra 110/10 | 6,3+6,3 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675 | 3.675 | opened | 248 | Ugra 110/10 | 6,3+6,3 | 0 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675 | 3.675 | opened
249 | Znamenka 110/35/10 | 10+10 | 2.13 | 1.19 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.56 | opened | 249 | Znamenka 110/35/10 | 10+10 | 2.42 | 4.55 | 1.19 | 120 | 3.36 | 0 | 10.5 | 7.14 | 7.14 | opened
| Nom. capacity MV, МVА | 10+10 | 1.16 | 1.16 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 1.16 | 1.16 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.97 | 0.03 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.42 | 3.39 | 0.03 | 120 | 3.36 | 0 | 10.5 | 7.14
250 | Losmino 35/10 | 2,5+2,5 | 0.58 | 0.4 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened | 250 | Losmino 35/10 | 2,5+2,5 | 0 | 0.58 | 0.4 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
251 | Vskhody 110/35/10 | 6,3+6,3 | 1.42 | 0.04 | 120 | 1.38 | 0 | 6.615 | 5.235 | 5.235 | opened | 251 | Vskhody 110/35/10 | 6,3+6,3 | 0 | 1.42 | 0.04 | 120 | 1.38 | 0 | 6.615 | 5.235 | 5.235 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.81 | 0.03 |  | 0.78 | 0 | 6.615 | 5.835 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.81 | 0.03 | 120 | 0.78 | 0 | 6.615 | 5.835
| Nom. capacity LV, МVА | 6,3+6,3 | 0.61 | 0.01 | 120 | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.61 | 0.01 | 120 | 0.6 | 0 | 6.615 | 6.015
| Total: | 3150.6 | 1137.993 | [8 empty] | 2: Total:; 3: 3150.6; 4: 516.17
| deficit | [8 empty] | -5.23 |  | 2: deficit; Мin. 12: -37.915
| proficit | [8 empty] | 1033.912 |  | 2: proficit; Мin. 12: 823.427

## брянск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load of main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | Lopandino | 6.3 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 1 | Lopandino | 6.3 |  | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
2 | Nerussa | 16 | 2.577 | 2.6 | 24 hours | -0.023 | 0 | 16.8 | 16.823 | 15.3 | opened | 2 | Nerussa | 16 |  | 2.577 | 2.6 | 24 hours | -0.023 | 0 | 16.8 | 16.823 | 15.3 | opened
| Nom. capacity MV, MVA | 16 | 1.5 | 1.5 | 24 hours | 0 | 0 | 16.8 | 15.3 |  |  |  | Nom. capacity MV, MVA | 16 |  | 1.5 | 1.5 | 24 hours | 0 | 0 | 16.8 | 15.3
| Nom. capacity LV, MVA | 16 | 1.077 | 1.1 | 24 hours | -0.023 | 0 | 16.8 | 16.823 |  |  |  | Nom. capacity LV, MVA | 16 |  | 1.077 | 1.1 | 24 hours | -0.023 | 0 | 16.8 | 16.823
3 | Svenskaya | 6.3 | 1.5 | 1.5 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 3 | Svenskaya | 6.3 |  | 1.5 | 1.5 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
4 | Khmelevskaya | 6.3 | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 4 | Khmelevskaya | 6.3 |  | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
5 | Energoremont | 10 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 5 | Energoremont | 10 |  | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
1 | Naytopovichi 8NA | 10 | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 1 | Naytopovichi 8NA | 10 |  | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
2 | Glybochka | 2.5 | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 2 | Glybochka | 2.5 |  | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
3 | Desyatukha | 6.3 | 1.187 | 1.187 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 3 | Desyatukha | 6.3 |  | 1.187 | 1.187 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
4 | Ivaytenki | 6.3 | 1.588 | 1.6 | 24 hours | -0.012 | 0 | 6.615 | 6.627 | 5.698 | opened | 4 | Ivaytenki | 6.3 | 0.006 | 1.594 | 1.6 | 24 hours | -0.006 | 0 | 6.615 | 6.621 | 5.698 | opened
| Nom. capacity MV, MVA | 6.3 | 0.917 | 0.9 | 24 hours | 0.017 | 0 | 6.615 | 5.698 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.917 | 0.9 | 24 hours | 0.017 | 0 | 6.615 | 5.698
| Nom. capacity LV, MVA | 6.3 | 0.671 | 0.7 | 24 hours | -0.029 | 0 | 6.615 | 6.644 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.006 | 0.677 | 0.7 | 24 hours | -0.023 | 0 | 6.615 | 6.638
5 | Lugovaya | 16 | 4.718 | 4.7 | 24 hours | 0.018 | 0 | 16.8 | 16.782 | 12.971 | opened | 5 | Lugovaya | 16 |  | 4.718 | 4.7 | 24 hours | 0.018 | 0 | 16.8 | 16.782 | 12.971 | opened
| Nom. capacity MV, MVA | 16 | 3.829 | 3.8 | 24 hours | 0.029 | 0 | 16.8 | 12.971 |  |  |  | Nom. capacity MV, MVA | 16 |  | 3.829 | 3.8 | 24 hours | 0.029 | 0 | 16.8 | 12.971
| Nom. capacity LV, MVA | 16 | 0.889 | 0.9 | 24 hours | -0.011 | 0 | 16.8 | 16.811 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.889 | 0.9 | 24 hours | -0.011 | 0 | 16.8 | 16.811
6 | Plyuskovo | 6.3 | 2.115 | 2.1 | 24 hours | 0.015 | 0 | 6.615 | 6.6 | 5.47 | opened | 6 | Plyuskovo | 6.3 |  | 2.115 | 2.1 | 24 hours | 0.015 | 0 | 6.615 | 6.6 | 5.47 | opened
| Nom. capacity MV, MVA | 6.3 | 1.145 | 1.1 | 24 hours | 0.045 | 0 | 6.615 | 5.47 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1.145 | 1.1 | 24 hours | 0.045 | 0 | 6.615 | 5.47
| Nom. capacity LV, MVA | 6.3 | 0.97 | 1 | 24 hours | -0.03 | 0 | 6.615 | 6.645 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.97 | 1 | 24 hours | -0.03 | 0 | 6.615 | 6.645
7 | Aleshinskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 7 | Aleshinskaya | 2.5 |  | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
8 | Altukhovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 8 | Altukhovskaya | 1.6 |  | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
9 | Domashovo | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 9 | Domashovo | 2.5 |  | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
10 | Dronovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 10 | Dronovskaya | 2.5 |  | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
11 | Kokorevskaya | 4 | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened | 11 | Kokorevskaya | 4 |  | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened
12 | Malopolpinskaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 12 | Malopolpinskaya | 4 |  | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
13 | Morachevskaya | 1.6 | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 | opened | 13 | Morachevskaya | 1.6 |  | 0.2 | 0.2 | 24 hours | 0.2 | 0 | 0.2 | 0 | 0 | opened
14 | Saltanovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 14 | Saltanovskaya | 2.5 |  | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
15 | Svetovo | 2.5 | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 | opened | 15 | Svetovo | 2.5 |  | 0.3 | 0.3 | 24 hours | 0.3 | 0 | 0.3 | 0 | 0 | opened
16 | Seshcha 10 kv | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 16 | Seshcha 10 kv | 2.5 |  | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
17 | Sovkhoznaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 17 | Sovkhoznaya | 4 |  | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
18 | Strachevskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 18 | Strachevskaya | 2.5 | 0.017 | 0.417 | 0.417 | 24 hours | 0.417 | 0 | 0.417 | 0 | 0 | opened
19 | Strashevichi | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 19 | Strashevichi | 4 |  | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
20 | Usozhskaya | 2.5 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened | 20 | Usozhskaya | 2.5 |  | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened
21 | Kharinovskaya | 1 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened | 21 | Kharinovskaya | 1 |  | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened
22 | Kharitonovskaya | 4 | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened | 22 | Kharitonovskaya | 4 |  | 0.7 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0 | 0 | opened
23 | Didovka | 2.5 | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened | 23 | Didovka | 2.5 |  | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened
24 | Molodkovo | 1 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 24 | Molodkovo | 1 |  | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
25 | Papsuevskaya | 2.5 | 0.283 | 0.283 | 24 hours | 0.283 | 0 | 0.283 | 0 | 0 | opened | 25 | Papsuevskaya | 2.5 |  | 0.283 | 0.283 | 24 hours | 0.283 | 0 | 0.283 | 0 | 0 | opened
26 | Radutinskaya | 1.6 | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened | 26 | Radutinskaya | 1.6 |  | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened
27 | Ushchepye 6 kv | 1.6 | 0.825 | 0.825 | 24 hours | 0.825 | 0 | 0.825 | 0 | 0 | opened | 27 | Ushchepye 6 kv | 1.6 |  | 0.825 | 0.825 | 24 hours | 0.825 | 0 | 0.825 | 0 | 0 | opened
28 | Ushchepye 10 kv | 1.6 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened | 28 | Ushchepye 10 kv | 1.6 |  | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened
29 | Yakovskaya | 2.5 | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened | 29 | Yakovskaya | 2.5 |  | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened
30 | Aksinino | 40+40 | 16.83 | 0 | 0 | 16.83 | 0 | 42 | 25.17 | 25.17 | opened | 30 | Aksinino | 40+40 |  | 16.83 | 0 | 0 | 16.83 | 0 | 42 | 25.17 | 25.17 | opened
| Nom. capacity MV, MVA | 40+40 | 14.45 | 0 | 0 | 14.45 | 0 | 42 | 27.55 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 14.45 | 0 | 0 | 14.45 | 0 | 42 | 27.55
| Nom. capacity LV, MVA | 40+40 | 2.38 | 0 | 0 | 2.38 | 0 | 42 | 39.62 |  |  |  | Nom. capacity LV, MVA | 40+40 |  | 2.38 | 0 | 0 | 2.38 | 0 | 42 | 39.62
31 | Airport | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 31 | Airport | 6,3+6,3 | 0.004 | 0.904 | 0 | 0 | 0.904 | 0 | 6.615 | 5.711 | 5.711 | opened
32 | Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed | 32 | Bezhitskaya | 25+40 |  | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed
33 | Water intake | 6,3+6,3 | 1.9 | 0 | 0 | 1.9 | 0 | 6.615 | 4.715 | 4.715 | opened | 33 | Water intake | 6,3+6,3 |  | 1.9 | 0 | 0 | 1.9 | 0 | 6.615 | 4.715 | 4.715 | opened
34 | Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed | 34 | Gorodishchenskaya | 16+16 | 0.226 | 25.786 | 1.5 | 12 hours | 24.286 | 0 | 16.8 | -7.486 | -7.486 | closed
35 | Dobrunskaya | 6,3+4 | 3.7 | 0 | 0 | 3.7 | 0 | 4.2 | 0.5 | 0.5 |  | 35 | Dobrunskaya | 6,3+4 | 0.484 | 4.184 | 0 | 0 | 4.184 | 0 | 4.2 | 0.016 | 0.016 | opened
36 | Dormashevskaya | 40+63 | 39.51 | 0 | 0 | 39.51 | 0 | 42 | 2.49 | 2.49 | opened | 36 | Dormashevskaya | 40+63 | 4.3 | 43.81 | 0 | 0 | 43.81 | 0 | 42 | -1.81 | -1.81 | closed
| Nom. capacity MV, MVA | 40+63 | 20.72 | 0 | 0 | 20.72 | 0 | 42 | 21.28 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 20.72 | 0 | 0 | 20.72 | 0 | 42 | 21.28
| Nom. capacity LV, MVA | 40+63 | 18.79 | 0 | 0 | 18.79 | 0 | 42 | 23.21 |  |  |  | Nom. capacity LV, MVA | 40+63 | 4.3 | 23.09 | 0 | 0 | 23.09 | 0 | 42 | 18.91
37 | Dubrovskaya | 16+16 | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened | 37 | Dubrovskaya | 16+16 |  | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened
| Nom. capacity MV, MVA | 16+16 | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33
| Nom. capacity MV, MVA | 16+16 | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9
38 | Dyatkovskaya | 25+25 | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -1.57 | -1.62 | closed | 38 | Dyatkovskaya | 25+25 |  | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -1.57 | -1.62 | closed
| Nom. capacity MV, MVA | 25+25 | 8.85 | 8.9 | 12 hours | -0.05 | 0 | 26.25 | 17.4 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 8.85 | 8.9 | 12 hours | -0.05 | 0 | 26.25 | 17.4
| Nom. capacity LV, MVA | 25+25 | 27.87 | 0 | 0 | 27.87 | 0 | 26.25 | -1.62 |  |  |  | Nom. capacity LV, MVA | 25+25 |  | 27.87 | 0 | 0 | 27.87 | 0 | 26.25 | -1.62
39 | Zhukovskaya | 16+25 | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | opened | 39 | Zhukovskaya | 16+25 |  | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | opened
| Nom. capacity MV, MVA | 16+25 | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8
| Nom. capacity LV, MVA | 16+25 | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1 |  |  |  | Nom. capacity LV, MVA | 16+25 |  | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1
40 | Zarechnaya | 10+10 | 5.92 | 0 | 0 | 5.92 | 0 | 10.5 | 4.58 | 4.58 | opened | 40 | Zarechnaya | 10+10 | 1.944 | 7.864 | 0 | 0 | 7.864 | 0 | 10.5 | 2.636 | 2.636 | opened
41 | Ivotskaya | 25+25 | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened | 41 | Ivotskaya | 25+25 |  | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened
| Nom. capacity MV, MVA | 25+25 | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89
| Nom. capacity LV, MVA | 25+25 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 |  | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | Kamvolnaya | 16+25 | 17.09 | 0 | 0 | 17.09 | 0 | 16.8 | -0.29 | -0.29 | closed | 42 | Kamvolnaya | 16+25 | 0.134 | 17.224 | 0 | 0 | 17.224 | 0 | 16.8 | -0.424 | -0.424 | closed
43 | Karachevskaya | 16+25 | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened | 43 | Karachevskaya | 16+25 |  | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened
44 | Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed | 44 | Karachizhskaya | 10+10 | 0.173 | 18.453 | 0 | 0 | 18.453 | 0 | 10.5 | -7.953 | -7.953 | yes
45 | Kletnyanskaya | 10+16 | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 45 | Kletnyanskaya | 10+16 |  | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened
| Nom. capacity MV, MVA | 10+16 | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6
| Nom. capacity LV, MVA | 10+16 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 |  |  |  | Nom. capacity LV, MVA | 10+16 |  | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3
46 | Komarichi | 16+16 | 9.89 | 3.7 | 6 hours | 6.19 | 0 | 16.8 | 10.61 | 10.61 | opened | 46 | Komarichi | 16+16 |  | 9.89 | 3.7 | 6 hours | 6.19 | 0 | 16.8 | 10.61 | 10.61 | opened
| Nom. capacity MV, MVA | 16+16 | 5 | 3.7 | 6 hours | 1.3 | 0 | 16.8 | 11.8 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5 | 3.7 | 6 hours | 1.3 | 0 | 16.8 | 11.8
| Nom. capacity LV, MVA | 16+16 | 4.89 | 0 | 0 | 4.89 | 0 | 16.8 | 11.91 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 4.89 | 0 | 0 | 4.89 | 0 | 16.8 | 11.91
47 | Letoshniki | 6,3+2,5 | 0.9 | 0 | 0 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | opened | 47 | Letoshniki | 6,3+2,5 |  | 0.9 | 0 | 0 | 0.9 | 0 | 2.625 | 1.725 | 1.725 | opened
48 | Mamonovskaya | 10+16 | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed | 48 | Mamonovskaya | 10+16 |  | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed
49 | Maritskaya | 10+16 | 5.23 | 4.5 | 6 hours | 0.73 | 0 | 10.5 | 9.77 | 5.97 | opened | 49 | Maritskaya | 10+16 |  | 5.23 | 4.5 | 6 hours | 0.73 | 0 | 10.5 | 9.77 | 5.97 | opened
| Nom. capacity MV, MVA | 10+16 | 4.53 | 4.5 | 6 hours | 0.03 | 0 | 10.5 | 5.97 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 4.53 | 4.5 | 6 hours | 0.03 | 0 | 10.5 | 5.97
| Nom. capacity LV, MVA | 10+16 | 0.7 | 0 | 0 | 0.7 | 0 | 10.5 | 9.8 |  |  |  | Nom. capacity LV, MVA | 10+16 |  | 0.7 | 0 | 0 | 0.7 | 0 | 10.5 | 9.8
50 | Michurinskaya | 6,3+10 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 | 4.315 | opened | 50 | Michurinskaya | 6,3+10 |  | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 | 4.315 | opened
51 | Molotinskaya | 6,3+6,3 | 2.4 | 0 | 0 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened | 51 | Molotinskaya | 6,3+6,3 |  | 2.4 | 0 | 0 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened
52 | Polpinskaya | 16+16 | 3.6 | 0 | 0 | 3.6 | 0 | 16.8 | 13.2 | 13.2 | opened | 52 | Polpinskaya | 16+16 |  | 3.6 | 0 | 0 | 3.6 | 0 | 16.8 | 13.2 | 13.2 | opened
53 | Sovetskaya | 16+16+25 | 49.27 | 0 | 0 | 49.27 | 0 | 33.6 | -15.67 | -15.67 | closed | 53 | Sovetskaya | 16+16+25+40 | 0.537 | 49.807 | 0 | 0 | 49.807 | 0 | 59.85 | 10.043 | 10.043 | opened
54 | Staleliteynaya | 40+31,5+40 | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened | 54 | Staleliteynaya | 40+31,5+40 |  | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened
55 | Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened | 55 | Teplichnaya | 10+10 |  | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened
56 | Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened | 56 | Uritskaya | 20+20 |  | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened
57 | Tsentralnaya | 16+16 | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened | 57 | Tsentralnaya | 16+16 |  | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened
| Nom. capacity MV, MVA | 16+16 | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98
| Nom. capacity LV, MVA | 16+16 | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56
58 | Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed | 58 | Yuzhnaya | 16+25 |  | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed
59 | Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened | 59 | Bobovichi | 6,3+2,5 |  | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened
60 | Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened | 60 | Belaya Berezka | 16+25 |  | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened
61 | Valuets | 4+6,3 | 1.114 | 0 | 0 | 1.114 | 0 | 4.2 | 3.086 | 3.086 | opened | 61 | Valuets | 4+6,3 |  | 1.114 | 0 | 0 | 1.114 | 0 | 4.2 | 3.086 | 3.086 | opened
62 | Vodoochistnaya | 10+6,3 | 1.808 | 0.54 | 3 hours | 1.268 | 0 | 42 | 40.732 | 40.731 | opened | 62 | Vodoochistnaya | 10+6,3 |  | 1.808 | 0.54 | 3 hours | 1.268 | 0 | 42 | 40.732 | 40.731 | opened
| Nom. capacity MV, MVA | 10+6,3 | 0.539 | 0.54 | 3 hours | -0.001 | 0 | 42 | 41.461 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.539 | 0.54 | 3 hours | -0.001 | 0 | 42 | 41.461
| Nom. capacity LV, MVA | 10+6,3 | 1.269 | 0 | 0 | 1.269 | 0 | 42 | 40.731 |  |  |  | Nom. capacity LV, MVA | 10+6,3 |  | 1.269 | 0 | 0 | 1.269 | 0 | 42 | 40.731
63 | Vysokoe | 40+40 | 20.732 | 0 | 0 | 20.732 | 0 | 42 | 21.268 | 21.268 | opened | 63 | Vysokoe | 40+40 |  | 20.732 | 0 | 0 | 20.732 | 0 | 42 | 21.268 | 21.268 | opened
64 | Zalineynaya | 10+6,3 | 3.931 | 0 | 0 | 3.931 | 0 | 6.615 | 2.684 | 2.684 | opened | 64 | Zalineynaya | 10+6,3 | 0.629 | 4.56 | 0 | 0 | 4.56 | 0 | 6.615 | 2.055 | 2.055 | opened
65 | Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened | 65 | Zapadnaya | 10+10 |  | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened
66 | Klimovo | 16+16 | 9.213 | 1.64 | 6 hours | 7.573 | 0 | 42 | 34.427 | 34.427 | opened | 66 | Klimovo | 16+16 | 0.006 | 9.219 | 1.64 | 6 hours | 7.579 | 0 | 42 | 34.421 | 34.421 | opened
| Nom. capacity MV, MVA | 16+16 | 3.123 | 1.64 | 6 hours | 1.483 | 0 | 42 | 38.877 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.123 | 1.64 | 6 hours | 1.483 | 0 | 42 | 38.877
| Nom. capacity LV, MVA | 16+16 | 6.09 | 0 | 0 | 6.09 | 0 | 42 | 35.91 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.006 | 6.096 | 0 | 0 | 6.096 | 0 | 42 | 35.904
67 | Kozhany | 10+10 | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened | 67 | Kozhany | 10+10 |  | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened
| Nom. capacity MV, MVA | 10+10 | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884
| Nom. capacity MV, MVA | 10+10 | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252
68 | Krasny Rog | 2,5+2,5 | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 68 | Krasny Rog | 2,5+2,5 |  | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened
69 | Pogar | 16+16+16 | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened | 69 | Pogar | 16+16+16 |  | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened
| Nom. capacity MV, MVA | 16+16 | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197
| Nom. capacity MV, MVA | 16+16 | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251
70 | Pochepskaya | 16+25 | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened | 70 | Pochepskaya | 16+25 |  | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened
| Nom. capacity MV, MVA | 16+25 | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792
| Nom. capacity LV, MVA | 16+25 | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213 |  |  |  | Nom. capacity LV, MVA | 16+25 |  | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213
71 | Semyachki | 2,5+2,5 | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened | 71 | Semyachki | 2,5+2,5 |  | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened
72 | Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened | 72 | Starodub | 16+16 |  | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771
73 | Staroselye | 6,3+6,3 | 0.97 | 0 | 0 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | opened | 73 | Staroselye | 6,3+6,3 |  | 0.97 | 0 | 0 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | opened
74 | Surazh | 16+16 | 18 | 3.04 | 6 hours | 14.96 | 0 | 42 | 27.04 | 27.04 | opened | 74 | Surazh | 16+16 |  | 18 | 3.04 | 6 hours | 14.96 | 0 | 42 | 27.04 | 27.04 | opened
| Nom. capacity MV, MVA | 16+16 | 4.7 | 3.04 | 6 hours | 1.66 | 0 | 42 | 37.3 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.7 | 3.04 | 6 hours | 1.66 | 0 | 42 | 37.3
| Nom. capacity LV, MVA | 16+16 | 13.3 | 0 | 0 | 13.3 | 0 | 42 | 28.7 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 13.3 | 0 | 0 | 13.3 | 0 | 42 | 28.7
75 | Trubchevsk | 16+10 | 7.399 | 0 | 0 | 7.399 | 0 | 10.5 | 3.101 | 3.101 | opened | 75 | Trubchevsk | 16+10 | 0.017 | 7.416 | 0 | 0 | 7.416 | 0 | 10.5 | 3.084 | 3.084 | opened
76 | Shelomy | 6,3+6,3 | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened | 76 | Shelomy | 6,3+6,3 |  | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened
77 | Yubileynaya | 16+16 | 13.67 | 6.45 | 3 hours | 7.22 | 0 | 42 | 34.78 | 34.775 | opened | 77 | Yubileynaya | 16+16 |  | 13.67 | 6.45 | 3 hours | 7.22 | 0 | 42 | 34.78 | 34.775 | opened
| Nom. capacity MV, MVA | 16+16 | 6.445 | 6.45 | 3 hours | -0.005 | 0 | 42 | 35.555 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.445 | 6.45 | 3 hours | -0.005 | 0 | 42 | 35.555
| Nom. capacity LV, MVA | 16+16 | 7.225 | 0 | 0 | 7.225 | 0 | 42 | 34.775 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 7.225 | 0 | 0 | 7.225 | 0 | 42 | 34.775
78 | Beloberezhskaya | 6,3+6,3 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened | 78 | Beloberezhskaya | 6,3+6,3 |  | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened
79 | Brasovskaya | 6,3+6,3 | 2.9 | 0 | 0 | 2.9 | 0 | 6.615 | 3.715 | 3.715 | opened | 79 | Brasovskaya | 6,3+6,3 |  | 2.9 | 0 | 0 | 2.9 | 0 | 6.615 | 3.715 | 3.715 | opened
80 | Bulshevskaya | 1,6+1,6 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened | 80 | Bulshevskaya | 1,6+1,6 |  | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
81 | Bytosh | 3,2+6,3 | 2.2 | 0 | 0 | 2.2 | 0 | 3.36 | 1.16 | 1.16 | opened | 81 | Bytosh | 3,2+6,3 | 0.272 | 2.472 | 0 | 0 | 2.472 | 0 | 3.36 | 0.888 | 0.888 | opened
82 | Velyaminovskaya | 4+4 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened | 82 | Velyaminovskaya | 4+4 |  | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened
83 | Vetma | 2,5+2,5 | 0.2 | 0 | 0 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 83 | Vetma | 2,5+2,5 |  | 0.2 | 0 | 0 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
84 | Volodarskaya | 10+6,3 | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.515 | -4.515 | closed | 84 | Volodarskaya | 10+6,3 |  | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.515 | -4.515 | closed
85 | Glodnevskaya | 4+2,5 | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened | 85 | Glodnevskaya | 4+2,5 |  | 1.1 | 0 | 0 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | opened
86 | Gorodskaya | 10+10 | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -0.38 | -0.38 | closed | 86 | Gorodskaya | 10+10 |  | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -0.38 | -0.38 | closed
87 | Grishina Sloboda | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 87 | Grishina Sloboda | 4+4 |  | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened
88 | Dobrovodye | 1,6+1,6 | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 88 | Dobrovodye | 1,6+1,6 |  | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
89 | Zhiryatinskaya | 4+4 | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 89 | Zhiryatinskaya | 4+4 |  | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened
90 | Igritskaya | 4+6,3 | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened | 90 | Igritskaya | 4+6,3 |  | 1.3 | 0 | 0 | 1.3 | 0 | 4.2 | 2.9 | 2.9 | opened
91 | Kasilovskaya | 2,5+1 | 0.1 | 0 | 0 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened | 91 | Kasilovskaya | 2,5+1 |  | 0.1 | 0 | 0 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened
92 | Kositskaya | 2,5+2,5 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened | 92 | Kositskaya | 2,5+2,5 |  | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened
93 | Krupets | 2,5+2,5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 93 | Krupets | 2,5+2,5 |  | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
94 | Luna | 1,6+1,6 | 1.1 | 0 | 0 | 1.1 | 0 | 1.68 | 0.58 | 0.58 | opened | 94 | Luna | 1,6+1,6 |  | 1.1 | 0 | 0 | 1.1 | 0 | 1.68 | 0.58 | 0.58 | opened
95 | Lyubokhna | 6,3+6,3 | 6.16 | 0 | 0 | 6.16 | 0 | 6.615 | 0.455 | 0.455 | opened | 95 | Lyubokhna | 6,3+6,3 |  | 6.16 | 0 | 0 | 6.16 | 0 | 6.615 | 0.455 | 0.455 | opened
96 | Mareevskaya | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 96 | Mareevskaya | 1,6+1,6 |  | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened
97 | Nevdolsk | 1,6+1,6 | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened | 97 | Nevdolsk | 1,6+1,6 |  | 0.2 | 0 | 0 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
98 | Norinskaya | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 98 | Norinskaya | 4+4 |  | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened
99 | Paltso | 4+2,5 | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened | 99 | Paltso | 4+2,5 |  | 0.4 | 0 | 0 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
100 | Pobeda | 4+4 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened | 100 | Pobeda | 4+4 |  | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened
101 | Pogreby | 4+4 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened | 101 | Pogreby | 4+4 |  | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened
102 | Privolskaya | 2,5+1,6 | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened | 102 | Privolskaya | 2,5+1,6 |  | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened
103 | Rzhanitskaya | 2,5+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 103 | Rzhanitskaya | 2,5+2,5 |  | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
104 | Rofnedinskaya | 4+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened | 104 | Rofnedinskaya | 4+6,3 |  | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened
105 | Ruzhnenskaya | 4+4 | 0.8 | 0 | 0 | 0.8 | 0 | 4.2 | 3.4 | 3.4 | opened | 105 | Ruzhnenskaya | 4+4 |  | 0.8 | 0 | 0 | 0.8 | 0 | 4.2 | 3.4 | 3.4 | opened
106 | Sevskaya | 6,3+6,3 | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened | 106 | Sevskaya | 6,3+6,3 |  | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened
107 | Seshcha 6 kv | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed | 107 | Seshcha 6 kv | 1,6+4 |  | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed
108 | Star | 10+10 | 3 | 0 | 0 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened | 108 | Star | 10+10 |  | 3 | 0 | 0 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened
109 | Teplovskaya | 2,5+2,5 | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened | 109 | Teplovskaya | 2,5+2,5 |  | 0.6 | 0 | 0 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
110 | Fedorovskaya | 1,6+1,8 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 110 | Fedorovskaya | 1,6+1,8 |  | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened
111 | Fokinskaya | 16+16 | 22.62 | 0 | 0 | 22.62 | 0 | 16.8 | -5.82 | -5.82 | closed | 111 | Fokinskaya | 16+16+16 | 2.558 | 25.178 | 0 | 0 | 25.178 | 0 | 33.6 | 8.422 | 8.422 | opened
112 | Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened | 112 | Fosforitnaya | 6,3+5,6+16 |  | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened
113 | Khvoshchevskaya | 2,5+2,5 | 0.8 | 0 | 0 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 113 | Khvoshchevskaya | 2,5+2,5 | 0.003 | 0.803 | 0 | 0 | 0.803 | 0 | 2.625 | 1.822 | 1.822 | opened
114 | Abarinskaya | 4+4 | 0.83 | 0 | 0 | 0.83 | 0 | 4.2 | 3.37 | 3.37 | opened | 114 | Abarinskaya | 4+4 |  | 0.83 | 0 | 0 | 0.83 | 0 | 4.2 | 3.37 | 3.37 | opened
115 | Andreykovichi | 2,5+2,5 | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 115 | Andreykovichi | 2,5+2,5 |  | 0.72 | 0 | 0 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
116 | Borshchevo | 1,6+1,6 | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0.6 | opened | 116 | Borshchevo | 1,6+1,6 |  | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0 | opened
117 | Vlazovichi | 2,5+1,6 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened | 117 | Vlazovichi | 2,5+1,6 |  | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened
118 | Water intake | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 118 | Water intake | 2,5+2,5 |  | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
119 | Voronok | 2,5+3,2 | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened | 119 | Voronok | 2,5+3,2 |  | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened
120 | Gordeevka | 4+4 | 2.82 | 0 | 0 | 2.82 | 0 | 4.2 | 1.38 | 1.38 | opened | 120 | Gordeevka | 4+4 | 0.038 | 2.858 | 0 | 0 | 2.858 | 0 | 4.2 | 1.342 | 1.342 | opened
121 | Gridenki | 2,5+3,2 | 1.3 | 0 | 0 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened | 121 | Gridenki | 2,5+3,2 |  | 1.3 | 0 | 0 | 1.3 | 0 | 2.625 | 1.325 | 1.325 | opened
122 | Zavodskaya | 4+2,5 |  | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 122 | Zavodskaya | 4+2,5 |  |  | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
123 | Istopki | 1,6+1,6 | 0.99 | 0 | 0 | 0.99 | 0 | 1.68 | 0.69 | 0.69 | opened | 123 | Istopki | 1,6+1,6 |  | 0.99 | 0 | 0 | 0.99 | 0 | 1.68 | 0.69 | 0.69 | opened
124 | Katashin | 1,6+1,6 | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened | 124 | Katashin | 1,6+1,6 |  | 0.67 | 0 | 0 | 0.67 | 0 | 1.68 | 1.01 | 1.01 | opened
125 | Kivay | 2,5+2,5 | 1.88 | 0 | 0 | 1.88 | 0 | 2.625 | 0.745 | 0.745 | opened | 125 | Kivay | 2,5+2,5 | 0.003 | 1.883 | 0 | 0 | 1.883 | 0 | 2.625 | 0.742 | 0.742 | opened
126 | Krutoyar | 2,5+1,6 | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 126 | Krutoyar | 2,5+1,6 |  | 0.58 | 0 | 0 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened
127 | Logovatoe | 2,5+1,6 | 0.985 | 0 | 0 | 0.985 | 0 | 1.68 | 0.695 | 0.695 | opened | 127 | Logovatoe | 2,5+1,6 |  | 0.985 | 0 | 0 | 0.985 | 0 | 1.68 | 0.695 | 0.695 | opened
128 | Lopazna | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 128 | Lopazna | 2,5+2,5 |  | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
129 | Mglinskaya | 4+4 | 3.04 | 0 | 0 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | opened | 129 | Mglinskaya | 4+4 |  | 3.04 | 0 | 0 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | opened
130 | Mishkovka | 2,5+1,6 | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened | 130 | Mishkovka | 2,5+1,6 |  | 0.51 | 0 | 0 | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened
131 | Novo-Drokov | 2,5+2,5 | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 131 | Novo-Drokov | 2,5+2,5 |  | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
132 | Putevaya | 6,3+6,3 | 5.24 | 0 | 0 | 5.24 | 0 | 6.615 | 1.375 | 1.375 | opened | 132 | Putevaya | 6,3+6,3 |  | 5.24 | 0 | 0 | 5.24 | 0 | 6.615 | 1.375 | 1.375 | opened
133 | Selishchanskaya | 2,5+2,5 | 0.95 | 0 | 0 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened | 133 | Selishchanskaya | 2,5+2,5 |  | 0.95 | 0 | 0 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened
134 | Slava | 2,5+1,6 | 1.06 | 0 | 0 | 1.06 | 0 | 1.68 | 0.62 | 0.62 | opened | 134 | Slava | 2,5+1,6 |  | 1.06 | 0 | 0 | 1.06 | 0 | 1.68 | 0.62 | 0.62 | opened
135 | Smolevichi | 6,3+6,3 | 3.22 | 0 | 0 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened | 135 | Smolevichi | 6,3+6,3 | 0.011 | 3.231 | 0 | 0 | 3.231 | 0 | 6.615 | 3.384 | 3.384 | opened
136 | Solovyovka | 1,6+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened | 136 | Solovyovka | 1,6+1,6 |  | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
137 | Sytaya Buda | 2,5+2,5 | 0.42 | 0 | 0 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened | 137 | Sytaya Buda | 2,5+2,5 |  | 0.42 | 0 | 0 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened
138 | Tembr | 4+4+3,2 | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened | 138 | Tembr | 4+4+3,2 |  | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened
139 | Churovichi | 2,5+4 | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 139 | Churovichi | 2,5+4 |  | 0.81 | 0 | 0 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened
140 | Shcherbinichi | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 140 | Shcherbinichi | 2,5+2,5 | 0.006 | 1.036 | 0 | 0 | 1.036 | 0 | 2.625 | 1.589 | 1.589 | opened
| Total: |  | 1003.411 | [8 empty] | 2: Total:; 5: 1019.091
| deficit | [8 empty] | -59.395 |  | 2: deficit; Мin. 12: -40.2
| proficit | [8 empty] | 716.066 |  | 2: proficit; Мin. 12: 728

## белгород
[11 empty] | Table 1 | [12 empty] | Table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  | МVА | МVА | Мin. | [11 empty] | МVА | min.
1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 1.453 | 1.457 | 45 | 1.457 | 0 | 1.457 | 0.004 | 0 | opened | 1 | SS-110/35/10kv D.Polyana | 6.3 | 0 | 1.453 | 1.457 | 45 | -0.004 | 0 | 1.457 | 0.004 | 0 | opened
| Sн. MV, МVА | 6.3 | 0.958 | 0.958 |  | 0.958 | 0 | 0.958 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0.958 | 0.958 |  | 0 | 0 | 0.958 | 0
| Sн. LV, МVА | 6.3 | 0.495 | 0.499 |  | 0.499 | 0 | 0.499 | 0.004 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.495 | 0.499 |  | -0.004 | 0 | 0.499 | 0.004
2 | SS-110/35/10kv Konshino | 6.3 | 0.383 | 0.39 | 20 | 0.39 | 0 | 0.39 | 0.007 | 0 | opened | 2 | SS-110/35/10kv Konshino | 6.3 | 0 | 0.383 | 0.39 | 20 | -0.007 | 0 | 0.39 | 0.007 | 0 | opened
| Sн. MV, МVА | 6.3 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 6.3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 0.383 | 0.39 |  | 0.39 | 0 | 0.39 | 0.007 |  |  |  | Sн. LV, МVА | 6.3 | 0 | 0.383 | 0.39 |  | -0.007 | 0 | 0.39 | 0.007
3 | SS-110/35/10kv Orositelnaya | 16 | 11.607 | 11.607 | 120 | 11.607 | 0 | 11.607 | 0 | 0 | opened | 3 | SS-110/35/10kv Orositelnaya | 16 | 0 | 11.607 | 11.607 | 120 | 0 | 0 | 11.607 | 0 | 0 | opened
| Sн. MV, МVА | 16 | 8.606 | 8.606 |  | 8.606 | 0 | 8.606 | 0 |  |  |  | Sн. MV, МVА | 16 | 0 | 8.606 | 8.606 |  | 0 | 0 | 8.606 | 0
| Sн. LV, МVА | 16 | 3.001 | 3.001 |  | 3.001 | 0 | 3.001 | 0 |  |  |  | Sн. LV, МVА | 16 | 0 | 3.001 | 3.001 |  | 0 | 0 | 3.001 | 0
4 | SS-110/35/6kv Pishcheprom | 25 | 6.431 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.248 | 0 | opened | 4 | SS-110/35/6kv Pishcheprom | 25 | 0.07 | 6.501 | 6.679 | 120 | -0.178 | 0 | 6.679 | 0.178 | 0 | opened
| Sн. MV, МVА | 12.5 | 2.022 | 2.022 |  | 2.022 | 0 | 2.022 | 0 |  |  |  | Sн. MV, МVА | 12.5 | 0 | 2.022 | 2.022 |  | 0 | 0 | 2.022 | 0
| Sн. LV, МVА | 12.5 | 4.409 | 4.657 |  | 4.657 | 0 | 4.657 | 0.248 |  |  |  | Sн. LV, МVА | 12.5 | 0.07 | 4.479 | 4.657 |  | -0.178 | 0 | 4.657 | 0.178
5 | SS-110/35/10kv Rovenki | 16 | 2.29 | 3.44 | 120 | 3.44 | 0 | 3.44 | 1.15 | 0 | opened | 5 | SS-110/35/10kv Rovenki | 16 | 0 | 2.29 | 3.44 | 120 | -1.15 | 0 | 3.44 | 1.15 | 0 | opened
| Sн. MV, МVА | 16 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 16 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, МVА | 16 | 2.29 | 3.44 |  | 3.44 | 0 | 3.44 | 1.15 |  |  |  | Sн. LV, МVА | 16 | 0 | 2.29 | 3.44 |  | -1.15 | 0 | 3.44 | 1.15
6 | SS-110/35/10kv Serebryanka | 10 | 1.234 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.546 | 0 | opened | 6 | SS-110/35/10kv Serebryanka | 10 | 0 | 1.234 | 1.78 | 45 | -0.546 | 0 | 1.78 | 0.546 | 0 | opened
| Sн. MV, МVА | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Sн. MV, МVА | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1.234 | 1.78 |  | 1.78 | 0 | 1.78 | 0.546 |  |  |  | Sн. LV, MVА | 10 | 0 | 1.234 | 1.78 |  | -0.546 | 0 | 1.78 | 0.546
7 | SS-35/10kv Afanasyevka | 1.6 | 0.70565 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.059246 | -0.059246 | closed | 7 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.70565 | 0.6464 | 45 | 0.059246 | 0 | 0.6464 | -0.059246 | -0.059246 | closed
8 | SS-35/10kv Borisovka | 1.6 | 0.6377 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.045804 | 0.045804 | opened | 8 | SS-35/10kv Borisovka | 1.6 | 0 | 0.6377 | 0.6835 | 45 | -0.045804 | 0 | 0.6835 | 0.045804 | 0.045804 | opened
9 | SS-35/10kv Borisy | 1.6 | 0.51253 | 0 | 20 | 0 | 0 | 0 | -0.51253 | -0.51253 | closed | 9 | SS-35/10kv Borisy | 1.6 | 0 | 0.51253 | 0 | 20 | 0.51253 | 0 | 0 | -0.51253 | -0.51253 | closed
10 | SS-35/10kv Gostishchevo | 4 | 2.5809 | 2.64 | 80 | 2.64 | 0 | 2.64 | 0.059085 | 0.059085 | opened | 10 | SS-35/10kv Gostishchevo | 4 | 0 | 2.5809 | 2.64 | 80 | -0.059085 | 0 | 2.64 | 0.059085 | 0.059085 | opened
11 | SS-35/10kv Gruzskoe | 1.6 | 0.61905 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.43095 | 0.43095 | opened | 11 | SS-35/10kv Gruzskoe | 1.6 | 0 | 0.61905 | 1.05 | 80 | -0.43095 | 0 | 1.05 | 0.43095 | 0.43095 | opened
12 | SS-35/10kv Zemsnaryad | 1.6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened | 12 | SS-35/10kv Zemsnaryad | 1.6 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0.38773 | 0 |  | 0 | 0 | 0 | -0.38773 | -0.38773 | closed | 13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.38773 | 0 |  | 0.38773 | 0 | 0 | -0.38773 | -0.38773 | closed
14 | SS-35/10kv Kamyzino | 2.5 | 1.1346 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.59359 | -0.59359 | closed | 14 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.1346 | 0.541 | 45 | 0.59359 | 0 | 0.541 | -0.59359 | -0.59359 | closed
15 | SS-35/10kv Koloskovo | 2.5 | 1.6498 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | 0.012776 | 0.012776 | opened | 15 | SS-35/10kv Koloskovo | 2.5 | 0 | 1.6498 | 1.6626 | 45 | -0.012776 | 0 | 1.6626 | 0.012776 | 0.012776 | opened
16 | SS-35/10jkv Kryukovo | 2.5 | 1.5379 | 1.55 | 45 | 1.55 | 0 | 1.55 | 0.012079 | 0.012079 | opened | 16 | SS-35/10jkv Kryukovo | 2.5 | 0 | 1.5379 | 1.55 | 45 | -0.012079 | 0 | 1.55 | 0.012079 | 0.012079 | opened
17 | SS-35/10kv Kushchino | 1.6 | 0.38137 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.028734 | 0.028734 | opened | 17 | SS-35/10kv Kushchino | 1.6 | 0 | 0.38137 | 0.4101 | 80 | -0.028734 | 0 | 0.4101 | 0.028734 | 0.028734 | opened
18 | SS-35/10kv Lopukhinka | 2.5 | 0.38666 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.020343 | 0.020343 | opened | 18 | SS-35/10kv Lopukhinka | 2.5 | 0 | 0.38666 | 0.407 | 20 | -0.020343 | 0 | 0.407 | 0.020343 | 0.020343 | opened
19 | SS-35/10kv Malakeevo | 2.5 | 1.3202 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.059782 | 0.059782 | opened | 19 | SS-35/10kv Malakeevo | 2.5 | 0 | 1.3202 | 1.38 | 120 | -0.059782 | 0 | 1.38 | 0.059782 | 0.059782 | opened
20 | SS-35/10kv Murom | 2.5 | 1.2542 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.28576 | 0.28576 | opened | 20 | SS-35/10kv Murom | 2.5 | 0 | 1.2542 | 1.54 | 45 | -0.28576 | 0 | 1.54 | 0.28576 | 0.28576 | opened
21 | SS-35/10kv Nikolaevka | 2.5 | 0.65277 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | 0.011927 | 0.011927 | opened | 21 | SS-35/10kv Nikolaevka | 2.5 | 0 | 0.65277 | 0.6647 | 45 | -0.011927 | 0 | 0.6647 | 0.011927 | 0.011927 | opened
22 | SS-35/10kv Nikolskoe | 4 | 1.6697 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.88968 | -0.88968 | closed | 22 | SS-35/10kv Nikolskoe | 4 | 0 | 1.6697 | 0.78 | 120 | 0.88968 | 0 | 0.78 | -0.88968 | -0.88968 | closed
23 | SS-35/10kv Pokrovka | 4 | 0.67755 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.044451 | 0.044451 | opened | 23 | SS-35/10kv Pokrovka | 4 | 0 | 0.67755 | 0.722 | 45 | -0.044451 | 0 | 0.722 | 0.044451 | 0.044451 | opened
24 | SS-35/10kv Pyatnitskoe | 4 | 2.4286 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.58861 | -0.58861 | closed | 24 | SS-35/10kv Pyatnitskoe | 4 | 0 | 2.4286 | 1.84 | 80 | 0.58861 | 0 | 1.84 | -0.58861 | -0.58861 | closed
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0.463 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.213 | 1.213 | opened | 25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 0 | 0.463 | 1.676 | 80 | -1.213 | 0 | 1.676 | 1.213 | 1.213 | opened
26 | SS-35/10kv Svistovka | 2.5 | 0.64045 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.04675 | 0.04675 | opened | 26 | SS-35/10kv Svistovka | 2.5 | 0 | 0.64045 | 0.6872 | 45 | -0.04675 | 0 | 0.6872 | 0.04675 | 0.04675 | opened
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0.54595 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.17785 | 0.17785 | opened | 27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 0 | 0.54595 | 0.7238 | 120 | -0.17785 | 0 | 0.7238 | 0.17785 | 0.17785 | opened
28 | SS-35/10kv Kharkovskoe | 2.5 | 0.4473 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.2324 | 0.2324 | opened | 28 | SS-35/10kv Kharkovskoe | 2.5 | 0 | 0.4473 | 0.6797 | 120 | -0.2324 | 0 | 0.6797 | 0.2324 | 0.2324 | opened
29 | SS-35/10kv Tserkovnaya | 2.5 | 1.1275 | 1 | 80 | 1 | 0 | 1 | -0.12755 | -0.12755 | closed | 29 | SS-35/10kv Tserkovnaya | 2.5 | 0.18 | 1.3075 | 1 | 80 | 0.30755 | 0 | 1 | -0.30755 | -0.30755 | closed
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 9.9792 | 3.561 | 45 | 6.4182 | 0 | 16.8 | 10.3818 | 10.3818 | opened | 30 | SS-110/6kv Automobile maintenance plant | 16+16 | 0.03 | 10.0092 | 3.561 | 45 | 6.4482 | 0 | 16.8 | 10.3518 | 10.3518 | opened
31 | SS-110/35/10kv Aydar | 16+10 | 8.4408 | 8.95 | 120 | -0.50918 | 0 | 10.5 | 11.0092 | 10.5 | opened | 31 | SS-110/35/10kv Aydar | 16+10 | 0.25 | 8.6908 | 8.95 | 120 | -0.25918 | 0 | 10.5 | 10.7592 | 10.5 | opened
| Sн. MV, МVА | 16+10 | 7.29 | 7.29 |  | 0 | 0 | 10.5 | 10.5 |  | opened |  | Sн. MV, МVА | 16+10 | 0 | 7.29 | 7.29 |  | 0 | 0 | 10.5 | 10.5 |  | opened
| Sн. LV, МVА | 16+10 | 1.1508 | 1.66 |  | -0.50918 | 0 | 10.5 | 11.0092 |  | opened |  | Sн. LV, МVА | 16+10 | 0.25 | 1.4008 | 1.66 |  | -0.25918 | 0 | 10.5 | 10.7592 |  | opened
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12.534 | 8.37 | 80 | 4.164 | 0 | 16.8 | 12.636 | 12.636 | opened | 32 | SS-110/35/10kv Alexandrovka | 16+16 | 0.073 | 12.607 | 8.37 | 80 | 4.237 | 0 | 16.8 | 12.563 | 12.563 | opened
| Sн. MV, МVА | 16+16 | 6.697 | 6.697 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 6.697 | 6.697 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 5.837 | 1.673 |  | 4.164 | 0 | 16.8 | 12.636 |  |  |  | Sн. LV, МVА | 16+16 | 0.073 | 5.91 | 1.673 |  | 4.237 | 0 | 16.8 | 12.563
33 | SS-110/35/10kv Alexeevka | 25+16+25 | 44.0632 | 0 | 120 | 44.0632 | 0 | 43.05 | -1.0132 | -1.0132 | closed | 33 | SS-110/35/10kv Alexeevka | 25+16+25 | 0 | 44.0632 | 0 | 120 | 44.0632 | 0 | 43.05 | -1.0132 | -1.0132 | closed
| Sн. MV, МVА | 25+16+25 | 19.821 | 0 |  | 19.821 | 0 | 43.05 | 23.229 |  |  |  | Sн. MV, МVА | 25+16+25 | 0 | 19.821 | 0 |  | 19.821 | 0 | 43.05 | 23.229
| Sн. LV, МVА | 25+16+25 | 24.2422 | 0 |  | 24.2422 | 0 | 43.05 | 18.8078 |  |  |  | Sн. LV, МVА | 25+16+25 | 0 | 24.2422 | 0 |  | 24.2422 | 0 | 43.05 | 18.8078
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 9.383 | 8.87 | 45 | 0.513 | 0 | 10.5 | 9.987 | 9.984 | opened | 34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 0 | 9.383 | 8.87 | 45 | 0.513 | 0 | 10.5 | 9.987 | 9.984 | opened
| Sн. MV, МVА | 10+16 | 8.867 | 8.867 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 8.867 | 8.867 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+16 | 0.516 | 0 |  | 0.516 | 0 | 10.5 | 9.984 |  |  |  | Sн. LV, МVА | 10+16 | 0 | 0.516 | 0 |  | 0.516 | 0 | 10.5 | 9.984
35 | SS-110/6kv Belgorod-1 | 40+48 | 44.5181 | 0 | 120 | 44.5181 | 0 | 42 | -2.5181 | -2.5181 | closed | 35 | SS-110/6kv Belgorod-1 | 40+48 | 4.372 | 48.8901 | 0 | 120 | 48.8901 | 0 | 42 | -6.8901 | -6.8901 | closed
36 | SS-110/35/10kv Borisovka | 16+16 | 14.4143 | 11.433 | 120 | 2.9813 | 0 | 16.8 | 13.8187 | 5.4187 | opened | 36 | SS-110/35/10kv Borisovka | 16+16 | 0.069 | 14.4833 | 11.433 | 120 | 3.0503 | 0 | 16.8 | 13.7497 | 5.3497 | opened
| Sн. MV, МVА | 16+8 | 8.133 | 8.133 |  | 0 | 0 | 8.4 | 8.4 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 8.133 | 8.133 |  | 0 | 0 | 8.4 | 8.4
| Sн. LV, МVА | 16+8 | 6.2813 | 3.3 |  | 2.9813 | 0 | 8.4 | 5.4187 |  |  |  | Sн. LV, МVА | 16+8 | 0.069 | 6.3503 | 3.3 |  | 3.0503 | 0 | 8.4 | 5.3497
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9.036 | 11.5 | 120 | -2.464 | 0 | 10.5 | 12.964 | 10.532 | opened | 37 | SS-110/35/10kv V.Pokrovka | 10+10 | 0 | 9.036 | 11.5 | 120 | -2.464 | 0 | 10.5 | 12.964 | 10.532 | opened
| Sн. MV, МVА | 10+10 | 7.768 | 7.8 |  | -0.032 | 0 | 10.5 | 10.532 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 7.768 | 7.8 |  | -0.032 | 0 | 10.5 | 10.532
| Sн. LV, МVА | 10+10 | 1.268 | 3.7 |  | -2.432 | 0 | 10.5 | 12.932 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 1.268 | 3.7 |  | -2.432 | 0 | 10.5 | 12.932
38 | SS-110/35/10kv Veydelevka | 10+10 | 7.9503 | 8.83 | 120 | -0.8797 | 0 | 10.5 | 11.3797 | 10.5 | opened | 38 | SS-110/35/10kv Veydelevka | 10+10 | 0 | 7.9503 | 8.83 | 120 | -0.8797 | 0 | 10.5 | 11.3797 | 10.5 | opened
| Sн. MV, МVА | 10+10 | 3.955 | 3.955 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 3.955 | 3.955 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+10 | 3.9953 | 4.875 |  | -0.8797 | 0 | 10.5 | 11.3797 |  |  |  | Sн. LV, МVА | 10+10 | 0 | 3.9953 | 4.875 |  | -0.8797 | 0 | 10.5 | 11.3797
39 | SS-110/6kv Vitamin plant | 25+25 | 11.7863 | 1.46 | 45 | 10.3263 | 0 | 26.25 | 15.9237 | 15.9237 | opened | 39 | SS-110/6kv Vitamin plant | 25+25 | 0.286 | 12.0723 | 1.46 | 45 | 10.6123 | 0 | 26.25 | 15.6377 | 15.6377 | opened
40 | SS-110/35/10kv Volokonovka | 25+25 | 15.9084 | 10.651 | 120 | 5.2574 | 0 | 26.25 | 20.9926 | 20.9926 | opened | 40 | SS-110/35/10kv Volokonovka | 25+25 | 0 | 15.9084 | 10.651 | 120 | 5.2574 | 0 | 26.25 | 20.9926 | 20.9926 | opened
| Sн. MV, МVА | 25+25 | 8.576 | 8.576 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 8.576 | 8.576 |  | 0 | 0 | 26.25 | 26.25
| Sн. LV, МVА | 25+25 | 7.3324 | 2.075 |  | 5.2574 | 0 | 26.25 | 20.9926 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 7.3324 | 2.075 |  | 5.2574 | 0 | 26.25 | 20.9926
41 | SS-110/35/6kv Vostochnaya | 25+25 | 41.987 | 25.07 | 120 | 16.917 | 0 | 26.25 | 9.333 | 7.447 | opened | 41 | SS-110/35/6kv Vostochnaya | 25+25 | 0.107 | 42.094 | 25.07 | 120 | 17.024 | 0 | 26.25 | 9.226 | 7.34 | opened
| Sн. MV, МVА | 25+25 | 19.414 | 21.3 |  | -1.886 | 0 | 26.25 | 28.136 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 19.414 | 21.3 |  | -1.886 | 0 | 26.25 | 28.136
| Sн. LV, МVА | 25+25 | 22.573 | 3.77 |  | 18.803 | 0 | 26.25 | 7.447 |  |  |  | Sн. LV, МVА | 25+25 | 0.107 | 22.68 | 3.77 |  | 18.91 | 0 | 26.25 | 7.34
42 | SS-110/10/6kv Golofeevka | 25+25 | 1.8481 | 0 |  | 1.8481 | 0 | 26.25 | 24.4019 | 11.277 | opened | 42 | SS-110/10/6kv Golofeevka | 25+25 | 0 | 1.8481 | 0 |  | 1.8481 | 0 | 26.25 | 24.4019 | 11.277 | opened
| Sн. MV, МVА | 12,5+12,5 | 1.848 | 0 |  | 1.848 | 0 | 13.125 | 11.277 |  |  |  | Sн. MV, МVА | 12,5+12,5 | 0 | 1.848 | 0 |  | 1.848 | 0 | 13.125 | 11.277
| Sн. LV, МVА | 12,5+12,5 | 6.5362e-05 | 0 |  | 6.5362e-05 | 0 | 13.125 | 13.1249 |  |  |  | Sн. LV, МVА | 12,5+12,5 | 0 | 6.5362e-05 | 0 |  | 6.5362e-05 | 0 | 13.125 | 13.1249
43 | SS-110/10kv Gotnya | 16+16 | 8.9986 | 6.43 | 120 | 2.5686 | 0 | 16.8 | 14.2314 | 14.2314 | opened | 43 | SS-110/10kv Gotnya | 16+16 | 0.005 | 9.0036 | 6.43 | 120 | 2.5736 | 0 | 16.8 | 14.2264 | 14.2264 | opened
44 | SS-110/35/10kv Grayvoron | 16+16 | 15.2094 | 13.953 | 80 | 1.2564 | 0 | 16.8 | 15.5436 | 15.5436 | opened | 44 | SS-110/35/10kv Grayvoron | 16+16 | 0.04 | 15.2494 | 13.953 | 80 | 1.2964 | 0 | 16.8 | 15.5036 | 15.5036 | opened
| Sн. MV, МVА | 16+25 | 10.903 | 10.903 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+25 | 0 | 10.903 | 10.903 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+25 | 4.3064 | 3.05 |  | 1.2564 | 0 | 16.8 | 15.5436 |  |  |  | Sн. LV, МVА | 16+25 | 0.04 | 4.3464 | 3.05 |  | 1.2964 | 0 | 16.8 | 15.5036
45 | SS-110/6kv Donets | 40+40 | 26.0404 | 6.73 | 120 | 19.3104 | 0 | 42 | 22.6896 | 22.6896 | opened | 45 | SS-110/6kv Donets | 40+40 | 1.222 | 27.2624 | 6.73 | 120 | 20.5324 | 0 | 42 | 21.4676 | 21.4676 | opened
46 | SS-110/10kv Dubovoe | 40+40 | 22.9597 | 11.23 | 120 | 11.7297 | 0 | 42 | 30.2703 | 30.2703 | opened | 46 | SS-110/10kv Dubovoe | 40+40 | 0.818 | 23.7777 | 11.23 | 120 | 12.5477 | 0 | 42 | 29.4523 | 29.4523 | opened
47 | SS-110/35/6kv Zhuravliki | 40+25 | 13.1662 | 12.4 | 120 | 0.76617 | 0 | 42 | 41.2338 | 41.2338 | opened | 47 | SS-110/35/6kv Zhuravliki | 40+25 | 0 | 13.1662 | 12.4 | 120 | 0.76617 | 0 | 42 | 41.2338 | 41.2338 | opened
| Sн. MV, МVА | 40+25 | 6.227 | 6.227 |  | 0 | 0 | 42 | 42 |  |  |  | Sн. MV, МVА | 40+25 | 0 | 6.227 | 6.227 |  | 0 | 0 | 42 | 42
| Sн. LV, МVА | 40+25 | 6.9392 | 6.173 |  | 0.76617 | 0 | 42 | 41.2338 |  |  |  | Sн. LV, МVА | 40+25 | 0 | 6.9392 | 6.173 |  | 0.76617 | 0 | 42 | 41.2338
48 | SS-110/10kv Zapadnaya | 16+16 | 16.9475 | 1.249 | 80 | 15.6985 | 0 | 16.8 | 1.1015 | 1.1015 | opened | 48 | SS-110/10kv Zapadnaya | 16+16 | 2.825 | 19.7725 | 1.249 | 80 | 18.5235 | 0 | 16.8 | -1.7235 | -1.7235 | closed
49 | SS-110/35/10kv Ivnya | 16+10 | 6.018 | 6.16 | 80 | -0.14205 | 0 | 10.5 | 10.642 | 10.5 | opened | 49 | SS-110/35/10kv Ivnya | 16+10 | 0 | 6.018 | 6.16 | 80 | -0.14205 | 0 | 10.5 | 10.642 | 10.5 | opened
| Sн. MV, МVА | 16+10 | 2.375 | 2.375 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 16+10 | 0 | 2.375 | 2.375 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 16+10 | 3.643 | 3.785 |  | -0.14205 | 0 | 10.5 | 10.642 |  |  |  | Sн. LV, МVА | 16+10 | 0 | 3.643 | 3.785 |  | -0.14205 | 0 | 10.5 | 10.642
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 11.3866 | 7.7116 | 120 | 3.675 | 0 | 16.8 | 13.125 | 13.125 | opened | 50 | SS-110/35/10kv K.Gvardiya | 16+16 | 0 | 11.3866 | 7.7116 | 120 | 3.675 | 0 | 16.8 | 13.125 | 13.125 | opened
| Sн. MV, МVА | 16+16 | 4.854 | 4.854 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.854 | 4.854 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 6.5326 | 2.8576 |  | 3.675 | 0 | 16.8 | 13.125 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 6.5326 | 2.8576 |  | 3.675 | 0 | 16.8 | 13.125
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 11.6977 | 9.65 | 80 | 2.0477 | 0 | 26.25 | 24.2023 | 19.9363 | opened | 51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 0 | 11.6977 | 9.65 | 80 | 2.0477 | 0 | 26.25 | 24.2023 | 19.9363 | opened
| Sн. MV, МVА | 25+25 | 1.384 | 1.384 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 1.384 | 1.384 |  | 0 | 0 | 26.25 | 26.25
| Sн. LV, МVА | 25+25 | 10.3137 | 4 |  | 6.3137 | 0 | 26.25 | 19.9363 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 10.3137 | 4 |  | 6.3137 | 0 | 26.25 | 19.9363
52 | SS-110/35/10kv Korocha | 10+10+10 | 18.4946 | 2.019 | 20 | 16.4756 | 0 | 21 | 4.5244 | 4.5244 | opened | 52 | SS-110/35/10kv Korocha | 10+10+10 | 0.014 | 18.5086 | 2.019 | 20 | 16.4896 | 0 | 21 | 4.5104 | 4.5104 | opened
| Sн. MV, МVА | 10+10+10 | 7.286 | 1.719 |  | 5.567 | 0 | 21 | 15.433 |  |  |  | Sн. MV, МVА | 10+10+10 | 0 | 7.286 | 1.719 |  | 5.567 | 0 | 21 | 15.433
| Sн. LV, МVА | 10+10+10 | 11.2086 | 0.3 |  | 10.9086 | 0 | 21 | 10.0914 |  |  |  | Sн. LV, МVА | 10+10+10 | 0.014 | 11.2226 | 0.3 |  | 10.9226 | 0 | 21 | 10.0774
53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 10.8277 | 9.158 | 120 | 1.6697 | 0 | 10.5 | 8.8303 | 8.826 | opened | 53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 0.005 | 10.8327 | 9.158 | 120 | 1.6747 | 0 | 10.5 | 8.8253 | 8.8253 | opened
| Sн. MV, МVА | 10+10 | 5.194 | 3.52 |  | 1.674 | 0 | 10.5 | 8.826 |  |  |  | Sн. MV, МVА | 10+10 | 0 | 5.194 | 3.52 |  | 1.674 | 0 | 10.5 | 8.826
| Sн. LV, МVА | 10+10 | 5.6337 | 5.638 |  | -0.004347 | 0 | 10.5 | 10.5043 |  |  |  | Sн. LV, МVА | 10+10 | 0.005 | 5.6387 | 5.638 |  | 0.00065303 | 0 | 10.5 | 10.4993
54 | SS-110/35/10kv Maximovka | 16+16 | 10.7359 | 11.48 | 45 | -0.7441 | 0 | 16.8 | 17.5441 | 16.8 | opened | 54 | SS-110/35/10kv Maximovka | 16+16 | 0 | 10.7359 | 11.48 | 45 | -0.7441 | 0 | 16.8 | 17.5441 | 16.8 | opened
| Sн. MV, МVА | 16+16 | 9.449 | 9.449 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 9.449 | 9.449 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 1.2869 | 2.031 |  | -0.7441 | 0 | 16.8 | 17.5441 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 1.2869 | 2.031 |  | -0.7441 | 0 | 16.8 | 17.5441
55 | SS-110/35/10kv N.Oskol | 25+31,5 | 19.8083 | 9.119 | 80 | 10.6893 | 0 | 26.25 | 15.5607 | 14.7647 | opened | 55 | SS-110/35/10kv N.Oskol | 25+31,5 | 0.068 | 19.8763 | 9.119 | 80 | 10.7573 | 0 | 26.25 | 15.4927 | 14.6967 | opened
| Sн. MV, МVА | 25+31,5 | 7.034 | 7.83 |  | -0.796 | 0 | 26.25 | 27.046 |  |  |  | Sн. MV, МVА | 25+31,5 | 0 | 7.034 | 7.83 |  | -0.796 | 0 | 26.25 | 27.046
| Sн. LV, МVА | 25+31,5 | 12.7743 | 1.289 |  | 11.4853 | 0 | 26.25 | 14.7647 |  |  |  | Sн. LV, МVА | 25+31,5 | 0.068 | 12.8423 | 1.289 |  | 11.5533 | 0 | 26.25 | 14.6967
56 | SS-110/10kv Obukhovskaya | 25+25 | 2.351 | 0 |  | 2.351 | 0 | 26.25 | 23.899 | 23.899 | opened | 56 | SS-110/10kv Obukhovskaya | 25+25 | 0 | 2.351 | 0 |  | 2.351 | 0 | 26.25 | 23.899 | 23.899 | opened
57 | SS-110/6kv Ochistnye | 16+16 | 6.5595 | 0 |  | 6.5595 | 0 | 16.8 | 10.2405 | 10.2405 | opened | 57 | SS-110/6kv Ochistnye | 16+16 | 0 | 6.5595 | 0 |  | 6.5595 | 0 | 16.8 | 10.2405 | 10.2405 | opened
58 | SS-110/10kv Promyshlennaya | 25+25 | 14.983 | 0 |  | 14.983 | 0 | 26.25 | 11.267 | 11.267 | opened | 58 | SS-110/10kv Promyshlennaya | 25+25 | 1 | 15.983 | 0 |  | 15.983 | 0 | 26.25 | 10.267 | 10.267 | opened
59 | SS-110/10kv Poultry plant | 16+16 | 10.559 | 1.296 | 80 | 9.263 | 0 | 16.8 | 7.537 | 7.537 | opened | 59 | SS-110/10kv Poultry plant | 16+16 | 0 | 10.559 | 1.296 | 80 | 9.263 | 0 | 16.8 | 7.537 | 7.537 | opened
60 | SS-110/10kv Pushkarnaya | 40+40 | 27.735 | 0 | 60 | 27.735 | 0 | 42 | 14.265 | 14.265 | opened | 60 | SS-110/10kv Pushkarnaya | 40+40 | 2.406 | 30.141 | 0 | 60 | 30.141 | 0 | 42 | 11.859 | 11.859 | opened
61 | SS-110/35/10kv Rakitnoe | 10+16 | 9.2018 | 8.98 | 120 | 0.22184 | 0 | 10.5 | 10.2782 | 10.2782 | opened | 61 | SS-110/35/10kv Rakitnoe | 10+16 | 0 | 9.2018 | 8.98 | 120 | 0.22184 | 0 | 10.5 | 10.2782 | 10.2782 | opened
| Sн. MV, МVА | 10+16 | 6.407 | 6.407 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Sн. MV, МVА | 10+16 | 0 | 6.407 | 6.407 |  | 0 | 0 | 10.5 | 10.5
| Sн. LV, МVА | 10+16 | 2.7948 | 2.573 |  | 0.22184 | 0 | 10.5 | 10.2782 |  |  |  | Sн. LV, МVА | 10+16 | 0 | 2.7948 | 2.573 |  | 0.22184 | 0 | 10.5 | 10.2782
62 | SS-110/35/6kv Rudnik | 25+25 | 14.117 | 10.46 | 45 | 3.657 | 0 | 26.25 | 22.593 | 21.474 | opened | 62 | SS-110/35/6kv Rudnik | 25+25 | 0 | 14.117 | 10.46 | 45 | 3.657 | 0 | 26.25 | 22.593 | 21.474 | opened
| Sн. MV, МVА | 25+25 | 9.341 | 10.46 |  | -1.119 | 0 | 26.25 | 27.369 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 9.341 | 10.46 |  | -1.119 | 0 | 26.25 | 27.369
| Sн. LV, МVА | 25+25 | 4.776 | 0 |  | 4.776 | 0 | 26.25 | 21.474 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 4.776 | 0 |  | 4.776 | 0 | 26.25 | 21.474
63 | SS-110/10kv Severnaya | 40+40 | 11.1616 | 3.312 | 45 | 7.8496 | 0 | 42 | 34.1504 | 34.1504 | opened | 63 | SS-110/10kv Severnaya | 40+40 | 6.45 | 17.6116 | 3.312 | 45 | 14.2996 | 0 | 42 | 27.7004 | 27.7004 | opened
64 | SS-110/35/10kv Skorodnoe | 16+16 | 11.5224 | 10.36 | 120 | 1.1624 | 0 | 16.8 | 15.6376 | 15.6376 | opened | 64 | SS-110/35/10kv Skorodnoe | 16+16 | 0 | 11.5224 | 10.36 | 120 | 1.1624 | 0 | 16.8 | 15.6376 | 15.6376 | opened
| Sн. MV, МVА | 16+16 | 7.562 | 7.562 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 7.562 | 7.562 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+16 | 3.9604 | 2.798 |  | 1.1624 | 0 | 16.8 | 15.6376 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 3.9604 | 2.798 |  | 1.1624 | 0 | 16.8 | 15.6376
65 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 28.8772 | 0 |  | 28.8772 | 0 | 47.25 | 18.3728 | 18.3728 | opened | 65 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 0.00675 | 28.8839 | 0 |  | 28.8839 | 0 | 47.25 | 18.3661 | 18.3661 | opened
| Sн. MV, МVА | 20+25+25 | 6.331 | 0 |  | 6.331 | 0 | 47.25 | 40.919 |  |  |  | Sн. MV, МVА | 20+25+25 | 0 | 6.331 | 0 |  | 6.331 | 0 | 47.25 | 40.919
| Sн. LV, МVА | 20+25+25 | 22.5462 | 0 |  | 22.5462 | 0 | 47.25 | 24.7038 |  |  |  | Sн. LV, МVА | 20+25+25 | 0.00675 | 22.5529 | 0 |  | 22.5529 | 0 | 47.25 | 24.6971
66 | SS-110/35/10kv Streletskaya | 16+16 | 4.2243 | 2.23 | 80 | 1.9943 | 0 | 16.8 | 14.8057 | 6.4057 | opened | 66 | SS-110/35/10kv Streletskaya | 16+16 | 0.06 | 4.2843 | 2.23 | 80 | 2.0543 | 0 | 16.8 | 14.7457 | 6.3457 | opened
| Sн. MV, МVА | 16+8 | 0 | 0 |  | 0 | 0 | 8.4 | 8.4 |  |  |  | Sн. MV, МVА | 16+8 | 0 | 0 | 0 |  | 0 | 0 | 8.4 | 8.4
| Sн. LV, МVА | 16+8 | 4.2243 | 2.23 |  | 1.9943 | 0 | 8.4 | 6.4057 |  |  |  | Sн. LV, МVА | 16+8 | 0.06 | 4.2843 | 2.23 |  | 2.0543 | 0 | 8.4 | 6.3457
67 | SS-110/6kv Stroitel | 15+15 | 13.298 | 0 |  | 13.298 | 0 | 15.75 | 2.452 | 2.452 | opened | 67 | SS-110/6kv Stroitel | 15+15 | 0.514 | 13.812 | 0 |  | 13.812 | 0 | 15.75 | 1.938 | 1.938 | opened
68 | SS-110/35/10kv Tomarovka | 16+16 | 12.5522 | 3.46 | 45 | 9.0922 | 0 | 16.8 | 7.7078 | 7.7078 | opened | 68 | SS-110/35/10kv Tomarovka | 16+16 | 0 | 12.5522 | 3.46 | 45 | 9.0922 | 0 | 16.8 | 7.7078 | 7.7078 | opened
| Sн. MV, МVА | 16+16 | 4.379 | 3.46 |  | 0.919 | 0 | 16.8 | 15.881 |  |  |  | Sн. MV, МVА | 16+16 | 0 | 4.379 | 3.46 |  | 0.919 | 0 | 16.8 | 15.881
| Sн. LV, МVА | 16+16 | 8.1732 | 0 |  | 8.1732 | 0 | 16.8 | 8.6268 |  |  |  | Sн. LV, МVА | 16+16 | 0 | 8.1732 | 0 |  | 8.1732 | 0 | 16.8 | 8.6268
69 | SS-110/6kv Chemical plant | 32+32 | 10.0162 | 5.56 | 45 | 4.4562 | 0 | 33.6 | 29.1438 | 29.1438 | opened | 69 | SS-110/6kv Chemical plant | 32+32 | 0 | 10.0162 | 5.56 | 45 | 4.4562 | 0 | 33.6 | 29.1438 | 29.1438 | opened
70 | SS-110/10kv Tsentralnaya | 40+40 | 22.8863 | 0 |  | 22.8863 | 0 | 42 | 19.1137 | 19.1137 | opened | 70 | SS-110/10kv Tsentralnaya | 40+40 | 0.181 | 23.0673 | 0 |  | 23.0673 | 0 | 42 | 18.9327 | 18.9327 | opened
71 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23.7143 | 20.54 | 80 | 3.1743 | 0 | 26.25 | 23.0757 | 23.0757 | opened | 71 | SS-110/35/10kv Cheremoshnoe | 25+25 | 0 | 23.7143 | 20.54 | 80 | 3.1743 | 0 | 26.25 | 23.0757 | 23.0757 | opened
| Sн. MV, МVА | 25+25 | 22.176 | 19.676 |  | 2.5 | 0 | 26.25 | 23.75 |  |  |  | Sн. MV, МVА | 25+25 | 0 | 22.176 | 19.676 |  | 2.5 | 0 | 26.25 | 23.75
| Sн. LV, МVА | 25+25 | 1.5383 | 0 |  | 1.5383 | 0 | 26.25 | 24.7117 |  |  |  | Sн. LV, МVА | 25+25 | 0 | 1.5383 | 0 |  | 1.5383 | 0 | 26.25 | 24.7117
72 | SS-110/35/10kv Chernyanka | 16+25 | 14.7605 | 5.969 | 120 | 8.7915 | 0 | 16.8 | 8.0085 | 8.0085 | opened | 72 | SS-110/35/10kv Chernyanka | 16+25 | 0.0556 | 14.8161 | 5.969 | 120 | 8.8471 | 0 | 16.8 | 7.9529 | 7.9529 | opened
| Sн. MV, МVА | 16+25 | 5.969 | 5.969 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Sн. MV, МVА | 16+25 | 0 | 5.969 | 5.969 |  | 0 | 0 | 16.8 | 16.8
| Sн. LV, МVА | 16+25 | 8.7915 | 0 |  | 8.7915 | 0 | 16.8 | 8.0085 |  |  |  | Sн. LV, МVА | 16+25 | 0.0556 | 8.8471 | 0 |  | 8.8471 | 0 | 16.8 | 7.9529
73 | SS-110/35/6kv Shebekino | 40+40 | 25.5429 | 16.65 | 120 | 8.8929 | 0 | 42 | 33.1071 | 33.1071 | opened | 73 | SS-110/35/6kv Shebekino | 40+40 | 0.248 | 25.7909 | 16.65 | 120 | 9.1409 | 0 | 42 | 32.8591 | 32.8591 | opened
| Sн. MV, МVА | 40+40 | 14.582 | 11.682 |  | 2.9 | 0 | 42 | 39.1 |  |  |  | Sн. MV, МVА | 40+40 | 0 | 14.582 | 11.682 |  | 2.9 | 0 | 42 | 39.1
| Sн. LV, МVА | 40+40 | 10.9609 | 4.968 |  | 5.9929 | 0 | 42 | 36.0071 |  |  |  | Sн. LV, МVА | 40+40 | 0.248 | 11.2089 | 4.968 |  | 6.2409 | 0 | 42 | 35.7591
74 | SS-110/10kv Sheino | 3,2+10 | 2.4086 | 0 |  | 2.4086 | 0 | 3.36 | 0.95136 | 0.95136 | opened | 74 | SS-110/10kv Sheino | 3,2+10 | 0.015 | 2.4236 | 0 |  | 2.4236 | 0 | 3.36 | 0.93636 | 0.93636 | opened
75 | SS-110/10/6kv Yuzhnaya | 40+40 | 43.0909 | 12.94 | 120 | 30.1509 | 0 | 42 | 11.8491 | 11.8491 | opened | 75 | SS-110/10/6kv Yuzhnaya | 40+40 | 0.801 | 43.8919 | 12.94 | 120 | 30.9519 | 0 | 42 | 11.0481 | 11.0481 | opened
| Sн. MV, МVА | 40+40 | 6.8549 | 3.42 |  | 3.4349 | 0 | 42 | 38.5651 |  |  |  | Sн. MV, МVА | 40+40 | 0.00434 | 6.8593 | 3.42 |  | 3.4393 | 0 | 42 | 38.5607
| Sн. LV, МVА | 40+40 | 36.236 | 9.52 |  | 26.716 | 0 | 42 | 15.284 |  |  |  | Sн. LV, МVА | 40+40 | 0.79666 | 37.0327 | 9.52 |  | 27.5127 | 0 | 42 | 14.4873
76 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0.68343 | 0.43267 | 120 | 0.25076 | 0 | 2.625 | 2.3742 | 2.3742 | opened | 76 | SS-35/10kv Aleynikovo | 2,5+2,5 | 0 | 0.68343 | 0.43267 | 120 | 0.25076 | 0 | 2.625 | 2.3742 | 2.3742 | opened
77 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 0.85294 | 0.46639 | 120 | 0.38655 | 0 | 2.625 | 2.2384 | 2.2384 | opened | 77 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 0 | 0.85294 | 0.46639 | 120 | 0.38655 | 0 | 2.625 | 2.2384 | 2.2384 | opened
78 | SS-35/10kv Alexeevka (kor.) | 2,5+4 | 2.7122 | 0 |  | 2.7122 | 0 | 2.625 | -0.087197 | -0.087197 | closed | 78 | SS-35/10kv Alexeevka (kor.) | 2,5+4 | 0 | 2.7122 | 0 |  | 2.7122 | 0 | 2.625 | -0.087197 | -0.087197 | closed
79 | SS-35/10kv Annovka | 2,5+2,5 | 0.82901 | 0.44652 | 80 | 0.38249 | 0 | 2.625 | 2.2425 | 2.2425 | opened | 79 | SS-35/10kv Annovka | 2,5+2,5 | 0 | 0.82901 | 0.44652 | 80 | 0.38249 | 0 | 2.625 | 2.2425 | 2.2425 | opened
80 | SS-35/10kv Artelnoe | 6,3+6,3 | 6.0242 | 0.55 | 45 | 5.4742 | 0 | 6.615 | 1.1408 | 1.1408 | opened | 80 | SS-35/10kv Artelnoe | 6,3+6,3 | 0 | 6.0242 | 0.55 | 45 | 5.4742 | 0 | 6.615 | 1.1408 | 1.1408 | opened
81 | SS-35/10kv B.Dvory | 4+4 | 2.4199 | 1.191 | 120 | 1.2289 | 0 | 4.2 | 2.9711 | 2.9711 | opened | 81 | SS-35/10kv B.Dvory | 4+4 | 0 | 2.4199 | 1.191 | 120 | 1.2289 | 0 | 4.2 | 2.9711 | 2.9711 | opened
82 | SS-35/10kv B.Ivanovka | 4+4 | 0.98132 | 0.62488 | 80 | 0.35644 | 0 | 4.2 | 3.8436 | 3.8436 | opened | 82 | SS-35/10kv B.Ivanovka | 4+4 | 0 | 0.98132 | 0.62488 | 80 | 0.35644 | 0 | 4.2 | 3.8436 | 3.8436 | opened
83 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0.71309 | 0.44779 | 45 | 0.2653 | 0 | 2.625 | 2.3597 | 2.3597 | opened | 83 | SS-35/10kv B.Kolodez | 2,5+2,5 | 0 | 0.71309 | 0.44779 | 45 | 0.2653 | 0 | 2.625 | 2.3597 | 2.3597 | opened
84 | SS-35/10kv B.Ples | 2,5+2,5 | 0.68493 | 0.606 | 45 | 0.078931 | 0 | 2.625 | 2.5461 | 2.5461 | opened | 84 | SS-35/10kv B.Ples | 2,5+2,5 | 0 | 0.68493 | 0.606 | 45 | 0.078931 | 0 | 2.625 | 2.5461 | 2.5461 | opened
85 | SS-35/10kv B.Troitsa | 6,3+6,3 | 4.2829 | 2.83 | 45 | 1.4529 | 0 | 6.615 | 5.1621 | 5.1621 | opened | 85 | SS-35/10kv B.Troitsa | 6,3+6,3 | 0.381 | 4.6639 | 2.83 | 45 | 1.8339 | 0 | 6.615 | 4.7811 | 4.7811 | opened
86 | SS-35/10kv Belovskoe | 4+4 | 3.6674 | 1.21 | 80 | 2.4574 | 0 | 4.2 | 1.7426 | 1.7426 | opened | 86 | SS-35/10kv Belovskoe | 4+4 | 0 | 3.6674 | 1.21 | 80 | 2.4574 | 0 | 4.2 | 1.7426 | 1.7426 | opened
87 | SS-35/10kv Belyanka | 2,5+4 | 2.1233 | 1.3214 | 45 | 0.80191 | 0 | 2.625 | 1.8231 | 1.8231 | opened | 87 | SS-35/10kv Belyanka | 2,5+4 | 0.139 | 2.2623 | 1.3214 | 45 | 0.94091 | 0 | 2.625 | 1.6841 | 1.6841 | opened
88 | SS-35/10kv Bessonovka | 6,3+6,3 | 6.1466 | 0.918 | 120 | 5.2286 | 0 | 6.615 | 1.3864 | 1.3864 | opened | 88 | SS-35/10kv Bessonovka | 6,3+6,3 | 0 | 6.1466 | 0.918 | 120 | 5.2286 | 0 | 6.615 | 1.3864 | 1.3864 | opened
89 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.89313 | 0.522 | 45 | 0.37113 | 0 | 1.68 | 1.3089 | 1.3089 | opened | 89 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 0.023 | 0.91613 | 0.522 | 45 | 0.39413 | 0 | 1.68 | 1.2859 | 1.2859 | opened
90 | SS-35/10kv V.Mikhailovka | 4+4 | 2.3356 | 1.45 | 80 | 0.88559 | 0 | 4.2 | 3.3144 | 3.3144 | opened | 90 | SS-35/10kv V.Mikhailovka | 4+4 | 0 | 2.3356 | 1.45 | 80 | 0.88559 | 0 | 4.2 | 3.3144 | 3.3144 | opened
91 | SS-35/10kv Varvarovka | 2,5+2,5 | 1.8017 | 1.0795 | 120 | 0.7222 | 0 | 2.625 | 1.9028 | 1.9028 | opened | 91 | SS-35/10kv Varvarovka | 2,5+2,5 | 0 | 1.8017 | 1.0795 | 120 | 0.7222 | 0 | 2.625 | 1.9028 | 1.9028 | opened
92 | SS-35/10kv Vengerovka | 2,5+2,5 | 1.0438 | 0.4 | 120 | 0.64378 | 0 | 2.625 | 1.9812 | 1.9812 | opened | 92 | SS-35/10kv Vengerovka | 2,5+2,5 | 0 | 1.0438 | 0.4 | 120 | 0.64378 | 0 | 2.625 | 1.9812 | 1.9812 | opened
93 | SS-35/10kv Verkhopenye | 2,5+4 | 1.6176 | 1.0177 | 45 | 0.59993 | 0 | 2.625 | 2.0251 | 2.0251 | opened | 93 | SS-35/10kv Verkhopenye | 2,5+4 | 0 | 1.6176 | 1.0177 | 45 | 0.59993 | 0 | 2.625 | 2.0251 | 2.0251 | opened
94 | SS-35/10kv Viktoropol | 2,5+4 | 1.2991 | 0.95536 | 120 | 0.34378 | 0 | 2.625 | 2.2812 | 2.2812 | opened | 94 | SS-35/10kv Viktoropol | 2,5+4 | 0 | 1.2991 | 0.95536 | 120 | 0.34378 | 0 | 2.625 | 2.2812 | 2.2812 | opened
95 | SS-35/10kv Vislaya Dubrava | 4+4 | 2.5729 | 0.616 | 80 | 1.9569 | 0 | 4.2 | 2.2431 | 2.2431 | opened | 95 | SS-35/10kv Vislaya Dubrava | 4+4 | 0 | 2.5729 | 0.616 | 80 | 1.9569 | 0 | 4.2 | 2.2431 | 2.2431 | opened
96 | SS-35/10kv Vladimirovka | 4+4 | 0.82947 | 0 |  | 0.82947 | 0 | 4.2 | 3.3705 | 3.3705 | opened | 96 | SS-35/10kv Vladimirovka | 4+4 | 0 | 0.82947 | 0 |  | 0.82947 | 0 | 4.2 | 3.3705 | 3.3705 | opened
97 | SS-35/10kv Water storage | 2,5+6,3 | 2.3374 | 0.305 | 45 | 2.0324 | 0 | 2.625 | 0.59262 | 0.59262 | opened | 97 | SS-35/10kv Water storage | 2,5+6,3 | 0.015 | 2.3524 | 0.305 | 45 | 2.0474 | 0 | 2.625 | 0.57762 | 0.57762 | opened
98 | SS-35/6kv Vostochnaya | 4+4 | 3.8357 | 1.43 | 120 | 2.4057 | 0 | 4.2 | 1.7943 | 1.7943 | opened | 98 | SS-35/6kv Vostochnaya | 4+4 | 0 | 3.8357 | 1.43 | 120 | 2.4057 | 0 | 4.2 | 1.7943 | 1.7943 | opened
99 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1.7363 | 0.99513 | 120 | 0.7412 | 0 | 2.625 | 1.8838 | 1.8838 | opened | 99 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 0 | 1.7363 | 0.99513 | 120 | 0.7412 | 0 | 2.625 | 1.8838 | 1.8838 | opened
100 | SS-35/10kv Glinnoe | 2,5+6,3 | 2.3586 | 1.4036 | 80 | 0.95502 | 0 | 2.625 | 1.67 | 1.67 | opened | 100 | SS-35/10kv Glinnoe | 2,5+6,3 | 0 | 2.3586 | 1.4036 | 80 | 0.95502 | 0 | 2.625 | 1.67 | 1.67 | opened
101 | SS-35/10kv Golovchino | 2,5+2,5 | 2.8532 | 0.617 | 45 | 2.2362 | 0 | 2.625 | 0.38878 | 0.38878 | opened | 101 | SS-35/10kv Golovchino | 2,5+2,5 | 0 | 2.8532 | 0.617 | 45 | 2.2362 | 0 | 2.625 | 0.38878 | 0.38878 | opened
102 | SS-35/10kv Gora-Podol | 2,5+4 | 2.1262 | 0.9085 | 45 | 1.2177 | 0 | 2.625 | 1.4073 | 1.4073 | opened | 102 | SS-35/10kv Gora-Podol | 2,5+4 | 0.04 | 2.1662 | 0.9085 | 45 | 1.2577 | 0 | 2.625 | 1.3673 | 1.3673 | opened
103 | SS-35/10kv Gorodishche | 4+4 | 2.0102 | 0 |  | 2.0102 | 0 | 4.2 | 2.1898 | 2.1898 | opened | 103 | SS-35/10kv Gorodishche | 4+4 | 0.04 | 2.0502 | 0 |  | 2.0502 | 0 | 4.2 | 2.1498 | 2.1498 | opened
104 | SS-35/10kv Dmitrievka | 4+4 | 1.1117 | 0.78237 | 80 | 0.32936 | 0 | 4.2 | 3.8706 | 3.8706 | opened | 104 | SS-35/10kv Dmitrievka | 4+4 | 0 | 1.1117 | 0.78237 | 80 | 0.32936 | 0 | 4.2 | 3.8706 | 3.8706 | opened
105 | SS-35/10kv Dorogoshch | 4+4 | 2.336 | 1.054 | 45 | 1.282 | 0 | 4.2 | 2.918 | 2.918 | opened | 105 | SS-35/10kv Dorogoshch | 4+4 | 0 | 2.336 | 1.054 | 45 | 1.282 | 0 | 4.2 | 2.918 | 2.918 | opened
106 | SS-35/10kv Dragunka | 2,5+2,5 | 0.91285 | 0.62999 | 80 | 0.28285 | 0 | 2.625 | 2.3421 | 2.3421 | opened | 106 | SS-35/10kv Dragunka | 2,5+2,5 | 0 | 0.91285 | 0.62999 | 80 | 0.28285 | 0 | 2.625 | 2.3421 | 2.3421 | opened
107 | SS-35/10kv Zhuravlevka | 2,5+4 | 1.0482 | 0.274 | 80 | 0.77423 | 0 | 2.625 | 1.8508 | 1.8508 | opened | 107 | SS-35/10kv Zhuravlevka | 2,5+4 | 0 | 1.0482 | 0.274 | 80 | 0.77423 | 0 | 2.625 | 1.8508 | 1.8508 | opened
108 | SS-35/6kv Zhuravliki | 10+10 | 2.7748 | 4.051 | 120 | -1.2762 | 0 | 10.5 | 11.7762 | 11.7762 | opened | 108 | SS-35/6kv Zhuravliki | 10+10 | 0.32 | 3.0948 | 4.051 | 120 | -0.95621 | 0 | 10.5 | 11.4562 | 11.4562 | opened
109 | SS-35/10kv Zavidovka | 2,5+2,5 | 0.5591 | 0.42 | 80 | 0.1391 | 0 | 2.625 | 2.4859 | 2.4859 | opened | 109 | SS-35/10kv Zavidovka | 2,5+2,5 | 0 | 0.5591 | 0.42 | 80 | 0.1391 | 0 | 2.625 | 2.4859 | 2.4859 | opened
110 | SS-35/6kv Zapadnaya | 10+10+10 | 6.669 | 1.707 | 120 | 4.962 | 0 | 21 | 16.038 | 16.038 | opened | 110 | SS-35/6kv Zapadnaya | 10+10+10 | 0 | 6.669 | 1.707 | 120 | 4.962 | 0 | 21 | 16.038 | 16.038 | opened
111 | SS-35/10kv Zozuli | 6,3+6,3 | 6.1054 | 3.88 | 80 | 2.2254 | 0 | 6.615 | 4.3896 | 4.3896 | opened | 111 | SS-35/10kv Zozuli | 6,3+6,3 | 0 | 6.1054 | 3.88 | 80 | 2.2254 | 0 | 6.615 | 4.3896 | 4.3896 | opened
112 | SS-35/10kv Ivitsa | 2,5+2,5 | 0.75033 | 0.58603 | 80 | 0.1643 | 0 | 2.625 | 2.4607 | 2.4607 | opened | 112 | SS-35/10kv Ivitsa | 2,5+2,5 | 0 | 0.75033 | 0.58603 | 80 | 0.1643 | 0 | 2.625 | 2.4607 | 2.4607 | opened
113 | SS-35/10kv Ilovka | 4+4 | 2.5108 | 2.056 | 45 | 0.45485 | 0 | 4.2 | 3.7452 | 3.7452 | opened | 113 | SS-35/10kv Ilovka | 4+4 | 0 | 2.5108 | 2.056 | 45 | 0.45485 | 0 | 4.2 | 3.7452 | 3.7452 | opened
114 | SS-35/10kv Istobnoe | 4+2,5 | 1.3347 | 0.93935 | 120 | 0.39532 | 0 | 2.625 | 2.2297 | 2.2297 | opened | 114 | SS-35/10kv Istobnoe | 4+2,5 | 0 | 1.3347 | 0.93935 | 120 | 0.39532 | 0 | 2.625 | 2.2297 | 2.2297 | opened
115 | SS-35/10kv Kazatskaya | 2,5+4 | 1.0803 | 0.87141 | 45 | 0.20887 | 0 | 2.625 | 2.4161 | 2.4161 | opened | 115 | SS-35/10kv Kazatskaya | 2,5+4 | 0 | 1.0803 | 0.87141 | 45 | 0.20887 | 0 | 2.625 | 2.4161 | 2.4161 | opened
116 | SS-35/10kv Kazinka | 4+4 | 2.7215 | 0.736 | 120 | 1.9855 | 0 | 4.2 | 2.2145 | 2.2145 | opened | 116 | SS-35/10kv Kazinka | 4+4 | 0 | 2.7215 | 0.736 | 120 | 1.9855 | 0 | 4.2 | 2.2145 | 2.2145 | opened
117 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1.0111 | 0.712 | 120 | 0.29912 | 0 | 2.625 | 2.3259 | 2.3259 | opened | 117 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 0 | 1.0111 | 0.712 | 120 | 0.29912 | 0 | 2.625 | 2.3259 | 2.3259 | opened
118 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3.3551 | 0.7035 | 120 | 2.6516 | 0 | 6.615 | 3.9634 | 3.9634 | opened | 118 | SS-35/10kv Kirovskaya | 6,3+6,3 | 0 | 3.3551 | 0.7035 | 120 | 2.6516 | 0 | 6.615 | 3.9634 | 3.9634 | opened
119 | SS-35/10kv Kotovo | 2,5+2,5 | 2.2315 | 1.648 | 20 | 0.58345 | 0 | 2.625 | 2.0416 | 2.0416 | opened | 119 | SS-35/10kv Kotovo | 2,5+2,5 | 0 | 2.2315 | 1.648 | 20 | 0.58345 | 0 | 2.625 | 2.0416 | 2.0416 | opened
120 | SS-35/10kv Kochetovka | 2,5+4 | 0.925 | 0.6286 | 45 | 0.2964 | 0 | 2.625 | 2.3286 | 2.3286 | opened | 120 | SS-35/10kv Kochetovka | 2,5+4 | 0 | 0.925 | 0.6286 | 45 | 0.2964 | 0 | 2.625 | 2.3286 | 2.3286 | opened
121 | SS-35/10kv Krasnoe | 4+2,5 | 1.4836 | 1.1395 | 80 | 0.34407 | 0 | 2.625 | 2.2809 | 2.2809 | opened | 121 | SS-35/10kv Krasnoe | 4+2,5 | 0 | 1.4836 | 1.1395 | 80 | 0.34407 | 0 | 2.625 | 2.2809 | 2.2809 | opened
122 | SS-35/10kv Kretovo | 4+2,5 | 1.2222 | 0.67818 | 120 | 0.54399 | 0 | 2.625 | 2.081 | 2.081 | opened | 122 | SS-35/10kv Kretovo | 4+2,5 | 0.007 | 1.2292 | 0.67818 | 120 | 0.55099 | 0 | 2.625 | 2.074 | 2.074 | opened
123 | SS-35/10kv Kurasovka | 4+4 | 2.9712 | 1.797 | 80 | 1.1742 | 0 | 4.2 | 3.0258 | 3.0258 | opened | 123 | SS-35/10kv Kurasovka | 4+4 | 0.03 | 3.0012 | 1.797 | 80 | 1.2042 | 0 | 4.2 | 2.9958 | 2.9958 | opened
124 | SS-35/6kv Lebedi | 4+5,6 | 4.2778 | 0.581 | 120 | 3.6968 | 0 | 4.2 | 0.50325 | 0.50325 | opened | 124 | SS-35/6kv Lebedi | 4+5,6 | 0 | 4.2778 | 0.581 | 120 | 3.6968 | 0 | 4.2 | 0.50325 | 0.50325 | opened
125 | SS-35/6kv Ledovaya | 4+4 | 2.6408 | 1.321 | 80 | 1.3198 | 0 | 4.2 | 2.8802 | 2.8802 | opened | 125 | SS-35/6kv Ledovaya | 4+4 | 0 | 2.6408 | 1.321 | 80 | 1.3198 | 0 | 4.2 | 2.8802 | 2.8802 | opened
126 | SS-35/10kv Livenka | 4+4 | 2.0098 | 1.541 | 120 | 0.46885 | 0 | 4.2 | 3.7312 | 3.7312 | opened | 126 | SS-35/10kv Livenka | 4+4 | 0.749 | 2.7588 | 1.541 | 120 | 1.2178 | 0 | 4.2 | 2.9822 | 2.9822 | opened
127 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0.87131 | 0.66672 | 80 | 0.2046 | 0 | 2.625 | 2.4204 | 2.4204 | opened | 127 | SS-35/10kv Lubyanoe | 2,5+2,5 | 0 | 0.87131 | 0.66672 | 80 | 0.2046 | 0 | 2.625 | 2.4204 | 2.4204 | opened
128 | SS-35/10kv M.Pristan | 6,3+6,3 | 6.3025 | 1.81 | 45 | 4.4925 | 0 | 6.615 | 2.1225 | 2.1225 | opened | 128 | SS-35/10kv M.Pristan | 6,3+6,3 | 0 | 6.3025 | 1.81 | 45 | 4.4925 | 0 | 6.615 | 2.1225 | 2.1225 | opened
129 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0.82513 | 0.60716 | 80 | 0.21797 | 0 | 2.625 | 2.407 | 2.407 | opened | 129 | SS-35/10kv М.Troitsa | 2,5+2,5 | 0 | 0.82513 | 0.60716 | 80 | 0.21797 | 0 | 2.625 | 2.407 | 2.407 | opened
130 | SS-35/10kv Malinovka | 10+10 | 6.2085 | 1.357 | 120 | 4.8515 | 0 | 10.5 | 5.6485 | 5.6485 | opened | 130 | SS-35/10kv Malinovka | 10+10 | 0 | 6.2085 | 1.357 | 120 | 4.8515 | 0 | 10.5 | 5.6485 | 5.6485 | opened
131 | SS-35/10kv Mandrovo | 2,5+2,5 | 1.3454 | 0.65565 | 80 | 0.68976 | 0 | 2.625 | 1.9352 | 1.9352 | opened | 131 | SS-35/10kv Mandrovo | 2,5+2,5 | 0 | 1.3454 | 0.65565 | 80 | 0.68976 | 0 | 2.625 | 1.9352 | 1.9352 | opened
132 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1.0881 | 0.643 | 80 | 0.44506 | 0 | 2.625 | 2.1799 | 2.1799 | opened | 132 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 0 | 1.0881 | 0.643 | 80 | 0.44506 | 0 | 2.625 | 2.1799 | 2.1799 | opened
133 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1.0776 | 0.59315 | 120 | 0.48443 | 0 | 2.625 | 2.1406 | 2.1406 | opened | 133 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 0 | 1.0776 | 0.59315 | 120 | 0.48443 | 0 | 2.625 | 2.1406 | 2.1406 | opened
134 | SS-35/10kv N.Derevnya | 4+4 | 4.6246 | 2.78 | 120 | 1.8446 | 0 | 4.2 | 2.3554 | 2.3554 | opened | 134 | SS-35/10kv N.Derevnya | 4+4 | 0 | 4.6246 | 2.78 | 120 | 1.8446 | 0 | 4.2 | 2.3554 | 2.3554 | opened
135 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 1.5956 | 0.842 | 45 | 0.75359 | 0 | 6.615 | 5.8614 | 5.8614 | opened | 135 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 0 | 1.5956 | 0.842 | 45 | 0.75359 | 0 | 6.615 | 5.8614 | 5.8614 | opened
136 | SS-35/10kv N.Ukolovo | 4+2,5 | 1.6545 | 0.57 | 80 | 1.0845 | 0 | 2.625 | 1.5405 | 1.5405 | opened | 136 | SS-35/10kv N.Ukolovo | 4+2,5 | 0 | 1.6545 | 0.57 | 80 | 1.0845 | 0 | 2.625 | 1.5405 | 1.5405 | opened
137 | SS-35/10kv N.Khutornoe | 2,5+4 | 0.30823 | 0.19 | 80 | 0.11823 | 0 | 2.625 | 2.5068 | 2.5068 | opened | 137 | SS-35/10kv N.Khutornoe | 2,5+4 | 0 | 0.30823 | 0.19 | 80 | 0.11823 | 0 | 2.625 | 2.5068 | 2.5068 | opened
138 | SS-35/10kv Neminushchee | 2,5+1,6 | 1.0176 | 0.65147 | 80 | 0.36609 | 0 | 1.68 | 1.3139 | 1.3139 | opened | 138 | SS-35/10kv Neminushchee | 2,5+1,6 | 0 | 1.0176 | 0.65147 | 80 | 0.36609 | 0 | 1.68 | 1.3139 | 1.3139 | opened
139 | SS-35/10kv Nechaevka | 4+4 | 1.8217 | 0.451 | 120 | 1.3707 | 0 | 4.2 | 2.8293 | 2.8293 | opened | 139 | SS-35/10kv Nechaevka | 4+4 | 0.05 | 1.8717 | 0.451 | 120 | 1.4207 | 0 | 4.2 | 2.7793 | 2.7793 | opened
140 | SS-35/10kv Nikitovka | 2,5+2,5 | 1.8019 | 1.4354 | 80 | 0.36645 | 0 | 2.625 | 2.2585 | 2.2585 | opened | 140 | SS-35/10kv Nikitovka | 2,5+2,5 | 0 | 1.8019 | 1.4354 | 80 | 0.36645 | 0 | 2.625 | 2.2585 | 2.2585 | opened
141 | SS-35/10kv Novenkoe | 4+4 | 2.1525 | 1.7332 | 80 | 0.41931 | 0 | 4.2 | 3.7807 | 3.7807 | opened | 141 | SS-35/10kv Novenkoe | 4+4 | 0 | 2.1525 | 1.7332 | 80 | 0.41931 | 0 | 4.2 | 3.7807 | 3.7807 | opened
142 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 8.1276 | 0.872 | 80 | 7.2556 | 0 | 6.615 | -0.64061 | -0.64061 | closed | 142 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.004 | 8.1316 | 0.872 | 80 | 7.2596 | 0 | 6.615 | -0.64461 | -0.64461 | closed
143 | SS-35/10kv Orlik | 4+4 | 2.0824 | 0.553 | 80 | 1.5294 | 0 | 4.2 | 2.6706 | 2.6706 | opened | 143 | SS-35/10kv Orlik | 4+4 | 0 | 2.0824 | 0.553 | 80 | 1.5294 | 0 | 4.2 | 2.6706 | 2.6706 | opened
144 | SS-35/10kv Podolkhi | 2,5+2,5 | 1.5603 | 1.1225 | 45 | 0.43784 | 0 | 2.625 | 2.1872 | 2.1872 | opened | 144 | SS-35/10kv Podolkhi | 2,5+2,5 | 0.0055 | 1.5658 | 1.1225 | 45 | 0.44334 | 0 | 2.625 | 2.1817 | 2.1817 | opened
145 | SS-35/10kv Popovka | 6,3+4 | 1.1758 | 0.64636 | 80 | 0.52942 | 0 | 4.2 | 3.6706 | 3.6706 | opened | 145 | SS-35/10kv Popovka | 6,3+4 | 0 | 1.1758 | 0.64636 | 80 | 0.52942 | 0 | 4.2 | 3.6706 | 3.6706 | opened
146 | SS-35/10kv Prelestnoe | 6,3+6,3 | 2.3992 | 0 |  | 2.3992 | 0 | 6.615 | 4.2158 | 4.2158 | opened | 146 | SS-35/10kv Prelestnoe | 6,3+6,3 | 0 | 2.3992 | 0 |  | 2.3992 | 0 | 6.615 | 4.2158 | 4.2158 | opened
147 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5.6912 | 0 |  | 5.6912 | 0 | 6.615 | 0.92376 | 0.92376 | opened | 147 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 0 | 5.6912 | 0 |  | 5.6912 | 0 | 6.615 | 0.92376 | 0.92376 | opened
148 | SS-35/10kv Prilepy | 2,5+4 | 0.49609 | 0.37638 | 80 | 0.11972 | 0 | 2.625 | 2.5053 | 2.5053 | opened | 148 | SS-35/10kv Prilepy | 2,5+4 | 0 | 0.49609 | 0.37638 | 80 | 0.11972 | 0 | 2.625 | 2.5053 | 2.5053 | opened
149 | SS-35/10kv Printsevka | 2,5+2,5 | 1.114 | 0.352 | 120 | 0.76204 | 0 | 2.625 | 1.863 | 1.863 | opened | 149 | SS-35/10kv Printsevka | 2,5+2,5 | 0 | 1.114 | 0.352 | 120 | 0.76204 | 0 | 2.625 | 1.863 | 1.863 | opened
150 | SS-35/10kv Radkovka | 4+4 | 2.5116 | 0.164 | 45 | 2.3476 | 0 | 4.2 | 1.8524 | 1.8524 | opened | 150 | SS-35/10kv Radkovka | 4+4 | 0 | 2.5116 | 0.164 | 45 | 2.3476 | 0 | 4.2 | 1.8524 | 1.8524 | opened
151 | SS-35/10kv Razdornoe | 2,5+2,5 | 1.1029 | 0.662 | 80 | 0.44089 | 0 | 2.625 | 2.1841 | 2.1841 | opened | 151 | SS-35/10kv Razdornoe | 2,5+2,5 | 0 | 1.1029 | 0.662 | 80 | 0.44089 | 0 | 2.625 | 2.1841 | 2.1841 | opened
152 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1.693 | 0.88491 | 80 | 0.80806 | 0 | 2.625 | 1.8169 | 1.8169 | opened | 152 | SS-35/10kv Repyakhovka | 2,5+2,5 | 0.001 | 1.694 | 0.88491 | 80 | 0.80906 | 0 | 2.625 | 1.8159 | 1.8159 | opened
153 | SS-35/10kv Rzhevka | 6,3+6,3 | 5.9105 | 2.53 | 45 | 3.3805 | 0 | 6.615 | 3.2345 | 3.2345 | opened | 153 | SS-35/10kv Rzhevka | 6,3+6,3 | 0 | 5.9105 | 2.53 | 45 | 3.3805 | 0 | 6.615 | 3.2345 | 3.2345 | opened
154 | SS-35/10kv Rovenki | 4+4 | 2.9281 | 1.7393 | 120 | 1.1888 | 0 | 4.2 | 3.0112 | 3.0112 | opened | 154 | SS-35/10kv Rovenki | 4+4 | 0 | 2.9281 | 1.7393 | 120 | 1.1888 | 0 | 4.2 | 3.0112 | 3.0112 | opened
155 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1.5623 | 0 |  | 1.5623 | 0 | 2.625 | 1.0627 | 1.0627 | opened | 155 | SS-35/10kv Rogovatoe | 2,5+2,5 | 0 | 1.5623 | 0 |  | 1.5623 | 0 | 2.625 | 1.0627 | 1.0627 | opened
156 | SS-35/10kv Saprykino | 2,5+2,5 | 0.45462 | 0.22751 | 120 | 0.22711 | 0 | 2.625 | 2.3979 | 2.3979 | opened | 156 | SS-35/10kv Saprykino | 2,5+2,5 | 0 | 0.45462 | 0.22751 | 120 | 0.22711 | 0 | 2.625 | 2.3979 | 2.3979 | opened
157 | SS-35/6kv Severnaya | 6,3+6,3 | 6.9665 | 4.8049 | 120 | 2.1616 | 0 | 6.615 | 4.4534 | 4.4534 | opened | 157 | SS-35/6kv Severnaya | 6,3+6,3 | 0.04447 | 7.011 | 4.8049 | 120 | 2.2061 | 0 | 6.615 | 4.4089 | 4.4089 | opened
158 | SS-35/10kv Setishche | 2,5+2,5 | 1.7003 | 1.0621 | 80 | 0.6382 | 0 | 2.625 | 1.9868 | 1.9868 | opened | 158 | SS-35/10kv Setishche | 2,5+2,5 | 0 | 1.7003 | 1.0621 | 80 | 0.6382 | 0 | 2.625 | 1.9868 | 1.9868 | opened
159 | SS-35/10kv Slonovka | 4+4 | 1.698 | 1.1306 | 120 | 0.56739 | 0 | 4.2 | 3.6326 | 3.6326 | opened | 159 | SS-35/10kv Slonovka | 4+4 | 0 | 1.698 | 1.1306 | 120 | 0.56739 | 0 | 4.2 | 3.6326 | 3.6326 | opened
160 | SS-35/6kv St.Oskol -2 | 16+16 | 9.3714 | 1.21 | 80 | 8.1614 | 0 | 16.8 | 8.6386 | 8.6386 | opened | 160 | SS-35/6kv St.Oskol -2 | 16+16 | 0 | 9.3714 | 1.21 | 80 | 8.1614 | 0 | 16.8 | 8.6386 | 8.6386 | opened
161 | SS-35/10kv Starikovo | 2,5+2,5 | 2.803 | 1.3453 | 45 | 1.4577 | 0 | 2.625 | 1.1673 | 1.1673 | opened | 161 | SS-35/10kv Starikovo | 2,5+2,5 | 0 | 2.803 | 1.3453 | 45 | 1.4577 | 0 | 2.625 | 1.1673 | 1.1673 | opened
162 | SS-35/10kv Tavrovo | 10+10 | 7.7046 | 0.531 | 45 | 7.1736 | 0 | 10.5 | 3.3264 | 3.3264 | opened | 162 | SS-35/10kv Tavrovo | 10+10 | 0.28 | 7.9846 | 0.531 | 45 | 7.4536 | 0 | 10.5 | 3.0464 | 3.0464 | opened
163 | SS-35/10kv Terebrino | 2,5+2,5 | 0.69752 | 0.44978 | 80 | 0.24773 | 0 | 2.625 | 2.3773 | 2.3773 | opened | 163 | SS-35/10kv Terebrino | 2,5+2,5 | 0 | 0.69752 | 0.44978 | 80 | 0.24773 | 0 | 2.625 | 2.3773 | 2.3773 | opened
164 | SS-35/10kv Urazovo | 6,3+6,3 | 4.571 | 1.39 | 120 | 3.181 | 0 | 6.615 | 3.434 | 3.434 | opened | 164 | SS-35/10kv Urazovo | 6,3+6,3 | 0 | 4.571 | 1.39 | 120 | 3.181 | 0 | 6.615 | 3.434 | 3.434 | opened
165 | SS-35/10kv Utochka | 1,6+2,5 | 0.74863 | 0.47242 | 80 | 0.27621 | 0 | 1.68 | 1.4038 | 1.4038 | opened | 165 | SS-35/10kv Utochka | 1,6+2,5 | 0 | 0.74863 | 0.47242 | 80 | 0.27621 | 0 | 1.68 | 1.4038 | 1.4038 | opened
166 | SS-35/6kv Fedoseevka | 4+4 | 1.9262 | 0 |  | 1.9262 | 0 | 4.2 | 2.2738 | 2.2738 | opened | 166 | SS-35/6kv Fedoseevka | 4+4 | 0 | 1.9262 | 0 |  | 1.9262 | 0 | 4.2 | 2.2738 | 2.2738 | opened
167 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0.90356 | 0.78681 | 45 | 0.11676 | 0 | 1.68 | 1.5632 | 1.5632 | opened | 167 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 0 | 0.90356 | 0.78681 | 45 | 0.11676 | 0 | 1.68 | 1.5632 | 1.5632 | opened
168 | SS-35/10kv Kholodnoe | 2,5+4 | 1.7614 | 0 |  | 1.7614 | 0 | 2.625 | 0.86363 | 0.86363 | opened | 168 | SS-35/10kv Kholodnoe | 2,5+4 | 0 | 1.7614 | 0 |  | 1.7614 | 0 | 2.625 | 0.86363 | 0.86363 | opened
169 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1.6135 | 1.3513 | 20 | 0.26228 | 0 | 6.615 | 6.3527 | 6.3527 | opened | 169 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 0.63 | 2.2435 | 1.3513 | 20 | 0.89228 | 0 | 6.615 | 5.7227 | 5.7227 | opened
170 | SS-35/10kv Shatalovka | 6,3+6,3 | 1.9373 | 0 |  | 1.9373 | 0 | 6.615 | 4.6777 | 4.6777 | opened | 170 | SS-35/10kv Shatalovka | 6,3+6,3 | 0 | 1.9373 | 0 |  | 1.9373 | 0 | 6.615 | 4.6777 | 4.6777 | opened
171 | SS-35/10kv Shakhovka | 2,5+2,5 | 1.5261 | 0.79066 | 80 | 0.73541 | 0 | 2.625 | 1.8896 | 1.8896 | opened | 171 | SS-35/10kv Shakhovka | 2,5+2,5 | 0 | 1.5261 | 0.79066 | 80 | 0.73541 | 0 | 2.625 | 1.8896 | 1.8896 | opened
172 | SS-35/10kv Shishino | 4+2,5 | 3.3728 | 1.03 | 80 | 2.3428 | 0 | 2.625 | 0.2822 | 0.2822 | opened | 172 | SS-35/10kv Shishino | 4+2,5 | 0.001 | 3.3738 | 1.03 | 80 | 2.3438 | 0 | 2.625 | 0.2812 | 0.2812 | opened
173 | SS-35/10kv Yablonovo | 4+4 | 1.6831 | 1.1284 | 80 | 0.55464 | 0 | 4.2 | 3.6454 | 3.6454 | opened | 173 | SS-35/10kv Yablonovo | 4+4 | 0 | 1.6831 | 1.1284 | 80 | 0.55464 | 0 | 4.2 | 3.6454 | 3.6454 | opened
174 | SS-35/10kv Yarskoe | 2,5+2,5 | 0.51053 | 0.14648 | 80 | 0.36405 | 0 | 2.625 | 2.2609 | 2.2609 | opened | 174 | SS-35/10kv Yarskoe | 2,5+2,5 | 0 | 0.51053 | 0.14648 | 80 | 0.36405 | 0 | 2.625 | 2.2609 | 2.2609 | opened
| TOTAL: | 3062.2 | 1015.675 | 448.6055 |  | 615.1843 | [5 empty] | 2: TOTAL:; 3: 3062.2; 4: 24.9313; 5: 1040.6064; МVА 6: 448.6055; min. 8: 592.0009
| deficit | [8 empty] | -6.3166 |  | 2: deficit; min. 12: -13.6976
| proficit | [8 empty] | 920.8657 |  | 2: proficit; min. 12: 903.6398

## липецк
Table 1
No. | Object of main substation, voltage class | Current deficit | [9 empty] | No. | Object of main substation, voltage class | Expected dificit / proficit | [8 empty] | Note | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  | Note |  |  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Expected load at Main Substation, MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | MVA | Мin. | [10 empty] | MVA | min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 2: One-transformer substations
1 | SS 110/10kv Lev Tolstoy | 10 | 2.3642 | 1 | 30 | 1 | 0 | 1 | -1.3642 | -1.3642 | closed | 1 | SS 110/10kv Lev Tolstoy | 10 | 0.05 | 2.4142 | 1 | 30 | 1 | 0 | 1 | -1.4142 | -1.4142 | closed
2 | SS 110/10 kv Dvurechki | 6.3 | 2.6469 | 0.31 | 120 | 0.31 | 0 | 0.31 | -2.3369 | -2.3369 | closed | 2 | SS 110/10 kv Dvurechki | 6.3 | 0.114 | 2.7609 | 0.31 | 120 | 0.31 | 0 | 0.31 | -2.4509 | -2.4509 | closed
3 | SS 35/10 kv Vesyoloe | 2.5 | 0.070668 | 0.37 | 120 | 0.37 | 0 | 0.37 | 0.29933 | 0.29933 | opened | 3 | SS 35/10 kv Vesyoloe | 2.5 |  | 0.070668 | 0.37 | 120 | 0.37 | 0 | 0.37 | 0.29933 | 0.29933 | opened
4 | SS 35/10 kv Kr.Palna | 3.2 | 0.90067 | 0.5 | 120 | 0.5 | 0 | 0.5 | -0.40067 | -0.40067 | closed | 4 | SS 35/10 kv Kr.Palna | 3.2 | 0.15 | 1.0507 | 0.5 | 120 | 0.5 | 0 | 0.5 | -0.55067 | -0.55067 | closed
5 | SS 35/10 kv Kamenka | 2.5 | 0.64259 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.27259 | -0.27259 | closed | 5 | SS 35/10 kv Kamenka | 2.5 | 0.5 | 1.1426 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.77259 | -0.77259 | closed
6 | SS 35/10 kv Krasotynovka | 2.5 | 0.25461 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.045389 | 0.045389 | opened | 6 | SS 35/10 kv Krasotynovka | 2.5 |  | 0.25461 | 0.3 | 120 | 0.3 | 0 | 0.3 | 0.045389 | 0.045389 | opened
7 | SS 35/10 kv Ozyorki | 2.5 | 0.11224 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | 0.25776 | 0.25776 | opened | 7 | SS 35/10 kv Ozyorki | 2.5 |  | 0.11224 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | 0.25776 | 0.25776 | opened
8 | SS 35/10 kv Pankratovka | 2.5 | 0.61834 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.24834 | -0.24834 | closed | 8 | SS 35/10 kv Pankratovka | 2.5 |  | 0.61834 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.24834 | -0.24834 | closed
9 | SS 35/10 kv Preobrazhenye | 2.5 | 0.41154 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | -0.011535 | -0.011535 | closed | 9 | SS 35/10 kv Preobrazhenye | 2.5 |  | 0.41154 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | -0.011535 | -0.011535 | closed
10 | SS 35/10 kv Yakovlevo | 2.5 | 0.71603 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | -0.34603 | -0.34603 | closed | 10 | SS 35/10 kv Yakovlevo | 2.5 |  | 0.71603 | 0.37 | 24 hours | 0.37 | 0 | 0.37 | -0.34603 | -0.34603 | closed
11 | SS 110/10kv Terbunsky gonchar | 25 | no load | [8 empty] | 1: 11; 2: SS 110/10kv Terbunsky gonchar; 3: 25; 4: 15
12 | SS 35/10 kv Pervomayskaya | 2.5 | 0.73439 | 0.25 | 90 | 0.25 | 0 | 0.25 | -0.48439 | -0.48439 | closed | 12 | SS 35/10 kv Pervomayskaya | 2.5 |  | 0.73439 | 0.25 | 90 | 0.25 | 0 | 0.25 | -0.48439 | -0.48439 | closed
13 | SS 35/10 kv Kamennaya Lubna | 2.5 | 0.81839 | 0.75 | 90 | 0.75 | 0 | 0.75 | -0.068394 | -0.068394 | closed | 13 | SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.81839 | 0.75 | 90 | 0.75 | 0 | 0.75 | -0.068394 | -0.068394 | closed
14 | SS 35/10 kv Znamenka | 2.5 | 0.85477 | 0.75 | 24 hours | 0.75 | 0 | 0.75 | -0.10477 | -0.10477 | closed | 14 | SS 35/10 kv Znamenka | 2.5 | 0.045 | 0.89977 | 0.75 | 24 hours | 0.75 | 0 | 0.75 | -0.14977 | -0.14977 | closed
15 | SS 35/10 kv Pikovo | 2.5 | 0.51407 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.23593 | 0.23593 | opened | 15 | SS 35/10 kv Pikovo | 2.5 |  | 0.51407 | 0.75 | 60 | 0.75 | 0 | 0.75 | 0.23593 | 0.23593 | opened
16 | SS 35/10 kv Nikolskoe | 4 | 0.44167 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.15833 | 0.15833 | opened | 16 | SS 35/10 kv Nikolskoe | 4 |  | 0.44167 | 0.6 | 120 | 0.6 | 0 | 0.6 | 0.15833 | 0.15833 | opened
17 | SS 35/10 kv Peskovatka | 1.6 | 0.14394 | 0.48 | 120 | 0.48 | 0 | 0.48 | 0.33606 | 0.33606 | opened | 17 | SS 35/10 kv Peskovatka | 1.6 |  | 0.14394 | 0.48 | 120 | 0.48 | 0 | 0.48 | 0.33606 | 0.33606 | opened
18 | SS 35/6 kv Druzhba | 5.6 | KPUNN-6kv not our | [7 empty] | opened | 1: 18; 2: SS 35/6 kv Druzhba; 3: 5.6; min. 13: opened
19 | SS 35/10 kv SOM | 1.6 | 0.1 | 0.16 | 120 | 0.16 | 0 | 0.16 | 0.06 | 0.06 | opened | 1: 19; 2: SS 35/10 kv SOM; 3: 1.6; min. 13: opened
20 | SS 35/6 kv Novonikolaevka | 4 | 0.69027 | 0.6 | 120 | 0.6 | 0 | 0.6 | -0.09027 | -0.09027 | closed | 20 | SS 35/6 kv Novonikolaevka | 4 |  | 0.69027 | 0.6 | 120 | 0.6 | 0 | 0.6 | -0.09027 | -0.09027 | closed
21 | SS 35/10 kv Sindyakino | 2.5 | 0.94458 | 0.2 | 60 | 0.2 | 0 | 0.2 | -0.74458 | -0.74458 | closed | 21 | SS 35/10 kv Sindyakino | 2.5 | 0.02 | 0.96458 | 0.2 | 60 | 0.2 | 0 | 0.2 | -0.76458 | -0.76458 | closed
22 | SS 35/10 kv Kurino | 2.5 | 0.3088 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.071195 | 0.071195 | opened | 22 | SS 35/10 kv Kurino | 2.5 | 0.02 | 0.32881 | 0.38 | 60 | 0.38 | 0 | 0.38 | 0.051195 | 0.051195 | opened
23 | SS 35/10 kv Novodubovoe | 2.5 | 0.54703 | 0.5 | 60 | 0.5 | 0 | 0.5 | -0.047026 | -0.047026 | closed | 23 | SS 35/10 kv Novodubovoe | 2.5 | 0.011 | 0.55803 | 0.5 | 60 | 0.5 | 0 | 0.5 | -0.058026 | -0.058026 | closed
24 | SS 35/10 kv Beryozovka | 2.5 | 1.1444 | 0.75 | 120 | 0.75 | 0 | 0.75 | -0.39439 | -0.39439 | closed | 24 | SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0.75 | 120 | 0.75 | 0 | 0.75 | -0.39439 | -0.39439 | closed
25 | SS 110/6 kv Agregatnaya | 16+16 | 13.1489 | 0 | 0 | 13.1489 | 0 | 16.8 | 3.6511 | 3.6511 | opened | 25 | SS 110/6 kv Agregatnaya | 16+16 | 2.6 | 15.7489 | 0 | 0 | 15.7489 | 0 | 16.8 | 1.0511 | 1.0511 | opened
26 | SS 110/6 kv Zapadnaya | 40+40 | 10.9119 | 0 | 0 | 10.9119 | 0 | 42 | 31.0881 | 31.0881 | opened | 26 | SS 110/6 kv Zapadnaya | 40+40 | 0.229 | 11.1409 | 0 | 0 | 11.1409 | 0 | 42 | 30.8591 | 30.8591 | opened
27 | SS 110/10 kv Kashary | 2,5+6,3 | 1.3621 | 0.25 | 120 | 1.1121 | 0 | 2.625 | 1.5129 | 1.5129 | opened | 27 | SS 110/10 kv Kashary | 2,5+6,3 | 0.63 | 1.9921 | 0.25 | 120 | 1.7421 | 0 | 2.625 | 0.88288 | 0.88288 | opened
28 | SS 110/6 kv Tabak | 16+16 | 13.4234 | 4.8 | 120 | 8.6234 | 0 | 16.8 | 8.1766 | 8.1766 | opened | 28 | SS 110/6 kv Tabak | 16+16 | 0.028 | 13.4514 | 4.8 | 120 | 8.6514 | 0 | 16.8 | 8.1486 | 8.1486 | opened
29 | SS 110/10 kv Lukoshkino | 10+2,5 | 0.9942 | 0 | 0 | 0.9942 | 0 | 2.625 | 1.6308 | 1.6308 | opened | 29 | SS 110/10 kv Lukoshkino | 10+2,5 | 0.01 | 1.0042 | 0 | 0 | 1.0042 | 0 | 2.625 | 1.6208 | 1.6208 | opened
30 | SS 110/10kv Niva | 10+10 | 4.3648 | 1 | 120 | 3.3648 | 0 | 10.5 | 7.1352 | 7.1352 | opened | 30 | SS 110/10kv Niva | 10+10 | 0.122 | 4.4868 | 1 | 120 | 3.4868 | 0 | 10.5 | 7.0132 | 7.0132 | opened
31 | SS 110/10 kv Olkhovets | 2,5+2,5 | 1.4807 | 0.63 | 120 | 0.85073 | 0 | 2.625 | 1.7743 | 1.7743 | opened | 31 | SS 110/10 kv Olkhovets | 2,5+2,5 | 0.034 | 1.5147 | 0.63 | 120 | 0.88473 | 0 | 2.625 | 1.7403 | 1.7403 | opened
32 | SS 110/10 kv Kuyman | 2,5+2,5 | 0.54767 | 0.63 | 120 | -0.082326 | 0 | 2.625 | 2.7073 | 2.7073 | opened | 32 | SS 110/10 kv Kuyman | 2,5+2,5 |  | 0.54767 | 0.63 | 120 | -0.082326 | 0 | 2.625 | 2.7073 | 2.7073 | opened
33 | SS 110/10 kv Lutoshkino | 2,5+2,5 | 0.2728 | 0.75 | 120 | -0.4772 | 0 | 2.625 | 3.1022 | 3.1022 | opened | 33 | SS 110/10 kv Lutoshkino | 2,5+2,5 |  | 0.2728 | 0.75 | 120 | -0.4772 | 0 | 2.625 | 3.1022 | 3.1022 | opened
34 | SS 110/10 kv Krugloe | 2,5+2,5 | 0.58197 | 0.75 | 120 | -0.16803 | 0 | 2.625 | 2.793 | 2.793 | opened | 34 | SS 110/10 kv Krugloe | 2,5+2,5 |  | 0.58197 | 0.75 | 120 | -0.16803 | 0 | 2.625 | 2.793 | 2.793 | opened
35 | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 40.3158 | 4.5 | 30 | 35.8158 | 0 | 42 | 6.1842 | 6.1842 | * | 35 | SS 110/10/6 kv Yugo-Zapadnaya | 40+40 | 1.673 | 41.9888 | 4.5 | 30 | 37.4888 | 0 | 42 | 4.5112 | 4.5112 | *
36 | SS 110/6 kv Privokzalnaya | 20+20+25 | 43.4403 | 1.38 | 30 | 42.0603 | 0 | 42 | -0.0603 | -0.0603 | opened | 36 | SS 110/6 kv Privokzalnaya | 20+20+25 | 0.354 | 43.7943 | 1.38 | 30 | 42.4143 | 0 | 42 | -0.4143 | -0.4143 | closed
37 | SS 110/10/6 kv Yuzhnaya | 40+40 | 40.3574 | 6 | 30 | 34.3574 | 0 | 42 | 7.6426 | 7.6426 | opened | 37 | SS 110/10/6 kv Yuzhnaya | 40+40 | 0.16 | 40.5174 | 6 | 30 | 34.5174 | 0 | 42 | 7.4826 | 7.4826 | opened
38 | SS 110/6 kv Sitovka | 10+10 | 4.0819 | 1.29 | 30 | 2.7919 | 0 | 10.5 | 7.7081 | 7.7081 | * | 38 | SS 110/6 kv Sitovka | 10+10 |  | 4.0819 | 1.29 | 30 | 2.7919 | 0 | 10.5 | 7.7081 | 7.7081 | *
39 | SS 110/6 kv LTP | 6,3+10 | 4.9599 | 0 | 0 | 4.9599 | 0 | 6.615 | 1.6551 | 1.6551 | opened | 39 | SS 110/6 kv LTP | 6,3+10 |  | 4.9599 | 0 | 0 | 4.9599 | 0 | 6.615 | 1.6551 | 1.6551 | opened
40 | SS 110/6 kv KPD | 10+10 | 2.768 | 0 | 0 | 2.768 | 0 | 10.5 | 7.732 | 7.732 | opened | 40 | SS 110/6 kv KPD | 10+10 | 0.1 | 2.868 | 0 | 0 | 2.868 | 0 | 10.5 | 7.632 | 7.632 | opened
41 | SS 110/10 kv Oktyabskaya | 40+40 | 14.7822 | 4 | 30 | 10.7822 | 0 | 42 | 31.2178 | 31.2178 | opened | 41 | SS 110/10 kv Oktyabskaya | 40+40 | 0.158 | 14.9402 | 4 | 30 | 10.9402 | 0 | 42 | 31.0598 | 31.0598 | opened
42 | SS 110/6 kv Teplichnaya | 15+15 | 6.6823 | 0 | 0 | 6.6823 | 0 | 15.75 | 9.0677 | 9.0677 | opened | 42 | SS 110/6 kv Teplichnaya | 15+15 | 0.005 | 6.6873 | 0 | 0 | 6.6873 | 0 | 15.75 | 9.0627 | 9.0627 | opened
43 | SS 110/6 kv GPP-2 LTZ | 63+63 | 12.4211 | 0 | 0 | 12.4211 | 0 | 66.15 | 53.7289 | 53.7289 | opened | 43 | SS 110/6 kv GPP-2 LTZ | 63+63 | 0.22 | 12.6411 | 0 | 0 | 12.6411 | 0 | 66.15 | 53.5089 | 53.5089 | opened
44 | SS 35/10 kv Avangard | 4+4 | 0.6296 | 0.6 | 120 | 0.0296 | 0 | 4.2 | 4.1704 | 4.1704 | opened | 44 | SS 35/10 kv Avangard | 4+4 | 0.217 | 0.8466 | 0.6 | 120 | 0.2466 | 0 | 4.2 | 3.9534 | 3.9534 | opened
45 | SS 35/10 kv Afanasysevo | 2,5+2,5 | 1.6472 | 0.37 | 120 | 1.2772 | 0 | 2.625 | 1.3478 | 1.3478 | opened | 45 | SS 35/10 kv Afanasysevo | 2,5+2,5 | 0.01 | 1.6572 | 0.37 | 120 | 1.2872 | 0 | 2.625 | 1.3378 | 1.3378 | opened
46 | SS 35/10 kv Babarykino | 2,5+2,5 | 0.2754 | 0.37 | 120 | -0.094604 | 0 | 2.625 | 2.7196 | 2.7196 | opened | 46 | SS 35/10 kv Babarykino | 2,5+2,5 | 0.015 | 0.2904 | 0.37 | 120 | -0.079604 | 0 | 2.625 | 2.7046 | 2.7046 | opened
47 | SS 35/10 kv Avrora | 2,5+2,5 | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened | 47 | SS 35/10 kv Avrora | 2,5+2,5 |  | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened
48 | SS 35/10 kv B.Boyovka | 2,5+2,5 | 0.29982 | 0.37 | 120 | -0.070182 | 0 | 2.625 | 2.6952 | 2.6952 | opened | 48 | SS 35/10 kv B.Boyovka | 2,5+2,5 | 0.01 | 0.30982 | 0.37 | 120 | -0.060182 | 0 | 2.625 | 2.6852 | 2.6852 | opened
49 | SS 35/10 kv Borki | 2,5+2,5 | 0.95644 | 0.37 | 120 | 0.58644 | 0 | 2.625 | 2.0386 | 2.0386 | opened | 49 | SS 35/10 kv Borki | 2,5+2,5 | 0.64 | 1.5964 | 0.37 | 120 | 1.2264 | 0 | 2.625 | 1.3986 | 1.3986 | opened
50 | SS 35/6kv Vostochnaya | 10+16 | 13.051 | 1 | 120 | 12.051 | 0 | 10.5 | -1.551 | -1.551 |  | 50 | SS 35/6kv Vostochnaya | 10+16 | 0.0796 | 13.1306 | 1 | 120 | 12.1306 | 0 | 10.5 | -1.6306 | -1.6306
51 | SS 35/10 kv Vasilyevka | 2,5+2,5 | 0.30242 | 0.37 | 120 | -0.067584 | 0 | 2.625 | 2.6926 | 2.6926 | opened | 51 | SS 35/10 kv Vasilyevka | 2,5+2,5 | 0.002 | 0.30442 | 0.37 | 120 | -0.065584 | 0 | 2.625 | 2.6906 | 2.6906 | opened
52 | SS 35/10 kv Voronets | 4+4 | 1.4393 | 0.6 | 120 | 0.83933 | 0 | 4.2 | 3.3607 | 3.3607 | opened | 52 | SS 35/10 kv Voronets | 4+4 | 0.048 | 1.4873 | 0.6 | 120 | 0.88733 | 0 | 4.2 | 3.3127 | 3.3127 | opened
53 | SS 35/6 kv Golikovo | 1,8+1,6 | 1.4722 | 0 | 0 | 1.4722 | 0 | 1.68 | 0.20776 | 0.20776 | opened | 53 | SS 35/6 kv Golikovo | 1,8+1,6 |  | 1.4722 | 0 | 0 | 1.4722 | 0 | 1.68 | 0.20776 | 0.20776 | opened
54 | SS 35/10 kv Gatishche | 2,5+2,5 | 0.23642 | 0 | 0 | 0.23642 | 0 | 2.625 | 2.3886 | 2.3886 | opened | 54 | SS 35/10 kv Gatishche | 2,5+2,5 |  | 0.23642 | 0 | 0 | 0.23642 | 0 | 2.625 | 2.3886 | 2.3886 | opened
55 | SS 35/10 kv Gnilusha | 6,3+6,3 | 1.0515 | 0.63 | 120 | 0.42153 | 0 | 6.615 | 6.1935 | 6.1935 | opened | 55 | SS 35/10 kv Gnilusha | 6,3+6,3 |  | 1.0515 | 0.63 | 120 | 0.42153 | 0 | 6.615 | 6.1935 | 6.1935 | opened
56 | SS 35/10kv Gryzlovo | 2,5+2,5 | 0.63393 | 0.37 | 120 | 0.26393 | 0 | 2.625 | 2.3611 | 2.3611 | opened | 56 | SS 35/10kv Gryzlovo | 2,5+2,5 |  | 0.63393 | 0.37 | 120 | 0.26393 | 0 | 2.625 | 2.3611 | 2.3611 | opened
57 | SS 35/10 kv Zhernovnoe | 2,5+2,5 | 0.32909 | 0.37 | 120 | -0.04091 | 0 | 2.625 | 2.6659 | 2.6659 | opened | 57 | SS 35/10 kv Zhernovnoe | 2,5+2,5 | 0.8 | 1.1291 | 0.37 | 120 | 0.75909 | 0 | 2.625 | 1.8659 | 1.8659 | opened
58 | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 2.1204 | 0 | 0 | 2.1204 | 0 | 1.68 | -0.44038 | -0.44038 |  | 58 | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.082 | 2.2024 | 0 | 0 | 2.2024 | 0 | 1.68 | -0.52238 | -0.52238
59 | SS 35/10 kv Zakharovka | 2,5+2,5 | 0.24318 | 0.37 | 120 | -0.12682 | 0 | 2.625 | 2.7518 | 2.7518 | opened | 59 | SS 35/10 kv Zakharovka | 2,5+2,5 |  | 0.24318 | 0.37 | 120 | -0.12682 | 0 | 2.625 | 2.7518 | 2.7518 | opened
60 | SS 35/10 kv Kazaki | 4+4 | 2.7713 | 0 | 0 | 2.7713 | 0 | 4.2 | 1.4287 | 1.4287 | opened | 60 | SS 35/10 kv Kazaki | 4+4 | 0.007 | 2.7783 | 0 | 0 | 2.7783 | 0 | 4.2 | 1.4217 | 1.4217 | opened
61 | SS 35/10 kv Kolesovo | 6,3+6,3 | 1.1639 | 0.63 | 120 | 0.53394 | 0 | 6.615 | 6.0811 | 6.0811 | оpened | 61 | SS 35/10 kv Kolesovo | 6,3+6,3 | 0.044 | 1.2079 | 0.63 | 120 | 0.57794 | 0 | 6.615 | 6.0371 | 6.0371 | opened
62 | SS 35/10 kv Knyazevo | 2,5+2,5 | 0.37326 | 0.37 | 120 | 0.0032569 | 0 | 2.625 | 2.6217 | 2.6217 | opened | 62 | SS 35/10 kv Knyazevo | 2,5+2,5 | 0.022 | 0.39526 | 0.37 | 120 | 0.025257 | 0 | 2.625 | 2.5997 | 2.5997 | opened
63 | SS 35/10 kv Kirillovo | 2,5+2,5 | 0.2676 | 0.37 | 120 | -0.1024 | 0 | 2.625 | 2.7274 | 2.7274 | opened | 63 | SS 35/10 kv Kirillovo | 2,5+2,5 |  | 0.2676 | 0.37 | 120 | -0.1024 | 0 | 2.625 | 2.7274 | 2.7274 | opened
64 | SS 35/10 kv Ksizovo | 2,5+2,5 | 0.28007 | 0.37 | 120 | -0.089927 | 0 | 2.625 | 2.7149 | 2.7149 | opened | 64 | SS 35/10 kv Ksizovo | 2,5+2,5 |  | 0.28007 | 0.37 | 120 | -0.089927 | 0 | 2.625 | 2.7149 | 2.7149 | opened
65 | SS 35/10 kv Lamskoe | 2,5+2,5 | 1.8543 | 0.37 | 120 | 1.4843 | 0 | 2.625 | 1.1407 | 1.1407 | opened | 65 | SS 35/10 kv Lamskoe | 2,5+2,5 | 0.003 | 1.8573 | 0.37 | 120 | 1.4873 | 0 | 2.625 | 1.1377 | 1.1377 | opened
66 | SS 35/10 kv Kazachye | 2,5+2,5 | 0.60016 | 0.37 | 120 | 0.23016 | 0 | 2.625 | 2.3948 | 2.3948 | opened | 66 | SS 35/10 kv Kazachye | 2,5+2,5 | 0.045 | 0.64516 | 0.37 | 120 | 0.27516 | 0 | 2.625 | 2.3498 | 2.3498 | opened
67 | SS 35/10 kv Lebyazhye | 2,5+1,6 | 0.37066 | 0.24 | 120 | 0.13066 | 0 | 1.68 | 1.5493 | 1.5493 | opened | 67 | SS 35/10 kv Lebyazhye | 2,5+1,6 | 0.002 | 0.37266 | 0.24 | 120 | 0.13266 | 0 | 1.68 | 1.5473 | 1.5473 | opened
68 | SS 35/10 kv Lomovets | 1,6+2,5 | 0.33463 | 0.24 | 120 | 0.094632 | 0 | 1.68 | 1.5854 | 1.5854 | opened | 68 | SS 35/10 kv Lomovets | 1,6+2,5 | 0.022 | 0.35663 | 0.24 | 120 | 0.11663 | 0 | 1.68 | 1.5634 | 1.5634 | opened
69 | SS 35/10 kv Olshanets | 2,5+4 | 1.0891 | 0 | 0 | 1.0891 | 0 | 2.625 | 1.5359 | 1.5359 | opened | 69 | SS 35/10 kv Olshanets | 2,5+4 | 0.01 | 1.0991 | 0 | 0 | 1.0991 | 0 | 2.625 | 1.5259 | 1.5259 | opened
70 | SS 35/10 kv Ploskoe | 4+4 | 3.4918 | 0.6 | 120 | 2.8918 | 0 | 4.2 | 1.3082 | 1.3082 | opened | 70 | SS 35/10 kv Ploskoe | 4+4 | 0.09 | 3.5818 | 0.6 | 120 | 2.9818 | 0 | 4.2 | 1.2182 | 1.2182 | opened
71 | SS 35/10 kv Stegalovka | 2,5+3,2 | 0.37845 | 0.37 | 120 | 0.0084531 | 0 | 2.625 | 2.6165 | 2.6165 | opened | 71 | SS 35/10 kv Stegalovka | 2,5+3,2 | 0.01 | 0.38845 | 0.37 | 120 | 0.018453 | 0 | 2.625 | 2.6065 | 2.6065 | opened
72 | SS 35/10 kv Solidarnost | 4+4 | 1.3432 | 0.6 | 120 | 0.74321 | 0 | 4.2 | 3.4568 | 3.4568 | opened | 72 | SS 35/10 kv Solidarnost | 4+4 | 0.087 | 1.4302 | 0.6 | 120 | 0.83021 | 0 | 4.2 | 3.3698 | 3.3698 | opened
73 | SS 35/10 kv Timiryazevo | 4+4 | 0.82532 | 0.6 | 120 | 0.22532 | 0 | 4.2 | 3.9747 | 3.9747 | opened | 73 | SS 35/10 kv Timiryazevo | 4+4 | 0.005 | 0.83032 | 0.6 | 120 | 0.23032 | 0 | 4.2 | 3.9697 | 3.9697 | opened
74 | SS 35/10 kv Talitsa | 2,5+2,5 | 1.6732 | 0 | 0 | 1.6732 | 0 | 2.625 | 0.95184 | 0.95184 | opened | 74 | SS 35/10 kv Talitsa | 2,5+2,5 | 0.023 | 1.6962 | 0 | 0 | 1.6962 | 0 | 2.625 | 0.92884 | 0.92884 | opened
75 | SS 35/10 kv the II Terbuny | 2,5+2,5 | 0.80783 | 0.37 | 120 | 0.43783 | 0 | 2.625 | 2.1872 | 2.1872 | opened | 75 | SS 35/10 kv the II Terbuny | 2,5+2,5 | 1.07 | 1.8778 | 0.37 | 120 | 1.5078 | 0 | 2.625 | 1.1172 | 1.1172 | opened
76 | SS 35/10 kv Tikhii Don | 4+4 | 0.41985 | 0.6 | 120 | -0.18015 | 0 | 4.2 | 4.3802 | 4.3802 | opened | 76 | SS 35/10 kv Tikhii Don | 4+4 | 0.015 | 0.43485 | 0.6 | 120 | -0.16515 | 0 | 4.2 | 4.3652 | 4.3652 | opened
77 | SS 35/10 kv Khitrovo | 6,3+6,3 | 0.77734 | 0 | 0 | 0.77734 | 0 |  | -0.77734 | -0.77734 | closed | 77 | SS 35/10 kv Khitrovo | 6,3+6,3 |  | 0.77734 | 0 | 0 | 0.77734 | 0 |  | -0.77734 | -0.77734 | closed
78 | SS 35/10 kv Chernava | 2,5+2,5 | 1.6591 | 0 | 0 | 1.6591 | 0 | 2.625 | 0.96587 | 0.96587 | opened | 78 | SS 35/10 kv Chernava | 2,5+2,5 | 0.005 | 1.6641 | 0 | 0 | 1.6641 | 0 | 2.625 | 0.96087 | 0.96087 | opened
79 | SS 35/10 kv Chernoles | 2,5+2,5 | 0.2702 | 0 | 0 | 0.2702 | 0 | 2.625 | 2.3548 | 2.3548 | opened | 79 | SS 35/10 kv Chernoles | 2,5+2,5 |  | 0.2702 | 0 | 0 | 0.2702 | 0 | 2.625 | 2.3548 | 2.3548 | opened
80 | SS 35/6 kv SS No. 5 | 6,3+3,2 | 1.149 | 0 | 0 | 1.149 | 0 |  | -1.149 | -1.149 | closed | 80 | SS 35/6 kv SS No. 5 | 6,3+3,2 |  | 1.149 | 0 | 0 | 1.149 | 0 |  | -1.149 | -1.149 | closed
81 | SS 35/10 kv Krasnoe | 4+4 | 3.3505 | 0.4 | 120 | 2.9505 | 0 | 4.2 | 1.2495 | 1.2495 | opened | 81 | SS 35/10 kv Krasnoe | 4+4 | 0.052 | 3.4025 | 0.4 | 120 | 3.0025 | 0 | 4.2 | 1.1975 | 1.1975 | opened
82 | SS 35/10 kv Tyoploe | 2,5+2,5 | 1.1016 | 0.25 | 120 | 0.85158 | 0 | 2.625 | 1.7734 | 1.7734 | opened | 82 | SS 35/10 kv Tyoploe | 2,5+2,5 | 0.006 | 1.1076 | 0.25 | 120 | 0.85758 | 0 | 2.625 | 1.7674 | 1.7674 | opened
83 | SS 35/10 kv Dankov-selskaya | 6,3+4 | 4.5726 | 0.4 | 120 | 4.1726 | 0 | 4.2 | 0.027386 | 0.027386 | opened | 83 | SS 35/10 kv Dankov-selskaya | 6,3+6,3 | 0.19 | 4.7626 | 0.4 | 120 | 4.3626 | 0 | 6.615 | 2.2524 | 2.2524 | opened
84 | SS 35/10 kv Kolybelskaya | 2,5+2,5 | 1.0184 | 0 | 0 | 1.0184 | 0 | 2.625 | 1.6066 | 1.6066 | opened | 84 | SS 35/10 kv Kolybelskaya | 2,5+2,5 |  | 1.0184 | 0 | 0 | 1.0184 | 0 | 2.625 | 1.6066 | 1.6066 | opened
85 | SS 35/10 kv Topki | 2,5+2,5 | 0.2728 | 0.5 | 120 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened | 85 | SS 35/10 kv Topki | 2,5+2,5 |  | 0.2728 | 0.5 | 120 | -0.2272 | 0 | 2.625 | 2.8522 | 2.8522 | opened
86 | SS 35/10 kv Agronom | 4+6,3 | 1.6494 | 0.8 | 120 | 0.84943 | 0 | 4.2 | 3.3506 | 3.3506 | opened | 86 | SS 35/10 kv Agronom | 4+6,3 |  | 1.6494 | 0.8 | 120 | 0.84943 | 0 | 4.2 | 3.3506 | 3.3506 | opened
87 | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 1.8013 | 0.5 | 120 | 1.3013 | 0 | 2.625 | 1.3237 | 1.3237 | opened | 87 | SS 35/10 kv Troekurovo-sovkhoznaya | 2,5+2,5 | 0.0255 | 1.8268 | 0.5 | 120 | 1.3268 | 0 | 2.625 | 1.2982 | 1.2982 | opened
88 | SS 35/10 kv Gagarino | 1,8+1,8 | 0.45466 | 0.36 | 120 | 0.094663 | 0 |  | -0.094663 | -0.094663 | closed | 88 | SS 35/10 kv Gagarino | 1,8+1,8 |  | 0.45466 | 0.36 | 120 | 0.094663 | 0 |  | -0.094663 | -0.094663 | closed
89 | SS 35/10 kv Ranenburg | 1,6+1,6 | 1.5852 | 0.16 | 120 | 1.4252 | 0 | 1.68 | 0.25483 | 0.25483 | opened | 89 | SS 35/10 kv Ranenburg | 1,6+1,6 | 0.015 | 1.6002 | 0.16 | 120 | 1.4402 | 0 | 1.68 | 0.23983 | 0.23983 | opened
90 | SS 35/10 kv Sergievka | 2,5+2,5 | 0.41829 | 0.25 | 120 | 0.16829 | 0 | 2.625 | 2.4567 | 2.4567 | opened | 90 | SS 35/10 kv Sergievka | 2,5+2,5 |  | 0.41829 | 0.25 | 120 | 0.16829 | 0 | 2.625 | 2.4567 | 2.4567 | opened
91 | SS 35/10 kv Drezgalovo | 1,6+1,6 | 0.37464 | 0.48 | 120 | -0.10536 | 0 | 1.68 | 1.7854 | 1.7854 | opened | 91 | SS 35/10 kv Drezgalovo | 1,6+1,6 |  | 0.37464 | 0.48 | 120 | -0.10536 | 0 | 1.68 | 1.7854 | 1.7854 | opened
92 | SS 35/10 kv Dolgoe | 2,5+2,5 | 0.25461 | 0 | 0 | 0.25461 | 0 | 2.625 | 2.3704 | 2.3704 | opened | 92 | SS 35/10 kv Dolgoe | 2,5+2,5 |  | 0.25461 | 0 | 0 | 0.25461 | 0 | 2.625 | 2.3704 | 2.3704 | opened
93 | SS 35/10 kv Voskresenovka | 1,6+1,6 | 0.60016 | 0 | 0 | 0.60016 | 0 | 1.68 | 1.0798 | 1.0798 | opened | 93 | SS 35/10 kv Voskresenovka | 1,6+1,6 | 0.01 | 0.61016 | 0 | 0 | 0.61016 | 0 | 1.68 | 1.0698 | 1.0698 | opened
94 | SS 35/10 kv Saprykino | 1,6+2,5 | 0.45033 | 0.16 | 120 | 0.29033 | 0 | 1.68 | 1.3897 | 1.3897 | opened | 94 | SS 35/10 kv Saprykino | 1,6+2,5 |  | 0.45033 | 0.16 | 120 | 0.29033 | 0 | 1.68 | 1.3897 | 1.3897 | opened
95 | SS 35/10 kv Nopolyanye | 2,5+2,5 | 0.57452 | 0 | 0 | 0.57452 | 0 | 2.625 | 2.0505 | 2.0505 | opened | 95 | SS 35/10 kv Nopolyanye | 2,5+2,5 | 0.012 | 0.58652 | 0 | 0 | 0.58652 | 0 | 2.625 | 2.0385 | 2.0385 | opened
96 | SS 35/10 kv Vednoe | 2,5+2,5 | 1.2003 | 0.25 | 120 | 0.95031 | 0 | 2.625 | 1.6747 | 1.6747 | opened | 96 | SS 35/10 kv Vednoe | 2,5+2,5 | 0.007 | 1.2073 | 0.25 | 120 | 0.95731 | 0 | 2.625 | 1.6677 | 1.6677 | opened
97 | SS 35/10 kv Bigildino | 2,5+2,5 | 0.98121 | 0 | 0 | 0.98121 | 0 | 2.625 | 1.6438 | 1.6438 | opened | 97 | SS 35/10 kv Bigildino | 2,5+2,5 |  | 0.98121 | 0 | 0 | 0.98121 | 0 | 2.625 | 1.6438 | 1.6438 | opened
98 | SS 35/10 kv Kultura | 2,5+2,5 | 0.95263 | 0.37 | 120 | 0.58263 | 0 | 2.625 | 2.0424 | 2.0424 | opened | 98 | SS 35/10 kv Kultura | 2,5+2,5 | 0.005 | 0.95763 | 0.37 | 120 | 0.58763 | 0 | 2.625 | 2.0374 | 2.0374 | opened
99 | SS 35/10 kv Baryatino | 2,5+2,5 | 0.29653 | 0 | 0 | 0.29653 | 0 | 2.625 | 2.3285 | 2.3285 | opened | 99 | SS 35/10 kv Baryatino | 2,5+2,5 |  | 0.29653 | 0 | 0 | 0.29653 | 0 | 2.625 | 2.3285 | 2.3285 | opened
100 | SS 35/10 kv B.Popovo | 2,5+2,5 | 1.3822 | 0.5 | 120 | 0.88218 | 0 | 2.625 | 1.7428 | 1.7428 | opened | 100 | SS 35/10 kv B.Popovo | 2,5+2,5 | 0.008 | 1.3902 | 0.5 | 120 | 0.89018 | 0 | 2.625 | 1.7348 | 1.7348 | opened
101 | SS 35/10 kv B. Izbishchi | 2,5+2,5 | 1.364 | 0.37 | 120 | 0.99399 | 0 | 2.625 | 1.631 | 1.631 | opened | 101 | SS 35/10 kv B. Izbishchi | 2,5+2,5 |  | 1.364 | 0.37 | 120 | 0.99399 | 0 | 2.625 | 1.631 | 1.631 | opened
102 | SS 35/10 kv Polibino | 2,5+2,5 | 0.29376 | 0 | 0 | 0.29376 | 0 | 2.625 | 2.3312 | 2.3312 | opened | 102 | SS 35/10 kv Polibino | 2,5+2,5 | 0.02 | 0.31376 | 0 | 0 | 0.31376 | 0 | 2.625 | 2.3112 | 2.3112 | opened
103 | SS 35/10 kv Dubrava | 2,5+2,5 | 0.17321 | 0 | 0 | 0.17321 | 0 | 2.625 | 2.4518 | 2.4518 | opened | 103 | SS 35/10 kv Dubrava | 2,5+2,5 |  | 0.17321 | 0 | 0 | 0.17321 | 0 | 2.625 | 2.4518 | 2.4518 | opened
104 | SS 35/10 kv Khrushchevo | 2,5+2,5 | 0.446 | 0 | 0 | 0.446 | 0 | 2.625 | 2.179 | 2.179 | opened | 104 | SS 35/10 kv Khrushchevo | 2,5+2,5 | 0.03 | 0.476 | 0 | 0 | 0.476 | 0 | 2.625 | 2.149 | 2.149 | opened
105 | SS 35/10 kv B. Verkh | 2,5+2,5 | 0.87295 | 0.25 | 120 | 0.62295 | 0 | 2.625 | 2.002 | 2.002 | opened | 105 | SS 35/10 kv B. Verkh | 2,5+2,5 |  | 0.87295 | 0.25 | 120 | 0.62295 | 0 | 2.625 | 2.002 | 2.002 | opened
106 | SS 35/10 kv Golovinshchino | 2,5+2,5 | 0.31177 | 0 | 0 | 0.31177 | 0 | 2.625 | 2.3132 | 2.3132 | opened | 106 | SS 35/10 kv Golovinshchino | 2,5+2,5 |  | 0.31177 | 0 | 0 | 0.31177 | 0 | 2.625 | 2.3132 | 2.3132 | opened
107 | SS 35/10 kv Yablonevoe | 2,5+2,5 | 0.51442 | 0.25 | 120 | 0.26442 | 0 | 2.625 | 2.3606 | 2.3606 | opened | 107 | SS 35/10 kv Yablonevoe | 2,5+2,5 | 0.01837 | 0.53279 | 0.25 | 120 | 0.28279 | 0 | 2.625 | 2.3422 | 2.3422 | opened
108 | SS 35/10 kv Politovo | 2,5+2,5 | 0.88958 | 0 | 0 | 0.88958 | 0 | 2.625 | 1.7354 | 1.7354 | opened | 108 | SS 35/10 kv Politovo | 2,5+2,5 |  | 0.88958 | 0 | 0 | 0.88958 | 0 | 2.625 | 1.7354 | 1.7354 | opened
109 | SS 35/10 kv Complex | 4+4 | 0.83398 | 1.2 | 120 | -0.36602 | 0 | 4.2 | 4.566 | 4.566 | opened | 109 | SS 35/10 kv Complex | 4+4 |  | 0.83398 | 1.2 | 120 | -0.36602 | 0 | 4.2 | 4.566 | 4.566 | opened
110 | SS 35/10 kv No.1 | 4+4 | 3.742 | 0.45 | 120 | 3.292 | 0 | 4.2 | 0.90801 | 0.90801 | opened | 110 | SS 35/10 kv No.1 | 4+4 | 0.165 | 3.907 | 0.45 | 120 | 3.457 | 0 | 4.2 | 0.74301 | 0.74301 | opened
111 | SS 35/6 kv No. 2 | 1+1+1 | 0.70844 | 0 | 0 | 0.70844 | 0 | 2.1 | 1.3916 | 1.3916 | opened | 111 | SS 35/6 kv No. 2 | 1+1+1 | 0.1 | 0.80844 | 0 | 0 | 0.80844 | 0 | 2.1 | 1.2916 | 1.2916 | opened
112 | SS 35/10 kv No. 3 | 2,5+2,5 | 1.1761 | 0.25 | 120 | 0.92605 | 0 | 2.625 | 1.6989 | 1.6989 | opened | 112 | SS 35/10 kv No. 3 | 2,5+2,5 | 0.0865 | 1.2626 | 0.25 | 120 | 1.0126 | 0 | 2.625 | 1.6124 | 1.6124 | opened
113 | SS 35/6 kv No. 4 | 4+4 | 2.6921 | 0.4 | 120 | 2.2921 | 0 | 4.2 | 1.9079 | 1.9079 | opened | 113 | SS 35/6 kv No. 4 | 4+4 | 0.073 | 2.7651 | 0.4 | 120 | 2.3651 | 0 | 4.2 | 1.8349 | 1.8349 | opened
114 | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 4.0735 | 0.56 | 120 | 3.5135 | 0 | 5.88 | 2.3665 | 2.3665 | opened | 114 | SS 35/6 kv Gryazi-gorod | 6,3+5,6 | 1.087 | 5.1605 | 0.56 | 120 | 4.6005 | 0 | 5.88 | 1.2795 | 1.2795 | opened
115 | SS 35/10 kv Butyrki | 5,6+4 | 5.7765 | 0.4 | 120 | 5.3765 | 0 | 4.2 | -1.1765 | -1.1765 | opened | 115 | SS 35/10 kv Butyrki | 5,6+4 | 0.6 | 6.3765 | 0.4 | 120 | 5.9765 | 0 | 4.2 | -1.7765 | -1.7765 | opened
116 | SS 35/10 kv Yarlukovo | 3,2+4 | 2.7334 | 0.32 | 120 | 2.4134 | 0 | 3.36 | 0.9466 | 0.9466 | opened | 116 | SS 35/10 kv Yarlukovo | 3,2+4 | 0.251 | 2.9844 | 0.32 | 120 | 2.6644 | 0 | 3.36 | 0.6956 | 0.6956 | opened
117 | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 0.45413 | 0.16 | 120 | 0.29413 | 0 | 1.68 | 1.3859 | 1.3859 | opened | 117 | SS 35/10 kv Knyazhya Baygora | 1,6+1,6 | 0.005 | 0.45913 | 0.16 | 120 | 0.29912 | 0 | 1.68 | 1.3809 | 1.3809 | opened
118 | SS 35/10 kv Pravda | 4+2,5 | 1.2534 | 0.25 | 120 | 1.0034 | 0 | 2.625 | 1.6216 | 1.6216 | opened | 118 | SS 35/10 kv Pravda | 4+2,5 | 0.01 | 1.2634 | 0.25 | 120 | 1.0134 | 0 | 2.625 | 1.6116 | 1.6116 | opened
119 | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 | 0.55775 | 0.38 | 120 | 0.17775 | 0 | 2.625 | 2.4472 | 2.4472 | opened | 119 | SS 35/10 kv Krasnaya Dubrava | 2,5+2,5 |  | 0.55775 | 0.38 | 120 | 0.17775 | 0 | 2.625 | 2.4472 | 2.4472 | opened
120 | SS 35/10 kv Matyra | 4+3,2 | 3.0054 | 0.45 | 120 | 2.5554 | 0 | 3.36 | 0.80464 | 0.80464 | opened | 120 | SS 35/10 kv Matyra | 4+3,2 | 0.176 | 3.1814 | 0.45 | 120 | 2.7314 | 0 | 3.36 | 0.62864 | 0.62864 | opened
121 | SS 35/10 kv Vperyod | 4+4 | 0.79926 | 0.8 | 120 | -0.00074 | 0 | 4.2 | 4.2007 | 4.2007 | opened | 121 | SS 35/10 kv Vperyod | 4+4 | 0.03 | 0.82926 | 0.8 | 120 | 0.02926 | 0 | 4.2 | 4.1707 | 4.1707 | opened
122 | SS 35/10 kv Maley | 4+2,5 | 0.3633 | 0.38 | 120 | -0.0167 | 0 | 2.625 | 2.6417 | 2.6417 | opened | 122 | SS 35/10 kv Maley | 4+2,5 |  | 0.3633 | 0.38 | 120 | -0.0167 | 0 | 2.625 | 2.6417 | 2.6417 | opened
123 | SS 35/10 kv SKhТ | 2,5+1,6 | 0.67055 | 0.48 | 120 | 0.19055 | 0 | 1.68 | 1.4895 | 1.4895 | opened | 123 | SS 35/10 kv SKhТ | 2,5+1,6 | 0.545 | 1.2155 | 0.48 | 120 | 0.73555 | 0 | 1.68 | 0.94445 | 0.94445 | opened
124 | SS 35/10 kv Soshki | 4+4 | 0.27507 | 0.4 | 120 | -0.12493 | 0 | 4.2 | 4.3249 | 4.3249 | opened | 124 | SS 35/10 kv Soshki | 4+4 | 0.04 | 0.31507 | 0.4 | 120 | -0.08493 | 0 | 4.2 | 4.2849 | 4.2849 | opened
125 | SS 35/6 kv Tavolzhanka | 4+4 | 2.7092 | 0.4 | 120 | 2.3092 | 0 | 4.2 | 1.8908 | 1.8908 | opened | 125 | SS 35/6 kv Tavolzhanka | 4+4 | 0.9705 | 3.6797 | 0.4 | 120 | 3.2797 | 0 | 4.2 | 0.92032 | 0.92032 | opened
126 | SS 35/10 kv Trubetchino | 2,5+2,5 | 1.0588 | 0.15 | 120 | 0.90876 | 0 | 2.625 | 1.7162 | 1.7162 | opened | 126 | SS 35/10 kv Trubetchino | 2,5+2,5 | 0.046 | 1.1048 | 0.15 | 120 | 0.95476 | 0 | 2.625 | 1.6702 | 1.6702 | opened
127 | SS 35/10 kv Ratchino | 2,5+2,5 | 0.96274 | 0.75 | 120 | 0.21274 | 0 | 2.625 | 2.4123 | 2.4123 | opened | 127 | SS 35/10 kv Ratchino | 2,5+2,5 | 0.005 | 0.96774 | 0.75 | 120 | 0.21774 | 0 | 2.625 | 2.4073 | 2.4073 | opened
128 | SS 35/10 kv Kalikino | 3,2+3,2 | 1.6321 | 0.3 | 120 | 1.3321 | 0 | 3.36 | 2.0279 | 2.0279 | opened | 128 | SS 35/10 kv Kalikino | 3,2+3,2 | 0.01 | 1.6421 | 0.3 | 120 | 1.3421 | 0 | 3.36 | 2.0179 | 2.0179 | opened
129 | SS 35/10 kv Borisovka | 4+2,5 | 2.7429 | 0.37 | 120 | 2.3729 | 0 | 2.625 | 0.25209 | 0.25209 | opened | 129 | SS 35/10 kv Borisovka | 4+2,5 | 0.56 | 3.3029 | 0.37 | 120 | 2.9329 | 0 | 2.625 | -0.30791 | -0.30791 | closed
130 | SS 35/10 kv Vvedenka | 4+4 | 3.0586 | 0.2 | 120 | 2.8586 | 0 | 4.2 | 1.3414 | 1.3414 | opened | 130 | SS 35/10 kv Vvedenka | 4+4 | 0.638 | 3.6966 | 0.2 | 120 | 3.4966 | 0 | 4.2 | 0.70336 | 0.70336 | opened
131 | SS 35/10 kv Gryaznoe | 4+4 | 2.5009 | 0 | 0 | 2.5009 | 0 | 4.2 | 1.6991 | 1.6991 | opened | 131 | SS 35/10 kv Gryaznoe | 4+4 | 0.025 | 2.5259 | 0 | 0 | 2.5259 | 0 | 4.2 | 1.6741 | 1.6741 | opened
132 | SS 35/10 kv Borino | 4+4 | 4.3596 | 0.2 | 120 | 4.1596 | 0 | 4.2 | 0.0404 | 0.0404 | opened | 132 | SS 35/10 kv Borino | 6,3+6,3 | 0.351 | 4.7106 | 0.2 | 120 | 4.5106 | 0 | 6.615 | 2.1044 | 2.1044 | opened
133 | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 1.1626 | 0.5 | 120 | 0.66256 | 0 | 2.625 | 1.9624 | 1.9624 | opened | 133 | SS 35/10 kv Chastaya Dubrava | 2,5+2,5 | 0.042 | 1.2046 | 0.5 | 120 | 0.70456 | 0 | 2.625 | 1.9204 | 1.9204 | opened
134 | SS 35/10 kv Troitskaya | 2,5+4 | 2.285 | 0.25 | 120 | 2.035 | 0 | 2.625 | 0.59002 | 0.59002 | opened | 134 | SS 35/10 kv Troitskaya | 2,5+4 | 0.099 | 2.384 | 0.25 | 120 | 2.134 | 0 | 2.625 | 0.49102 | 0.49102 | opened
135 | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.80445 | 0 | 0 | 0.80445 | 0 | 2.625 | 1.8205 | 1.8205 | opened | 135 | SS 35/6 kv Veshalovka | 2,5+2,5 | 0.005 | 0.80945 | 0 | 0 | 0.80945 | 0 | 2.625 | 1.8155 | 1.8155 | opened
136 | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.7266 | 0 | 0 | 0.7266 | 0 | 2.625 | 1.8984 | 1.8984 | opened | 136 | SS 35/10 kv Pruzhinki | 2,5+2,5 | 0.014 | 0.7406 | 0 | 0 | 0.7406 | 0 | 2.625 | 1.8844 | 1.8844 | opened
137 | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.95288 | 0.13 | 120 | 0.82288 | 0 | 2.625 | 1.8021 | 1.8021 | opened | 137 | SS 35/10 kv Stebaevo | 2,5+2,5 | 0.007 | 0.95988 | 0.13 | 120 | 0.82988 | 0 | 2.625 | 1.7951 | 1.7951 | opened
138 | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 4.8129 | 0.63 | 120 | 4.1829 | 0 | 6.615 | 2.4321 | 2.4321 | opened | 138 | SS 35/10 kv Khleboprodukty | 6,3+6,3 | 0.017 | 4.8299 | 0.63 | 120 | 4.1999 | 0 | 6.615 | 2.4151 | 2.4151 | opened
139 | SS 35/10 kv Sentsovo | 10+10 | 6.8603 | 0.5 | 120 | 6.3603 | 0 | 10.5 | 4.1397 | 4.1397 | opened | 139 | SS 35/10 kv Sentsovo | 10+10 | 0.026 | 6.8863 | 0.5 | 120 | 6.3863 | 0 | 10.5 | 4.1137 | 4.1137 | opened
140 | SS 35/10 kv Meet processing factory | 6,3+6,3 | 4.8578 | 1.26 | 0 | 3.5978 | 0 | 6.62 | 3.0222 | 3.0222 | opened | 140 | SS 35/10 kv Meet processing factory | 6,3+6,3 | 0.55 | 5.4078 | 1.26 | 0 | 4.1478 | 0 | 6.62 | 2.4722 | 2.4722 | opened
141 | SS 35/6 kv Poultry plant | 4+4 | 2.9894 | 0 | 0 | 2.9894 | 0 | 4.2 | 1.2106 | 1.2106 | opened | 141 | SS 35/6 kv Poultry plant | 4+4 | 0.005 | 2.9944 | 0 | 0 | 2.9944 | 0 | 4.2 | 1.2056 | 1.2056 | opened
142 | SS 35/6 kv Water intake | 10+10 | 1.1292 | 0 | 0 | 1.1292 | 0 | 10.5 | 9.3708 | 9.3708 | opened | 142 | SS 35/6 kv Water intake | 10+10 | 0.1325 | 1.2617 | 0 | 0 | 1.2617 | 0 | 10.5 | 9.2383 | 9.2383 | opened
143 | SS 35/10 kv Petrovskaya | 2,5+4 | 1.3698 | 0.25 | 120 | 1.1198 | 0 | 2.625 | 1.5052 | 1.5052 | opened | 143 | SS 35/10 kv Petrovskaya | 2,5+4 | 0.005 | 1.3748 | 0.25 | 120 | 1.1248 | 0 | 2.625 | 1.5002 | 1.5002 | opened
144 | SS 35/10 kv Lebedyanka | 2,5+2,5 | 0.33008 | 0.25 | 120 | 0.080084 | 0 | 2.625 | 2.5449 | 2.5449 | opened | 144 | SS 35/10 kv Lebedyanka | 2,5+2,5 |  | 0.33008 | 0.25 | 120 | 0.080084 | 0 | 2.625 | 2.5449 | 2.5449 | opened
145 | SS 35/10 kv Novocherkutino | 4+4 | 0.833 | 0.4 | 120 | 0.433 | 0 | 4.2 | 3.767 | 3.767 | opened | 145 | SS 35/10 kv Novocherkutino | 4+4 |  | 0.833 | 0.4 | 120 | 0.433 | 0 | 4.2 | 3.767 | 3.767 | opened
146 | SS 35/10 kv Ivanovka | 2,5+2,5 | 0.92659 | 0 | 0 | 0.92659 | 0 | 2.625 | 1.6984 | 1.6984 | opened | 146 | SS 35/10 kv Ivanovka | 2,5+2,5 |  | 0.92659 | 0 | 0 | 0.92659 | 0 | 2.625 | 1.6984 | 1.6984 | opened
147 | SS 35/10 kv Poddubrovka | 2,5+2,5 | 1.1335 | 0.3 | 0 | 0.8335 | 0 | 2.625 | 1.7915 | 1.7915 | opened | 147 | SS 35/10 kv Poddubrovka | 2,5+2,5 | 0.025 | 1.1585 | 0.3 | 0 | 0.8585 | 0 | 2.625 | 1.7665 | 1.7665 | opened
148 | SS 35/10 kv Plavitsa | 1,6+1,6 | 0.69494 | 0.16 | 120 | 0.53494 | 0 | 1.68 | 1.1451 | 1.1451 | opened | 148 | SS 35/10 kv Plavitsa | 1,6+1,6 | 0.005 | 0.69994 | 0.16 | 120 | 0.53994 | 0 | 1.68 | 1.1401 | 1.1401 | opened
149 | SS 35/10 kv Parshinovka | 1,6+2,5 | 0.34842 | 0 | 0 | 0.34842 | 0 | 1.68 | 1.3316 | 1.3316 | opened | 149 | SS 35/10 kv Parshinovka | 1,6+2,5 |  | 0.34842 | 0 | 0 | 0.34842 | 0 | 1.68 | 1.3316 | 1.3316 | opened
150 | SS 35/10 kv Talitsky Chamlyk | 3,2+4 | 1.2103 | 0.32 | 120 | 0.89031 | 0 | 3.36 | 2.4697 | 2.4697 | opened | 150 | SS 35/10 kv Talitsky Chamlyk | 3,2+4 |  | 1.2103 | 0.32 | 120 | 0.89031 | 0 | 3.36 | 2.4697 | 2.4697 | opened
151 | SS 35/10 kv Demshinka | 2,5+2,5 | 0.21383 | 0.25 | 120 | -0.036172 | 0 | 2.625 | 2.6612 | 2.6612 | opened | 151 | SS 35/10 kv Demshinka | 2,5+2,5 |  | 0.21383 | 0.25 | 120 | -0.036172 | 0 | 2.625 | 2.6612 | 2.6612 | opened
152 | SS 35/10 kv Bereznyagovka | 1,6+1,6 | 0.81742 | 0.24 | 120 | 0.57742 | 0 | 1.68 | 1.1026 | 1.1026 | opened | 152 | SS 35/10 kv Bereznyagovka | 1,6+1,6 |  | 0.81742 | 0.24 | 120 | 0.57742 | 0 | 1.68 | 1.1026 | 1.1026 | opened
153 | SS 35/10 kv Dmitrievka | 2,5+2,5 | 0.41382 | 0.38 | 120 | 0.033816 | 0 | 2.625 | 2.5912 | 2.5912 | opened | 153 | SS 35/10 kv Dmitrievka | 2,5+2,5 |  | 0.41382 | 0.38 | 120 | 0.033816 | 0 | 2.625 | 2.5912 | 2.5912 | opened
154 | SS 35/10 kv Pashkovo | 2,5+2,5 | 1.0513 | 0.38 | 120 | 0.67132 | 0 | 2.625 | 1.9537 | 1.9537 | opened | 154 | SS 35/10 kv Pashkovo | 2,5+2,5 |  | 1.0513 | 0.38 | 120 | 0.67132 | 0 | 2.625 | 1.9537 | 1.9537 | opened
155 | SS 35/10 kv Moskovka | 1,6+1,6 | 0.52678 | 0.24 | 120 | 0.28679 | 0 | 1.68 | 1.3932 | 1.3932 | opened | 155 | SS 35/10 kv Moskovka | 1,6+1,6 | 0.028 | 0.55478 | 0.24 | 120 | 0.31478 | 0 | 1.68 | 1.3652 | 1.3652 | opened
156 | SS 35/10 kv Bochinovka | 4+4 | 2.5189 | 0.6 | 120 | 1.9189 | 0 | 4.2 | 2.2811 | 2.2811 | opened | 156 | SS 35/10 kv Bochinovka | 4+4 | 1.175 | 3.6939 | 0.6 | 120 | 3.0939 | 0 | 4.2 | 1.1061 | 1.1061 | opened
157 | SS 35/10 kv Fyodorovka | 2,5+2,5 | 0.33008 | 0.38 | 120 | -0.049916 | 0 | 2.625 | 2.6749 | 2.6749 | opened | 157 | SS 35/10 kv Fyodorovka | 2,5+2,5 |  | 0.33008 | 0.38 | 120 | -0.049916 | 0 | 2.625 | 2.6749 | 2.6749 | opened
158 | SS 35/10 kv Kulikovo | 2,5+2,5 | 0.30586 | 0 | 0 | 0.30586 | 0 | 2.625 | 2.3191 | 2.3191 | opened | 158 | SS 35/10 kv Kulikovo | 2,5+2,5 | 0.002 | 0.30786 | 0 | 0 | 0.30786 | 0 | 2.625 | 2.3171 | 2.3171 | opened
159 | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 1.0536 | 0.25 | 120 | 0.80357 | 0 | 2.625 | 1.8214 | 1.8214 | opened | 159 | SS 35/10 kv Kon-Kolodez | 2,5+2,5 | 0.205 | 1.2586 | 0.25 | 120 | 1.0086 | 0 | 2.625 | 1.6164 | 1.6164 | opened
160 | SS 35/10 kv Dmitryashevka | 2,5+2,5 | 0.12369 | 0.25 | 120 | -0.12631 | 0 | 2.625 | 2.7513 | 2.7513 | opened | 160 | SS 35/10 kv Dmitryashevka | 2,5+2,5 |  | 0.12369 | 0.25 | 120 | -0.12631 | 0 | 2.625 | 2.7513 | 2.7513 | opened
161 | SS 35/10 kv Rechnaya | 4+4 | 0.49045 | 0.6 | 120 | -0.10955 | 0 | 4.2 | 4.3095 | 4.3095 | opened | 161 | SS 35/10 kv Rechnaya | 4+4 | 0.016 | 0.50645 | 0.6 | 120 | -0.093545 | 0 | 4.2 | 4.2935 | 4.2935 | opened
162 | SS 35/10 kv Negachevka | 2,5+2,5 | 0 | 0.25 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | opened | 162 | SS 35/10 kv Negachevka | 2,5+2,5 | 0.0015 | 0.0015 | 0.25 | 120 | -0.2485 | 0 | 2.625 | 2.8735 | 2.8735 | opened
163 | SS 35/10 kv Karamyshevo | 10+10 | 0.49045 | 1 | 120 | -0.50955 | 0 | 10.5 | 11.0095 | 11.0095 | opened | 163 | SS 35/10 kv Karamyshevo | 10+10 | 0.041 | 0.53146 | 1 | 120 | -0.46854 | 0 | 10.5 | 10.9685 | 10.9685 | opened
164 | SS 35/10 kv Tyushevka | 1,6+1,6 |  | 0.08 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened | 164 | SS 35/10 kv Tyushevka | 1,6+1,6 |  | 0 | 0.08 | 120 | -0.08 | 0 | 1.68 | 1.76 | 1.76 | opened
165 | SS 110/35/10 kv Terbuny-110 | 10+10 | 8.7815 | 11 |  | -2.2185 | 0 | 10.5 | 12.7185 | 5.7946 | opened | 165 | SS 110/35/10 kv Terbuny-110 | 10+25 |  | 9.9475 | 11 |  | -1.0525 | 0 | 10.5 | 0.5525 | 0.5525 | opened
| Nom. Capacity MV, МVA | 10+10 | 3.0761 | 10 | 10 | -6.9239 | 0 | 10.5 | 7.4239 |  |  |  | Nom. Capacity MV, МVA | 10+10 |  | 3.0761 | 10 | 10 | -6.9239 | 0 | 10.5 | 7.4239
| Nom. capacity LV, МVA | 10+10 | 5.7054 | 1 | 120 | 4.7054 | 0 | 10.5 | 5.7946 |  |  |  | Nom. capacity LV, МVA | 10+10 | 1.166 | 6.8714 | 1 | 120 | 5.8714 | 0 | 10.5 | 4.6286
166 | SS 110/35/10 kv Dolgorukovo | 6,3+10 | 6.1983 | 6.93 |  | -0.73168 | 0 | 6.615 | 7.3467 | 2.9808 | opened | 166 | SS 110/35/10 kv Dolgorukovo | 6,3+10 |  | 6.2163 | 6.93 |  | -0.71368 | 0 | 6.615 | 0.39868 | 0.39868 | opened
| Nom. capacity MV, МVA | 6,3+10 | 3.6342 | 6.3 | 10 | -2.6658 | 0 | 6.615 | 2.9808 |  |  |  | Nom. capacity MV, МVA | 6,3+10 |  | 3.6342 | 6.3 | 10 | -2.6658 | 0 | 6.615 | 2.9808
| Nom. capacity LV, МVA | 6,3+10 | 2.5641 | 0.63 | 120 | 1.9341 | 0 | 6.615 | 4.6809 |  |  |  | Nom. capacity LV, МVA | 6,3+10 | 0.018 | 2.5821 | 0.63 | 120 | 1.9521 | 0 | 6.615 | 4.6629
167 | SS 110/35/10 kv Volovo | 10+10 | 3.1984 | 3.8 |  | -0.60159 | 0 | 10.5 | 11.1016 | 8.3016 | opened | 167 | SS 110/35/10 kv Volovo | 10+10 |  | 3.2034 | 3.8 |  | -0.59659 | 0 | 10.5 | 7.2966 | 7.2966 | opened
| Nom. capacity MV, МVA | 10+10 | 0 | 2.8 | 20 | -2.8 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVA | 10+10 |  | 0 | 2.8 | 20 | -2.8 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 3.1984 | 1 | 120 | 2.1984 | 0 | 10.5 | 8.3016 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.005 | 3.2034 | 1 | 120 | 2.2034 | 0 | 10.5 | 8.2966
168 | SS 110/35/10 kv Izmalkovo | 10+10 | 6.1332 | 2.5 |  | 3.6332 | 0 | 10.5 | 6.8668 | 6.8668 | opened | 168 | SS 110/35/10 kv Izmalkovo | 10+10 |  | 6.1842 | 2.5 |  | 3.6842 | 0 | 10.5 | 6.8158 | 6.8158 | opened
| Nom. capacity MV, МVА | 10+10 | 2.4595 | 1.5 | 20 | 0.95951 | 0 | 10.5 | 8.0405 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.4595 | 1.5 | 20 | 0.95951 | 0 | 10.5 | 9.5405
| Nom. capacity LV, МVА | 10+10 | 3.6737 | 1 | 120 | 2.6737 | 0 | 10.5 | 7.8263 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.051 | 3.7247 | 1 | 120 | 2.7247 | 0 | 10.5 | 7.7753
169 | SS 110/35/10 kv Gorokhovskaya | 16+16 | 10.0313 | 9.6 |  | 0.43135 | 0 | 16.8 | 16.3687 | 9.9134 | opened | 169 | SS 110/35/10 kv Gorokhovskaya | 16+16 |  | 10.1833 | 9.6 |  | 0.58335 | 0 | 16.8 | 16.2167 | 9.9134 | opened
| Nom. capacity MV, МVА | 16+16 | 6.8866 | 8 | 20 | -1.1134 | 0 | 16.8 | 9.9134 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.8866 | 8 | 20 | -1.1134 | 0 | 16.8 | 9.9134
| Nom. capacity LV, МVА | 16+16 | 3.1447 | 1.6 | 120 | 1.5447 | 0 | 16.8 | 15.2553 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.152 | 3.2967 | 1.6 | 120 | 1.6967 | 0 | 16.8 | 15.1033
170 | SS 110/35/10 kv Donskaya | 10+10 | 5.4128 | 3 |  | 2.4128 | 0 | 10.5 | 8.0872 | 8.0872 | opened | 170 | SS 110/35/10 kv Donskaya | 10+10 |  | 5.4398 | 3 |  | 2.4398 | 0 | 10.5 | 8.0602 | 8.0602 | opened
| Nom. capacity MV, МVА | 10+10 | 2.1124 | 2 | 20 | 0.11241 | 0 | 10.5 | 8.3876 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.1124 | 2 | 20 | 0.11241 | 0 | 10.5 | 10.3876
| Nom. capacity LV, МVА | 10+10 | 3.3004 | 1 | 120 | 2.3004 | 0 | 10.5 | 8.1996 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.027 | 3.3274 | 1 | 120 | 2.3274 | 0 | 10.5 | 8.1726
171 | SS 110/35/10 kv Lebedyan | 16+16 | 20.4417 | 17.6 |  | 2.8417 | 0 | 16.8 | 13.9583 | 7.1975 | opened | 171 | SS 110/35/10 kv Lebedyan | 16+16 |  | 20.6057 | 17.6 |  | 3.0057 | 0 | 16.8 | 13.7943 | 7.1975 | opened
| Nom. capacity MV, МVА | 16+16 | 9.6025 | 16 | 10 | -6.3975 | 0 | 16.8 | 7.1975 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 9.6025 | 16 | 10 | -6.3975 | 0 | 16.8 | 7.1975
| Nom. capacity LV, МVА | 16+16 | 10.8392 | 1.6 | 120 | 9.2392 | 0 | 16.8 | 7.5608 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.164 | 11.0032 | 1.6 | 120 | 9.4032 | 0 | 16.8 | 7.3968
172 | SS 110/35/10 kv Chaplygin-novaya | 16+16 | 9.4414 | 33.6 |  | -24.1586 | 0 | 16.8 | 40.9586 | 9.9411 | opened | 172 | SS 110/35/10 kv Chaplygin-novaya | 16+16 |  | 9.4674 | 33.6 |  | -24.1326 | 0 | 16.8 | 7.3326 | 7.3326 | opened
| Nom. capacity MV, МVА | 16+16 | 6.8589 | 32 | 10 | -25.1411 | 0 | 16.8 | 9.9411 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.8589 | 32 | 10 | -25.1411 | 0 | 16.8 | 9.9411
| Nom. capacity LV, МVА | 16+16 | 2.5825 | 1.6 | 120 | 0.98249 | 0 | 16.8 | 15.8175 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.026 | 2.6085 | 1.6 | 120 | 1.0085 | 0 | 16.8 | 15.7915
173 | SS 110/35/10 kv Kompressornaya | 16+16 | 5.5166 | 33.6 |  | -28.0834 | 0 | 16.8 | 44.8834 | 12.5565 | opened | 173 | SS 110/35/10 kv Kompressornaya | 16+16 |  | 5.5246 | 33.6 |  | -28.0754 | 0 | 16.8 | 11.2754 | 11.2754 | opened
| Nom. Capacity MV, МVА | 16+16 | 4.2435 | 32 | 10 | -27.7565 | 0 | 16.8 | 12.5565 |  |  |  | Nom. Capacity MV, МVА | 16+16 |  | 4.2435 | 32 | 10 | -27.7565 | 0 | 16.8 | 12.5565
| Nom. capacity LV, МVА | 16+16 | 1.2731 | 1.6 | 120 | -0.32694 | 0 | 16.8 | 17.1269 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.008 | 1.2811 | 1.6 | 120 | -0.31894 | 0 | 16.8 | 15.5189
174 | SS 110/35/10 kv Russia | 16+16 | 1.7147 | 26.8 |  | -25.0853 | 0 | 16.8 | 41.8853 | 15.9513 | opened | 174 | SS 110/35/10 kv Russia | 16+16 |  | 1.7161 | 26.8 |  | -25.0839 | 0 | 16.8 | 15.0839 | 15.0839 | opened
| Nom. capacity MV, МVА | 16+16 | 0.8487 | 26 |  | -25.1513 | 0 | 16.8 | 15.9513 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 0.8487 | 26 |  | -25.1513 | 0 | 16.8 | 15.9513
| Nom. capacity LV, МVА | 16+16 | 0.86603 | 0.8 | 120 | 0.066025 | 0 | 16.8 | 16.734 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.0014 | 0.86743 | 0.8 | 120 | 0.067425 | 0 | 16.8 | 16.7326
175 | SS 110/35/10 kv Beryozovka | 16+10 | 2.1498 | 25 |  | -22.8502 | 0 | 10.5 | 33.3502 | 9.58 | opened | 175 | SS 110/35/10 kv Beryozovka | 16+10 |  | 2.1998 | 25 |  | -22.8002 | 0 | 10.5 | 8.3002 | 8.3002 | opened
| Nom. capacity MV, МVА | 16+10 | 0.92 | 24 | 10 | -23.08 | 0 | 10.5 | 9.58 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 0.92 | 24 | 10 | -23.08 | 0 | 10.5 | 9.58
| Nom. capacity LV, МVА | 16+10 | 1.2298 | 1 | 120 | 0.22976 | 0 | 10.5 | 10.2702 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.05 | 1.2798 | 1 | 120 | 0.27976 | 0 | 10.5 | 10.2202
176 | SS 110/35/10 kv Astapovo | 16+16 | 3.4139 | 32.8 |  | -29.3861 | 0 | 16.8 | 46.1861 | 14.9917 | opened | 176 | SS 110/35/10 kv Astapovo | 16+16 |  | 3.4519 | 32.8 |  | -29.3481 | 0 | 16.8 | 13.3481 | 13.3481 | opened
| Nom. capacity MV, МVА | 16+16 | 1.8083 | 32 | 10 | -30.1917 | 0 | 16.8 | 14.9917 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 1.8083 | 32 | 10 | -30.1917 | 0 | 16.8 | 14.9917
| Nom. capacity LV, МVА | 16+16 | 1.6056 | 0.8 | 120 | 0.80561 | 0 | 16.8 | 15.9944 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.038 | 1.6436 | 0.8 | 120 | 0.84361 | 0 | 16.8 | 15.9564
177 | SS 110/35/10 kv Khimicheskaya | 16+16 | 9.732 | 15.6 |  | -5.868 | 0 | 16.8 | 22.668 | 9.0466 | opened | 177 | SS 110/35/10 kv Khimicheskaya | 16+16 |  | 9.8 | 15.6 |  | -5.8 | 0 | 16.8 | 7 | 7 | opened
| Nom. capacity MV, МVА | 16+16 | 7.7534 | 14 | 10 | -6.2466 | 0 | 16.8 | 9.0466 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 7.7534 | 14 | 10 | -6.2466 | 0 | 16.8 | 9.0466
| Nom. capacity LV, МVА | 16+16 | 1.9787 | 1.6 | 120 | 0.37869 | 0 | 16.8 | 16.4213 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.068 | 2.0467 | 1.6 | 120 | 0.44669 | 0 | 16.8 | 16.3533
178 | SS 110/35/6 kv Bugor | 15+15+25 | 30.8 | 0.5 |  | 30.3 | 0 | 26.25 | -4.05 | -4.05 | closed | 178 | SS 110/35/6 kv Bugor | 15+15+25 |  | 33.772 | 0.5 |  | 33.272 | 0 | 26.25 | -7.022 | -7.022 | closed
| Nom. capacity MV, МVА | 15+15+25 | 9.8 | 0 | 0 | 9.8 | 0 | 26.25 | 16.45 |  |  |  | Nom. capacity MV, МVА | 15+15+25 |  | 9.8 | 0 | 0 | 9.8 | 0 | 26.25 | 16.45
| Nom. capacity LV, МVА | 15+15+25 | 21 | 0.5 | 40 | 20.5 | 0 | 26.25 | 5.75 |  |  |  | Nom. capacity LV, МVА | 15+15+25 | 2.972 | 23.972 | 0.5 | 40 | 23.472 | 0 | 26.25 | 2.778
179 | SS 110/35/6 kvВ Tsementnaya | 63+32+20 | 29.3754 | 3.5 |  | 25.8754 | 0 | 54.6 | 28.7246 | -1.836 | closed | 179 | SS 110/35/6 kvВ Tsementnaya | 63+32+20 |  | 29.3754 | 0 |  | 29.3754 | 0 | 54.6 | 25.2246 | -1.836 | closed
| Nom. capacity MV, МVА | 63+20 | 22.836 | 0 | 0 | 22.836 | 0 | 21 | -1.836 |  |  |  | Nom. capacity MV, МVА | 63+20 |  | 22.836 | 0 | 0 | 22.836 | 0 | 21 | -1.836
| Nom. capacity LV, МVА | 63+32+20 | 6.5394 | 3.5 | 30 | 3.0394 | 0 | 54.6 | 51.5606 |  |  |  | Nom. capacity LV, МVА | 63+32+20 |  | 6.5394 | 0 | 30 | 6.5394 | 0 | 54.6 | 48.0606
180 | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 | 6.8551 | 10 |  | -3.1449 | 0 | 52.5 | 55.6449 | 1.2632 | opened | 180 | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 |  | 7.3051 | 10 |  | -2.6949 | 0 | 52.5 | 45.1949 | -3.7368 | closed
| Nom. capacity MV, МVА | 31.5 | 3.7368 | 5 | 10 | -1.2632 | 0 | 5 | 1.2632 |  |  |  | Nom. capacity MV, МVА | 31.5 |  | 3.7368 | 5 | 10 | -1.2632 | 0 | 0 | -3.7368
| Nom. capacity LV, МVА | 25+25+31,5 | 3.1183 | 5 | 120 | -1.8817 | 0 | 52.5 | 54.3817 |  |  |  | Nom. capacity LV, МVА | 25+25+31,5 | 0.45 | 3.5683 | 5 | 120 | -1.4317 | 0 | 52.5 | 48.9317
181 | SS 110/35/10 kv Usman | 16+16 | 14.5932 | 17.6 |  | -3.0068 | 0 | 16.8 | 19.8068 | 9.1888 | opened | 181 | SS 110/35/10 kv Usman | 16+16 |  | 15.0282 | 17.6 |  | -2.5718 | 0 | 16.8 | 1.7718 | 1.7718 | opened
| Nom. capacity MV, МVА | 16+16 | 5.382 | 16 | 10 | -10.618 | 0 | 16.8 | 11.418 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 5.382 | 16 | 10 | -10.618 | 0 | 16.8 | 11.418
| Nom. Capacity LV, МVА | 16+16 | 9.2112 | 1.6 | 120 | 7.6112 | 0 | 16.8 | 9.1888 |  |  |  | Nom. Capacity LV, МVА | 16+16 | 0.435 | 9.6462 | 1.6 | 120 | 8.0462 | 0 | 16.8 | 8.7538
182 | SS 110/35/10 kv Aksai | 10+10 | 5.9425 | 11.4 |  | -5.4574 | 0 | 10.5 | 15.9574 | 6.7632 | opened | 182 | SS 110/35/10 kv Aksai | 10+10 |  | 6.0225 | 11.4 |  | -5.3774 | 0 | 10.5 | 4.4775 | 4.4775 | opened
| Nom. Capacity MV, МVА | 10+10 | 3.7368 | 10 | 10 | -6.2632 | 0 | 10.5 | 6.7632 |  |  |  | Nom. Capacity MV, МVА | 10+10 |  | 3.7368 | 10 | 10 | -6.2632 | 0 | 10.5 | 6.7632
| Nom. capacity LV, МVА | 10+10 | 2.2058 | 1.4 | 120 | 0.80575 | 0 | 10.5 | 9.6943 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.08 | 2.2858 | 1.4 | 120 | 0.88575 | 0 | 10.5 | 9.6143
183 | SS 110/35/10 kv Nikolskaya | 6,3+6,3 | 4.3631 | 7 |  | -2.6369 | 0 | 6.615 | 9.2519 | 3.4214 | opened | 183 | SS 110/35/10 kv Nikolskaya | 6,3+6,3 |  | 4.3631 | 7 |  | -2.6369 | 0 | 6.615 | 2.2519 | 2.2519 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 3.1936 | 6.3 | 10 | -3.1064 | 0 | 6.615 | 3.4214 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 3.1936 | 6.3 | 10 | -3.1064 | 0 | 6.615 | 3.4214
| Nom. capacity LV, МVА | 6,3+6,3 | 1.1695 | 0.7 | 120 | 0.46948 | 0 | 6.615 | 6.1455 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 |  | 1.1695 | 0.7 | 120 | 0.46948 | 0 | 6.615 | 6.1455
184 | SS 110/35/10 kv Khvorostyanka | 10+16 | 11.2592 | 7 |  | 4.2592 | 0 | 10.5 | 6.2408 | 1.9054 | opened | 184 | SS 110/35/10 kv Khvorostyanka | 10+16 |  | 11.2732 | 7 |  | 4.2732 | 0 | 10.5 | 6.2268 | 6.2268 | opened
| Nom. capacity MV, МVА | 10+16 | 8.5946 | 6 | 10 | 2.5946 | 0 | 10.5 | 1.9054 |  |  |  | Nom. capacity MV, МVА | 10+16 |  | 8.5946 | 6 | 10 | 2.5946 | 0 | 10.5 | 7.9054
| Nom. capacity LV, МVА | 10+16 | 2.6645 | 1 | 120 | 1.6645 | 0 | 10.5 | 8.8355 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.014 | 2.6785 | 1 | 120 | 1.6785 | 0 | 10.5 | 8.8215
185 | SS 110/35/10 kv Dobrinka | 16+10 | 6.9312 | 5.1 |  | 1.8312 | 0 | 10.5 | 8.6688 | 7.5651 | opened | 185 | SS 110/35/10 kv Dobrinka | 16+10 |  | 7.3452 | 5.1 |  | 2.2452 | 0 | 10.5 | 8.2548 | 7.5651 | opened
| Nom. capacity СН, МВА | 16+10 | 2.9349 | 3.5 | 20 | -0.56505 | 0 | 10.5 | 7.5651 |  |  |  | Nom. capacity СН, МВА | 16+10 |  | 2.9349 | 3.5 | 20 | -0.56505 | 0 | 10.5 | 7.5651
| Nom. capacity LV, МVА | 16+10 | 3.9963 | 1.6 | 120 | 2.3963 | 0 | 10.5 | 8.1037 |  |  |  | Nom. capacity LV, МVА | 16+10 | 0.414 | 4.4103 | 1.6 | 120 | 2.8103 | 0 | 10.5 | 7.6897
186 | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 | 1.0795 | 4.13 |  | -3.0505 | 0 | 6.615 | 9.6655 | 6.2413 | opened | 186 | SS 110/35/10 kv Verkhnyaya Matryonka | 6,3+6,3 |  | 1.0895 | 4.13 |  | -3.0405 | 0 | 6.615 | 5.5255 | 5.5255 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.37368 | 3.5 | 20 | -3.1263 | 0 | 6.615 | 6.2413 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 0.37368 | 3.5 | 20 | -3.1263 | 0 | 6.615 | 6.2413
| Nom. capacity LV, МVА | 6,3+6,3 | 0.70584 | 0.63 | 120 | 0.07584 | 0 | 6.615 | 6.5392 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.01 | 0.71584 | 0.63 | 120 | 0.08584 | 0 | 6.615 | 6.5292
187 | SS 110/35/10 kv Kazinka | 16+16 | 13.2042 | 7.6 |  | 5.6042 | 0 | 16.8 | 11.1958 | 7.6941 | opened | 187 | SS 110/35/10 kv Kazinka | 16+16 |  | 13.6192 | 7.6 |  | 6.0192 | 0 | 16.8 | 10.7808 | 10.7808 | opened
| Nom. capacity MV, МVА | 16+16 | 9.1059 | 7.3 | 10 | 1.8059 | 0 | 16.8 | 7.6941 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 9.1059 | 7.3 | 10 | 1.8059 | 0 | 16.8 | 14.9941
| Nom. capacity LV, МVА | 16+16 | 4.0984 | 0.3 | 120 | 3.7984 | 0 | 16.8 | 13.0016 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.415 | 4.5134 | 0.3 | 120 | 4.2134 | 0 | 16.8 | 12.5866
188 | SS 110/35/10 kv Dobroe | 16+16 | 9.9897 | 9.2 |  | 0.78971 | 0 | 16.8 | 16.0103 | 10.6796 | opened | 188 | SS 110/35/10 kv Dobroe | 16+16 |  | 10.2727 | 9.2 |  | 1.0727 | 0 | 16.8 | 15.7273 | 15.7273 | opened
| Nom. capacity MV, МVА | 16+16 | 6.1204 | 6 | 10 | 0.12039 | 0 | 16.8 | 10.6796 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 6.1204 | 6 | 10 | 0.12039 | 0 | 16.8 | 16.6796
| Nom. capacity LV, МVА | 16+16 | 3.8693 | 3.2 | 120 | 0.66932 | 0 | 16.8 | 16.1307 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.283 | 4.1523 | 3.2 | 120 | 0.95232 | 0 | 16.8 | 15.8477
189 | SS 110/35/6 kv Novaya Derevnya | 10+6,3 | 7.8348 | 5.63 |  | 2.2048 | 0 | 6.615 | 4.4102 | 1.0721 | opened | 189 | SS 110/35/6 kv Novaya Derevnya | 10+6,3 |  | 7.8758 | 5.63 |  | 2.2458 | 0 | 6.615 | 4.3692 | 4.3692 | opened
| Nom. capacity MV, МVА | 10+6,3 | 5.5429 | 5 | 10 | 0.54292 | 0 | 6.615 | 1.0721 |  |  |  | Nom. capacity MV, МVА | 10+6,3 |  | 5.5429 | 5 | 10 | 0.54292 | 0 | 6.615 | 6.0721
| Nom. capacity LV, МVА | 10+6,3 | 2.2919 | 0.63 | 120 | 1.6619 | 0 | 6.615 | 4.9531 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.041 | 2.3329 | 0.63 | 120 | 1.7029 | 0 | 6.615 | 4.9121
190 | SS 110/35/6 kv Verbilovo | 10+6,3 | 0.90462 | 2 |  | -1.0954 | 0 | 6.62 | 7.7154 | 5.7154 | opened | 190 | SS 110/35/6 kv Verbilovo | 10+6,3 |  | 0.91462 | 2 |  | -1.0854 | 0 | 6.62 | 5.7054 | 5.7054 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0 | 2 | 10 | -2 | 0 | 6.62 | 6.62 |  |  |  | Nom. capacity MV, МV | 10+6,3 |  | 0 | 2 | 10 | -2 | 0 | 6.62 | 6.62
| Nom. capacity LV, МVА | 10+6,3 | 0.90462 | 0 | 0 | 0.90462 | 0 | 6.62 | 5.7154 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.01 | 0.91462 | 0 | 0 | 0.91462 | 0 | 6.62 | 5.7054
191 | SS 110/35/10 kv Khlevnoe | 16+16 | 8.7676 | 7.4 |  | 1.3676 | 0 | 16.8 | 15.4324 | 11.7744 | opened | 191 | SS 110/35/10 kv Khlevnoe | 16+16 |  | 10.1416 | 7.4 |  | 2.7416 | 0 | 16.8 | 14.0584 | 14.0584 | opened
| Nom. capacity MV, МVА | 16+16 | 5.0256 | 5 | 10 | 0.02565 | 0 | 16.8 | 11.7744 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 5.0256 | 5 | 10 | 0.02565 | 0 | 16.8 | 16.7743
| Nom. capacity LV, МVА | 16+16 | 3.742 | 2.4 | 120 | 1.342 | 0 | 16.8 | 15.458 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.374 | 5.116 | 2.4 | 120 | 2.716 | 0 | 16.8 | 14.084
192 | SS 110/35/10 kv Naberezhnoe | 6,3+10 | 1.6732 | 6.93 |  | -5.2568 | 0 | 6.62 | 11.8768 | 5.747 | opened | 192 | SS 110/35/10 kv Naberezhnoe | 6,3+10 |  | 1.6982 | 6.93 |  | -5.2318 | 0 | 6.62 | 11.8518 | 6.4248 | opened
| Nom. capacity MV, МVА | 6,3+10 | 0.87295 | 6.3 | 10 | -5.427 | 0 | 6.62 | 5.747 |  |  |  | Nom. capacity MV, МVА | 6,3+10 |  | 0.87295 | 6.3 | 10 | -5.427 | 0 | 6.62 | 12.047
| Nom. capacity LV, МVА | 6,3+10 | 0.80021 | 0.63 | 120 | 0.17021 | 0 | 6.62 | 6.4498 |  |  |  | Nom. capacity LV, МVА | 6,3+10 | 0.025 | 0.82521 | 0.63 | 120 | 0.19521 | 0 | 6.62 | 6.4248
193 | SS 110/35/10 kv Chaplygin | 7,5+6,3 | 8.5927 | 0.63 |  | 7.9627 | 0 | 6.62 | -1.3427 | -1.3427 | closed | 193 | SS 110/35/10 kv Chaplygin | 7,5+6,3 |  | 8.7427 | 0.63 |  | 8.1127 | 0 | 6.62 | -1.4927 | -1.4927 | closed
| Nom. capacity MV, МVА | 7,5+6,3 | 3.1177 | 0 | 0 | 3.1177 | 0 | 6.62 | 3.5023 |  |  |  | Nom. capacity MV, МVА | 7,5+6,3 |  | 3.1177 | 0 | 0 | 3.1177 | 0 | 6.62 | 3.5023
| Nom. capacity LV, МVА | 7,5+6,3 | 5.475 | 0.63 | 120 | 4.845 | 0 | 6.62 | 1.775 |  |  |  | Nom. capacity LV, МVА | 7,5+6,3 | 0.15 | 5.625 | 0.63 | 120 | 4.995 | 0 | 6.62 | 1.625
194 | SS 110/35/10 kv Troekurovo | 10+6,3 | 0.84004 | 10.63 |  | -9.79 | 0 | 6.62 | 16.41 | 6.3169 | opened | 194 | SS 110/35/10 kv Troekurovo | 10+6,3 |  | 0.84004 | 10.63 |  | -9.79 | 0 | 6.62 | 5.78 | 5.78 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.30311 | 10 | 10 | -9.6969 | 0 | 6.62 | 6.3169 |  |  |  | Nom. capacity MV, МVА | 10+6,3 |  | 0.30311 | 10 | 10 | -9.6969 | 0 | 6.62 | 6.3169
| Nom. capacity LV, МVА | 10+6,3 | 0.53694 | 0.63 | 120 | -0.093064 | 0 | 6.62 | 6.7131 |  |  |  | Nom. capacity LV, МVА | 10+6,3 |  | 0.53694 | 0.63 | 120 | -0.093064 | 0 | 6.62 | 6.0831
| Total | 2515.6 | 653.6513 | [8 empty] | 2: Total; 3: 2522.5; MVA 5: 681.1692
| deficit | [8 empty] | -19.392 |  | 2: deficit; min. 12: -28.5644
| proficit | [8 empty] | 660.23 |  | 2: proficit; min. 12: 634.83

## кострома
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total redistributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Sandogora 35/6 kv | 1 | 0.3 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.25 | 0.25 | opened | 1 | Sandogora 35/6 kv | 1 | 0.033 | 0.333 | 0.55 | 120 | -0.217 | 0 | 0.55 | 0.217 | 0.217 | opened
2 | Gridino 35/10 kv | 1.8 | 0.45 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.75 | 0.75 | opened | 2 | Gridino 35/10 kv | 1.8 | 0.72 | 1.17 | 1.2 | 120 | -0.03 | 0 | 1.2 | 0.03 | 0.03 | opened
3 | Novinki 35/10 kv | 1.8 | 0.09 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.35 | 1.35 | opened | 3 | Novinki 35/10 kv | 1.8 | 0.294 | 0.384 | 1.44 | 120 | -1.056 | 0 | 1.44 | 1.056 | 1.056 | opened
4 | Priskokovo 35/10kv | 2.5 | 1.32 | 1.45 | 120 | 1.45 | 0 | 1.45 | 0.13 | 0.13 | opened | 4 | Priskokovo 35/10kv | 2.5 | 0.072 | 1.392 | 1.45 | 120 | -0.058 | 0 | 1.45 | 0.058 | 0.058 | opened
5 | Grigortsevo 110/10 kv | 2.5 | 0.22 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.28 | 1.28 | opened | 5 | Grigortsevo 110/10 kv | 2.5 | 0.025 | 0.245 | 1.5 | 120 | -1.255 | 0 | 1.5 | 1.255 | 1.255 | opened
6 | Klementyevo 110/10 kv | 6.3 | 0.47 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.23 | 3.23 | opened | 6 | Klementyevo 110/10 kv | 6.3 | 3.01 | 3.48 | 3.7 | 120 | -0.22 | 0 | 3.7 | 0.22 | 0.22 | opened
7 | Rudino 35/10 kv | 2.5 | 0.43 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.07 | 1.07 | opened | 7 | Rudino 35/10 kv | 2.5 | 1.053 | 1.483 | 1.5 | 120 | -0.017 | 0 | 1.5 | 0.017 | 0.017 | opened
8 | Stoyankovo 35/10 kv | 1.6 | 0.2 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.52 | 0.52 | opened | 8 | Stoyankovo 35/10 kv | 1.6 | 0.072 | 0.272 | 0.72 | 120 | -0.448 | 0 | 0.72 | 0.448 | 0.448 | opened
9 | Adishchevo 35/10 kv | 4 | 1.15 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.45 | 1.45 | opened | 9 | Adishchevo 35/10 kv | 4 | 0.007 | 1.157 | 2.6 | 120 | -1.443 | 0 | 2.6 | 1.443 | 1.443 | opened
10 | Stolbovo 110/10 kv | 10 | 0.41 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.19 | 4.19 | opened | 10 | Stolbovo 110/10 kv | 10 | 0.01 | 0.42 | 4.6 | 120 | -4.18 | 0 | 4.6 | 4.18 | 4.18 | opened
11 | Raslovo 35/10 kv | 2.5 | 0.73 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.65 | 0.65 | opened | 11 | Raslovo 35/10 kv | 2.5 | 0.24 | 0.97 | 1.38 | 120 | -0.41 | 0 | 1.38 | 0.41 | 0.41 | opened
12 | Andreevskoe 35/10 kv | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | opened | 12 | Andreevskoe 35/10 kv | 1.6 | 0 | 0.18 | 0.93 | 120 | -0.75 | 0 | 0.93 | 0.75 | 0.75 | opened
13 | Popadyino 35/10 kv | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | opened | 13 | Popadyino 35/10 kv | 1.6 | 0 | 0.22 | 0.88 | 120 | -0.66 | 0 | 0.88 | 0.66 | 0.66 | opened
14 | Elegino 110/10 kv | 2.5 | 0.18 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.8 | 0.8 | opened | 14 | Elegino 110/10 kv | 2.5 | 0.07 | 0.25 | 0.98 | 120 | -0.73 | 0 | 0.98 | 0.73 | 0.73 | opened
15 | Krenyovo 35/10 kv | 2.5 | 0.21 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.29 | 2.29 | opened | 15 | Krenyovo 35/10 kv | 2.5 | 0.099 | 0.309 | 2.5 | 24 hours | -2.191 | 0 | 2.5 | 2.191 | 2.191 | opened
16 | Semyonovskoe 35/10 kv | 1.6 | 0.28 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.32 | 1.32 | opened | 16 | Semyonovskoe 35/10 kv | 1.6 | 0.01 | 0.29 | 1.6 | 24 hours | -1.31 | 0 | 1.6 | 1.31 | 1.31 | opened
17 | Khimik 35/10 kv | 3.2 | 0.08 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.36 | 1.36 | opened | 17 | Khimik 35/10 kv | 3.2 | 0 | 0.08 | 1.44 | 120 | -1.36 | 0 | 1.44 | 1.36 | 1.36 | opened
18 | N. Beryozovets 35/10 kv | 2.5 | 0.24 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.19 | 0.19 | opened | 18 | N. Beryozovets 35/10 kv | 2.5 | 0.02 | 0.26 | 0.43 | 120 | -0.17 | 0 | 0.43 | 0.17 | 0.17 | opened
19 | Stepanovo 35/10 kv | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | opened | 19 | Stepanovo 35/10 kv | 4 | 0.085 | 0.405 | 2.32 | 120 | -1.915 | 0 | 2.32 | 1.915 | 1.915 | opened
20 | Gorbachevo 35/10 kv | 1 | 0.01 | 0.78 | 120 | 0.78 | 0 | 0.78 | 0.77 | 0.77 | opened | 20 | Gorbachevo 35/10 kv | 1 | 0.01 | 0.02 | 0.78 | 120 | -0.76 | 0 | 0.78 | 0.76 | 0.76 | opened
21 | Kalinino 35/10 kv | 1 | 0.12 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.44 | 0.44 | opened | 21 | Kalinino 35/10 kv | 1 | 0 | 0.12 | 0.56 | 120 | -0.44 | 0 | 0.56 | 0.44 | 0.44 | opened
22 | Kuzemino 35/10 kv | 1.6 | 0.27 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.33 | 1.33 | opened | 22 | Kuzemino 35/10 kv | 1.6 | 0.01 | 0.28 | 1.6 | 24 hours | -1.32 | 0 | 1.6 | 1.32 | 1.32 | opened
23 | Sovega 35/10 kv | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | opened | 23 | Sovega 35/10 kv | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | opened
24 | Lukovtsino 110/10 kv | 2.5 | 0.12 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.26 | 1.26 | opened | 24 | Lukovtsino 110/10 kv | 2.5 | 0 | 0.12 | 1.38 | 120 | -1.26 | 0 | 1.38 | 1.26 | 1.26 | opened
25 | Fyodorovskoe 110/10 kv | 2.5 | 0.03 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.47 | 1.47 | opened | 25 | Fyodorovskoe 110/10 kv | 2.5 | 0.01 | 0.04 | 1.5 | 120 | -1.46 | 0 | 1.5 | 1.46 | 1.46 | opened
26 | Pankratovo 35/10 kv | 1 | 0.08 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.31 | 0.31 | opened | 26 | Pankratovo 35/10 kv | 1 | 0 | 0.08 | 0.39 | 120 | -0.31 | 0 | 0.39 | 0.31 | 0.31 | opened
27 | Petrovskoe 35/10 kv | 1.6 | 0.23 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.54 | 0.54 | opened | 27 | Petrovskoe 35/10 kv | 1.6 | 0.02 | 0.25 | 0.77 | 120 | -0.52 | 0 | 0.77 | 0.52 | 0.52 | opened
28 | Kotelnikovo 35/10 kv | 1 | 0.1 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.16 | 0.16 | opened | 28 | Kotelnikovo 35/10 kv | 1 | 0.01 | 0.11 | 0.26 | 120 | -0.15 | 0 | 0.26 | 0.15 | 0.15 | opened
29 | Legitovo 35/10 kv | 2.5 | 0.33 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.77 | 0.77 | opened | 29 | Legitovo 35/10 kv | 2.5 | 0 | 0.33 | 1.1 | 120 | -0.77 | 0 | 1.1 | 0.77 | 0.77 | opened
30 | Sloboda 35/10 kv | 2.5 | 0.05 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened | 30 | Sloboda 35/10 kv | 2.5 | 0 | 0.05 | 0.85 | 120 | -0.8 | 0 | 0.85 | 0.8 | 0.8 | opened
31 | Zavrazhye 35/10 kv | 1.6 | 0.18 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.56 | 0.56 | opened | 31 | Zavrazhye 35/10 kv | 1.6 | 0.06 | 0.24 | 0.74 | 120 | -0.5 | 0 | 0.74 | 0.5 | 0.5 | opened
32 | Okulovo 35/10 kv | 1.6 | 0.17 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.73 | 0.73 | opened | 32 | Okulovo 35/10 kv | 1.6 | 0.302 | 0.472 | 0.9 | 120 | -0.428 | 0 | 0.9 | 0.428 | 0.428 | opened
33 | Chernyshevo 35/10 kv | 4 | 0.47 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.33 | 1.33 | opened | 33 | Chernyshevo 35/10 kv | 4 | 0.048 | 0.518 | 1.8 | 120 | -1.282 | 0 | 1.8 | 1.282 | 1.282 | opened
34 | Yakovlevo 110/35/10 kv | 10 | 0.08 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.22 | 5.22 | opened | 34 | Yakovlevo 110/35/10 kv | 10 | 0.025 | 0.105 | 5.3 | 120 | -5.195 | 0 | 5.3 | 5.195 | 5.195 | opened
| Nom. Capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | opened |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | opened
| Nom. Capacity LV, MVA | 10 | 0.08 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.22 |  | opened |  | Nom. Capacity LV, MVA | 10 | 0.03 | 0.11 | 5.3 | 120 | -5.19 | 0 | 5.3 | 5.19 |  | opened
35 | Chermenino 35/10 kv | 1.6 | 0.08 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.78 | 0.78 | opened | 35 | Chermenino 35/10 kv | 1.6 | 0 | 0.08 | 0.86 | 120 | -0.78 | 0 | 0.86 | 0.78 | 0.78 | opened
36 | Nezhitino 35/10 kv | 1 | 0.12 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.42 | 0.42 | opened | 36 | Nezhitino 35/10 kv | 1 | 0.01 | 0.13 | 0.54 | 120 | -0.41 | 0 | 0.54 | 0.41 | 0.41 | opened
37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.37 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.62 | 0.62 | opened | 37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.124 | 0.494 | 0.99 | 120 | -0.496 | 0 | 0.99 | 0.496 | 0.496 | opened
38 | Gusevo 110/10 kv | 2.5 | 0.37 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.26 | 1.26 | opened | 38 | Gusevo 110/10 kv | 2.5 | 0 | 0.37 | 1.63 | 120 | -1.26 | 0 | 1.63 | 1.26 | 1.26 | opened
39 | Medveditsa 35/10 kv | 2.5 | 0.1 | 1.3 | 120 | 1.3 | 0 | 1.3 | 1.2 | 1.2 | opened | 39 | Medveditsa 35/10 kv | 2.5 | 0.02 | 0.12 | 1.3 | 120 | -1.18 | 0 | 1.3 | 1.18 | 1.18 | opened
40 | Novinskoe 110/10 kv | 2.5 | 0.05 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.18 | 1.18 | opened | 40 | Novinskoe 110/10 kv | 2.5 | 0 | 0.05 | 1.23 | 120 | -1.18 | 0 | 1.23 | 1.18 | 1.18 | opened
41 | Filino 35/10 kv | 1.6 | 0.35 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.61 | 0.61 | opened | 41 | Filino 35/10 kv | 1.6 | 0.1 | 0.45 | 0.96 | 120 | -0.51 | 0 | 0.96 | 0.51 | 0.51 | opened
42 | Dyakonovo 110/10 kv | 2.5 | 0.25 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.88 | 0.88 | opened | 42 | Dyakonovo 110/10 kv | 2.5 | 0 | 0.25 | 1.13 | 120 | -0.88 | 0 | 1.13 | 0.88 | 0.88 | opened
43 | Oktyabrskaya 110/10 kv | 2.5 | 0.58 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.92 | 1.92 | opened | 43 | Oktyabrskaya 110/10 kv | 2.5 | 0.01 | 0.59 | 2.5 | 24 hours | -1.91 | 0 | 2.5 | 1.91 | 1.91 | opened
44 | Kuzhbal 35/10 kv | 2.5 | 0.27 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.21 | 1.21 | opened | 44 | Kuzhbal 35/10 kv | 2.5 | 0.01 | 0.28 | 1.48 | 120 | -1.2 | 0 | 1.48 | 1.2 | 1.2 | opened
45 | Nikolo-Poloma 110/10 kv | 2.5 | 0.95 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.18 | 0.18 | opened | 45 | Nikolo-Poloma 110/10 kv | 2.5 | 0.02 | 0.97 | 1.13 | 120 | -0.16 | 0 | 1.13 | 0.16 | 0.16 | opened
46 | Nikola 110/35/10 kv | 6.3 | 0.2 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.95 | 2.95 | opened | 46 | Nikola 110/35/10 kv | 6.3 | 0.038 | 0.238 | 3.15 | 120 | -2.912 | 0 | 3.15 | 2.912 | 2.912 | opened
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  | opened |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  | opened
| Nom. Capacity LV, MVA | 6.3 | 0.2 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.95 |  | opened |  | Nom. Capacity LV, MVA | 6.3 | 0.04 | 0.24 | 3.15 | 120 | -2.91 | 0 | 3.15 | 2.91 |  | opened
47 | Zavetluzhye 35/10 kv | 1.6 | 0.1 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.57 | 0.57 | opened | 47 | Zavetluzhye 35/10 kv | 1.6 | 0 | 0.1 | 0.67 | 120 | -0.57 | 0 | 0.67 | 0.57 | 0.57 | opened
48 | Talitsa 35/10 kv | 1.6 | 0.28 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.32 | 1.32 | opened | 48 | Talitsa 35/10 kv | 1.6 | 0 | 0.28 | 1.6 | 24 hours | -1.32 | 0 | 1.6 | 1.32 | 1.32 | opened
49 | Khoroshaya 35/10 kv | 2.5 | 0.05 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.9 | 1.9 | opened | 49 | Khoroshaya 35/10 kv | 2.5 | 0 | 0.05 | 1.95 | 120 | -1.9 | 0 | 1.95 | 1.9 | 1.9 | opened
50 | Zabegaevo 35/10 kv | 1.6 | 0.08 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.8 | 0.8 | opened | 50 | Zabegaevo 35/10 kv | 1.6 | 0.02 | 0.1 | 0.88 | 120 | -0.78 | 0 | 0.88 | 0.78 | 0.78 | opened
51 | Ilyinskoe 35/10 kv | 1.6 | 0.07 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.83 | 0.83 | opened | 51 | Ilyinskoe 35/10 kv | 1.6 | 0 | 0.07 | 0.9 | 120 | -0.83 | 0 | 0.9 | 0.83 | 0.83 | opened
52 | Luptyug 35/10 kv | 2.5 | 0.13 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.22 | 1.22 | opened | 52 | Luptyug 35/10 kv | 2.5 | 0 | 0.13 | 1.35 | 120 | -1.22 | 0 | 1.35 | 1.22 | 1.22 | opened
53 | Solovetskoe 35/10 kv | 1.6 | 0.08 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.64 | 0.64 | opened | 53 | Solovetskoe 35/10 kv | 1.6 | 0 | 0.08 | 0.72 | 120 | -0.64 | 0 | 0.72 | 0.64 | 0.64 | opened
54 | Gudkovo 110/10 kv | 2.5 | 0.08 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.3 | 1.3 | opened | 54 | Gudkovo 110/10 kv | 2.5 | 0 | 0.08 | 1.38 | 120 | -1.3 | 0 | 1.38 | 1.3 | 1.3 | opened
55 | Shortyug 110/10 kv | 6.3 | 0.38 | 3.47 | 120 | 3.47 | 0 | 3.47 | 3.09 | 3.09 | opened | 55 | Shortyug 110/10 kv | 6.3 | 0.037 | 0.417 | 3.47 | 120 | -3.053 | 0 | 3.47 | 3.053 | 3.053 | opened
56 | Yakshanga 110/10 kv | 6.3 | 1.17 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.3 | 2.3 | opened | 56 | Yakshanga 110/10 kv | 6.3 | 0.035 | 1.205 | 3.47 | 120 | -2.265 | 0 | 3.47 | 2.265 | 2.265 | opened
57 | Katunino 35/10 kv | 2.5 | 0.22 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.91 | 0.91 | opened | 57 | Katunino 35/10 kv | 2.5 | 0 | 0.22 | 1.13 | 120 | -0.91 | 0 | 1.13 | 0.91 | 0.91 | opened
58 | Konyovo 35/10 kv | 1.6 | 0.17 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.71 | 0.71 | opened | 58 | Konyovo 35/10 kv | 1.6 | 0 | 0.17 | 0.88 | 120 | -0.71 | 0 | 0.88 | 0.71 | 0.71 | opened
59 | Shekshema 110/10 kv | 6.3 | 0.28 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.22 | 2.22 | opened | 59 | Shekshema 110/10 kv | 6.3 | 0.03 | 0.31 | 2.5 | 24 hours | -2.19 | 0 | 2.5 | 2.19 | 2.19 | opened
60 | Golovino 35/10 kv | 1 | 0.05 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.07 | 0.07 | opened | 60 | Golovino 35/10 kv | 1 | 0 | 0.05 | 0.12 | 120 | -0.07 | 0 | 0.12 | 0.07 | 0.07 | opened
61 | Matveevskoe 35/10 kv | 1 | 0.02 | 0.69 | 120 | 0.69 | 0 | 0.69 | 0.67 | 0.67 | opened | 61 | Matveevskoe 35/10 kv | 1 | 0 | 0.02 | 0.69 | 120 | -0.67 | 0 | 0.69 | 0.67 | 0.67 | opened
62 | Pishchyovka 35/10 kv | 1 | 0.17 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.28 | 0.28 | opened | 62 | Pishchyovka 35/10 kv | 1 | 0.03 | 0.2 | 0.45 | 120 | -0.25 | 0 | 0.45 | 0.25 | 0.25 | opened
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
63 | Vasilyovo 110/35/10 kv | 10+10 | 2.04 | 0.86 | 120 | 1.18 | 0 | 10.5 | 9.32 | 9.32 | opened | 63 | Vasilyovo 110/35/10 kv | 10+10 | 3.27 | 5.31 | 0.86 | 120 | 4.45 | 0 | 10.5 | 6.05 | 6.05 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.75 | 0 | 120 | 0.75 |  | 10.5 | 9.75 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.75 | 0 | 120 | 0.75 | 0 | 10.5 | 9.75
| Nom. Capacity LV, MVA | 10+10 | 1.29 | 0.86 | 120 | 0.43 |  | 10.5 | 10.07 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 3.272 | 4.562 | 0.86 | 120 | 3.702 | 0 | 10.5 | 6.798
64 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 3.49 | 1.15 | 120 | 2.34 | 0 | 12.18 | 9.84 | 9.84 | opened | 64 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 0.28 | 3.77 | 1.15 | 120 | 2.62 | 0 | 12.18 | 9.56 | 9.56 | opened
| Nom. Capacity MV, MVA | 10+10+1,6 | 1.51 | 0 | 120 | 1.51 |  | 12.18 | 10.67 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 1.51 | 0 | 120 | 1.51 | 0 | 12.18 | 10.67
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.98 | 1.15 | 120 | 0.83 |  | 12.18 | 11.35 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.277 | 2.257 | 1.15 | 120 | 1.107 | 0 | 12.18 | 11.073
65 | Apraksino 35/10 kv | 2,5+2,5 | 1.69 | 0.425 | 120 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 65 | Apraksino 35/10 kv | 2,5+2,5 | 0.21 | 1.9 | 0.425 | 120 | 1.475 | 0 | 2.625 | 1.15 | 1.15 | opened
66 | Borshchino 35/10 kv | 4+4 | 0.66 | 0.62 | 120 | 0.04 | 0 | 4.2 | 4.16 | 4.16 | opened | 66 | Borshchino 35/10 kv | 4+4 | 0.037 | 0.697 | 0.62 | 120 | 0.077 | 0 | 4.2 | 4.123 | 4.123 | opened
67 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened | 67 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | opened
68 | Ilyinskoe 35/10 kv | 2,5+2,5 | 1.93 | 0.55 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | opened | 68 | Ilyinskoe 35/10 kv | 2,5+2,5 | 0.21 | 2.14 | 0.55 | 120 | 1.59 | 0 | 2.625 | 1.035 | 1.035 | opened
69 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.98 | 0.4 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 69 | Kuznetsovo 35/10 kv | 2,5+2,5 | 0.047 | 1.027 | 0.4 | 120 | 0.627 | 0 | 2.625 | 1.998 | 1.998 | opened
70 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.51 | 0.29 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened | 70 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.037 | 0.547 | 0.29 | 120 | 0.257 | 0 | 1.68 | 1.423 | 1.423 | opened
71 | Minskoe 35/10 kv | 2,5+2,5 | 1.13 | 0.43 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 71 | Minskoe 35/10 kv | 2,5+2,5 | 1.494 | 2.624 | 0.43 | 120 | 2.194 | 0 | 2.625 | 0.431 | 0.431 | opened
72 | Miskovo 35/6 kv | 1,8+1,8 | 0.36 | 0.2 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | opened | 72 | Miskovo 35/6 kv | 1,8+1,8 | 0.038 | 0.398 | 0.2 | 120 | 0.198 | 0 | 1.89 | 1.692 | 1.692 | opened
73 | Nikolskoe 35/6 kv | 4+4 | 2.42 | 0.92 | 120 | 1.5 | 0 | 4.2 | 2.7 | 2.7 | opened | 73 | Nikolskoe 35/6 kv | 4+4 | 0.681 | 3.101 | 0.92 | 120 | 2.181 | 0 | 4.2 | 2.019 | 2.019 | opened
74 | Samet 35/6 kv | 1,6+4 | 0.97 | 0 | 0 | 0.97 | 0 | 1.68 | 0.71 | 0.71 | opened | 74 | Samet 35/6 kv | 1,6+4 | 0.494 | 1.464 | 0 | 0 | 1.464 | 0 | 1.68 | 0.216 | 0.216 | opened
75 | Sukhonogovo 35/10 kv | 3,2+4 | 1.96 | 0 | 0 | 1.96 | 0 | 3.36 | 1.4 | 1.4 | opened | 75 | Sukhonogovo 35/10 kv | 3,2+4 | 1.962 | 3.922 | 0 | 0 | 3.922 | 0 | 3.36 | -0.562 | -0.562 | Change of transformers is provided
76 | Sushchevo 35/10 kv | 4+4 | 3.24 | 0.76 | 120 | 2.48 | 0 | 4.2 | 1.72 | 1.72 | opened | 76 | Sushchevo 35/10 kv | 4+4 | 0.188 | 3.428 | 0.76 | 120 | 2.668 | 0 | 4.2 | 1.532 | 1.532 | opened
77 | EMZ 35/6 kv | 1+1 | 0.78 | 0 | 0 | 0.78 | 0 | 1.05 | 0.27 | 0.27 | opened | 77 | EMZ 35/6 kv | 1+1 | 0.006 | 0.786 | 0 | 0 | 0.786 | 0 | 1.05 | 0.264 | 0.264 | opened
78 | Krasnoe 110/35/10 kv | 16+16 | 9.76 | 0 | 0 | 9.76 | 0 | 16.8 | 7.04 | 7.04 | opened | 78 | Krasnoe 110/35/10 kv | 16+16 | 1.647 | 11.407 | 0 | 0 | 11.407 | 0 | 16.8 | 5.393 | 5.393 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.99 | 0 | 120 | 0.99 |  | 16.8 | 15.81 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.99 | 0 | 120 | 0.99 | 0 | 16.8 | 15.81
| Nom. Capacity LV, MVA | 16+16 | 8.77 | 0 | 120 | 8.77 |  | 16.8 | 8.03 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 1.65 | 10.42 | 0 | 120 | 10.42 | 0 | 16.8 | 6.38
79 | Isaevo 35/10 kv | 4+4 | 1.33 | 1.03 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 79 | Isaevo 35/10 kv | 4+4 | 1.658 | 2.988 | 1.03 | 120 | 1.958 | 0 | 4.2 | 2.242 | 2.242 | opened
80 | Chapaevo 35/10 kv | 2,5+2,5 | 0.78 | 0.43 | 120 | 0.35 | 0 | 2.625 | 2.275 | 2.275 | opened | 80 | Chapaevo 35/10 kv | 2,5+2,5 | 0.076 | 0.856 | 0.43 | 120 | 0.426 | 0 | 2.625 | 2.199 | 2.199 | opened
81 | Chernevo 35/10 kv | 1,8+1,8 | 0.23 | 0.15 | 120 | 0.08 | 0 | 1.89 | 1.81 | 1.81 | opened | 81 | Chernevo 35/10 kv | 1,8+1,8 | 0 | 0.23 | 0.15 | 120 | 0.08 | 0 | 1.89 | 1.81 | 1.81 | opened
82 | Nerekhta-1 110/35/10 kv | 25+25 | 17.94 | 2.75 | 120 | 15.19 | 0 | 26.25 | 11.06 | 11.06 | opened | 82 | Nerekhta-1 110/35/10 kv | 25+25 | 1.067 | 19.007 | 2.75 | 120 | 16.257 | 0 | 26.25 | 9.993 | 9.993 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.76 | 0 | 120 | 5.76 |  | 26.25 | 20.49 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.76 | 0 | 120 | 5.76 | 0 | 26.25 | 20.49
| Nom. Capacity LV, MVA | 25+25 | 10.38 | 2.75 | 120 | 7.63 |  | 26.25 | 18.62 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 1.067 | 11.447 | 2.75 | 120 | 8.697 | 0 | 26.25 | 17.553
| Nerekhta-1 110/10 kv | 16+16 | 1.8 | 2.2 | 120 | -0.4 | 0 | 16.8 | 17.2 |  |  |  | Nerekhta-1 110/10 kv | 16+16 | 0 | 1.8 | 2.2 | 120 | -0.4 | 0 | 16.8 | 17.2
83 | Nerekhta-2 110/10/6 kv | 5,6+10 | 2.26 | 1.55 | 120 | 0.71 | 0 | 5.88 | 5.17 | 5.17 | opened | 83 | Nerekhta-2 110/10/6 kv | 5,6+10 | 0.281 | 2.541 | 1.55 | 120 | 0.991 | 0 | 5.88 | 4.889 | 4.889 | opened
84 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.36 | 0.41 | 120 | -0.05 | 0 | 1.68 | 1.73 | 1.73 | opened | 84 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.01 | 0.37 | 0.41 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened
85 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.6 | 0.23 | 120 | 0.37 | 0 | 6.615 | 6.245 | 6.245 | opened | 85 | Tatrskoe 35/10 kv | 1,6+1,6 | 0.01 | 0.61 | 0.23 | 120 | 0.38 | 0 | 6.615 | 6.235 | 6.235 | opened
86 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 4.81 | 0.76 | 120 | 4.05 | 0 | 6.615 | 2.565 | 2.565 | opened | 86 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 0.02 | 4.83 | 0.76 | 120 | 4.07 | 0 | 6.615 | 2.545 | 2.545 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 3.07 | 0 | 120 | 3.07 |  | 6.615 | 3.545 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 3.07 | 0 | 120 | 3.07 | 0 | 6.615 | 3.545
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.74 | 0.76 | 120 | 0.98 |  | 6.615 | 5.635 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.02 | 1.76 | 0.76 | 120 | 1 | 0 | 6.615 | 5.615
87 | Krasnaya Polyana 110/35/10 kv | 10+10 | 4.37 | 1.28 | 120 | 3.09 | 0 | 10.5 | 7.41 | 7.41 | opened | 87 | Krasnaya Polyana 110/35/10 kv | 10+10 | 0.159 | 4.529 | 1.28 | 120 | 3.249 | 0 | 10.5 | 7.251 | 7.251 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.41 | 0 | 120 | 1.41 |  | 10.5 | 9.09 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.41 | 0 | 120 | 1.41 | 0 | 10.5 | 9.09
| Nom. Capacity LV, MVA | 10+10 | 2.96 | 1.28 | 120 | 1.68 |  | 10.5 | 8.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.127 | 3.087 | 1.28 | 120 | 1.807 | 0 | 10.5 | 8.693
88 | Igodovo 35/10 kv | 1,6+1,6 | 0.34 | 0.25 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened | 88 | Igodovo 35/10 kv | 1,6+1,6 | 0.03 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened
89 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.82 | 0.56 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | opened | 89 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.02 | 0.84 | 0.56 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | opened
90 | Ostrovskoe 35/10 kv | 2,5+2,5 | 1.13 | 0.52 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | opened | 90 | Ostrovskoe 35/10 kv | 2,5+2,5 | 0.06 | 1.19 | 0.52 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | opened
91 | Sudislavl 110/10 kv | 10+10 | 6 | 1.8 | 120 | 4.2 | 0 | 10.5 | 6.3 | 6.3 | opened | 91 | Sudislavl 110/10 kv | 10+10 | 0.586 | 6.586 | 1.8 | 120 | 4.786 | 0 | 10.5 | 5.714 | 5.714 | opened
92 | Voronye 35/10 kv | 1,8+1,8 | 0.51 | 0.4 | 120 | 0.11 | 0 | 1.89 | 1.78 | 1.78 | opened | 92 | Voronye 35/10 kv | 1,8+1,8 | 0.03 | 0.54 | 0.4 | 120 | 0.14 | 0 | 1.89 | 1.75 | 1.75 | opened
93 | Susanino 110/35/10 kv | 10+10 | 5.9 | 1.89 | 120 | 4.01 | 0 | 10.5 | 6.49 | 6.49 | opened | 93 | Susanino 110/35/10 kv | 10+10 | 0.47 | 6.37 | 1.89 | 120 | 4.48 | 0 | 10.5 | 6.02 | 6.02 | opened
| Nom. Capacity MV, MVA | 10+10 | 2.96 | 0 | 120 | 2.96 |  | 10.5 | 7.54 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 2.96 | 0 | 120 | 2.96 | 0 | 10.5 | 7.54
| Nom. Capacity LV, MVA | 10+10 | 2.94 | 1.89 | 120 | 1.05 |  | 10.5 | 9.45 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.47 | 3.41 | 1.89 | 120 | 1.52 | 0 | 10.5 | 8.98
94 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.16 | 0.07 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | открыт | 94 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.01 | 0.17 | 0.07 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
95 | Airport 110/35/6 kv | 16+16 | 5.95 | 2.88 | 120 | 3.07 | 0 | 16.8 | 13.73 | 13.73 | opened | 95 | Airport 110/35/6 kv | 16+16 | 4.167 | 10.117 | 2.88 | 120 | 7.237 | 0 | 16.8 | 9.563 | 9.56 | opened
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 |  | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.95 | 2.88 | 120 | 3.07 |  | 16.8 | 13.73 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 4.17 | 10.12 | 2.88 | 120 | 7.24 | 0 | 16.8 | 9.56
96 | Vostochnaya-2 110/35/10 kv | 25+25 | 33.66 | 0.02 | 120 | 33.64 | 0 | 26.25 | -7.39 | -7.39 | Load is transferred to new SS Davydovskaya | 96 | Vostochnaya-2 110/35/10 kv | 25+25 | 5.846 | 39.506 | 0.02 | 120 | 39.486 | 0 | 26.25 | -13.236 | -13.236 | Load is transferred to new SS Davydovskaya
| Nom. Capacity MV, MVA | 25+25 | 21.51 | 0 | 120 | 21.51 |  | 26.25 | 4.74 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 21.51 | 0 | 120 | 21.51 | 0 | 26.25 | 4.74
| Nom. Capacity LV, MVA | 25+25 | 12.15 | 0.02 | 120 | 12.13 |  | 26.25 | 14.12 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 5.85 | 18 | 0.02 | 120 | 17.98 | 0 | 26.25 | 8.27
97 | Kostroma-3 110/35/10 kv | 10+16 | 8.81 | 0 | 0 | 8.81 | 0 | 10.5 | 1.69 | 1.69 | opened | 97 | Kostroma-3 110/35/10 kv | 10+16 | 1.117 | 9.927 | 0 | 0 | 9.927 | 0 | 10.5 | 0.573 | 0.573 | opened
| Nom. Capacity MV, MVA | 10+16 | 1.76 | 0 | 120 | 1.76 |  | 10.5 | 8.74 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 1.76 | 0 | 120 | 1.76 | 0 | 10.5 | 8.74
| Nom. Capacity LV, MVA | 10+16 | 7.05 | 0 | 120 | 7.05 |  | 10.5 | 3.45 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 1.12 | 8.17 | 0 | 120 | 8.17 | 0 | 10.5 | 2.33
98 | Yuzhnaya 110/35/10 kv | 25+25 | 15.12 | 0 | 0 | 15.12 | 0 | 26.25 | 11.13 | 11.13 | opened | 98 | Yuzhnaya 110/35/10 kv | 25+25 | 6.95 | 22.07 | 0 | 0 | 22.07 | 0 | 26.25 | 4.18 | 4.18 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.55 | 0 | 120 | 5.55 |  | 26.25 | 20.7 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 5.55 | 0 | 120 | 5.55 | 0 | 26.25 | 20.7
| Nom. Capacity LV, MVA | 25+25 | 9.57 | 0 | 120 | 9.57 |  | 26.25 | 16.68 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 6.95 | 16.52 | 0 | 120 | 16.52 | 0 | 26.25 | 9.73
99 | Kostroma-1 110/6 kv | 10+10 | 10.08 | 0 | 0 | 10.08 | 0 | 10.5 | 0.42 | 0.42 | opened | 99 | Kostroma-1 110/6 kv | 10+10 | 1.935 | 12.015 | 0 | 0 | 12.015 | 0 | 10.5 | -1.515 | -1.515 | Change of transformers is provided
100 | Severnaya 110/6 kv | 20+25 | 17.9 | 0 | 0 | 17.9 | 0 | 21 | 3.1 | 3.1 | opened | 100 | Severnaya 110/6 kv | 20+25 | 6.82 | 24.72 | 0 | 0 | 24.72 | 0 | 21 | -3.72 | -3.72 | Change of transformers is provided
101 | Strommashina 110/6 kv | 40+40 | 8.81 | 0 | 0 | 8.81 | 0 | 42 | 33.19 | 33.19 | opened | 101 | Strommashina 110/6 kv | 40+40 | 8.827 | 17.637 | 0 | 0 | 17.637 | 0 | 42 | 24.363 | 24.363 | opened
102 | Tsentralnaya 110/10/6 kv | 25+25 | 15.63 | 0 | 0 | 15.63 | 0 | 26.25 | 10.62 | 10.62 | opened | 102 | Tsentralnaya 110/10/6 kv | 25+25 | 14.673 | 30.303 | 0 | 0 | 30.303 | 0 | 26.25 | -4.053 | -4.053 | Change of transformers is provided
103 | Baydarka 35/6 kv | 6,3+6,3 | 2.26 | 1.2 | 120 | 1.06 | 0 | 6.615 | 5.555 | 5.555 | opened | 103 | Baydarka 35/6 kv | 6,3+6,3 | 1 | 3.26 | 1.2 | 120 | 2.06 | 0 | 6.615 | 4.555 | 4.555 | opened
104 | Volzhskaya 35/6 kv | 4+4 | 1 | 0.76 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened | 104 | Volzhskaya 35/6 kv | 4+4 | 1.425 | 2.425 | 0.76 | 120 | 1.665 | 0 | 4.2 | 2.535 | 2.535
105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 19.44 | 0 | 0 | 19.44 | 0 | 17.115 | -2.325 | -2.325 | Transition to 110 kv with chage of transformers is provided | 105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 2.381 | 21.821 | 0 | 0 | 21.821 | 0 | 17.115 | -4.706 | -4.706 | Transition to 110 kv with chage of transformers is provided
106 | Karavaevo 35/10 kv | 6,3+6,3 | 3.92 | 0 | 0 | 3.92 | 0 | 6.615 | 2.695 | 2.695 | opened | 106 | Karavaevo 35/10 kv | 6,3+6,3 | 1.327 | 5.247 | 0 | 0 | 5.247 | 0 | 6.615 | 1.368 | 1.368 | opened
107 | Korkino 35/10 kv | 2,5+2,5 | 2.13 | 0.85 | 120 | 1.28 | 0 | 2.625 | 1.345 | 1.345 | opened | 107 | Korkino 35/10 kv | 2,5+2,5 | 0.286 | 2.416 | 0.85 | 120 | 1.566 | 0 | 2.625 | 1.059 | 1.059 | opened
108 | KPD 110/35/10 kv | 16+16 | 4.64 | 1.44 | 120 | 3.2 | 0 | 16.8 | 13.6 | 13.6 | opened | 108 | KPD 110/35/10 kv | 16+16 | 0 | 4.64 | 1.44 | 120 | 3.2 | 0 | 16.8 | 13.6 | 13.6 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.39 | 0 | 120 | 0.39 |  | 16.8 | 16.41 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.39 | 0 | 120 | 0.39 | 0 | 16.8 | 16.41
| Nom. Capacity LV, MVA | 16+16 | 4.25 | 1.44 | 120 | 2.81 |  | 16.8 | 13.99 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 0 | 4.25 | 1.44 | 120 | 2.81 | 0 | 16.8 | 13.99
109 | SM State district power station 110/35/6 kv | 10+16 | 6.75 | 0 | 0 | 6.75 | 0 | 10.5 | 3.75 | 3.75 | opened | 109 | SM State district power station 110/35/6 kv | 10+16 | 4.034 | 10.784 | 0 | 0 | 10.784 | 0 | 10.5 | -0.284 | -0.284 | Change of transformers is provided
| Nom. Capacity MV, MVA | 10+16 | 0.71 | 0 | 120 | 0.71 |  | 10.5 | 9.79 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.71 | 0 | 120 | 0.71 | 0 | 10.5 | 9.79
| Nom. Capacity LV, MVA | 10+16 | 6.04 | 0 | 120 | 6.04 |  | 10.5 | 4.46 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 4.03 | 10.07 | 0 | 120 | 10.07 | 0 | 10.5 | 0.43
110 | Sidorovskoe 35/6 kv | 2,5+4 | 1.18 | 0.82 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.071 | 1.251 | 0.82 | 120 | 0.431 | 0 | 2.625 | 2.194 | 2.194 | opened
111 | Buy (r) 110/35/10 kv | 4+10 | 0.9 | 0 | 0 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened | 111 | Buy (r) 110/35/10 kv | 4+10 | 12.611 | 13.511 | 0 | 0 | 13.511 | 0 | 4.2 | -9.311 | -9.311 | Change of transformers is provided
| Nom. Capacity MV, MVA | 4+10 | 0.9 | 0 | 120 | 0.9 |  | 4.2 | 3.3 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 12.61 | 13.51 | 0 | 120 | 13.51 | 0 | 4.2 | -9.31
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 120 | 0 |  | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2
112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 5.52 | 1.2 | 120 | 4.32 | 0 | 6.615 | 2.295 | 2.295 | opened | 112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 1.091 | 6.611 | 1.2 | 120 | 5.411 | 0 | 6.615 | 1.204 | 1.204 | opened
113 | Zapadnaya 110/10 kv | 10+10 | 3.6 | 2.63 | 120 | 0.97 | 0 | 10.5 | 9.53 | 9.53 | opened | 113 | Zapadnaya 110/10 kv | 10+10 | 0.01 | 3.61 | 2.63 | 120 | 0.98 | 0 | 10.5 | 9.52 | 9.52 | opened
114 | Dor 35/10 kv | 1,6+1,6 | 0.52 | 0.06 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened | 114 | Dor 35/10 kv | 1,6+1,6 | 0.03 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.68 | 1.19 | 1.19 | opened
115 | Dyakonovo 35/10 kv | 1+1 | 0.24 | 0.26 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | opened | 115 | Dyakonovo 35/10 kv | 1+1 | 0 | 0.24 | 0.26 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | opened
116 | Likurga 35/10 kv | 1,8+1,6 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 116 | Likurga 35/10 kv | 1,8+1,6 | 0.01 | 0.13 | 0.12 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
117 | Shushkodom 35/10 kv | 1+1 | 0.28 | 0.06 | 120 | 0.22 | 0 | 1.05 | 0.83 | 0.83 | opened | 117 | Shushkodom 35/10 kv | 1+1 | 0.02 | 0.3 | 0.06 | 120 | 0.24 | 0 | 1.05 | 0.81 | 0.81 | opened
118 | Novaya 110/35/10 kv | 6,3+6,3 | 1.54 | 0.64 | 120 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 118 | Novaya 110/35/10 kv | 6,3+6,3 | 0.707 | 2.247 | 0.64 | 120 | 1.607 | 0 | 6.615 | 5.008 | 5.008 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.34 | 0 | 120 | 0.34 | 0 | 6.615 | 6.275 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.34 | 0 | 120 | 0.34 | 0 | 6.615 | 6.275
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.2 | 0.64 | 120 | 0.56 | 0 | 6.615 | 6.055 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.71 | 1.91 | 0.64 | 120 | 1.27 | 0 | 6.615 | 5.345
119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 1.84 | 0 | 0 | 1.84 | 0 | 6.615 | 4.775 | 4.775 | opened | 119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 0.14 | 1.98 | 0 | 0 | 1.98 | 0 | 6.615 | 4.635 | 4.635 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.2 | 0 | 120 | 1.2 |  | 6.615 | 5.415 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.2 | 0 | 120 | 1.2 | 0 | 6.615 | 5.415
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.64 | 0 | 120 | 0.64 |  | 6.615 | 5.975 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.14 | 0.78 | 0 | 120 | 0.78 | 0 | 6.615 | 5.835
120 | Loparevo 110/10 kv | 2,5+2,5 | 0.36 | 0.55 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened | 120 | Loparevo 110/10 kv | 2,5+2,5 | 0.237 | 0.597 | 0.55 | 120 | 0.047 | 0 | 2.625 | 2.578 | 2.578 | opened
121 | Galichskaya poultry farm 35/10 kv | 4+4 | 1 | 1.28 | 120 | -0.28 | 0 | 4.2 | 4.48 | 4.48 | opened | 121 | Galichskaya poultry farm 35/10 kv | 4+4 | 0.101 | 1.101 | 1.28 | 120 | -0.179 | 0 | 4.2 | 4.379 | 4.379 | opened
122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.12 | 0.22 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.01 | 0.13 | 0.22 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | opened
123 | Levkovo 35/10 kv | 1,6+1,6 | 0.4 | 0.74 | 120 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | opened | 123 | Levkovo 35/10 kv | 1,6+1,6 | 0 | 0.4 | 0.74 | 120 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | opened
124 | Pronino 35/10 kv | 4+2,5 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 124 | Pronino 35/10 kv | 4+2,5 | 0 | 0.36 | 0.2 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.16 | 0.13 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened | 125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.296 | 0.456 | 0.13 | 120 | 0.326 | 0 | 2.625 | 2.299 | 2.299 | opened
126 | Soligalich 110/35/10 kv | 10+10 | 3.7 | 1.7 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | opened | 126 | Soligalich 110/35/10 kv | 10+10 | 0.621 | 4.321 | 1.7 | 120 | 2.621 | 0 | 10.5 | 7.879 | 7.879 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.7 | 0 | 120 | 0.7 |  | 10.5 | 9.8 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.7 | 0 | 120 | 0.7 | 0 | 10.5 | 9.8
| Nom. Capacity LV, MVA | 10+10 | 3 | 1.7 | 120 | 1.3 |  | 10.5 | 9.2 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.62 | 3.62 | 1.7 | 120 | 1.92 | 0 | 10.5 | 8.58
127 | Pochinok 35/10 kv | 1,6+2,5 | 0.48 | 0.34 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 127 | Pochinok 35/10 kv | 1,6+2,5 | 0.01 | 0.49 | 0.34 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 1.6 | 2.06 | 120 | -0.46 | 0 | 6.615 | 7.075 | 6.615 | opened | 128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 0.465 | 2.065 | 2.06 | 120 | 0.005 | 0 | 6.615 | 6.61 | 6.605 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0 | 120 | 0 |  | 6.615 | 6.615 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0 | 0 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.6 | 2.06 | 120 | -0.46 |  | 6.615 | 7.075 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.47 | 2.07 | 2.06 | 120 | 0.01 | 0 | 6.615 | 6.605
129 | Suday 35/10 kv | 1,6+1,6 | 0.64 | 0.49 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 129 | Suday 35/10 kv | 1,6+1,6 | 0.03 | 0.67 | 0.49 | 120 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | opened
130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 4.31 | 0.38 | 120 | 3.93 | 0 | 6.615 | 2.685 | 2.685 | opened | 130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 0.157 | 4.467 | 0.38 | 120 | 4.087 | 0 | 6.615 | 2.528 | 2.528 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 2.94 | 0 | 120 | 2.94 |  | 6.615 | 3.675 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 2.94 | 0 | 120 | 2.94 | 0 | 6.615 | 3.675
| Nom. Capacity LV, MVA | 6,3+16 | 1.37 | 0.38 | 120 | 0.99 |  | 6.615 | 5.625 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.16 | 1.53 | 0.38 | 120 | 1.15 | 0 | 6.615 | 5.465
131 | Palkino 35/10 kv | 2,5+4 | 0.66 | 0.45 | 120 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 131 | Palkino 35/10 kv | 2,5+4 | 0.059 | 0.719 | 0.45 | 120 | 0.269 | 0 | 2.625 | 2.356 | 2.356 | opened
132 | Slovinka 35/10 kv | 1,6+1,6 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened | 132 | Slovinka 35/10 kv | 1,6+1,6 | 0 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened
133 | Kady 110/35/10 kv | 10+10 | 2.73 | 0.69 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | opened | 133 | Kady 110/35/10 kv | 10+10 | 0.356 | 3.086 | 0.69 | 120 | 2.396 | 0 | 10.5 | 8.104 | 8.104 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.83 | 0 | 120 | 0.83 |  | 10.5 | 9.67 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.83 | 0 | 120 | 0.83 | 0 | 10.5 | 9.67
| Nom. Capacity LV, MVA | 10+10 | 1.9 | 0.69 | 120 | 1.21 |  | 10.5 | 9.29 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.36 | 2.26 | 0.69 | 120 | 1.57 | 0 | 10.5 | 8.93
134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.1 | 0.1 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.02 | 0.12 | 0.1 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened
135 | Ilyinskoe 110/35/10 kv | 10+10 | 4.13 | 0.04 | 120 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened | 135 | Ilyinskoe 110/35/10 kv | 10+10 | 0 | 4.13 | 0.04 | 120 | 4.09 | 0 | 10.5 | 6.41 | 6.41 | opened
| Nom. Capacity MV, MVA | 10+10 | 4.06 | 0 | 120 | 4.06 |  | 10.5 | 6.44 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 4.06 | 0 | 120 | 4.06 | 0 | 10.5 | 6.44
| Nom. Capacity LV, MVA | 10+10 | 0.07 | 0.04 | 120 | 0.03 |  | 10.5 | 10.47 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0 | 0.07 | 0.04 | 120 | 0.03 | 0 | 10.5 | 10.47
136 | Kologriv 35/10 kv | 4+4 | 1.42 | 1.42 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 136 | Kologriv 35/10 kv | 4+4 | 0.183 | 1.603 | 1.42 | 120 | 0.183 | 0 | 4.2 | 4.017 | 4.017 | opened
137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.2 | 0.08 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened | 137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.006 | 0.206 | 0.08 | 120 | 0.126 | 0 | 1.68 | 1.554 | 1.554 | opened
138 | Makaryev-1 110/35/10 kv | 10+10 | 1.65 | 0.8 | 120 | 0.85 | 0 | 10.5 | 9.65 | 8.85 | opened | 138 | Makaryev-1 110/35/10 kv | 10+10 | 0.106 | 1.756 | 0.8 | 120 | 0.956 | 0 | 10.5 | 9.544 | 8.85 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.65 | 0 | 120 | 1.65 |  | 10.5 | 8.85 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.65 | 0 | 120 | 1.65 | 0 | 10.5 | 8.85
| Nom. Capacity MV, MVA | 10+10 | 0 | 0.8 | 120 | -0.8 |  | 10.5 | 11.3 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.11 | 0.11 | 0.8 | 120 | -0.69 | 0 | 10.5 | 11.19
139 | Gorchukha 35/10 kv | 2,5+2,5 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened | 139 | Gorchukha 35/10 kv | 2,5+2,5 | 0 | 0.75 | 0 | 0 | 0.75 | 0 | 2.625 | 1.875 | 1.875 | opened
140 | Makaryev-2 35/10 kv | 4+4 | 1.5 | 1.58 | 120 | -0.08 | 0 | 4.2 | 4.28 | 4.28 | opened | 140 | Makaryev-2 35/10 kv | 4+4 | 0.375 | 1.875 | 1.58 | 120 | 0.295 | 0 | 4.2 | 3.905 | 3.905 | opened
141 | Timoshino 35/10 kv | 1+1 | 0.12 | 0 | 0 | 0.12 | 0 | 1.05 | 0.93 | 0.93 | opened | 141 | Timoshino 35/10 kv | 1+1 | 0.084 | 0.204 | 0 | 0 | 0.204 | 0 | 1.05 | 0.846 | 0.846 | opened
142 | Unzha 35/10 kv | 1+1,6 | 0.25 | 0.1 | 120 | 0.15 | 0 | 1.05 | 0.9 | 0.9 | opened | 142 | Unzha 35/10 kv | 1+1,6 | 0.02 | 0.27 | 0.1 | 120 | 0.17 | 0 | 1.05 | 0.88 | 0.88 | opened
143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.15 | 0.32 | 120 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | opened | 143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.01 | 0.16 | 0.32 | 120 | -0.16 | 0 | 1.68 | 1.84 | 1.84 | opened
144 | BKhZ 110/6 kv | 25+25 | 0.72 | 0 | 0 | 0.72 | 0 | 26.25 | 25.53 | 25.53 | opened | 144 | BKhZ 110/6 kv | 25+25 | 0.163 | 0.883 | 0 | 0 | 0.883 | 0 | 26.25 | 25.367 | 25.367 | opened
145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.22 | 0.15 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | opened | 145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.02 | 0.24 | 0.15 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
146 | Georgievskoe 35/10 kv | 2,5+2,5 | 1.62 | 0.82 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 146 | Georgievskoe 35/10 kv | 2,5+2,5 | 0.52 | 2.14 | 0.82 | 120 | 1.32 | 0 | 2.625 | 1.305 | 1.305 | opened
147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 7.36 | 3.6 | 120 | 3.76 | 0 | 48.615 | 44.855 | 44.855 | opened | 147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 0.616 | 7.976 | 3.6 | 120 | 4.376 | 0 | 48.615 | 44.239 | 44.239 | opened
| Nom. Capacity MV, MVA | 40+40+6,3 | 1.19 | 0 | 120 | 1.19 |  | 48.615 | 47.425 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 1.19 | 0 | 120 | 1.19 | 0 | 48.615 | 47.425
| Nom. Capacity LV, MVA | 40+40+6,3 | 6.17 | 3.6 | 120 | 2.57 |  | 48.615 | 46.045 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.62 | 6.79 | 3.6 | 120 | 3.19 | 0 | 48.615 | 45.425
148 | Vozherovo 35/10 kv | 1,6+1,6 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 148 | Vozherovo 35/10 kv | 1,6+1,6 | 0 | 0.12 | 0.12 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
149 | Matveevo 35/10 kv | 1,8+4 | 0.38 | 0.42 | 120 | -0.04 | 0 | 1.89 | 1.93 | 1.93 | opened | 149 | Matveevo 35/10 kv | 1,8+4 | 0 | 0.38 | 0.42 | 120 | -0.04 | 0 | 1.89 | 1.93 | 1.93 | opened
150 | Parfenyevo 35/10 kv | 4+4 | 2.02 | 1.89 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | opened | 150 | Parfenyevo 35/10 kv | 4+4 | 0.642 | 2.662 | 1.89 | 120 | 0.772 | 0 | 4.2 | 3.428 | 3.428 | opened
151 | Vokhma 110/35/10 kv | 6,3+16 | 4.85 | 0 | 0 | 4.85 | 0 | 6.615 | 1.765 | 1.765 | opened | 151 | Vokhma 110/35/10 kv | 6,3+16 | 0.439 | 5.289 | 0 | 0 | 5.289 | 0 | 6.615 | 1.326 | 1.326 | opened
| Nom. Capacity MV, MVA | 6,3+8 | 2.3 | 0 | 120 | 2.3 |  | 6.615 | 4.315 |  |  |  | Nom. Capacity MV, MVA | 6,3+8 | 0 | 2.3 | 0 | 120 | 2.3 | 0 | 6.615 | 4.315
| Nom. Capacity LV, MVA | 6,3+8 | 2.55 | 0 | 120 | 2.55 |  | 6.615 | 4.065 |  |  |  | Nom. Capacity LV, MVA | 6,3+8 | 0.44 | 2.99 | 0 | 120 | 2.99 | 0 | 6.615 | 3.625
152 | Lapshino 35/10 kv | 2,5+2,5 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened | 152 | Lapshino 35/10 kv | 2,5+2,5 | 0 | 0.13 | 0.05 | 120 | 0.08 | 0 | 2.625 | 2.545 | 2.545 | opened
153 | Spass 35/10 kv | 1,6+2,5 | 0.4 | 0.35 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | opened | 153 | Spass 35/10 kv | 1,6+2,5 | 0.01 | 0.41 | 0.35 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened
154 | Bogovarovo 35/10 kv | 2,5+4 | 1.47 | 1 | 120 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | opened | 154 | Bogovarovo 35/10 kv | 2,5+4 | 0.12 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
155 | Pavino 110/35/10 kv | 10+6,3 | 1.96 | 0 | 0 | 1.96 | 0 | 6.615 | 4.655 | 4.655 | opened | 155 | Pavino 110/35/10 kv | 10+6,3 | 0.04 | 2 | 0 | 0 | 2 | 0 | 6.615 | 4.615 | 4.615 | opened
| Nom. Capacity MV, MVA | 10+6,3 | 0.36 | 0 | 120 | 0.36 |  | 6.615 | 6.255 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 6.615 | 6.255
| Nom. Capacity LV, MVA | 10+6,3 | 1.6 | 0 | 120 | 1.6 |  | 6.615 | 5.015 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.04 | 1.64 | 0 | 120 | 1.64 | 0 | 6.615 | 4.975
156 | Ledengskaya 35/10 kv | 1,6+4 | 0.07 | 0.07 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 156 | Ledengskaya 35/10 kv | 1,6+4 | 0 | 0.07 | 0.07 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 2.09 | 0 | 0 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened | 157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 0.16 | 2.25 | 0 | 0 | 2.25 | 0 | 6.615 | 4.365 | 4.365 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 120 | 0.12 |  | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 120 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.97 | 0 | 120 | 1.97 |  | 6.615 | 4.645 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.16 | 2.13 | 0 | 120 | 2.13 | 0 | 6.615 | 4.485
158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 1.55 | 0.75 | 120 | 0.8 | 0 | 4.2 | 3.4 | 3.4 | opened | 158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 0.101 | 1.651 | 0.75 | 120 | 0.901 | 0 | 4.2 | 3.299 | 3.299 | opened
| Nom. Capacity MV, MVA | 10+4 | 0.55 | 0 | 120 | 0.55 |  | 4.2 | 3.65 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.55 | 0 | 120 | 0.55 | 0 | 4.2 | 3.65
| Nom. Capacity LV, MVA | 10+4 | 1 | 0.75 | 120 | 0.25 |  | 4.2 | 3.95 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.101 | 1.101 | 0.75 | 120 | 0.351 | 0 | 4.2 | 3.849
159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.27 | 0.2 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | opened | 159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.02 | 0.29 | 0.2 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
160 | Sharya (r) 110/35/6 kv | 20+25 | 14.09 | 2 | 120 | 12.09 | 0 | 21 | 8.91 | 8.91 | opened | 160 | Sharya (r) 110/35/6 kv | 20+25 | 0.381 | 14.471 | 2 | 120 | 12.471 | 0 | 21 | 8.529 | 8.529 | opened
| Nom. Capacity MV, MVA | 20+25 | 8.24 | 0 | 120 | 8.24 |  | 21 | 12.76 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 8.24 | 0 | 120 | 8.24 | 0 | 21 | 12.76
| Nom. Capacity LV, MVA | 20+25 | 5.85 | 2 | 120 | 3.85 |  | 21 | 17.15 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.38 | 6.23 | 2 | 120 | 4.23 | 0 | 21 | 16.77
161 | Industrial hub 110/6/6 kv | 25+25 | 3.15 | 2.5 | 120 | 0.65 | 0 | 26.25 | 25.6 | 25.6 | opened | 161 | Industrial hub 110/6/6 kv | 25+25 | 0.764 | 3.914 | 2.5 | 120 | 1.414 | 0 | 26.25 | 24.836 | 24.836 | opened
162 | Krivyachka 35/10 kv | 1,6+1 | 0.47 | 0.57 | 120 | -0.1 | 0 | 1.05 | 1.15 | 1.15 | opened | 162 | Krivyachka 35/10 kv | 1,6+1 | 0.03 | 0.5 | 0.57 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | opened
163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.02 | 0.82 | 0 | 0 | 0.82 | 0 | 1.68 | 0.86 | 0.86 | opened
164 | Tsentralnaya 35/6 kv | 10+10 | 8.1 | 3 | 120 | 5.1 | 0 | 10.5 | 5.4 | 5.4 | opened | 164 | Tsentralnaya 35/6 kv | 10+10 | 2.478 | 10.578 | 3 | 120 | 7.578 | 0 | 10.5 | 2.922 | 2.922 | opened
| Total over Kostromaenergo | 1656 | 349.09 | [8 empty] | 2: Total over Kostromaenergo; 3: 1656; 5: 456.125
| deficit | [8 empty] | -9.715 | 2 SS-deficit | 2: deficit; Мин. 12: -37.387; Мин. 13: 8 SS - deficit
| proficit | [8 empty] | 553.04 | 162-proficit | 2: proficit; Мин. 12: 474.235; Мин. 13: 156 SS - proficit

## ярославль
Table 1
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected dificit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, МVА | Expected load at main substation, MVA | Total re-distributed capacity in future including fulfillment of measures of technical specifications or other measures relating to reconstruction of network, investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit / proficit of main substation, MVA
|  |  |  | МVА | Мin. | [11 empty] | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 0.27 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.53 | 0.53 | opened | 1 | SS 35/10 Matveevo | 1.6 |  | 0.27 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.53 | 0.53 | opened
2 | SS 35/10 Mikhailovskoe | 6.3 | 1.43 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.19 | 5.19 | opened | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.433 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.187 | 5.187 | opened
3 | SS 35/10 Shirinye | 2.5 | 1.79 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.31 | 0.31 | opened | 3 | SS 35/10 Shirinye | 2.5 | 0.008 | 1.798 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 0.302 | 0.302 | opened
4 | SS 110/10 Pokrov | 2.5 | 0.3 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1 | 1 | opened | 4 | SS 110/10 Pokrov | 2.5 |  | 0.3 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1 | 1 | opened
5 | SS 35/10 Obnora | 1.6 | 0.18 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.92 | 0.92 | opened | 5 | SS 35/10 Obnora | 1.6 |  | 0.18 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.92 | 0.92 | opened
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 8.67 |  |  | 8.67 | 0 | 10.5 | 1.83 | 1.83 | opened | 6 | SS 110/35/10 Abbakumtsevo | 25+25 | 5.8384 | 8.7584 |  |  | 8.7584 | 0 | 10.5 | 1.7415 | 1.7415 | opened
| Nom. capacity MV, МVА | 10+10 | 5.75 |  |  | 5.75 | 0 | 10.5 | 4.75 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.8244 | 5.8244 |  |  | 5.8244 | 0 | 10.5 | 4.6756
| Nom. capacity LV, МVА | 10+10 | 2.92 |  |  | 2.92 | 0 | 10.5 | 7.58 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.014 | 2.934 |  |  | 2.934 | 0 | 10.5 | 7.566
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.15 |  |  | 1.15 | 0 | 1.68 | 0.53 | 0.53 | opened | 7 | SS 35/10 Ananyino | 1,6+1,6 |  | 1.15 |  |  | 1.15 | 0 | 1.68 | 0.53 | 0.53 | opened
8 | SS 110/10/10 Bragino | 40+40 | 34.1 | 2.38 | 120 | 31.72 | 0 | 42 | 10.28 | 10.28 | opened | 8 | SS 110/10/10 Bragino | 40+40 | 4.9967 | 39.0967 | 2.38 | 120 | 36.7167 | 0 | 42 | 5.2833 | 5.2833 | opened
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.91 | 0.1 | 120 | 0.81 | 0 | 4.2 | 3.39 | 3.39 | opened | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.0855 | 0.9955 | 0.1 | 120 | 0.8955 | 0 | 4.2 | 3.3045 | 3.3045 | opened
10 | SS 35/10 Vatolino | 2,5+4,0 | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -0.85 | closed | 10 | SS 35/10 Vatolino | 2,5+4,0 |  | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -0.85 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 5.37 |  |  | 5.37 | 0 | 6.62 | 1.25 | 1.25 | opened | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.42405 | 5.7941 |  |  | 5.7941 | 0 | 6.62 | 0.82595 | 0.82595 | opened
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 2 |  |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.1579 | 2.1579 |  |  | 2.1579 | 0 | 4.2 | 2.0421 | 2.0421 | opened
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.78 |  |  | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.06 | 0.84 |  |  | 0.84 | 0 | 1.68 | 0.84 | 0.84 | opened
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.74 |  |  | 1.74 | 0 | 4.2 | 2.46 | 2.46 | opened | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 0.8179 | 2.5579 |  |  | 2.5579 | 0 | 4.2 | 1.6421 | 1.6421 | opened
15 | SS 35/10 Volna | 2,5+2,5 | 3.06 |  |  | 3.06 | 0 | 2.63 | -0.43 | -0.43 | closed | 15 | SS 35/10 Volna | 2,5+2,5 | 0.2 | 3.26 |  |  | 3.26 | 0 | 2.63 | -0.63 | -0.63 | closed
16 | SS 35/10 Vyatskoe | 4,0+4,0 | 1.92 | 0.17 | 120 | 1.75 | 0 | 4.2 | 2.45 | 2.45 | opened | 16 | SS 35/10 Vyatskoe | 4,0+4,0 | 0.033 | 1.953 | 0.17 | 120 | 1.783 | 0 | 4.2 | 2.417 | 2.417 | opened
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.68 | 0.2 | 120 | 0.48 | 0 | 2.63 | 2.15 | 2.15 | opened | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.062 | 0.742 | 0.2 | 120 | 0.542 | 0 | 2.63 | 2.088 | 2.088 | opened
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 3.41 | 0.37 | 120 | 3.04 | 0 | 4.2 | 1.16 | 1.16 | opened | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.003 | 3.413 | 0.37 | 120 | 3.043 | 0 | 4.2 | 1.157 | 1.157 | opened
19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.14 | 1.02 | 120 | 1.12 | 0 | 4.2 | 3.08 | 3.08 | opened | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 0.0829 | 2.2229 | 1.02 | 120 | 1.2029 | 0 | 4.2 | 2.9971 | 2.9971 | opened
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 2.1 |  |  | 2.1 | 0 | 6.62 | 4.52 | 4.52 | opened | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 |  | 2.1 |  |  | 2.1 | 0 | 6.62 | 4.52 | 4.52 | opened
21 | SS 110/6 Depo | 16+16 | 2.37 |  |  | 2.37 | 0 | 16.8 | 14.43 | 14.43 | opened | 21 | SS 110/6 Depo | 16+16 | 12.1265 | 14.4965 |  |  | 14.4965 | 0 | 16.8 | 2.3035 | 2.3035 | opened
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.79 | 1.17 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.008 | 1.798 | 1.17 | 120 | 0.628 | 0 | 1.68 | 1.052 | 1.052 | opened
23 | SS 110/10 Druzhba | 16+16 | 6.8 | 0.16 | 120 | 6.64 | 0 | 16.8 | 10.16 | 10.16 | opened | 23 | SS 110/10 Druzhba | 16+16 | 0.136 | 6.936 | 0.16 | 120 | 6.776 | 0 | 16.8 | 10.024 | 10.024 | opened
24 | SS 35/10 Dubki | 6,3+6,3 | 3.48 | 0.67 | 120 | 2.81 | 0 | 6.62 | 3.81 | 3.81 | opened | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.7445 | 4.2245 | 0.67 | 120 | 3.5545 | 0 | 6.62 | 3.0655 | 3.0655 | opened
25 | SS 35/10 Dybino | 2,5+2,5 | 1.16 |  |  | 1.16 | 0 | 2.63 | 1.47 | 1.47 | opened | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.25 | 1.41 |  |  | 1.41 | 0 | 2.63 | 1.22 | 1.22 | opened
26 | SS 35/6 Zavolzhskaya | 10+10 | 10.31 |  |  | 10.31 | 0 | 10.5 | 0.19 | 0.19 | opened | 26 | SS 35/6 Zavolzhskaya | 10+10 | 1.8815 | 12.1915 |  |  | 12.1915 | 0 | 10.5 | -1.6915 | -1.6915 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 37.53 |  |  | 37.53 | 0 | 42 | 4.47 | 4.47 | opened | 27 | SS 110/6 Institutskaya | 40+40 | 4.6946 | 42.2246 |  |  | 42.2246 | 0 | 42 | -0.22459 | -0.22459 | closed
28 | SS 35/10 Koza | 1,6+1,6 | 0.41 | 0.16 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | opened | 28 | SS 35/10 Koza | 1,6+1,6 | 0.021 | 0.431 | 0.16 | 120 | 0.271 | 0 | 1.68 | 1.409 | 1.409 | opened
29 | SS 110/35/6 Konstatinovo | 20+20 | 10.53 | 0.1 | 120 | 10.43 | 0 | 21 | 10.57 | 10.57 | opened | 29 | SS 110/35/6 Konstatinovo | 20+20 | 7.0915 | 10.7715 | 0.1 | 120 | 10.6715 | 0 | 21 | 10.3285 | 10.3285 | opened
| Nom. capacity MV, МVА | 20+20 | 6.85 |  |  | 6.85 | 0 | 21 | 14.15 |  |  |  | Nom. capacity MV, МVА | 20+20 | 7.0915 | 7.0915 |  |  | 7.0915 | 0 | 21 | 13.9085
| Nom. capacity LV, МVА | 20+20 | 3.68 | 0.1 | 120 | 3.58 | 0 | 21 | 17.42 |  |  |  | Nom. capacity LV, МVА | 20+20 |  | 3.68 | 0.1 | 120 | 3.58 | 0 | 21 | 17.42
30 | SS 35/10 Kurba | 2,5+2,5 | 1.79 | 0.71 | 120 | 1.08 | 0 | 2.63 | 1.55 | 1.55 | opened | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.5 | 2.29 | 0.71 | 120 | 1.58 | 0 | 2.63 | 1.05 | 1.05 | opened
31 | SS 35/10 Lesnye Polyany | 10+10 | 5.38 |  |  | 5.38 | 0 | 10.5 | 5.12 | 5.12 | opened | 31 | SS 35/10 Lesnye Polyany | 10+10 | 0.2461 | 5.6261 |  |  | 5.6261 | 0 | 10.5 | 4.8739 | 4.8739 | opened
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 4.72 | 3.69 | 120 | 1.03 | 0 | 6.62 | 5.59 | 5.59 | opened | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 0.2145 | 4.9345 | 3.69 | 120 | 1.2445 | 0 | 6.62 | 5.3755 | 5.3755 | opened
33 | SS 35/10 Nekrasovo | 10+10 | 11.67 |  |  | 11.67 | 0 | 10.5 | -1.17 | -1.17 | closed | 33 | SS 35/10 Nekrasovo | 10+10 | 0.432 | 12.102 |  |  | 12.102 | 0 | 10.5 | -1.602 | -1.602 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.88 | 0.38 | 120 | 0.5 | 0 | 2.63 | 2.13 | 2.13 | opened | 34 | SS 35/10 Nikolskoe | 2,5+2,5 |  | 0.88 | 0.38 | 120 | 0.5 | 0 | 2.63 | 2.13 | 2.13 | opened
35 | SS 110/35/6 Oil refinary plant | 25+25 | 16.93 |  |  | 16.93 | 0 | 26.25 | 9.32 | 9.32 | opened | 35 | SS 110/35/6 Oil refinary plant | 25+25 | 14.494 | 24.3541 |  |  | 24.3541 | 0 | 26.25 | 1.896 | 1.896 | opened
| Nom. capacity MV, МVА | 25+25 | 7.07 |  |  | 7.07 | 0 | 26.25 | 19.18 |  |  |  | Nom. capacity MV, МVА | 25+25 | 7.494 | 7.494 |  |  | 7.494 | 0 | 26.25 | 18.7559
| Nom. capacity LV, МVА | 25+25 | 9.86 |  |  | 9.86 | 0 | 26.25 | 16.39 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7 | 16.86 |  |  | 16.86 | 0 | 26.25 | 9.39
36 | SS 110/6/6 Orion | 40+40 | 16.01 |  |  | 16.01 | 0 | 42 | 25.99 | 25.99 |  | 36 | SS 110/6/6 Orion | 40+40 | 0.93459 | 16.9446 |  |  | 16.9446 | 0 | 42 | 25.0554 | 25.0554 | opened
37 | SS 110/35/6 Pavlovskaya | 20+25 | 25.25 |  |  | 25.25 | 0 | 21 | -4.25 | -4.25 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 | 8.5515 | 25.2515 |  |  | 25.2515 | 0 | 21 | -4.2515 | -4.2515 | closed
| Nom. capacity MV, МVА | 20+25 | 8.55 |  |  | 8.55 | 0 | 21 | 12.45 |  |  |  | Nom. capacity MV, МVА | 20+25 | 8.5515 | 8.5515 |  |  | 8.5515 | 0 | 21 | 12.4485
| Nom. capaity LV, МVА | 20+25 | 16.7 |  |  | 16.7 | 0 | 21 | 4.3 |  |  | 2: Nom. capaity LV, МVА; 3: 20+25; 5: 16.7; Мin. 8: 16.7; Мin. 9: 0; Мin. 10: 21; Мin. 11: 4.3
38 | SS 110/10 Pereval | 16+16 | 5.59 |  |  | 5.59 | 0 | 16.8 | 11.21 | 11.21 | opened | 38 | SS 110/10 Pereval | 16+16 | 3.4179 | 9.0079 |  |  | 9.0079 | 0 | 16.8 | 7.7921 | 7.7921 | opened
39 | SS 110/6/6 Perekop | 25+25 | 10.42 |  |  | 10.42 | 0 | 26.25 | 15.83 | 15.83 | opened | 39 | SS 110/6/6 Perekop | 25+25 | 4.0585 | 14.4785 |  |  | 14.4785 | 0 | 26.25 | 11.7715 | 11.7715 | opened
40 | SS 110/6/6 Poligraf | 40+40 | 45.91 |  |  | 45.91 | 0 | 42 | -3.91 | -3.91 | closed | 40 | SS 110/6/6 Poligraf | 40+40 | 5.3149 | 51.2249 |  |  | 51.2249 | 0 | 42 | -9.2249 | -9.2249 | closed
41 | SS 110/35/10 Prechistoe | 10+10 | 5.62 | 0.24 | 120 | 5.38 | 0 | 10.5 | 5.12 | 5.12 | opened | 41 | SS 110/35/10 Prechistoe | 10+10 | 2.5444 | 5.7245 | 0.24 | 120 | 5.4844 | 0 | 10.5 | 5.0156 | 5.0156 | opened
| Nom. capacity MV, МVА | 10+10 | 2.44 |  |  | 2.44 | 0 | 10.5 | 8.06 |  |  |  | Nom. capacity MV, МVА | 10+10 | 2.54 | 2.54 |  |  | 2.54 | 0 | 10.5 | 7.96
| Nom. capacity LV, МVА | 10+10 | 3.18 | 0.24 | 120 | 2.94 | 0 | 10.5 | 7.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.0045 | 3.1845 | 0.24 | 120 | 2.9445 | 0 | 10.5 | 7.5555
42 | SS 35/10 Preventorium | 2,5+2,5 | 1.21 | 0.39 | 120 | 0.82 | 0 | 2.63 | 1.81 | 1.81 | opened | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.027 | 3.237 | 0.39 | 120 | 2.847 | 0 | 2.63 | -0.217 | -0.217 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.53 | 0.04 | 120 | 0.49 | 0 | 2.63 | 2.14 | 2.14 | opened | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.04 | 0.57 | 0.04 | 120 | 0.53 | 0 | 2.63 | 2.1 | 2.1 | opened
44 | SS 110/6/6 Severnaya | 63+63 | 38.17 |  |  | 38.17 | 0 | 66.15 | 27.98 | 27.98 | opened | 44 | SS 110/6/6 Severnaya | 63+63 | 15.9666 | 54.1366 |  |  | 54.1366 | 0 | 66.15 | 12.0134 | 12.0134 | opened
45 | SS 35/10 Sereda | 2,5+2,5 | 1.5 | 0.11 | 120 | 1.39 | 0 | 2.63 | 1.24 | 1.24 | opened | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.0645 | 1.5645 | 0.11 | 120 | 1.4545 | 0 | 2.63 | 1.1755 | 1.1755 | opened
46 | SS 110/6 Tormoznaya | 16+16 | 12.31 |  |  | 12.31 | 0 | 16.8 | 4.49 | 4.49 | opened | 46 | SS 110/6 Tormoznaya | 16+16 | 0.79432 | 13.1043 |  |  | 13.1043 | 0 | 16.8 | 3.6957 | 3.6957 | opened
47 | SS 110/6 Petrol station pump | 16+16 | 6.43 |  |  | 6.43 | 0 | 16.8 | 10.37 | 10.37 | opened | 47 | SS 110/6 Petrol station pump | 16+16 | 3.2 | 9.63 |  |  | 9.63 | 0 | 16.8 | 7.17 | 7.17 | opened
48 | SS 35/10 Troitsa | 2,5+2,5 | 0.66 | 0.14 | 120 | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened | 48 | SS 35/10 Troitsa | 2,5+2,5 |  | 0.66 | 0.14 | 120 | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened
49 | SS 35/10 Tunoshna | 4,0+2,5 | 1.53 | 0.01 | 120 | 1.52 | 0 | 2.63 | 1.11 | 1.11 | opened | 49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.457 | 1.987 | 0.01 | 120 | 1.977 | 0 | 2.63 | 0.653 | 0.653 | opened
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.83 |  |  | 6.83 | 0 | 6.62 | -0.21 | -0.21 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.01 | 6.84 |  |  | 6.84 | 0 | 6.62 | -0.22 | -0.22 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.6 |  |  | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.136 | 0.736 |  |  | 0.736 | 0 | 2.63 | 1.894 | 1.894 | opened
52 | SS 35/10 Urozhay | 4,0+4,0 | 1.63 | 0.74 | 120 | 0.89 | 0 | 4.2 | 3.31 | 3.31 | opened | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.448 | 2.078 | 0.74 | 120 | 1.338 | 0 | 4.2 | 2.862 | 2.862 | opened
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.46 | 0.28 | 120 | 0.62 | 0 | 3.36 | 2.74 | 2.74 | opened | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.0922 | 1.15 | 0.28 | 120 | 0.87 | 0 | 3.36 | 2.49 | 2.49 | opened
| Nom. capacity MV, МVА | 6.3 | 2.56 | [8 empty] | 2: Nom. capacity MV, МVА; 3: 6.3; 4: 2.8422
| Nom. capacity LV, МVА | 6.3 | 0.9 | 0.28 | 120 | 0.62 | 0 | 3.36 | 2.74 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.25 | 1.15 | 0.28 | 120 | 0.87 | 0 | 3.36 | 2.49
54 | SS 110/10 Chayka | 25+25 | 16.2 |  |  | 16.2 | 0 | 26.25 | 10.05 | 10.05 | opened | 54 | SS 110/10 Chayka | 25+25 | 23.7523 | 39.9523 |  |  | 39.9523 | 0 | 26.25 | -13.7023 | -13.7023 | closed
55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.53 | 0.19 | 120 | 1.34 | 0 | 2.63 | 1.29 | 1.29 | opened | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 0.04 | 1.57 | 0.19 | 120 | 1.38 | 0 | 2.63 | 1.25 | 1.25 | opened
56 | SS 35/10 Shchedrino | 4,0+4,0 | 1.51 |  |  | 1.51 | 0 | 4.2 | 2.69 | 2.69 | opened | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.732 | 2.242 |  |  | 2.242 | 0 | 4.2 | 1.958 | 1.958 | opened
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 29.43 |  |  | 29.43 | 0 | 42 | 12.57 | 12.57 | opened | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 8.6438 | 38.0738 |  |  | 38.0738 | 0 | 42 | 3.9262 | 3.9262 | opened
58 | SS 110/10/6 Yartsevo | 25+25 | 5.48 |  |  | 5.48 | 0 | 26.25 | 20.77 | 20.77 | opened | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.02175 | 5.5018 |  |  | 5.5018 | 0 | 26.25 | 20.7482 | 20.7482 | opened
59 | SS 110/10 Altynovo | 6,3+6,3 | 3.19 |  |  | 3.19 | 0 | 6.62 | 3.43 | 3.43 | opened | 59 | SS 110/10 Altynovo | 6,3+6,3 | 0.07 | 3.26 |  |  | 3.26 | 0 | 6.62 | 3.36 | 3.36 | opened
60 | SS 110/35/10 Borisogleb | 10+16 | 7.8 |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | opened | 60 | SS 110/35/10 Borisogleb | 10+16 | 2.2258 | 8.6958 |  |  | 8.6958 | 0 | 10.5 | 1.8042 | 1.8042 | opened
| Nom. capacity MV, МVА | 10+16 | 1.33 |  |  | 1.33 | 0 | 10.5 | 9.17 |  |  |  | Nom. capacity MV, МVА | 10+16 | 1.4338 | 1.4338 |  |  | 1.4338 | 0 | 10.5 | 9.0662
| Nom. capacity LV, МVА | 10+16 | 6.47 |  |  | 6.47 | 0 | 10.5 | 4.03 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.792 | 7.262 |  |  | 7.262 | 0 | 10.5 | 3.238
61 | SS 110/35/10 Vasilkovo | 10+10 | 2.02 | 0.28 | 120 | 1.74 | 0 | 10.5 | 8.76 | 8.76 | opened | 61 | SS 110/35/10 Vasilkovo | 10+10 | 1.6457 | 2.2257 | 0.28 | 120 | 1.9457 | 0 | 10.5 | 8.5543 | 8.5543 | opened
| Nom. capacity MV, МVА | 10+10 | 1.44 |  |  | 1.44 | 0 | 10.5 | 9.06 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.5028 | 1.5028 |  |  | 1.5028 | 0 | 10.5 | 8.9972
| Nom. capacity LV, МVА | 10+10 | 0.58 | 0.28 | 120 | 0.3 | 0 | 10.5 | 10.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.1429 | 0.7229 | 0.28 | 120 | 0.4429 | 0 | 10.5 | 10.0571
62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.34 | 0.09 | 120 | 0.25 | 0 | 6.62 | 6.37 | 6.37 | opened | 62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.002 | 0.342 | 0.09 | 120 | 0.252 | 0 | 6.62 | 6.368 | 6.368 | opened
63 | SS 110/6 Gavrilov Yam | 16+16 | 13.53 |  |  | 13.53 | 0 | 16.8 | 3.27 | 3.27 | opened | 63 | SS 110/6 Gavrilov Yam | 16+16 |  | 13.53 |  |  | 13.53 | 0 | 16.8 | 3.27 | 3.27 | opened
64 | SS 110/6 Kinoplyonka | 6,3+10 | 9.57 |  |  | 9.57 | 0 | 6.62 | -2.95 | -2.95 | closed | 64 | SS 110/6 Kinoplyonka | 6,3+10 | 0.587 | 10.157 |  |  | 10.157 | 0 | 6.62 | -3.537 | -3.537 | closed
65 | SS 110/35/10 Klimatino | 6,3+6,3 | 1.85 |  |  | 1.85 | 0 | 6.62 | 4.77 | 4.77 | opened | 65 | SS 110/35/10 Klimatino | 6,3+6,3 | 0.723 | 1.943 |  |  | 1.943 | 0 | 6.62 | 4.677 | 4.677 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.63 |  |  | 0.63 | 0 | 6.62 | 5.99 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.63 | 0.63 |  |  | 0.63 | 0 | 6.62 | 5.99
| Nom. capacity LV, МVА | 6,3+6,3 | 1.22 |  |  | 1.22 | 0 | 6.62 | 5.4 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.093 | 1.313 |  |  | 1.313 | 0 | 6.62 | 5.307
66 | SS 110/35/10 Nila | 6,3+6,3 | 7.61 | 0.37 | 120 | 7.24 | 0 | 6.62 | -0.62 | -0.62 | closed | 66 | SS 110/35/10 Nila | 6,3+6,3 | 7.5755 | 9.3555 | 0.37 | 120 | 8.9855 | 0 | 6.62 | -2.3655 | -2.3655 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 5.83 |  |  | 5.83 | 0 | 6.62 | 0.79 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 6.9215 | 6.9215 |  |  | 6.9215 | 0 | 6.62 | -0.3015
| Nom. capacity LV, МVА | 6,3+6,3 | 1.78 | 0.37 | 120 | 1.41 | 0 | 6.62 | 5.21 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.654 | 2.434 | 0.37 | 120 | 2.064 | 0 | 6.62 | 4.556
67 | SS 110/35/6 Pereslavl | 25+25 | 22.95 |  |  | 22.95 | 0 | 26.25 | 3.3 | 3.3 | opened | 67 | SS 110/35/6 Pereslavl | 25+25 | 14.4054 | 27.9154 |  |  | 27.9154 | 0 | 26.25 | -1.6654 | -1.6654 | closed
| Nom. capacity MV, МVА | 25+25 | 9.44 |  |  | 9.44 | 0 | 26.25 | 16.81 |  |  |  | Nom. capacity MV, МVА | 25+25 | 14.0704 | 14.0704 |  |  | 14.0704 | 0 | 26.25 | 12.1796
| Nom. capacity LV, МVА | 25+25 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.335 | 13.845 |  |  | 13.845 | 0 | 26.25 | 12.405
68 | SS 110/10 Ploski | 2,5+2,5 | 1.47 |  |  | 1.47 | 0 | 2.63 | 1.16 | 1.16 | opened | 68 | SS 110/10 Ploski | 2,5+2,5 | 0.645 | 2.115 |  |  | 2.115 | 0 | 2.63 | 0.515 | 0.515 | opened
69 | SS 110/35/10 Rostov | 25+20 | 20.15 |  |  | 20.15 | 0 | 21 | 0.85 | 0.85 | opened | 69 | SS 110/35/10 Rostov | 25+20 | 3.4781 | 21.7981 |  |  | 21.7981 | 0 | 21 | -0.7981 | -0.7981 | closed
| Nom. capacity MV, МVА | 25+20 | 1.83 |  |  | 1.83 | 0 | 21 | 19.17 |  |  |  | Nom. capacity MV, МVА | 25+20 | 1.8878 | 1.8878 |  |  | 1.8878 | 0 | 21 | 19.1122
| Nom. Capacity LV, МVА | 25+20 | 18.32 |  |  | 18.32 | 0 | 21 | 2.68 |  |  |  | Nom. capacity LV, МVА | 25+20 | 1.5903 | 19.9103 |  |  | 19.9103 | 0 | 21 | 1.0897
70 | SS 110/35/10 Technical school | 6,3+6,3 | 5.27 |  |  | 5.27 | 0 | 6.62 | 1.35 | 1.35 | opened | 70 | SS 110/35/10 Technical school | 6,3+6,3 | 3.5926 | 6.3925 |  |  | 6.3925 | 0 | 6.62 | 0.22745 | 0.22745 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 2.47 |  |  | 2.47 | 0 | 6.62 | 4.15 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 2.7748 | 2.7748 |  |  | 2.7748 | 0 | 6.62 | 3.8453
| Nom. capacity LV, МVА | 6,3+6,3 | 2.8 |  |  | 2.8 | 0 | 6.62 | 3.82 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.8178 | 3.6178 |  |  | 3.6178 | 0 | 6.62 | 3.0022
71 | SS 110/35/10 Uglich | 25+25 | 22.82 |  |  | 22.82 | 0 | 26.25 | 3.43 | 3.43 | opened | 71 | SS 110/35/10 Uglich | 25+25 | 25.538 | 30.568 |  |  | 30.568 | 0 | 26.25 | -4.318 | -4.318 | closed
| Nom. capacidty MV, МVА | 25+25 | 17.79 |  |  | 17.79 | 0 | 26.25 | 8.46 |  |  |  | Nom. capacity MV, МVА | 25+25 | 24.798 | 24.798 |  |  | 24.798 | 0 | 26.25 | 1.452
| Nom. capacity LV, МVА | 25+25 | 5.03 |  |  | 5.03 | 0 | 26.25 | 21.22 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.74 | 5.77 |  |  | 5.77 | 0 | 26.25 | 20.48
72 | SS 110/10 Ustye | 10+10 | 3.86 | 0.32 | 120 | 3.54 | 0 | 10.5 | 6.96 | 6.96 | opened | 72 | SS 110/10 Ustye | 10+10 | 0.15 | 4.01 | 0.32 | 120 | 3.69 | 0 | 10.5 | 6.81 | 6.81 | opened
73 | SS 110/10 Shurskol | 10+10 | 1.97 | 1.01 | 120 | 0.96 | 0 | 10.5 | 9.54 | 9.54 | opened | 73 | SS 110/10 Shurskol | 10+10 | 0.445 | 2.415 | 1.01 | 120 | 1.405 | 0 | 10.5 | 9.095 | 9.095 | opened
74 | SS 110/10 Yur.Sloboda | 10+10 | 8.32 | 0.23 | 120 | 8.09 | 0 | 10.5 | 2.41 | 2.41 | opened | 74 | SS 110/10 Yur.Sloboda | 10+10 | 0.6072 | 8.9272 | 0.23 | 120 | 8.6972 | 0 | 10.5 | 1.8028 | 1.8028 | opened
75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.52 |  |  | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened | 75 | SS 35/10 Aleshkino | 2,5+2,5 |  | 0.52 |  |  | 0.52 | 0 | 2.63 | 2.11 | 2.11 | opened
76 | SS 35/6 Batki | 1,6+1,6 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | opened | 76 | SS 35/6 Batki | 1,6+1,6 | 0.4013 | 1.5813 |  |  | 1.5813 | 0 | 1.68 | 0.0987 | 0.0987 | opened
77 | SS 35/10 Beregovaya | 1.6 | 0.18 | 1.64 | 24 hours | 1.64 | 0 | 1.64 | 1.46 | 1.46 | opened | 77 | SS 35/10 Beregovaya | 1.6 | 0.06 | 0.24 | 1.64 | 24 hours | 1.64 | 0 | 1.64 | 1.4 | 1.4 | opened
78 | SS 35/10 Berendeevo | 2,5+2,5 | 1.63 | 0.12 | 120 | 1.51 | 0 | 2.63 | 1.12 | 1.12 | opened | 78 | SS 35/10 Berendeevo | 2,5+2,5 | 0.188 | 1.818 | 0.12 | 120 | 1.698 | 0 | 2.63 | 0.932 | 0.932 | opened
79 | SS 35/10 Vorzha | 1,8+1,8 | 0.39 | 0.3 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened | 79 | SS 35/10 Vorzha | 1,8+1,8 | 0.3439 | 0.7339 | 0.3 | 120 | 0.4339 | 0 | 1.89 | 1.4561 | 1.4561 | opened
80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.79 | 0.21 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 |  | 0.79 | 0.21 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened
81 | SS 35/10 Glebovo | 2,5+2,5 | 2.76 |  |  | 2.76 | 0 | 2.63 | -0.13 | -0.13 | closed | 81 | SS 35/10 Glebovo | 2,5+2,5 | 1.645 | 4.405 |  |  | 4.405 | 0 | 2.63 | -1.775 | -1.775 | closed
82 | SS 35/10 Gorki | 2,5+2,5 | 1.13 |  |  | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 82 | SS 35/10 Gorki | 2,5+2,5 | 0.005 | 1.135 |  |  | 1.135 | 0 | 2.63 | 1.495 | 1.495 | opened
83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.26 |  |  | 1.26 | 0 | 1.68 | 0.42 | 0.42 | opened | 83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.072 | 1.332 |  |  | 1.332 | 0 | 1.68 | 0.348 | 0.348 | opened
84 | SS 35/10 Zaozerye | 2,5+1,6 | 1.12 |  |  | 1.12 | 0 | 1.68 | 0.56 | 0.56 | opened | 84 | SS 35/10 Zaozerye | 2,5+1,6 | 0.008 | 1.128 |  |  | 1.128 | 0 | 1.68 | 0.552 | 0.552 | opened
85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 1.46 |  |  | 1.46 | 0 | 2.63 | 1.17 | 1.17 | opened | 85 | SS 35/10 Ilyinskoe | 2,5+2,5 |  | 1.46 |  |  | 1.46 | 0 | 2.63 | 1.17 | 1.17 | opened
86 | SS 35/10 Kibernetik | 2,5+2,5 | 2.45 |  |  | 2.45 | 0 | 2.63 | 0.18 | 0.18 | opened | 86 | SS 35/10 Kibernetik | 2,5+2,5 | 0.273 | 2.723 |  |  | 2.723 | 0 | 2.63 | -0.093 | -0.093 | closed
87 | SS 35/10 Klementyevo | 2.5 | 0.29 | 0.69 | 24 hours | 0.69 | 0 | 0.69 | 0.4 | 0.4 | opened | 87 | SS 35/10 Klementyevo | 2.5 |  | 0.29 | 0.69 | 24 hours | 0.69 | 0 | 0.69 | 0.4 | 0.4 | opened
88 | SS 35/10 Krasnoe | 4,0+2,5 | 1.09 | 0.3 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | opened | 88 | SS 35/10 Krasnoe | 4+2,5 | 2.193 | 3.283 | 0.3 | 120 | 2.983 | 0 | 2.63 | -0.353 | -0.353 | closed
89 | SS 35/10 Kulakovo | 2,5+2,5 | 1.66 |  |  | 1.66 | 0 | 2.63 | 0.97 | 0.97 | opened | 89 | SS 35/10 Kulakovo | 2,5+2,5 | 0.0105 | 1.6705 |  |  | 1.6705 | 0 | 2.63 | 0.9595 | 0.9595 | opened
90 | SS 35/6 Kupan | 2,5+2,5 | 2.58 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | opened | 90 | SS 35/6 Kupan | 2,5+2,5 | 0.35 | 2.93 |  |  | 2.93 | 0 | 2.63 | -0.3 | -0.3 | closed
91 | SS 35/10 Markovo | 2,5+2,5 | 0.82 | 0.27 | 120 | 0.55 | 0 | 2.63 | 2.08 | 2.08 | opened | 91 | SS 35/10 Markovo | 2,5+2,5 |  | 0.82 | 0.27 | 120 | 0.55 | 0 | 2.63 | 2.08 | 2.08 | opened
92 | SS 35/10 Nagorye | 4,0+4,0 | 3.23 |  |  | 3.23 | 0 | 4.2 | 0.97 | 0.97 | opened | 92 | SS 35/10 Nagorye | 4+4 | 0.223 | 3.453 |  |  | 3.453 | 0 | 4.2 | 0.747 | 0.747 | opened
93 | SS 35/10 Porechye | 6,3+6,3 | 1.9 | 0.61 | 120 | 1.29 | 0 | 6.62 | 5.33 | 5.33 | opened | 93 | SS 35/10 Porechye | 6,3+6,3 | 0.0056 | 1.9056 | 0.61 | 120 | 1.2956 | 0 | 6.62 | 5.3244 | 5.3244 | opened
94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened | 94 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.012 | 0.862 |  |  | 0.862 | 0 | 2.63 | 1.768 | 1.768 | opened
95 | SS 35/10 Ramenye | 2,5+2,5 | 0.8 | 0.26 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened | 95 | SS 35/10 Ramenye | 2,5+2,5 | 0.02 | 0.82 | 0.26 | 120 | 0.56 | 0 | 2.63 | 2.07 | 2.07 | opened
96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 1.51 |  |  | 1.51 | 0 | 1.68 | 0.17 | 0.17 | opened | 96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 0.003 | 1.513 |  |  | 1.513 | 0 | 1.68 | 0.167 | 0.167 | opened
97 | SS 35/10 Saraevo | 1+1,6 | 0.84 |  |  | 0.84 | 0 | 1.05 | 0.21 | 0.21 | opened | 97 | SS 35/10 Saraevo | 1+1,6 | 0.63 | 1.47 |  |  | 1.47 | 0 | 1.05 | -0.42 | -0.42 | closed
98 | SS 35/10 Selifontovo | 2,5+2,5 | 1.87 | 0.16 | 120 | 1.71 | 0 | 2.63 | 0.92 | 0.92 | opened | 98 | SS 35/10 Selifontovo | 2,5+2,5 |  | 1.87 | 0.16 | 120 | 1.71 | 0 | 2.63 | 0.92 | 0.92 | opened
99 | SS 35/10 Semibratovo | 4,0+4,0 | 0.78 | 0.25 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 99 | SS 35/10 Semibratovo | 4+4 | 0.1156 | 0.8956 | 0.25 | 120 | 0.25 | 0 | 0.25 | -0.6456 | -0.6456 | closed
100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.94 |  |  | 0.94 | 0 | 1.68 | 0.74 | 0.74 | opened | 100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.1156 | 1.0556 |  |  | 1.0556 | 0 | 1.68 | 0.6244 | 0.6244 | opened
101 | SS 35/10 Solomidino | 2.5 | 0.57 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | 0.24 | 0.24 | opened | 101 | SS 35/10 Solomidino | 2.5 | 0.0066 | 0.5766 | 0.81 | 24 hours | 0.81 | 0 | 0.81 | 0.2334 | 0.2334 | opened
102 | SS 35/10 Stavotino | 4,0+4,0 | 1.72 | 0.51 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened | 102 | SS 35/10 Stavotino | 4+4 | 0.1615 | 1.8815 | 0.51 | 120 | 1.3715 | 0 | 4.2 | 2.8285 | 2.8285 | opened
103 | SS 35/10 Urusovo | 2,5+2,5 | 0.79 | 0.06 | 120 | 0.73 | 0 | 2.63 | 1.9 | 1.9 | opened | 103 | SS 35/10 Urusovo | 2,5+2,5 |  | 0.79 | 0.06 | 120 | 0.73 | 0 | 2.63 | 1.9 | 1.9 | opened
104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.87 |  |  | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened | 104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.042 | 0.912 |  |  | 0.912 | 0 | 2.63 | 1.718 | 1.718 | opened
105 | SS 35/10 Choporovo | 2,5+2,5 | 0.54 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened | 105 | SS 35/10 Choporovo | 2,5+2,5 | 0.1 | 0.64 |  |  | 0.64 | 0 | 2.63 | 1.99 | 1.99 | opened
106 | SS 35/10 Shchurovo | 2,5+2,5 | 1.31 | 0.27 | 120 | 1.04 | 0 | 2.63 | 1.59 | 1.59 | opened | 106 | SS 35/10 Shchurovo | 2,5+2,5 | 0.01 | 1.32 | 0.27 | 120 | 1.05 | 0 | 2.63 | 1.58 | 1.58 | opened
107 | SS 35/10 Neksans | 10+10 | 1.2 |  |  | 1.2 | 0 | 10.5 | 9.3 | 9.3 | opened | 107 | SS 35/10 Neksans | 10+10 | 7 | 8.2 |  |  | 8.2 | 0 | 10.5 | 2.3 | 2.3 | opened
108 | SS 35/6 Pribrezhnaya | 10+10 | 11.28 |  |  | 11.28 | 0 | 10.5 | -0.78 | -0.78 | closed | 108 | SS 35/6 Pribrezhnaya | 10+10 |  | 11.28 |  |  | 11.28 | 0 | 10.5 | -0.78 | -0.78 | closed
109 | SS 110/10 Product pipeline | 6,3+6,3 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened | 109 | SS 110/10 Product pipeline | 6,3+6,3 |  | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened
110 | SS 110/10 Nekouz | 6,3+6,3 | 4.3 | 0.1 | 120 | 4.2 | 0 | 6.62 | 2.42 | 2.42 | opened | 110 | SS 110/10 Nekouz | 6,3+6,3 | 0.004 | 4.304 | 0.1 | 120 | 4.204 | 0 | 6.62 | 2.416 | 2.416 | opened
111 | SS 110/6 Yuzhnaya | 25+25 | 21.25 |  |  | 21.25 | 0 | 26.25 | 5 | 5 | opened | 111 | SS 110/6 Yuzhnaya | 25+25 | 0.17004 | 21.42 |  |  | 21.42 | 0 | 26.25 | 4.83 | 4.83 | opened
112 | SS 110/10 Optika | 10+10 | 4.9 | 1.18 | 120 | 3.72 | 0 | 10.5 | 6.78 | 6.78 | opened | 112 | SS 110/10 Optika | 10+10 | 0.671 | 5.571 | 1.18 | 120 | 4.391 | 0 | 10.5 | 6.109 | 6.109 | opened
113 | SS 110/6 Poligrafmash | 16+16 | 10.4 |  |  | 10.4 | 0 | 16.8 | 6.4 | 6.4 | opened | 113 | SS 110/6 Poligrafmash | 16+16 | 0.48025 | 10.8803 |  |  | 10.8803 | 0 | 16.8 | 5.9197 | 5.9197 | opened
114 | SS 110/6/6 Zapadnaya | 63+63 | 52.3 |  |  | 52.3 | 0 | 66.15 | 13.85 | 13.85 | opened | 114 | SS 110/6/6 Zapadnaya | 63+63 | 1.1713 | 53.4713 |  |  | 53.4713 | 0 | 66.15 | 12.6787 | 12.6787 | opened
115 | SS 110/35/6 Volzhskaya | 40+40 | 26 |  |  | 26 | 0 | 42 | 16 | 16 | opened | 115 | SS 110/35/6 Volzhskaya | 40+40 | 4.2048 | 30.2048 |  |  | 30.2048 | 0 | 42 | 11.7952 | 11.7952 | opened
| Nom. capacity MV, МVА | 40+40 | [9 empty] | 2: Nom. capacity MV, МVА; 3: 40+40
| Nom. capacity LV, МVА | 40+40 | 26 |  |  | 26 | 0 | 42 | 16 |  |  |  | Nom. capacity LV, МVА | 40+40 | 4.205 | 30.205 |  |  | 30.205 | 0 | 42 | 11.8
116 | SS 110/35/6 Levoberezhnaya | 16+16 | 12.2 |  |  | 12.2 | 0 | 16.8 | 4.6 | 4.6 | opened | 116 | SS 110/35/6 Levoberezhnaya | 16+16 | 8.095 | 12.455 |  |  | 12.455 | 0 | 16.8 | 4.345 | 4.345 | opened
| Nom. capacity MV, МVА | 16+16 | 7.84 |  |  | 7.84 | 0 | 16.8 | 8.96 |  |  |  | Nom. capacity MV, МVА | 16+16 | 7.95 | 7.95 |  |  | 7.95 | 0 | 16.8 | 8.85
| Nom. capacity LV, МVА | 16+16 | 4.36 |  |  | 4.36 | 0 | 16.8 | 12.44 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.145 | 4.505 |  |  | 4.505 | 0 | 16.8 | 12.295
117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 2.4 |  |  | 2.4 | 0 | 7.88 | 5.48 | 5.48 | opened | 117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 1.482 | 2.432 |  |  | 2.432 | 0 | 7.88 | 5.448 | 5.448 | opened
| Nom. capacity MV, МVА | 7,5+7,5 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 | 1.45 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43
| Nom. capacity LV, МVА | 7,5+7,5 | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0.032 | 0.982 |  |  | 0.982 | 0 | 7.88 | 6.898
118 | SS 110/6 Dock yard | 10+10 | 4.4 |  |  | 4.4 | 0 | 10.5 | 6.1 | 6.1 | opened | 118 | SS 110/6 Dock yard | 10+10 | 0.055 | 4.455 |  |  | 4.455 | 0 | 10.5 | 6.045 | 6.045 | opened
119 | SS 110/6 Selekhovo | 6,3+6,3 | 3.4 |  |  | 3.4 | 0 | 6.62 | 3.22 | 3.22 | opened | 119 | SS 110/6 Selekhovo | 6,3+6,3 | 0.01 | 3.41 |  |  | 3.41 | 0 | 6.62 | 3.21 | 3.21 | opened
120 | SS 35/6 Kamenniki | 4,0+4,0 | 2.32 |  |  | 2.32 | 0 | 4.2 | 1.88 | 1.88 | opened | 120 | SS 35/6 Kamenniki | 4+4 | 0.149 | 2.469 |  |  | 2.469 | 0 | 4.2 | 1.731 | 1.731 | opened
121 | SS 35/10 Shashkovo | 1,6+1,6 | 1.49 | 0.52 | 120 | 0.97 | 0 | 1.68 | 0.71 | 0.71 | opened | 121 | SS 35/10 Shashkovo | 1,6+1,6 | 0.08 | 1.57 | 0.52 | 120 | 1.05 | 0 | 1.68 | 0.63 | 0.63 | opened
122 | SS 110/6 Мукуену | 25+25 | 17.75 |  |  | 17.75 | 0 | 26.25 | 8.5 | 8.5 | opened | 122 | SS 110/6 Мукуену | 25+25 | 1.5481 | 19.2981 |  |  | 19.2981 | 0 | 26.25 | 6.9519 | 6.9519 | opened
123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.08 | 0.73 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 1.332 | 3.412 | 0.73 | 120 | 2.682 | 0 | 4.2 | 1.518 | 1.518 | opened
124 | SS 35/10 Arefino | 2,5+2,5 | 1.65 | 0.52 | 120 | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 124 | SS 35/10 Arefino | 2,5+2,5 | 0.025 | 1.675 | 0.52 | 120 | 1.155 | 0 | 2.63 | 1.475 | 1.475 | opened
125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.62 |  |  | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.01 | 0.63 |  |  | 0.63 | 0 | 1.68 | 1.05 | 1.05 | opened
126 | SS 35/10 Pokrov | 1,6+1,6 | 0.58 | 0.87 | 120 | -0.29 | 0 | 1.68 | 1.97 | 1.97 | opened | 126 | SS 35/10 Pokrov | 1,6+1,6 | 0.014 | 0.594 | 0.87 | 120 | -0.276 | 0 | 1.68 | 1.956 | 1.956 | opened
127 | SS 35/10 Anikovo | 2,5+2,5 | 0.88 | 0.04 | 120 | 0.84 | 0 | 2.63 | 1.79 | 1.79 | opened | 127 | SS 35/10 Anikovo | 2,5+2,5 | 0.03 | 0.91 | 0.04 | 120 | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened
128 | SS 35/10 Novoe selo | 2,5+2,5 | 1.13 |  |  | 1.13 | 0 | 2.63 | 1.5 | 1.5 | opened | 128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.102 | 1.232 |  |  | 1.232 | 0 | 2.63 | 1.398 | 1.398 | opened
129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 4.6 |  |  | 4.6 | 0 | 6.62 | 2.02 | 2.02 | opened | 129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.2185 | 4.8185 |  |  | 4.8185 | 0 | 6.62 | 1.8015 | 1.8015 | opened
130 | SS 35/10 Breytovo | 4,0+4,0 | 3.92 |  |  | 3.92 | 0 | 4.2 | 0.28 | 0.28 | opened | 130 | SS 35/10 Breytovo | 4+4 | 0.561 | 4.481 |  |  | 4.481 | 0 | 4.2 | -0.281 | -0.281 | closed
131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.83 | 0.21 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened | 131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.035 | 0.865 | 0.21 | 120 | 0.655 | 0 | 1.68 | 1.025 | 1.025 | opened
132 | SS 35/10 Znamovo | 2,5+2,5 | 1.03 | 0.25 | 120 | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened | 132 | SS 35/10 Znamovo | 2,5+2,5 |  | 1.03 | 0.25 | 120 | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened
133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 1.18 |  |  | 1.18 | 0 | 2.63 | 1.45 | 1.45 | opened | 133 | SS 35/10 Rozhdestvenno | 2,5+2,5 |  | 1.18 |  |  | 1.18 | 0 | 2.63 | 1.45 | 1.45 | opened
134 | SS 35/10 Zapolye | 2,5+2,5 | 0.6 |  |  | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened | 134 | SS 35/10 Zapolye | 2,5+2,5 |  | 0.6 |  |  | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened
135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.31 | 0.82 | 120 | 0.49 | 0 | 1.68 | 1.19 | 1.19 | opened | 135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.0385 | 1.3485 | 0.82 | 120 | 0.5285 | 0 | 1.68 | 1.1515 | 1.1515 | opened
136 | SS 35/10 Latskoe | 1,6+2,5 | 0.43 | 0.1 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened | 136 | SS 35/10 Latskoe | 1,6+2,5 |  | 0.43 | 0.1 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
137 | SS 35/10 Borok | 2,5+4,0 | 1.25 | 0.46 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | opened | 137 | SS 35/10 Borok | 2,5+4 | 0.008 | 1.258 | 0.46 | 120 | 0.798 | 0 | 2.63 | 1.832 | 1.832 | opened
138 | SS 35/10 Myshkin | 4,0+6,3 | 3.97 | 0.41 | 120 | 3.56 | 0 | 4.2 | 0.64 | 0.64 | opened | 138 | SS 35/10 Myshkin | 4+6,3 | 0.5287 | 4.4987 | 0.41 | 120 | 4.0887 | 0 | 4.2 | 0.1113 | 0.1113 | opened
139 | SS 110/10 Volga | 6,3+5,6 | 2.03 |  |  | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened | 139 | SS 110/10 Volga | 6,3+5,6 |  | 2.03 |  |  | 2.03 | 0 | 5.88 | 3.85 | 3.85 | opened
140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 2.38 | 0.29 | 120 | 2.09 | 0 | 2.63 | 0.54 | 0.54 | opened | 140 | SS 35/10 Krasnaya Gorka | 4+2,5 | 0.01 | 2.39 | 0.29 | 120 | 2.1 | 0 | 2.63 | 0.53 | 0.53 | opened
141 | SS 110/35/6 Vostochnaya | 25+25 | 19.29 |  |  | 19.29 | 0 | 26.25 | 6.96 | 6.96 | opened | 141 | SS 110/35/6 Vostochnaya | 25+25 | 4.0996 | 20.4396 |  |  | 20.4396 | 0 | 26.25 | 5.8104 | 5.8104 | opened
| Nom. capacity MV, МVА | 25+25 | 2.95 |  |  | 2.95 | 0 | 26.25 | 23.3 |  |  |  | Nom. capacity MV, МVА | 25+25 | 3.626 | 3.626 |  |  | 3.626 | 0 | 26.25 | 22.624
| Nom. capacity LV, МVА | 25+25 | 16.34 |  |  | 16.34 | 0 | 26.25 | 9.91 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.47357 | 16.8136 |  |  | 16.8136 | 0 | 26.25 | 9.4364
142 | SS 110/35/10 Zalesye | 10+10 | 8.54 | 1.65 | 120 | 6.89 | 0 | 10.5 | 3.61 | 3.61 | opened | 142 | SS 110/35/10 Zalesye | 10+10 | 2.36 | 8.98 | 1.65 | 120 | 7.33 | 0 | 10.5 | 3.17 | 3.17 | opened
| Nom. capacity MV, МVА | 10+10 | 1.92 |  |  | 1.92 | 0 | 10.5 | 8.58 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.92 | 1.92 |  |  | 1.92 | 0 | 10.5 | 8.58
| Nom. capacity LV, МVА | 10+10 | 6.62 | 1.65 | 120 | 4.97 | 0 | 10.5 | 5.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.44 | 7.06 | 1.65 | 120 | 5.41 | 0 | 10.5 | 5.09
143 | SS 110/10 Lugovaya | 6,3+6,3 | 3.7 |  |  | 3.7 | 0 | 6.62 | 2.92 | 2.92 | opened | 143 | SS 110/10 Lugovaya | 6,3+6,3 | 0.162 | 3.862 |  |  | 3.862 | 0 | 6.62 | 2.758 | 2.758 | opened
144 | SS 110/35/10 Lom | 10+10 | 8.06 | 1.07 | 120 | 6.99 | 0 | 10.5 | 3.51 | 3.51 | opened | 144 | SS 110/35/10 Lom | 10+10 | 7.1305 | 8.5405 | 1.07 | 120 | 7.4705 | 0 | 10.5 | 3.0295 | 3.0295 | opened
| Nom. capacity MV, МVА | 10+10 | 6.65 |  |  | 6.65 | 0 | 10.5 | 3.85 |  |  |  | Nom. capacity MV, МVА | 10+10 | 6.9705 | 6.9705 |  |  | 6.9705 | 0 | 10.5 | 3.5295
| Nom. capacity LV, МVА | 10+10 | 1.41 | 1.07 | 120 | 0.34 | 0 | 10.5 | 10.16 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.16 | 1.57 | 1.07 | 120 | 0.5 | 0 | 10.5 | 10
145 | SS 35/10 Varegovo | 2,5+1,6 | 0.88 |  |  | 0.88 | 0 | 1.68 | 0.8 | 0.8 | opened | 145 | SS 35/10 Varegovo | 2,5+1,6 | 0.24 | 1.12 |  |  | 1.12 | 0 | 1.68 | 0.56 | 0.56 | opened
146 | SS 110/35/10 Shestikhino | 10+10 | 5.14 | 0.27 | 120 | 4.87 | 0 | 10.5 | 5.63 | 5.63 | opened | 146 | SS 110/35/10 Shestikhino | 10+10 | 5.5973 | 6.1474 | 0.27 | 120 | 5.8773 | 0 | 10.5 | 4.6227 | 4.6227 | opened
| Nom. capacity MV, МVА | 10+10 | 4.59 |  |  | 4.59 | 0 | 10.5 | 5.91 |  |  |  | Nom. capacity MV, МVА | 10+10 | 5.3953 | 5.3953 |  |  | 5.3953 | 0 | 10.5 | 5.1047
| Nom. capacity LV, МVА | 10+10 | 0.55 | 0.27 | 120 | 0.28 | 0 | 10.5 | 10.22 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.202 | 0.752 | 0.27 | 120 | 0.482 | 0 | 10.5 | 10.018
147 | SS 110/35/10 Kryukovo | 6.3 | 4.28 | 0.87 | 24 hours | 3.41 | 0 | 6.62 | 3.21 | 2.64 | opened | 147 | SS 110/35/10 Kryukovo | 6.3 | 4.2443 | 4.5443 | 0.87 | 24 hours | 3.6744 | 0 | 6.62 | 2.9457 | 2.3756 | opened
| Nom. capacidty MV, МVА | 6.3 | 3.98 |  |  | 3.98 | 0 | 6.62 | 2.64 |  |  |  | Nom. capacidty MV, МVА | 6.3 | 4.2443 | 4.2443 |  |  | 4.2443 | 0 | 6.62 | 2.3756
| Nom. capacity LV, МVА | 6.3 | 0.3 | 0.87 | 24 hours | -0.57 | 0 | 6.62 | 7.19 |  |  |  | Nom. capacity LV, МVА | 6.3 |  | 0.3 | 0.87 | 24 hours | -0.57 | 0 | 6.62 | 7.19
148 | SS 35/10 Beloe | 2.5 | 0.73 | 1.24 | 24 hours | 1.24 | 0 | 1.24 | 0.51 | 0.51 | opened | 148 | SS 35/10 Beloe | 2.5 |  | 0.73 | 1.24 | 24 hours | 1.24 | 0 | 1.24 | 0.51 | 0.51 | opened
149 | SS 110/35/10 Glebovo | 10 | 5.13 | 0.6 | 24 hours | 4.53 | 0 | 10.5 | 5.97 | 5.97 | opened | 149 | SS 110/35/10 Glebovo | 10 | 5.1895 | 7.2995 | 0.6 | 24 hours | 6.6995 | 0 | 10.5 | 3.8005 | 3.8005 | opened
| Nom. capacity MV, МVА | 10 | 3.02 |  |  | 3.02 | 0 | 10.5 | 7.48 |  |  |  | Nom. capacity MV, МVА | 10 | 3.7245 | 3.7245 |  |  | 3.7245 | 0 | 10.5 | 6.7755
| Nom. capacity LV, МVА | 10 | 2.11 | 0.6 | 24 hours | 1.51 | 0 | 10.5 | 8.99 |  |  |  | Nom. capacity LV, МVА | 10 | 1.465 | 3.575 | 0.6 | 24 hours | 2.975 | 0 | 10.5 | 7.525
150 | SS 35/10 Ermakovo | 1.6 | 0.83 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.04 | 0.04 | opened | 150 | SS 35/10 Ermakovo | 1.6 | 0.015 | 0.845 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.025 | 0.025 | opened
151 | SS 35/10 Milyushino | 1.6 | 0.72 | 0.32 | 24 hours | 0.32 | 0 | 0.32 | -0.4 | -0.4 | closed | 151 | SS 35/10 Milyushino | 1.6 |  | 0.72 | 0.32 | 24 hours | 0.32 | 0 | 0.32 | -0.4 | -0.4 | closed
152 | SS 35/10 Sutka | 2.5 | 0.6 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | -0.02 | -0.02 | closed | 152 | SS 35/10 Sutka | 2.5 | 0.01 | 0.61 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | -0.03 | -0.03 | closed
153 | SS 35/10 Sit | 1.6 | 0.53 | 0.44 | 24 hours | 0.44 | 0 | 0.44 | -0.09 | -0.09 | closed | 153 | SS 35/10 Sit | 1.6 | 0.0033 | 0.5333 | 0.44 | 24 hours | 0.44 | 0 | 0.44 | -0.0933 | -0.0933 | closed
154 | SS 35/10 Gorelovo | 1.6 | 0.38 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0.23 | 0.23 | opened | 154 | SS 35/10 Gorelovo | 1.6 | 0.235 | 0.615 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | -0.005 | -0.005 | closed
155 | SS 35/6 Pishchalkino | 1.6 | 0.94 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.74 | 0.74 | opened | 155 | SS 35/6 Pishchalkino | 1.6 |  | 0.94 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.74 | 0.74 | opened
156 | SS 35/6 Varegovo | 1.6 | 0.22 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.46 | 1.46 | opened | 156 | SS 35/6 Varegovo | 1.6 |  | 0.22 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.46 | 1.46 | opened
| Total: | 2610.2 | 869.07 | [8 empty] | 2: Total:; 3: 2610.2; 5: 1025.7123
| deficit | [8 empty] | -15.3 |  | 2: deficit; Мin. 12: -49.5142
| proficit | [8 empty] | 541 |  | 2: proficit; Мin. 12: 411.81

## тамбов
[9 empty] | table 1 | [13 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number in future providing that technical specifications at TS or other actions concerning reconstruction of main substation are fulfilled pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load at main substation , MVA | Total capacity distributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
SS 110 kv | [11 empty] | 1: SS 110 kv
1 | Tambovskaya No.2 | 40 + 25 | 18.55 | 0 |  | 18.55 | 0 | 26.25 | 7.7 | 7.7 | opened | 1 | Tambovskaya No.2 | 40 + 25 | 0 | 18.55 | 0 |  | 18.55 | 0 | 26.25 | 7.7 | 7.7 | opened
2 | Tambovskaya No.3 | 2*25 | 13.26 | 0 |  | 13.26 | 0 | 26.25 | 12.99 | 12.99 | opened | 2 | Tambovskaya No.3 | 2*25 | 0.4 | 13.66 | 0 |  | 13.66 | 0 | 26.25 | 12.59 | 12.59 | opened
3 | Tambovskaya No.5 | 16 + 12,5 | 13.77 | 0 |  | 13.77 | 0 | 13.125 | -0.645 | -0.645 | closed | 3 | Tambovskaya No.5 | 16 + 12,5 | 0.95 | 14.72 | 0 |  | 14.72 | 0 | 13.125 | -1.595 | -1.595 | closed
4 | Tambovskaya No.7 | 2*25 | 18.76 | 0 |  | 18.76 | 0 | 26.25 | 7.49 | 7.49 | opened | 4 | Tambovskaya No.7 | 2*25 | 0 | 18.76 | 0 |  | 18.76 | 0 | 26.25 | 7.49 | 7.49 | opened
5 | Pigment | 2*63 | 30.51 | 27.68 | 80 | 2.83 | 0 | 66.15 | 63.32 | 63.32 | opened | 5 | Pigment | 2*63 | 0 | 30.51 | 27.68 | 80 | 2.83 | 0 | 66.15 | 63.32 | 63.32 | opened
6 | Tambovskaya No.8 | 2*16 | 11.6 | 0 |  | 11.6 | 0 | 16.8 | 5.2 | 5.2 | opened | 6 | Tambovskaya No.8 | 2*16 | 0.7 | 12.3 | 0 |  | 12.3 | 0 | 16.8 | 4.5 | 4.5 | opened
7 | Malinovskaya | 2*40 | 11.5 | 4.75 | 120 | 6.75 | 0 | 42 | 35.25 | 35.25 | opened | 7 | Malinovskaya | 2*40 | 0 | 11.5 | 4.75 | 120 | 6.75 | 0 | 42 | 35.25 | 35.25 | opened
8 | Tambovskaya No.6 | 2*10 | 8.74 | 1.25 | 120 | 7.49 | 0 | 10.5 | 3.01 | 3.01 | opened | 8 | Tambovskaya No.6 | 2*10 | 0.22 | 8.96 | 1.25 | 120 | 7.71 | 0 | 10.5 | 2.79 | 2.79 | opened
9 | N.Lyadinskaya | 2*6,3 | 3.18 | 1.62 | 120 | 1.56 | 0 | 6.615 | 5.055 | 5.055 | opened | 9 | N.Lyadinskaya | 10+6,3 | 5.5 | 8.68 | 7.12 | 80 | 1.56 | 0 | 6.615 | 5.055 | 5.055 | opened
10 | Komsomolskaya | 2*10 | 7.24 | 4 | 80 | 3.24 | 0 | 10.5 | 7.26 | 7.26 | opened | 10 | Komsomolskaya | 2*10 | 0.17 | 7.41 | 4 | 80 | 3.41 | 0 | 10.5 | 7.09 | 7.09 | opened
11 | M.Talinskaya | 10 | 0.52 | 0.52 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 11 | M.Talinskaya | 10 | 5.39 | 5.91 | 5.91 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
12 | Promyshlennaya | 2*40 | 23.04 | 10.2 | 120 | 12.84 | 0 | 42 | 29.16 | 29.16 | opened | 12 | Promyshlennaya | 2*40 | 0.91 | 23.95 | 10.2 | 120 | 13.75 | 0 | 42 | 28.25 | 28.25 | opened
13 | Arzhenskaya | 2*10 | 3.92 | 3.92 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 13 | Arzhenskaya | 2*10 | 0 | 3.92 | 3.92 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
14 | Teleshovskaya | 2*2,5 | 0.56 | 0 |  | 0.56 | 0 | 2.625 | 2.065 | 2.065 | opened | 14 | Teleshovskaya | 2*2,5 | 0.58 | 1.14 | 0 |  | 1.14 | 0 | 2.625 | 1.485 | 1.485 | opened
15 | Oktyabrskaya | 2*25 | 6.11 | 0 |  | 6.11 | 0 | 26.25 | 20.14 | 20.14 | opened | 15 | Oktyabrskaya | 2*25 | 0 | 6.11 | 0 |  | 6.11 | 0 | 26.25 | 20.14 | 20.14 | opened
16 | Spasskaya | 2*6,3 | 1.97 | 0 |  | 1.97 | 0 | 6.615 | 4.645 | 4.645 | opened | 16 | Spasskaya | 2*6,3 | 0 | 1.97 | 0 |  | 1.97 | 0 | 6.615 | 4.645 | 4.645 | opened
17 | Kuzminskaya | 16+10 | 5.15 | 5.02 | 45 | 0.13 | 0 | 10.5 | 10.37 | 10.37 | opened | 17 | Kuzminskaya | 16+10 | 0 | 5.15 | 5.02 | 45 | 0.13 | 0 | 10.5 | 10.37 | 10.37 | opened
18 | Sampurskaya | 10+16 | 5.67 | 4.33 | 80 | 1.34 | 0 | 10.5 | 9.16 | 9.16 | opened | 18 | Sampurskaya | 10+16 | 0 | 5.67 | 4.33 | 80 | 1.34 | 0 | 10.5 | 9.16 | 9.16 | opened
19 | Tennery | 2*10 | 1.1 | 0 |  | 1.1 | 0 | 10.5 | 9.4 | 9.4 | opened | 19 | Tennery | 2*10 | 0 | 1.1 | 0 |  | 1.1 | 0 | 10.5 | 9.4 | 9.4 | opened
20 | Rasskazovskaya | 25+20 | 19.93 | 3.04 | 120 | 16.89 | 0 | 21 | 4.11 | 4.11 | opened | 20 | Rasskazovskaya | 25+20 | 0 | 19.93 | 3.04 | 120 | 16.89 | 0 | 21 | 4.11 | 4.11 | opened
21 | Volchkovskaya | 2*10 | 4.11 | 0.95 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened | 21 | Volchkovskaya | 2*10 | 0 | 4.11 | 0.95 | 120 | 3.16 | 0 | 10.5 | 7.34 | 7.34 | opened
22 | Staroyuryevskaya | 6,3+16 | 3.75 | 1.66 | 120 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened | 22 | Staroyuryevskaya | 6,3+16 | 0 | 3.75 | 1.66 | 120 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | opened
23 | Khmelevskaya | 2*10 | 1.6 | 0.92 | 120 | 0.68 | 0 | 10.5 | 9.82 | 9.82 | opened | 23 | Khmelevskaya | 2*10 | 0 | 1.6 | 0.92 | 120 | 0.68 | 0 | 10.5 | 9.82 | 9.82 | opened
24 | Khobotovskaya | 2*6,3 | 5.66 | 2.84 | 80 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 24 | Khobotovskaya | 2*6,3 | 0 | 5.66 | 2.84 | 80 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened
25 | Nikiforovskaya | 10+16 | 5.89 | 2.81 | 120 | 3.08 | 0 | 10.5 | 7.42 | 7.42 | opened | 25 | Nikiforovskaya | 10+16 | 0 | 5.89 | 2.81 | 120 | 3.08 | 0 | 10.5 | 7.42 | 7.42 | opened
26 | Novo-Seslavinskaya | 2.5 | 0.47 | 0.47 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 26 | Novo-Seslavinskaya | 2.5 | 0 | 0.47 | 0.47 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
27 | Nov. Arkhangelskaya | 2.5 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 27 | Nov. Arkhangelskaya | 2.5 | 0 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
28 | Ilovayskaya | 2*2,5 | 0.02 | 0 |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened | 28 | Ilovayskaya | 2*2,5 | 0 | 0.02 | 0 |  | 0.02 | 0 | 2.625 | 2.605 | 2.605 | opened
29 | Yuzhnaya | 16 | 8.51 | 8.51 | 120 | 0 | 0 | 16.8 | 16.8 | 16.8 | opened | 29 | Yuzhnaya | 16 | 0 | 8.51 | 8.51 | 120 | 0 | 0 | 16.8 | 16.8 | 16.8 | opened
30 | Pervomayskaya | 2*31,5 | 17.83 | 9.45 | 120 | 8.38 | 0 | 33.075 | 24.695 | 24.695 | opened | 30 | Pervomayskaya | 2*31,5 | 0.68 | 18.51 | 9.45 | 120 | 9.06 | 0 | 33.075 | 24.015 | 24.015 | opened
31 | Sosnovskaya | 2*16 | 6.6 | 6.6 | 80 | 0 | 0 | 16.8 | 16.8 | 16.8 | opened | 31 | Sosnovskaya | 2*16 | 0.27 | 6.87 | 6.6 | 80 | 0.27 | 0 | 16.8 | 16.53 | 16.53 | opened
32 | Pichaevskaya | 2*10 | 4.19 | 4.19 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 32 | Pichaevskaya | 2*10 | 0 | 4.19 | 4.19 | 80 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
33 | Algasovskaya | 2*40 | 2.99 | 2.9168 | 120 | 0.07322 | 0 | 42 | 41.9268 | 41.9268 | opened | 33 | Algasovskaya | 2*40 | 3.26 | 6.25 | 2.9168 | 120 | 3.3332 | 0 | 42 | 38.6668 | 38.6668 | opened
34 | Morshanskaya | 40+25 | 13.06 | 7.2005 | 120 | 5.8595 | 0 | 26.25 | 20.3905 | 20.3905 | opened | 34 | Morshanskaya | 40+25 | 0 | 13.06 | 7.2005 | 120 | 5.8595 | 0 | 26.25 | 20.3905 | 20.3905 | opened
35 | Kamvolnaya | 16+25 | 9.12 | 7.2 | 80 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened | 35 | Kamvolnaya | 16+25 | 0 | 9.12 | 7.2 | 80 | 1.92 | 0 | 16.8 | 14.88 | 14.88 | opened
36 | Grazhdanovskaya | 2*10 | 0.63 | 0.63 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 36 | Grazhdanovskaya | 2*10 | 0 | 0.63 | 0.63 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
37 | Nashchekinskaya | 2*10 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 37 | Nashchekinskaya | 2*10 | 0 | 2.05 | 2.05 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
38 | Shachinskaya | 2.5 | 0.05 | 0.054495 | 120 | -0.004495 | 0 | 2.625 | 2.6295 | 2.6295 | opened | 38 | Shachinskaya | 2.5 | 1.18 | 1.23 | 1.23 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
39 | Uvarovskaya | 16+16 | 9.46 | 9.027 | 45 | 0.43301 | 0 | 16.8 | 16.367 | 16.367 | opened | 39 | Uvarovskaya | 16+16 | 0 | 9.46 | 9.027 | 45 | 0.43301 | 0 | 16.8 | 16.367 | 16.367 | opened
40 | Muchkapskaya | 2*10 | 3.77 | 1.3519 | 120 | 2.4181 | 0 | 10.5 | 8.0819 | 8.0819 | opened | 40 | Muchkapskaya | 2*10 | 0 | 3.77 | 1.3519 | 120 | 2.4181 | 0 | 10.5 | 8.0819 | 8.0819 | opened
41 | M.Alabushskaya | 2*2,5 | 0.71 | 0.66667 | 120 | 0.043333 | 0 | 2.625 | 2.5817 | 2.5817 | opened | 41 | M.Alabushskaya | 2*2,5 | 0 | 0.71 | 0.66667 | 120 | 0.043333 | 0 | 2.625 | 2.5817 | 2.5817 | opened
42 | M.Gorkovskaya | 10+16 | 1.4 | 1.2921 | 120 | 0.10795 | 0 | 10.5 | 10.3921 | 10.3921 | opened | 42 | M.Gorkovskaya | 10+16 | 0 | 1.4 | 1.2921 | 120 | 0.10795 | 0 | 10.5 | 10.3921 | 10.3921 | opened
43 | Shpikulovskaya | 2*2,5 | 0.67 | 0.61404 | 120 | 0.055965 | 0 | 2.625 | 2.569 | 2.569 | opened | 43 | Shpikulovskaya | 2*2,5 | 0.19 | 0.86 | 0.61404 | 120 | 0.24596 | 0 | 2.625 | 2.379 | 2.379 | opened
44 | Zherdevskaya | 2*16 | 6.32 | 5.6533 | 80 | 0.66675 | 0 | 16.8 | 16.1333 | 16.1333 | opened | 44 | Zherdevskaya | 2*16 | 0 | 6.32 | 5.6533 | 80 | 0.66675 | 0 | 16.8 | 16.1333 | 16.1333 | opened
45 | Rzhaksinskaya | 2*10 | 4.52 | 0.58824 | 120 | 3.9318 | 0 | 10.5 | 6.5682 | 6.5682 | opened | 45 | Rzhaksinskaya | 2*10 | 0 | 4.52 | 0.58824 | 120 | 3.9318 | 0 | 10.5 | 6.5682 | 6.5682 | opened
46 | Bogdanovskaya | 2*2,5 | 0.47 | 0.42105 | 120 | 0.048947 | 0 | 2.625 | 2.5761 | 2.5761 | opened | 46 | Bogdanovskaya | 2*2,5 | 0 | 0.47 | 0.42105 | 120 | 0.048947 | 0 | 2.625 | 2.5761 | 2.5761 | opened
47 | Tokarevskaya | 2*25 | 7.54 | 6.0846 | 120 | 1.4554 | 0 | 26.25 | 24.7946 | 24.7946 | opened | 47 | Tokarevskaya | 2*25 | 0 | 7.54 | 6.0846 | 120 | 1.4554 | 0 | 26.25 | 24.7946 | 24.7946 | opened
48 | Zveryaevskaya | 6,3+10 | 1.02 | 0.90918 | 120 | 0.11082 | 0 | 6.615 | 6.5042 | 6.5042 | opened | 48 | Zveryaevskaya | 6,3+10 | 0 | 1.02 | 0.90918 | 120 | 0.11082 | 0 | 6.615 | 6.5042 | 6.5042 | opened
49 | Mordovskaya | 2*10 | 4.41 | 1.8937 | 120 | 2.5163 | 0 | 10.5 | 7.9837 | 7.9837 | opened | 49 | Mordovskaya | 2*10 | 0 | 4.41 | 1.8937 | 120 | 2.5163 | 0 | 10.5 | 7.9837 | 7.9837 | opened
50 | Pavlovskaya | 10 | 1.56 | 1.56 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 50 | Pavlovskaya | 10 | 0 | 1.56 | 1.56 | 120 | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
51 | Kirsanovskaya | 2*25 | 13.09 | 5.989 | 120 | 7.101 | 0 | 26.25 | 19.149 | 19.149 | opened | 51 | Kirsanovskaya | 2*25 | 0 | 13.09 | 5.989 | 120 | 7.101 | 0 | 26.25 | 19.149 | 19.149 | opened
52 | Inzhavinskaya | 2*16 | 7.92 | 3.41 | 120 | 4.51 | 0 | 16.8 | 12.29 | 12.29 | opened | 52 | Inzhavinskaya | 2*16 | 0.2 | 8.12 | 3.41 | 120 | 4.71 | 0 | 16.8 | 12.09 | 12.09 | opened
53 | Umyotskaya | 2*10 | 4.9 | 4.5 | 80 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | opened | 53 | Umyotskaya | 2*10 | 0 | 4.9 | 4.5 | 80 | 0.4 | 0 | 10.5 | 10.1 | 10.1 | opened
54 | Kovylskaya | 2*10 | 1.97 | 1.347 | 120 | 0.623 | 0 | 10.5 | 9.877 | 9.877 | opened | 54 | Kovylskaya | 2*10 | 0 | 1.97 | 1.347 | 120 | 0.623 | 0 | 10.5 | 9.877 | 9.877 | opened
55 | Inokovskaya | 2.5 | 0.18 | 0.184 | 120 | -0.004 | 0 | 2.625 | 2.629 | 2.629 | opened | 55 | Inokovskaya | 2.5 | 0 | 0.18 | 0.184 | 120 | -0.004 | 0 | 2.625 | 2.629 | 2.629 | opened
SS 35 kv | [11 empty] | 1: SS 35 kv
56 | Pervomayskaya | 2*2,5 | 1.94 | 0 |  | 1.94 | 0 | 2.625 | 0.685 | 0.685 | opened | 56 | Pervomayskaya | 2*2,5 | 0 | 1.94 | 0 |  | 1.94 | 0 | 2.625 | 0.685 | 0.685 | opened
57 | Picherskaya | 2*2,5 | 0.45 | 0 |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened | 57 | Picherskaya | 2*2,5 | 0 | 0.45 | 0 |  | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
58 | Osinovskaya | 2*2,5 | 0.88 | 0 |  | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened | 58 | Osinovskaya | 2*2,5 | 0 | 0.88 | 0 |  | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
59 | Koptevskaya | 2*2,5 | 0.19 | 0 |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 59 | Koptevskaya | 2*2,5 | 0 | 0.19 | 0 |  | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
60 | Sayukinskaya | 2*2,5 | 0.5 | 0.5 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 60 | Sayukinskaya | 2*2,5 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
61 | Zelyonaya | 2*4 | 2 | 0 |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened | 61 | Zelyonaya | 2*4 | 0 | 2 | 0 |  | 2 | 0 | 4.2 | 2.2 | 2.2 | opened
62 | Pyatiletka | 2*4 | 0.27 | 0 |  | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened | 62 | Pyatiletka | 2*4 | 0 | 0.27 | 0 |  | 0.27 | 0 | 4.2 | 3.93 | 3.93 | opened
63 | Yaroslavskaya | 2*2,5 | 0.92 | 0 |  | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened | 63 | Yaroslavskaya | 2*2,5 | 0 | 0.92 | 0 |  | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
64 | Platonovskaya | 2*6,3 | 3.06 | 0.24 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened | 64 | Platonovskaya | 2*6,3 | 0 | 3.06 | 0.24 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened
65 | Znamenskaya | 4+6,3 | 2.49 | 1.54 | 120 | 0.95 | 0 | 4.2 | 3.25 | 3.25 | opened | 65 | Znamenskaya | 4+6,3 | 0.3 | 2.79 | 1.54 | 120 | 1.25 | 0 | 4.2 | 2.95 | 2.95 | opened
66 | Sukhotinskaya | 2.5 | 0.35 | 0 |  | 0.35 | 0 | 0 | -0.35 | -0.35 | closed | 66 | Sukhotinskaya | 2*2,5 | 0 | 0.35 | 0 |  | 0.35 | 0 | 0 | -0.35 | -0.35 | closed
67 | P.Marfinskaya | 2,5+1,6 | 0.98 | 0 |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened | 67 | P.Marfinskaya | 2,5+1,6 | 0 | 0.98 | 0 |  | 0.98 | 0 | 1.68 | 0.7 | 0.7 | opened
68 | Aleksandrovskaya | 1,6+2,5 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 68 | Aleksandrovskaya | 1,6+2,5 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
69 | Stepnaya | 2*4 | 1.7 | 1.7 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 69 | Stepnaya | 2*4 | 0 | 1.7 | 1.7 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
70 | Ivanovskaya | 2*4 | 0.97 | 0.97 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 70 | Ivanovskaya | 2*4 | 0 | 0.97 | 0.97 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
71 | verkhotsenskaya | 2,5+1,6 | 0.47 | 0.47 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 71 | verkhotsenskaya | 2,5+1,6 | 0 | 0.47 | 0.47 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
72 | Gorelskaya | 4+6,3 | 1.71 | 1.71 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 72 | Gorelskaya | 4+6,3 | 0 | 1.71 | 1.71 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
73 | B.Dvoynyovskaya | 2*2,5 | 0.62 | 0 |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 73 | B.Dvoynyovskaya | 2*2,5 | 0 | 0.62 | 0 |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
74 | Avangardskaya | 2*2,5 | 0.34 | 0 |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened | 74 | Avangardskaya | 2*2,5 | 0 | 0.34 | 0 |  | 0.34 | 0 | 2.625 | 2.285 | 2.285 | opened
75 | Suravskaya | 1,6+2,5 | 0.45 | 0.45 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 75 | Suravskaya | 1,6+2,5 | 0 | 0.45 | 0.45 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
76 | Seleznzyovskaya | 4+4+6,3 | 3.6 | 0 |  | 3.6 | 0 | 8.4 | 4.8 | 4.8 | opened | 76 | Seleznzyovskaya | 4+4+6,3 | 0.75 | 4.35 | 0 |  | 4.35 | 0 | 8.4 | 4.05 | 4.05 | opened
77 | Chernyanskaya | 1,6+2,5 | 1.3 | 0.68 | 80 | 0.62 | 0 | 0.68 | 0.06 | 0.06 | opened | 77 | Chernyanskaya | 1,6+2,5 | 0 | 1.3 | 0.68 | 80 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | opened
78 | Viktorskaya | 2.5 | 0.57 | 0 |  | 0.57 | 0 | 0 | -0.57 | -0.57 | closed | 78 | Viktorskaya | 2.5 | 0 | 0.57 | 0 |  | 0.57 | 0 | 0 | -0.57 | -0.57 | closed
79 | Novoseltsevskaya | 2*1,6 | 0.61 | 0 |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | opened | 79 | Novoseltsevskaya | 2*1,6 | 0 | 0.61 | 0 |  | 0.61 | 0 | 1.68 | 1.07 | 1.07 | opened
80 | Avdeevskaya | 2*2,5 | 0.72 | 0 |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened | 80 | Avdeevskaya | 2*2,5 | 0 | 0.72 | 0 |  | 0.72 | 0 | 2.625 | 1.905 | 1.905 | opened
81 | Tatanovskaya | 2*2,5 | 2.14 | 0 |  | 2.14 | 0 | 2.625 | 0.485 | 0.485 | opened | 81 | Tatanovskaya | 2*2,5 | 0.11 | 2.25 | 0 |  | 2.25 | 0 | 2.625 | 0.375 | 0.375 | opened
82 | Timiryazevskaya | 2,5+2,5+4 | 3.02 | 0.63 | 60 | 2.39 | 0 | 5.25 | 2.86 | 2.86 | opened | 82 | Timiryazevskaya | 2,5+2,5+4 | 0 | 3.02 | 0.63 | 60 | 2.39 | 0 | 5.25 | 2.86 | 2.86 | opened
83 | P.Prigorodnaya | 2*4 | 5.38 | 0 |  | 5.38 | 0 | 4.2 | -1.18 | -1.18 | closed | 83 | P.Prigorodnaya | 2*4 | 0.44 | 5.82 | 0 |  | 5.82 | 0 | 4.2 | -1.62 | -1.62 | closed
84 | Bokinskaya | 2*6,3 | 3.04 | 0.92 | 30 | 2.12 | 0 | 6.615 | 4.495 | 4.495 | opened | 84 | Bokinskaya | 2*6,3 | 0.43 | 3.47 | 0.92 | 30 | 2.55 | 0 | 6.615 | 4.065 | 4.065 | opened
85 | Stolovskaya | 4 | 0.52 | 0.52 | 50 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 85 | Stolovskaya | 4 | 0 | 0.52 | 0.52 | 50 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
86 | Tulinovskaya | 2*2,5 | 1.32 | 0 |  | 1.32 | 0 | 2.625 | 1.305 | 1.305 | opened | 86 | Tulinovskaya | 2*2,5 | 0.35 | 1.67 | 0 |  | 1.67 | 0 | 2.625 | 0.955 | 0.955 | opened
87 | Serebryakovskaya | 2*1,6 | 1.09 | 0 |  | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened | 87 | Serebryakovskaya | 2*1,6 | 0 | 1.09 | 0 |  | 1.09 | 0 | 1.68 | 0.59 | 0.59 | opened
88 | B.Doroga | 2*1,6 | 0.34 | 0.34 | 60 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 88 | B.Doroga | 2*1,6 | 0 | 0.34 | 0.34 | 60 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
89 | B.Izberdeevskaya | 2*2,5 | 0.62 | 0 |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened | 89 | B.Izberdeevskaya | 2*2,5 | 0 | 0.62 | 0 |  | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
90 | Vishnevskaya | 2*2,5 | 0.37 | 0.26 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 90 | Vishnevskaya | 2*2,5 | 0 | 0.37 | 0.26 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
91 | Vyrubovskaya | 2*2,5 | 0.32 | 0.32 | 50 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 91 | Vyrubovskaya | 2*2,5 | 0 | 0.32 | 0.32 | 50 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
92 | Glazkovskaya | 2*4 | 0.82 | 0.71 | 120 | 0.11 | 0 | 4.2 | 4.09 | 4.09 | opened | 92 | Glazkovskaya | 2*4 | 0 | 0.82 | 0.71 | 120 | 0.11 | 0 | 4.2 | 4.09 | 4.09 | opened
93 | Dmitirievskaya | 2*2,5 | 0.09 | 0 |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 93 | Dmitirievskaya | 2*2,5 | 0 | 0.09 | 0 |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
94 | Donskaya | 6.3 | 3.65 | 3.65 | 120 | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 94 | Donskaya | 6.3 | 0 | 3.65 | 3.65 |  | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
95 | Druzhba | 2.5 | 0.16 | 0.16 | 120 | 0 | 0 | 0 | 0 | 0 | opened | 95 | Druzhba | 2.5 | 0 | 0.16 | 0.16 | 120 | 0 | 0 | 0 | 0 | 0 | opened
96 | Ekaterininskaya | 2*2,5 | 0.35 | 0.23 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 96 | Ekaterininskaya | 2*2,5 | 0 | 0.35 | 0.23 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
97 | Zhidilovskaya | 2,5+1,6 | 0.33 | 0.25 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened | 97 | Zhidilovskaya | 2,5+1,6 | 0 | 0.33 | 0.25 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened
98 | Izosimovskaya | 6,3+2,5 | 1.28 | 1.08 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 98 | Izosimovskaya | 6,3+2,5 | 0 | 1.28 | 1.08 | 80 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened
99 | KIM | 2,5+4 | 0.86 | 0.74 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 99 | KIM | 2,5+4 | 0 | 0.86 | 0.74 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
100 | Klenskaya | 2*2,5 | 0.23 | 0.22 | 120 | 0.01 | 0 | 2.625 | 2.615 | 2.615 | opened | 100 | Klenskaya | 2*2,5 | 0.38 | 0.61 | 0.22 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
101 | Kozmodemyanovskaya | 2*2,5 | 0.82 | 0.6 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 101 | Kozmodemyanovskaya | 2*2,5 | 0 | 0.82 | 0.6 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
102 | Komintern | 2*2,5 | 0.26 | 0.22 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 102 | Komintern | 2*2,5 | 0.39 | 0.65 | 0.22 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
103 | Kochetovskaya | 6.3 | 0.2 | 0.2 | 120 | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 103 | Kochetovskaya | 6.3 | 0 | 0.2 | 0.2 | 120 | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
104 | Nov.Vasilyevskaya | 2*2,5 | 0.14 | 0.14 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 104 | Nov.Vasilyevskaya | 2*2,5 | 0 | 0.14 | 0.14 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
105 | Nov.Tarbeevskaya | 2.5 | 0.85 | 0.66 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 105 | Nov.Tarbeevskaya | 2.5 | 0 | 0.85 | 0.66 | 120 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened
106 | Nov.Yuryevskaya | 2*1,6 | 0.34 | 0.28 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened | 106 | Nov.Yuryevskaya | 2*1,6 | 0 | 0.34 | 0.28 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | opened
107 | Petrovskaya | 2*4 | 2.88 | 1.2 | 120 | 1.68 | 0 | 4.2 | 2.52 | 2.52 | opened | 107 | Petrovskaya | 2*4 | 0 | 2.88 | 1.2 | 120 | 1.68 | 0 | 4.2 | 2.52 | 2.52 | opened
108 | Prigorodnaya | 2*5,6 | 0.71 | 0.62 | 120 | 0.09 | 0 | 5.88 | 5.79 | 5.79 | opened | 108 | Prigorodnaya | 2*5,6 | 0 | 0.71 | 0.62 | 120 | 0.09 | 0 | 5.88 | 5.79 | 5.79 | opened
109 | Progress | 2*10 | 8.49 | 0 |  | 8.49 | 0 | 10.5 | 2.01 | 2.01 | opened | 109 | Progress | 2*10 | 0 | 8.49 | 0 |  | 8.49 | 0 | 10.5 | 2.01 | 2.01 | opened
110 | Raninskaya | 1.6 | 0.32 | 0.32 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 110 | Raninskaya | 1.6 | 0 | 0.32 | 0.32 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
111 | Rakhmaninskaya | 2*1,6 | 0.19 | 0 |  | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened | 111 | Rakhmaninskaya | 2*1,6 | 0 | 0.19 | 0 |  | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened
112 | Saburovskaya | 2*2,5 | 1.99 | 0 |  | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened | 112 | Saburovskaya | 2*2,5 | 0 | 1.99 | 0 |  | 1.99 | 0 | 2.625 | 0.635 | 0.635 | opened
113 | Sestryonskaya | 1.6 | 0.49 | 0 |  | 0.49 | 0 | 0 | -0.49 | -0.49 | closed | 113 | Sestryonskaya | 1.6 | 0 | 0.49 | 0 |  | 0.49 | 0 | 0 | -0.49 | -0.49 | closed
114 | Sitovskaya | 1.6 | 0.5 | 0.5 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 114 | Sitovskaya | 1.6 | 0 | 0.5 | 0.5 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
115 | Skobelevskaya | 1.6 | 0.24 | 0.24 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 115 | Skobelevskaya | 1.6 | 0 | 0.24 | 0.24 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
116 | Ustyinskaya | 2.5 | 1.06 | 1.06 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 116 | Ustyinskaya | 2.5 | 0 | 1.06 | 1.06 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
117 | Yurlovskaya | 2*2,5 | 0.41 | 0 |  | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened | 117 | Yurlovskaya | 2*2,5 | 0 | 0.41 | 0 |  | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened
118 | Yablonovetskaya | 2*2,5 | 0.7 | 0 |  | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 118 | Yablonovetskaya | 2*2,5 | 0 | 0.7 | 0 |  | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
119 | Agroprom | 2*4 | 1.42 | 0 |  | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened | 119 | Agroprom | 2*4 | 0 | 1.42 | 0 |  | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened
120 | Alekseevskaya | 1,6+2,5 | 0.34 | 0 |  | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened | 120 | Alekseevskaya | 1,6+2,5 | 0 | 0.34 | 0 |  | 0.34 | 0 | 1.68 | 1.34 | 1.34 | opened
121 | Vanovskaya | 2*2,5 | 0.07 | 0.07 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 121 | Vanovskaya | 2*2,5 | 0 | 0.07 | 0.07 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
122 | Vyazhlinskaya | 1.8 | 1.04 | 0.81 | 80 | 0.23 | 0 | 1.89 | 1.66 | 1.66 | opened | 122 | Vyazhlinskaya | 1.8 | 0 | 1.04 | 0.81 | 80 | 0.23 | 0 | 1.89 | 1.66 | 1.66 | opened
123 | Kryukovskaya | 2*2,5 | 0.66 | 0.6593 | 120 | 0.000697 | 0 | 2.625 | 2.6243 | 2.6243 | opened | 123 | Kryukovskaya | 2*2,5 | 0 | 0.66 | 0.6593 | 120 | 0.000697 | 0 | 2.625 | 2.6243 | 2.6243 | opened
124 | Lugovaya | 4 | 0.95 | 0.94977 | 120 | 0.00023 | 0 | 4.2 | 4.1998 | 4.1998 | opened | 124 | Lugovaya | 4 | 0 | 0.95 | 0.94977 | 120 | 0.00023 | 0 | 4.2 | 4.1998 | 4.1998 | opened
125 | Lyubvinskaya | 2*2,5 | 0.15 | 0.1467 | 120 | 0.003296 | 0 | 2.625 | 2.6217 | 2.6217 | opened | 125 | Lyubvinskaya | 2*2,5 | 0 | 0.15 | 0.1467 | 120 | 0.003296 | 0 | 2.625 | 2.6217 | 2.6217 | opened
126 | Morshanskaya | 2*4 | 2.29 | 0 |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | opened | 126 | Morshanskaya | 2*4 | 0 | 2.29 | 0 |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | opened
127 | Piterskaya | 2.5 | 0.93 | 0.93 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 127 | Piterskaya | 2.5 | 0 | 0.93 | 0.93 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
128 | Rakshinskaya | 2*4 | 1.62 | 1.6137 | 80 | 0.006256 | 0 | 4.2 | 4.1937 | 4.1937 | opened | 128 | Rakshinskaya | 2*4 | 0 | 1.62 | 1.6137 | 80 | 0.006256 | 0 | 4.2 | 4.1937 | 4.1937 | opened
129 | Rybinskaya | 2*2,5 | 1.05 | 1.0536 | 80 | -0.00357 | 0 | 2.625 | 2.6286 | 2.6286 | opened | 129 | Rybinskaya | 2*2,5 | 0 | 1.05 | 1.0536 | 80 | -0.00357 | 0 | 2.625 | 2.6286 | 2.6286 | opened
130 | Serpovskaya | 2*2,5 | 0.7 | 0.7 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 130 | Serpovskaya | 2*2,5 | 0 | 0.7 | 0.7 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
131 | St.Tomnikovskaya | 1 | 0.09 | 0.092555 | 120 | -0.002555 | 0 | 1.05 | 1.0526 | 1.0526 | opened | 131 | St.Tomnikovskaya | 1 | 0 | 0.09 | 0.092555 | 120 | -0.002555 | 0 | 1.05 | 1.0526 | 1.0526 | opened
132 | Chernitovskaya | 2.5 | 0.4 | 0.39963 | 120 | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened | 132 | Chernitovskaya | 2.5 | 0 | 0.4 | 0.39963 | 120 | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened
133 | Bondarskaya | 2*2,5 | 0.93 | 0.93 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 133 | Bondarskaya | 2*2,5 | 0.43 | 1.36 | 0.93524 | 80 | 0.42476 | 0 | 2.625 | 2.2002 | 2.2002 | opened
134 | Vernadovskaya | 2,5+1,6 | 0.53 | 0.53457 | 80 | -0.00457 | 0 | 1.68 | 1.6846 | 1.6846 | opened | 134 | Vernadovskaya | 2,5+1,6 | 0 | 0.53 | 0.53457 | 80 | -0.00457 | 0 | 1.68 | 1.6846 | 1.6846 | opened
135 | Gagarinskaya | 2,5+1,6 | 0.15 | 0.14532 | 120 | 0.00468 | 0 | 1.68 | 1.6753 | 1.6753 | opened | 135 | Gagarinskaya | 2,5+1,6 | 0.27 | 0.42 | 0.14532 | 120 | 0.27468 | 0 | 1.68 | 1.4053 | 1.4053 | opened
136 | Egorovskaya | 2,5+3,2 | 0.71 | 0.71276 | 120 | -0.00276 | 0 | 2.625 | 2.6278 | 2.6278 | opened | 136 | Egorovskaya | 2,5+3,2 | 0 | 0.71 | 0.71276 | 120 | -0.00276 | 0 | 2.625 | 2.6278 | 2.6278 | opened
137 | Kershinskaya | 1,6+2,5 | 0.15 | 0 |  | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 137 | Kershinskaya | 1,6+2,5 | 0 | 0.15 | 0 |  | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
138 | Kurovshchinskaya | 2*1,6 | 0.05 | 0.054495 | 120 | -0.004495 | 0 | 1.68 | 1.6845 | 1.6845 | opened | 138 | Kurovshchinskaya | 2*1,6 | 0 | 0.05 | 0.054495 | 120 | -0.004495 | 0 | 1.68 | 1.6845 | 1.6845 | opened
139 | Lipovskaya | 2.5 | 0.27 | 0.26988 | 120 | 0.00012 | 0 | 2.625 | 2.6249 | 2.6249 | opened | 139 | Lipovskaya | 2.5 | 0 | 0.27 | 0.26988 | 120 | 0.00012 | 0 | 2.625 | 2.6249 | 2.6249 | opened
140 | Lomovisskaya | 3,2+2,5 | 0.11 | 0.11 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 140 | Lomovisskaya | 3,2+2,5 | 0 | 0.11 | 0.11 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
141 | Mitropolskaya | 2.5 | 0.28 | 0.28 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 141 | Mitropolskaya | 2.5 | 0.11 | 0.39 | 0.28 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
142 | P.Uglovskaya | 1.6 | 0.35 | 0.35292 | 120 | -0.00292 | 0 | 1.68 | 1.6829 | 1.6829 | opened | 142 | P.Uglovskaya | 1.6 | 0 | 0.35 | 0.35292 | 120 | -0.00292 | 0 | 1.68 | 1.6829 | 1.6829 | opened
143 | Rudovskaya | 2*2,5 | 0.52 | 0 |  | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened | 143 | Rudovskaya | 2*2,5 | 1.18 | 1.7 | 1.18 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
144 | V.yaroslavskaya | 2.5 | 0.23 | 0.23 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 144 | V.yaroslavskaya | 2.5 | 0 | 0.23 | 0.23 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
145 | Degtyanskaya | 2.5 | 0.9 | 0.9 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 145 | Degtyanskaya | 2.5 | 0 | 0.9 | 0.9 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
146 | Zelenaya | 1.6 | 0.18 | 0.17992 | 120 | 8e-05 | 0 | 1.68 | 1.6799 | 1.6799 | opened | 146 | Zelenaya | 1.6 | 0 | 0.18 | 0.17992 | 120 | 8e-05 | 0 | 1.68 | 1.6799 | 1.6799 | opened
147 | Kulevatovskaya | 2*4 | 1.81 | 1.81 | 80 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 147 | Kulevatovskaya | 2*4 | 0.11 | 1.92 | 1.8165 | 80 | 0.1035 | 0 | 4.2 | 4.0965 | 4.0965 | opened
148 | Lamskaya | 4+2,5 | 0.2 | 0.20362 | 120 | -0.003621 | 0 | 2.625 | 2.6286 | 2.6286 | opened | 148 | Lamskaya | 4+2,5 | 0 | 0.2 | 0.20362 | 120 | -0.003621 | 0 | 2.625 | 2.6286 | 2.6286 | opened
149 | Gryaznovskaya | 2*2,5 | 0.09 | 0 |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 149 | Gryaznovskaya | 2*2,5 | 0 | 0.09 | 0 |  | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened
150 | Otyasskaya | 2*2,5 | 0.4 | 0.39963 | 120 | 0.00037 | 0 | 2.625 | 2.6246 | 2.6246 | opened | 150 | Otyasskaya | 2*2,5 | 0.16 | 0.56 | 0.39963 | 120 | 0.16037 | 0 | 2.625 | 2.4646 | 2.4646 | opened
151 | P.Vasilyevskaya | 1.6 | 0.19 | 0.1903 | 120 | -0.0003 | 0 | 1.68 | 1.6803 | 1.6803 | opened | 151 | P.Vasilyevskaya | 1.6 | 0 | 0.19 | 0.1903 | 120 | -0.0003 | 0 | 1.68 | 1.6803 | 1.6803 | opened
152 | Podlesnaya | 2*2,5 | 0.42 | 0.41935 | 120 | 0.000648 | 0 | 2.625 | 2.6244 | 2.6244 | opened | 152 | Podlesnaya | 2*2,5 | 0 | 0.42 | 0.41935 | 120 | 0.000648 | 0 | 2.625 | 2.6244 | 2.6244 | opened
153 | Tr.Roslyayskaya | 2*2,5 | 0.38 | 0.38146 | 120 | -0.001465 | 0 | 2.625 | 2.6265 | 2.6265 | opened | 153 | Tr.Roslyayskaya | 2*2,5 | 0 | 0.38 | 0.38146 | 120 | -0.001465 | 0 | 2.625 | 2.6265 | 2.6265 | opened
154 | Zherdevskaya | 10 | 2.51 | 2.25 | 45 | 0.26 | 0 | 10.5 | 10.24 | 10.24 | opened | 154 | Zherdevskaya | 10 | 0 | 2.51 | 2.25 | 45 | 0.26 | 0 | 10.5 | 10.24 | 10.24 | opened
155 | Sukmanovskaya | 2*2,5 | 0.16 | 0 |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 155 | Sukmanovskaya | 2*2,5 | 0 | 0.16 | 0 |  | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
156 | Tugolukovskaya | 2,5+4 | 0.29 | 0.29 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 156 | Tugolukovskaya | 2,5+4 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
157 | Artemovskaya | 2*2,5 | 0.39 | 0.35 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 157 | Artemovskaya | 2*2,5 | 0 | 0.39 | 0.35 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
158 | RSKhO | 2,5+4 | 1.29 | 1.16 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened | 158 | RSKhO | 2,5+4 | 0 | 1.29 | 1.16 | 80 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
159 | Maksimovskaya | 2*1,6 | 0.2 | 0.18 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened | 159 | Maksimovskaya | 2*1,6 | 0 | 0.2 | 0.18 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened
160 | Burnakskaya | 5,6+6,3 | 1.9 | 0 |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened | 160 | Burnakskaya | 5,6+6,3 | 0 | 1.9 | 0 |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | opened
161 | Poletaevskaya | 2*4 | 0.22 | 0.19 | 120 | 0.03 | 2.18 | 4.2 | 1.99 | 1.99 | opened | 161 | Poletaevskaya | 2*4 | 0 | 0.22 | 0.19 | 120 | 0.03 | 2.18 | 4.2 | 1.99 | 1.99 | opened
162 | T.Roslyayskaya | 2*4 | 0.98 | 0 |  | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 162 | T.Roslyayskaya | 2*4 | 0 | 0.98 | 0 |  | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened
163 | Pioner | 1,6+2,5 | 1.24 | 0.72 | 60 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened | 163 | Pioner | 1,6+2,5 | 0 | 1.24 | 0.72 | 60 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
164 | Lvovskaya | 2*2,5 | 0.53 | 0.47 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened | 164 | Lvovskaya | 2*2,5 | 0 | 0.53 | 0.47 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
165 | Nadezhdinskaya | 1.6 | 0.28 | 0.28 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 165 | Nadezhdinskaya | 1.6 | 0 | 0.28 | 0.28 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
166 | Kuleshovskaya | 2.5 | 0.26 | 0.26 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 166 | Kuleshovskaya | 2.5 | 0 | 0.26 | 0.26 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
167 | Chernyaevskaya | 4+2,5 | 1.49 | 0 |  | 1.49 | 0 | 2.625 | 1.135 | 1.135 | opened | 167 | Chernyaevskaya | 4+2,5 | 0 | 1.49 | 0 |  | 1.49 | 0 | 2.625 | 1.135 | 1.135 | opened
168 | Ivanovskaya | 2*2,5 | 0.33 | 0 |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 168 | Ivanovskaya | 2*2,5 | 0 | 0.33 | 0 |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
169 | Shulginskaya | 2*4 | 1 | 0.02 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened | 169 | Shulginskaya | 2*4 | 0 | 1 | 0.02 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened
170 | Lavrovskaya | 2*2,5 | 0.14 | 0 |  | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 170 | Lavrovskaya | 2*2,5 | 0 | 0.14 | 0 |  | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened
171 | N.Sergievskaya | 3.2 | 0.49 | 0.49 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 171 | N.Sergievskaya | 3.2 | 0 | 0.49 | 0.49 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
172 | Kamenskaya | 2*2,5 | 0.31 | 0 |  | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened | 172 | Kamenskaya | 2*2,5 | 0 | 0.31 | 0 |  | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
173 | Protasovskaya | 4+2,5 | 0.33 | 0 |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened | 173 | Protasovskaya | 4+2,5 | 0 | 0.33 | 0 |  | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
174 | Chakinskaya | 4 | 0.37 | 0 |  | 0.37 | 0 | 0 | -0.37 | -0.37 | closed | 174 | Chakinskaya | 4 | 0 | 0.37 | 0 |  | 0.37 | 0 | 0 | -0.37 | -0.37 | closed
175 | Lukinskaya | 2.5 | 0.22 | 0.22 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 175 | Lukinskaya | 2.5 | 0 | 0.22 | 0.22 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
176 | Zolotovskaya | 2.5 | 0.37 | 0.37 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 176 | Zolotovskaya | 2.5 | 0 | 0.37 | 0.37 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
177 | Mozdokskaya | 2.5 | 0.2 | 0 |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed | 177 | Mozdokskaya | 2.5 | 0 | 0.2 | 0 |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed
178 | Oblovskaya | 2*2,5 | 0.69 | 0.65 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened | 178 | Oblovskaya | 2*2,5 | 0 | 0.69 | 0.65 | 120 | 0.04 | 0 | 2.625 | 2.585 | 2.585 | opened
179 | V.Vershinskaya | 2,5+4 | 0.35 | 0.07 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 179 | V.Vershinskaya | 2,5+4 | 0 | 0.35 | 0.07 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
180 | Luchevskaya | 2,5+1,6 | 0.14 | 0 |  | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened | 180 | Luchevskaya | 2,5+1,6 | 0 | 0.14 | 0 |  | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
181 | Olshanskaya | 4+2,5 | 1.12 | 0.32 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 181 | Olshanskaya | 4+2,5 | 0 | 1.12 | 0.32 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
182 | Pavlodarskaya | 2.5 | 0.1 | 0.1 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 182 | Pavlodarskaya | 2.5 | 0 | 0.1 | 0.1 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
183 | Berezovskaya | 2*2,5 | 0.22 | 0 |  | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 183 | Berezovskaya | 2*2,5 | 0 | 0.22 | 0 |  | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
184 | K.Zvezdinskaya | 2*1,6 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 184 | K.Zvezdinskaya | 2*1,6 | 0 | 0.29 | 0.29 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
185 | Prudkovskaya | 1,6+2,5 | 0.24 | 0 |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened | 185 | Prudkovskaya | 1,6+2,5 | 0 | 0.24 | 0 |  | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
186 | Shapkinskaya | 2*4 | 0.86 | 0 |  | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 186 | Shapkinskaya | 2*4 | 0 | 0.86 | 0 |  | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
187 | Maryinskaya | 2*1,6 | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened | 187 | Maryinskaya | 2*1,6 | 0 | 0.25 | 0.25 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
188 | Irskaya | 1,6+2,5 | 0.37 | 0.345 | 120 | 0.025 | 0 | 1.68 | 1.655 | 1.655 | opened | 188 | Irskaya | 1,6+2,5 | 0 | 0.37 | 0.345 | 120 | 0.025 | 0 | 1.68 | 1.655 | 1.655 | opened
189 | Zavodskaya | 2*4 | 1.25 | 1.25 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 189 | Zavodskaya | 2*4 | 0 | 1.25 | 1.25 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
190 | Kalaisskaya | 2.5 | 0.58 | 0.58 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 190 | Kalaisskaya | 2.5 | 0.27 | 0.85 | 0.58 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened
191 | Sokolovskaya | 2*2,5 | 1.02 | 1.02 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 191 | Sokolovskaya | 2*2,5 | 1.55 | 2.57 | 2.57 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
192 | Veterinarnaya | 2.5 | 0.13 | 0.13 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 192 | Veterinarnaya | 2.5 | 0 | 0.13 | 0.13 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
193 | Glukhovskaya | 2.5 | 0.09 | 0.09 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 193 | Glukhovskaya | 2.5 | 0 | 0.09 | 0.09 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
194 | Orzhevskaya | 2.5 | 0.47 | 0.47 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 194 | Orzhevskaya | 2.5 | 0.22 | 0.69 | 0.69 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
195 | Umyotskaya | 2*4 | 1.54 | 1.54 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened | 195 | Umyotskaya | 2*4 | 0 | 1.54 | 1.54 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
196 | Gavrilovskaya | 2*4 | 1.07 | 0.996 | 120 | 0.074 | 0 | 4.2 | 4.126 | 4.126 | opened | 196 | Gavrilovskaya | 2*4 | 0 | 1.07 | 0.996 | 120 | 0.074 | 0 | 4.2 | 4.126 | 4.126 | opened
197 | Peresypkinskaya | 2*2,5 | 0.76 | 0.76 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 197 | Peresypkinskaya | 2*2,5 | 0 | 0.76 | 0.76 | 80 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
198 | Annenskaya | 2*2,5 | 0.87 | 0.806 | 80 | 0.064 | 0 | 2.625 | 2.561 | 2.561 | opened | 198 | Annenskaya | 2*2,5 | 1.55 | 2.42 | 2.356 | 80 | 0.064 | 0 | 2.625 | 2.561 | 2.561 | opened
199 | Filatovskaya | 2*2,5 | 0.33 | 0.33 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 199 | Filatovskaya | 2*2,5 | 0 | 0.33 | 0.33 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
200 | Nikitenskaya | 2,5+1,6 | 0.15 | 0.135 | 120 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | opened | 200 | Nikitenskaya | 2,5+1,6 | 0 | 0.15 | 0.135 | 120 | 0.015 | 0 | 1.68 | 1.665 | 1.665 | opened
201 | Balykleyskaya | 2*2,5 | 0.49 | 0.414 | 120 | 0.076 | 0 | 2.625 | 2.549 | 2.549 | opened | 201 | Balykleyskaya | 2*2,5 | 0 | 0.49 | 0.414 | 120 | 0.076 | 0 | 2.625 | 2.549 | 2.549 | opened
202 | Karavainskaya | 2*1,6 | 0.58 | 0.548 | 80 | 0.032 | 0 | 1.68 | 1.648 | 1.648 | opened | 202 | Karavainskaya | 2*1,6 | 0 | 0.58 | 0.548 | 80 | 0.032 | 0 | 1.68 | 1.648 | 1.648 | opened
203 | PTF | 2*2,5 |  | 0 |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 203 | PTF | 2*2,5 | 0 | 0 | 0 |  | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
204 | Pavlovskaya | 3.2 | 0.28 | 0.28 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 204 | Pavlovskaya | 3.2 | 0.22 | 0.5 | 0.5 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
| Total: | 2383.4 | 485.91 | [8 empty] | 2: Total:; 3: 2397.1; 5: 515.73
| deficit | [8 empty] | -3.805 |  | 2: deficit; Мин. 12: -5.195
| proficit | [8 empty] | 989.307 |  | 2: proficit; Мин. 12: 975.8942

## Свод.ожид.деф.
List of closed main sustations of IDGC of Centre, JSC according to expected loads including new powers on technologocal connection and another development of electric grid complex.
No. | Object of main substation, voltage class | Expected deficit / proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, МVА
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | Tambovskaya No.5 | 16 + 12,5 | 0.95 | 14.72 | 0 |  | 14.72 | 0 | 13.125 | -1.595 | -1.595 | closed
2 | Sukhotinskaya | 2*2,5 | 0 | 0.35 | 0 |  | 0.35 | 0 | 0 | -0.35 | -0.35 | closed
3 | Viktoriya | 2.5 | 0 | 0.57 | 0 |  | 0.57 | 0 | 0 | -0.57 | -0.57 | closed
4 | P.Prigorodnaya | 2*4 | 0.44 | 5.82 | 0 |  | 5.82 | 0 | 4.2 | -1.62 | -1.62 | closed
5 | Sestryonskaya | 1.6 | 0 | 0.49 | 0 |  | 0.49 | 0 | 0 | -0.49 | -0.49 | closed
6 | Chakinskaya | 4 | 0 | 0.37 | 0 |  | 0.37 | 0 | 0 | -0.37 | -0.37 | closed
7 | Mozdokskaya | 2.5 | 0 | 0.2 | 0 |  | 0.2 | 0 | 0 | -0.2 | -0.2 | closed
| Total: | [9 empty] | -5.195
yarenergo
1 | SS 35/10 Vatolino | 2,5+4,0 |  | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -0.85 | closed
2 | SS 35/10 Volna | 2,5+2,5 | 0.2 | 3.26 |  |  | 3.26 | 0 | 2.63 | -0.63 | -0.63 | closed
3 | SS 35/6 Zavolzhskaya | 10+10 | 1.8815 | 12.1915 |  |  | 12.1915 | 0 | 10.5 | -1.6915 | -1.6915 | closed
4 | SS 110/6 Institutskaya | 40+40 | 4.6946 | 42.2246 |  |  | 42.2246 | 0 | 42 | -0.22459 | -0.22459 | closed
5 | SS 35/10 Nekrasovo | 10+10 | 0.432 | 12.102 |  |  | 12.102 | 0 | 10.5 | -1.602 | -1.602 | closed
6 | SS 110/35/6 Pavlovskaya | 20+25 | 8.5515 | 25.2515 |  |  | 25.2515 | 0 | 21 | -4.2515 | -4.2515 | closed
| Nom. capacity MV, МVА | 20+25 | 8.5515 | 8.5515 |  |  | 8.5515 | 0 | 21 | 12.4485
| Nom. capacity LV, МVА | 20+25 |  | 16.7 |  |  | 16.7 | 0 | 21 | 4.3
7 | SS 110/6 Poligraf | 40+40 | 5.3149 | 51.2249 |  |  | 51.2249 | 0 | 42 | -9.2249 | -9.2249 | closed
8 | SS 35/10 Preventorium | 2,5+2,5 | 2.027 | 3.237 | 0.39 | 120 | 2.847 | 0 | 2.63 | -0.217 | -0.217 | closed
9 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.01 | 6.84 |  |  | 6.84 | 0 | 6.62 | -0.22 | -0.22 | closed
10 | SS 110/10 Chayka | 25+25 | 23.7523 | 39.9523 |  |  | 39.9523 | 0 | 26.25 | -13.7023 | -13.7023 | closed
11 | SS 110/6 Kinoplyonka | 6,3+10 | 0.587 | 10.157 |  |  | 10.157 | 0 | 6.62 | -3.537 | -3.537 | closed
12 | SS 110/35/10 Nila | 6,3+6,3 | 7.5755 | 9.3555 | 0.37 | 120 | 8.9855 | 0 | 6.62 | -2.3655 | -2.3655 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 6.9215 | 6.9215 |  |  | 6.9215 | 0 | 6.62 | -0.3015
| Nom. capacity LV, МVА | 6,3+6,3 | 0.654 | 2.434 | 0.37 | 120 | 2.064 | 0 | 6.62 | 4.556
13 | SS 110/35/6 Pereslavl | 25+25 | 14.4054 | 27.9154 |  |  | 27.9154 | 0 | 26.25 | -1.6654 | -1.6654 | closed
| Nom. capacity MV, МVА | 25+25 | 14.0704 | 14.0704 |  |  | 14.0704 | 0 | 26.25 | 12.1796
| Nom. capacity LV, МVА | 25+25 | 0.335 | 13.845 |  |  | 13.845 | 0 | 26.25 | 12.405
14 | SS 110/35/10 Rostov | 25+20 | 3.4781 | 21.7981 |  |  | 21.7981 | 0 | 21 | -0.7981 | -0.7981 | closed
| Nom. Capacity MV, МVА | 25+20 | 1.8878 | 1.8878 |  |  | 1.8878 | 0 | 21 | 19.1122
| Nom. capacity LV, МVА | 25+20 | 1.5903 | 19.9103 |  |  | 19.9103 | 0 | 21 | 1.0897
15 | SS 110/35/10 Uglich | 25+25 | 25.538 | 30.568 |  |  | 30.568 | 0 | 26.25 | -4.318 | -4.318 | closed
| Nom. capacity MV, МVА | 25+25 | 24.798 | 24.798 |  |  | 24.798 | 0 | 26.25 | 1.452
| Nom. capacity LV, МVА | 25+25 | 0.74 | 5.77 |  |  | 5.77 | 0 | 26.25 | 20.48
16 | SS 35/10 Glebovo | 2,5+2,5 | 1.645 | 4.405 |  |  | 4.405 | 0 | 2.63 | -1.775 | -1.775 | closed
17 | SS 35/10 Kibernetik | 2,5+2,5 | 0.273 | 2.723 |  |  | 2.723 | 0 | 2.63 | -0.093 | -0.093 | closed
18 | SS 35/10 Krasnoe | 4+2,5 | 2.193 | 3.283 | 0.3 | 120 | 2.983 | 0 | 2.63 | -0.353 | -0.353 | closed
19 | SS 35/6 Kupan | 2,5+2,5 | 0.35 | 2.93 |  |  | 2.93 | 0 | 2.63 | -0.3 | -0.3 | closed
20 | SS 35/10 Saraevo | 1+1,6 | 0.63 | 1.47 |  |  | 1.47 | 0 | 1.05 | -0.42 | -0.42 | closed
21 | SS 35/10 Semibratovo | 4+4 | 0.1156 | 0.8956 | 0.25 | 120 | 0.25 | 0 | 0.25 | -0.6456 | -0.6456 | closed
22 | SS 35/6 Pribrezhnaya | 10+10 |  | 11.28 |  |  | 11.28 | 0 | 10.5 | -0.78 | -0.78 | closed
23 | SS 35/10 Breytovo | 4+4 | 0.561 | 4.481 |  |  | 4.481 | 0 | 4.2 | -0.281 | -0.281 | closed
24 | SS 35/10 Milyushino | 1.6 |  | 0.72 | 0.32 | 1 сутки | 0.32 | 0 | 0.32 | -0.4 | -0.4 | closed
25 | SS 35/10 Sutka | 2.5 | 0.01 | 0.61 | 0.58 | 1 сутки | 0.58 | 0 | 0.58 | -0.03 | -0.03 | closed
26 | SS 35/10 Sit | 1.6 | 0.0033 | 0.5333 | 0.44 | 1 сутки | 0.44 | 0 | 0.44 | -0.0933 | -0.0933 | closed
27 | SS 35/10 Gorelovo | 1.6 | 0.235 | 0.615 | 0.61 | 1 сутки | 0.61 | 0 | 0.61 | -0.005 | -0.005 | closed
| Total: | [9 empty] | -50.4737
kostromaenergo
1 | Sukhonogovo 35/10 kv | 3,2+4 | 1.962 | 3.922 | 0 | 0 | 3.922 | 0 | 3.36 | -0.562 | -0.562 | Change of transformers is provided
2 | Vostochnaya-2 110/35/10 kv | 25+25 | 5.846 | 39.506 | 0.02 | 120 | 39.486 | 0 | 26.25 | -13.236 | -13.236 | Load is transferred to new SS Davydovskaya
| Nom. capacity MV, МVА | 25+25 | 0 | 21.51 | 0 | 120 | 21.51 | 0 | 26.25 | 4.74
| Nom. capacity LV, МVА | 25+25 | 5.85 | 18 | 0.02 | 120 | 17.98 | 0 | 26.25 | 8.27
3 | Kostroma-1 110/6 kv | 10+10 | 1.935 | 12.015 | 0 | 0 | 12.015 | 0 | 10.5 | -1.515 | -1.515 | Change of transformers is provided
4 | Severnaya 110/6 kv | 20+25 | 6.82 | 24.72 | 0 | 0 | 24.72 | 0 | 21 | -3.72 | -3.72 | Change of transformers is provided
5 | Tsentralnaya 110/10/6 kv | 25+25 | 14.673 | 30.303 | 0 | 0 | 30.303 | 0 | 26.25 | -4.053 | -4.053 | Change of transformers is provided
6 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 2.381 | 21.821 | 0 | 0 | 21.821 | 0 | 17.115 | -4.706 | -4.706 | Transition to 110 kv with change of transformers is provided
7 | SM State District Power Station 110/35/6 kv | 10+16 | 4.034 | 10.784 | 0 | 0 | 10.784 | 0 | 10.5 | -0.284 | -0.284 | Change of transformers is provided
| Nom. capacity MV, МVА | 10+16 | 0 | 0.71 | 0 | 120 | 0.71 | 0 | 10.5 | 9.79
| Nom. capacity LV, МVА | 10+16 | 4.03 | 10.07 | 0 | 120 | 10.07 | 0 | 10.5 | 0.43
8 | Buy (r) 110/35/10 kv | 4+10 | 12.611 | 13.511 | 0 | 0 | 13.511 | 0 | 4.2 | -9.311 | -9.311 | Change of transformers is provided
| Nom. capacity MV, МVА | 4+10 | 12.61 | 13.51 | 0 | 120 | 13.51 | 0 | 4.2 | -9.31
| Nom. capacity LV, МVА | 4+10 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2
| Total: | [9 empty] | -37.387
lipetskenergo
1 | SS 110/10kv Lev Tolstoy | 10 | 0.05 | 2.4142 | 1 | 30 | 1 | 0 | 1 | -1.4142 | -1.4142 | closed
2 | SS 110/10 kv Dvurechki | 6.3 | 0.114 | 2.7609 | 0.31 | 120 | 0.31 | 0 | 0.31 | -2.4509 | -2.4509 | closed
4 | SS 35/10 kv Kr.Palna | 3.2 | 0.15 | 1.0507 | 0.5 | 120 | 0.5 | 0 | 0.5 | -0.55067 | -0.55067 | closed
5 | SS 35/10 kv Kamenka | 2.5 | 0.5 | 1.1426 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.77259 | -0.77259 | closed
8 | SS 35/10 kv Pankratovka | 2.5 |  | 0.61834 | 0.37 | 120 | 0.37 | 0 | 0.37 | -0.24834 | -0.24834 | closed
9 | SS 35/10 kv Preobrazhenye | 2.5 |  | 0.41154 | 0.4 | 1 сутки | 0.4 | 0 | 0.4 | -0.011535 | -0.011535 | closed
10 | SS 35/10 kv Yakovlevo | 2.5 |  | 0.71603 | 0.37 | 1 сутки | 0.37 | 0 | 0.37 | -0.34603 | -0.34603 | closed
12 | SS 35/10 kv Pervomayskaya | 2.5 |  | 0.73439 | 0.25 | 90 | 0.25 | 0 | 0.25 | -0.48439 | -0.48439 | closed
13 | SS 35/10 kv Kamennaya Lubna | 2.5 |  | 0.81839 | 0.75 | 90 | 0.75 | 0 | 0.75 | -0.068394 | -0.068394 | closed
14 | SS 35/10 kv Znamenka | 2.5 | 0.045 | 0.89977 | 0.75 | 1 сутки | 0.75 | 0 | 0.75 | -0.14977 | -0.14977 | closed
15 | SS 35/6 kv Novonikolaevka | 4 |  | 0.69027 | 0.6 | 120 | 0.6 | 0 | 0.6 | -0.09027 | -0.09027 | closed
16 | SS 35/10 kv Sindyakino | 2.5 | 0.02 | 0.96458 | 0.2 | 60 | 0.2 | 0 | 0.2 | -0.76458 | -0.76458 | closed
17 | SS 35/10 kv Novodubovoe | 2.5 | 0.011 | 0.55803 | 0.5 | 60 | 0.5 | 0 | 0.5 | -0.058026 | -0.058026 | closed
18 | SS 35/10 kv Beryozovka | 2.5 |  | 1.1444 | 0.75 | 120 | 0.75 | 0 | 0.75 | -0.39439 | -0.39439 | closed
19 | SS 35/6kv Vostochnaya | 10+16 | 0.0796 | 13.1306 | 1 | 120 | 12.1306 | 0 | 10.5 | -1.6306 | -1.6306 | closed
20 | SS 35/10 kv Zadonsk-selsk. | 3,2+1,6 | 0.082 | 2.2024 | 0 | 0 | 2.2024 | 0 | 1.68 | -0.52238 | -0.52238 | closed
21 | SS 35/10 kv Khitrovo | 6,3+6,3 |  | 0.77734 | 0 | 0 | 0.77734 | 0 |  | -0.77734 | -0.77734 | closed
22 | SS 35/6 kv SS No. 5 | 6,3+3,2 |  | 1.149 | 0 | 0 | 1.149 | 0 |  | -1.149 | -1.149 | closed
23 | SS 35/10 kv Gagarino | 1,8+1,8 |  | 0.45466 | 0.36 | 120 | 0.094663 | 0 |  | -0.094663 | -0.094663 | closed
24 | SS 35/10 kv Butyrki | 5,6+4 | 0.6 | 6.3765 | 0.4 | 120 | 5.9765 | 0 | 4.2 | -1.7765 | -1.7765 | closed
25 | SS 35/10 kv Borisovka | 4+2,5 | 0.56 | 3.3029 | 0.37 | 120 | 2.9329 | 0 | 2.625 | -0.30791 | -0.30791 | closed
26 | SS 110/35/6 kv Bugor | 15+15+25 |  | 33.772 | 0.5 |  | 33.272 | 0 | 26.25 | -7.022 | -7.022 | closed
| Nom. capacity MV, МVА | 15+15+25 |  | 9.8 | 0 | 0 | 9.8 | 0 | 26.25 | 16.45
| Nom. capacity LV, МVА | 15+15+25 | 2.972 | 23.972 | 0.5 | 40 | 23.472 | 0 | 26.25 | 2.778
27 | SS 110/35/6 kv Tsementnaya | 63+32+20 |  | 29.3754 | 0 |  | 29.3754 | 0 | 54.6 | 25.2246 | -1.836 | closed
| Nom. capacity MV, МVА | 63+20 |  | 22.836 | 0 | 0 | 22.836 | 0 | 21 | -1.836
| Nom. capacity LV, МVА | 63+32+20 |  | 6.5394 | 0 | 30 | 6.5394 | 0 | 54.6 | 48.0606
28 | SS 110/35/10/60 kv Gidrooborudovanie | 25+25+31,5 |  | 7.3051 | 10 |  | -2.6949 | 0 | 52.5 | 45.1949 | -3.7368 | closed
| Nom. capacity MV, МVА | 31.5 |  | 3.7368 | 5 | 10 | -1.2632 | 0 | 0 | -3.7368
| Nom. capacity LV, МVА | 25+25+31,5 | 0.45 | 3.5683 | 5 | 120 | -1.4317 | 0 | 52.5 | 48.9317
29 | SS 110/35/10 kv Chaplygin | 7,5+6,3 |  | 8.7427 | 0.63 |  | 8.1127 | 0 | 6.62 | -1.4927 | -1.4927 | closed
| Nom. capacity MV, МVА | 7,5+6,3 |  | 3.1177 | 0 | 0 | 3.1177 | 0 | 6.62 | 3.5023
| Nom. capacity LV, МVА | 7,5+6,3 | 0.15 | 5.625 | 0.63 | 120 | 4.995 | 0 | 6.62 | 1.625
30 | SS 110/6 kv Privokzalnaya | 20+20+25 | 0.354 | 43.7943 | 1.38 | 30 | 42.4143 | 0 | 42 | -0.4143 | -0.4143 | closed
| Total: | [9 empty] | -28.5644
belgorodenergo
1 | SS-35/10kv Afanasyevka | 1.6 | 0 | 0.70565 | 0.6464 | 45 | 0.059246 | 0 | 0.6464 | -0.059246 | -0.059246 | closed
2 | SS-35/10kv Borisy | 1.6 | 0 | 0.51253 | 0 | 20 | 0.51253 | 0 | 0 | -0.51253 | -0.51253 | closed
3 | SS-35/10kv Kazachya Lisitsa | 2.5 | 0 | 0.38773 | 0 |  | 0.38773 | 0 | 0 | -0.38773 | -0.38773 | closed
4 | SS-35/10kv Kamyzino | 2.5 | 0 | 1.1346 | 0.541 | 45 | 0.59359 | 0 | 0.541 | -0.59359 | -0.59359 | closed
5 | SS-35/10kv Nikolskoe | 4 | 0 | 1.6697 | 0.78 | 120 | 0.88968 | 0 | 0.78 | -0.88968 | -0.88968 | closed
6 | SS-35/10kv Pyatnitskoe | 4 | 0 | 2.4286 | 1.84 | 80 | 0.58861 | 0 | 1.84 | -0.58861 | -0.58861 | closed
7 | SS-35/10kv Tserkovnaya | 2.5 | 0.18 | 1.3075 | 1 | 80 | 0.30755 | 0 | 1 | -0.30755 | -0.30755 | closed
8 | SS-110/35/10kv Alexeevka | 25+16+25 | 0 | 44.0632 | 0 | 120 | 44.0632 | 0 | 43.05 | -1.0132 | -1.0132 | closed
| Sн. MV, МVА | 25+16+25 | 0 | 19.821 | 0 |  | 19.821 | 0 | 43.05 | 23.229
| Sн. LV, МVА | 25+16+25 | 0 | 24.2422 | 0 |  | 24.2422 | 0 | 43.05 | 18.8078
9 | SS-110/6kv Belgorod-1 | 40+48 | 4.372 | 48.8901 | 0 | 120 | 48.8901 | 0 | 42 | -6.8901 | -6.8901 | closed
10 | SS-110/10kv Zapadnaya | 16+16 | 2.825 | 19.7725 | 1.249 | 80 | 18.5235 | 0 | 16.8 | -1.7235 | -1.7235 | closed
11 | SS-35/10kv Alexeevka (kor.) | 2,5+4 | 0 | 2.7122 | 0 |  | 2.7122 | 0 | 2.625 | -0.087197 | -0.087197 | closed
12 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 0.004 | 8.1316 | 0.872 | 80 | 7.2596 | 0 | 6.615 | -0.64461 | -0.64461 | closed
| TOTAL: | [9 empty] | -13.6976
bryanskenergo
1 | Bezhitskaya | 25+40 |  | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed
2 | Gorodishchenskaya | 16+16 | 0.226 | 25.786 | 1.5 | 12 час | 24.286 | 0 | 16.8 | -7.486 | -7.486 | closed
3 | Dormashevskaya | 40+63 | 4.3 | 43.81 | 0 | 0 | 43.81 | 0 | 42 | -1.81 | -1.81 | closed
| Nom. capacity MV, МVА | 40+63 |  | 20.72 | 0 | 0 | 20.72 | 0 | 42 | 21.28
| Nom. capacdity LV, МVА | 40+63 | 4.3 | 23.09 | 0 | 0 | 23.09 | 0 | 42 | 18.91
4 | Dyadkovskaya | 25+25 |  | 36.72 | 8.9 | 12 час | 27.82 | 0 | 26.25 | -1.57 | -1.62 | closed
| Nom. capacity MV, МВА | 25+25 |  | 8.85 | 8.9 | 12 час | -0.05 | 0 | 26.25 | 17.4
| Nom. capacity LV, МVА | 25+25 |  | 27.87 | 0 | 0 | 27.87 | 0 | 26.25 | -1.62
5 | Kamvolnaya | 16+25 | 0.134 | 17.224 | 0 | 0 | 17.224 | 0 | 16.8 | -0.424 | -0.424 | closed
6 | Karachizhskaya | 10+10 | 0.173 | 18.453 | 0 | 0 | 18.453 | 0 | 10.5 | -7.953 | -7.953 | yes
7 | Mamonovskaya | 10+16 |  | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed
8 | Yuzhnaya | 16+25 |  | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed
9 | Volodarskaya | 10+6,3 |  | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.515 | -4.515 | closed
10 | Gorodskaya | 10+10 |  | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -0.38 | -0.38 | closed
11 | Seshcha 6 kv | 1,6+4 |  | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed
| Total: | [9 empty] | -40.248
smolenskenergo
1 | Merlino 110/35/10 | 6.3 | 0.47 | 0.85 | 0.54 | 1 сутки | 0.31 | 0 | 0.54 | -0.31 | -0.31 | closed
| Nom. capacity MV, МVА | 6.3 | 0.44 | 0.44 | 0.44 |  | 0 | 0 | 0.44 | 0
| Nom. capacity LV, МVА | 6.3 | 0.03 | 0.28 | 0.1 | 1 сутки | 0.18 | 0 | 0.1 | -0.18
2 | Vasino 35/10 | 2.5 | 0 | 0.34 | 0 | 1 сутки | 0.34 | 0 | 0 | -0.34 | -0.34 | closed
3 | Avrora 35/10 | 2.5 | 2 | 2.14 | 0.68 | 1 сутки | 1.46 | 0 | 0.68 | -1.46 | -1.46 | closed
4 | Mytishino 35/10 | 1.6 | 0 | 0.09 | 0 | 1 сутки | 0.09 | 0 | 0 | -0.09 | -0.09 | closed
5 | Ekimtsevo 110/10 | 2.5 | 2.22 | 2.42 | 1.73 | 1 сутки | 0.69 | 0 | 1.73 | -0.69 | -0.69 | closed
6 | Water intake 35/6 | 4+4 | 4.62 | 7.97 | 1.2 | 120 | 6.77 | 0 | 4.2 | -2.57 | -2.57 | closed
7 | Diffuzion 110/6 | 25+25 | 16.87 | 30.97 | 1.06 | 120 | 29.91 | 0 | 26.25 | -3.66 | -3.66 | closed
8 | Yasennaya 35/6 | 6,3+10 | 0.98 | 12.19 | 0 | 120 | 12.19 | 0 | 6.615 | -5.575 | -5.575 | closed
9 | Zapadnaya 110/6 | 25+16 | 9.71 | 22.7 | 0.63 | 120 | 22.07 | 0 | 16.8 | -5.27 | -5.27 | closed
10 | Katyn 1 35/10 | 4+4 | 2.81 | 4.44 | 0.05 | 120 | 4.39 | 0 | 4.2 | -0.19 | -0.19 | closed
11 | Kozino 110/35/10 | 10+10 | 4.71 | 13.99 | 3.22 | 120 | 10.77 | 0 | 10.5 | -0.27 | -0.27 | closed
| Nom. capacity MV, МVА | 10+10 | 3.6 | 9.87 | 3.21 |  | 6.66 | 0 | 10.5 | 3.84
| Nom. capacity LV, МVА | 10+10 | 1.11 | 4.12 | 0.01 | 120 | 4.11 | 0 | 10.5 | 6.39
12 | Kolodnya 35/6 | 6,3+4 | 0.61 | 4.29 | 0 | 120 | 4.29 | 0 | 4.2 | -0.09 | -0.09 | closed
13 | Chernushki 110/10/6 | 25+25 | 10.07 | 31.07 | 2.12 | 120 | 28.95 | 0 | 26.25 | -2.7 | -2.7 | closed
| Nom. capacity MV, МVА | 25+25 | 5.07 | 12.36 | 0 |  | 12.36 | 0 | 26.25 | 13.89
| Nom. capacity LV, МVА | 25+25 | 5 | 18.71 | 2.12 | 120 | 16.59 | 0 | 26.25 | 9.66
14 | Yuzhnaya 110/35/6 | 40+40 | 20.86 | 67.44 | 22.16 | 120 | 45.28 | 0 | 42 | -3.28 | -3.28 | closed
| Nom. capacity MV, МVА | 40+40 | 1.53 | 16.44 | 16.44 |  | 0 | 0 | 42 | 42
| Nom. capacdity LV, МVА | 40+40 | 19.33 | 51 | 5.72 | 120 | 45.28 | 0 | 42 | -3.28
15 | Zhukovskaya 35/10 | 4+4 | 2.36 | 4.4 | 0.19 | 120 | 4.21 | 0 | 4.2 | -0.01 | -0.01 | closed
16 | Kamenka 35/10 | 2,5+2,5 | 0.96 | 3.28 | 0.42 | 120 | 2.86 | 0 | 2.625 | -0.235 | -0.235 | closed
17 | Belei 35/10 | 2,5+2,5 | 3.39 | 5.16 | 0.75 | 120 | 4.41 | 0 | 2.625 | -1.785 | -1.785 | closed
18 | Igorevskaya 110/10 | 10+10 | 1.75 | 11.22 | 0 | 120 | 11.22 | 0 | 10.5 | -0.72 | -0.72 | closed
19 | Kholm-Zhirki 35/10 | 2,5+4 | 0.52 | 3.6 | 0.4 | 120 | 3.2 | 0 | 2.625 | -0.575 | -0.575 | closed
20 | Industrialnaya 110/35/6 | 16+16 | 10.93 | 15.78 | 0.51 | 120 | 15.27 | 0 | 16.8 | 1.53 | -4.035 | closed
| Nom. capacity MV, МVА | 16,3+5,3 | 0 | 0.51 | 0.51 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 10.93 | 15.27 | 0 | 120 | 15.27 | 0 | 11.235 | -4.035
21 | Beryozka 35/10 | 4+4 | 3.93 | 4.54 | 0 | 120 | 4.54 | 0 | 4.2 | -0.34 | -0.34 | closed
22 | Flour mill 35/10 | 10+10 | 6.03 | 12.79 | 0.13 | 120 | 12.66 | 0 | 10.5 | -2.16 | -2.16 | closed
23 | Vyazma 2 110/10 | 16+16 | 4.47 | 17.86 | 0 | 120 | 17.86 | 0 | 16.8 | -1.06 | -1.06 | closed
24 | Gagarin 110/35/10 | 25+25 | 8.57 | 33.57 | 6.82 | 120 | 26.75 | 0 | 26.25 | -0.5 | -0.5 | closed
| Nom. capacity MV, МVА | 25+25 | 2.74 | 7.69 | 5.1 |  | 2.59 | 0 | 26.25 | 23.66
| Nom. capacity LV, МVА | 25+25 | 5.83 | 25.88 | 1.72 | 120 | 24.16 | 0 | 26.25 | 2.09
| Total: | [9 empty] | -37.915
tverenergo
1 | SS Borisovskoe 35/10 kv | 1 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed
2 | SS Ivanovo 110/35/10 kv | 6.3 | 0.3363 | 1.3363 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | -0.0363 | -1.1363 | MS is closed
| Nom. capacity MV, МVА | 6.3 | 0.3363 | 1.1363 | 0 | 1 сутки | 0 | 0 | 0 | -1.1363
| Nom. capacity LV, МVА | 6.3 | 0 | 0.2 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | 1.1
3 | SS Kesma 110/35/10 kv | 6.3 | 0 | 1 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.4 | -0.2 | MS is closed
| Nom. capacidty MV, МVА | 6.3 | 0 | 0.2 | 0 | 1 сутки | 0 | 0 | 0 | -0.2
| Nom. capacity LV, МVА | 6.3 | 0 | 0.8 | 1.4 | 1 сутки | 1.4 | 0 | 1.4 | 0.6
4 | SS Morkiny Gory 110/35/10 kv | 5.6 | 0 | 0.4 | 1.2 | 1 сутки | 1.2 | 0 | 1.2 | 0.8 | -0.2 | MS is closed
| Nom. capacity СН, МВА | 5.6 | 0 | 0.2 | 0 | 1 сутки | 0 | 0 | 0 | -0.2
| Nom. capacity LV, МVА | 5.6 | 0 | 0.2 | 1.2 | 1 сутки | 1.2 | 0 | 1.2 | 1
5 | SS Belsky Karyer 35/6 kv | 4 | 0 | 0.08 | 0.01 | 1 сутки | 0.01 | 0 | 0.01 | -0.07 | -0.07 | MS is closed
6 | SS Zhilotkovo 35/10 kv | 1.8 | 0 | 0.19 | 0 |  | 0 | 0 | 0 | -0.19 | -0.19 | MS is closed
7 | SS Luzhnikovo 35/10 kv | 2.5 | 0 | 0.102 | 0.1 | 1 сутки | 0.1 | 0 | 0.1 | -0.002 | -0.002 | MS is closed
8 | SS Nasakino 35/10 kv | 0.56 | 0 | 0.05 | 0 |  | 0 | 0 | 0 | -0.05 | -0.05 | MS is closed
9 | SS Porozhki 35/10 kv | 1 | 0.0491 | 0.4791 | 0.43 | 1 сутки | 0.43 | 0 | 0.43 | -0.0491 | -0.0491 | MS is closed
10 | SS KhBK 35/6 kv | 4 | 0 | 2.7 | 0.9 | 1 сутки | 0.9 | 0 | 0.9 | -1.8 | -1.8 | MS is closed
11 | SS DOZ 35/10 kv | 4+4 | 0 | 6.205 | 0 |  | 6.205 | 0 | 4.2 | -2.005 | -2.005 | MS is closed
12 | 35/10 kv Kalyazin | 6,3 +6,3 | 0.1363 | 7.2841 | 0 |  | 7.2841 | 0 | 6.615 | -0.66914 | -0.66914 | MS is closed
13 | 35/10 kv Mayak | 6,3 +6,3 | 3.467 | 6.9365 | 0 |  | 6.9365 | 0 | 6.615 | -0.32151 | -0.32151 | MS is closed
14 | 110/35/10 kv Luch | 16,0+16,0 | 1.5431 | 18.2632 | 0 |  | 18.2632 | 0 | 16.8 | -1.4632 | -1.4632 | MS is closed
| Nom. capacity MV, МVА | 16,0+16,0 | 0.4566 | 13.4506 | 0 |  | 13.4506 | 0 | 16.8 | 3.3494
| Nom. capacity LV, МVА | 16,0+16,0 | 1.0865 | 4.8126 | 0 |  | 4.8126 | 0 | 16.8 | 11.9874
15 | SS 35/10 kv Glazomichi | 2.5 | 0 | 0.1 | 0 |  | 0 | 0 | 0 | -0.1 | -0.1 | MS is closed
16 | SS 35/10 kv Zharki | 10 | 0.138 | 2.338 | 0 |  | 0 | 0 | 0 | -2.338 | -2.338 | MS is closed
17 | SS 110/10 kv Monino | 6.3 | 0.165 | 1.465 | 1 | 1сутки | 1 | 0 | 1 | -0.465 | -0.465 | MS is closed
18 | SS 35/10 kv Ozerets | 1.6 | 0 | 0.2 | 0 |  | 0 | 0 | 0 | -0.2 | -0.2 | MS is closed
19 | SS 35/10 kv Ulin | 1.6 | 0 | 0.3 | 0 |  | 0 | 0 | 0 | -0.3 | -0.3 | MS is closed
20 | SS 110/35/10 kv Andreapol | 10+10 | 5.2542 | 12.2042 | 0.7 | 120 | 11.5042 | 0 | 10.5 | -1.0042 | -1.0042 | MS is closed
| Nom. capacity MV, МVА | 10+10 | 0.39 | 1.14 | 0 |  | 1.14 | 0 | 10.5 | 9.36
| Nom. capacity LV, МVА | 10+10 | 4.8642 | 11.0642 | 0.7 | 120 | 10.3642 | 0 | 10.5 | 0.1358
21 | SS Pyatnitskoe 35/10kv | 2.5 | 0.03 | 0.21165 | 0.18165 | 240 | 0.18165 | 0 | 0.18165 | -0.03 | -0.03 | MS is closed
22 | SS Karamzino 35/10kv | 1.6 | 0 | 0.3633 | 0 |  | 0 | 0 | 0 | -0.3633 | -0.3633 | MS is closed
23 | SS Kn.Gory 35/10kv | 2.5 | 0.5 | 1.7715 | 0.23333 | 240 | 0.23333 | 0 | 0.23333 | -1.5382 | -1.5382 | MS is closed
24 | SS Salino 35/10kv | 2.5 | 0.25 | 0.6998 | 0 |  | 0 | 0 | 0 | -0.6998 | -0.6998 | MS is closed
25 | SS Mol.Tud 35/10kv | 2.5 | 0.015 | 0.46913 | 0.45413 | 120 | 0.45413 | 0 | 0.45413 | -0.015 | -0.015 | MS is closed
26 | SS Rodnya 35/10kv | 2.5 | 0.022 | 0.4808 | 0.4588 | 120 | 0.4588 | 0 | 0.4588 | -0.022 | -0.022 | MS is closed
27 | SS Bernovo 35/10kv | 1.6 | 0 | 0.5792 | 0 |  | 0 | 0 | 0 | -0.5792 | -0.5792 | MS is closed
28 | SS Min.Dvory 35/10kv | 2,5+3,2 | 1.5415 | 3.1215 | 0 |  | 3.1215 | 0 | 2.625 | -0.4965 | -0.4965 | MS is closed
29 | SS Zubtsov 35/10kv | 6,3+6,3 | 1.884 | 11.964 | 1.2167 | 120 | 10.7473 | 0 | 6.615 | -4.1323 | -4.1323 | MS is closed
30 | SS Rzhev 110/35/10kv | 40.5+40 | 4.3885 | 52.5885 | 5.1851 | 1 сутки | 47.4034 | 0 | 42 | -5.4034 | -5.4034 | MS is closed
| Nom. capacity MV, МVA | 40.5+40 | 4.2635 | 42.8335 | 2.7684 | 1 сутки | 40.0651 | 0 | 42 | 1.9349
| Nom. capacity LV, МVА | 40.5+40 | 0.125 | 9.755 | 2.4167 | 120 | 7.3383 | 0 | 42 | 34.6617
31 | SS Krasnogorskasya 35/10 | 1.6 | 0.10625 | 0.93625 | 0 |  | 0 | 0 | 0 | -0.93625 | -0.93625 | MS is closed
32 | SS Lisitsky Bor 35/10 | 2.5 | 0.032 | 1.402 | 0 |  | 0 | 0 | 0 | -1.402 | -1.402 | MS is closed
33 | SS No.6 35/10 | 1 | 0 | 0.03 | 0 |  | 0 | 0 | 0 | -0.03 | -0.03 | MS is closed
34 | SS No.1 35/6 | 1 | 0 | 0.5 | 0 |  | 0 | 0 | 0 | -0.5 | -0.5 | MS is closed
| SS No.1 35/10 | 2.5 | 1.1027 | 2.6827 | 0 |  | 0 | 0 | 0 | -2.6827 | -2.6827 | MS is closed
35 | SS No.16 35/6 | 1 | 0 | 0.12 | 0 |  | 0 | 0 | 0 | -0.12 | -0.12 | MS is closed
| SS No.16 35/10 | 2.5 | 0 | 0.85 | 0 |  | 0 | 0 | 0 | -0.85 | -0.85 | MS is closed
36 | SS No.17 35/10 | 4 | 0 | 0.62 | 0 |  | 0 | 0 | 0 | -0.62 | -0.62 | MS is closed
37 | SS Pervitino 35/10 | 1.6 | 0 | 0.34 | 0 |  | 0 | 0 | 0 | -0.34 | -0.34 | MS is closed
38 | SS No. 8 35/10 | 2.5 | 0.04125 | 1.5713 | 0 |  | 0 | 0 | 0 | -1.5713 | -1.5713 | MS is closed
39 | SS Alexino 35/6 | 2.5 | 0.324 | 1.344 | 0 |  | 0 | 0 | 0 | -1.344 | -1.344 | MS is closed
40 | SS Bezborodovo 35/10 | 2.5 | 0 | 1.58 | 0 |  | 0 | 0 | 0 | -1.58 | -1.58 | MS is closed
41 | SS Medvidikha 110/10 | 2.5 | 0.026 | 0.596 | 0.57 | 1сутки | 0.57 | 0 | 0.57 | -0.026 | -0.026 | MS is closed
42 | SS Kivirichi 35/10 | 2.5 | 0 | 0.7 | 0 |  | 0 | 0 | 0 | -0.7 | -0.7 | MS is closed
43 | SS No.27 35/6 | 10+10 | 0.06375 | 13.5137 | 0 |  | 13.5137 | 0 | 10.5 | -3.0137 | -3.0137 | MS is closed
44 | SS Vagzhanovskaya 35/6 | 16+16 | 0.1125 | 20.5525 | 0 |  | 20.5525 | 0 | 16.8 | -3.7525 | -3.7525 | MS is closed
45 | SS Kaposhvar 35/10 | 10+10 | 3.875 | 13.535 | 0 |  | 13.535 | 0 | 10.5 | -3.035 | -3.035 | MS is closed
46 | SS Mamulino 110/10 | 6,3+6,3 | 5.8825 | 7.1525 | 0 |  | 7.1525 | 0 | 6.62 | -0.5325 | -0.5325 | MS is closed
47 | SS Sakharovo 35/10 | 2,5+2,5 | 0.8139 | 3.0639 | 0 |  | 3.0639 | 0 | 2.62 | -0.4439 | -0.4439 | MS is closed
48 | SS Grishkino 35/10 | 10+6,3 (according to TS) | 5.4356 | 8.3556 | 0 |  | 8.3556 | 0 | 6.6 | -1.7556 | -1.7556 | MS is closed
49 | SS Pushkino 110/35/10 | 10 | 0.7171 | 5.5371 | 4.82 | 1 сутки | 4.82 | 0 | 4.82 | -0.7171 | -0.7171 | MS is closed
| Nom. capacity MV, МVА | 8.83 | 0.7171 | 5.3671 | 4.65 | 1 сутки | 4.65 | 0 | 4.65 | 0
| Nom. capacity LV, МVА | 8.75 | 0 | 0.17 | 0.17 | 1 сутки | 0.17 | 0 | 0.17 | 0
50 | SS Kr. Gorodok 35/10 kv | 0.56 | 0 | 0.02 | 0 |  | 0 | 0 | 0 | -0.02 | -0.02 | MS is closed
51 | SS Pen 35/10 kv | 1.6 | 0 | 0.16 | 0 |  | 0 | 0 | 0 | -0.16 | -0.16 | MS is closed
52 | SS Maximkovo 35/10 kv | 4 | 0.035 | 0.615 | 0.58 | 1 сутки | 0.58 | 0 | 0.58 | -0.035 | -0.035 | MS is closed
53 | SS Okovtsy 35/10 kv | 1 | 0.025 | 0.615 | 0.59 | 1 сутки | 0.59 | 0 | 0.59 | -0.025 | -0.025 | MS is closed
54 | SS Seliger 35/10 kv | 4 | 1.69 | 5.02 | 0 |  | 0 | 0 | 0 | -5.02 | -5.02 | MS is closed
55 | SS Moshary 35/10 kv | 1.6 | 0 | 0.26 | 0 |  | 0 | 0 | 0 | -0.26 | -0.26 | MS is closed
56 | SS Voroshilovo 35/10 kv | 1 | 0 | 0.39 | 0 |  | 0 | 0 | 0 | -0.39 | -0.39 | MS is closed
57 | SS Slautino 35/10 kv | 1.6 | 0.0685 | 0.5385 | 0 |  | 0 | 0 | 0 | -0.5385 | -0.5385 | MS is closed
58 | SS Moshki 35/10 kv | 2,5+2,5 | 0.0805 | 2.8505 | 0 |  | 2.8505 | 0 | 2.63 | -0.2205 | -0.2205 | MS is closed
59 | SS Selizharovo 110/35/10 kv | 16+10 | 2.2761 | 11.0661 | 0 |  | 11.0661 | 0 | 10.5 | -0.5661 | -0.5661 | MS is closed
| Nom. capacity MV, МVА | 16+10 | 0 | 2.13 | 0 |  | 2.13 | 0 | 10.5 | 8.37
| Nom. capacity LV, МVА | 16+10 | 2.2761 | 8.9361 | 0 |  | 8.9361 | 0 | 10.5 | 1.5639
60 | SS N. Rozhok 110/35/10 kv | 10+10 | 1.85 | 17.42 | 0 |  | 17.42 | 0 | 10.5 | -6.92 | -6.92 | MS is closed
| Nom. capacity MV, МVА | 10+10 | 1.69 | 4.09 | 0 |  | 4.09 | 0 | 10.5 | 6.41
| Nom. capacity LV, МVА | 10+10 | 0.16 | 13.33 | 0 |  | 13.33 | 0 | 10.5 | -2.83
Total: | [10 empty] | -66.051
voronezhenergo
1 | No. 44 | 10 | 2.065 | 2.125 | 0 | 0 | 2.125 | 0 | 0 | -2.125 | -2.125 | closed
2 | Semidesyatnoe | 2.5 | 0.089 | 0.379 | 0 | 0 | 0.379 | 0 | 0 | -0.379 | -0.379 | closed
2 | Arkhangelskoe | 3.2 | 0.06139 | 0.64139 | 0 | 0 | 0.64139 | 0 | 0 | -0.64139 | -0.64139 | closed
4 | Khokhol-2 | 2.5 | 0.1 | 1.1 | 0 | 0 | 1.1 | 0 | 0 | -1.1 | -1.1 | closed
4.5 | Troitskoe | 2.5 | 0.0105 | 0.3205 | 0 | 0 | 0.3205 | 0 | 0 | -0.3205 | -0.3205 | closed
5.4 | Zemlyansk | 4 | 0.012 | 0.922 | 0 | 0 | 0.922 | 0 | 0 | -0.922 | -0.922 | closed
6.3 | N. Kalitva | 6.3 | 0.034048 | 1.584 | 0.78 | 240 | 0.80405 | 0 | 0.78 | -0.80405 | -0.80405 | closed
7.2 | Azovka | 10 | 2.13 | 3.6 | 3.12 | 180 | 0.47996 | 0 | 3.12 | -0.47996 | -0.47996 | closed
8.1 | Sergeevka | 4 | 0.040324 | 0.35032 | 0 | 0 | 0.35032 | 0 | 0 | -0.35032 | -0.35032 | closed
9 | Andreevka | 2.5 | 0.017125 | 0.10712 | 0 | 0 | 0.10712 | 0 | 0 | -0.10712 | -0.10712 | closed
9.9 | Kulikovka | 4 | 0.18075 | 1.4507 | 0 | 0 | 1.4507 | 0 | 0 | -1.4507 | -1.4507 | closed
10.8 | Kr. Polyana | 2.5 | 0.010524 | 0.23052 | 0 | 0 | 0.23052 | 0 | 0 | -0.23052 | -0.23052 | closed
11.7 | Uryv | 2.5 | 0.044 | 0.594 | 0 | 0 | 0.594 | 0 | 0 | -0.594 | -0.594 | closed
12.6 | Zaluzhnoe | 2.5 | 0.23352 | 1.6435 | 1.56 | 240 | 0.083524 | 0 | 1.56 | -0.083524 | -0.083524 | closed
13.5 | N. Elan | 2.5 | 0.027174 | 0.43717 | 0 | 0 | 0.43717 | 0 | 0 | -0.43717 | -0.43717 | closed
14.4 | Pykhovka | 2.5 | 0.044565 | 0.33457 | 0 | 0 | 0.33457 | 0 | 0 | -0.33457 | -0.33457 | closed
15.3 | Mayskaya | 2.5 | 0.016304 | 0.6563 | 0 | 0 | 0.6563 | 0 | 0 | -0.6563 | -0.6563 | closed
16 | Khleborodnoe | 2.5 | 0.058696 | 0.5387 | 0 | 0 | 0.5387 | 0 | 0 | -0.5387 | -0.5387 | closed
17 | B.Kazinka | 6.3 | 5.9887 | 6.5088 | 0 | 0 | 6.5088 | 0 | 0 | -6.5088 | -6.5088 | closed
| Sн. MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 5.9887 | 6.5088 | 0 | 0 | 6.5088 | 0 | 0 | -6.5088
18 | Derezovka | 6.3 | 0.017 | 0.357 | 0 | 0 | 0.357 | 0 | 0 | -0.357 | -0.357 | closed
19 | Osetrovka | 6.3 | 2.6424 | 2.6424 | 1.5 | 1 сутки | 1.1424 | 0 | 1.5 | -1.1424 | -1.1424 | closed
20 | sovkhoz Radchensky | 10 | 0.01325 | 1.2833 | 2 | 1 сутки | -0.71675 | 0 | 2 | 0.71675 | -1.14 | closed
| Sн. MV, МVА | 10 | 0 | 1.14 | 0 | 1 сутки | 1.14 | 0 | 0 | -1.14
| Sн. LV, МVА | 10 | 0.01325 | 0.14325 | 2 | 1 сутки | -1.8567 | 0 | 2 | 1.8567
21 | R. Zhuravka | 2.5 | 0.014 | 0.714 | 0 | 0 | 0.714 | 0 | 0 | -0.714 | -0.714 | closed
22 | Shurinovka | 2.5 | 0.002 | 0.312 | 0 | 0 | 0.312 | 0 | 0 | -0.312 | -0.312 | closed
23 | Tverdokhlebovka | 4 | 0.004 | 0.274 | 0 | 0 | 0.274 | 0 | 0 | -0.274 | -0.274 | closed
24 | Krinitsa | 2.5 | 0.00596 | 0.25596 | 0 | 0 | 0.25596 | 0 | 0 | -0.25596 | -0.25596 | closed
25 | Krasnogorovka | 2.5 | 0.0114 | 0.1114 | 0 | 0 | 0.1114 | 0 | 0 | -0.1114 | -0.1114 | closed
26 | No. 2 | 25+25 | 18.007 | 36.727 | 4.8 | 120 | 31.927 | 0 | 26.25 | -5.677 | -5.677 | closed
27 | No. 3 | 6,3 + 10 | 0.458 | 9.348 | 2.5 | 120 | 6.848 | 0 | 6.615 | -0.233 | -0.233 | closed
28 | No. 9 | 16+25 | 10.927 | 34.527 | 3.3 | 120 | 31.227 | 0 | 16.8 | -14.427 | -14.427 | Change of transformers is provided
29 | No. 10 | 20+20 | 14.678 | 45.078 | 13.3 | 120 | 31.778 | 0 | 21 | -10.778 | -10.778 | Reconstraction is provided
30 | No. 13 | 6,3+6,3 | 3.591 | 13.111 | 4.2 | 120 | 8.911 | 0 | 6.615 | -2.296 | -2.296 | Change of transformers is provided
31 | No. 21 | 25,0+20,0+40,0 | 25.844 | 63.024 | 4.6 | 180 | 58.424 | 0 | 47.25 | -11.174 | -11.174 | Reconstraction is provided
32 | No. 23 | 7,5+6,3 | 0.792 | 7.612 | 0.8 | 120 | 6.812 | 0 | 6.615 | -0.197 | -0.197 | Change of transformers is provided
33 | No. 28 | 10+10 | 3.6057 | 15.6057 | 0 | 0 | 15.6057 | 0 | 10.5 | -5.1057 | -5.1057 | Change of transformers is provided
34 | No. 34 | 2,5+1,8 | 0 | 2.32 | 0 | 0 | 2.32 | 0 | 1.89 | -0.43 | -0.43 | closed
35 | No. 35 | 10+10 | 0.012 | 13.112 | 2.4 | 120 | 10.712 | 0 | 10.5 | -0.212 | -0.212 | Reconstraction is provided
36 | No. 39 | 25+25 | 3 | 30.82 | 4.1 | 120 | 26.72 | 0 | 26.25 | -0.47 | -0.47 | Change of transformers is provided
37 | Don | 2,5+2,5 | 0.4687 | 3.3187 | 0 | 0 | 3.3187 | 0 | 2.625 | -0.6937 | -0.6937 | closed
38 | Moskovskoe | 10+10 | 0.039 | 11.519 | 1.8 | 120 | 9.719 | 0 | 10.5 | 0.781 | -0.1 | closed
| Sн. MV, МVА | 10+10 | 0 | 10.6 | 0 | 0 | 10.6 | 0 | 10.5 | -0.1
| Sн. LV, МVА | 10+10 | 0.039 | 0.919 | 1.8 | 120 | -0.881 | 0 | 10.5 | 11.381
39 | Usman-1 | 10,0+6,3 | 5.1182 | 16.3682 | 0 | 0 | 16.3682 | 0 | 6.615 | -9.7532 | -9.7532 | Transition to 110 kv and reconstruction of SS are planned
40 | Usman-2 | 4+6,3 | 0.6936 | 10.0436 | 0 | 0 | 10.0436 | 0 | 4.2 | -5.8436 | -5.8436 | Transition to 110 kv and reconstruction of SS are planned
41 | No. 31 | 16+25 | 0 | 23.15 | 5.6 | 120 | 17.55 | 0 | 16.8 | -0.75 | -0.75 | closed
| Sн. MV, МVА | 16+25 | 0 | 15 | 5.6 | 120 | 9.4 | 0 | 16.8 | 7.4
| Sн. LV, МVА | 16+25 | 0 | 8.15 | 0 | 0 | 8.15 | 0 | 16.8 | 8.65
| TOTAL: | [9 empty] | -90.5106
kurskenergo
1 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.75 | 9.85 | 6.64 | 1 сутки | 6.64 | 0 | 6.64 | -3.21 | -3.21 | closed
2 | SS 35/10 Water storage | 1 х 4,0 | 3.509 | 3.599 | 2.72 | 1 сутки | 2.72 | 0 | 2.72 | -0.879 | -0.879 | closed
3 | SS 110/35/10 Kamyshi | 2*6,3 | 6.2977 | 14.1677 | 6.45 | 20 | 7.7177 | 0 | 6.62 | -1.0977 | -1.9377 | closed
| Nom. capacity MV, МVА | 6.3 | 6.2977 | 13.0077 | 4.45 | 0 | 8.5577 | 0 | 6.62 | -1.9377
| Nom. capacidty LV, МVА | 6.3 | 0 | 1.16 | 2 | 20 | 2 | 0 | 6.62 | 4.62
4 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.315 | 17.015 | 6.25 | 20 | 10.765 | 0 | 10.5 | -0.265 | -0.265 | opened
| TOTAL: | [9 empty] | -6.2917
Total IDGC | [10 empty] | -376.3339