## МРСК
Table 1
No. | Name of supply center, voltage class | Current deficit | [10 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | P | Q | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
[5 empty] | MVA | MVA | Min
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12
One-transformer substations
1 | SS-110/35/10kV D.Polyana | 6.3 | 262 | 185 | 0.32073 | 1.457 | 45 | 1.457 | 0 | 1.457 | 1.1363 | 0.20865 |  |  | D. Polyana | 1.4535
| S nom MV, МVА | 6.3 | 6 | 48 | 0.048374 | 0.958 |  | 0.958 | 0 | 0.958 | 0.90963 |  |  |  | Konshino | 0.38327
| S nom LV, МVА | 6.3 | 256 | 137 | 0.29035 | 0.499 |  | 0.499 | 0 | 0.499 | 0.20865 |  |  |  | Orositelnaya | 11.6065
2 | SS-110/35/10kV Konshino | 6.3 | 349 | 215 | 0.40991 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01991 | -0.01991 |  |  | Pischeprom | 6.4309
| S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Rovenky-110 | 2.2902
| S nom LV, МVА | 6.3 | 349 | 215 | 0.40991 | 0.39 |  | 0.39 | 0 | 0.39 | -0.01991 |  |  |  | Serebryanka | 1.2339
3 | SS-110/35/10kV Orositelnaya | 16 | 13836 | 4805 | 14.6466 | 11.607 | 120 | 11.607 | 0 | 11.607 | -3.0396 | -3.0396
| S nom MV, МVА | 16 | 8659 | 2940 | 9.1445 | 8.606 |  | 8.606 | 0 | 8.606 | -0.5385
| S nom LV, МVА | 16 | 5177 | 1865 | 5.5027 | 3.001 |  | 3.001 | 0 | 3.001 | -2.5017
4 | SS-110/35/10kV Rovenki | 16 | 2189 | 988 | 2.4016 | 3.44 | 120 | 3.44 | 0 | 3.44 | 1.0384 | 1.0384
| S nom MV, МVА | 16 | 2 | 34 | 0.034059 | 4 |  | 4 | 0 | 4 | 3.9659
| S nom LV, МVА | 16 | 2187 | 954 | 2.386 | 3.44 |  | 3.44 | 0 | 3.44 | 1.054
5 | SS-110/35/10kV Serebryanka | 10 | 966 | 389 | 1.0414 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.73862 | 0
| S nom MV, МVА | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| S nom LV, MVА | 10 | 966 | 389 | 1.0414 | 1.78 |  | 1.78 | 0 | 1.78 | 0.73862
6 | SS-35/10kV Afanasyevka | 1.6 | 784 | 288 | 0.83522 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.18882 | -0.18882
7 | SS-35/10kV Borisovka | 1.6 | 776 | 224 | 0.80768 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | -0.12418 | -0.12418
8 | SS-35/10kV Borisy | 1.6 | 780 | 360 | 0.85907 | 0 | 20 | 0 | 0 | 0 | -0.85907 | -0.85907
9 | SS-35/10kV Gostishchevo | 4 | 2984 | 1184 | 3.2103 | 2.64 | 80 | 2.64 | 0 | 2.64 | -0.57031 | -0.57031
10 | SS-35/10kV Gruzskoe | 1.6 | 684 | 330 | 0.75944 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.29056 | 0.29056
11 | SS-35/10kV Zemsnaryad | 1 | 14 | 19 | 0.023601 | 0 |  | 0 | 0 | 0 | -0.023601 | -0.023601
12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 324 | 132 | 0.34986 | 0 |  | 0 | 0 | 0 | -0.34986 | -0.34986
13 | SS-35/10kV Kamyzino | 2.5 | 880 | 376 | 0.95696 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.41596 | -0.41596
14 | SS-35/10kV Koloskovo | 2.5 | 1600 | 512 | 1.6799 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.017324 | -0.017324
15 | SS-35/10jkV Kryukovo | 2.5 | 1560 | 492 | 1.6357 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.085746 | -0.085746
16 | SS-35/10kV Kushchino | 1.6 | 336 | 108 | 0.35293 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.057169 | 0.057169
17 | SS-35/10kV Lopukhinka | 2.5 | 304 | 144 | 0.33638 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.070619 | 0.070619
18 | SS-35/10kV Malakeevo | 2.5 | 1164 | 600 | 1.3095 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.07046 | 0.07046
19 | SS-35/10kV Murom | 2.5 | 920 | 256 | 0.95495 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.58505 | 0.58505
20 | SS-35/10kV Nikolaevka | 2.5 | 656 | 288 | 0.71644 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.051736 | -0.051736
21 | SS-35/10kV Nikolskoe | 4 | 1536 | 384 | 1.5833 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.80327 | -0.80327
22 | SS-35/10kV Pokrovka | 2.5 | 576 | 276 | 0.63871 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.083289 | 0.083289
23 | SS-35/10kV Pyatnitskoe | 4 | 2305 | 974 | 2.5023 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.66234 | -0.66234
24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 122 | 72 | 0.14166 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.5343 | 1.5343
25 | SS-35/10kV Svistovka | 2.5 | 504 | 224 | 0.55154 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.13566 | 0.13566
26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 572 | 180 | 0.59965 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.12415 | 0.12415
27 | SS-35/10kV Kharkovskaya | 2.5 | 552 | 236 | 0.60033 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.079367 | 0.079367
Two- and more transformer substations
28 | SS-110/6kV Automobile maintenance plant | 16+16 | 11143 | 5340 | 12.3565 | 3.561 | 45 | 8.7955 | 0 | 16.8 | 8.0045 | 8.0045 |  | 1.05 | 16 |  | Avtoremzavod | 9.9792
29 | SS-110/35/10kV Aydar | 16+10 | 8156 | 3395 | 8.8344 | 8.95 | 120 | -0.11561 | 0 | 10.5 | 10.6156 | 10.3916 |  | 1.05 | 10 |  | Aidar | 8.4408
| S nom MV, МVА | 16+10 | 6832 | 2839 | 7.3984 | 7.29 |  | 0.10839 | 0 | 10.5 | 10.3916 |  |  | 1.05 | 10 |  | Aleksandrivka | 12.534
| S nom LV, МVА | 16+10 | 1324 | 556 | 1.436 | 1.66 |  | -0.22399 | 0 | 10.5 | 10.724 |  |  | 1.05 | 10 |  | Alekseevka | 44.0632
30 | SS-110/35/10kV Alexandrovka | 25+25 | 7539 | 3956 | 8.5139 | 8.37 | 80 | 0.1439 | 0 | 26.25 | 26.1061 | 25.1649 |  | 1.05 | 25 |  | Arkhangelskoye | 9.383
| S nom MV, МVА | 25+25 | 7157 | 3056 | 7.7821 | 6.697 |  | 1.0851 | 0 | 26.25 | 25.1649 |  |  | 1.05 | 25 |  | Belgorod-1 | 44.5181
| S nom LV, МVА | 25+25 | 382 | 900 | 0.97771 | 1.673 |  | -0.69529 | 0 | 26.25 | 26.9453 |  |  | 1.05 | 25 |  | Borisovka | 14.4143
31 | SS-110/35/10kV Alexeevka | 25+25+25 | 40243 | 18062 | 44.1105 | 5.322 | 120 | 38.7885 | 0 | 52.5 | 13.7115 | 13.7115 |  | 1.05 | 50 |  | V. Pokrovka | 9.036
| S nom MV, МVА | 25+25+25 | 17603 | 7822 | 19.2626 | 3.102 |  | 16.1606 | 0 | 52.5 | 36.3394 |  |  | 1.05 | 50 |  | Veydelevka | 7.9503
| S nom LV, МVА | 25+25+25 | 22640 | 10240 | 24.8481 | 2.22 |  | 22.6281 | 0 | 52.5 | 29.8719 |  |  | 1.05 | 50 |  | Vitamin Complex | 11.7863
32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 9058 | 3808 | 9.8259 | 8.87 | 45 | 0.9559 | 0 | 10.5 | 9.5441 | 9.5441 |  | 1.05 | 10 |  | Volokonovka | 15.9084
| S nom MV, МVА | 10+16 | 8537 | 3612 | 9.2697 | 8.867 |  | 0.40268 | 0 | 10.5 | 10.0973 |  |  | 1.05 | 10 |  | Vostochnaya | 41.987
| S nom LV, МVА | 10+16 | 521 | 196 | 0.55665 | 0 |  | 0.55665 | 0 | 10.5 | 9.9434 |  |  | 1.05 | 10 |  | Golofeevka | 1.8481
33 | SS-110/6kV Belgorod-1 | 40+48 | 38071 | 13708 | 40.4637 | 0 | 120 | 40.4637 | 0 | 42 | 1.5363 | 1.5363 |  | 1.05 | 40 |  | Gotnya | 8.9986
34 | SS-110/35/10kV Borisovka | 16+16 | 11357 | 4974 | 12.3985 | 11.433 | 120 | 0.96547 | 0 | 16.8 | 15.8345 | 5.4899 |  | 1.05 | 16 |  | Graivoron | 15.2094
| S nom MV, МVА | 16+8 | 5565 | 2734 | 6.2003 | 8.133 |  | -1.9327 | 0 | 8.4 | 10.3327 |  |  | 1.05 | 8 |  | Donets | 26.0404
| S nom LV, МVА | 16+8 | 5792 | 2240 | 6.2101 | 3.3 |  | 2.9101 | 0 | 8.4 | 5.4899 |  |  | 1.05 | 8 |  | Dubovoe | 22.9597
35 | SS-110/35/10kV V.Pokrovka | 10+10 | 9454 | 3886 | 10.2215 | 11.5 | 120 | -1.2785 | 0 | 10.5 | 11.7785 | 9.2237 |  | 1.05 | 10 |  | Zhuravliki | 13.1662
| S nom MV, МVА | 10+10 | 8360 | 3534 | 9.0763 | 7.8 |  | 1.2763 | 0 | 10.5 | 9.2237 |  |  | 1.05 | 10 |  | Zapadnaya | 16.9475
| S nom LV, МVА | 10+10 | 1094 | 352 | 1.1492 | 3.7 |  | -2.5508 | 0 | 10.5 | 13.0508 |  |  | 1.05 | 10 |  | Ivnya | 6.018
36 | SS-110/35/10kV Veydelevka | 10+10 | 8214 | 3266 | 8.8395 | 8.83 | 120 | 0.0094882 | 0 | 10.5 | 10.4905 | 9.675 |  | 1.05 | 10
| S nom MV, МVА | 10+10 | 4429 | 1798 | 4.78 | 3.955 |  | 0.82505 | 0 | 10.5 | 9.675 |  |  | 1.05 | 10
| S nom LV, МVА | 10+10 | 3785 | 1468 | 4.0597 | 4.875 |  | -0.81529 | 0 | 10.5 | 11.3153 |  |  | 1.05 | 10
37 | SS-110/6kV Vitamin plant | 25+25 | 14250 | 6848 | 15.81 | 1.46 | 45 | 14.35 | 0 | 26.25 | 11.9 | 11.9 |  | 1.05 | 25
38 | SS-110/35/10kV Volokonovka | 25+25 | 17621 | 8868 | 19.7267 | 10.651 | 120 | 9.0757 | 0 | 26.25 | 17.1743 | 17.1743 |  | 1.05 | 25
| S nom MV, МVА | 25+25 | 9620 | 4914 | 10.8024 | 8.576 |  | 2.2264 | 0 | 26.25 | 24.0236 |  |  | 1.05 | 25
| S nom LV, МVА | 25+25 | 8001 | 3954 | 8.9247 | 2.075 |  | 6.8497 | 0 | 26.25 | 19.4003 |  |  | 1.05 | 25
39 | SS-110/35/6kV Vostochnaya | 25+25 | 36574 | 16648 | 40.1847 |  | 120 | 40.1847 | 0 | 26.25 | -13.9347 | -13.9347 |  | 1.05 | 25
| S nom MV, МVА | 25+25 | 15809 | 5210 | 16.6454 |  |  | 16.6454 | 0 | 26.25 | 9.6046 |  |  | 1.05 | 25
| S nom LV, МVА | 25+25 | 20765 | 11438 | 23.7068 |  |  | 23.7068 | 0 | 26.25 | 2.5432 |  |  | 1.05 | 25
40 | SS-110/10/6kV Golofeevka | 16+16 | 2038 | 882 | 2.2207 | 0 |  | 2.2207 | 0 | 26.25 | 24.0293 | 10.9043 |  | 1.05 | 25
| S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  | 1.05 | 12.5
| S nom LV, МVА | 16+16 | 2038 | 882 | 2.2207 | 0 |  | 2.2207 | 0 | 13.125 | 10.9043 |  |  | 1.05 | 12.5
41 | SS-110/10kV Gotnya | 16+16 | 8429 | 4606 | 9.6054 | 6.43 | 120 | 3.1754 | 0 | 16.8 | 13.6246 | 13.6246 |  | 1.05 | 16
42 | SS-110/35/10kV Grayvoron | 16+16 | 15102 | 14219 | 20.7425 | 13.953 | 80 | 6.7895 | 0 | 16.8 | 10.0105 | 6.9944 |  | 1.05 | 16
| S nom MV, МVА | 16+16 | 7808 | 3633 | 8.6118 | 10.903 |  | -2.2912 | 0 | 16.8 | 19.0912 |  |  | 1.05 | 16
| S nom LV, МVА | 16+16 | 7294 | 10586 | 12.8556 | 3.05 |  | 9.8056 | 0 | 16.8 | 6.9944 |  |  | 1.05 | 16 |  | K.Gvardiya | 11.3866
43 | SS-110/6kV Donets | 40+40 | 24528 | 8016 | 25.8046 | 6.73 | 120 | 19.0746 | 0 | 42 | 22.9254 | 22.9254 |  | 1.05 | 40 |  | Kazatskie Bugry | 11.6977
44 | SS-110/10kV Dubovoe | 40+40 | 22234 | 5735 | 22.9617 | 11.23 | 120 | 11.7317 | 0 | 42 | 30.2683 | 30.2683 |  | 1.05 | 40 |  | Korocha | 18.4946
45 | SS-110/35/6kV Zhuravliki | 40+25 | 20132 | 7256 | 21.3997 | 12.4 | 120 | 8.9997 | 0 | 42 | 33.0003 | 32.261 |  | 1.05 | 40 |  | Krasnaya Yaruga | 10.8277
| S nom MV, МVА | 40+25 | 14761 | 6085 | 15.966 | 6.227 |  | 9.739 | 0 | 42 | 32.261 |  |  | 1.05 | 40 |  | Maximovka | 10.7359
| S nom LV, МVА | 40+25 | 5371 | 1171 | 5.4972 | 6.173 |  | -0.67583 | 0 | 42 | 42.6758 |  |  | 1.05 | 40 |  | N.Oskol | 19.8083
46 | SS-110/10kV Zapadnaya | 16+16 | 15750 | 4520 | 16.3858 | 1.249 | 80 | 15.1368 | 0 | 16.8 | 1.6632 | 1.6632 |  | 1.05 | 16
47 | SS-110/35/10kV Ivnya | 10+10 | 11674 | 4784 | 12.6162 | 6.16 | 80 | 6.4562 | 0 | 10.5 | 4.0438 | 3.8937 |  | 1.05 | 10
| S nom MV, МVА | 10+10 | 8312 | 3402 | 8.9813 | 2.375 |  | 6.6063 | 0 | 10.5 | 3.8937 |  |  | 1.05 | 10
| S nom LV, МVА | 10+10 | 3362 | 1382 | 3.635 | 3.785 |  | -0.15004 | 0 | 10.5 | 10.65 |  |  | 1.05 | 10
48 | SS-110/35/10kV K.Gvardiya | 16+16 | 13335 | 6036 | 14.6375 | 7.7116 | 120 | 6.9259 | 0 | 16.8 | 9.8741 | 9.8741 |  | 1.05 | 16
| S nom MV, МVА | 16+16 | 6823 | 3368 | 7.609 | 4.854 |  | 2.755 | 0 | 16.8 | 14.045 |  |  | 1.05 | 16
| S nom LV, МVА | 16+16 | 6512 | 2668 | 7.0374 | 2.8576 |  | 4.1798 | 0 | 16.8 | 12.6202 |  |  | 1.05 | 16
49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 11009 | 4506 | 11.8955 | 9.65 | 80 | 2.2455 | 0 | 26.25 | 24.0045 | 20.0068 |  | 1.05 | 25
| S nom MV, МVА | 25+25 | 1548 | 580 | 1.6531 | 1.384 |  | 0.26909 | 0 | 26.25 | 25.9809 |  |  | 1.05 | 25
| S nom LV, МVА | 25+25 | 9461 | 3926 | 10.2432 | 4 |  | 6.2432 | 0 | 26.25 | 20.0068 |  |  | 1.05 | 25
50 | SS-110/35/10kV Korocha | 16+16+16 | 19319 | 8126 | 20.9584 | 2.019 | 20 | 18.9394 | 0 | 33.6 | 14.6606 | 14.6606 |  | 1.05 | 32
| S nom MV, МVА | 16+16+16 | 7145 | 2668 | 7.6269 | 1.719 |  | 5.9079 | 0 | 33.6 | 27.6921 |  |  | 1.05 | 32
| S nom LV, МVА | 16+16+16 | 12174 | 5458 | 13.3415 | 0.3 |  | 13.0415 | 0 | 33.6 | 20.5585 |  |  | 1.05 | 32
51 | SS-110/10kV Krapivenskaya | 16+16 | 823 | 139 | 0.83466 | 0 | 0 | 0.83466 | 0 | 16.8 | 15.9653 | 15.9653 |  | 1.05 | 16
52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 9465 | 4131 | 10.3272 | 9.158 | 120 | 1.1692 | 0 | 10.5 | 9.3308 | 9.3308 |  | 1.05 | 10
| S nom MV, МVА | 10+10 | 4111 | 1829 | 4.4995 | 3.52 |  | 0.97951 | 0 | 10.5 | 9.5205 |  |  | 1.05 | 10
| S nom LV, МVА | 10+10 | 5354 | 2302 | 5.8279 | 5.638 |  | 0.18991 | 0 | 10.5 | 10.3101 |  |  | 1.05 | 10
53 | SS-110/10/10kV Mayskaya | 40+40 | 6141 | 1360 | 6.2898 |  |  | 6.2898 | 0 | 42 | 35.7102 | 35.7102 |  | 1.05 | 40
54 | SS-110/35/10kV Maximovka | 16+16 | 8770 | 4874 | 10.0334 | 11.48 | 45 | -1.4466 | 0 | 16.8 | 18.2466 | 17.2826 |  | 1.05 | 16
| S nom MV, МVА | 16+16 | 7336 | 4290 | 8.4983 | 9.449 |  | -0.95071 | 0 | 16.8 | 17.7507 |  |  | 1.05 | 16
| S nom LV, МVА | 16+16 | 1434 | 584 | 1.5484 | 2.031 |  | -0.48264 | 0 | 16.8 | 17.2826 |  |  | 1.05 | 16
55 | SS-110/35/10kV N.Oskol | 25+31,5 | 17666 | 7970 | 19.3806 | 9.119 | 80 | 10.2616 | 0 | 26.25 | 15.9884 | 15.2237 |  | 1.05 | 25
| S nom MV, МVА | 25+31,5 | 6226 | 3410 | 7.0987 | 7.83 |  | -0.73133 | 0 | 26.25 | 26.9813 |  |  | 1.05 | 25 |  | Obukhovskaya | 2.351
| S nom LV, МVА | 25+31,5 | 11440 | 4560 | 12.3153 | 1.289 |  | 11.0263 | 0 | 26.25 | 15.2237 |  |  | 1.05 | 25 |  | Ochistnye | 6.5595
56 | SS-110/10kV Obukhovskaya | 25+25 | 2178 | 699 | 2.2874 | 0 |  | 2.2874 | 0 | 26.25 | 23.9626 | 23.9626 |  | 1.05 | 25 |  | Promyshlennaya | 14.983
57 | SS-110/6kV Ochistnye | 16+16 | 4625 | 2214 | 5.1276 | 0 |  | 5.1276 | 0 | 16.8 | 11.6724 | 11.6724 |  | 1.05 | 16 |  | Poultry plant | 10.559
58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 0 | 0 | 6.679 | 120 | 6.679 | 0 | 26.25 | 26.25 | 26.25 |  | 1.05 | 25
| S nom MV, МVА | 25+25 | 0 | 0 | 0 | 2.022 |  | 2.022 | 0 | 26.25 | 26.25 |  |  | 1.05 | 25
| S nom LV, МVА | 25+25 | 0 | 0 | 0 | 4.657 |  | 4.657 | 0 | 26.25 | 26.25 |  |  | 1.05 | 25
59 | SS-110/10kV Promyshlennaya | 25+25 | 16234 | 8957 | 18.5411 | 0 |  | 18.5411 | 0 | 26.25 | 7.7089 | 7.7089 |  | 1.05 | 25 |  | Pushkarnaya | 27.735
60 | SS-110/10kV Poultry plant | 16+16 | 12347 | 7576 | 14.486 | 1.296 | 80 | 13.19 | 0 | 16.8 | 3.61 | 3.61 |  | 1.05 | 16 |  | Rakitnoe | 9.2018
61 | SS-110/10kV Pushkarnaya | 40+40 | 30306 | 8850 | 31.5718 | 0 | 60 | 31.5718 | 0 | 42 | 10.4282 | 10.4282 |  | 1.05 | 40 |  | Rudnik | 14.117
62 | SS-110/35/10kV Rakitnoe | 10+10 | 11816 | 6776 | 13.621 | 8.98 | 120 | 4.641 | 0 | 10.5 | 5.859 | 5.859 |  | 1.05 | 10 |  | Severnaya | 11.1616
| S nom MV, МVА | 10+10 | 8826 | 5366 | 10.3292 | 6.407 |  | 3.9222 | 0 | 10.5 | 6.5778 |  |  | 1.05 | 10 |  | Skorodnoe | 11.5224
| S nom LV, МVА | 10+10 | 2990 | 1410 | 3.3058 | 2.573 |  | 0.73278 | 0 | 10.5 | 9.7672 |  |  | 1.05 | 10 |  | St.Oskol - 1 | 28.8772
63 | SS-110/35/6kV Rudnik | 25+25 | 17350 | 10404 | 20.2303 | 10.46 | 45 | 9.7703 | 0 | 26.25 | 16.4797 | 16.4797 |  | 1.05 | 25 |  | Streletskaya | 4.2243
| S nom MV, МVА | 25+25 | 10731 | 5534 | 12.0739 | 10.46 |  | 1.6139 | 0 | 26.25 | 24.6361 |  |  | 1.05 | 25 |  | Stroitel | 13.298
| S nom LV, МVА | 25+25 | 6619 | 4870 | 8.2175 | 0 |  | 8.2175 | 0 | 26.25 | 18.0325 |  |  | 1.05 | 25 |  | Tomarovka | 12.5522
64 | SS-110/10kV Severnaya | 40+40 | 11204 | 3168 | 11.6433 | 3.312 | 45 | 8.3313 | 0 | 42 | 33.6687 | 33.6687 |  | 1.05 | 40 |  | Chemical plant | 10.0162
65 | SS-110/35/10kV Skorodnoe | 16+16 | 13755 | 5418 | 14.7836 | 10.36 | 120 | 4.4236 | 0 | 16.8 | 12.3764 | 12.3764 |  | 1.05 | 16 |  | Tsentralnaya | 22.8863
| S nom MV, МVА | 16+16 | 9853 | 3809 | 10.5636 | 7.562 |  | 3.0016 | 0 | 16.8 | 13.7984 |  |  | 1.05 | 16 |  | Cheremoshnoe | 23.7143
| S nom LV, МVА | 16+16 | 3902 | 1609 | 4.2207 | 2.798 |  | 1.4227 | 0 | 16.8 | 15.3773 |  |  | 1.05 | 16 |  | Chernyanka | 14.7605
66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 30931 | 16493 | 35.0535 | 0 |  | 35.0535 | 0 | 47.25 | 12.1965 | 12.1965 |  | 1.05 | 45 |  | Shebekino | 25.5429
| S nom MV, МVА | 20+25+25 | 9757 | 6686 | 11.828 | 0 |  | 11.828 | 0 | 47.25 | 35.422 |  |  | 1.05 | 45 |  | Sheino | 2.4086
| S nom LV, МVА | 20+25+25 | 21174 | 9807 | 23.3349 | 0 |  | 23.3349 | 0 | 47.25 | 23.9151 |  |  | 1.05 | 45 |  | Yuzhnaya | 43.0909
67 | SS-110/35/10kV Streletskaya | 16+16 | 4735 | 1291 | 4.9078 | 2.23 | 80 | 2.6778 | 0 | 16.8 | 14.1222 | 5.6812 |  | 1.05 | 16
| S nom MV, МVА | 16+8 | -14 | -101 | 0.10197 | 0 |  | 0.10197 | 0 | 8.4 | 8.298 |  |  | 1.05 | 8
| S nom LV, МVА | 16+8 | 4749 | 1392 | 4.9488 | 2.23 |  | 2.7188 | 0 | 8.4 | 5.6812 |  |  | 1.05 | 8
68 | SS-110/6kV Stroitel | 15+15 | 12862 | 4982 | 13.7932 | 0 |  | 13.7932 | 0 | 15.75 | 1.9568 | 1.9568 |  | 1.05 | 15
69 | SS-110/35/10kV Tomarovka | 16+16 | 9989 | 4296 | 10.8736 | 3.46 | 45 | 7.4136 | 0 | 16.8 | 9.3864 | 8.9293 |  | 1.05 | 16
| S nom MV, МVА | 16+16 | 2817 | 1054 | 3.0077 | 3.46 |  | -0.45228 | 0 | 16.8 | 17.2523 |  |  | 1.05 | 16
| S nom LV, МVА | 16+16 | 7172 | 3242 | 7.8707 | 0 |  | 7.8707 | 0 | 16.8 | 8.9293 |  |  | 1.05 | 16
70 | SS-110/6kV Chemical plant | 32+32 | 10973 | 4879 | 12.0088 | 5.56 | 45 | 6.4488 | 0 | 33.6 | 27.1512 | 27.1512 |  | 1.05 | 32
71 | SS-110/10kV Tsentralnaya | 40+40 | 27342 | 4998 | 27.7951 | 0 |  | 27.7951 | 0 | 42 | 14.2049 | 14.2049 |  | 1.05 | 40
72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 19256 | 7574 | 20.692 | 20.54 | 80 | 0.152 | 0 | 26.25 | 26.098 | 24.6811 |  | 1.05 | 25
| S nom MV, МVА | 25+25 | 17936 | 6726 | 19.1557 | 19.676 |  | -0.52034 | 0 | 26.25 | 26.7703 |  |  | 1.05 | 25
| S nom LV, МVА | 25+25 | 1320 | 848 | 1.5689 | 0 |  | 1.5689 | 0 | 26.25 | 24.6811 |  |  | 1.05 | 25
73 | SS-110/35/10kV Chernyanka | 16+16 | 15254 | 6791 | 16.6974 | 5.969 | 120 | 10.7284 | 0 | 16.8 | 6.0716 | 6.0716 |  | 1.05 | 16
| S nom MV, МVА | 16+16 | 7509 | 3847 | 8.4371 | 5.969 |  | 2.4681 | 0 | 16.8 | 14.3319 |  |  | 1.05 | 16
| S nom LV, МVА | 16+16 | 7745 | 2944 | 8.2857 | 0 |  | 8.2857 | 0 | 16.8 | 8.5143 |  |  | 1.05 | 16
74 | SS-110/35/6kV Shebekino | 40+40 | 26611 | 13133 | 29.6753 | 16.65 | 120 | 13.0253 | 0 | 42 | 28.9747 | 28.9747 |  | 1.05 | 40
| S nom MV, МVА | 40+40 | 15078 | 8022 | 17.0792 | 11.682 |  | 5.3972 | 0 | 42 | 36.6028 |  |  | 1.05 | 40
| S nom LV, МVА | 40+40 | 11533 | 5111 | 12.6148 | 4.968 |  | 7.6468 | 0 | 42 | 34.3532 |  |  | 1.05 | 40
75 | SS-110/10kV Sheino | 3,2+10 | 3265 | 1144 | 3.4596 | 0 |  | 3.4596 | 0 | 3.36 | -0.099619 | -0.099619 |  | 1.05 | 3.2
76 | SS-110/10/6kV Yuzhnaya | 40+40 | 38807 | 11568 | 40.4945 | 12.94 | 120 | 27.5545 | 0 | 42 | 14.4455 | 14.4455 |  | 1.05 | 40
| S nom MV, МVА | 40+40 | 6846 | 1506 | 7.0097 | 3.42 |  | 3.5897 | 0 | 42 | 38.4103 |  |  | 1.05 | 40
| S nom LV, МVА | 40+40 | 31961 | 10062 | 33.5075 | 9.52 |  | 23.9875 | 0 | 42 | 18.0125 |  |  | 1.05 | 40
77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 704 | 264 | 0.75187 | 0.43267 | 120 | 0.31921 | 0 | 2.625 | 2.3058 | 2.3058 |  | 1.05 | 2.5
78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 872 | 280 | 0.91585 | 0.46639 | 120 | 0.44946 | 0 | 2.625 | 2.1755 | 2.1755 |  | 1.05 | 2.5
79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 2352 | 1056 | 2.5782 | 0 |  | 2.5782 | 0 | 4.2 | 1.6218 | 1.6218 |  | 1.05 | 4
80 | SS-35/10kV Annovka | 2,5+2,5 | 876 | 354 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267 |  | 1.05 | 2.5
81 | SS-35/10kV Artelnoe | 6,3+6,3 | 3664 | 2840 | 4.6358 | 0.55 | 45 | 4.0858 | 0 | 6.615 | 2.5292 | 2.5292 |  | 1.05 | 6.3
82 | SS-35/10kV B.Dvory | 4+4 | 2304 | 928 | 2.4839 | 1.191 | 120 | 1.2929 | 0 | 4.2 | 2.9071 | 2.9071 |  | 1.05 | 4
83 | SS-35/10kV B.Ivanovka | 4+4 | 640 | 272 | 0.6954 | 0.62488 | 80 | 0.070521 | 0 | 4.2 | 4.1295 | 4.1295 |  | 1.05 | 4
84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 744 | 306 | 0.80447 | 0.44779 | 45 | 0.35668 | 0 | 2.625 | 2.2683 | 2.2683 |  | 1.05 | 2.5
85 | SS-35/10kV B.Ples | 2,5+2,5 | 720 | 336 | 0.79454 | 0.606 | 45 | 0.18854 | 0 | 2.625 | 2.4365 | 2.4365 |  | 1.05 | 2.5
86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 2960 | 1312 | 3.2377 | 2.83 | 45 | 0.40774 | 0 | 6.615 | 6.2073 | 6.2073 |  | 1.05 | 6.3
87 | SS-35/10kV Belovskoe | 4+4 | 3544 | 1432 | 3.8224 | 1.21 | 80 | 2.6124 | 0 | 4.2 | 1.5876 | 1.5876 |  | 1.05 | 4
88 | SS-35/10kV Belyanka | 2,5+4 | 1824 | 720 | 1.961 | 1.3214 | 45 | 0.63956 | 0 | 2.625 | 1.9854 | 1.9854 |  | 1.05 | 2.5
89 | SS-35/10kV Bessonovka | 6,3+6,3 | 6336 | 2568 | 6.8366 | 0.918 | 120 | 5.9186 | 0 | 6.615 | 0.69637 | 0.69637 |  | 1.05 | 6.3
90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 1008 | 336 | 1.0625 | 0.522 | 45 | 0.54053 | 0 | 1.68 | 1.1395 | 1.1395 |  | 1.05 | 1.6
91 | SS-35/10kV V.Mikhailovka | 4+4 | 1968 | 816 | 2.1305 | 1.45 | 80 | 0.68046 | 0 | 4.2 | 3.5195 | 3.5195 |  | 1.05 | 4
92 | SS-35/10kV Varvarovka | 2,5+2,5 | 1648 | 696 | 1.7889 | 1.0795 | 120 | 0.70939 | 0 | 2.625 | 1.9156 | 1.9156 |  | 1.05 | 2.5
93 | SS-35/10kV Vengerovka | 2,5+2,5 | 1164 | 348 | 1.2149 | 0.4 | 120 | 0.81491 | 0 | 2.625 | 1.8101 | 1.8101 |  | 1.05 | 2.5
94 | SS-35/10kV Verkhopenye | 2,5+4 | 1448 | 616 | 1.5736 | 1.0177 | 45 | 0.55593 | 0 | 2.625 | 2.0691 | 2.0691 |  | 1.05 | 2.5
95 | SS-35/10kV Viktoropol | 2,5+4 | 1344 | 508 | 1.4368 | 0.95536 | 120 | 0.48145 | 0 | 2.625 | 2.1436 | 2.1436 |  | 1.05 | 2.5
96 | SS-35/10kV Vislaya Dubrava | 4+4 | 1956 | 624 | 2.0531 | 0.616 | 80 | 1.4371 | 0 | 4.2 | 2.7629 | 2.7629 |  | 1.05 | 4
97 | SS-35/10kV Vladimirovka | 4+4 | 679 | 430 | 0.8037 | 0 |  | 0.8037 | 0 | 4.2 | 3.3963 | 3.3963 |  | 1.05 | 4
98 | SS-35/10kV Water storage | 4+6,3 | 2040 | 588 | 2.1231 | 0.305 | 45 | 1.8181 | 0 | 4.2 | 2.3819 | 2.3819 |  | 1.05 | 4
99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 3586 | 1282 | 3.8083 | 1.43 | 120 | 2.3783 | 0 | 6.615 | 4.2367 | 4.2367 |  | 1.05 | 6.3
100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 1578 | 618 | 1.6947 | 0.99513 | 120 | 0.69957 | 0 | 2.625 | 1.9254 | 1.9254 |  | 1.05 | 2.5
101 | SS-35/10kV Glinnoe | 6,3+6,3 | 2816 | 1664 | 3.2709 | 1.4036 | 80 | 1.8673 | 0 | 6.615 | 4.7477 | 4.7477 |  | 1.05 | 6.3
102 | SS-35/10kV Golovchino | 2,5+2,5 | 2592 | 960 | 2.7641 | 0.617 | 45 | 2.1471 | 0 | 2.625 | 0.47793 | 0.47793 |  | 1.05 | 2.5
103 | SS-35/10kV Gora-Podol | 2,5+4 | 1464 | 596 | 1.5807 | 0.9085 | 45 | 0.67217 | 0 | 2.625 | 1.9528 | 1.9528 |  | 1.05 | 2.5
104 | SS-35/10kV Gorodishche | 4+4 | 2816 | 1440 | 3.1628 | 0 |  | 3.1628 | 0 | 4.2 | 1.0372 | 1.0372 |  | 1.05 | 4
105 | SS-35/10kV Dmitrievka | 4+4 | 1164 | 552 | 1.2883 | 0.78237 | 80 | 0.50588 | 0 | 4.2 | 3.6941 | 3.6941 |  | 1.05 | 4
106 | SS-35/10kV Dorogoshch | 4+4 | 2384 | 952 | 2.5671 | 1.054 | 45 | 1.5131 | 0 | 4.2 | 2.6869 | 2.6869 |  | 1.05 | 4
107 | SS-35/10kV Dragunka | 2,5+2,5 | 800 | 312 | 0.85869 | 0.62999 | 80 | 0.2287 | 0 | 2.625 | 2.3963 | 2.3963 |  | 1.05 | 2.5
108 | SS-35/10kV Zhuravlevka | 2,5+4 | 1552 | 392 | 1.6007 | 0.274 | 80 | 1.3267 | 0 | 2.625 | 1.2983 | 1.2983 |  | 1.05 | 2.5
109 | SS-35/6kV Zhuravliki | 10+10 | 7248 | 2448 | 7.6502 | 4.051 | 120 | 3.5992 | 0 | 10.5 | 6.9008 | 6.9008 |  | 1.05 | 10
110 | SS-35/10kV Zavidovka | 2,5+2,5 | 876 | 492 | 1.0047 | 0.42 | 80 | 0.58471 | 0 | 2.625 | 2.0403 | 2.0403 |  | 1.05 | 2.5
111 | SS-35/6kV Zapadnaya | 10+10+10 | 6216 | 3216 | 6.9987 | 1.707 | 120 | 5.2917 | 0 | 21 | 15.7083 | 15.7083 |  | 1.05 | 20
112 | SS-35/10kV Zozuli | 6,3+6,3 | 5808 | 2528 | 6.3343 | 3.88 | 80 | 2.4543 | 0 | 6.615 | 4.1607 | 4.1607 |  | 1.05 | 6.3
113 | SS-35/10kV Ivitsa | 2,5+2,5 | 1056 | 376 | 1.1209 | 0.58603 | 80 | 0.53491 | 0 | 2.625 | 2.0901 | 2.0901 |  | 1.05 | 2.5
114 | SS-35/10kV Ilovka | 4+4 | 2264 | 848 | 2.4176 | 2.056 | 45 | 0.3616 | 0 | 4.2 | 3.8384 | 3.8384 |  | 1.05 | 4
115 | SS-35/10kV Istobnoe | 4+2,5 | 1128 | 592 | 1.2739 | 0.93935 | 120 | 0.33456 | 0 | 2.625 | 2.2904 | 2.2904 |  | 1.05 | 2.5
116 | SS-35/10kV Kazatskaya | 2,5+4 | 1293 | 458 | 1.3717 | 0.87141 | 45 | 0.50031 | 0 | 2.625 | 2.1247 | 2.1247 |  | 1.05 | 2.5
117 | SS-35/10kV Kazinka | 4+4 | 2784 | 924 | 2.9333 | 0.736 | 120 | 2.1973 | 0 | 4.2 | 2.0027 | 2.0027 |  | 1.05 | 4
118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 972 | 328 | 1.0258 | 0.712 | 120 | 0.31385 | 0 | 2.625 | 2.3112 | 2.3112 |  | 1.05 | 2.5
119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 3000 | 1284 | 3.2632 | 0.7035 | 120 | 2.5597 | 0 | 6.615 | 4.0553 | 4.0553 |  | 1.05 | 6.3
120 | SS-35/10kV Kotovo | 2,5+2,5 | 2384 | 752 | 2.4998 | 1.648 | 20 | 0.85178 | 0 | 2.625 | 1.7732 | 1.7732 |  | 1.05 | 2.5
121 | SS-35/10kV Kochetovka | 2,5+4 | 684 | 240 | 0.72488 | 0.6286 | 45 | 0.096288 | 0 | 2.625 | 2.5287 | 2.5287 |  | 1.05 | 2.5
122 | SS-35/10kV Krasnoe | 4+2,5 | 1040 | 416 | 1.1201 | 1.1395 | 80 | -0.019407 | 0 | 2.625 | 2.6444 | 2.6444 |  | 1.05 | 2.5
123 | SS-35/10kV Kretovo | 4+2,5 | 1116 | 468 | 1.2102 | 0.67818 | 120 | 0.53198 | 0 | 2.625 | 2.093 | 2.093 |  | 1.05 | 2.5
124 | SS-35/10kV Kurasovka | 4+4 | 2768 | 1408 | 3.1055 | 1.797 | 80 | 1.3085 | 0 | 4.2 | 2.8915 | 2.8915 |  | 1.05 | 4
125 | SS-35/6kV Lebedi | 4+5,6 | 3801 | 1252 | 4.0019 | 0.581 | 120 | 3.4209 | 0 | 4.2 | 0.77911 | 0.77911 |  | 1.05 | 4
126 | SS-35/6kV Ledovaya | 4+4 | 2520 | 1239 | 2.8081 | 1.321 | 80 | 1.4871 | 0 | 4.2 | 2.7129 | 2.7129 |  | 1.05 | 4
127 | SS-35/10kV Livenka | 4+4 | 3528 | 1776 | 3.9498 | 1.541 | 120 | 2.4088 | 0 | 4.2 | 1.7912 | 1.7912 |  | 1.05 | 4
128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 768 | 324 | 0.83355 | 0.66672 | 80 | 0.16683 | 0 | 2.625 | 2.4582 | 2.4582 |  | 1.05 | 2.5
129 | SS-35/10kV M.Pristan | 6,3+6,3 | 6768 | 3336 | 7.5455 | 1.81 | 45 | 5.7355 | 0 | 6.615 | 0.87949 | 0.87949 |  | 1.05 | 6.3
130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 792 | 336 | 0.86033 | 0.60716 | 80 | 0.25316 | 0 | 2.625 | 2.3718 | 2.3718 |  | 1.05 | 2.5
131 | SS-35/10kV Malinovka | 10+10 | 6400 | 3728 | 7.4066 | 1.357 | 120 | 6.0496 | 0 | 10.5 | 4.4504 | 4.4504 |  | 1.05 | 10
132 | SS-35/10kV Mandrovo | 2,5+2,5 | 1152 | 288 | 1.1875 | 0.65565 | 80 | 0.53181 | 0 | 2.625 | 2.0932 | 2.0932 |  | 1.05 | 2.5
133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 1236 | 462 | 1.3195 | 0.643 | 80 | 0.67652 | 0 | 2.625 | 1.9485 | 1.9485 |  | 1.05 | 2.5
134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 1176 | 492 | 1.2748 | 0.59315 | 120 | 0.68162 | 0 | 2.625 | 1.9434 | 1.9434 |  | 1.05 | 2.5
135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 608 | 288 | 0.67276 | 2.78 | 120 | -2.1072 | 0 | #VALUE! | #VALUE! | #VALUE! |  | 1.05 | 6,3
136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 3312 | 1248 | 3.5393 | 0.842 | 45 | 2.6973 | 0 | 6.615 | 3.9177 | 3.9177 |  | 1.05 | 6.3
137 | SS-35/10kV N.Ukolovo | 4+2,5 | 1436 | 580 | 1.5487 | 0.57 | 80 | 0.97871 | 0 | 2.625 | 1.6463 | 1.6463 |  | 1.05 | 2.5
138 | SS-35/10kV N.Khutornoe | 2,5+4 | 279 | 99 | 0.29604 | 0.19 | 80 | 0.10604 | 0 | 2.625 | 2.519 | 2.519 |  | 1.05 | 2.5
139 | SS-35/10kV Neminushchee | 2,5+2,5 | 1674 | 560 | 1.7652 | 0.65147 | 80 | 1.1137 | 0 | 2.625 | 1.5113 | 1.5113 |  | 1.05 | 2.5
140 | SS-35/10kV Nechaevka | 4+4 | 1304 | 416 | 1.3687 | 0.451 | 120 | 0.91775 | 0 | 4.2 | 3.2823 | 3.2823 |  | 1.05 | 4
141 | SS-35/10kV Nikitovka | 2,5+2,5 | 1856 | 648 | 1.9659 | 1.4354 | 80 | 0.53044 | 0 | 2.625 | 2.0946 | 2.0946 |  | 1.05 | 2.5
142 | SS-35/10kV Novenkoe | 4+4 | 2056 | 600 | 2.1418 | 1.7332 | 80 | 0.40855 | 0 | 4.2 | 3.7915 | 3.7915 |  | 1.05 | 4
143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 6128 | 2176 | 6.5029 | 0.872 | 80 | 5.6309 | 0 | 6.615 | 0.98413 | 0.98413 |  | 1.05 | 6.3
144 | SS-35/10kV Orlik | 4+4 | 1836 | 756 | 1.9856 | 0.553 | 80 | 1.4326 | 0 | 4.2 | 2.7674 | 2.7674 |  | 1.05 | 4
145 | SS-35/10kV Podolkhi | 2,5+2,5 | 2014 | 792 | 2.1641 | 1.1225 | 45 | 1.0416 | 0 | 2.625 | 1.5834 | 1.5834 |  | 1.05 | 2.5
146 | SS-35/10kV Popovka | 6,3+4 | 1152 | 532 | 1.2689 | 0.64636 | 80 | 0.62255 | 0 | 4.2 | 3.5775 | 3.5775 |  | 1.05 | 4
147 | SS-35/10kV Prelestnoe | 4+4 | 4020 | 1524 | 4.2992 | 0 |  | 4.2992 | 0 | 4.2 | -0.099183 | -0.099183 |  | 1.05 | 4
148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 5242 | 2492 | 5.8042 | 0 |  | 5.8042 | 0 | 6.615 | 0.81081 | 0.81081 |  | 1.05 | 6.3
149 | SS-35/10kV Prilepy | 2,5+2,5 | 600 | 378 | 0.70914 | 0.37638 | 80 | 0.33277 | 0 | 2.625 | 2.2922 | 2.2922 |  | 1.05 | 2.5
150 | SS-35/10kV Printsevka | 2,5+2,5 | 1616 | 640 | 1.7381 | 0.352 | 120 | 1.3861 | 0 | 2.625 | 1.2389 | 1.2389 |  | 1.05 | 2.5
151 | SS-35/10kV Radkovka | 6,3+6,3 | 4736 | 1888 | 5.0985 | 0.164 | 45 | 4.9345 | 0 | 6.615 | 1.6805 | 1.6805 |  | 1.05 | 6.3
152 | SS-35/10kV Razdornoe | 2,5+2,5 | 1278 | 684 | 1.4495 | 0.662 | 80 | 0.78753 | 0 | 2.625 | 1.8375 | 1.8375 |  | 1.05 | 2.5
153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 1536 | 744 | 1.7067 | 0.88491 | 80 | 0.82179 | 0 | 2.625 | 1.8032 | 1.8032 |  | 1.05 | 2.5
154 | SS-35/10kV Rzhevka | 10+10 | 5736 | 2664 | 6.3244 | 2.53 | 45 | 3.7944 | 0 | 10.5 | 6.7056 | 6.7056 |  | 1.05 | 10
155 | SS-35/10kV Rovenki | 4+4 | 3000 | 1188 | 3.2267 | 1.7393 | 120 | 1.4874 | 0 | 4.2 | 2.7126 | 2.7126 |  | 1.05 | 4
156 | SS-35/10kV Rogovatoe | 4+4 | 1648 | 736 | 1.8049 | 0 |  | 1.8049 | 0 | 2.625 | 0.82012 | 0.82012 |  | 1.05 | 2.5
157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 805 | 381 | 0.89061 | 0 | 0 | 0.89061 | 0 | 2.625 | 1.7344 | 1.7344 |  | 1.05 | 2.5
158 | SS-35/10kV Saprykino | 2,5+2,5 | 288 | 152 | 0.32565 | 0.22751 | 120 | 0.098137 | 0 | 2.625 | 2.5269 | 2.5269 |  | 1.05 | 2.5
159 | SS-35/6kV Severnaya | 6,3+6,3 | 6278 | 1901 | 6.5595 | 4.8049 | 120 | 1.7546 | 0 | 6.615 | 4.8604 | 4.8604 |  | 1.05 | 6.3
160 | SS-35/10kV Setishche | 2,5+2,5 | 1806 | 754 | 1.9571 | 1.0621 | 80 | 0.89496 | 0 | 2.625 | 1.73 | 1.73 |  | 1.05 | 2.5
161 | SS-35/10kV Slonovka | 4+4 | 2288 | 1184 | 2.5762 | 1.1306 | 120 | 1.4456 | 0 | 4.2 | 2.7544 | 2.7544 |  | 1.05 | 4
162 | SS-35/6kV St.Oskol -2 | 16+16 | 10742 | 4668 | 11.7124 | 1.21 | 80 | 10.5024 | 0 | 16.8 | 6.2976 | 6.2976 |  | 1.05 | 16
163 | SS-35/10kV Starikovo | 4+4 | 2028 | 684 | 2.1402 | 1.3453 | 45 | 0.79494 | 0 | 4.2 | 3.4051 | 3.4051 |  | 1.05 | 4
164 | SS-35/10kV Tavrovo | 10+10 | 8592 | 1656 | 8.7501 | 0.531 | 45 | 8.2191 | 0 | 10.5 | 2.2809 | 2.2809 |  | 1.05 | 10
165 | SS-35/10kV Terebrino | 2,5+2,5 | 960 | 504 | 1.0843 | 0.44978 | 80 | 0.63448 | 0 | 2.625 | 1.9905 | 1.9905 |  | 1.05 | 2.5
166 | SS-35/10kV Urazovo | 6,3+6,3 | 4116 | 1140 | 4.271 | 1.39 | 120 | 2.881 | 0 | 6.615 | 3.734 | 3.734 |  | 1.05 | 6.3
167 | SS-35/10kV Utochka | 1,6+2,5 | 728 | 284 | 0.78143 | 0.47242 | 80 | 0.30902 | 0 | 1.68 | 1.371 | 1.371 |  | 1.05 | 1.6
168 | SS-35/6kV Fedoseevka | 4+4 | 1795 | 643 | 1.9067 | 0 |  | 1.9067 | 0 | 4.2 | 2.2933 | 2.2933 |  | 1.05 | 4
169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 872 | 392 | 0.95606 | 0.78681 | 45 | 0.16925 | 0 | 1.68 | 1.5107 | 1.5107 |  | 1.05 | 1.6
170 | SS-35/10kV Kholodnoe | 4+4 | 1796 | 556 | 1.8801 | 0 |  | 1.8801 | 0 | 4.2 | 2.3199 | 2.3199 |  | 1.05 | 4
171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 2160 | 1500 | 2.6298 | 1.3513 | 20 | 1.2785 | 0 | 6.615 | 5.3365 | 5.3365 |  | 1.05 | 6.3
172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0 | 0 | 0 | 1 | 80 | -1 | 0 | 2.625 | 3.625 | 3.625 |  | 1.05 | 2.5
173 | SS-35/10kV Shatalovka | 6,3+6,3 | 1704 | 744 | 1.8593 | 0 |  | 1.8593 | 0 | 6.615 | 4.7557 | 4.7557 |  | 1.05 | 6.3
174 | SS-35/10kV Shakhovka | 2,5+2,5 | 1668 | 582 | 1.7666 | 0.79066 | 80 | 0.97596 | 0 | 2.625 | 1.649 | 1.649 |  | 1.05 | 2.5
175 | SS-35/10kV Shishino | 6,3+6,3 | 3376 | 944 | 3.5055 | 1.03 | 80 | 2.4755 | 0 | 4.2 | 1.7245 | 1.7245 |  | 1.05 | 4
176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 254 | 197 | 0.32144 | 0 | 0 | 0.32144 | 0 | 1.68 | 1.3586 | 1.3586 |  | 1.05 | 1.6
177 | SS-35/10kV Yablonovo | 4+4 | 1440 | 624 | 1.5694 | 1.1284 | 80 | 0.44096 | 0 | 4.2 | 3.759 | 3.759 |  | 1.05 | 4
178 | SS-35/10kV Yarskoe | 2,5+2,5 | 492 | 204 | 0.53262 | 0.14648 | 80 | 0.38614 | 0 | 2.625 | 2.2389 | 2.2389 |  | 1.05 | 2.5
| TOTAL: | 3271.1 |  |  | 1637.6648 | 638.6111 |  | #N/A | [5 empty] | 1.05
| deficit | [10 empty] | -21.3453 |  | 1.05
| proficit | [10 empty] | #VALUE! |  | 1.05

## МРСК 2
Table 2
No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note | Примечание
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
[5 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations
1 | SS-110/35/10kV D.Polyana | 6.3 | 0 | 0.32073 | 1.457 | 45 | -1.1363 | 0 | 1.457 | 1.1363 | 0.20865 |  |  |  |  | 6.3
0 | S nom MV, МVА | 6.3 | 0 | 0.048374 | 0.958 |  | -0.90963 | 0 | 0.958 | 0.90963 | [5 empty] | 0
0 | S nom LV, МVА | 6.3 | 0 | 0.29035 | 0.499 |  | -0.20865 | 0 | 0.499 | 0.20865 | [5 empty] | 0
2 | SS-110/35/10kV Konshino | 6.3 | 0 | 0.40991 | 0.39 | 20 | 0.01991 | 0 | 0.39 | -0.01991 | -0.01991 |  |  |  |  | 6.3
0 | S nom MV, МVА | 6.3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
0 | S nom LV, МVА | 6.3 | 0 | 0.40991 | 0.39 |  | 0.01991 | 0 | 0.39 | -0.01991 | [5 empty] | 0
3 | SS-110/35/10kV Orositelnaya | 16 | 0 | 14.6466 | 11.607 | 120 | 3.0396 | 0 | 11.607 | -3.0396 | -3.0396 |  |  |  |  | 16
0 | S nom MV, МVА | 16 | 0 | 9.1445 | 8.606 |  | 0.5385 | 0 | 8.606 | -0.5385 | [5 empty] | 0
0 | S nom LV, МVА | 16 | 0 | 5.5027 | 3.001 |  | 2.5017 | 0 | 3.001 | -2.5017 | [5 empty] | 0
4 | SS-110/35/10kV Rovenki | 16 | 0 | 2.4016 | 3.44 | 120 | -1.0384 | 0 | 3.44 | 1.0384 | 1.0384 |  |  |  |  | 16
0 | S nom MV, МVА | 16 | 0 | 0.034059 | 4 |  | -3.9659 | 0 | 4 | 3.9659 | [5 empty] | 0
0 | S nom LV, МVА | 16 | 0 | 2.386 | 3.44 |  | -1.054 | 0 | 3.44 | 1.054 | [5 empty] | 0
5 | SS-110/35/10kV Serebryanka | 10 | 0 | 1.0414 | 1.78 | 45 | -0.73862 | 0 | 1.78 | 0.73862 | 0 |  |  |  |  | 10
0 | S nom MV, МVА | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
0 | S nom LV, MVА | 10 | 0 | 1.0414 | 1.78 |  | -0.73862 | 0 | 1.78 | 0.73862 | [5 empty] | 0
6 | SS-35/10kV Afanasyevka | 1.6 | 0 | 0.83522 | 0.6464 | 45 | 0.18882 | 0 | 0.6464 | -0.18882 | -0.18882 |  |  |  |  | 1.6
7 | SS-35/10kV Borisovka | 1.6 | 0 | 0.80768 | 0.6835 | 45 | 0.12418 | 0 | 0.6835 | -0.12418 | -0.12418 |  |  |  |  | 1.6
8 | SS-35/10kV Borisy | 1.6 | 0 | 0.85907 | 0 | 20 | 0.85907 | 0 | 0 | -0.85907 | -0.85907 |  |  |  |  | 1.6
9 | SS-35/10kV Gostishchevo | 4 | 0 | 3.2103 | 2.64 | 80 | 0.57031 | 0 | 2.64 | -0.57031 | -0.57031 |  |  |  |  | 4
10 | SS-35/10kV Gruzskoe | 1.6 | 0 | 0.75944 | 1.05 | 80 | -0.29056 | 0 | 1.05 | 0.29056 | 0.29056 |  |  |  |  | 1.6
11 | SS-35/10kV Zemsnaryad | 1.6 | 0.19 | 0.2136 | 0 |  | 0.2136 | 0 | 0 | -0.2136 | -0.2136 |  |  |  | 0.19 | 1.6
12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 0 | 0.34986 | 0 |  | 0.34986 | 0 | 0 | -0.34986 | -0.34986 |  |  |  |  | 2.5
13 | SS-35/10kV Kamyzino | 2.5 | 0 | 0.95696 | 0.541 | 45 | 0.41596 | 0 | 0.541 | -0.41596 | -0.41596 |  |  |  |  | 2.5
14 | SS-35/10kV Koloskovo | 2.5 | 0 | 1.6799 | 1.6626 | 45 | 0.017324 | 0 | 1.6626 | -0.017324 | -0.017324 |  |  |  |  | 2.5
15 | SS-35/10jkV Kryukovo | 2.5 | 0 | 1.6357 | 1.55 | 45 | 0.085746 | 0 | 1.55 | -0.085746 | -0.085746 |  |  |  |  | 2.5
16 | SS-35/10kV Kushchino | 1.6 | 0 | 0.35293 | 0.4101 | 80 | -0.057169 | 0 | 0.4101 | 0.057169 | 0.057169 |  |  |  |  | 1.6
17 | SS-35/10kV Lopukhinka | 2.5 | 0 | 0.33638 | 0.407 | 20 | -0.070619 | 0 | 0.407 | 0.070619 | 0.070619 |  |  |  |  | 2.5
18 | SS-35/10kV Malakeevo | 2.5 | 0.19 | 1.4995 | 1.38 | 120 | 0.11954 | 0 | 1.38 | -0.11954 | -0.11954 |  |  |  | 0.19 | 2.5
19 | SS-35/10kV Murom | 2.5 | 0.4 | 1.355 | 1.54 | 45 | -0.18505 | 0 | 1.54 | 0.18505 | 0.18505 |  |  |  | 0.4 | 2.5
20 | SS-35/10kV Nikolaevka | 2.5 | 0.19 | 0.90644 | 0.6647 | 45 | 0.24174 | 0 | 0.6647 | -0.24174 | -0.24174 |  |  |  | 0.19 | 2.5
21 | SS-35/10kV Nikolskoe | 4 | 0.03 | 1.6133 | 0.78 | 120 | 0.83327 | 0 | 0.78 | -0.83327 | -0.83327 |  |  |  | 0.03 | 4
22 | SS-35/10kV Pokrovka | 4 | 0 | 0.63871 | 0.722 | 45 | -0.083289 | 0 | 0.722 | 0.083289 | 0.083289 |  |  |  |  | 4
23 | SS-35/10kV Pyatnitskoe | 4 | 0.02 | 2.5223 | 1.84 | 80 | 0.68234 | 0 | 1.84 | -0.68234 | -0.68234 |  |  |  | 0.02 | 4
24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 0 | 0.14166 | 1.676 | 80 | -1.5343 | 0 | 1.676 | 1.5343 | 1.5343 |  |  |  |  | 2.5
25 | SS-35/10kV Svistovka | 2.5 | 0 | 0.55154 | 0.6872 | 45 | -0.13566 | 0 | 0.6872 | 0.13566 | 0.13566 |  |  |  |  | 2.5
26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 0 | 0.59965 | 0.7238 | 120 | -0.12415 | 0 | 0.7238 | 0.12415 | 0.12415 |  |  |  |  | 2.5
27 | SS-35/10kV Kharkovskaya | 2.5 | 0 | 0.60033 | 0.6797 | 120 | -0.079367 | 0 | 0.6797 | 0.079367 | 0.079367 |  |  |  |  | 2.5
Two- and more transformer substations | [15 empty] | 110.2
28 | SS-110/6kV Automobile maintenance plant | 16+16 | 0.6 | 12.9565 | 3.561 | 45 | 9.3955 | 0 | 16.8 | 7.4045 | 7.4045 |  | 1.05 | 16 | 0.6 | 16+16 | 32
29 | SS-110/35/10kV Aydar | 16+10 | 0 | 8.8344 | 8.95 | 120 | -0.11561 | 0 | 10.5 | 10.6156 | 10.3916 |  | 1.05 | 10 |  | 16+10 | 26
0 | S nom MV, МVА | 16+10 | 0 | 7.3984 | 7.29 |  | 0.10839 | 0 | 10.5 | 10.3916 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 16+10 | 0 | 1.436 | 1.66 |  | -0.22399 | 0 | 10.5 | 10.724 |  |  | 1.05 | 10 |  | 0
30 | SS-110/35/10kV Alexandrovka | 25+25 | 11.83 | 20.3439 | 8.37 | 80 | 11.9739 | 0 | 26.25 | 14.2761 | 14.2761 |  | 1.05 | 16 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 7.7821 | 6.697 |  | 1.0851 | 0 | 26.25 | 25.1649 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 25+25 | 11.83 | 12.8077 | 1.673 |  | 11.1347 | 0 | 26.25 | 15.1153 |  |  | 1.05 | 16 | 11.83 | 0
31 | SS-110/35/10kV Alexeevka | 25+25+25 | 0.12 | 44.2305 | 5.322 | 120 | 38.9085 | 0 | 52.5 | 13.5915 | 13.5915 |  | 1.05 | 41 |  | 25+25+25 | 75
0 | S nom MV, МVА | 25+25+25 | 0 | 19.2626 | 3.102 |  | 16.1606 | 0 | 52.5 | 36.3394 |  |  | 1.05 | 41 |  | 0
0 | S nom LV, МVА | 25+25+25 | 0.12 | 24.9681 | 2.22 |  | 22.7481 | 0 | 52.5 | 29.7519 |  |  | 1.05 | 41 | 0.12 | 0
32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 0 | 9.8259 | 8.87 | 45 | 0.9559 | 0 | 10.5 | 9.5441 | 9.5441 |  | 1.05 | 10 |  | 10+16 | 26
0 | S nom MV, МVА | 10+16 | 0 | 9.2697 | 8.867 |  | 0.40268 | 0 | 10.5 | 10.0973 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 10+16 | 0 | 0.55665 | 0 |  | 0.55665 | 0 | 10.5 | 9.9434 |  |  | 1.05 | 10 |  | 0
33 | SS-110/6kV Belgorod-1 | 40+48 | 0.85 | 41.3137 | 0 | 120 | 41.3137 | 0 | 42 | 0.68631 | 0.68631 |  | 1.05 | 40 | 0.85 | 40+48 | 88
34 | SS-110/35/10kV Borisovka | 16+16 | 0 | 12.3985 | 11.433 | 120 | 0.96547 | 0 | 16.8 | 15.8345 | 5.4899 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+8 | 0 | 6.2003 | 8.133 |  | -1.9327 | 0 | 8.4 | 10.3327 |  |  | 1.05 | 8 |  | 0
0 | S nom LV, МVА | 16+8 | 0 | 6.2101 | 3.3 |  | 2.9101 | 0 | 8.4 | 5.4899 |  |  | 1.05 | 8 |  | 0
35 | SS-110/35/10kV V.Pokrovka | 10+10 | 0.01 | 10.2315 | 11.5 | 120 | -1.2685 | 0 | 10.5 | 11.7685 | 9.2237 |  | 1.05 | 10 |  | 10+10 | 20
0 | S nom MV, МVА | 10+10 | 0 | 9.0763 | 7.8 |  | 1.2763 | 0 | 10.5 | 9.2237 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 10+10 | 0.01 | 1.1592 | 3.7 |  | -2.5408 | 0 | 10.5 | 13.0408 |  |  | 1.05 | 10 | 0.01 | 0
36 | SS-110/35/10kV Veydelevka | 10+10 | 0.79 | 9.6295 | 8.83 | 120 | 0.79949 | 0 | 10.5 | 9.7005 | 9.675 |  | 1.05 | 10 |  | 10+10 | 20
0 | S nom MV, МVА | 10+10 | 0 | 4.78 | 3.955 |  | 0.82505 | 0 | 10.5 | 9.675 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 10+10 | 0.79 | 4.8497 | 4.875 |  | -0.02529 | 0 | 10.5 | 10.5253 |  |  | 1.05 | 10 | 0.79 | 0
37 | SS-110/6kV Vitamin plant | 25+25 | 1.85 | 17.66 | 1.46 | 45 | 16.2 | 0 | 26.25 | 10.05 | 10.05 |  | 1.05 | 25 | 1.85 | 25+25 | 50
38 | SS-110/35/10kV Volokonovka | 25+25 | 0.05 | 19.7767 | 10.651 | 120 | 9.1257 | 0 | 26.25 | 17.1243 | 17.1243 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 10.8024 | 8.576 |  | 2.2264 | 0 | 26.25 | 24.0236 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+25 | 0.05 | 8.9747 | 2.075 |  | 6.8997 | 0 | 26.25 | 19.3503 |  |  | 1.05 | 25 | 0.05 | 0
39 | SS-110/35/6kV Vostochnaya | 25+25 | 3.05 | 43.2347 |  | 120 | 43.2347 | 0 | 26.25 | -16.9847 | -16.9847 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 16.6454 |  |  | 16.6454 | 0 | 26.25 | 9.6046 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+25 | 3.05 | 26.7568 |  |  | 26.7568 | 0 | 26.25 | -0.50681 |  |  | 1.05 | 25 | 3.05 | 0
40 | SS-110/10/6kV Golofeevka | 16+16 | 0 | 2.2207 | 0 |  | 2.2207 | 0 | 26.25 | 24.0293 | 10.9043 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 16+16 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125 |  |  | 1.05 | 12.5 |  | 0
0 | S nom LV, МVА | 16+16 | 0 | 2.2207 | 0 |  | 2.2207 | 0 | 13.125 | 10.9043 |  |  | 1.05 | 12.5 |  | 0
41 | SS-110/10kV Gotnya | 16+16 | 0.45 | 10.0554 | 6.43 | 120 | 3.6254 | 0 | 16.8 | 13.1746 | 13.1746 |  | 1.05 | 16 | 0.45 | 16+16 | 32
42 | SS-110/35/10kV Grayvoron | 16+16 | 0.02 | 20.7625 | 13.953 | 80 | 6.8095 | 0 | 16.8 | 9.9905 | 6.9744 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 8.6118 | 10.903 |  | -2.2912 | 0 | 16.8 | 19.0912 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0.02 | 12.8756 | 3.05 |  | 9.8256 | 0 | 16.8 | 6.9744 |  |  | 1.05 | 16 | 0.02 | 0
43 | SS-110/6kV Donets | 40+40 | 0.62 | 26.4246 | 6.73 | 120 | 19.6946 | 0 | 42 | 22.3054 | 22.3054 |  | 1.05 | 40 | 0.62 | 40+40 | 80
44 | SS-110/10kV Dubovoe | 40+40 | 1.12 | 24.0817 | 11.23 | 120 | 12.8517 | 0 | 42 | 29.1483 | 29.1483 |  | 1.05 | 40 | 1.12 | 40+40 | 80
45 | SS-110/35/6kV Zhuravliki | 40+25 | 0 | 21.3997 | 12.4 | 120 | 8.9997 | 0 | 42 | 33.0003 | 32.261 |  | 1.05 | 40 |  | 40+25 | 65
0 | S nom MV, МVА | 40+25 | 0 | 15.966 | 6.227 |  | 9.739 | 0 | 42 | 32.261 |  |  | 1.05 | 40 |  | 0
0 | S nom LV, МVА | 40+25 | 0 | 5.4972 | 6.173 |  | -0.67583 | 0 | 42 | 42.6758 |  |  | 1.05 | 40 |  | 0
46 | SS-110/10kV Zapadnaya | 16+16 | 0.88 | 17.2658 | 1.249 | 80 | 16.0168 | 0 | 16.8 | 0.78325 | 0.78325 |  | 1.05 | 16 | 0.88 | 16+16 | 32
47 | SS-110/35/10kV Ivnya | 10+10 | 0 | 12.6162 | 6.16 | 80 | 6.4562 | 0 | 10.5 | 4.0438 | 3.8937 |  | 1.05 | 10 |  | 10+10 | 20
0 | S nom MV, МVА | 10+10 | 0 | 8.9813 | 2.375 |  | 6.6063 | 0 | 10.5 | 3.8937 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 10+10 | 0 | 3.635 | 3.785 |  | -0.15004 | 0 | 10.5 | 10.65 |  |  | 1.05 | 10 |  | 0
48 | SS-110/35/10kV K.Gvardiya | 16+16 | 0.04 | 14.6775 | 7.7116 | 120 | 6.9659 | 0 | 16.8 | 9.8341 | 9.8341 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 7.609 | 4.854 |  | 2.755 | 0 | 16.8 | 14.045 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0.04 | 7.0774 | 2.8576 |  | 4.2198 | 0 | 16.8 | 12.5802 |  |  | 1.05 | 16 | 0.04 | 0
49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 0 | 11.8955 | 9.65 | 80 | 2.2455 | 0 | 26.25 | 24.0045 | 20.0068 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 1.6531 | 1.384 |  | 0.26909 | 0 | 26.25 | 25.9809 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+25 | 0 | 10.2432 | 4 |  | 6.2432 | 0 | 26.25 | 20.0068 |  |  | 1.05 | 25 |  | 0
50 | SS-110/35/10kV Korocha | 16+16+16 | 0.63 | 21.5884 | 2.019 | 20 | 19.5694 | 0 | 33.6 | 14.0306 | 14.0306 |  | 1.05 | 32 |  | 16+16+16 | 48
0 | S nom MV, МVА | 16+16+16 | 0 | 7.6269 | 1.719 |  | 5.9079 | 0 | 33.6 | 27.6921 |  |  | 1.05 | 32 |  | 0
0 | S nom LV, МVА | 16+16+16 | 0.63 | 13.9715 | 0.3 |  | 13.6715 | 0 | 33.6 | 19.9285 |  |  | 1.05 | 32 | 0.63 | 0
51 | SS-110/10kV Krapivenskaya | 10+10 | 0.01 | 10.3372 | 9.158 | 120 | 1.1792 | 0 | 10.5 | 9.3208 | 9.3208 |  | 1.05 | 10 |  | 10+10 | 20
52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 0 | 4.4995 | 3.52 |  | 0.97951 | 0 | 10.5 | 9.5205 |  |  | 1.05 | 10 |  | 0
0 | S nom MV, МVА | 10+10 | 0.01 | 5.8379 | 5.638 |  | 0.19991 | 0 | 10.5 | 10.3001 |  |  | 1.05 | 10 | 0.01 | 0
0 | S nom LV, МVА | 16+16 | 1.19 | 2.0247 | 0 | 0 | 2.0247 | 0 | 16.8 | 14.7753 | 14.7753 |  |  |  | 1.19 |  | 32
53 | SS-110/10/10kV Mayskaya | 40+40 | 0.26 | 6.5498 |  |  | 6.5498 | 0 | 42 | 35.4502 | 35.4502 |  | 1.05 | 16 | 0.26 | 16+16 | 80
54 | SS-110/35/10kV Maximovka | 16+16 | 0 | 10.0334 | 11.48 | 45 | -1.4466 | 0 | 16.8 | 18.2466 | 17.2826 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 8.4983 | 9.449 |  | -0.95071 | 0 | 16.8 | 17.7507 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0 | 1.5484 | 2.031 |  | -0.48264 | 0 | 16.8 | 17.2826 |  |  | 1.05 | 16 |  | 0
55 | SS-110/35/10kV N.Oskol | 25+31,5 | 0.13 | 19.5106 | 9.119 | 80 | 10.3916 | 0 | 26.25 | 15.8584 | 15.0937 |  | 1.05 | 25 |  | 25+31,5 | 56.5
0 | S nom MV, МVА | 25+31,5 | 0 | 7.0987 | 7.83 |  | -0.73133 | 0 | 26.25 | 26.9813 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+31,5 | 0.13 | 12.4453 | 1.289 |  | 11.1563 | 0 | 26.25 | 15.0937 |  |  | 1.05 | 25 | 0.13 | 0
56 | SS-110/10kV Obukhovskaya | 25+25 | 0 | 2.2874 | 0 |  | 2.2874 | 0 | 26.25 | 23.9626 | 23.9626 |  | 1.05 | 25 |  | 25+25 | 50
57 | SS-110/6kV Ochistnye | 16+16 | 0 | 5.1276 | 0 |  | 5.1276 | 0 | 16.8 | 11.6724 | 11.6724 |  | 1.05 | 16 |  | 16+16 | 32
58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 0 | 6.679 | 120 | -6.679 | 0 | 26.25 | 26.25 | 26.25 |  |  |  |  | 25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 0 | 2.022 |  | -2.022 | 0 | 26.25 | 26.25 | [5 empty] | 0
0 | S nom LV, МVА | 25+25 | 0 | 0 | 4.657 |  | -4.657 | 0 | 26.25 | 26.25 | [5 empty] | 0
59 | SS-110/10kV Promyshlennaya | 25+25 | 0 | 18.5411 | 0 |  | 18.5411 | 0 | 26.25 | 7.7089 | 7.7089 |  | 1.05 | 25 |  | 25+25 | 50
60 | SS-110/10kV Poultry plant | 16+16 | 0 | 14.486 | 1.296 | 80 | 13.19 | 0 | 16.8 | 3.61 | 3.61 |  | 1.05 | 16 |  | 16+16 | 32
61 | SS-110/10kV Pushkarnaya | 40+40 | 0 | 31.5718 | 0 | 60 | 31.5718 | 0 | 42 | 10.4282 | 10.4282 |  | 1.05 | 40 |  | 40+40 | 80
62 | SS-110/35/10kV Rakitnoe | 10+10 | 0.33 | 13.951 | 8.98 | 120 | 4.971 | 0 | 10.5 | 5.529 | 5.529 |  | 1.05 | 10 |  | 10+10 | 20
0 | S nom MV, МVА | 10+10 | 0 | 10.3292 | 6.407 |  | 3.9222 | 0 | 10.5 | 6.5778 |  |  | 1.05 | 10 |  | 0
0 | S nom LV, МVА | 10+10 | 0.33 | 3.6358 | 2.573 |  | 1.0628 | 0 | 10.5 | 9.4372 |  |  | 1.05 | 10 | 0.33 | 0
63 | SS-110/35/6kV Rudnik | 25+25 | 0.04 | 20.2703 | 10.46 | 45 | 9.8103 | 0 | 26.25 | 16.4397 | 16.4397 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 12.0739 | 10.46 |  | 1.6139 | 0 | 26.25 | 24.6361 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+25 | 0.04 | 8.2575 | 0 |  | 8.2575 | 0 | 26.25 | 17.9925 |  |  | 1.05 | 25 | 0.04 | 0
64 | SS-110/10kV Severnaya | 40+40 | 5.13 | 16.7733 | 3.312 | 45 | 13.4613 | 0 | 42 | 28.5387 | 28.5387 |  | 1.05 | 40 | 5.13 | 40+40 | 80
65 | SS-110/35/10kV Skorodnoe | 16+16 | 0 | 14.7836 | 10.36 | 120 | 4.4236 | 0 | 16.8 | 12.3764 | 12.3764 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 10.5636 | 7.562 |  | 3.0016 | 0 | 16.8 | 13.7984 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0 | 4.2207 | 2.798 |  | 1.4227 | 0 | 16.8 | 15.3773 |  |  | 1.05 | 16 |  | 0
66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 0.05 | 35.1035 | 0 |  | 35.1035 | 0 | 47.25 | 12.1465 | 12.1465 |  | 1.05 | 45 |  | 20+25+25 | 70
0 | S nom MV, МVА | 20+25+25 | 0 | 11.828 | 0 |  | 11.828 | 0 | 47.25 | 35.422 |  |  | 1.05 | 45 |  | 0
0 | S nom LV, МVА | 20+25+25 | 0.05 | 23.3849 | 0 |  | 23.3849 | 0 | 47.25 | 23.8651 |  |  | 1.05 | 45 | 0.05 | 0
67 | SS-110/35/10kV Streletskaya | 16+16 | 0.19 | 5.0978 | 2.23 | 80 | 2.8678 | 0 | 16.8 | 13.9322 | 5.4912 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+8 | 0 | 0.10197 | 0 |  | 0.10197 | 0 | 8.4 | 8.298 |  |  | 1.05 | 8 |  | 0
0 | S nom LV, МVА | 16+8 | 0.19 | 5.1388 | 2.23 |  | 2.9088 | 0 | 8.4 | 5.4912 |  |  | 1.05 | 8 | 0.19 | 0
68 | SS-110/6kV Stroitel | 15+15 | 0.49 | 14.2832 | 0 |  | 14.2832 | 0 | 15.75 | 1.4668 | 1.4668 |  | 1.05 | 15 | 0.49 | 15+15 | 30
69 | SS-110/35/10kV Tomarovka | 16+16 | 0.03 | 10.9036 | 3.46 | 45 | 7.4436 | 0 | 16.8 | 9.3564 | 8.8993 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 3.0077 | 3.46 |  | -0.45228 | 0 | 16.8 | 17.2523 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0.03 | 7.9007 | 0 |  | 7.9007 | 0 | 16.8 | 8.8993 |  |  | 1.05 | 16 | 0.03 | 0
70 | SS-110/6kV Chemical plant | 32+32 | 5 | 17.0088 | 5.56 | 45 | 11.4488 | 0 | 33.6 | 22.1512 | 22.1512 |  | 1.05 | 32 | 5 | 32+32 | 64
71 | SS-110/10kV Tsentralnaya | 40+40 | 0.01 | 27.8051 | 0 |  | 27.8051 | 0 | 42 | 14.1949 | 14.1949 |  | 1.05 | 40 | 0.01 | 40+40 | 80
72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 0.26 | 20.952 | 20.54 | 80 | 0.412 | 0 | 26.25 | 25.838 | 24.4211 |  | 1.05 | 25 |  | 25+25 | 50
0 | S nom MV, МVА | 25+25 | 0 | 19.1557 | 19.676 |  | -0.52034 | 0 | 26.25 | 26.7703 |  |  | 1.05 | 25 |  | 0
0 | S nom LV, МVА | 25+25 | 0.26 | 1.8289 | 0 |  | 1.8289 | 0 | 26.25 | 24.4211 |  |  | 1.05 | 25 | 0.26 | 0
73 | SS-110/35/10kV Chernyanka | 16+16 | 0.04 | 16.7374 | 5.969 | 120 | 10.7684 | 0 | 16.8 | 6.0316 | 6.0316 |  | 1.05 | 16 |  | 16+16 | 32
0 | S nom MV, МVА | 16+16 | 0 | 8.4371 | 5.969 |  | 2.4681 | 0 | 16.8 | 14.3319 |  |  | 1.05 | 16 |  | 0
0 | S nom LV, МVА | 16+16 | 0.04 | 8.3257 | 0 |  | 8.3257 | 0 | 16.8 | 8.4743 |  |  | 1.05 | 16 | 0.04 | 0
74 | SS-110/35/6kV Shebekino | 40+40 | 0.47 | 30.1453 | 16.65 | 120 | 13.4953 | 0 | 42 | 28.5047 | 28.5047 |  | 1.05 | 40 |  | 40+40 | 80
0 | S nom MV, МVА | 40+40 | 0 | 17.0792 | 11.682 |  | 5.3972 | 0 | 42 | 36.6028 |  |  | 1.05 | 40 |  | 0
0 | S nom LV, МVА | 40+40 | 0.47 | 13.0848 | 4.968 |  | 8.1168 | 0 | 42 | 33.8832 |  |  | 1.05 | 40 | 0.47 | 0
75 | SS-110/10kV Sheino | 3,2+10 | 0.04 | 3.4996 | 0 |  | 3.4996 | 0 | 3.36 | -0.13962 | -0.13962 |  | 1.05 | 3.2 | 0.04 | 3,2+10 | 13.2
76 | SS-110/10/6kV Yuzhnaya | 40+40 | 1.53 | 42.0245 | 12.94 | 120 | 29.0845 | 0 | 42 | 12.9155 | 12.9155 |  | 1.05 | 40 |  | 40+40 | 80
0 | S nom MV, МVА | 40+40 | 0 | 7.0097 | 3.42 |  | 3.5897 | 0 | 42 | 38.4103 |  |  | 1.05 | 40 |  | 0
0 | S nom LV, МVА | 40+40 | 1.53 | 35.0375 | 9.52 |  | 25.5175 | 0 | 42 | 16.4825 |  |  | 1.05 | 40 | 1.53 | 0
77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 0 | 0.75187 | 0.43267 | 120 | 0.31921 | 0 | 2.625 | 2.3058 | 2.3058 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 0 | 0.91585 | 0.46639 | 120 | 0.44946 | 0 | 2.625 | 2.1755 | 2.1755 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 0.12 | 2.6982 | 0 |  | 2.6982 | 0 | 4.2 | 1.5018 | 1.5018 |  | 1.05 | 2.5 | 0.12 | 4+4 | 8
80 | SS-35/10kV Annovka | 2,5+2,5 | 0 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
81 | SS-35/10kV Artelnoe | 6,3+6,3 | 0 | 4.6358 | 0.55 | 45 | 4.0858 | 0 | 6.615 | 2.5292 | 2.5292 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
82 | SS-35/10kV B.Dvory | 4+4 | 0 | 2.4839 | 1.191 | 120 | 1.2929 | 0 | 4.2 | 2.9071 | 2.9071 |  | 1.05 | 4 |  | 4+4 | 8
83 | SS-35/10kV B.Ivanovka | 4+4 | 0 | 0.6954 | 0.62488 | 80 | 0.070521 | 0 | 4.2 | 4.1295 | 4.1295 |  | 1.05 | 4 |  | 4+4 | 8
84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 0.49 | 1.2945 | 0.44779 | 45 | 0.84668 | 0 | 2.625 | 1.7783 | 1.7783 |  | 1.05 | 2.5 | 0.49 | 2,5+2,5 | 5
85 | SS-35/10kV B.Ples | 2,5+2,5 | 0 | 0.79454 | 0.606 | 45 | 0.18854 | 0 | 2.625 | 2.4365 | 2.4365 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 0.1 | 3.3377 | 2.83 | 45 | 0.50774 | 0 | 6.615 | 6.1073 | 6.1073 |  | 1.05 | 6.3 | 0.1 | 6,3+6,3 | 12.6
87 | SS-35/10kV Belovskoe | 4+4 | 0.07 | 3.8924 | 1.21 | 80 | 2.6824 | 0 | 4.2 | 1.5176 | 1.5176 |  | 1.05 | 4 | 0.07 | 4+4 | 8
88 | SS-35/10kV Belyanka | 2,5+4 | 0.02 | 1.981 | 1.3214 | 45 | 0.65956 | 0 | 2.625 | 1.9654 | 1.9654 |  | 1.05 | 2.5 | 0.02 | 2,5+4 | 6.5
89 | SS-35/10kV Bessonovka | 6,3+6,3 | 0 | 6.8366 | 0.918 | 120 | 5.9186 | 0 | 6.615 | 0.69637 | 0.69637 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 0 | 1.0625 | 0.522 | 45 | 0.54053 | 0 | 1.68 | 1.1395 | 1.1395 |  | 1.05 | 1.6 |  | 2,5+1,6 | 4.1
91 | SS-35/10kV V.Mikhailovka | 4+4 | 0 | 2.1305 | 1.45 | 80 | 0.68046 | 0 | 4.2 | 3.5195 | 3.5195 |  | 1.05 | 4 |  | 4+4 | 8
92 | SS-35/10kV Varvarovka | 2,5+2,5 | 0.2 | 1.9889 | 1.0795 | 120 | 0.90939 | 0 | 2.625 | 1.7156 | 1.7156 |  | 1.05 | 2.5 | 0.2 | 2,5+2,5 | 5
93 | SS-35/10kV Vengerovka | 2,5+2,5 | 0.02 | 1.2349 | 0.4 | 120 | 0.83491 | 0 | 2.625 | 1.7901 | 1.7901 |  | 1.05 | 2.5 | 0.02 | 2,5+2,5 | 5
94 | SS-35/10kV Verkhopenye | 2,5+4 | 0.02 | 1.5936 | 1.0177 | 45 | 0.57593 | 0 | 2.625 | 2.0491 | 2.0491 |  | 1.05 | 2.5 | 0.02 | 2,5+4 | 6.5
95 | SS-35/10kV Viktoropol | 2,5+4 | 0.49 | 1.9268 | 0.95536 | 120 | 0.97145 | 0 | 2.625 | 1.6536 | 1.6536 |  | 1.05 | 2.5 | 0.49 | 2,5+4 | 6.5
96 | SS-35/10kV Vislaya Dubrava | 4+4 | 0 | 2.0531 | 0.616 | 80 | 1.4371 | 0 | 4.2 | 2.7629 | 2.7629 |  | 1.05 | 4 |  | 4+4 | 8
97 | SS-35/10kV Vladimirovka | 4+4 | 0 | 0.8037 | 0 |  | 0.8037 | 0 | 4.2 | 3.3963 | 3.3963 |  | 1.05 | 4 |  | 4+4 | 8
98 | SS-35/10kV Water storage | 4+6,3 | 0.02 | 2.1431 | 0.305 | 45 | 1.8381 | 0 | 4.2 | 2.3619 | 2.3619 |  | 1.05 | 2.5 | 0.02 | 4+6,3 | 10.3
99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 0.08 | 3.8883 | 1.43 | 120 | 2.4583 | 0 | 6.615 | 4.1567 | 4.1567 |  | 1.05 | 4 | 0.08 | 6,3+6,3 | 12.6
100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 0 | 1.6947 | 0.99513 | 120 | 0.69957 | 0 | 2.625 | 1.9254 | 1.9254 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
101 | SS-35/10kV Glinnoe | 6,3+6,3 | 0 | 3.2709 | 1.4036 | 80 | 1.8673 | 0 | 6.615 | 4.7477 | 4.7477 |  | 1.05 | 2.5 |  | 6,3+6,3 | 12.3
102 | SS-35/10kV Golovchino | 2,5+2,5 | 0 | 2.7641 | 0.617 | 45 | 2.1471 | 0 | 2.625 | 0.47793 | 0.47793 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
103 | SS-35/10kV Gora-Podol | 2,5+4 | 0.05 | 1.6307 | 0.9085 | 45 | 0.72217 | 0 | 2.625 | 1.9028 | 1.9028 |  | 1.05 | 2.5 | 0.05 | 2,5+4 | 6.5
104 | SS-35/10kV Gorodishche | 4+4 | 0 | 3.1628 | 0 |  | 3.1628 | 0 | 4.2 | 1.0372 | 1.0372 |  | 1.05 | 4 |  | 4+4 | 8
105 | SS-35/10kV Dmitrievka | 4+4 | 0 | 1.2883 | 0.78237 | 80 | 0.50588 | 0 | 4.2 | 3.6941 | 3.6941 |  | 1.05 | 4 |  | 4+4 | 8
106 | SS-35/10kV Dorogoshch | 4+4 | 0 | 2.5671 | 1.054 | 45 | 1.5131 | 0 | 4.2 | 2.6869 | 2.6869 |  | 1.05 | 4 |  | 4+4 | 8
107 | SS-35/10kV Dragunka | 2,5+2,5 | 1.33 | 2.1887 | 0.62999 | 80 | 1.5587 | 0 | 2.625 | 1.0663 | 1.0663 |  | 1.05 | 2.5 | 1.33 | 2,5+2,5 | 5
108 | SS-35/10kV Zhuravlevka | 2,5+4 | 0.14 | 1.7407 | 0.274 | 80 | 1.4667 | 0 | 2.625 | 1.1583 | 1.1583 |  | 1.05 | 2.5 | 0.14 | 2,5+4 | 6.5
109 | SS-35/6kV Zhuravliki | 10+10 | 0 | 7.6502 | 4.051 | 120 | 3.5992 | 0 | 10.5 | 6.9008 | 6.9008 |  | 1.05 | 10 |  | 10+10 | 20
110 | SS-35/10kV Zavidovka | 2,5+2,5 | 0 | 1.0047 | 0.42 | 80 | 0.58471 | 0 | 2.625 | 2.0403 | 2.0403 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
111 | SS-35/6kV Zapadnaya | 10+10+10 | 0 | 6.9987 | 1.707 | 120 | 5.2917 | 0 | 21 | 15.7083 | 15.7083 |  | 1.05 | 20 |  | 10+10+10 | 30
112 | SS-35/10kV Zozuli | 6,3+6,3 | 0 | 6.3343 | 3.88 | 80 | 2.4543 | 0 | 6.615 | 4.1607 | 4.1607 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
113 | SS-35/10kV Ivitsa | 2,5+2,5 | 0 | 1.1209 | 0.58603 | 80 | 0.53491 | 0 | 2.625 | 2.0901 | 2.0901 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
114 | SS-35/10kV Ilovka | 4+4 | 0 | 2.4176 | 2.056 | 45 | 0.3616 | 0 | 4.2 | 3.8384 | 3.8384 |  | 1.05 | 4 |  | 4+4 | 8
115 | SS-35/10kV Istobnoe | 4+2,5 | 0 | 1.2739 | 0.93935 | 120 | 0.33456 | 0 | 2.625 | 2.2904 | 2.2904 |  | 1.05 | 2.5 |  | 4+2,5 | 6.5
116 | SS-35/10kV Kazatskaya | 2,5+4 | 0 | 1.3717 | 0.87141 | 45 | 0.50031 | 0 | 2.625 | 2.1247 | 2.1247 |  | 1.05 | 2.5 |  | 2,5+4 | 6.5
117 | SS-35/10kV Kazinka | 4+4 | 0 | 2.9333 | 0.736 | 120 | 2.1973 | 0 | 4.2 | 2.0027 | 2.0027 |  | 1.05 | 4 |  | 4+4 | 8
118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 0 | 1.0258 | 0.712 | 120 | 0.31385 | 0 | 2.625 | 2.3112 | 2.3112 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 0 | 3.2632 | 0.7035 | 120 | 2.5597 | 0 | 6.615 | 4.0553 | 4.0553 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
120 | SS-35/10kV Kotovo | 2,5+2,5 | 0 | 2.4998 | 1.648 | 20 | 0.85178 | 0 | 2.625 | 1.7732 | 1.7732 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
121 | SS-35/10kV Kochetovka | 2,5+4 | 1.09 | 1.8149 | 0.6286 | 45 | 1.1863 | 0 | 2.625 | 1.4387 | 1.4387 |  | 1.05 | 2.5 | 1.09 | 2,5+4 | 6.5
122 | SS-35/10kV Krasnoe | 4+2,5 | 0 | 1.1201 | 1.1395 | 80 | -0.019407 | 0 | 2.625 | 2.6444 | 2.6444 |  | 1.05 | 2.5 |  | 4+2,5 | 6.5
123 | SS-35/10kV Kretovo | 4+2,5 | 0 | 1.2102 | 0.67818 | 120 | 0.53198 | 0 | 2.625 | 2.093 | 2.093 |  | 1.05 | 2.5 |  | 4+2,5 | 6.5
124 | SS-35/10kV Kurasovka | 4+4 | 0.37 | 3.4755 | 1.797 | 80 | 1.6785 | 0 | 4.2 | 2.5215 | 2.5215 |  | 1.05 | 4 | 0.37 | 4+4 | 8
125 | SS-35/6kV Lebedi | 4+5,6 | 0.12 | 4.1219 | 0.581 | 120 | 3.5409 | 0 | 4.2 | 0.65911 | 0.65911 |  | 1.05 | 4 | 0.12 | 4+5,6 | 9.6
126 | SS-35/6kV Ledovaya | 4+4 | 0 | 2.8081 | 1.321 | 80 | 1.4871 | 0 | 4.2 | 2.7129 | 2.7129 |  | 1.05 | 4 |  | 4+4 | 8
127 | SS-35/10kV Livenka | 4+4 | 0.63 | 4.5798 | 1.541 | 120 | 3.0388 | 0 | 4.2 | 1.1612 | 1.1612 |  | 1.05 | 4 | 0.63 | 4+4 | 8
128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 0 | 0.83355 | 0.66672 | 80 | 0.16683 | 0 | 2.625 | 2.4582 | 2.4582 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
129 | SS-35/10kV M.Pristan | 6,3+6,3 | 0.1 | 7.6455 | 1.81 | 45 | 5.8355 | 0 | 6.615 | 0.77949 | 0.77949 |  | 1.05 | 6.3 | 0.1 | 6,3+6,3 | 12.6
130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 0 | 0.86033 | 0.60716 | 80 | 0.25316 | 0 | 2.625 | 2.3718 | 2.3718 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
131 | SS-35/10kV Malinovka | 10+10 | 0.53 | 7.9366 | 1.357 | 120 | 6.5796 | 0 | 10.5 | 3.9204 | 3.9204 |  | 1.05 | 10 | 0.53 | 10+10 | 20
132 | SS-35/10kV Mandrovo | 2,5+2,5 | 0 | 1.1875 | 0.65565 | 80 | 0.53181 | 0 | 2.625 | 2.0932 | 2.0932 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 0 | 1.3195 | 0.643 | 80 | 0.67652 | 0 | 2.625 | 1.9485 | 1.9485 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 0 | 1.2748 | 0.59315 | 120 | 0.68162 | 0 | 2.625 | 1.9434 | 1.9434 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 0.35 | 1.0228 | 2.78 | 120 | -1.7572 | 0 | #VALUE! | #VALUE! | #VALUE! |  | 1.05 | 4 | 0.35 | 6,3+6,3 | 12.6
136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 0.31 | 3.8493 | 0.842 | 45 | 3.0073 | 0 | 6.615 | 3.6077 | 3.6077 |  | 1.05 | 6,3 | 0.31 | 6,3+6,3 | 12.6
137 | SS-35/10kV N.Ukolovo | 4+2,5 | 0 | 1.5487 | 0.57 | 80 | 0.97871 | 0 | 2.625 | 1.6463 | 1.6463 |  | 1.05 | 2,5 |  | 4+2,5 | 6.5
138 | SS-35/10kV N.Khutornoe | 2,5+4 | 0 | 0.29604 | 0.19 | 80 | 0.10604 | 0 | 2.625 | 2.519 | 2.519 |  | 1.05 | 2,5 |  | 2,5+4 | 6.5
139 | SS-35/10kV Neminushchee | 2,5+2,5 | 0 | 1.7652 | 0.65147 | 80 | 1.1137 | 0 | 2.625 | 1.5113 | 1.5113 |  | 1.05 | 1,6 |  | 2,5+2,5 | 5
140 | SS-35/10kV Nechaevka | 4+4 | 0 | 1.3687 | 0.451 | 120 | 0.91775 | 0 | 4.2 | 3.2823 | 3.2823 |  | 1.05 | 4 |  | 4+4 | 8
141 | SS-35/10kV Nikitovka | 2,5+2,5 | 0 | 1.9659 | 1.4354 | 80 | 0.53044 | 0 | 2.625 | 2.0946 | 2.0946 |  | 1.05 | 2,5 |  | 2,5+2,5 | 5
142 | SS-35/10kV Novenkoe | 4+4 | 0 | 2.1418 | 1.7332 | 80 | 0.40855 | 0 | 4.2 | 3.7915 | 3.7915 |  | 1.05 | 4 |  | 4+4 | 8
143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 2.1 | 8.6029 | 0.872 | 80 | 7.7309 | 0 | 6.615 | -1.1159 | -1.1159 |  | 1.05 | 6,3 | 2.1 | 6,3+6,3 | 12.6
144 | SS-35/10kV Orlik | 4+4 | 0 | 1.9856 | 0.553 | 80 | 1.4326 | 0 | 4.2 | 2.7674 | 2.7674 |  | 1.05 | 4 |  | 4+4 | 8
145 | SS-35/10kV Podolkhi | 2,5+2,5 | 0.77 | 2.9341 | 1.1225 | 45 | 1.8116 | 0 | 2.625 | 0.81336 | 0.81336 |  | 1.05 | 2,5 | 0.77 | 2,5+2,5 | 5
146 | SS-35/10kV Popovka | 6,3+4 | 0 | 1.2689 | 0.64636 | 80 | 0.62255 | 0 | 4.2 | 3.5775 | 3.5775 |  | 1.05 | 4 |  | 6,3+4 | 10.4
147 | SS-35/10kV Prelestnoe | 4+4 | 0 | 4.2992 | 0 |  | 4.2992 | 0 | 4.2 | -0.099183 | -0.099183 |  | 1.05 | 6,3 |  | 4+4 | 8
148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 0 | 5.8042 | 0 |  | 5.8042 | 0 | 6.615 | 0.81081 | 0.81081 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
149 | SS-35/10kV Prilepy | 2,5+2,5 | 0 | 0.70914 | 0.37638 | 80 | 0.33277 | 0 | 2.625 | 2.2922 | 2.2922 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
150 | SS-35/10kV Printsevka | 2,5+2,5 | 0.09 | 1.8281 | 0.352 | 120 | 1.4761 | 0 | 2.625 | 1.1489 | 1.1489 |  | 1.05 | 2.5 | 0.09 | 2,5+2,5 | 5
151 | SS-35/10kV Radkovka | 6,3+6,3 | 0 | 5.0985 | 0.164 | 45 | 4.9345 | 0 | 6.615 | 1.6805 | 1.6805 |  | 1.05 | 4 |  | 6,3+6,3 | 12.6
152 | SS-35/10kV Razdornoe | 2,5+2,5 | 0 | 1.4495 | 0.662 | 80 | 0.78753 | 0 | 2.625 | 1.8375 | 1.8375 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 0.04 | 1.7467 | 0.88491 | 80 | 0.86179 | 0 | 2.625 | 1.7632 | 1.7632 |  | 1.05 | 2.5 | 0.04 | 2,5+2,5 | 5
154 | SS-35/10kV Rzhevka | 10+10 | 0 | 6.3244 | 2.53 | 45 | 3.7944 | 0 | 10.5 | 6.7056 | 6.7056 |  | 1.05 | 6.3 |  | 10+10 | 20
155 | SS-35/10kV Rovenki | 4+4 | 0 | 3.2267 | 1.7393 | 120 | 1.4874 | 0 | 4.2 | 2.7126 | 2.7126 |  | 1.05 | 4 |  | 4+4 | 8
156 | SS-35/10kV Rogovatoe | 4+4 | 0 | 1.8049 | 0 |  | 1.8049 | 0 | 2.625 | 0.82012 | 0.82012 |  | 1.05 | 2.5 |  | 4+4 | 5
157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 0 |  | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625 |  |  |  |  | 2,5+2,5 | 5
158 | SS-35/10kV Saprykino | 2,5+2,5 | 0 | 0.32565 | 0.22751 | 120 | 0.098137 | 0 | 2.625 | 2.5269 | 2.5269 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
159 | SS-35/6kV Severnaya | 6,3+6,3 | 0 | 6.5595 | 4.8049 | 120 | 1.7546 | 0 | 6.615 | 4.8604 | 4.8604 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
160 | SS-35/10kV Setishche | 2,5+2,5 | 0 | 1.9571 | 1.0621 | 80 | 0.89496 | 0 | 2.625 | 1.73 | 1.73 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
161 | SS-35/10kV Slonovka | 4+4 | 0.85 | 3.4262 | 1.1306 | 120 | 2.2956 | 0 | 4.2 | 1.9044 | 1.9044 |  | 1.05 | 4 | 0.85 | 4+4 | 8
162 | SS-35/6kV St.Oskol -2 | 16+16 | 0 | 11.7124 | 1.21 | 80 | 10.5024 | 0 | 16.8 | 6.2976 | 6.2976 |  | 1.05 | 16 |  | 16+16 | 32
163 | SS-35/10kV Starikovo | 4+4 | 0 | 2.1402 | 1.3453 | 45 | 0.79494 | 0 | 4.2 | 3.4051 | 3.4051 |  | 1.05 | 2.5 |  | 4+4 | 8
164 | SS-35/10kV Tavrovo | 10+10 | 0.29 | 9.0401 | 0.531 | 45 | 8.5091 | 0 | 10.5 | 1.9909 | 1.9909 |  | 1.05 | 10 | 0.29 | 10+10 | 20
165 | SS-35/10kV Terebrino | 2,5+2,5 | 0 | 1.0843 | 0.44978 | 80 | 0.63448 | 0 | 2.625 | 1.9905 | 1.9905 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
166 | SS-35/10kV Urazovo | 6,3+6,3 | 0.04 | 4.311 | 1.39 | 120 | 2.921 | 0 | 6.615 | 3.694 | 3.694 |  | 1.05 | 6.3 | 0.04 | 6,3+6,3 | 12.6
167 | SS-35/10kV Utochka | 1,6+2,5 | 0 | 0.78143 | 0.47242 | 80 | 0.30902 | 0 | 1.68 | 1.371 | 1.371 |  | 1.05 | 1.6 |  | 1,6+2,5 | 4.1
168 | SS-35/6kV Fedoseevka | 4+4 | 0.14 | 2.0467 | 0 |  | 2.0467 | 0 | 4.2 | 2.1533 | 2.1533 |  | 1.05 | 4 | 0.14 | 4+4 | 8
169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 0 | 0.95606 | 0.78681 | 45 | 0.16925 | 0 | 1.68 | 1.5107 | 1.5107 |  | 1.05 | 1.6 |  | 1,6+2,5 | 4.1
170 | SS-35/10kV Kholodnoe | 4+4 | 0.37 | 2.2501 | 0 |  | 2.2501 | 0 | 4.2 | 1.9499 | 1.9499 |  | 1.05 | 2.5 | 0.37 | 4+4 | 8
171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 0.03 | 2.6598 | 1.3513 | 20 | 1.3085 | 0 | 6.615 | 5.3065 | 5.3065 |  | 1.05 | 6.3 | 0.03 | 7,5+6,3 | 13.8
172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0 | 0 | 1 | 80 | -1 | 0 | 1 | 2 | 2 |  |  |  |  | 2,5+2,5 | 5
173 | SS-35/10kV Shatalovka | 6,3+6,3 | 0 | 1.8593 | 0 |  | 1.8593 | 0 | 6.615 | 4.7557 | 4.7557 |  | 1.05 | 6.3 |  | 6,3+6,3 | 12.6
174 | SS-35/10kV Shakhovka | 2,5+2,5 | 0.06 | 1.8266 | 0.79066 | 80 | 1.036 | 0 | 2.625 | 1.589 | 1.589 |  | 1.05 | 2.5 | 0.06 | 2,5+2,5 | 5
175 | SS-35/10kV Shishino | 6,3+6,3 | 0.46 | 3.9655 | 1.03 | 80 | 2.9355 | 0 | 4.2 | 1.2645 | 1.2645 |  | 1.05 | 2.5 | 0.46 | 6,3+6,3 | 10.3
176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 0 |  | 0 | 0 | 0 | 0 | 1.68 | 1.68 | 1.68 |  |  |  |  | 1,6+1,6 | 3.2
177 | SS-35/10kV Yablonovo | 4+4 | 0.46 | 2.0294 | 1.1284 | 80 | 0.90096 | 0 | 4.2 | 3.299 | 3.299 |  | 1.05 | 4 | 0.46 | 4+4 | 8
178 | SS-35/10kV Yarskoe | 2,5+2,5 | 0 | 0.53262 | 0.14648 | 80 | 0.38614 | 0 | 2.625 | 2.2389 | 2.2389 |  | 1.05 | 2.5 |  | 2,5+2,5 | 5
| TOTAL: | 3271.1 | #N/A | #N/A | #N/A |  | #N/A | [9 empty] | 3160.9
| deficit | [9 empty] | -26.1007
| proficit | [9 empty] | #VALUE! |  |  |  | 51.48 |  | 3271.1

## Итоговая
[13 empty] | Table 1 | [12 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [10 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | P | Q | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
[5 empty] | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Однотрансформаторные ПС | [13 empty] | 1: Однотрансформаторные ПС
1 | SS-110/35/10kV D.Polyana | 6.3 | 262 | 185 | 0.32073 | 1.457 | 45 | 1.457 | 0 | 1.457 | 1.1363 | 0.20865 |  | 1 | SS-110/35/10kV D.Polyana | 6.3 | 0 | 0.32073 | 1.457 | 45 | -1.1363 | 0 | 1.457 | 1.1363 | 0.20865
| S nom MV, МVА | 6.3 | 6 | 48 | 0.048374 | 0.958 | 0 | 0.958 | 0 | 0.958 | 0.90963 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0.048374 | 0.958 | 0 | -0.90963 | 0 | 0.958 | 0.90963
| S nom LV, МVА | 6.3 | 256 | 137 | 0.29035 | 0.499 | 0 | 0.499 | 0 | 0.499 | 0.20865 |  |  |  | S nom LV, МVА | 6.3 | 0 | 0.29035 | 0.499 | 0 | -0.20865 | 0 | 0.499 | 0.20865
2 | SS-110/35/10kV Konshino | 6.3 | 349 | 215 | 0.40991 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01991 | -0.01991 |  | 2 | SS-110/35/10kV Konshino | 6.3 | 0 | 0.40991 | 0.39 | 20 | 0.01991 | 0 | 0.39 | -0.01991 | -0.01991
| S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, МVА | 6.3 | 349 | 215 | 0.40991 | 0.39 | 0 | 0.39 | 0 | 0.39 | -0.01991 |  |  |  | S nom LV, МVА | 6.3 | 0 | 0.40991 | 0.39 | 0 | 0.01991 | 0 | 0.39 | -0.01991
3 | SS-110/35/10kV Orositelnaya | 16 | 13836 | 4805 | 14.6466 | 11.607 | 120 | 11.607 | 0 | 11.607 | -3.0396 | -3.0396 |  | 3 | SS-110/35/10kV Orositelnaya | 16 | 0 | 14.6466 | 11.607 | 120 | 3.0396 | 0 | 11.607 | -3.0396 | -3.0396
| S nom MV, МVА | 16 | 8659 | 2940 | 9.1445 | 8.606 | 0 | 8.606 | 0 | 8.606 | -0.5385 |  |  |  | S nom MV, МVА | 16 | 0 | 9.1445 | 8.606 | 0 | 0.5385 | 0 | 8.606 | -0.5385
| S nom LV, МVА | 16 | 5177 | 1865 | 5.5027 | 3.001 | 0 | 3.001 | 0 | 3.001 | -2.5017 |  |  |  | S nom LV, МVА | 16 | 0 | 5.5027 | 3.001 | 0 | 2.5017 | 0 | 3.001 | -2.5017
4 | SS-110/35/10kV Rovenki | 16 | 2189 | 988 | 2.4016 | 3.44 | 120 | 3.44 | 0 | 3.44 | 1.0384 | 1.0384 |  | 4 | SS-110/35/10kV Rovenki | 16 | 0 | 2.4016 | 3.44 | 120 | -1.0384 | 0 | 3.44 | 1.0384 | 1.0384
| S nom MV, МVА | 16 | 2 | 34 | 0.034059 | 4 | 0 | 4 | 0 | 4 | 3.9659 |  |  |  | S nom MV, МVА | 16 | 0 | 0.034059 | 4 | 0 | -3.9659 | 0 | 4 | 3.9659
| S nom LV, МVА | 16 | 2187 | 954 | 2.386 | 3.44 | 0 | 3.44 | 0 | 3.44 | 1.054 |  |  |  | S nom LV, МVА | 16 | 0 | 2.386 | 3.44 | 0 | -1.054 | 0 | 3.44 | 1.054
5 | SS-110/35/10kV Serebryanka | 10 | 966 | 389 | 1.0414 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.73862 | 0 |  | 5 | SS-110/35/10kV Serebryanka | 10 | 0 | 1.0414 | 1.78 | 45 | -0.73862 | 0 | 1.78 | 0.73862 | 0
| S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | S nom MV, МVА | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S nom LV, MVА | 10 | 966 | 389 | 1.0414 | 1.78 | 0 | 1.78 | 0 | 1.78 | 0.73862 |  |  |  | S nom LV, MVА | 10 | 0 | 1.0414 | 1.78 | 0 | -0.73862 | 0 | 1.78 | 0.73862
6 | SS-35/10kV Afanasyevka | 1.6 | 784 | 288 | 0.83522 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.18882 | -0.18882 |  | 6 | SS-35/10kV Afanasyevka | 1.6 | 0 | 0.83522 | 0.6464 | 45 | 0.18882 | 0 | 0.6464 | -0.18882 | -0.18882
7 | SS-35/10kV Borisovka | 1.6 | 776 | 224 | 0.80768 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | -0.12418 | -0.12418 |  | 7 | SS-35/10kV Borisovka | 1.6 | 0 | 0.80768 | 0.6835 | 45 | 0.12418 | 0 | 0.6835 | -0.12418 | -0.12418
8 | SS-35/10kV Borisy | 1.6 | 780 | 360 | 0.85907 | 0 | 20 | 0 | 0 | 0 | -0.85907 | -0.85907 |  | 8 | SS-35/10kV Borisy | 1.6 | 0 | 0.85907 | 0 | 20 | 0.85907 | 0 | 0 | -0.85907 | -0.85907
9 | SS-35/10kV Gostishchevo | 4 | 2984 | 1184 | 3.2103 | 2.64 | 80 | 2.64 | 0 | 2.64 | -0.57031 | -0.57031 |  | 9 | SS-35/10kV Gostishchevo | 4 | 0 | 3.2103 | 2.64 | 80 | 0.57031 | 0 | 2.64 | -0.57031 | -0.57031
10 | SS-35/10kV Gruzskoe | 1.6 | 684 | 330 | 0.75944 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.29056 | 0.29056 |  | 10 | SS-35/10kV Gruzskoe | 1.6 | 0 | 0.75944 | 1.05 | 80 | -0.29056 | 0 | 1.05 | 0.29056 | 0.29056
11 | SS-35/10kV Zemsnaryad | 1 | 14 | 19 | 0.023601 | 0 | 0 | 0 | 0 | 0 | -0.023601 | -0.023601 |  | 11 | SS-35/10kV Zemsnaryad | 1.6 | 0.19 | 0.2136 | 0 | 0 | 0.2136 | 0 | 0 | -0.2136 | -0.2136
12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 324 | 132 | 0.34986 | 0 | 0 | 0 | 0 | 0 | -0.34986 | -0.34986 |  | 12 | SS-35/10kV Kazachya Lisitsa | 2.5 | 0 | 0.34986 | 0 | 0 | 0.34986 | 0 | 0 | -0.34986 | -0.34986
13 | SS-35/10kV Kamyzino | 2.5 | 880 | 376 | 0.95696 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.41596 | -0.41596 |  | 13 | SS-35/10kV Kamyzino | 2.5 | 0 | 0.95696 | 0.541 | 45 | 0.41596 | 0 | 0.541 | -0.41596 | -0.41596
14 | SS-35/10kV Koloskovo | 2.5 | 1600 | 512 | 1.6799 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.017324 | -0.017324 |  | 14 | SS-35/10kV Koloskovo | 2.5 | 0 | 1.6799 | 1.6626 | 45 | 0.017324 | 0 | 1.6626 | -0.017324 | -0.017324
15 | SS-35/10jkV Kryukovo | 2.5 | 1560 | 492 | 1.6357 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.085746 | -0.085746 |  | 15 | SS-35/10jkV Kryukovo | 2.5 | 0 | 1.6357 | 1.55 | 45 | 0.085746 | 0 | 1.55 | -0.085746 | -0.085746
16 | SS-35/10kV Kushchino | 1.6 | 336 | 108 | 0.35293 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | 0.057169 | 0.057169 |  | 16 | SS-35/10kV Kushchino | 1.6 | 0 | 0.35293 | 0.4101 | 80 | -0.057169 | 0 | 0.4101 | 0.057169 | 0.057169
17 | SS-35/10kV Lopukhinka | 2.5 | 304 | 144 | 0.33638 | 0.407 | 20 | 0.407 | 0 | 0.407 | 0.070619 | 0.070619 |  | 17 | SS-35/10kV Lopukhinka | 2.5 | 0 | 0.33638 | 0.407 | 20 | -0.070619 | 0 | 0.407 | 0.070619 | 0.070619
18 | SS-35/10kV Malakeevo | 2.5 | 1164 | 600 | 1.3095 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.07046 | 0.07046 |  | 18 | SS-35/10kV Malakeevo | 2.5 | 0.19 | 1.4995 | 1.38 | 120 | 0.11954 | 0 | 1.38 | -0.11954 | -0.11954
19 | SS-35/10kV Murom | 2.5 | 920 | 256 | 0.95495 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.58505 | 0.58505 |  | 19 | SS-35/10kV Murom | 2.5 | 0.4 | 1.355 | 1.54 | 45 | -0.18505 | 0 | 1.54 | 0.18505 | 0.18505
20 | SS-35/10kV Nikolaevka | 2.5 | 656 | 288 | 0.71644 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.051736 | -0.051736 |  | 20 | SS-35/10kV Nikolaevka | 2.5 | 0.19 | 0.90644 | 0.6647 | 45 | 0.24174 | 0 | 0.6647 | -0.24174 | -0.24174
21 | SS-35/10kV Nikolskoe | 4 | 1536 | 384 | 1.5833 | 0.78 | 120 | 0.78 | 0 | 0.78 | -0.80327 | -0.80327 |  | 21 | SS-35/10kV Nikolskoe | 4 | 0.03 | 1.6133 | 0.78 | 120 | 0.83327 | 0 | 0.78 | -0.83327 | -0.83327
22 | SS-35/10kV Pokrovka | 2.5 | 576 | 276 | 0.63871 | 0.722 | 45 | 0.722 | 0 | 0.722 | 0.083289 | 0.083289 |  | 22 | SS-35/10kV Pokrovka | 4 | 0 | 0.63871 | 0.722 | 45 | -0.083289 | 0 | 0.722 | 0.083289 | 0.083289
23 | SS-35/10kV Pyatnitskoe | 4 | 2305 | 974 | 2.5023 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.66234 | -0.66234 |  | 23 | SS-35/10kV Pyatnitskoe | 4 | 0.02 | 2.5223 | 1.84 | 80 | 0.68234 | 0 | 1.84 | -0.68234 | -0.68234
24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 122 | 72 | 0.14166 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.5343 | 1.5343 |  | 24 | SS-35/10kV Sugar plant Ivnya | 2.5 | 0 | 0.14166 | 1.676 | 80 | -1.5343 | 0 | 1.676 | 1.5343 | 1.5343
25 | SS-35/10kV Svistovka | 2.5 | 504 | 224 | 0.55154 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.13566 | 0.13566 |  | 25 | SS-35/10kV Svistovka | 2.5 | 0 | 0.55154 | 0.6872 | 45 | -0.13566 | 0 | 0.6872 | 0.13566 | 0.13566
26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 572 | 180 | 0.59965 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | 0.12415 | 0.12415 |  | 26 | SS-35/10kV sovkhoz "Urazovsky" | 2.5 | 0 | 0.59965 | 0.7238 | 120 | -0.12415 | 0 | 0.7238 | 0.12415 | 0.12415
27 | SS-35/10kV Kharkovskaya | 2.5 | 552 | 236 | 0.60033 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | 0.079367 | 0.079367 |  | 27 | SS-35/10kV Kharkovskaya | 2.5 | 0 | 0.60033 | 0.6797 | 120 | -0.079367 | 0 | 0.6797 | 0.079367 | 0.079367
Двух- и более трансформаторные ПС | [13 empty] | 1: Двух- и более трансформаторные ПС
28 | SS-110/6kV Automobile maintenance plant | 16+16 | 11143 | 5340 | 12.3565 | 3.561 | 45 | 8.7955 | 0 | 16.8 | 8.0045 | 8.0045 |  | 28 | SS-110/6kV Automobile maintenance plant | 16+16 | 0.6 | 12.9565 | 3.561 | 45 | 9.3955 | 0 | 16.8 | 7.4045 | 7.4045
29 | SS-110/35/10kV Aydar | 16+10 | 8156 | 3395 | 8.8344 | 8.95 | 120 | -0.11561 | 0 | 10.5 | 10.6156 | 10.3916 |  | 29 | SS-110/35/10kV Aydar | 16+10 | 0 | 8.8344 | 8.95 | 120 | -0.11561 | 0 | 10.5 | 10.6156 | 10.3916
| S nom MV, МVА | 16+10 | 6832 | 2839 | 7.3984 | 7.29 | 0 | 0.10839 | 0 | 10.5 | 10.3916 |  |  |  | S nom MV, МVА | 16+10 | 0 | 7.3984 | 7.29 | 0 | 0.10839 | 0 | 10.5 | 10.3916
| S nom LV, МVА | 16+10 | 1324 | 556 | 1.436 | 1.66 | 0 | -0.22399 | 0 | 10.5 | 10.724 |  |  |  | S nom LV, МVА | 16+10 | 0 | 1.436 | 1.66 | 0 | -0.22399 | 0 | 10.5 | 10.724
30 | SS-110/35/10kV Alexandrovka | 25+25 | 7539 | 3956 | 8.5139 | 8.37 | 80 | 0.1439 | 0 | 26.25 | 26.1061 | 25.1649 |  | 30 | SS-110/35/10kV Alexandrovka | 25+25 | 11.83 | 20.3439 | 8.37 | 80 | 11.9739 | 0 | 26.25 | 14.2761 | 14.2761
| S nom MV, МVА | 25+25 | 7157 | 3056 | 7.7821 | 6.697 | 0 | 1.0851 | 0 | 26.25 | 25.1649 |  |  |  | S nom MV, МVА | 25+25 | 0 | 7.7821 | 6.697 | 0 | 1.0851 | 0 | 26.25 | 25.1649
| S nom LV, МVА | 25+25 | 382 | 900 | 0.97771 | 1.673 | 0 | -0.69529 | 0 | 26.25 | 26.9453 |  |  |  | S nom LV, МVА | 25+25 | 11.83 | 12.8077 | 1.673 | 0 | 11.1347 | 0 | 26.25 | 15.1153
31 | SS-110/35/10kV Alexeevka | 25+25+25 | 40243 | 18062 | 44.1105 | 5.322 | 120 | 38.7885 | 0 | 52.5 | 13.7115 | 13.7115 |  | 31 | SS-110/35/10kV Alexeevka | 25+25+25 | 0.12 | 44.2305 | 5.322 | 120 | 38.9085 | 0 | 52.5 | 13.5915 | 13.5915
| S nom MV, МVА | 25+25+25 | 17603 | 7822 | 19.2626 | 3.102 | 0 | 16.1606 | 0 | 52.5 | 36.3394 |  |  |  | S nom MV, МVА | 25+25+25 | 0 | 19.2626 | 3.102 | 0 | 16.1606 | 0 | 52.5 | 36.3394
| S nom LV, МVА | 25+25+25 | 22640 | 10240 | 24.8481 | 2.22 | 0 | 22.6281 | 0 | 52.5 | 29.8719 |  |  |  | S nom LV, МVА | 25+25+25 | 0.12 | 24.9681 | 2.22 | 0 | 22.7481 | 0 | 52.5 | 29.7519
32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 9058 | 3808 | 9.8259 | 8.87 | 45 | 0.9559 | 0 | 10.5 | 9.5441 | 9.5441 |  | 32 | SS-110/35/10kV Arkhangelskoe | 10+16 | 0 | 9.8259 | 8.87 | 45 | 0.9559 | 0 | 10.5 | 9.5441 | 9.5441
| S nom MV, МVА | 10+16 | 8537 | 3612 | 9.2697 | 8.867 | 0 | 0.40268 | 0 | 10.5 | 10.0973 |  |  |  | S nom MV, МVА | 10+16 | 0 | 9.2697 | 8.867 | 0 | 0.40268 | 0 | 10.5 | 10.0973
| S nom LV, МVА | 10+16 | 521 | 196 | 0.55665 | 0 | 0 | 0.55665 | 0 | 10.5 | 9.9434 |  |  |  | S nom LV, МVА | 10+16 | 0 | 0.55665 | 0 | 0 | 0.55665 | 0 | 10.5 | 9.9434
33 | SS-110/6kV Belgorod-1 | 40+48 | 38071 | 13708 | 40.4637 | 0 | 120 | 40.4637 | 0 | 42 | 1.5363 | 1.5363 |  | 33 | SS-110/6kV Belgorod-1 | 40+48 | 0.85 | 41.3137 | 0 | 120 | 41.3137 | 0 | 42 | 0.68631 | 0.68631
34 | SS-110/35/10kV Borisovka | 16+16 | 11357 | 4974 | 12.3985 | 11.433 | 120 | 0.96547 | 0 | 16.8 | 15.8345 | 5.4899 |  | 34 | SS-110/35/10kV Borisovka | 16+16 | 0 | 12.3985 | 11.433 | 120 | 0.96547 | 0 | 16.8 | 15.8345 | 5.4899
| S nom MV, МVА | 16+8 | 5565 | 2734 | 6.2003 | 8.133 | 0 | -1.9327 | 0 | 8.4 | 10.3327 |  |  |  | S nom MV, МVА | 16+8 | 0 | 6.2003 | 8.133 | 0 | -1.9327 | 0 | 8.4 | 10.3327
| S nom LV, МVА | 16+8 | 5792 | 2240 | 6.2101 | 3.3 | 0 | 2.9101 | 0 | 8.4 | 5.4899 |  |  |  | S nom LV, МVА | 16+8 | 0 | 6.2101 | 3.3 | 0 | 2.9101 | 0 | 8.4 | 5.4899
35 | SS-110/35/10kV V.Pokrovka | 10+10 | 9454 | 3886 | 10.2215 | 11.5 | 120 | -1.2785 | 0 | 10.5 | 11.7785 | 9.2237 |  | 35 | SS-110/35/10kV V.Pokrovka | 10+10 | 0.01 | 10.2315 | 11.5 | 120 | -1.2685 | 0 | 10.5 | 11.7685 | 9.2237
| S nom MV, МVА | 10+10 | 8360 | 3534 | 9.0763 | 7.8 | 0 | 1.2763 | 0 | 10.5 | 9.2237 |  |  |  | S nom MV, МVА | 10+10 | 0 | 9.0763 | 7.8 | 0 | 1.2763 | 0 | 10.5 | 9.2237
| S nom LV, МVА | 10+10 | 1094 | 352 | 1.1492 | 3.7 | 0 | -2.5508 | 0 | 10.5 | 13.0508 |  |  |  | S nom LV, МVА | 10+10 | 0.01 | 1.1592 | 3.7 | 0 | -2.5408 | 0 | 10.5 | 13.0408
36 | SS-110/35/10kV Veydelevka | 10+10 | 8214 | 3266 | 8.8395 | 8.83 | 120 | 0.0094882 | 0 | 10.5 | 10.4905 | 9.675 |  | 36 | SS-110/35/10kV Veydelevka | 10+10 | 0.79 | 9.6295 | 8.83 | 120 | 0.79949 | 0 | 10.5 | 9.7005 | 9.675
| S nom MV, МVА | 10+10 | 4429 | 1798 | 4.78 | 3.955 | 0 | 0.82505 | 0 | 10.5 | 9.675 |  |  |  | S nom MV, МVА | 10+10 | 0 | 4.78 | 3.955 | 0 | 0.82505 | 0 | 10.5 | 9.675
| S nom LV, МVА | 10+10 | 3785 | 1468 | 4.0597 | 4.875 | 0 | -0.81529 | 0 | 10.5 | 11.3153 |  |  |  | S nom LV, МVА | 10+10 | 0.79 | 4.8497 | 4.875 | 0 | -0.02529 | 0 | 10.5 | 10.5253
37 | SS-110/6kV Vitamin plant | 25+25 | 14250 | 6848 | 15.81 | 1.46 | 45 | 14.35 | 0 | 26.25 | 11.9 | 11.9 |  | 37 | SS-110/6kV Vitamin plant | 25+25 | 1.85 | 17.66 | 1.46 | 45 | 16.2 | 0 | 26.25 | 10.05 | 10.05
38 | SS-110/35/10kV Volokonovka | 25+25 | 17621 | 8868 | 19.7267 | 10.651 | 120 | 9.0757 | 0 | 26.25 | 17.1743 | 17.1743 |  | 38 | SS-110/35/10kV Volokonovka | 25+25 | 0.05 | 19.7767 | 10.651 | 120 | 9.1257 | 0 | 26.25 | 17.1243 | 17.1243
| S nom MV, МVА | 25+25 | 9620 | 4914 | 10.8024 | 8.576 | 0 | 2.2264 | 0 | 26.25 | 24.0236 |  |  |  | S nom MV, МVА | 25+25 | 0 | 10.8024 | 8.576 | 0 | 2.2264 | 0 | 26.25 | 24.0236
| S nom LV, МVА | 25+25 | 8001 | 3954 | 8.9247 | 2.075 | 0 | 6.8497 | 0 | 26.25 | 19.4003 |  |  |  | S nom LV, МVА | 25+25 | 0.05 | 8.9747 | 2.075 | 0 | 6.8997 | 0 | 26.25 | 19.3503
39 | SS-110/35/6kV Vostochnaya | 25+25 | 36574 | 16648 | 40.1847 | 0 | 120 | 40.1847 | 0 | 26.25 | -13.9347 | -13.9347 |  | 39 | SS-110/35/6kV Vostochnaya | 25+25 | 3.05 | 43.2347 | 0 | 120 | 43.2347 | 0 | 26.25 | -16.9847 | -16.9847
| S nom MV, МVА | 25+25 | 15809 | 5210 | 16.6454 | 0 | 0 | 16.6454 | 0 | 26.25 | 9.6046 |  |  |  | S nom MV, МVА | 25+25 | 0 | 16.6454 | 0 | 0 | 16.6454 | 0 | 26.25 | 9.6046
| S nom LV, МVА | 25+25 | 20765 | 11438 | 23.7068 | 0 | 0 | 23.7068 | 0 | 26.25 | 2.5432 |  |  |  | S nom LV, МVА | 25+25 | 3.05 | 26.7568 | 0 | 0 | 26.7568 | 0 | 26.25 | -0.50681
40 | SS-110/10/6kV Golofeevka | 16+16 | 2038 | 882 | 2.2207 | 0 | 0 | 2.2207 | 0 | 26.25 | 24.0293 | 10.9043 |  | 40 | SS-110/10/6kV Golofeevka | 16+16 | 0 | 2.2207 | 0 | 0 | 2.2207 | 0 | 26.25 | 24.0293 | 10.9043
| S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.125 | 13.125 |  |  |  | S nom MV, МVА | 16+16 | 0 | 0 | 0 | 0 | 0 | 0 | 13.125 | 13.125
| S nom LV, МVА | 16+16 | 2038 | 882 | 2.2207 | 0 | 0 | 2.2207 | 0 | 13.125 | 10.9043 |  |  |  | S nom LV, МVА | 16+16 | 0 | 2.2207 | 0 | 0 | 2.2207 | 0 | 13.125 | 10.9043
41 | SS-110/10kV Gotnya | 16+16 | 8429 | 4606 | 9.6054 | 6.43 | 120 | 3.1754 | 0 | 16.8 | 13.6246 | 13.6246 |  | 41 | SS-110/10kV Gotnya | 16+16 | 0.45 | 10.0554 | 6.43 | 120 | 3.6254 | 0 | 16.8 | 13.1746 | 13.1746
42 | SS-110/35/10kV Grayvoron | 16+16 | 15102 | 14219 | 20.7425 | 13.953 | 80 | 6.7895 | 0 | 16.8 | 10.0105 | 6.9944 |  | 42 | SS-110/35/10kV Grayvoron | 16+16 | 0.02 | 20.7625 | 13.953 | 80 | 6.8095 | 0 | 16.8 | 9.9905 | 6.9744
| S nom MV, МVА | 16+16 | 7808 | 3633 | 8.6118 | 10.903 | 0 | -2.2912 | 0 | 16.8 | 19.0912 |  |  |  | S nom MV, МVА | 16+16 | 0 | 8.6118 | 10.903 | 0 | -2.2912 | 0 | 16.8 | 19.0912
| S nom LV, МVА | 16+16 | 7294 | 10586 | 12.8556 | 3.05 | 0 | 9.8056 | 0 | 16.8 | 6.9944 |  |  |  | S nom LV, МVА | 16+16 | 0.02 | 12.8756 | 3.05 | 0 | 9.8256 | 0 | 16.8 | 6.9744
43 | SS-110/6kV Donets | 40+40 | 24528 | 8016 | 25.8046 | 6.73 | 120 | 19.0746 | 0 | 42 | 22.9254 | 22.9254 |  | 43 | SS-110/6kV Donets | 40+40 | 0.62 | 26.4246 | 6.73 | 120 | 19.6946 | 0 | 42 | 22.3054 | 22.3054
44 | SS-110/10kV Dubovoe | 40+40 | 22234 | 5735 | 22.9617 | 11.23 | 120 | 11.7317 | 0 | 42 | 30.2683 | 30.2683 |  | 44 | SS-110/10kV Dubovoe | 40+40 | 1.12 | 24.0817 | 11.23 | 120 | 12.8517 | 0 | 42 | 29.1483 | 29.1483
45 | SS-110/35/6kV Zhuravliki | 40+25 | 20132 | 7256 | 21.3997 | 12.4 | 120 | 8.9997 | 0 | 42 | 33.0003 | 32.261 |  | 45 | SS-110/35/6kV Zhuravliki | 40+25 | 0 | 21.3997 | 12.4 | 120 | 8.9997 | 0 | 42 | 33.0003 | 32.261
| S nom MV, МVА | 40+25 | 14761 | 6085 | 15.966 | 6.227 | 0 | 9.739 | 0 | 42 | 32.261 |  |  |  | S nom MV, МVА | 40+25 | 0 | 15.966 | 6.227 | 0 | 9.739 | 0 | 42 | 32.261
| S nom LV, МVА | 40+25 | 5371 | 1171 | 5.4972 | 6.173 | 0 | -0.67583 | 0 | 42 | 42.6758 |  |  |  | S nom LV, МVА | 40+25 | 0 | 5.4972 | 6.173 | 0 | -0.67583 | 0 | 42 | 42.6758
46 | SS-110/10kV Zapadnaya | 16+16 | 15750 | 4520 | 16.3858 | 1.249 | 80 | 15.1368 | 0 | 16.8 | 1.6632 | 1.6632 |  | 46 | SS-110/10kV Zapadnaya | 16+16 | 0.88 | 17.2658 | 1.249 | 80 | 16.0168 | 0 | 16.8 | 0.78325 | 0.78325
47 | SS-110/35/10kV Ivnya | 10+10 | 11674 | 4784 | 12.6162 | 6.16 | 80 | 6.4562 | 0 | 10.5 | 4.0438 | 3.8937 |  | 47 | SS-110/35/10kV Ivnya | 10+10 | 0 | 12.6162 | 6.16 | 80 | 6.4562 | 0 | 10.5 | 4.0438 | 3.8937
| S nom MV, МVА | 10+10 | 8312 | 3402 | 8.9813 | 2.375 | 0 | 6.6063 | 0 | 10.5 | 3.8937 |  |  |  | S nom MV, МVА | 10+10 | 0 | 8.9813 | 2.375 | 0 | 6.6063 | 0 | 10.5 | 3.8937
| S nom LV, МVА | 10+10 | 3362 | 1382 | 3.635 | 3.785 | 0 | -0.15004 | 0 | 10.5 | 10.65 |  |  |  | S nom LV, МVА | 10+10 | 0 | 3.635 | 3.785 | 0 | -0.15004 | 0 | 10.5 | 10.65
48 | SS-110/35/10kV K.Gvardiya | 16+16 | 13335 | 6036 | 14.6375 | 7.7116 | 120 | 6.9259 | 0 | 16.8 | 9.8741 | 9.8741 |  | 48 | SS-110/35/10kV K.Gvardiya | 16+16 | 0.04 | 14.6775 | 7.7116 | 120 | 6.9659 | 0 | 16.8 | 9.8341 | 9.8341
| S nom MV, МVА | 16+16 | 6823 | 3368 | 7.609 | 4.854 | 0 | 2.755 | 0 | 16.8 | 14.045 |  |  |  | S nom MV, МVА | 16+16 | 0 | 7.609 | 4.854 | 0 | 2.755 | 0 | 16.8 | 14.045
| S nom LV, МVА | 16+16 | 6512 | 2668 | 7.0374 | 2.8576 | 0 | 4.1798 | 0 | 16.8 | 12.6202 |  |  |  | S nom LV, МVА | 16+16 | 0.04 | 7.0774 | 2.8576 | 0 | 4.2198 | 0 | 16.8 | 12.5802
49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 11009 | 4506 | 11.8955 | 9.65 | 80 | 2.2455 | 0 | 26.25 | 24.0045 | 20.0068 |  | 49 | SS-110/10/6kV Kazatskie Bugry | 25+25 | 0 | 11.8955 | 9.65 | 80 | 2.2455 | 0 | 26.25 | 24.0045 | 20.0068
| S nom MV, МVА | 25+25 | 1548 | 580 | 1.6531 | 1.384 | 0 | 0.26909 | 0 | 26.25 | 25.9809 |  |  |  | S nom MV, МVА | 25+25 | 0 | 1.6531 | 1.384 | 0 | 0.26909 | 0 | 26.25 | 25.9809
| S nom LV, МVА | 25+25 | 9461 | 3926 | 10.2432 | 4 | 0 | 6.2432 | 0 | 26.25 | 20.0068 |  |  |  | S nom LV, МVА | 25+25 | 0 | 10.2432 | 4 | 0 | 6.2432 | 0 | 26.25 | 20.0068
50 | SS-110/35/10kV Korocha | 16+16+16 | 19319 | 8126 | 20.9584 | 2.019 | 20 | 18.9394 | 0 | 33.6 | 14.6606 | 14.6606 |  | 50 | SS-110/35/10kV Korocha | 16+16+16 | 0.63 | 21.5884 | 2.019 | 20 | 19.5694 | 0 | 33.6 | 14.0306 | 14.0306
| S nom MV, МVА | 16+16+16 | 7145 | 2668 | 7.6269 | 1.719 | 0 | 5.9079 | 0 | 33.6 | 27.6921 |  |  |  | S nom MV, МVА | 16+16+16 | 0 | 7.6269 | 1.719 | 0 | 5.9079 | 0 | 33.6 | 27.6921
| S nom LV, МVА | 16+16+16 | 12174 | 5458 | 13.3415 | 0.3 | 0 | 13.0415 | 0 | 33.6 | 20.5585 |  |  |  | S nom LV, МVА | 16+16+16 | 0.63 | 13.9715 | 0.3 | 0 | 13.6715 | 0 | 33.6 | 19.9285
51 | SS-110/10kV Krapivenskaya | 16+16 | 823 | 139 | 0.83466 | 0 | 0 | 0.83466 | 0 | 16.8 | 15.9653 | 15.9653 |  | 51 | SS-110/10kV Krapivenskaya | 10+10 | 0.01 | 10.3372 | 9.158 | 120 | 1.1792 | 0 | 10.5 | 9.3208 | 9.3208
52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 9465 | 4131 | 10.3272 | 9.158 | 120 | 1.1692 | 0 | 10.5 | 9.3308 | 9.3308 |  | 52 | SS-110/35/10kV Krasnaya Yaruga | 10+10 | 0 | 4.4995 | 3.52 | 0 | 0.97951 | 0 | 10.5 | 9.5205
| S nom MV, МVА | 10+10 | 4111 | 1829 | 4.4995 | 3.52 | 0 | 0.97951 | 0 | 10.5 | 9.5205 |  |  |  | S nom MV, МVА | 10+10 | 0.01 | 5.8379 | 5.638 | 0 | 0.19991 | 0 | 10.5 | 10.3001
| S nom LV, МVА | 10+10 | 5354 | 2302 | 5.8279 | 5.638 | 0 | 0.18991 | 0 | 10.5 | 10.3101 |  |  |  | S nom LV, МVА | 16+16 | 1.19 | 2.0247 | 0 | 0 | 2.0247 | 0 | 16.8 | 14.7753 | 14.7753
53 | SS-110/10/10kV Mayskaya | 40+40 | 6141 | 1360 | 6.2898 | 0 | 0 | 6.2898 | 0 | 42 | 35.7102 | 35.7102 |  | 53 | SS-110/10/10kV Mayskaya | 40+40 | 0.26 | 6.5498 | 0 | 0 | 6.5498 | 0 | 42 | 35.4502 | 35.4502
54 | SS-110/35/10kV Maximovka | 16+16 | 8770 | 4874 | 10.0334 | 11.48 | 45 | -1.4466 | 0 | 16.8 | 18.2466 | 17.2826 |  | 54 | SS-110/35/10kV Maximovka | 16+16 | 0 | 10.0334 | 11.48 | 45 | -1.4466 | 0 | 16.8 | 18.2466 | 17.2826
| S nom MV, МVА | 16+16 | 7336 | 4290 | 8.4983 | 9.449 | 0 | -0.95071 | 0 | 16.8 | 17.7507 |  |  |  | S nom MV, МVА | 16+16 | 0 | 8.4983 | 9.449 | 0 | -0.95071 | 0 | 16.8 | 17.7507
| S nom LV, МVА | 16+16 | 1434 | 584 | 1.5484 | 2.031 | 0 | -0.48264 | 0 | 16.8 | 17.2826 |  |  |  | S nom LV, МVА | 16+16 | 0 | 1.5484 | 2.031 | 0 | -0.48264 | 0 | 16.8 | 17.2826
55 | SS-110/35/10kV N.Oskol | 25+31,5 | 17666 | 7970 | 19.3806 | 9.119 | 80 | 10.2616 | 0 | 26.25 | 15.9884 | 15.2237 |  | 55 | SS-110/35/10kV N.Oskol | 25+31,5 | 0.13 | 19.5106 | 9.119 | 80 | 10.3916 | 0 | 26.25 | 15.8584 | 15.0937
| S nom MV, МVА | 25+31,5 | 6226 | 3410 | 7.0987 | 7.83 | 0 | -0.73133 | 0 | 26.25 | 26.9813 |  |  |  | S nom MV, МVА | 25+31,5 | 0 | 7.0987 | 7.83 | 0 | -0.73133 | 0 | 26.25 | 26.9813
| S nom LV, МVА | 25+31,5 | 11440 | 4560 | 12.3153 | 1.289 | 0 | 11.0263 | 0 | 26.25 | 15.2237 |  |  |  | S nom LV, МVА | 25+31,5 | 0.13 | 12.4453 | 1.289 | 0 | 11.1563 | 0 | 26.25 | 15.0937
56 | SS-110/10kV Obukhovskaya | 25+25 | 2178 | 699 | 2.2874 | 0 | 0 | 2.2874 | 0 | 26.25 | 23.9626 | 23.9626 |  | 56 | SS-110/10kV Obukhovskaya | 25+25 | 0 | 2.2874 | 0 | 0 | 2.2874 | 0 | 26.25 | 23.9626 | 23.9626
57 | SS-110/6kV Ochistnye | 16+16 | 4625 | 2214 | 5.1276 | 0 | 0 | 5.1276 | 0 | 16.8 | 11.6724 | 11.6724 |  | 57 | SS-110/6kV Ochistnye | 16+16 | 0 | 5.1276 | 0 | 0 | 5.1276 | 0 | 16.8 | 11.6724 | 11.6724
58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 0 | 0 | 6.679 | 120 | 6.679 | 0 | 26.25 | 26.25 | 26.25 |  | 58 | SS-110/35/6kV Pishcheprom | 25+25 | 0 | 0 | 6.679 | 120 | -6.679 | 0 | 26.25 | 26.25 | 26.25
| S nom MV, МVА | 25+25 | 0 | 0 | 0 | 2.022 | 0 | 2.022 | 0 | 26.25 | 26.25 |  |  |  | S nom MV, МVА | 25+25 | 0 | 0 | 2.022 | 0 | -2.022 | 0 | 26.25 | 26.25
| S nom LV, МVА | 25+25 | 0 | 0 | 0 | 4.657 | 0 | 4.657 | 0 | 26.25 | 26.25 |  |  |  | S nom LV, МVА | 25+25 | 0 | 0 | 4.657 | 0 | -4.657 | 0 | 26.25 | 26.25
59 | SS-110/10kV Promyshlennaya | 25+25 | 16234 | 8957 | 18.5411 | 0 | 0 | 18.5411 | 0 | 26.25 | 7.7089 | 7.7089 |  | 59 | SS-110/10kV Promyshlennaya | 25+25 | 0 | 18.5411 | 0 | 0 | 18.5411 | 0 | 26.25 | 7.7089 | 7.7089
60 | SS-110/10kV Poultry plant | 16+16 | 12347 | 7576 | 14.486 | 1.296 | 80 | 13.19 | 0 | 16.8 | 3.61 | 3.61 |  | 60 | SS-110/10kV Poultry plant | 16+16 | 0 | 14.486 | 1.296 | 80 | 13.19 | 0 | 16.8 | 3.61 | 3.61
61 | SS-110/10kV Pushkarnaya | 40+40 | 30306 | 8850 | 31.5718 | 0 | 60 | 31.5718 | 0 | 42 | 10.4282 | 10.4282 |  | 61 | SS-110/10kV Pushkarnaya | 40+40 | 0 | 31.5718 | 0 | 60 | 31.5718 | 0 | 42 | 10.4282 | 10.4282
62 | SS-110/35/10kV Rakitnoe | 10+10 | 11816 | 6776 | 13.621 | 8.98 | 120 | 4.641 | 0 | 10.5 | 5.859 | 5.859 |  | 62 | SS-110/35/10kV Rakitnoe | 10+10 | 0.33 | 13.951 | 8.98 | 120 | 4.971 | 0 | 10.5 | 5.529 | 5.529
| S nom MV, МVА | 10+10 | 8826 | 5366 | 10.3292 | 6.407 | 0 | 3.9222 | 0 | 10.5 | 6.5778 |  |  |  | S nom MV, МVА | 10+10 | 0 | 10.3292 | 6.407 | 0 | 3.9222 | 0 | 10.5 | 6.5778
| S nom LV, МVА | 10+10 | 2990 | 1410 | 3.3058 | 2.573 | 0 | 0.73278 | 0 | 10.5 | 9.7672 |  |  |  | S nom LV, МVА | 10+10 | 0.33 | 3.6358 | 2.573 | 0 | 1.0628 | 0 | 10.5 | 9.4372
63 | SS-110/35/6kV Rudnik | 25+25 | 17350 | 10404 | 20.2303 | 10.46 | 45 | 9.7703 | 0 | 26.25 | 16.4797 | 16.4797 |  | 63 | SS-110/35/6kV Rudnik | 25+25 | 0.04 | 20.2703 | 10.46 | 45 | 9.8103 | 0 | 26.25 | 16.4397 | 16.4397
| S nom MV, МVА | 25+25 | 10731 | 5534 | 12.0739 | 10.46 | 0 | 1.6139 | 0 | 26.25 | 24.6361 |  |  |  | S nom MV, МVА | 25+25 | 0 | 12.0739 | 10.46 | 0 | 1.6139 | 0 | 26.25 | 24.6361
| S nom LV, МVА | 25+25 | 6619 | 4870 | 8.2175 | 0 | 0 | 8.2175 | 0 | 26.25 | 18.0325 |  |  |  | S nom LV, МVА | 25+25 | 0.04 | 8.2575 | 0 | 0 | 8.2575 | 0 | 26.25 | 17.9925
64 | SS-110/10kV Severnaya | 40+40 | 11204 | 3168 | 11.6433 | 3.312 | 45 | 8.3313 | 0 | 42 | 33.6687 | 33.6687 |  | 64 | SS-110/10kV Severnaya | 40+40 | 5.13 | 16.7733 | 3.312 | 45 | 13.4613 | 0 | 42 | 28.5387 | 28.5387
65 | SS-110/35/10kV Skorodnoe | 16+16 | 13755 | 5418 | 14.7836 | 10.36 | 120 | 4.4236 | 0 | 16.8 | 12.3764 | 12.3764 |  | 65 | SS-110/35/10kV Skorodnoe | 16+16 | 0 | 14.7836 | 10.36 | 120 | 4.4236 | 0 | 16.8 | 12.3764 | 12.3764
| S nom MV, МVА | 16+16 | 9853 | 3809 | 10.5636 | 7.562 | 0 | 3.0016 | 0 | 16.8 | 13.7984 |  |  |  | S nom MV, МVА | 16+16 | 0 | 10.5636 | 7.562 | 0 | 3.0016 | 0 | 16.8 | 13.7984
| S nom LV, МVА | 16+16 | 3902 | 1609 | 4.2207 | 2.798 | 0 | 1.4227 | 0 | 16.8 | 15.3773 |  |  |  | S nom LV, МVА | 16+16 | 0 | 4.2207 | 2.798 | 0 | 1.4227 | 0 | 16.8 | 15.3773
66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 30931 | 16493 | 35.0535 | 0 | 0 | 35.0535 | 0 | 47.25 | 12.1965 | 12.1965 |  | 66 | SS-110/35/6kV St.Oskol - 1 | 20+25+25 | 0.05 | 35.1035 | 0 | 0 | 35.1035 | 0 | 47.25 | 12.1465 | 12.1465
| S nom MV, МVА | 20+25+25 | 9757 | 6686 | 11.828 | 0 | 0 | 11.828 | 0 | 47.25 | 35.422 |  |  |  | S nom MV, МVА | 20+25+25 | 0 | 11.828 | 0 | 0 | 11.828 | 0 | 47.25 | 35.422
| S nom LV, МVА | 20+25+25 | 21174 | 9807 | 23.3349 | 0 | 0 | 23.3349 | 0 | 47.25 | 23.9151 |  |  |  | S nom LV, МVА | 20+25+25 | 0.05 | 23.3849 | 0 | 0 | 23.3849 | 0 | 47.25 | 23.8651
67 | SS-110/35/10kV Streletskaya | 16+16 | 4735 | 1291 | 4.9078 | 2.23 | 80 | 2.6778 | 0 | 16.8 | 14.1222 | 5.6812 |  | 67 | SS-110/35/10kV Streletskaya | 16+16 | 0.19 | 5.0978 | 2.23 | 80 | 2.8678 | 0 | 16.8 | 13.9322 | 5.4912
| S nom MV, МVА | 16+8 | -14 | -101 | 0.10197 | 0 | 0 | 0.10197 | 0 | 8.4 | 8.298 |  |  |  | S nom MV, МVА | 16+8 | 0 | 0.10197 | 0 | 0 | 0.10197 | 0 | 8.4 | 8.298
| S nom LV, МVА | 16+8 | 4749 | 1392 | 4.9488 | 2.23 | 0 | 2.7188 | 0 | 8.4 | 5.6812 |  |  |  | S nom LV, МVА | 16+8 | 0.19 | 5.1388 | 2.23 | 0 | 2.9088 | 0 | 8.4 | 5.4912
68 | SS-110/6kV Stroitel | 15+15 | 12862 | 4982 | 13.7932 | 0 | 0 | 13.7932 | 0 | 15.75 | 1.9568 | 1.9568 |  | 68 | SS-110/6kV Stroitel | 15+15 | 0.49 | 14.2832 | 0 | 0 | 14.2832 | 0 | 15.75 | 1.4668 | 1.4668
69 | SS-110/35/10kV Tomarovka | 16+16 | 9989 | 4296 | 10.8736 | 3.46 | 45 | 7.4136 | 0 | 16.8 | 9.3864 | 8.9293 |  | 69 | SS-110/35/10kV Tomarovka | 16+16 | 0.03 | 10.9036 | 3.46 | 45 | 7.4436 | 0 | 16.8 | 9.3564 | 8.8993
| S nom MV, МVА | 16+16 | 2817 | 1054 | 3.0077 | 3.46 | 0 | -0.45228 | 0 | 16.8 | 17.2523 |  |  |  | S nom MV, МVА | 16+16 | 0 | 3.0077 | 3.46 | 0 | -0.45228 | 0 | 16.8 | 17.2523
| S nom LV, МVА | 16+16 | 7172 | 3242 | 7.8707 | 0 | 0 | 7.8707 | 0 | 16.8 | 8.9293 |  |  |  | S nom LV, МVА | 16+16 | 0.03 | 7.9007 | 0 | 0 | 7.9007 | 0 | 16.8 | 8.8993
70 | SS-110/6kV Chemical plant | 32+32 | 10973 | 4879 | 12.0088 | 5.56 | 45 | 6.4488 | 0 | 33.6 | 27.1512 | 27.1512 |  | 70 | SS-110/6kV Chemical plant | 32+32 | 5 | 17.0088 | 5.56 | 45 | 11.4488 | 0 | 33.6 | 22.1512 | 22.1512
71 | SS-110/10kV Tsentralnaya | 40+40 | 27342 | 4998 | 27.7951 | 0 | 0 | 27.7951 | 0 | 42 | 14.2049 | 14.2049 |  | 71 | SS-110/10kV Tsentralnaya | 40+40 | 0.01 | 27.8051 | 0 | 0 | 27.8051 | 0 | 42 | 14.1949 | 14.1949
72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 19256 | 7574 | 20.692 | 20.54 | 80 | 0.152 | 0 | 26.25 | 26.098 | 24.6811 |  | 72 | SS-110/35/10kV Cheremoshnoe | 25+25 | 0.26 | 20.952 | 20.54 | 80 | 0.412 | 0 | 26.25 | 25.838 | 24.4211
| S nom MV, МVА | 25+25 | 17936 | 6726 | 19.1557 | 19.676 | 0 | -0.52034 | 0 | 26.25 | 26.7703 |  |  |  | S nom MV, МVА | 25+25 | 0 | 19.1557 | 19.676 | 0 | -0.52034 | 0 | 26.25 | 26.7703
| S nom LV, МVА | 25+25 | 1320 | 848 | 1.5689 | 0 | 0 | 1.5689 | 0 | 26.25 | 24.6811 |  |  |  | S nom LV, МVА | 25+25 | 0.26 | 1.8289 | 0 | 0 | 1.8289 | 0 | 26.25 | 24.4211
73 | SS-110/35/10kV Chernyanka | 16+16 | 15254 | 6791 | 16.6974 | 5.969 | 120 | 10.7284 | 0 | 16.8 | 6.0716 | 6.0716 |  | 73 | SS-110/35/10kV Chernyanka | 16+16 | 0.04 | 16.7374 | 5.969 | 120 | 10.7684 | 0 | 16.8 | 6.0316 | 6.0316
| S nom MV, МVА | 16+16 | 7509 | 3847 | 8.4371 | 5.969 | 0 | 2.4681 | 0 | 16.8 | 14.3319 |  |  |  | S nom MV, МVА | 16+16 | 0 | 8.4371 | 5.969 | 0 | 2.4681 | 0 | 16.8 | 14.3319
| S nom LV, МVА | 16+16 | 7745 | 2944 | 8.2857 | 0 | 0 | 8.2857 | 0 | 16.8 | 8.5143 |  |  |  | S nom LV, МVА | 16+16 | 0.04 | 8.3257 | 0 | 0 | 8.3257 | 0 | 16.8 | 8.4743
74 | SS-110/35/6kV Shebekino | 40+40 | 26611 | 13133 | 29.6753 | 16.65 | 120 | 13.0253 | 0 | 42 | 28.9747 | 28.9747 |  | 74 | SS-110/35/6kV Shebekino | 40+40 | 0.47 | 30.1453 | 16.65 | 120 | 13.4953 | 0 | 42 | 28.5047 | 28.5047
| S nom MV, МVА | 40+40 | 15078 | 8022 | 17.0792 | 11.682 | 0 | 5.3972 | 0 | 42 | 36.6028 |  |  |  | S nom MV, МVА | 40+40 | 0 | 17.0792 | 11.682 | 0 | 5.3972 | 0 | 42 | 36.6028
| S nom LV, МVА | 40+40 | 11533 | 5111 | 12.6148 | 4.968 | 0 | 7.6468 | 0 | 42 | 34.3532 |  |  |  | S nom LV, МVА | 40+40 | 0.47 | 13.0848 | 4.968 | 0 | 8.1168 | 0 | 42 | 33.8832
75 | SS-110/10kV Sheino | 3,2+10 | 3265 | 1144 | 3.4596 | 0 | 0 | 3.4596 | 0 | 3.36 | -0.099619 | -0.099619 |  | 75 | SS-110/10kV Sheino | 3,2+10 | 0.04 | 3.4996 | 0 | 0 | 3.4996 | 0 | 3.36 | -0.13962 | -0.13962
76 | SS-110/10/6kV Yuzhnaya | 40+40 | 38807 | 11568 | 40.4945 | 12.94 | 120 | 27.5545 | 0 | 42 | 14.4455 | 14.4455 |  | 76 | SS-110/10/6kV Yuzhnaya | 40+40 | 1.53 | 42.0245 | 12.94 | 120 | 29.0845 | 0 | 42 | 12.9155 | 12.9155
| S nom MV, МVА | 40+40 | 6846 | 1506 | 7.0097 | 3.42 | 0 | 3.5897 | 0 | 42 | 38.4103 |  |  |  | S nom MV, МVА | 40+40 | 0 | 7.0097 | 3.42 | 0 | 3.5897 | 0 | 42 | 38.4103
| S nom LV, МVА | 40+40 | 31961 | 10062 | 33.5075 | 9.52 | 0 | 23.9875 | 0 | 42 | 18.0125 |  |  |  | S nom LV, МVА | 40+40 | 1.53 | 35.0375 | 9.52 | 0 | 25.5175 | 0 | 42 | 16.4825
77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 704 | 264 | 0.75187 | 0.43267 | 120 | 0.31921 | 0 | 2.625 | 2.3058 | 2.3058 |  | 77 | SS-35/10kV Aleynikovo | 2,5+2,5 | 0 | 0.75187 | 0.43267 | 120 | 0.31921 | 0 | 2.625 | 2.3058 | 2.3058
78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 872 | 280 | 0.91585 | 0.46639 | 120 | 0.44946 | 0 | 2.625 | 2.1755 | 2.1755 |  | 78 | SS-35/10kV Alexeevka (yak.) | 2,5+2,5 | 0 | 0.91585 | 0.46639 | 120 | 0.44946 | 0 | 2.625 | 2.1755 | 2.1755
79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 2352 | 1056 | 2.5782 | 0 | 0 | 2.5782 | 0 | 4.2 | 1.6218 | 1.6218 |  | 79 | SS-35/10kV Alexeevka (kor.) | 4+4 | 0.12 | 2.6982 | 0 | 0 | 2.6982 | 0 | 4.2 | 1.5018 | 1.5018
80 | SS-35/10kV Annovka | 2,5+2,5 | 876 | 354 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267 |  | 80 | SS-35/10kV Annovka | 2,5+2,5 | 0 | 0.94482 | 0.44652 | 80 | 0.49831 | 0 | 2.625 | 2.1267 | 2.1267
81 | SS-35/10kV Artelnoe | 6,3+6,3 | 3664 | 2840 | 4.6358 | 0.55 | 45 | 4.0858 | 0 | 6.615 | 2.5292 | 2.5292 |  | 81 | SS-35/10kV Artelnoe | 6,3+6,3 | 0 | 4.6358 | 0.55 | 45 | 4.0858 | 0 | 6.615 | 2.5292 | 2.5292
82 | SS-35/10kV B.Dvory | 4+4 | 2304 | 928 | 2.4839 | 1.191 | 120 | 1.2929 | 0 | 4.2 | 2.9071 | 2.9071 |  | 82 | SS-35/10kV B.Dvory | 4+4 | 0 | 2.4839 | 1.191 | 120 | 1.2929 | 0 | 4.2 | 2.9071 | 2.9071
83 | SS-35/10kV B.Ivanovka | 4+4 | 640 | 272 | 0.6954 | 0.62488 | 80 | 0.070521 | 0 | 4.2 | 4.1295 | 4.1295 |  | 83 | SS-35/10kV B.Ivanovka | 4+4 | 0 | 0.6954 | 0.62488 | 80 | 0.070521 | 0 | 4.2 | 4.1295 | 4.1295
84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 744 | 306 | 0.80447 | 0.44779 | 45 | 0.35668 | 0 | 2.625 | 2.2683 | 2.2683 |  | 84 | SS-35/10kV B.Kolodez | 2,5+2,5 | 0.49 | 1.2945 | 0.44779 | 45 | 0.84668 | 0 | 2.625 | 1.7783 | 1.7783
85 | SS-35/10kV B.Ples | 2,5+2,5 | 720 | 336 | 0.79454 | 0.606 | 45 | 0.18854 | 0 | 2.625 | 2.4365 | 2.4365 |  | 85 | SS-35/10kV B.Ples | 2,5+2,5 | 0 | 0.79454 | 0.606 | 45 | 0.18854 | 0 | 2.625 | 2.4365 | 2.4365
86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 2960 | 1312 | 3.2377 | 2.83 | 45 | 0.40774 | 0 | 6.615 | 6.2073 | 6.2073 |  | 86 | SS-35/10kV B.Troitsa | 6,3+6,3 | 0.1 | 3.3377 | 2.83 | 45 | 0.50774 | 0 | 6.615 | 6.1073 | 6.1073
87 | SS-35/10kV Belovskoe | 4+4 | 3544 | 1432 | 3.8224 | 1.21 | 80 | 2.6124 | 0 | 4.2 | 1.5876 | 1.5876 |  | 87 | SS-35/10kV Belovskoe | 4+4 | 0.07 | 3.8924 | 1.21 | 80 | 2.6824 | 0 | 4.2 | 1.5176 | 1.5176
88 | SS-35/10kV Belyanka | 2,5+4 | 1824 | 720 | 1.961 | 1.3214 | 45 | 0.63956 | 0 | 2.625 | 1.9854 | 1.9854 |  | 88 | SS-35/10kV Belyanka | 2,5+4 | 0.02 | 1.981 | 1.3214 | 45 | 0.65956 | 0 | 2.625 | 1.9654 | 1.9654
89 | SS-35/10kV Bessonovka | 6,3+6,3 | 6336 | 2568 | 6.8366 | 0.918 | 120 | 5.9186 | 0 | 6.615 | 0.69637 | 0.69637 |  | 89 | SS-35/10kV Bessonovka | 6,3+6,3 | 0 | 6.8366 | 0.918 | 120 | 5.9186 | 0 | 6.615 | 0.69637 | 0.69637
90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 1008 | 336 | 1.0625 | 0.522 | 45 | 0.54053 | 0 | 1.68 | 1.1395 | 1.1395 |  | 90 | SS-35/10kV B.Lubyanki | 2,5+1,6 | 0 | 1.0625 | 0.522 | 45 | 0.54053 | 0 | 1.68 | 1.1395 | 1.1395
91 | SS-35/10kV V.Mikhailovka | 4+4 | 1968 | 816 | 2.1305 | 1.45 | 80 | 0.68046 | 0 | 4.2 | 3.5195 | 3.5195 |  | 91 | SS-35/10kV V.Mikhailovka | 4+4 | 0 | 2.1305 | 1.45 | 80 | 0.68046 | 0 | 4.2 | 3.5195 | 3.5195
92 | SS-35/10kV Varvarovka | 2,5+2,5 | 1648 | 696 | 1.7889 | 1.0795 | 120 | 0.70939 | 0 | 2.625 | 1.9156 | 1.9156 |  | 92 | SS-35/10kV Varvarovka | 2,5+2,5 | 0.2 | 1.9889 | 1.0795 | 120 | 0.90939 | 0 | 2.625 | 1.7156 | 1.7156
93 | SS-35/10kV Vengerovka | 2,5+2,5 | 1164 | 348 | 1.2149 | 0.4 | 120 | 0.81491 | 0 | 2.625 | 1.8101 | 1.8101 |  | 93 | SS-35/10kV Vengerovka | 2,5+2,5 | 0.02 | 1.2349 | 0.4 | 120 | 0.83491 | 0 | 2.625 | 1.7901 | 1.7901
94 | SS-35/10kV Verkhopenye | 2,5+4 | 1448 | 616 | 1.5736 | 1.0177 | 45 | 0.55593 | 0 | 2.625 | 2.0691 | 2.0691 |  | 94 | SS-35/10kV Verkhopenye | 2,5+4 | 0.02 | 1.5936 | 1.0177 | 45 | 0.57593 | 0 | 2.625 | 2.0491 | 2.0491
95 | SS-35/10kV Viktoropol | 2,5+4 | 1344 | 508 | 1.4368 | 0.95536 | 120 | 0.48145 | 0 | 2.625 | 2.1436 | 2.1436 |  | 95 | SS-35/10kV Viktoropol | 2,5+4 | 0.49 | 1.9268 | 0.95536 | 120 | 0.97145 | 0 | 2.625 | 1.6536 | 1.6536
96 | SS-35/10kV Vislaya Dubrava | 4+4 | 1956 | 624 | 2.0531 | 0.616 | 80 | 1.4371 | 0 | 4.2 | 2.7629 | 2.7629 |  | 96 | SS-35/10kV Vislaya Dubrava | 4+4 | 0 | 2.0531 | 0.616 | 80 | 1.4371 | 0 | 4.2 | 2.7629 | 2.7629
97 | SS-35/10kV Vladimirovka | 4+4 | 679 | 430 | 0.8037 | 0 | 0 | 0.8037 | 0 | 4.2 | 3.3963 | 3.3963 |  | 97 | SS-35/10kV Vladimirovka | 4+4 | 0 | 0.8037 | 0 | 0 | 0.8037 | 0 | 4.2 | 3.3963 | 3.3963
98 | SS-35/10kV Water storage | 4+6,3 | 2040 | 588 | 2.1231 | 0.305 | 45 | 1.8181 | 0 | 4.2 | 2.3819 | 2.3819 |  | 98 | SS-35/10kV Water storage | 4+6,3 | 0.02 | 2.1431 | 0.305 | 45 | 1.8381 | 0 | 4.2 | 2.3619 | 2.3619
99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 3586 | 1282 | 3.8083 | 1.43 | 120 | 2.3783 | 0 | 6.615 | 4.2367 | 4.2367 |  | 99 | SS-35/6kV Vostochnaya | 6,3+6,3 | 0.08 | 3.8883 | 1.43 | 120 | 2.4583 | 0 | 6.615 | 4.1567 | 4.1567
100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 1578 | 618 | 1.6947 | 0.99513 | 120 | 0.69957 | 0 | 2.625 | 1.9254 | 1.9254 |  | 100 | SS-35/10kV Vsesvyatka | 2,5+2,5 | 0 | 1.6947 | 0.99513 | 120 | 0.69957 | 0 | 2.625 | 1.9254 | 1.9254
101 | SS-35/10kV Glinnoe | 6,3+6,3 | 2816 | 1664 | 3.2709 | 1.4036 | 80 | 1.8673 | 0 | 6.615 | 4.7477 | 4.7477 |  | 101 | SS-35/10kV Glinnoe | 6,3+6,3 | 0 | 3.2709 | 1.4036 | 80 | 1.8673 | 0 | 6.615 | 4.7477 | 4.7477
102 | SS-35/10kV Golovchino | 2,5+2,5 | 2592 | 960 | 2.7641 | 0.617 | 45 | 2.1471 | 0 | 2.625 | 0.47793 | 0.47793 |  | 102 | SS-35/10kV Golovchino | 2,5+2,5 | 0 | 2.7641 | 0.617 | 45 | 2.1471 | 0 | 2.625 | 0.47793 | 0.47793
103 | SS-35/10kV Gora-Podol | 2,5+4 | 1464 | 596 | 1.5807 | 0.9085 | 45 | 0.67217 | 0 | 2.625 | 1.9528 | 1.9528 |  | 103 | SS-35/10kV Gora-Podol | 2,5+4 | 0.05 | 1.6307 | 0.9085 | 45 | 0.72217 | 0 | 2.625 | 1.9028 | 1.9028
104 | SS-35/10kV Gorodishche | 4+4 | 2816 | 1440 | 3.1628 | 0 | 0 | 3.1628 | 0 | 4.2 | 1.0372 | 1.0372 |  | 104 | SS-35/10kV Gorodishche | 4+4 | 0 | 3.1628 | 0 | 0 | 3.1628 | 0 | 4.2 | 1.0372 | 1.0372
105 | SS-35/10kV Dmitrievka | 4+4 | 1164 | 552 | 1.2883 | 0.78237 | 80 | 0.50588 | 0 | 4.2 | 3.6941 | 3.6941 |  | 105 | SS-35/10kV Dmitrievka | 4+4 | 0 | 1.2883 | 0.78237 | 80 | 0.50588 | 0 | 4.2 | 3.6941 | 3.6941
106 | SS-35/10kV Dorogoshch | 4+4 | 2384 | 952 | 2.5671 | 1.054 | 45 | 1.5131 | 0 | 4.2 | 2.6869 | 2.6869 |  | 106 | SS-35/10kV Dorogoshch | 4+4 | 0 | 2.5671 | 1.054 | 45 | 1.5131 | 0 | 4.2 | 2.6869 | 2.6869
107 | SS-35/10kV Dragunka | 2,5+2,5 | 800 | 312 | 0.85869 | 0.62999 | 80 | 0.2287 | 0 | 2.625 | 2.3963 | 2.3963 |  | 107 | SS-35/10kV Dragunka | 2,5+2,5 | 1.33 | 2.1887 | 0.62999 | 80 | 1.5587 | 0 | 2.625 | 1.0663 | 1.0663
108 | SS-35/10kV Zhuravlevka | 2,5+4 | 1552 | 392 | 1.6007 | 0.274 | 80 | 1.3267 | 0 | 2.625 | 1.2983 | 1.2983 |  | 108 | SS-35/10kV Zhuravlevka | 2,5+4 | 0.14 | 1.7407 | 0.274 | 80 | 1.4667 | 0 | 2.625 | 1.1583 | 1.1583
109 | SS-35/6kV Zhuravliki | 10+10 | 7248 | 2448 | 7.6502 | 4.051 | 120 | 3.5992 | 0 | 10.5 | 6.9008 | 6.9008 |  | 109 | SS-35/6kV Zhuravliki | 10+10 | 0 | 7.6502 | 4.051 | 120 | 3.5992 | 0 | 10.5 | 6.9008 | 6.9008
110 | SS-35/10kV Zavidovka | 2,5+2,5 | 876 | 492 | 1.0047 | 0.42 | 80 | 0.58471 | 0 | 2.625 | 2.0403 | 2.0403 |  | 110 | SS-35/10kV Zavidovka | 2,5+2,5 | 0 | 1.0047 | 0.42 | 80 | 0.58471 | 0 | 2.625 | 2.0403 | 2.0403
111 | SS-35/6kV Zapadnaya | 10+10+10 | 6216 | 3216 | 6.9987 | 1.707 | 120 | 5.2917 | 0 | 21 | 15.7083 | 15.7083 |  | 111 | SS-35/6kV Zapadnaya | 10+10+10 | 0 | 6.9987 | 1.707 | 120 | 5.2917 | 0 | 21 | 15.7083 | 15.7083
112 | SS-35/10kV Zozuli | 6,3+6,3 | 5808 | 2528 | 6.3343 | 3.88 | 80 | 2.4543 | 0 | 6.615 | 4.1607 | 4.1607 |  | 112 | SS-35/10kV Zozuli | 6,3+6,3 | 0 | 6.3343 | 3.88 | 80 | 2.4543 | 0 | 6.615 | 4.1607 | 4.1607
113 | SS-35/10kV Ivitsa | 2,5+2,5 | 1056 | 376 | 1.1209 | 0.58603 | 80 | 0.53491 | 0 | 2.625 | 2.0901 | 2.0901 |  | 113 | SS-35/10kV Ivitsa | 2,5+2,5 | 0 | 1.1209 | 0.58603 | 80 | 0.53491 | 0 | 2.625 | 2.0901 | 2.0901
114 | SS-35/10kV Ilovka | 4+4 | 2264 | 848 | 2.4176 | 2.056 | 45 | 0.3616 | 0 | 4.2 | 3.8384 | 3.8384 |  | 114 | SS-35/10kV Ilovka | 4+4 | 0 | 2.4176 | 2.056 | 45 | 0.3616 | 0 | 4.2 | 3.8384 | 3.8384
115 | SS-35/10kV Istobnoe | 4+2,5 | 1128 | 592 | 1.2739 | 0.93935 | 120 | 0.33456 | 0 | 2.625 | 2.2904 | 2.2904 |  | 115 | SS-35/10kV Istobnoe | 4+2,5 | 0 | 1.2739 | 0.93935 | 120 | 0.33456 | 0 | 2.625 | 2.2904 | 2.2904
116 | SS-35/10kV Kazatskaya | 2,5+4 | 1293 | 458 | 1.3717 | 0.87141 | 45 | 0.50031 | 0 | 2.625 | 2.1247 | 2.1247 |  | 116 | SS-35/10kV Kazatskaya | 2,5+4 | 0 | 1.3717 | 0.87141 | 45 | 0.50031 | 0 | 2.625 | 2.1247 | 2.1247
117 | SS-35/10kV Kazinka | 4+4 | 2784 | 924 | 2.9333 | 0.736 | 120 | 2.1973 | 0 | 4.2 | 2.0027 | 2.0027 |  | 117 | SS-35/10kV Kazinka | 4+4 | 0 | 2.9333 | 0.736 | 120 | 2.1973 | 0 | 4.2 | 2.0027 | 2.0027
118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 972 | 328 | 1.0258 | 0.712 | 120 | 0.31385 | 0 | 2.625 | 2.3112 | 2.3112 |  | 118 | SS-35/10kV Kamyshevatoe | 2,5+2,5 | 0 | 1.0258 | 0.712 | 120 | 0.31385 | 0 | 2.625 | 2.3112 | 2.3112
119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 3000 | 1284 | 3.2632 | 0.7035 | 120 | 2.5597 | 0 | 6.615 | 4.0553 | 4.0553 |  | 119 | SS-35/10kV Kirovskaya | 6,3+6,3 | 0 | 3.2632 | 0.7035 | 120 | 2.5597 | 0 | 6.615 | 4.0553 | 4.0553
120 | SS-35/10kV Kotovo | 2,5+2,5 | 2384 | 752 | 2.4998 | 1.648 | 20 | 0.85178 | 0 | 2.625 | 1.7732 | 1.7732 |  | 120 | SS-35/10kV Kotovo | 2,5+2,5 | 0 | 2.4998 | 1.648 | 20 | 0.85178 | 0 | 2.625 | 1.7732 | 1.7732
121 | SS-35/10kV Kochetovka | 2,5+4 | 684 | 240 | 0.72488 | 0.6286 | 45 | 0.096288 | 0 | 2.625 | 2.5287 | 2.5287 |  | 121 | SS-35/10kV Kochetovka | 2,5+4 | 1.09 | 1.8149 | 0.6286 | 45 | 1.1863 | 0 | 2.625 | 1.4387 | 1.4387
122 | SS-35/10kV Krasnoe | 4+2,5 | 1040 | 416 | 1.1201 | 1.1395 | 80 | -0.019407 | 0 | 2.625 | 2.6444 | 2.6444 |  | 122 | SS-35/10kV Krasnoe | 4+2,5 | 0 | 1.1201 | 1.1395 | 80 | -0.019407 | 0 | 2.625 | 2.6444 | 2.6444
123 | SS-35/10kV Kretovo | 4+2,5 | 1116 | 468 | 1.2102 | 0.67818 | 120 | 0.53198 | 0 | 2.625 | 2.093 | 2.093 |  | 123 | SS-35/10kV Kretovo | 4+2,5 | 0 | 1.2102 | 0.67818 | 120 | 0.53198 | 0 | 2.625 | 2.093 | 2.093
124 | SS-35/10kV Kurasovka | 4+4 | 2768 | 1408 | 3.1055 | 1.797 | 80 | 1.3085 | 0 | 4.2 | 2.8915 | 2.8915 |  | 124 | SS-35/10kV Kurasovka | 4+4 | 0.37 | 3.4755 | 1.797 | 80 | 1.6785 | 0 | 4.2 | 2.5215 | 2.5215
125 | SS-35/6kV Lebedi | 4+5,6 | 3801 | 1252 | 4.0019 | 0.581 | 120 | 3.4209 | 0 | 4.2 | 0.77911 | 0.77911 |  | 125 | SS-35/6kV Lebedi | 4+5,6 | 0.12 | 4.1219 | 0.581 | 120 | 3.5409 | 0 | 4.2 | 0.65911 | 0.65911
126 | SS-35/6kV Ledovaya | 4+4 | 2520 | 1239 | 2.8081 | 1.321 | 80 | 1.4871 | 0 | 4.2 | 2.7129 | 2.7129 |  | 126 | SS-35/6kV Ledovaya | 4+4 | 0 | 2.8081 | 1.321 | 80 | 1.4871 | 0 | 4.2 | 2.7129 | 2.7129
127 | SS-35/10kV Livenka | 4+4 | 3528 | 1776 | 3.9498 | 1.541 | 120 | 2.4088 | 0 | 4.2 | 1.7912 | 1.7912 |  | 127 | SS-35/10kV Livenka | 4+4 | 0.63 | 4.5798 | 1.541 | 120 | 3.0388 | 0 | 4.2 | 1.1612 | 1.1612
128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 768 | 324 | 0.83355 | 0.66672 | 80 | 0.16683 | 0 | 2.625 | 2.4582 | 2.4582 |  | 128 | SS-35/10kV Lubyanoe | 2,5+2,5 | 0 | 0.83355 | 0.66672 | 80 | 0.16683 | 0 | 2.625 | 2.4582 | 2.4582
129 | SS-35/10kV M.Pristan | 6,3+6,3 | 6768 | 3336 | 7.5455 | 1.81 | 45 | 5.7355 | 0 | 6.615 | 0.87949 | 0.87949 |  | 129 | SS-35/10kV M.Pristan | 6,3+6,3 | 0.1 | 7.6455 | 1.81 | 45 | 5.8355 | 0 | 6.615 | 0.77949 | 0.77949
130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 792 | 336 | 0.86033 | 0.60716 | 80 | 0.25316 | 0 | 2.625 | 2.3718 | 2.3718 |  | 130 | SS-35/10kV М.Troitsa | 2,5+2,5 | 0 | 0.86033 | 0.60716 | 80 | 0.25316 | 0 | 2.625 | 2.3718 | 2.3718
131 | SS-35/10kV Malinovka | 10+10 | 6400 | 3728 | 7.4066 | 1.357 | 120 | 6.0496 | 0 | 10.5 | 4.4504 | 4.4504 |  | 131 | SS-35/10kV Malinovka | 10+10 | 0.53 | 7.9366 | 1.357 | 120 | 6.5796 | 0 | 10.5 | 3.9204 | 3.9204
132 | SS-35/10kV Mandrovo | 2,5+2,5 | 1152 | 288 | 1.1875 | 0.65565 | 80 | 0.53181 | 0 | 2.625 | 2.0932 | 2.0932 |  | 132 | SS-35/10kV Mandrovo | 2,5+2,5 | 0 | 1.1875 | 0.65565 | 80 | 0.53181 | 0 | 2.625 | 2.0932 | 2.0932
133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 1236 | 462 | 1.3195 | 0.643 | 80 | 0.67652 | 0 | 2.625 | 1.9485 | 1.9485 |  | 133 | SS-35/10kV Mukhouderovka | 2,5+2,5 | 0 | 1.3195 | 0.643 | 80 | 0.67652 | 0 | 2.625 | 1.9485 | 1.9485
134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 1176 | 492 | 1.2748 | 0.59315 | 120 | 0.68162 | 0 | 2.625 | 1.9434 | 1.9434 |  | 134 | SS-35/10kV N.Alexandrovka | 2,5+2,5 | 0 | 1.2748 | 0.59315 | 120 | 0.68162 | 0 | 2.625 | 1.9434 | 1.9434
135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 608 | 288 | 0.67276 | 2.78 | 120 | -2.1072 | 0 | #VALUE! | #VALUE! | #VALUE! |  | 135 | SS-35/10kV N.Derevnya | 6,3+6,3 | 0.35 | 1.0228 | 2.78 | 120 | -1.7572 | 0 | #VALUE! | #VALUE! | #VALUE!
136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 3312 | 1248 | 3.5393 | 0.842 | 45 | 2.6973 | 0 | 6.615 | 3.9177 | 3.9177 |  | 136 | SS-35/10kV N.Tavolzhanka | 6,3+6,3 | 0.31 | 3.8493 | 0.842 | 45 | 3.0073 | 0 | 6.615 | 3.6077 | 3.6077
137 | SS-35/10kV N.Ukolovo | 4+2,5 | 1436 | 580 | 1.5487 | 0.57 | 80 | 0.97871 | 0 | 2.625 | 1.6463 | 1.6463 |  | 137 | SS-35/10kV N.Ukolovo | 4+2,5 | 0 | 1.5487 | 0.57 | 80 | 0.97871 | 0 | 2.625 | 1.6463 | 1.6463
138 | SS-35/10kV N.Khutornoe | 2,5+4 | 279 | 99 | 0.29604 | 0.19 | 80 | 0.10604 | 0 | 2.625 | 2.519 | 2.519 |  | 138 | SS-35/10kV N.Khutornoe | 2,5+4 | 0 | 0.29604 | 0.19 | 80 | 0.10604 | 0 | 2.625 | 2.519 | 2.519
139 | SS-35/10kV Neminushchee | 2,5+2,5 | 1674 | 560 | 1.7652 | 0.65147 | 80 | 1.1137 | 0 | 2.625 | 1.5113 | 1.5113 |  | 139 | SS-35/10kV Neminushchee | 2,5+2,5 | 0 | 1.7652 | 0.65147 | 80 | 1.1137 | 0 | 2.625 | 1.5113 | 1.5113
140 | SS-35/10kV Nechaevka | 4+4 | 1304 | 416 | 1.3687 | 0.451 | 120 | 0.91775 | 0 | 4.2 | 3.2823 | 3.2823 |  | 140 | SS-35/10kV Nechaevka | 4+4 | 0 | 1.3687 | 0.451 | 120 | 0.91775 | 0 | 4.2 | 3.2823 | 3.2823
141 | SS-35/10kV Nikitovka | 2,5+2,5 | 1856 | 648 | 1.9659 | 1.4354 | 80 | 0.53044 | 0 | 2.625 | 2.0946 | 2.0946 |  | 141 | SS-35/10kV Nikitovka | 2,5+2,5 | 0 | 1.9659 | 1.4354 | 80 | 0.53044 | 0 | 2.625 | 2.0946 | 2.0946
142 | SS-35/10kV Novenkoe | 4+4 | 2056 | 600 | 2.1418 | 1.7332 | 80 | 0.40855 | 0 | 4.2 | 3.7915 | 3.7915 |  | 142 | SS-35/10kV Novenkoe | 4+4 | 0 | 2.1418 | 1.7332 | 80 | 0.40855 | 0 | 4.2 | 3.7915 | 3.7915
143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 6128 | 2176 | 6.5029 | 0.872 | 80 | 5.6309 | 0 | 6.615 | 0.98413 | 0.98413 |  | 143 | SS-35/10kV Oktyabrskaya | 6,3+6,3 | 2.1 | 8.6029 | 0.872 | 80 | 7.7309 | 0 | 6.615 | -1.1159 | -1.1159
144 | SS-35/10kV Orlik | 4+4 | 1836 | 756 | 1.9856 | 0.553 | 80 | 1.4326 | 0 | 4.2 | 2.7674 | 2.7674 |  | 144 | SS-35/10kV Orlik | 4+4 | 0 | 1.9856 | 0.553 | 80 | 1.4326 | 0 | 4.2 | 2.7674 | 2.7674
145 | SS-35/10kV Podolkhi | 2,5+2,5 | 2014 | 792 | 2.1641 | 1.1225 | 45 | 1.0416 | 0 | 2.625 | 1.5834 | 1.5834 |  | 145 | SS-35/10kV Podolkhi | 2,5+2,5 | 0.77 | 2.9341 | 1.1225 | 45 | 1.8116 | 0 | 2.625 | 0.81336 | 0.81336
146 | SS-35/10kV Popovka | 6,3+4 | 1152 | 532 | 1.2689 | 0.64636 | 80 | 0.62255 | 0 | 4.2 | 3.5775 | 3.5775 |  | 146 | SS-35/10kV Popovka | 6,3+4 | 0 | 1.2689 | 0.64636 | 80 | 0.62255 | 0 | 4.2 | 3.5775 | 3.5775
147 | SS-35/10kV Prelestnoe | 4+4 | 4020 | 1524 | 4.2992 | 0 | 0 | 4.2992 | 0 | 4.2 | -0.099183 | -0.099183 |  | 147 | SS-35/10kV Prelestnoe | 4+4 | 0 | 4.2992 | 0 | 0 | 4.2992 | 0 | 4.2 | -0.099183 | -0.099183
148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 5242 | 2492 | 5.8042 | 0 | 0 | 5.8042 | 0 | 6.615 | 0.81081 | 0.81081 |  | 148 | SS-35/6kV Privokzalnaya | 6,3+6,3 | 0 | 5.8042 | 0 | 0 | 5.8042 | 0 | 6.615 | 0.81081 | 0.81081
149 | SS-35/10kV Prilepy | 2,5+2,5 | 600 | 378 | 0.70914 | 0.37638 | 80 | 0.33277 | 0 | 2.625 | 2.2922 | 2.2922 |  | 149 | SS-35/10kV Prilepy | 2,5+2,5 | 0 | 0.70914 | 0.37638 | 80 | 0.33277 | 0 | 2.625 | 2.2922 | 2.2922
150 | SS-35/10kV Printsevka | 2,5+2,5 | 1616 | 640 | 1.7381 | 0.352 | 120 | 1.3861 | 0 | 2.625 | 1.2389 | 1.2389 |  | 150 | SS-35/10kV Printsevka | 2,5+2,5 | 0.09 | 1.8281 | 0.352 | 120 | 1.4761 | 0 | 2.625 | 1.1489 | 1.1489
151 | SS-35/10kV Radkovka | 6,3+6,3 | 4736 | 1888 | 5.0985 | 0.164 | 45 | 4.9345 | 0 | 6.615 | 1.6805 | 1.6805 |  | 151 | SS-35/10kV Radkovka | 6,3+6,3 | 0 | 5.0985 | 0.164 | 45 | 4.9345 | 0 | 6.615 | 1.6805 | 1.6805
152 | SS-35/10kV Razdornoe | 2,5+2,5 | 1278 | 684 | 1.4495 | 0.662 | 80 | 0.78753 | 0 | 2.625 | 1.8375 | 1.8375 |  | 152 | SS-35/10kV Razdornoe | 2,5+2,5 | 0 | 1.4495 | 0.662 | 80 | 0.78753 | 0 | 2.625 | 1.8375 | 1.8375
153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 1536 | 744 | 1.7067 | 0.88491 | 80 | 0.82179 | 0 | 2.625 | 1.8032 | 1.8032 |  | 153 | SS-35/10kV Repyakhovka | 2,5+2,5 | 0.04 | 1.7467 | 0.88491 | 80 | 0.86179 | 0 | 2.625 | 1.7632 | 1.7632
154 | SS-35/10kV Rzhevka | 10+10 | 5736 | 2664 | 6.3244 | 2.53 | 45 | 3.7944 | 0 | 10.5 | 6.7056 | 6.7056 |  | 154 | SS-35/10kV Rzhevka | 10+10 | 0 | 6.3244 | 2.53 | 45 | 3.7944 | 0 | 10.5 | 6.7056 | 6.7056
155 | SS-35/10kV Rovenki | 4+4 | 3000 | 1188 | 3.2267 | 1.7393 | 120 | 1.4874 | 0 | 4.2 | 2.7126 | 2.7126 |  | 155 | SS-35/10kV Rovenki | 4+4 | 0 | 3.2267 | 1.7393 | 120 | 1.4874 | 0 | 4.2 | 2.7126 | 2.7126
156 | SS-35/10kV Rogovatoe | 4+4 | 1648 | 736 | 1.8049 | 0 | 0 | 1.8049 | 0 | 2.625 | 0.82012 | 0.82012 |  | 156 | SS-35/10kV Rogovatoe | 4+4 | 0 | 1.8049 | 0 | 0 | 1.8049 | 0 | 2.625 | 0.82012 | 0.82012
157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 805 | 381 | 0.89061 | 0 | 0 | 0.89061 | 0 | 2.625 | 1.7344 | 1.7344 |  | 157 | SS-35/0,4kV Rozhdestvenskaya | 2,5+2,5 | 0 | 0 | 0 | 0 | 0 | 0 | 2.625 | 2.625 | 2.625
158 | SS-35/10kV Saprykino | 2,5+2,5 | 288 | 152 | 0.32565 | 0.22751 | 120 | 0.098137 | 0 | 2.625 | 2.5269 | 2.5269 |  | 158 | SS-35/10kV Saprykino | 2,5+2,5 | 0 | 0.32565 | 0.22751 | 120 | 0.098137 | 0 | 2.625 | 2.5269 | 2.5269
159 | SS-35/6kV Severnaya | 6,3+6,3 | 6278 | 1901 | 6.5595 | 4.8049 | 120 | 1.7546 | 0 | 6.615 | 4.8604 | 4.8604 |  | 159 | SS-35/6kV Severnaya | 6,3+6,3 | 0 | 6.5595 | 4.8049 | 120 | 1.7546 | 0 | 6.615 | 4.8604 | 4.8604
160 | SS-35/10kV Setishche | 2,5+2,5 | 1806 | 754 | 1.9571 | 1.0621 | 80 | 0.89496 | 0 | 2.625 | 1.73 | 1.73 |  | 160 | SS-35/10kV Setishche | 2,5+2,5 | 0 | 1.9571 | 1.0621 | 80 | 0.89496 | 0 | 2.625 | 1.73 | 1.73
161 | SS-35/10kV Slonovka | 4+4 | 2288 | 1184 | 2.5762 | 1.1306 | 120 | 1.4456 | 0 | 4.2 | 2.7544 | 2.7544 |  | 161 | SS-35/10kV Slonovka | 4+4 | 0.85 | 3.4262 | 1.1306 | 120 | 2.2956 | 0 | 4.2 | 1.9044 | 1.9044
162 | SS-35/6kV St.Oskol -2 | 16+16 | 10742 | 4668 | 11.7124 | 1.21 | 80 | 10.5024 | 0 | 16.8 | 6.2976 | 6.2976 |  | 162 | SS-35/6kV St.Oskol -2 | 16+16 | 0 | 11.7124 | 1.21 | 80 | 10.5024 | 0 | 16.8 | 6.2976 | 6.2976
163 | SS-35/10kV Starikovo | 4+4 | 2028 | 684 | 2.1402 | 1.3453 | 45 | 0.79494 | 0 | 4.2 | 3.4051 | 3.4051 |  | 163 | SS-35/10kV Starikovo | 4+4 | 0 | 2.1402 | 1.3453 | 45 | 0.79494 | 0 | 4.2 | 3.4051 | 3.4051
164 | SS-35/10kV Tavrovo | 10+10 | 8592 | 1656 | 8.7501 | 0.531 | 45 | 8.2191 | 0 | 10.5 | 2.2809 | 2.2809 |  | 164 | SS-35/10kV Tavrovo | 10+10 | 0.29 | 9.0401 | 0.531 | 45 | 8.5091 | 0 | 10.5 | 1.9909 | 1.9909
165 | SS-35/10kV Terebrino | 2,5+2,5 | 960 | 504 | 1.0843 | 0.44978 | 80 | 0.63448 | 0 | 2.625 | 1.9905 | 1.9905 |  | 165 | SS-35/10kV Terebrino | 2,5+2,5 | 0 | 1.0843 | 0.44978 | 80 | 0.63448 | 0 | 2.625 | 1.9905 | 1.9905
166 | SS-35/10kV Urazovo | 6,3+6,3 | 4116 | 1140 | 4.271 | 1.39 | 120 | 2.881 | 0 | 6.615 | 3.734 | 3.734 |  | 166 | SS-35/10kV Urazovo | 6,3+6,3 | 0.04 | 4.311 | 1.39 | 120 | 2.921 | 0 | 6.615 | 3.694 | 3.694
167 | SS-35/10kV Utochka | 1,6+2,5 | 728 | 284 | 0.78143 | 0.47242 | 80 | 0.30902 | 0 | 1.68 | 1.371 | 1.371 |  | 167 | SS-35/10kV Utochka | 1,6+2,5 | 0 | 0.78143 | 0.47242 | 80 | 0.30902 | 0 | 1.68 | 1.371 | 1.371
168 | SS-35/6kV Fedoseevka | 4+4 | 1795 | 643 | 1.9067 | 0 | 0 | 1.9067 | 0 | 4.2 | 2.2933 | 2.2933 |  | 168 | SS-35/6kV Fedoseevka | 4+4 | 0.14 | 2.0467 | 0 | 0 | 2.0467 | 0 | 4.2 | 2.1533 | 2.1533
169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 872 | 392 | 0.95606 | 0.78681 | 45 | 0.16925 | 0 | 1.68 | 1.5107 | 1.5107 |  | 169 | SS-35/10kV Foshchevatvo | 1,6+2,5 | 0 | 0.95606 | 0.78681 | 45 | 0.16925 | 0 | 1.68 | 1.5107 | 1.5107
170 | SS-35/10kV Kholodnoe | 4+4 | 1796 | 556 | 1.8801 | 0 | 0 | 1.8801 | 0 | 4.2 | 2.3199 | 2.3199 |  | 170 | SS-35/10kV Kholodnoe | 4+4 | 0.37 | 2.2501 | 0 | 0 | 2.2501 | 0 | 4.2 | 1.9499 | 1.9499
171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 2160 | 1500 | 2.6298 | 1.3513 | 20 | 1.2785 | 0 | 6.615 | 5.3365 | 5.3365 |  | 171 | SS-35/6kV Chernyansky sugar plant | 7,5+6,3 | 0.03 | 2.6598 | 1.3513 | 20 | 1.3085 | 0 | 6.615 | 5.3065 | 5.3065
172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0 | 0 | 0 | 1 | 80 | -1 | 0 | 2.625 | 3.625 | 3.625 |  | 172 | SS-35/10kV Tserkovnaya | 2,5+2,5 | 0 | 0 | 1 | 80 | -1 | 0 | 1 | 2 | 2
173 | SS-35/10kV Shatalovka | 6,3+6,3 | 1704 | 744 | 1.8593 | 0 | 0 | 1.8593 | 0 | 6.615 | 4.7557 | 4.7557 |  | 173 | SS-35/10kV Shatalovka | 6,3+6,3 | 0 | 1.8593 | 0 | 0 | 1.8593 | 0 | 6.615 | 4.7557 | 4.7557
174 | SS-35/10kV Shakhovka | 2,5+2,5 | 1668 | 582 | 1.7666 | 0.79066 | 80 | 0.97596 | 0 | 2.625 | 1.649 | 1.649 |  | 174 | SS-35/10kV Shakhovka | 2,5+2,5 | 0.06 | 1.8266 | 0.79066 | 80 | 1.036 | 0 | 2.625 | 1.589 | 1.589
175 | SS-35/10kV Shishino | 6,3+6,3 | 3376 | 944 | 3.5055 | 1.03 | 80 | 2.4755 | 0 | 4.2 | 1.7245 | 1.7245 |  | 175 | SS-35/10kV Shishino | 6,3+6,3 | 0.46 | 3.9655 | 1.03 | 80 | 2.9355 | 0 | 4.2 | 1.2645 | 1.2645
176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 254 | 197 | 0.32144 | 0 | 0 | 0.32144 | 0 | 1.68 | 1.3586 | 1.3586 |  | 176 | SS-35/0,4kV Yubileynaya | 1,6+1,6 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 1.68 | 1.68
177 | SS-35/10kV Yablonovo | 4+4 | 1440 | 624 | 1.5694 | 1.1284 | 80 | 0.44096 | 0 | 4.2 | 3.759 | 3.759 |  | 177 | SS-35/10kV Yablonovo | 4+4 | 0.46 | 2.0294 | 1.1284 | 80 | 0.90096 | 0 | 4.2 | 3.299 | 3.299
178 | SS-35/10kV Yarskoe | 2,5+2,5 | 492 | 204 | 0.53262 | 0.14648 | 80 | 0.38614 | 0 | 2.625 | 2.2389 | 2.2389 |  | 178 | SS-35/10kV Yarskoe | 2,5+2,5 | 0 | 0.53262 | 0.14648 | 80 | 0.38614 | 0 | 2.625 | 2.2389 | 2.2389
| ИТОГО: | 3271.1 |  |  | #N/A | #N/A |  | #N/A | [5 empty] | 2: ИТОГО:; 3: 3211.9; 4: #N/A; 5: #N/A; MVA 6: #N/A; Min 8: #N/A
| дефицит | [10 empty] | -21.3453 |  | 2: дефицит; Min 12: 0
| профицит | [10 empty] | #VALUE! |  | 2: профицит; Min 12: #VALUE!

## Текущий дефицит - зима
The list of closed supply centers of IDGC of Centre (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA
Belgorodenergo
1 | SS-110/35/10kV Konshino | 6.3 | -0.01991
2 | SS-110/35/10kV Orositelnaya | 16 | -3.0396
3 | SS-35/10kV Afanasevka | 1.6 | -0.18882
4 | SS-35/10kV Borisovka | 1.6 | -0.12418
5 | SS-35/10kV Borisiy | 1.6 | -0.85907
6 | SS-35/10kV Gostischevo | 4 | -0.57031
7 | SS-35/10kV Zemsnaryad | 1 | -0.023601
8 | SS-35/10kV Kazachya Lisitsa | 2.5 | -0.34986
9 | SS-35/10kV Kamyzino | 2.5 | -0.41596
10 | SS-35/10kV Koloskovo | 2.5 | -0.017324
11 | SS-35/10kV Kryukovo | 2.5 | -0.085746
12 | SS-35/10kV Nikolaevka | 2.5 | -0.051736
13 | SS-35/10kV Nikolskoye | 4 | -0.80327
14 | SS-35/10kV Pyatnitskoe | 4 | -0.66234
15 | SS-110/35/6kV Vostochnaya | 25+25 | -13.9347
16 | SS-110/10kV Sheino | 3,2+10 | -0.099619
17 | SS-35/10kV Prelestnoye | 4+4 | -0.099183
Total current deficit |  |  | -21.3453

## Ожидаемый дефицит
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class |  | Current deficit, MVA
Belgorodenergo
1 | SS-110/35/10kV Konshino | 6.3 | -0.01991 | closed
2 | SS-110/35/10kV Orositelnaya | 16 | -3.0396 | closed
3 | SS-35/10kV Afanasevka | 1.6 | -0.18882 | closed
4 | SS-35/10kV Borisovka | 1.6 | -0.12418 | closed
5 | SS-35/10kV Borisiy | 1.6 | -0.85907 | closed
6 | SS-35/10kV Gostischevo | 4 | -0.57031 | closed
7 | SS-35/10kV Zemsnaryad | 1 | -0.023601 | closed
8 | SS-35/10kV Kazachya Lisitsa | 2.5 | -0.34986 | closed
9 | SS-35/10kV Kamyzino | 2.5 | -0.41596 | closed
10 | SS-35/10kV Koloskovo | 2.5 | -0.017324 | closed
11 | SS-35/10kV Kryukovo | 2.5 | -0.085746 | closed
| SS-35/10kV Malakeevo | 2.5 | -0.11954
12 | SS-35/10kV Nikolaevka | 2.5 | -0.051736 | closed
13 | SS-35/10kV Nikolskoye | 4 | -0.80327 | closed
14 | SS-35/10kV Pyatnitskoe | 4 | -0.66234 | closed
15 | SS-110/35/6kV Vostochnaya | 25+25 | -13.9347 | closed
16 | SS-110/10kV Sheino | 3,2+10 | -0.099619 | closed
17 | SS-35/10kV Prelestnoye | 4+4 | -0.099183 | closed
| SS-35/10kV Oktyabrskaya | 6,3+6,3 | -1.1159
Total current deficit |  |  | -22.5807