## апрель 2010
Calculation of transmission capacity of Main substations of the branch "Belgorodenergo" of IDGC of Centre, JSC following the results of winter measurement of peak load of 2009.
Table 1
No. | Object of main substation, voltage class | Current deficit | [10 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | P | Q | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
[5 empty] | MVA | MVA | Min.
1 | 2 | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12
One-transformer substations
1 | SS-110/35/10kv D.Polyana | 6.3 | 1523 | 679 | 1.6675 | 1.457 | 45 | 1.457 | 0 | 1.457 | -0.2105 | -0.57942
| Sн. MV, МVА | 6.3 | 513 | 301 | 0.59479 | 0.958 |  | 0.958 | 0 | 0.958 | 0.36321
| Sн. LV, МVА | 6.3 | 1010 | 378 | 1.0784 | 0.499 |  | 0.499 | 0 | 0.499 | -0.57942
2 | SS-110/35/10kv Konshino | 6.3 | 375 | 154 | 0.40539 | 0.39 | 20 | 0.39 | 0 | 0.39 | -0.01539 | -0.01539
| Sн. MV, МVА | 6.3 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, МVА | 6.3 | 375 | 154 | 0.40539 | 0.39 |  | 0.39 | 0 | 0.39 | -0.01539
3 | SS-110/35/10kv Orositelnaya | 16 | 11884 | 2898 | 12.2322 | 11.607 | 120 | 11.607 | 0 | 11.607 | -0.62525 | -0.90525
| Sн. MV, МVА | 16 | 9059 | 2898 | 9.5113 | 8.606 |  | 8.606 | 0 | 8.606 | -0.90525
| Sн. LV, МVА | 16 | 2825 |  | 2.825 | 3.001 |  | 3.001 | 0 | 3.001 | 0.176
4 | SS-110/35/6kv Pishcheprom | 25 | 6036 | 1850 | 6.3131 | 6.679 | 120 | 6.679 | 0 | 6.679 | 0.36586 | -0.24769
| Sн. MV, МVА | 12.5 | 2171 | 662 | 2.2697 | 2.022 |  | 2.022 | 0 | 2.022 | -0.24769
| Sн. LV, МVА | 12.5 | 3865 | 1188 | 4.0435 | 4.657 |  | 4.657 | 0 | 4.657 | 0.61354
5 | SS-110/35/10kv Rovenki | 16 | 2453 | 976 | 2.64 | 3.44 | 120 | 3.44 | 0 | 3.44 | 0.79996 | 0.79996
| Sн. MV, МVА | 16 | 2 | 34 | 0.034059 | 4 |  | 4 | 0 | 4 | 3.9659
| Sн. LV, МVА | 16 | 2451 | 942 | 2.6258 | 3.44 |  | 3.44 | 0 | 3.44 | 0.81421
6 | SS-110/35/10kv Serebryanka | 10 | 1181 | 534 | 1.2961 | 1.78 | 45 | 1.78 | 0 | 1.78 | 0.48388 | 0
| Sн. MV, МVА | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Sн. LV, MVА | 10 | 1181 | 534 | 1.2961 | 1.78 |  | 1.78 | 0 | 1.78 | 0.48388
7 | SS-35/10kv Afanasyevka | 1.6 | 868 | 280 | 0.91204 | 0.6464 | 45 | 0.6464 | 0 | 0.6464 | -0.26564 | -0.26564
8 | SS-35/10kv Borisovka | 1.6 | 576 | 192 | 0.60716 | 0.6835 | 45 | 0.6835 | 0 | 0.6835 | 0.076343 | 0.076343
9 | SS-35/10kv Borisy | 1.6 | 432 | 234 | 0.4913 | 0 | 20 | 0 | 0 | 0 | -0.4913 | -0.4913
10 | SS-35/10kv Gostishchevo | 4 | 3792 | 1440 | 4.0562 | 2.64 | 80 | 2.64 | 0 | 2.64 | -1.4162 | -1.4162
11 | SS-35/10kv Gruzskoe | 1.6 | 606 | 264 | 0.66101 | 1.05 | 80 | 1.05 | 0 | 1.05 | 0.38899 | 0.38899
12 | SS-35/10kv Zemsnaryad | 1.6 | 14 | 14 | 0.019799 | 0 |  | 0 | 0 | 0 | -0.019799 | -0.019799
13 | SS-35/10kv Kazachya Lisitsa | 2.5 | 360 | 112 | 0.37702 | 0 |  | 0 | 0 | 0 | -0.37702 | -0.37702
14 | SS-35/10kv Kamyzino | 2.5 | 992 | 392 | 1.0666 | 0.541 | 45 | 0.541 | 0 | 0.541 | -0.52564 | -0.52564
15 | SS-35/10kv Koloskovo | 2.5 | 2000 | 624 | 2.0951 | 1.6626 | 45 | 1.6626 | 0 | 1.6626 | -0.43248 | -0.43248
16 | SS-35/10jkv Kryukovo | 2.5 | 1584 | 492 | 1.6587 | 1.55 | 45 | 1.55 | 0 | 1.55 | -0.10865 | -0.10865
17 | SS-35/10kv Kushchino | 1.6 | 384 | 144 | 0.41011 | 0.4101 | 80 | 0.4101 | 0 | 0.4101 | -1.218e-05 | -1.218e-05
18 | SS-35/10kv Lopukhinka | 2.5 | 384 | 160 | 0.416 | 0.407 | 20 | 0.407 | 0 | 0.407 | -0.009 | -0.009
19 | SS-35/10kv Malakeevo | 2.5 | 1296 | 648 | 1.449 | 1.38 | 120 | 1.38 | 0 | 1.38 | -0.068972 | -0.068972
20 | SS-35/10kv Murom | 2.5 | 1336 | 432 | 1.4041 | 1.54 | 45 | 1.54 | 0 | 1.54 | 0.13589 | 0.13589
21 | SS-35/10kv Nikolaevka | 2.5 | 664 | 288 | 0.72377 | 0.6647 | 45 | 0.6647 | 0 | 0.6647 | -0.059068 | -0.059068
22 | SS-35/10kv Nikolskoe | 4 | 1776 | 396 | 1.8196 | 0.78 | 120 | 0.78 | 0 | 0.78 | -1.0396 | -1.0396
23 | SS-35/10kv Pokrovka | 4 | 708 | 300 | 0.76894 | 0.722 | 45 | 0.722 | 0 | 0.722 | -0.046937 | -0.046937
24 | SS-35/10kv Pyatnitskoe | 4 | 2441 | 768 | 2.559 | 1.84 | 80 | 1.84 | 0 | 1.84 | -0.71897 | -0.71897
25 | SS-35/10kv Sugar plant Ivnya | 2.5 | 94 | 151 | 0.17787 | 1.676 | 80 | 1.676 | 0 | 1.676 | 1.4981 | 1.4981
26 | SS-35/10kv Svistovka | 2.5 | 616 | 304 | 0.68693 | 0.6872 | 45 | 0.6872 | 0 | 0.6872 | 0.0002706 | 0.0002706
27 | SS-35/10kv sovkhoz "Urazovsky" | 2.5 | 688 | 244 | 0.72999 | 0.7238 | 120 | 0.7238 | 0 | 0.7238 | -0.0061863 | -0.0061863
28 | SS-35/10kv Kharkovskoe | 2.5 | 660 | 304 | 0.72665 | 0.6797 | 120 | 0.6797 | 0 | 0.6797 | -0.046947 | -0.046947
29 | SS-35/10kv Tserkovnaya | 2.5 | 1112 | 288 | 1.1487 | 1 | 80 | 1 | 0 | 1 | -0.14869 | -0.14869
Two- and more transformer substations
30 | SS-110/6kv Automobile maintenance plant | 16+16 | 13361 | 7836 | 15.4893 | 3.561 | 45 | 11.9283 | 0 | 16.8 | 4.8717 | 4.8717
31 | SS-110/35/10kv Aydar | 16+10 | 9152 | 3513 | 9.8031 | 8.95 | 120 | 0.85307 | 0 | 10.5 | 9.6469 | 9.6416
| Sн. MV, МVА | 16+10 | 7582 | 2985 | 8.1484 | 7.29 |  | 0.85843 | 0 | 10.5 | 9.6416
| Sн. LV, МVА | 16+10 | 1570 | 528 | 1.6564 | 1.66 |  | -0.003593 | 0 | 10.5 | 10.5036
32 | SS-110/35/10kv Alexandrovka | 16+16 | 12411 | 4290 | 13.1315 | 8.37 | 80 | 4.7615 | 0 | 16.8 | 12.0385 | 12.0385
| Sн. MV, МVА | 16+16 | 6573 | 2264 | 6.952 | 6.697 |  | 0.25498 | 0 | 16.8 | 16.545
| Sн. LV, МVА | 16+16 | 5838 | 2026 | 6.1796 | 1.673 |  | 4.5066 | 0 | 16.8 | 12.2934
33 | SS-110/35/10kv Alexeevka | 25+25+25 | 39765 | 17571 | 43.4741 | 5.322 | 120 | 38.1521 | 0 | 52.5 | 14.3479 | 14.3479
| Sн. MV, МVА | 25+25+25 | 16965 | 8691 | 19.0616 | 3.102 |  | 15.9596 | 0 | 52.5 | 36.5404
| Sн. LV, МVА | 25+25+25 | 22800 | 8880 | 24.4682 | 2.22 |  | 22.2482 | 0 | 52.5 | 30.2518
34 | SS-110/35/10kv Arkhangelskoe | 10+16 | 10006 | 3960 | 10.7611 | 8.87 | 45 | 1.8911 | 0 | 10.5 | 8.6089 | 8.6089
| Sн. MV, МVА | 10+16 | 9416 | 3776 | 10.1449 | 8.867 |  | 1.2779 | 0 | 10.5 | 9.2221
| Sн. LV, МVА | 10+16 | 590 | 184 | 0.61803 | 0 |  | 0.61803 | 0 | 10.5 | 9.882
35 | SS-110/6kv Belgorod-1 | 40+48 | 42786 | 13076 | 44.7395 | 0 | 120 | 44.7395 | 0 | 42 | -2.7395 | -2.7395
36 | SS-110/35/10kv Borisovka | 16+16 | 11354 | 4570 | 12.2392 | 11.433 | 120 | 0.80621 | 0 | 16.8 | 15.9938 | 4.8462
| Sн. MV, МVА | 16+8 | 4826 | 2482 | 5.4268 | 8.133 |  | -2.7062 | 0 | 8.4 | 11.1062
| Sн. LV, МVА | 16+8 | 6528 | 2088 | 6.8538 | 3.3 |  | 3.5538 | 0 | 8.4 | 4.8462
37 | SS-110/35/10kv V.Pokrovka | 10+10 | 9651 | 3834 | 10.3847 | 11.5 | 120 | -1.1153 | 0 | 10.5 | 11.6153 | 9.4887
| Sн. MV, МVА | 10+10 | 8148 | 3354 | 8.8113 | 7.8 |  | 1.0113 | 0 | 10.5 | 9.4887
| Sн. LV, МVА | 10+10 | 1503 | 480 | 1.5778 | 3.7 |  | -2.1222 | 0 | 10.5 | 12.6222
38 | SS-110/35/10kv Veydelevka | 10+10 | 9151 | 3160 | 9.6812 | 8.83 | 120 | 0.85124 | 0 | 10.5 | 9.6488 | 9.1219
| Sн. MV, МVА | 10+10 | 4999 | 1858 | 5.3331 | 3.955 |  | 1.3781 | 0 | 10.5 | 9.1219
| Sн. LV, МVА | 10+10 | 4152 | 1302 | 4.3514 | 4.875 |  | -0.52364 | 0 | 10.5 | 11.0236
39 | SS-110/6kv Vitamin plant | 25+25 | 13429 | 6832 | 15.067 | 1.46 | 45 | 13.607 | 0 | 26.25 | 12.643 | 12.643
40 | SS-110/35/10kv Volokonovka | 25+25 | 18812 | 6807 | 20.0057 | 10.651 | 120 | 9.3547 | 0 | 26.25 | 16.8953 | 16.8953
| Sн. MV, МVА | 25+25 | 10517 | 4038 | 11.2656 | 8.576 |  | 2.6896 | 0 | 26.25 | 23.5604
| Sн. LV, МVА | 25+25 | 8295 | 2769 | 8.745 | 2.075 |  | 6.67 | 0 | 26.25 | 19.58
41 | SS-110/35/6kv Vostochnaya | 25+25 | 37165 | 16321 | 40.5908 | 25.07 | 120 | 15.5208 | 0 | 26.25 | 10.7292 | 6.2914
| Sн. MV, МVА | 25+25 | 16029 | 5536 | 16.9581 | 21.3 |  | -4.3419 | 0 | 26.25 | 30.5919
| Sн. LV, МVА | 25+25 | 21136 | 10785 | 23.7286 | 3.77 |  | 19.9586 | 0 | 26.25 | 6.2914
42 | SS-110/10/6kv Golofeevka | 25+25 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 26.25 | 23.6599 | 10.5349
| Sн. MV, МVА | 12,5+12,5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13.125 | 13.125
| Sн. LV, МVА | 12,5+12,5 | 2404 | 964 | 2.5901 | 0 |  | 2.5901 | 0 | 13.125 | 10.5349
43 | SS-110/10kv Gotnya | 16+16 | 8388 | 3608 | 9.1311 | 6.43 | 120 | 2.7011 | 0 | 16.8 | 14.0989 | 14.0989
44 | SS-110/35/10kv Grayvoron | 16+16 | 13281 | 5063 | 14.2133 | 13.953 | 80 | 0.26034 | 0 | 16.8 | 16.5397 | 14.4501
| Sн. MV, МVА | 16+16 | 8161 | 3347 | 8.8207 | 10.903 |  | -2.0823 | 0 | 16.8 | 18.8823
| Sн. LV, МVА | 16+16 | 5120 | 1716 | 5.3999 | 3.05 |  | 2.3499 | 0 | 16.8 | 14.4501
45 | SS-110/6kv Donets | 40+40 | 26016 | 7584 | 27.0989 | 6.73 | 120 | 20.3689 | 0 | 42 | 21.6311 | 21.6311
46 | SS-110/10kv Dubovoe | 40+40 | 23785 | 4642 | 24.2337 | 11.23 | 120 | 13.0037 | 0 | 42 | 28.9963 | 28.9963
47 | SS-110/35/6kv Zhuravliki | 40+25 | 23335 | 7691 | 24.5698 | 12.4 | 120 | 12.1698 | 0 | 42 | 29.8302 | 29.8302
| Sн. MV, МVА | 40+25 | 16567 | 6202 | 17.6898 | 6.227 |  | 11.4628 | 0 | 42 | 30.5372
| Sн. LV, МVА | 40+25 | 6768 | 1489 | 6.9299 | 6.173 |  | 0.75686 | 0 | 42 | 41.2431
48 | SS-110/10kv Zapadnaya | 16+16 | 15459 | 3295 | 15.8063 | 1.249 | 80 | 14.5573 | 0 | 16.8 | 2.2427 | 2.2427
49 | SS-110/35/10kv Ivnya | 10+10 | 5960 | 2270 | 6.3777 | 6.16 | 80 | 0.21766 | 0 | 10.5 | 10.2823 | 10.2823
| Sн. MV, МVА | 10+10 | 2266 | 1008 | 2.4801 | 2.375 |  | 0.10508 | 0 | 10.5 | 10.3949
| Sн. LV, МVА | 10+10 | 3694 | 1262 | 3.9036 | 3.785 |  | 0.11862 | 0 | 10.5 | 10.3814
50 | SS-110/35/10kv K.Gvardiya | 16+16 | 16357 | 6666 | 17.6632 | 7.7116 | 120 | 9.9516 | 0 | 16.8 | 6.8484 | 6.8484
| Sн. MV, МVА | 16+16 | 8971 | 4110 | 9.8677 | 4.854 |  | 5.0137 | 0 | 16.8 | 11.7863
| Sн. LV, МVА | 16+16 | 7386 | 2556 | 7.8158 | 2.8576 |  | 4.9582 | 0 | 16.8 | 11.8418
51 | SS-110/10/6kv Kazatskie Bugry | 25+25 | 12571 | 3927 | 13.1701 | 9.65 | 80 | 3.5201 | 0 | 26.25 | 22.7299 | 18.8414
| Sн. MV, МVА | 25+25 | 1720 | 404 | 1.7668 | 1.384 |  | 0.38281 | 0 | 26.25 | 25.8672
| Sн. LV, МVА | 25+25 | 10851 | 3523 | 11.4086 | 4 |  | 7.4086 | 0 | 26.25 | 18.8414
52 | SS-110/35/10kv Korocha | 16+16+16 | 20632 | 7838 | 22.0707 | 2.019 | 20 | 20.0517 | 0 | 21 | 0.94835 | 0.94835
| Sн. MV, МVА | 16+16+16 | 8114 | 2802 | 8.5842 | 1.719 |  | 6.8652 | 0 | 21 | 14.1348
| Sн. LV, МVА | 16+16+16 | 12518 | 5036 | 13.493 | 0.3 |  | 13.193 | 0 | 21 | 7.807
53 | SS-110/35/10kv Krasnaya Yaruga | 10+10 | 9903 | 3556 | 10.5221 | 9.158 | 120 | 1.3641 | 0 | 10.5 | 9.1359 | 9.1359
| Sн. MV, МVА | 10+10 | 4393 | 1542 | 4.6558 | 3.52 |  | 1.1358 | 0 | 10.5 | 9.3642
| Sн. LV, МVА | 10+10 | 5510 | 2014 | 5.8665 | 5.638 |  | 0.22854 | 0 | 10.5 | 10.2715
54 | SS-110/10/10kv Mayskaya | 40+40 | 2581 | 670 | 2.6665 |  |  | 2.6665 | 0 | 42 | 39.3335 | 39.3335
55 | SS-110/35/10kv Maximovka | 16+16 | 7328 | 4264 | 8.4783 | 11.48 | 45 | -3.0017 | 0 | 16.8 | 19.8017 | 17.792
| Sн. MV, МVА | 16+16 | 6384 | 3830 | 7.4448 | 9.449 |  | -2.0042 | 0 | 16.8 | 18.8042
| Sн. LV, МVА | 16+16 | 944 | 434 | 1.039 | 2.031 |  | -0.99201 | 0 | 16.8 | 17.792
56 | SS-110/35/10kv N.Oskol | 25+31,5 | 21159 | 8583 | 22.8336 | 9.119 | 80 | 13.7146 | 0 | 26.25 | 12.5354 | 12.5354
| Sн. MV, МVА | 25+31,5 | 7395 | 3599 | 8.2243 | 7.83 |  | 0.39428 | 0 | 26.25 | 25.8557
| Sн. LV, МVА | 25+31,5 | 13764 | 4984 | 14.6386 | 1.289 |  | 13.3496 | 0 | 26.25 | 12.9004
57 | SS-110/10kv Obukhovskaya | 25+25 | 2272 | 372 | 2.3023 | 0 |  | 2.3023 | 0 | 26.25 | 23.9477 | 23.9477
58 | SS-110/6kv Ochistnye | 16+16 | 5231 | 2499 | 5.7973 | 0 |  | 5.7973 | 0 | 16.8 | 11.0027 | 11.0027
59 | SS-110/10kv Promyshlennaya | 25+25 | 15509 | 7413 | 17.1896 | 0 |  | 17.1896 | 0 | 26.25 | 9.0604 | 9.0604
60 | SS-110/10kv Poultry plant | 16+16 | 9980 | 5649 | 11.4679 | 1.296 | 80 | 10.1719 | 0 | 16.8 | 6.6281 | 6.6281
61 | SS-110/10kv Pushkarnaya | 40+40 | 33540 | 9360 | 34.8216 | 0 | 60 | 34.8216 | 0 | 42 | 7.1784 | 7.1784
62 | SS-110/35/10kv Rakitnoe | 10+10 | 10160 | 3946 | 10.8994 | 8.98 | 120 | 1.9194 | 0 | 10.5 | 8.5806 | 7.7972
| Sн. MV, МVА | 10+10 | 4944 | 3154 | 5.8644 | 6.407 |  | -0.54263 | 0 | 10.5 | 11.0426
| Sн. LV, МVА | 10+10 | 5216 | 792 | 5.2758 | 2.573 |  | 2.7028 | 0 | 10.5 | 7.7972
63 | SS-110/35/6kv Rudnik | 25+25 | 16284 | 8685 | 18.4553 | 10.46 | 45 | 7.9953 | 0 | 26.25 | 18.2547 | 18.2547
| Sн. MV, МVА | 25+25 | 10147 | 5511 | 11.547 | 10.46 |  | 1.087 | 0 | 26.25 | 25.163
| Sн. LV, МVА | 25+25 | 6137 | 3174 | 6.9092 | 0 |  | 6.9092 | 0 | 26.25 | 19.3408
64 | SS-110/10kv Severnaya | 40+40 | 12059 | 3183 | 12.472 | 3.312 | 45 | 9.16 | 0 | 42 | 32.84 | 32.84
65 | SS-110/35/10kv Skorodnoe | 16+16 | 11370 | 3385 | 11.8632 | 10.36 | 120 | 1.5032 | 0 | 16.8 | 15.2968 | 15.2968
| Sн. MV, МVА | 16+16 | 7443 | 2214 | 7.7653 | 7.562 |  | 0.20331 | 0 | 16.8 | 16.5967
| Sн. LV, МVА | 16+16 | 3927 | 1171 | 4.0979 | 2.798 |  | 1.2999 | 0 | 16.8 | 15.5001
66 | SS-110/35/6kv St.Oskol - 1 | 20+25+25 | 27161 | 10201 | 29.0135 | 0 |  | 29.0135 | 0 | 47.25 | 18.2365 | 18.2365
| Sн. MV, МVА | 20+25+25 | 5305 | 2289 | 5.7778 | 0 |  | 5.7778 | 0 | 47.25 | 41.4722
| Sн. LV, МVА | 20+25+25 | 21856 | 7912 | 23.244 | 0 |  | 23.244 | 0 | 47.25 | 24.006
67 | SS-110/35/10kv Streletskaya | 16+16 | 6052 | 1769 | 6.3052 | 2.23 | 80 | 4.0752 | 0 | 16.8 | 12.7248 | 4.3575
| Sн. MV, МVА | 16+8 | 7 | 95 | 0.095258 | 0 |  | 0.095258 | 0 | 8.4 | 8.3047
| Sн. LV, МVА | 16+8 | 6045 | 1674 | 6.2725 | 2.23 |  | 4.0425 | 0 | 8.4 | 4.3575
68 | SS-110/6kv Stroitel | 15+15 | 14665 | 5743 | 15.7494 | 0 |  | 15.7494 | 0 | 15.75 | 0.00057861 | 0.00057861
69 | SS-110/35/10kv Tomarovka | 16+16 | 12522 | 4336 | 13.2515 | 3.46 | 45 | 9.7915 | 0 | 16.8 | 7.0085 | 7.0085
| Sн. MV, МVА | 16+16 | 4590 | 1614 | 4.8655 | 3.46 |  | 1.4055 | 0 | 16.8 | 15.3945
| Sн. LV, МVА | 16+16 | 7932 | 2722 | 8.3861 | 0 |  | 8.3861 | 0 | 16.8 | 8.4139
70 | SS-110/6kv Chemical plant | 32+32 | 8580 | 3308 | 9.1956 | 5.56 | 45 | 3.6356 | 0 | 33.6 | 29.9644 | 29.9644
71 | SS-110/10kv Tsentralnaya | 40+40 | 31170 | 5706 | 31.688 | 0 |  | 31.688 | 0 | 42 | 10.312 | 10.312
72 | SS-110/35/10kv Cheremoshnoe | 25+25 | 23134 | 8712 | 24.7201 | 20.54 | 80 | 4.1801 | 0 | 26.25 | 22.0699 | 22.0699
| Sн. MV, МVА | 25+25 | 21521 | 7872 | 22.9155 | 19.676 |  | 3.2395 | 0 | 26.25 | 23.0105
| Sн. LV, МVА | 25+25 | 1613 | 840 | 1.8186 | 0 |  | 1.8186 | 0 | 26.25 | 24.4314
73 | SS-110/35/10kv Chernyanka | 16+16 | 16319 | 6059 | 17.4075 | 5.969 | 120 | 11.4385 | 0 | 16.8 | 5.3615 | 5.3615
| Sн. MV, МVА | 16+16 | 7422 | 3146 | 8.0612 | 5.969 |  | 2.0922 | 0 | 16.8 | 14.7078
| Sн. LV, МVА | 16+16 | 8897 | 2913 | 9.3617 | 0 |  | 9.3617 | 0 | 16.8 | 7.4383
74 | SS-110/35/6kv Shebekino | 40+40 | 27508 | 12250 | 30.1123 | 16.65 | 120 | 13.4623 | 0 | 42 | 28.5377 | 28.5377
| Sн. MV, МVА | 40+40 | 15624 | 7736 | 17.4343 | 11.682 |  | 5.7523 | 0 | 42 | 36.2477
| Sн. LV, МVА | 40+40 | 11884 | 4514 | 12.7124 | 4.968 |  | 7.7444 | 0 | 42 | 34.2556
75 | SS-110/10kv Sheino | 3,2+10 | 2394 | 805 | 2.5257 | 0 |  | 2.5257 | 0 | 3.36 | 0.83428 | 0.83428
76 | SS-110/10/6kv Yuzhnaya | 40+40 | 44406 | 12168 | 46.0429 | 12.94 | 120 | 33.1029 | 0 | 42 | 8.8971 | 8.8971
| Sн. MV, МVА | 40+40 | 7092 | 1440 | 7.2367 | 3.42 |  | 3.8167 | 0 | 42 | 38.1833
| Sн. LV, МVА | 40+40 | 37314 | 10728 | 38.8256 | 9.52 |  | 29.3056 | 0 | 42 | 12.6944
77 | SS-35/10kv Aleynikovo | 2,5+2,5 | 776 | 312 | 0.83637 | 0.43267 | 120 | 0.40371 | 0 | 2.625 | 2.2213 | 2.2213
78 | SS-35/10kv Alexeevka (yak.) | 2,5+2,5 | 928 | 280 | 0.96932 | 0.46639 | 120 | 0.50293 | 0 | 2.625 | 2.1221 | 2.1221
79 | SS-35/10kv Alexeevka (kor.) | 4+4 | 872 | 312 | 0.92614 | 0 |  | 0.92614 | 0 | 4.2 | 3.2739 | 3.2739
80 | SS-35/10kv Annovka | 2,5+2,5 | 1014 | 366 | 1.078 | 0.44652 | 80 | 0.63151 | 0 | 2.625 | 1.9935 | 1.9935
81 | SS-35/10kv Artelnoe | 6,3+6,3 | 3332 | 2520 | 4.1776 | 0.55 | 45 | 3.6276 | 0 | 6.615 | 2.9874 | 2.9874
82 | SS-35/10kv B.Dvory | 4+4 | 2632 | 912 | 2.7855 | 1.191 | 120 | 1.5945 | 0 | 4.2 | 2.6055 | 2.6055
83 | SS-35/10kv B.Ivanovka | 4+4 | 1136 | 448 | 1.2211 | 0.62488 | 80 | 0.59627 | 0 | 4.2 | 3.6037 | 3.6037
84 | SS-35/10kv B.Kolodez | 2,5+2,5 | 1032 | 420 | 1.1142 | 0.44779 | 45 | 0.6664 | 0 | 2.625 | 1.9586 | 1.9586
85 | SS-35/10kv B.Ples | 2,5+2,5 | 808 | 408 | 0.90517 | 0.606 | 45 | 0.29917 | 0 | 2.625 | 2.3258 | 2.3258
86 | SS-35/10kv B.Troitsa | 6,3+6,3 | 3564 | 1236 | 3.7722 | 2.83 | 45 | 0.94224 | 0 | 6.615 | 5.6728 | 5.6728
87 | SS-35/10kv Belovskoe | 4+4 | 3592 | 1632 | 3.9454 | 1.21 | 80 | 2.7354 | 0 | 4.2 | 1.4646 | 1.4646
88 | SS-35/10kv Belyanka | 2,5+4 | 1936 | 800 | 2.0948 | 1.3214 | 45 | 0.77338 | 0 | 2.625 | 1.8516 | 1.8516
89 | SS-35/10kv Bessonovka | 6,3+6,3 | 6464 | 2896 | 7.0831 | 0.918 | 120 | 6.1651 | 0 | 6.615 | 0.44991 | 0.44991
90 | SS-35/10kv B.Lubyanki | 2,5+1,6 | 1208 | 368 | 1.2628 | 0.522 | 45 | 0.74081 | 0 | 1.68 | 0.93919 | 0.93919
91 | SS-35/10kv V.Mikhailovka | 4+4 | 2544 | 1200 | 2.8128 | 1.45 | 80 | 1.3628 | 0 | 4.2 | 2.8372 | 2.8372
92 | SS-35/10kv Varvarovka | 2,5+2,5 | 1820 | 844 | 2.0062 | 1.0795 | 120 | 0.92663 | 0 | 2.625 | 1.6984 | 1.6984
93 | SS-35/10kv Vengerovka | 2,5+2,5 | 1056 | 324 | 1.1046 | 0.4 | 120 | 0.70459 | 0 | 2.625 | 1.9204 | 1.9204
94 | SS-35/10kv Verkhopenye | 2,5+4 | 1448 | 640 | 1.5831 | 1.0177 | 45 | 0.56548 | 0 | 2.625 | 2.0595 | 2.0595
95 | SS-35/10kv Viktoropol | 2,5+4 | 1328 | 456 | 1.4041 | 0.95536 | 120 | 0.44875 | 0 | 2.625 | 2.1762 | 2.1762
96 | SS-35/10kv Vislaya Dubrava | 4+4 | 2616 | 756 | 2.723 | 0.616 | 80 | 2.107 | 0 | 4.2 | 2.093 | 2.093
97 | SS-35/10kv Vladimirovka | 4+4 | 645 | 391 | 0.75426 | 0 |  | 0.75426 | 0 | 4.2 | 3.4457 | 3.4457
98 | SS-35/10kv Water storage | 4+6,3 | 2136 | 420 | 2.1769 | 0.305 | 45 | 1.8719 | 0 | 4.2 | 2.3281 | 2.3281
99 | SS-35/6kv Vostochnaya | 6,3+6,3 | 4320 | 1469 | 4.5629 | 1.43 | 120 | 3.1329 | 0 | 6.615 | 3.4821 | 3.4821
100 | SS-35/10kv Vsesvyatka | 2,5+2,5 | 1926 | 774 | 2.0757 | 0.99513 | 120 | 1.0806 | 0 | 2.625 | 1.5444 | 1.5444
101 | SS-35/10kv Glinnoe | 6,3+6,3 | 2432 | 1600 | 2.9111 | 1.4036 | 80 | 1.5075 | 0 | 6.615 | 5.1075 | 5.1075
102 | SS-35/10kv Golovchino | 2,5+2,5 | 2688 | 996 | 2.8666 | 0.617 | 45 | 2.2496 | 0 | 2.625 | 0.37541 | 0.37541
103 | SS-35/10kv Gora-Podol | 2,5+4 | 1504 | 516 | 1.5901 | 0.9085 | 45 | 0.68155 | 0 | 2.625 | 1.9434 | 1.9434
104 | SS-35/10kv Gorodishche | 4+4 | 3232 | 1600 | 3.6064 | 0 |  | 3.6064 | 0 | 4.2 | 0.59364 | 0.59364
105 | SS-35/10kv Dmitrievka | 4+4 | 1200 | 528 | 1.311 | 0.78237 | 80 | 0.52865 | 0 | 4.2 | 3.6713 | 3.6713
106 | SS-35/10kv Dorogoshch | 4+4 | 2600 | 936 | 2.7633 | 1.054 | 45 | 1.7093 | 0 | 4.2 | 2.4907 | 2.4907
107 | SS-35/10kv Dragunka | 2,5+2,5 | 912 | 352 | 0.97757 | 0.62999 | 80 | 0.34758 | 0 | 2.625 | 2.2774 | 2.2774
108 | SS-35/10kv Zhuravlevka | 2,5+4 | 1216 | 336 | 1.2616 | 0.274 | 80 | 0.98757 | 0 | 2.625 | 1.6374 | 1.6374
109 | SS-35/6kv Zhuravliki | 10+10 | 7464 | 2112 | 7.7571 | 4.051 | 120 | 3.7061 | 0 | 10.5 | 6.7939 | 6.7939
110 | SS-35/10kv Zavidovka | 2,5+2,5 | 606 | 282 | 0.6684 | 0.42 | 80 | 0.2484 | 0 | 2.625 | 2.3766 | 2.3766
111 | SS-35/6kv Zapadnaya | 10+10+10 | 6552 | 3360 | 7.3633 | 1.707 | 120 | 5.6563 | 0 | 21 | 15.3437 | 15.3437
112 | SS-35/10kv Zozuli | 6,3+6,3 | 5744 | 3088 | 6.5214 | 3.88 | 80 | 2.6414 | 0 | 6.615 | 3.9736 | 3.9736
113 | SS-35/10kv Ivitsa | 2,5+2,5 | 1192 | 392 | 1.2548 | 0.58603 | 80 | 0.66877 | 0 | 2.625 | 1.9562 | 1.9562
114 | SS-35/10kv Ilovka | 4+4 | 2872 | 904 | 3.0109 | 2.056 | 45 | 0.95491 | 0 | 4.2 | 3.2451 | 3.2451
115 | SS-35/10kv Istobnoe | 4+2,5 | 1224 | 632 | 1.3775 | 0.93935 | 120 | 0.43818 | 0 | 2.625 | 2.1868 | 2.1868
116 | SS-35/10kv Kazatskaya | 2,5+4 | 1589 | 525 | 1.6735 | 0.87141 | 45 | 0.80207 | 0 | 2.625 | 1.8229 | 1.8229
117 | SS-35/10kv Kazinka | 4+4 | 2412 | 672 | 2.5039 | 0.736 | 120 | 1.7679 | 0 | 4.2 | 2.4321 | 2.4321
118 | SS-35/10kv Kamyshevatoe | 2,5+2,5 | 1040 | 360 | 1.1005 | 0.712 | 120 | 0.38855 | 0 | 2.625 | 2.2365 | 2.2365
119 | SS-35/10kv Kirovskaya | 6,3+6,3 | 3132 | 1536 | 3.4884 | 0.7035 | 120 | 2.7849 | 0 | 6.615 | 3.8301 | 3.8301
120 | SS-35/10kv Kotovo | 2,5+2,5 | 2672 | 768 | 2.7802 | 1.648 | 20 | 1.1322 | 0 | 2.625 | 1.4928 | 1.4928
121 | SS-35/10kv Kochetovka | 2,5+4 | 858 | 294 | 0.90697 | 0.6286 | 45 | 0.27838 | 0 | 2.625 | 2.3466 | 2.3466
122 | SS-35/10kv Krasnoe | 4+2,5 | 1128 | 424 | 1.2051 | 1.1395 | 80 | 0.065535 | 0 | 2.625 | 2.5595 | 2.5595
123 | SS-35/10kv Kretovo | 4+2,5 | 1096 | 508 | 1.208 | 0.67818 | 120 | 0.52983 | 0 | 2.625 | 2.0952 | 2.0952
124 | SS-35/10kv Kurasovka | 4+4 | 2800 | 1168 | 3.0338 | 1.797 | 80 | 1.2368 | 0 | 4.2 | 2.9632 | 2.9632
125 | SS-35/6kv Lebedi | 4+5,6 | 4392 | 1469 | 4.6312 | 0.581 | 120 | 4.0502 | 0 | 4.2 | 0.14984 | 0.14984
126 | SS-35/6kv Ledovaya | 4+4 | 2578 | 1325 | 2.8986 | 1.321 | 80 | 1.5776 | 0 | 4.2 | 2.6224 | 2.6224
127 | SS-35/10kv Livenka | 4+4 | 3360 | 2364 | 4.1083 | 1.541 | 120 | 2.5673 | 0 | 4.2 | 1.6327 | 1.6327
128 | SS-35/10kv Lubyanoe | 2,5+2,5 | 828 | 336 | 0.89358 | 0.66672 | 80 | 0.22686 | 0 | 2.625 | 2.3981 | 2.3981
129 | SS-35/10kv M.Pristan | 6,3+6,3 | 6264 | 2844 | 6.8794 | 1.81 | 45 | 5.0694 | 0 | 6.615 | 1.5456 | 1.5456
130 | SS-35/10kv М.Troitsa | 2,5+2,5 | 568 | 368 | 0.67679 | 0.60716 | 80 | 0.069632 | 0 | 2.625 | 2.5554 | 2.5554
131 | SS-35/10kv Malinovka | 10+10 | 5808 | 3776 | 6.9276 | 1.357 | 120 | 5.5706 | 0 | 10.5 | 4.9294 | 4.9294
132 | SS-35/10kv Mandrovo | 2,5+2,5 | 1488 | 438 | 1.5511 | 0.65565 | 80 | 0.89548 | 0 | 2.625 | 1.7295 | 1.7295
133 | SS-35/10kv Mukhouderovka | 2,5+2,5 | 1362 | 510 | 1.4544 | 0.643 | 80 | 0.81135 | 0 | 2.625 | 1.8136 | 1.8136
134 | SS-35/10kv N.Alexandrovka | 2,5+2,5 | 1110 | 522 | 1.2266 | 0.59315 | 120 | 0.63346 | 0 | 2.625 | 1.9915 | 1.9915
135 | SS-35/10kv N.Derevnya | 6,3+6,3 | 5888 | 1920 | 6.1931 | 2.78 | 120 | 3.4131 | 0 | 6.615 | 3.2019 | 3.2019
136 | SS-35/10kv N.Tavolzhanka | 6,3+6,3 | 3360 | 912 | 3.4816 | 0.842 | 45 | 2.6396 | 0 | 6.615 | 3.9754 | 3.9754
137 | SS-35/10kv N.Ukolovo | 4+2,5 | 1608 | 764 | 1.7803 | 0.57 | 80 | 1.2103 | 0 | 2.625 | 1.4147 | 1.4147
138 | SS-35/10kv N.Khutornoe | 2,5+4 | 294 | 142 | 0.3265 | 0.19 | 80 | 0.1365 | 0 | 2.625 | 2.4885 | 2.4885
139 | SS-35/10kv Neminushchee | 4+2,5 | 1474 | 706 | 1.6344 | 0.65147 | 80 | 0.98288 | 0 | 2.625 | 1.6421 | 1.6421
140 | SS-35/10kv Nechaevka | 4+4 | 1328 | 392 | 1.3846 | 0.451 | 120 | 0.93365 | 0 | 4.2 | 3.2664 | 3.2664
141 | SS-35/10kv Nikitovka | 2,5+2,5 | 1888 | 744 | 2.0293 | 1.4354 | 80 | 0.59387 | 0 | 2.625 | 2.0311 | 2.0311
142 | SS-35/10kv Novenkoe | 4+4 | 2216 | 964 | 2.4166 | 1.7332 | 80 | 0.68339 | 0 | 4.2 | 3.5166 | 3.5166
143 | SS-35/10kv Oktyabrskaya | 6,3+6,3 | 7040 | 2384 | 7.4327 | 0.872 | 80 | 6.5607 | 0 | 6.615 | 0.054298 | 0.054298
144 | SS-35/10kv Orlik | 4+4 | 2172 | 768 | 2.3038 | 0.553 | 80 | 1.7508 | 0 | 4.2 | 2.4492 | 2.4492
145 | SS-35/10kv Podolkhi | 2,5+2,5 | 1528 | 664 | 1.666 | 1.1225 | 45 | 0.54355 | 0 | 2.625 | 2.0815 | 2.0815
146 | SS-35/10kv Popovka | 6,3+4 | 1152 | 528 | 1.2672 | 0.64636 | 80 | 0.62088 | 0 | 4.2 | 3.5791 | 3.5791
147 | SS-35/10kv Prelestnoe | 4+4 | 2268 | 780 | 2.3984 | 0 |  | 2.3984 | 0 | 4.2 | 1.8016 | 1.8016
148 | SS-35/6kv Privokzalnaya | 6,3+6,3 | 5357 | 2160 | 5.7761 | 0 |  | 5.7761 | 0 | 6.615 | 0.83892 | 0.83892
149 | SS-35/10kv Prilepy | 2,5+2,5 | 544 | 360 | 0.65233 | 0.37638 | 80 | 0.27596 | 0 | 2.625 | 2.349 | 2.349
150 | SS-35/10kv Printsevka | 2,5+2,5 | 1502 | 424 | 1.5607 | 0.352 | 120 | 1.2087 | 0 | 2.625 | 1.4163 | 1.4163
151 | SS-35/10kv Radkovka | 6,3+6,3 | 2624 | 992 | 2.8053 | 0.164 | 45 | 2.6413 | 0 | 6.615 | 3.9737 | 3.9737
152 | SS-35/10kv Razdornoe | 2,5+2,5 | 1314 | 576 | 1.4347 | 0.662 | 80 | 0.7727 | 0 | 2.625 | 1.8523 | 1.8523
153 | SS-35/10kv Repyakhovka | 2,5+2,5 | 1464 | 736 | 1.6386 | 0.88491 | 80 | 0.75368 | 0 | 2.625 | 1.8713 | 1.8713
154 | SS-35/10kv Rzhevka | 10+10 | 6576 | 3408 | 7.4066 | 2.53 | 45 | 4.8766 | 0 | 10.5 | 5.6234 | 5.6234
155 | SS-35/10kv Rovenki | 4+4 | 3240 | 1272 | 3.4807 | 1.7393 | 120 | 1.7414 | 0 | 4.2 | 2.4586 | 2.4586
156 | SS-35/10kv Rogovatoe | 2,5+2,5 | 1536 | 720 | 1.6964 | 0 |  | 1.6964 | 0 | 2.625 | 0.92862 | 0.92862
157 | SS-35/10kv Saprykino | 2,5+2,5 | 384 | 192 | 0.42933 | 0.22751 | 120 | 0.20181 | 0 | 2.625 | 2.4232 | 2.4232
158 | SS-35/6kv Severnaya | 6,3+6,3 | 6264 | 1887 | 6.5421 | 4.8049 | 120 | 1.7371 | 0 | 6.615 | 4.8779 | 4.8779
159 | SS-35/10kv Setishche | 2,5+2,5 | 1830 | 852 | 2.0186 | 1.0621 | 80 | 0.9565 | 0 | 2.625 | 1.6685 | 1.6685
160 | SS-35/10kv Slonovka | 4+4 | 2224 | 1392 | 2.6237 | 1.1306 | 120 | 1.4931 | 0 | 4.2 | 2.7069 | 2.7069
161 | SS-35/6kv St.Oskol -2 | 16+16 | 11806 | 4574 | 12.6611 | 1.21 | 80 | 11.4511 | 0 | 16.8 | 5.3489 | 5.3489
162 | SS-35/10kv Starikovo | 4+4 | 1464 | 660 | 1.6059 | 1.3453 | 45 | 0.26059 | 0 | 4.2 | 3.9394 | 3.9394
163 | SS-35/10kv Tavrovo | 10+10 | 8592 | 1296 | 8.6892 | 0.531 | 45 | 8.1582 | 0 | 10.5 | 2.3418 | 2.3418
164 | SS-35/10kv Terebrino | 2,5+2,5 | 1116 | 636 | 1.2845 | 0.44978 | 80 | 0.83472 | 0 | 2.625 | 1.7903 | 1.7903
165 | SS-35/10kv Urazovo | 6,3+6,3 | 4776 | 1524 | 5.0133 | 1.39 | 120 | 3.6233 | 0 | 6.615 | 2.9917 | 2.9917
166 | SS-35/10kv Utochka | 1,6+2,5 | 682 | 272 | 0.73424 | 0.47242 | 80 | 0.26182 | 0 | 1.68 | 1.4182 | 1.4182
167 | SS-35/6kv Fedoseevka | 4+4 | 2160 | 682 | 2.2651 | 0 |  | 2.2651 | 0 | 4.2 | 1.9349 | 1.9349
168 | SS-35/10kv Foshchevatvo | 1,6+2,5 | 980 | 408 | 1.0615 | 0.78681 | 45 | 0.27473 | 0 | 1.68 | 1.4053 | 1.4053
169 | SS-35/10kv Kholodnoe | 4+4 | 1708 | 516 | 1.7842 | 0 |  | 1.7842 | 0 | 4.2 | 2.4158 | 2.4158
170 | SS-35/6kv Chernyansky sugar plant | 7,5+6,3 | 1608 | 1128 | 1.9642 | 1.3513 | 20 | 0.61293 | 0 | 6.615 | 6.0021 | 6.0021
171 | SS-35/10kv Shatalovka | 6,3+6,3 | 1928 | 736 | 2.0637 | 0 |  | 2.0637 | 0 | 6.615 | 4.5513 | 4.5513
172 | SS-35/10kv Shakhovka | 2,5+2,5 | 1596 | 588 | 1.7009 | 0.79066 | 80 | 0.91021 | 0 | 2.625 | 1.7148 | 1.7148
173 | SS-35/10kv Shishino | 4+6,3 | 3456 | 904 | 3.5723 | 1.03 | 80 | 2.5423 | 0 | 4.2 | 1.6577 | 1.6577
174 | SS-35/10kv Yablonovo | 4+4 | 1664 | 688 | 1.8006 | 1.1284 | 80 | 0.6722 | 0 | 4.2 | 3.5278 | 3.5278
175 | SS-35/10kv Yarskoe | 2,5+2,5 | 504 | 264 | 0.56896 | 0.14648 | 80 | 0.42248 | 0 | 2.625 | 2.2025 | 2.2025
| Total: | 3186.9 |  |  | #N/A | #N/A |  | #N/A
| deficit | [10 empty] | 10.268
| proficit | [10 empty] | 878.691