## Ярославль
[13 empty] | table 1 | [13 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | open | 1 | SS 35/10 Matveevo | 1.6 | 0.027 | 0.287 | 0.779 | 1 day and night | 0.287 | 0 | 0.779 | 0.492 | 0.492 | open
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | open | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | open
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | closed | 3 | SS 35/10 Shirinye | 2.5 | 0.18 | 2.33 | 1.68 | 1 day and night | 2.33 | 0 | 1.68 | -0.65 | -0.65 | closed
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | open | 4 | SS 110/10 Pokrov | 2.5 | 0.006 | 0.276 | 1.282 | 1 day and night | 0.276 | 0 | 1.282 | 1.006 | 1.006 | open
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | open | 5 | SS 35/10 Obnora | 1.6 | 0.058 | 0.258 | 1.212 | 1 day and night | 0.258 | 0 | 1.212 | 0.954 | 0.954 | open
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | open | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 19.9994 |  |  | 19.9994 | 0 | 10.5 | -9.4994 | -9.4994 | closed
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 16.1489 |  |  | 16.1489 | 0 | 10.5 | -5.6489
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.8805 | 3.8505 |  |  | 3.8505 | 0 | 10.5 | 6.6495
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | open | 7 | SS 35/10 Ananyino | 1,6+1,6 | 0.768 | 2.078 |  |  | 2.078 | 0 | 1.68 | -0.398 | -0.398 | closed
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | open | 8 | SS 110/10/10 Bragino | 40+40 | 3.2436 | 38.1536 | 2.338 | 120 | 35.8156 | 0 | 42 | 6.1844 | 6.1844 | open
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | open | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.749 | 2.779 | 0.554 | 120 | 2.225 | 0 | 4.2 | 1.975 | 1.975 | open
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | open | 10 | SS 35/10 Vatolino | 4,0+4,0 | 2.862 | 6.282 |  |  | 6.282 | 0 | 4.2 | -2.082 | -2.082 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | open | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.1206 | 4.2406 |  |  | 4.2406 | 0 | 6.62 | 2.3794 | 2.3794 | open
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | open | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.06 | 2.03 |  |  | 2.03 | 0 | 4.2 | 2.17 | 2.17 | open
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | open | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.072 | 0.782 |  |  | 0.782 | 0 | 1.68 | 0.898 | 0.898 | open
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | open | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 2.3274 | 3.4974 |  |  | 3.4974 | 0 | 4.2 | 0.7026 | 0.7026 | open
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | open | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | open
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | open | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.192 | 2.402 | 0.139 | 120 | 2.263 | 0 | 2.63 | 0.367 | 0.367 | open
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | open | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.071 | 0.731 | 0.329 | 120 | 0.402 | 0 | 2.63 | 2.228 | 2.228 | open
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | open | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.642 | 3.252 | 0.312 | 120 | 2.94 | 0 | 4.2 | 1.26 | 1.26 | open
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | open | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 5.3839 | 8.2539 | 0.866 | 120 | 7.3879 | 0 | 4.2 | -3.1879 | -3.1879 | closed
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | open | 21 | SS 110/6 Depo | 16+16 | 3.207 | 10.277 |  |  | 10.277 | 0 | 16.8 | 6.523 | 6.523 | open
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | open | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.825 | 2.415 | 1.039 | 120 | 1.376 | 0 | 1.68 | 0.304 | 0.304 | open
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | open | 23 | SS 110/10 Druzhba | 16+16 | 0.3913 | 5.9013 | 1.932 | 120 | 3.9693 | 0 | 16.8 | 12.8307 | 12.8307 | open
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | open | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.7165 | 5.5865 | 1.386 | 120 | 4.2005 | 0 | 6.62 | 2.4195 | 2.4195 | open
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | open | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.453 | 1.683 |  |  | 1.683 | 0 | 2.63 | 0.947 | 0.947 | open
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | open | 26 | SS 35/6 Zavolzhskaya | 10+10 | 1.0857 | 10.8057 |  |  | 10.8057 | 0 | 10.5 | -0.30575 | -0.30575 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | open | 27 | SS 110/6/6 Institutskaya | 40+40 | 3.1434 | 34.9734 |  |  | 34.9734 | 0 | 42 | 7.0266 | 7.0266 | open
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | open | 28 | SS 35/10 Koza | 1,6+1,6 | 0.03 | 0.33 | 0.052 | 120 | 0.278 | 0 | 1.68 | 1.402 | 1.402 | open
29 | SS 110/35/6 Konstantinovo | 20+16 | 20 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | open | 29 | SS 110/35/6 Konstantinovo | 20+16 |  | 12.8 | 0.021 | 120 | 12.779 | 0 | 16.8 | 4.021 | 4.021 | open
| Nom. capacity MV, МVА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 16.8 | 9.33 |  |  |  | Nom. capacity MV, МVА | 20+16 |  | 9.329 |  |  | 9.329 | 0 | 16.8 | 7.471
| Nom. capacity LV, МVА | 20+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Nom. capacity LV, МVА | 20+16 | 0.381 | 3.471 | 0.021 | 120 | 3.45 | 0 | 16.8 | 13.35
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | open | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.106 | 2.586 | 0.242 | 120 | 2.344 | 0 | 2.63 | 0.286 | 0.286 | open
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | open | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.003 | 8.083 | 1.212 | 120 | 6.871 | 0 | 10.5 | 3.629 | 3.629 | open
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | open | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 5.241 | 11.091 | 2.338 | 120 | 8.753 | 0 | 6.62 | -2.133 | -2.133 | closed
33 | SS 35/10 Nekrasovo | 10+10 | 10 | 10 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 10.5 | -0.67 | -0.67 | closed | 33 | SS 35/10 Nekrasovo | 10+10 | 2.0344 | 13.2044 |  |  | 13.2044 | 0 | 10.5 | -2.7044 | -2.7044 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | open | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.07 | 0.8 | 0.398 | 120 | 0.402 | 0 | 2.63 | 2.228 | 2.228 | open
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | open | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.7506 |  |  | 22.7506 | 0 | 26.25 | 3.4994 | 3.4994 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 8.4306 |  |  | 8.4306 | 0 | 26.25 | 17.8194
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.05 | 14.32 |  |  | 14.32 | 0 | 26.25 | 11.93
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | open | 36 | SS 110/6/6 Orion | 40+40 | 0.69633 | 15.4063 |  |  | 15.4063 | 0 | 42 | 26.5937 | 26.5937 | open
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 23.9307 |  |  | 23.9307 | 0 | 21 | -2.9307 | -2.9307 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.031 |  |  | 6.031 | 0 | 21 | 14.969
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.049702 | 17.8997 |  |  | 17.8997 | 0 | 21 | 3.1003
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | open | 38 | SS 110/10 Pereval | 16+16 | 9.7739 | 18.2839 |  |  | 18.2839 | 0 | 16.8 | -1.4839 | -1.4839 | closed
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | open | 39 | SS 110/6/6 Perekop | 25+25 | 0.66746 | 10.9975 |  |  | 10.9975 | 0 | 26.25 | 15.2525 | 15.2525 | open
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | open | 40 | SS 110/6/6 Poligraf | 40+40 | 2.9648 | 36.9348 |  |  | 36.9348 | 0 | 42 | 5.0652 | 5.0652 | open
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | open | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.201 | 0.52 | 120 | 3.681 | 0 | 10.5 | 6.819 | 6.819 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 1.067 |  |  | 1.067 | 0 | 10.5 | 9.433
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.314 | 3.134 | 0.52 | 120 | 2.614 | 0 | 10.5 | 7.886
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | open | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.7173 | 3.7673 | 0.26 | 120 | 3.5073 | 0 | 2.63 | -0.8773 | -0.8773 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | open | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.01 | 0.24 | 0.052 | 120 | 0.188 | 0 | 2.63 | 2.442 | 2.442 | open
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | open | 44 | SS 110/6/6 Severnaya | 63+63 | 5.7027 | 43.6927 |  |  | 43.6927 | 0 | 66.15 | 22.4573 | 22.4573 | open
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | open | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.614 | 1.954 | 0.987 | 120 | 0.967 | 0 | 2.63 | 1.663 | 1.663 | open
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | open | 46 | SS 110/6 Tormoznaya | 16+16 | 0.33824 | 14.8462 |  |  | 14.8462 | 0 | 16.8 | 1.9538 | 1.9538 | open
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | open | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.007 | 0.347 | 0.277 | 120 | 0.07 | 0 | 2.63 | 2.56 | 2.56 | open
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | open | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.329 | 1.019 | 0.191 | 120 | 0.828 | 0 | 2.63 | 1.802 | 1.802 | open
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.313 | 7.573 |  |  | 7.573 | 0 | 6.62 | -0.953 | -0.953 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | open | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.2994 | 1.0194 |  |  | 1.0194 | 0 | 2.63 | 1.6106 | 1.6106 | open
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | open | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.903 | 2.483 | 0.346 | 120 | 2.137 | 0 | 4.2 | 2.063 | 2.063 | open
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | MVA 4: 2.92; Min 11: 2.83; Min 12: open | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8025 |  |  |  | 0 |  |  | 2.8175 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 2.13; MVA Т-2: 2.13 |  | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0125 | 0.8025 | 0.26 | 120 | 0.5425 | 0 | 3.36 | 2.8175
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | open | 54 | SS 110/10 Chayka | 25+25 | 1.1322 | 20.5123 |  |  | 20.5123 | 0 | 26.25 | 5.7378 | 5.7378 | open
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | open | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.472 | 3.042 | 0.156 | 120 | 2.886 | 0 | 2.63 | -0.256 | -0.256 | closed
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | open | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.67 | 2.1 |  |  | 2.1 | 0 | 4.2 | 2.1 | 2.1 | open
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | open | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 5.4059 | 37.3859 |  |  | 37.3859 | 0 | 42 | 4.6141 | 4.6141 | open
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | open | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.616 | 7.496 |  |  | 7.496 | 0 | 26.25 | 18.754 | 18.754 | open
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | open | 59 | ПС 110/6/6 Kotorosl | 25+25 | 1.2554 | 7.2954 |  |  | 7.2954 |  | 26.25 | 18.9546 | 18.9546 | open
60 | SS 35/6 Kelnot | 4 | 4 |  | 0.29 | 0.29 |  | 4.2 | 1 day and night | 0.29 | 0 | 4.2 | 3.91 | 3.91 | open | 60 | SS 35/6 Kelnot | 4 | 0 | 0.29 | 4.2 | 1 day and night | 0.29 |  | 4.2 | 3.91 | 3.91 | open
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | open | 61 | SS 110/10 Altynovo | 6,3+6,3 | 0.9663 | 4.2663 |  |  | 4.2663 | 0 | 6.62 | 2.3537 | 2.3537 | open
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | open | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 10.3718 |  |  | 10.3718 | 0 | 10.5 | 0.12825 | 0.12825 | open
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 4.1806 |  |  | 4.1806 | 0 | 10.5 | 6.3194
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Nom. capacity LV, МVА | 16+10 | 1.7412 | 6.1912 |  |  | 6.1912 | 0 | 10.5 | 4.3088
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | open | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.546 | 0.537 | 120 | 3.009 | 0 | 10.5 | 7.491 | 7.491 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.205 |  |  | 2.205 | 0 | 10.5 | 8.295
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.041 | 1.341 | 0.537 | 120 | 0.804 | 0 | 10.5 | 9.696
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | open | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | open
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | closed | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | closed
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | open | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.7435 |  |  | 1.7435 | 0 | 6.62 | 4.8765 | 4.8765 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 0.36; MVA Т-2: 0.36; Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.3725 |  |  | 0.3725 | 0 | 6.62 | 6.2475
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.031 | 1.371 |  |  | 1.371 | 0 | 6.62 | 5.249
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | closed | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 24.7112 | 0.97 | 120 | 23.7412 | 0 | 6.62 | -17.1212 | -17.1212 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.2147 |  |  | 11.2147 | 0 | 6.62 | -4.5947
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 10.8065 | 13.4965 | 0.97 | 120 | 12.5265 | 0 | 6.62 | -5.9065
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | open | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 33.7395 |  |  | 33.7395 | 0 | 26.25 | -7.4895 | -7.4895 | closed
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 19.1385 |  |  | 19.1385 | 0 | 26.25 | 7.1115
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | open | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.4795 | 2.2395 |  |  | 2.2395 | 0 | 2.63 | 0.3905 | 0.3905 | open
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | closed | 71 | SS 110/35/10 Rostov | 20+25 |  | 23.354 |  |  | 23.354 | 0 | 21 | -2.354 | -2.354 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 2.028 |  |  | 2.028 | 0 | 21 | 18.972
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 1.776 | 21.326 |  |  | 21.326 | 0 | 21 | -0.326
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | closed | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 12.6438 |  |  | 12.6438 | 0 | 6.62 | -6.0237 | -6.0237 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 5.8448 |  |  | 5.8448 | 0 | 6.62 | 0.77525
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 3.309 | 6.799 |  |  | 6.799 | 0 | 6.62 | -0.179
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | open | 73 | SS 110/35/10 Uglich | 25+25 |  | 27.2479 |  |  | 27.2479 | 0 | 26.25 | -0.9979 | -0.9979 | closed
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 18.7809 |  |  | 18.7809 | 0 | 26.25 | 7.4691
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.877 | 8.467 |  |  | 8.467 | 0 | 26.25 | 17.783
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | open | 74 | SS 110/10 Ustye | 10+10 | 0.285 | 4.635 | 0.797 | 120 | 3.838 | 0 | 10.5 | 6.662 | 6.662 | open
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | open | 75 | SS 110/10 Shurskol | 10+10 | 0.075 | 1.415 | 0.97 | 120 | 0.445 | 0 | 10.5 | 10.055 | 10.055 | open
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | open | 76 | SS 110/10 Yur.Sloboda | 10+10 | 0.928 | 8.098 | 0.866 | 120 | 7.232 | 0 | 10.5 | 3.268 | 3.268 | open
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.075 | 1.005 |  |  | 1.005 | 0 | 2.63 | 1.625 | 1.625 | open
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | open | 78 | SS 35/6 Batki | 1,6+1,6 | 0.316 | 1.456 |  |  | 1.456 | 0 | 1.68 | 0.224 | 0.224 | open
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | open | 79 | SS 35/10 Beregovaya | 1,6 | 0.01 | 0.19 | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | open
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | open | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.065 | 1.825 | 0.225 |  | 1.6 | 0 | 2.63 | 1.03 | 1.03 | open
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | open | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.012 | 0.512 | 0.087 | 120 | 0.425 | 0 | 1.68 | 1.255 | 1.255 | open
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | open | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.188 | 0.938 | 0.52 | 120 | 0.418 | 0 | 1.68 | 1.262 | 1.262 | open
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | open | 83 | SS 35/10 Glebovo | 2,5+2,5 | 2.73 | 4.81 |  |  | 4.81 | 0 | 2.63 | -2.18 | -2.18 | closed
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.227 | 1.157 |  |  | 1.157 | 0 | 2.63 | 1.473 | 1.473 | open
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | open | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.082 | 1.192 |  |  | 1.192 | 0 | 1.68 | 0.488 | 0.488 | open
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | open | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.093 | 1.633 |  |  | 1.633 | 0 | 1.68 | 0.047 | 0.047 | open
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | open | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0855 | 1.5755 |  |  | 1.5755 | 0 | 2.63 | 1.0545 | 1.0545 | open
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | open | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 2.502 | 4.742 |  |  | 4.742 | 0 | 6.62 | 1.878 | 1.878 | open
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | open | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | open
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | open | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.204 | 2.934 | 0.953 | 120 | 1.981 | 0 | 4.2 | 2.219 | 2.219 | open
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | open | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.358 | 1.708 |  |  | 1.708 | 0 | 2.63 | 0.922 | 0.922 | open
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | open | 92 | SS 35/6 Kupan | 2,5+2,5 | 1.0107 | 3.5907 |  |  | 3.5907 | 0 | 2.63 | -0.96074 | -0.96074 | closed
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | open | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.239 | 1.229 | 0.502 | 120 | 0.727 | 0 | 2.63 | 1.903 | 1.903 | open
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | open | 94 | SS 35/10 Nagorye | 4,0+4,0 | 1.701 | 5.191 |  |  | 5.191 | 0 | 4.2 | -0.991 | -0.991 | closed
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | open | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.166 | 2.296 | 0.087 | 120 | 2.209 | 0 | 4.2 | 1.991 | 1.991 | open
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | open | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.2165 | 1.3265 |  |  | 1.3265 | 0 | 2.63 | 1.3035 | 1.3035 | open
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | open | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.026 | 0.936 | 0.035 | 120 | 0.901 | 0 | 2.63 | 1.729 | 1.729 | open
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | open | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.077 | 1.357 |  |  | 1.357 | 0 | 2.63 | 1.273 | 1.273 | open
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | closed | 99 | SS 35/10 Saraevo | 1+1,6 | 0.81 | 2.13 |  |  | 2.13 | 0 | 1.05 | -1.08 | -1.08 | closed
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | open | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 0.987 | 2.437 | 0.953 | 120 | 1.484 | 0 | 2.63 | 1.146 | 1.146 | open
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | open | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.19 | 0.81 | 0.052 | 120 | 0.758 | 0 | 4.2 | 3.442 | 3.442 | open
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | open | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.9591 | 2.0591 |  |  | 2.0591 | 0 | 1.68 | -0.3791 | -0.3791 | closed
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | closed | 103 | SS 35/10 Solomidino | 2.5 | 0.976 | 2.176 | 0.866 | 1 day and night | 2.176 | 0 | 0.866 | -1.31 | -1.31 | closed
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | open | 104 | SS 35/10 Stavotino | 4,0+4,0 | 0.387 | 1.857 | 0.346 | 120 | 1.511 | 0 | 4.2 | 2.689 | 2.689 | open
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | open | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.034 | 0.434 | 0.052 | 120 | 0.382 | 0 | 2.63 | 2.248 | 2.248 | open
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | open | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 0.845 | 1.695 |  |  | 1.695 | 0 | 2.63 | 0.935 | 0.935 | open
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | open | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.224 | 0.604 |  |  | 0.604 | 0 | 2.63 | 2.026 | 2.026 | open
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | open | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.047 | 1.157 | 0.242 | 120 | 0.915 | 0 | 2.63 | 1.715 | 1.715 | open
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | open | 109 | SS 35/10 Neksans | 10+10 | 0 | 1.93 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | open
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | closed | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.0964 | 10.7964 |  |  | 10.7964 | 0 | 10.5 | -0.2964 | -0.2964 | closed
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | open | 111 | SS 110/10 Tishino | 25+25 | 0.173 | 18.423 |  |  | 18.423 | 0 | 26.25 | 7.827 | 7.827 | open
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | open | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.027 | 2.387 | 0.069 | 120 | 2.318 | 0 | 6.62 | 4.302 | 4.302 | open
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | open | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.16466 | 20.1947 |  |  | 20.1947 | 0 | 26.25 | 6.0553 | 6.0553 | open
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | open | 115 | SS 110/10 Optika | 10+10 | 0.301 | 5.691 | 0.26 | 120 | 5.431 | 0 | 10.5 | 5.069 | 5.069 | open
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | open | 116 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 7.82 |  |  | 7.82 | 0 | 16.8 | 8.98 | 8.98 | open
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | open | 117 | SS 110/6/6 Zapadnaya | 63+63 | 1.2415 | 29.1415 |  |  | 29.1415 | 0 | 66.15 | 37.0085 | 37.0085 | open
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | open | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.881 |  |  | 10.881 | 0 | 42 | 31.119 | 31.119 | open
| Nom. capacity MV, МVА | 40+40 |  |  | MVA 4: 0; MVA Т-1: 0; MVA Т-2: 0 |  | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.131 | 10.881 |  |  | 10.881 | 0 | 42 | 31.119
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | open | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.2125 |  |  | 15.2125 | 0 | 16.8 | 1.5875 | 1.5875 | open
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 10.2215 |  |  | 10.2215 | 0 | 16.8 | 6.5785
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.031 | 4.991 |  |  | 4.991 | 0 | 16.8 | 11.809
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open | 121 | SS 110/6 Dock yard | 10+10 | 0.144 | 5.464 |  |  | 5.464 | 0 | 10.5 | 5.036 | 5.036 | open
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | open | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.575 | 3.995 |  |  | 3.995 | 0 | 6.62 | 2.625 | 2.625 | open
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | open | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 2.449 |  |  | 2.449 | 0 | 4.2 | 1.751 | 1.751 | open
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | open | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.292 | 0.972 |  |  | 0.972 | 0 | 1.68 | 0.708 | 0.708 | open
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | open | 125 | SS 110/6 Veretye | 25+25 | 1.142 | 22.502 |  |  | 22.502 | 0 | 26.25 | 3.748 | 3.748 | open
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | open | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 1.2418 | 4.0418 | 0.554 | 120 | 3.4878 | 0 | 4.2 | 0.7122 | 0.7122 | open
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | open | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.016 | 1.216 | 0.017 | 120 | 1.199 | 0 | 2.63 | 1.431 | 1.431 | open
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | open | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.083 | 0.903 |  |  | 0.903 | 0 | 1.68 | 0.777 | 0.777 | open
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | open | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.003 | 0.593 | 0.294 | 120 | 0.299 | 0 | 1.68 | 1.381 | 1.381 | open
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | open | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | open
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | open | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.533 | 1.843 |  |  | 1.843 | 0 | 2.63 | 0.787 | 0.787 | open
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | open | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.7263 | 5.0363 |  |  | 5.0363 | 0 | 6.62 | 1.5837 | 1.5837 | open
133 | SS 35/10 Breytovo | 6,3+4,0 | 6.3 | 4 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 4.2 | -0.4 | -0.4 | closed | 133 | SS 35/10 Breytovo | 6,3+4,0 | 1.22 | 5.82 |  |  | 5.82 | 0 | 4.2 | -1.62 | -1.62 | closed
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | open | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.015 | 1.075 | 0.208 | 120 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | open
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | open | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.01 | 0.92 | 0.173 | 120 | 0.747 | 0 | 2.63 | 1.883 | 1.883 | open
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | open | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.025 | 0.985 |  |  | 0.985 | 0 | 2.63 | 1.645 | 1.645 | open
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | open | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.094 | 0.634 |  |  | 0.634 | 0 | 2.63 | 1.996 | 1.996 | open
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | open | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.119 | 1.519 | 0.364 | 120 | 1.155 | 0 | 1.68 | 0.525 | 0.525 | open
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | open | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.01 | 0.23 | 0.017 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | open
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | open | 140 | SS 35/10 Borok | 2,5+4,0 | 0.231 | 1.791 | 0.277 | 120 | 1.514 | 0 | 2.63 | 1.116 | 1.116 | open
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | open | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.582 | 4.342 |  |  | 4.342 | 0 | 6.62 | 2.278 | 2.278 | open
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open | 142 | SS 110/10 Volga | 5,6+6,3 | 0 | 2.13 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | open | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.379 | 2.469 | 0.104 | 120 | 2.365 | 0 | 2.63 | 0.265 | 0.265 | open
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | open | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 21.2339 |  |  | 21.2339 | 0 | 26.25 | 5.0161 | 5.0161 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 4.7639 |  |  | 4.7639 | 0 | 26.25 | 21.4861
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.06 | 16.47 |  |  | 16.47 | 0 | 26.25 | 9.78
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | open | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.11 | 1.212 | 120 | 6.898 | 0 | 10.5 | 3.602 | 3.602 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 0.79 |  |  | 0.79 | 0 | 10.5 | 9.71
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.07 | 7.32 | 1.212 | 120 | 6.108 | 0 | 10.5 | 4.392
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | open | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.328 | 3.178 |  |  | 3.178 | 0 | 6.62 | 3.442 | 3.442 | open
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | open | 147 | SS 110/35/10 Lom | 10+10 |  | 9.2879 | 1.368 | 120 | 7.9199 | 0 | 10.5 | 2.5801 | 2.5801 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 7.4243 |  |  | 7.4243 | 0 | 10.5 | 3.0757
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.3836 | 1.8636 | 1.368 | 120 | 0.4956 | 0 | 10.5 | 10.0044
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | open | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.095 | 0.895 |  |  | 0.895 | 0 | 1.68 | 0.785 | 0.785 | open
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | open | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 9.518 | 0.242 | 120 | 9.276 | 0 | 10.5 | 1.224 | 1.224 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 8.763 |  |  | 8.763 | 0 | 10.5 | 1.737
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.135 | 0.755 | 0.242 | 120 | 0.513 | 0 | 10.5 | 9.987
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | MVA 4: 3.21; Min 11: 1.432; Min 12: open | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.501 |  |  |  | 0 |  |  | 1.432 | open
| Nom. capacidty MV, МVА | 6.3 |  |  | MVA 4: 2.91; MVA Т-1: 2.91 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.201 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.3 | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | open | 151 | SS 35/10 Beloe | 2.5 | 0.059 | 0.769 | 1.472 | 1 day and night | 0.769 | 0 | 1.472 | 0.703 | 0.703 | open
152 | SS 110/35/10 Glebovo | 10 | 10 |  | MVA 4: 6.05; Min 11: -2.505; Min 12: closed | 152 | SS 110/35/10 Glebovo | 10 |  | 8.2199 |  |  |  | 0 |  |  | -3.935 | closed
| Nom. capacity MV, МVА | 10 |  |  | MVA 4: 2.87; MVA Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 3.6099 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.43 | 4.61 | 0.675 | 1 day and night | 4.61 | 0 | 0.675 | -3.935
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | open | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | open
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | open | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | open
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | open | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | open
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | open | 157 | SS 35/10 Ermakovo | 1.6 | 0.08 | 1.1 | 1.212 | 1 day and night | 1.1 | 0 | 1.212 | 0.112 | 0.112 | open
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | open | 158 | SS 35/10 Milyushino | 1.6 | 0.657 | 1.497 | 0.918 | 1 day and night | 1.497 | 0 | 0.918 | -0.579 | -0.579 | closed
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | closed | 159 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 day and night | 0.779 | 0 | 0.554 | -0.225 | -0.225 | closed
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | open | 160 | SS 35/10 Sit | 1.6 | 0.241 | 0.911 | 0.68 | 1 day and night | 0.911 | 0 | 0.68 | -0.231 | -0.231 | closed
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | closed | 161 | SS 35/10 Gorelovo | 1.6 | 0.451 | 1.651 | 0.901 | 1 day and night | 1.651 | 0 | 0.901 | -0.75 | -0.75 | closed
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | open | 164 | SS 35/10 Levoberezhnaya | 4 | 0.367 | 1.677 | 1.334 | 1 day and night | 1.677 |  | 1.334 | -0.343 | -0.343 | closed
| Total: | 2858.7 | 1456.3 | 1402.4 | MVA 4: 885.648 |  | Total: | 2857.9 |  | 1000.8415
| deficit |  |  |  | Min 11: -15.784 |  | deficit | [9 empty] | -82.462
| proficit |  |  |  | Min 11: 650.045 |  | proficit | [9 empty] | 545.634
Note on G194: Т2
Note on G214: Т3
Note on G216: Т3
Note on H194: Т3

## Свод тек.деф.зима
The list of closed supply centers of IDGC of Centre (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA |  |  |  | Current deficit, MVA
Yarenergo
1 | SS 35/10 Shirinye | 2.5 |  |  |  |  | -0.47
2 | SS 35/10 Nekrasovo | 10+10 |  |  |  |  | -0.67
3 | SS 110/35/6 Pavlovskaya | 20+25 |  |  |  |  | -2.56
4 | SS 35/10 Tutaev-35 | 6,3+6,3 |  |  |  |  | -0.64
5 | SS 110/6 Kinoplyonka | 6,3+10 |  |  |  |  | -3.28
6 | SS 110/35/10 Nila | 6,3+6,3 |  |  |  |  | -2.76
7 | SS 110/35/10 Rostov | 20+25 |  |  |  |  | -0.21
8 | SS 110/35/10 Technical school | 6,3+6,3 | 3.48 | 3.48 | 0 | 2.63 | -1
9 | SS 35/10 Saraevo | 1+1,6 | 11.67 | 11.67 | 0 | 10.5 | -0.27
10 | SS 35/10 Solomidino | 2.5 | 25.25 | 25.25 | 0 | 21 | -0.334
11 | SS 35/6 Pribrezhnaya | 10+10 | 45.91 | 45.91 | 0 | 42 | -0.2
12 | SS 35/10 Breytovo | 6,3+4,0 | 6.83 | 6.83 | 0 | 6.62 | -0.4
13 | SS 110/35/10 Glebovo | 10 |  |  |  |  | -2.505
14 | SS 35/10 Sutka | 2.5 |  |  |  |  | -0.186
15 | SS 35/10 Gorelovo | 1.6 |  |  |  |  | -0.299
Total current deficit (winter) | [6 empty] | -15.784

## Свод ожид.деф.зима
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
Пропускная способность Центров питания филиала ОАО "МРСК Центра" - "Ярэнерго" по итогам зимнего замера максимума нагрузки 2010 г.
таблица 1
№ п/п | Наименование объекта центра питания, класс напряжения | Текущий дефицит | [12 empty] | Примечание | №п/п | Наименование объекта центра питания, класс напряжения | [10 empty] | Note
|  | Установленная мощность трансформаторов Sуст. с указанием их количества, шт/ МВА | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Суммарная полная мощность ЦП по результатам замеров максимума нагрузки Sмах , МВА | ячейки скрыть |  | Полная мощность, перераспределяемая в соответствии с ПТЭ, МВА за время |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Дефицит/профицит ЦП, МВА |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Дополнительная мощность по выданным ТУ на ТП, МВт | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Supply Center deficit/proficit, MVA
[8 empty] | МВА | Мин. | [11 empty] | МВА | Мин.
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | ПС 35/10 Матвеево | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 сутки | 0.26 | 0 | 0.779 | 0.519 | 0.519 | открыт | 1 | ПС 35/10 Матвеево | 1.6 | 0.027 | 0.287 | 0.779 | 1 сутки | 0.287 | 0 | 0.779 | 0.492 | 0.492 | открыт
2 | ПС 35/10 Михайловское | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 сутки | 1.11 | 0 | 6.62 | 5.51 | 5.51 | открыт | 2 | ПС 35/10 Михайловское | 6.3 | 0.003 | 1.113 | 6.62 | 1 сутки | 1.113 | 0 | 6.62 | 5.507 | 5.507 | открыт
3 | ПС 35/10 Ширинье | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 сутки | 2.15 | 0 | 1.68 | -0.47 | -0.47 | закрыт | 1 | SS 35/10 Shirinye | 2.5 | 0.18 | 2.33 | 1.68 | 1 сутки | 2.33 | 0 | 1.68 | -0.65 | -0.65 | closed
4 | ПС 110/10 Покров | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 сутки | 0.27 | 0 | 1.282 | 1.012 | 1.012 | открыт | 4 | ПС 110/10 Покров | 2.5 | 0.006 | 0.276 | 1.282 | 1 сутки | 0.276 | 0 | 1.282 | 1.006 | 1.006 | открыт
5 | ПС 35/10 Обнора | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 сутки | 0.2 | 0 | 1.212 | 1.012 | 1.012 | открыт | 5 | ПС 35/10 Обнора | 1.6 | 0.058 | 0.258 | 1.212 | 1 сутки | 0.258 | 0 | 1.212 | 0.954 | 0.954 | открыт
6 | ПС 110/35/10 Аббакумцево | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | открыт | 2 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 19.9994 |  |  | 19.9994 | 0 | 10.5 | -9.4994 | -9.4994 | closed
| Ном. Мощность СН, МВА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 16.1489 |  |  | 16.1489 | 0 | 10.5 | -5.6489
| Ном. мощность НН, МВА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.8805 | 3.8505 |  |  | 3.8505 | 0 | 10.5 | 6.6495
7 | ПС 35/10 Ананьино | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | открыт | 3 | SS 35/10 Ananyino | 1,6+1,6 | 0.768 | 2.078 |  |  | 2.078 | 0 | 1.68 | -0.398 | -0.398 | closed
8 | ПС 110/10/10 Брагино | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | открыт | 8 | ПС 110/10/10 Брагино | 40+40 | 3.2436 | 38.1536 | 2.338 | 120 | 35.8156 | 0 | 42 | 6.1844 | 6.1844 | открыт
9 | ПС 35/10 Бурмакино-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | открыт | 9 | ПС 35/10 Бурмакино-1 | 4,0+4,0 | 0.749 | 2.779 | 0.554 | 120 | 2.225 | 0 | 4.2 | 1.975 | 1.975 | открыт
10 | ПС 35/10 Ватолино | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | открыт | 4 | SS 35/10 Vatolino | 4,0+4,0 | 2.862 | 6.282 |  |  | 6.282 | 0 | 4.2 | -2.082 | -2.082 | closed
11 | ПС 35/6 Ведерники | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | открыт | 11 | ПС 35/6 Ведерники | 6,3+6,3 | 0.1206 | 4.2406 |  |  | 4.2406 | 0 | 6.62 | 2.3794 | 2.3794 | открыт
12 | ПС 35/10 Великовская | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | открыт | 12 | ПС 35/10 Великовская | 4,0+4,0 | 0.06 | 2.03 |  |  | 2.03 | 0 | 4.2 | 2.17 | 2.17 | открыт
13 | ПС 35/10 Великое Село | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | открыт | 13 | ПС 35/10 Великое Село | 1,6+1,6 | 0.072 | 0.782 |  |  | 0.782 | 0 | 1.68 | 0.898 | 0.898 | открыт
14 | ПС 35/10 Возрождение | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | открыт | 14 | ПС 35/10 Возрождение | 4,0+4,0 | 2.3274 | 3.4974 |  |  | 3.4974 | 0 | 4.2 | 0.7026 | 0.7026 | открыт
15 | ПС 35/10 Волна | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | открыт | 15 | ПС 35/10 Волна | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | открыт
16 | ПС 35/10 Вятское | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | открыт | 16 | ПС 35/10 Вятское | 2,5+2,5 | 0.192 | 2.402 | 0.139 | 120 | 2.263 | 0 | 2.63 | 0.367 | 0.367 | открыт
17 | ПС 35/10 Горинская | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | открыт | 17 | ПС 35/10 Горинская | 2,5+2,5 | 0.071 | 0.731 | 0.329 | 120 | 0.402 | 0 | 2.63 | 2.228 | 2.228 | открыт
18 | ПС 35/10 Григорьевское | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | открыт | 18 | ПС 35/10 Григорьевское | 4,0+4,0 | 0.642 | 3.252 | 0.312 | 120 | 2.94 | 0 | 4.2 | 1.26 | 1.26 | открыт
19 | ПС 35/10 Гузицино | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | открыт | 5 | SS 35/10 Guzitsino | 4,0+4,0 | 5.3839 | 8.2539 | 0.866 | 120 | 7.3879 | 0 | 4.2 | -3.1879 | -3.1879 | closed
20 | ПС 35/10 ГПС Ярославль | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | открыт | 20 | ПС 35/10 ГПС Ярославль | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | открыт
21 | ПС 110/6 Депо | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | открыт | 21 | ПС 110/6 Депо | 16+16 | 3.207 | 10.277 |  |  | 10.277 | 0 | 16.8 | 6.523 | 6.523 | открыт
22 | ПС 35/10 Дорожаево | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | открыт | 22 | ПС 35/10 Дорожаево | 1,6+1,6 | 0.825 | 2.415 | 1.039 | 120 | 1.376 | 0 | 1.68 | 0.304 | 0.304 | открыт
23 | ПС 110/10 Дружба | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | открыт | 23 | ПС 110/10 Дружба | 16+16 | 0.3913 | 5.9013 | 1.932 | 120 | 3.9693 | 0 | 16.8 | 12.8307 | 12.8307 | открыт
24 | ПС 35/10 Дубки | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | открыт | 24 | ПС 35/10 Дубки | 6,3+6,3 | 0.7165 | 5.5865 | 1.386 | 120 | 4.2005 | 0 | 6.62 | 2.4195 | 2.4195 | открыт
25 | ПС 35/10 Дыбино | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | открыт | 25 | ПС 35/10 Дыбино | 2,5+2,5 | 0.453 | 1.683 |  |  | 1.683 | 0 | 2.63 | 0.947 | 0.947 | открыт
26 | ПС 35/6 Заволжская | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | открыт | 6 | SS 35/6 Zavolzhskaya | 10+10 | 1.0857 | 10.8057 |  |  | 10.8057 | 0 | 10.5 | -0.30575 | -0.30575 | closed
27 | ПС 110/6/6 Институтская | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | открыт | 27 | ПС 110/6/6 Институтская | 40+40 | 3.1434 | 34.9734 |  |  | 34.9734 | 0 | 42 | 7.0266 | 7.0266 | открыт
28 | ПС 35/10 Коза | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | открыт | 28 | ПС 35/10 Коза | 1,6+1,6 | 0.03 | 0.33 | 0.052 | 120 | 0.278 | 0 | 1.68 | 1.402 | 1.402 | открыт
29 | ПС 110/35/6 Константиново | 20+16 | 20 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | открыт | 29 | ПС 110/35/6 Константиново | 20+16 |  | 12.8 | 0.021 | 120 | 12.779 | 0 | 16.8 | 4.021 | 4.021 | открыт
| Ном. Мощность СН, МВА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 16.8 | 9.33 |  |  |  | Ном. Мощность СН, МВА | 20+16 |  | 9.329 |  |  | 9.329 | 0 | 16.8 | 7.471
| Ном. мощность НН, МВА | 20+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Ном. мощность НН, МВА | 20+16 | 0.381 | 3.471 | 0.021 | 120 | 3.45 | 0 | 16.8 | 13.35
30 | ПС 35/10 Курба | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | открыт | 30 | ПС 35/10 Курба | 2,5+2,5 | 0.106 | 2.586 | 0.242 | 120 | 2.344 | 0 | 2.63 | 0.286 | 0.286 | открыт
31 | ПС 35/10 Лесные Поляны | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | открыт | 31 | ПС 35/10 Лесные Поляны | 10+10 | 1.003 | 8.083 | 1.212 | 120 | 6.871 | 0 | 10.5 | 3.629 | 3.629 | открыт
32 | ПС 35/10 Моделово-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | открыт | 7 | SS 35/10 Modelovo-2 | 6,3+6,3 | 5.241 | 11.091 | 2.338 | 120 | 8.753 | 0 | 6.62 | -2.133 | -2.133 | closed
33 | ПС 35/10 Некрасово | 10+10 | 10 | 10 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 10.5 | -0.67 | -0.67 | закрыт | 8 | SS 35/10 Nekrasovo | 10+10 | 2.0344 | 13.2044 |  |  | 13.2044 | 0 | 10.5 | -2.7044 | -2.7044 | closed
34 | ПС 35/10 Никольское | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | открыт | 9 | ПС 35/10 Никольское | 2,5+2,5 | 0.07 | 0.8 | 0.398 | 120 | 0.402 | 0 | 2.63 | 2.228 | 2.228 | открыт
35 | ПС 110/35/6 НПЗ | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | открыт | 35 | ПС 110/35/6 НПЗ | 25+25 |  | 22.7506 |  |  | 22.7506 | 0 | 26.25 | 3.4994 | 3.4994 | открыт
| Ном. Мощность СН, МВА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Ном. Мощность СН, МВА | 25+25 |  | 8.4306 |  |  | 8.4306 | 0 | 26.25 | 17.8194
| Ном. мощность НН, МВА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Ном. мощность НН, МВА | 25+25 | 7.05 | 14.32 |  |  | 14.32 | 0 | 26.25 | 11.93
36 | ПС 110/6/6 Орион | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | открыт | 36 | ПС 110/6/6 Орион | 40+40 | 0.69633 | 15.4063 |  |  | 15.4063 | 0 | 42 | 26.5937 | 26.5937 | открыт
37 | ПС 110/35/6 Павловская | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | закрыт | 9 | SS 110/35/6 Pavlovskaya | 20+25 |  | 23.9307 |  |  | 23.9307 | 0 | 21 | -2.9307 | -2.9307 | closed
| Ном. Мощность СН, МВА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.031 |  |  | 6.031 | 0 | 21 | 14.969
| Ном. мощность НН, МВА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.049702 | 17.8997 |  |  | 17.8997 | 0 | 21 | 3.1003
38 | ПС 110/10 Перевал | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | открыт | 10 | SS 110/10 Pereval | 16+16 | 9.7739 | 18.2839 |  |  | 18.2839 | 0 | 16.8 | -1.4839 | -1.4839 | closed
39 | ПС 110/6/6 Перекоп | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | открыт | 39 | ПС 110/6/6 Перекоп | 25+25 | 0.66746 | 10.9975 |  |  | 10.9975 | 0 | 26.25 | 15.2525 | 15.2525 | открыт
40 | ПС 110/6/6 Полиграф | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | открыт | 40 | ПС 110/6/6 Полиграф | 40+40 | 2.9648 | 36.9348 |  |  | 36.9348 | 0 | 42 | 5.0652 | 5.0652 | открыт
41 | ПС 110/35/10 Пречистое | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | открыт | 41 | ПС 110/35/10 Пречистое | 10+10 |  | 4.201 | 0.52 | 120 | 3.681 | 0 | 10.5 | 6.819 | 6.819 | открыт
| Ном. Мощность СН, МВА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 1.067 |  |  | 1.067 | 0 | 10.5 | 9.433
| Ном. мощность НН, МВА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.314 | 3.134 | 0.52 | 120 | 2.614 | 0 | 10.5 | 7.886
42 | ПС 35/10 Профилакторий | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | открыт | 11 | SS 35/10 Preventorium | 2,5+2,5 | 2.7173 | 3.7673 | 0.26 | 120 | 3.5073 | 0 | 2.63 | -0.8773 | -0.8773 | closed
43 | ПС 35/10 Рождествено | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | открыт | 43 | ПС 35/10 Рождествено | 2,5+2,5 | 0.01 | 0.24 | 0.052 | 120 | 0.188 | 0 | 2.63 | 2.442 | 2.442 | открыт
44 | ПС 110/6/6 Северная | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | открыт | 44 | ПС 110/6/6 Северная | 63+63 | 5.7027 | 43.6927 |  |  | 43.6927 | 0 | 66.15 | 22.4573 | 22.4573 | открыт
45 | ПС 35/10 Середа | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | открыт | 45 | ПС 35/10 Середа | 2,5+2,5 | 0.614 | 1.954 | 0.987 | 120 | 0.967 | 0 | 2.63 | 1.663 | 1.663 | открыт
46 | ПС 110/6 Тормозная | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | открыт | 46 | ПС 110/6 Тормозная | 16+16 | 0.33824 | 14.8462 |  |  | 14.8462 | 0 | 16.8 | 1.9538 | 1.9538 | открыт
47 | ПС 110/6 ТРК | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | открыт | 47 | ПС 110/6 ТРК | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | открыт
48 | ПС 35/10 Троица | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | открыт | 48 | ПС 35/10 Троица | 2,5+2,5 | 0.007 | 0.347 | 0.277 | 120 | 0.07 | 0 | 2.63 | 2.56 | 2.56 | открыт
49 | ПС 35/10 Туношна | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | открыт | 49 | ПС 35/10 Туношна | 2,5+2,5 | 0.329 | 1.019 | 0.191 | 120 | 0.828 | 0 | 2.63 | 1.802 | 1.802 | открыт
50 | ПС 35/10 Тутаев-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | закрыт | 12 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.313 | 7.573 |  |  | 7.573 | 0 | 6.62 | -0.953 | -0.953 | closed
51 | ПС 110/10 Туфаново | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | открыт | 51 | ПС 110/10 Туфаново | 2,5+2,5 | 0.2994 | 1.0194 |  |  | 1.0194 | 0 | 2.63 | 1.6106 | 1.6106 | открыт
52 | ПС 35/10 Урожай | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | открыт | 52 | ПС 35/10 Урожай | 4,0+4,0 | 0.903 | 2.483 | 0.346 | 120 | 2.137 | 0 | 4.2 | 2.063 | 2.063 | открыт
53 | ПС 110/35/10 Халдеево | 3,2+6,3 | 3.2 | 6.3 | 4: 2.92; Мин. 11: 2.83; Мин. 12: открыт | 53 | ПС 110/35/10 Халдеево | 3,2+6,3 |  | 0.8025 |  |  |  | 0 |  |  | 2.8175 | открыт
| Ном. Мощность СН, МВА | 0+6,3 |  |  | 4: 2.13; Т-2: 2.13 |  | Ном. Мощность СН, МВА | 0+6,3
| Ном. мощность НН, МВА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Ном. мощность НН, МВА | 3.2+6.3 | 0.0125 | 0.8025 | 0.26 | 120 | 0.5425 | 0 | 3.36 | 2.8175
54 | ПС 110/10/10 Чайка | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | открыт | 54 | ПС 110/10/10 Чайка | 25+25 | 1.1322 | 20.5123 |  |  | 20.5123 | 0 | 26.25 | 5.7378 | 5.7378 | открыт
55 | ПС 35/6 Чебаково | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | открыт | 13 | SS 35/6 Chebakovo | 2,5+2,5 | 1.472 | 3.042 | 0.156 | 120 | 2.886 | 0 | 2.63 | -0.256 | -0.256 | closed
56 | ПС 35/10 Щедрино | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | открыт | 56 | ПС 35/10 Щедрино | 4,0+4,0 | 0.67 | 2.1 |  |  | 2.1 | 0 | 4.2 | 2.1 | 2.1 | открыт
57 | ПС 110/6/6 Южная | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | открыт | 57 | ПС 110/6/6 Южная | 40+40 | 5.4059 | 37.3859 |  |  | 37.3859 | 0 | 42 | 4.6141 | 4.6141 | открыт
58 | ПС 110/10/6 Ярцево | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | открыт | 58 | ПС 110/10/6 Ярцево | 25+25 | 0.616 | 7.496 |  |  | 7.496 | 0 | 26.25 | 18.754 | 18.754 | открыт
59 | ПС 110/6/6 Которосль | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | открыт | 59 | ПС 110/6/6 Которосль | 25+25 | 1.2554 | 7.2954 |  |  | 7.2954 |  | 26.25 | 18.9546 | 18.9546 | открыт
60 | ПС 35/6 Келноть | 4 | 4 |  | 0.29 | 0.29 |  | 4.2 | 1 сутки | 0.29 | 0 | 4.2 | 3.91 | 3.91 | открыт | 60 | ПС 35/6 Келноть | 4 | 0 | 0.29 | 4.2 | 1 сутки | 0.29 |  | 4.2 | 3.91 | 3.91 | открыт
61 | ПС 110/10 Алтыново | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | открыт | 61 | ПС 110/10 Алтыново | 6,3+6,3 | 0.9663 | 4.2663 |  |  | 4.2663 | 0 | 6.62 | 2.3537 | 2.3537 | открыт
62 | ПС 110/35/10 Борисоглеб | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | открыт | 62 | ПС 110/35/10 Борисоглеб | 16+10 |  | 10.3718 |  |  | 10.3718 | 0 | 10.5 | 0.12825 | 0.12825 | открыт
| Ном. Мощность СН, МВА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Ном. Мощность СН, МВА | 16+10 |  | 4.1806 |  |  | 4.1806 | 0 | 10.5 | 6.3194
| Ном. мощность НН, МВА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Ном. мощность НН, МВА | 16+10 | 1.7412 | 6.1912 |  |  | 6.1912 | 0 | 10.5 | 4.3088
63 | ПС 110/35/10 Васильково | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | открыт | 63 | ПС 110/35/10 Васильково | 10+10 |  | 3.546 | 0.537 | 120 | 3.009 | 0 | 10.5 | 7.491 | 7.491 | открыт
| Ном. Мощность СН, МВА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 2.205 |  |  | 2.205 | 0 | 10.5 | 8.295
| Ном. мощность НН, МВА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.041 | 1.341 | 0.537 | 120 | 0.804 | 0 | 10.5 | 9.696
64 | ПС 110/10 Вахрушево | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | открыт | 64 | ПС 110/10 Вахрушево | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | открыт
65 | ПС 110/6 Гаврилов Ям | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | открыт | 65 | ПС 110/6 Гаврилов Ям | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | открыт
66 | ПС 110/6 Кинопленка | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | закрыт | 14 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | closed
67 | ПС 110/35/10 Климатино | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | открыт | 67 | ПС 110/35/10 Климатино | 6,3+6,3 |  | 1.7435 |  |  | 1.7435 | 0 | 6.62 | 4.8765 | 4.8765 | открыт
| Ном. Мощность СН, МВА | 0+6,3 |  |  | 4: 0.36; Т-2: 0.36; Мин. 7: 0.36; Мин. 8: 0; Мин. 9: 6.62; Мин. 10: 6.26 |  | Ном. Мощность СН, МВА | 0+6,3 |  | 0.3725 |  |  | 0.3725 | 0 | 6.62 | 6.2475
| Ном. мощность НН, МВА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Ном. мощность НН, МВА | 6,3+6,3 | 0.031 | 1.371 |  |  | 1.371 | 0 | 6.62 | 5.249
68 | ПС 110/35/10 Нила | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | закрыт | 15 | SS 110/35/10 Nila | 6,3+6,3 |  | 24.7112 | 0.97 | 120 | 23.7412 | 0 | 6.62 | -17.1212 | -17.1212 | closed
| Ном. Мощность СН, МВА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.2147 |  |  | 11.2147 | 0 | 6.62 | -4.5947
| Ном. мощность НН, МВА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 10.8065 | 13.4965 | 0.97 | 120 | 12.5265 | 0 | 6.62 | -5.9065
69 | ПС 110/35/6 Переславль | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | открыт | 16 | SS 110/35/6 Pereslavl | 25+25 |  | 33.7395 |  |  | 33.7395 | 0 | 26.25 | -7.4895 | -7.4895 | closed
| Ном. Мощность СН, МВА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 19.1385 |  |  | 19.1385 | 0 | 26.25 | 7.1115
| Ном. мощность НН, МВА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | ПС 110/10 Плоски | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | открыт | 70 | ПС 110/10 Плоски | 2,5+2,5 | 0.4795 | 2.2395 |  |  | 2.2395 | 0 | 2.63 | 0.3905 | 0.3905 | открыт
71 | ПС 110/35/10 Ростов | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | закрыт | 17 | SS 110/35/10 Rostov | 20+25 |  | 23.354 |  |  | 23.354 | 0 | 21 | -2.354 | -2.354 | closed
| Ном. Мощность СН, МВА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 2.028 |  |  | 2.028 | 0 | 21 | 18.972
| Ном. мощность НН, МВА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 1.776 | 21.326 |  |  | 21.326 | 0 | 21 | -0.326
72 | ПС 110/35/10 Техникум | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | закрыт | 18 | SS 110/35/10 Technical school | 6,3+6,3 |  | 12.6438 |  |  | 12.6438 | 0 | 6.62 | -6.0237 | -6.0237 | closed
| Ном. Мощность СН, МВА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 5.8448 |  |  | 5.8448 | 0 | 6.62 | 0.77525
| Ном. мощность НН, МВА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 3.309 | 6.799 |  |  | 6.799 | 0 | 6.62 | -0.179
73 | ПС 110/35/10 Углич | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | открыт | 19 | SS 110/35/10 Uglich | 25+25 |  | 27.2479 |  |  | 27.2479 | 0 | 26.25 | -0.9979 | -0.9979 | closed
| Ном. Мощность СН, МВА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 18.7809 |  |  | 18.7809 | 0 | 26.25 | 7.4691
| Ном. мощность НН, МВА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.877 | 8.467 |  |  | 8.467 | 0 | 26.25 | 17.783
74 | ПС 110/10 Устье | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | открыт | 74 | ПС 110/10 Устье | 10+10 | 0.285 | 4.635 | 0.797 | 120 | 3.838 | 0 | 10.5 | 6.662 | 6.662 | открыт
75 | ПС 110/10 Шурскол | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | открыт | 75 | ПС 110/10 Шурскол | 10+10 | 0.075 | 1.415 | 0.97 | 120 | 0.445 | 0 | 10.5 | 10.055 | 10.055 | открыт
76 | ПС 110/10 Юр.Слобода | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | открыт | 76 | ПС 110/10 Юр.Слобода | 10+10 | 0.928 | 8.098 | 0.866 | 120 | 7.232 | 0 | 10.5 | 3.268 | 3.268 | открыт
77 | ПС 35/10 Алешкино | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | открыт | 77 | ПС 35/10 Алешкино | 2,5+2,5 | 0.075 | 1.005 |  |  | 1.005 | 0 | 2.63 | 1.625 | 1.625 | открыт
78 | ПС 35/6 Батьки | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | открыт | 78 | ПС 35/6 Батьки | 1,6+1,6 | 0.316 | 1.456 |  |  | 1.456 | 0 | 1.68 | 0.224 | 0.224 | открыт
79 | ПС 35/10 Береговая | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 сутки | 0.18 | 0 | 3.031 | 2.851 | 2.851 | открыт | 79 | ПС 35/10 Береговая | 1,6 | 0.01 | 0.19 | 3.031 | 1 сутки | 0.19 | 0 | 3.031 | 2.841 | 2.841 | открыт
80 | ПС 35/10 Берендеево | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | открыт | 80 | ПС 35/10 Берендеево | 2,5+2,5 | 0.065 | 1.825 | 0.225 |  | 1.6 | 0 | 2.63 | 1.03 | 1.03 | открыт
81 | ПС 35/10 Воржа | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | открыт | 81 | ПС 35/10 Воржа | 1,8+1,6 | 0.012 | 0.512 | 0.087 | 120 | 0.425 | 0 | 1.68 | 1.255 | 1.255 | открыт
82 | ПС 35/10 Вощажниково | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | открыт | 82 | ПС 35/10 Вощажниково | 1,6+2,5 | 0.188 | 0.938 | 0.52 | 120 | 0.418 | 0 | 1.68 | 1.262 | 1.262 | открыт
83 | ПС 35/10 Глебово | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | открыт | 20 | SS 35/10 Glebovo | 2,5+2,5 | 2.73 | 4.81 |  |  | 4.81 | 0 | 2.63 | -2.18 | -2.18 | closed
84 | ПС 35/10 Горки | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | открыт | 84 | ПС 35/10 Горки | 2,5+2,5 | 0.227 | 1.157 |  |  | 1.157 | 0 | 2.63 | 1.473 | 1.473 | открыт
85 | ПС 35/10 Дмитрианово | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | открыт | 85 | ПС 35/10 Дмитрианово | 1,6+1,6 | 0.082 | 1.192 |  |  | 1.192 | 0 | 1.68 | 0.488 | 0.488 | открыт
86 | ПС 35/10 Заозерье | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | открыт | 86 | ПС 35/10 Заозерье | 2,5+1,6 | 0.093 | 1.633 |  |  | 1.633 | 0 | 1.68 | 0.047 | 0.047 | открыт
87 | ПС 35/10 Ильинское | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | открыт | 87 | ПС 35/10 Ильинское | 2,5+2,5 | 0.0855 | 1.5755 |  |  | 1.5755 | 0 | 2.63 | 1.0545 | 1.0545 | открыт
88 | ПС 35/10 Кибернетик | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | открыт | 88 | ПС 35/10 Кибернетик | 6,3+6,3 | 2.502 | 4.742 |  |  | 4.742 | 0 | 6.62 | 1.878 | 1.878 | открыт
89 | ПС 35/10 Клементьево | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 сутки | 0.32 | 0 | 0.485 | 0.165 | 0.165 | открыт | 89 | ПС 35/10 Клементьево | 1,6 | 0.016 | 0.336 | 0.485 | 1 сутки | 0.336 | 0 | 0.485 | 0.149 | 0.149 | открыт
90 | ПС 35/10 Красное | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | открыт | 90 | ПС 35/10 Красное | 4,0+4,0 | 1.204 | 2.934 | 0.953 | 120 | 1.981 | 0 | 4.2 | 2.219 | 2.219 | открыт
91 | ПС 35/10 Кулаково | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | открыт | 91 | ПС 35/10 Кулаково | 2,5+2,5 | 0.358 | 1.708 |  |  | 1.708 | 0 | 2.63 | 0.922 | 0.922 | открыт
92 | ПС 35/6 Купань | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | открыт | 21 | SS 35/6 Kupan | 2,5+2,5 | 1.0107 | 3.5907 |  |  | 3.5907 | 0 | 2.63 | -0.96074 | -0.96074 | closed
93 | ПС 35/10 Марково | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | открыт | 93 | ПС 35/10 Марково | 2,5+2,5 | 0.239 | 1.229 | 0.502 | 120 | 0.727 | 0 | 2.63 | 1.903 | 1.903 | открыт
94 | ПС 35/10 Нагорье | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | открыт | 22 | SS 35/10 Nagorye | 4,0+4,0 | 1.701 | 5.191 |  |  | 5.191 | 0 | 4.2 | -0.991 | -0.991 | closed
95 | ПС 35/10 Поречье | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | открыт | 95 | ПС 35/10 Поречье | 4,0+4,0 | 0.166 | 2.296 | 0.087 | 120 | 2.209 | 0 | 4.2 | 1.991 | 1.991 | открыт
96 | ПС 35/10 Пружинино | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | открыт | 96 | ПС 35/10 Пружинино | 2,5+2,5 | 0.2165 | 1.3265 |  |  | 1.3265 | 0 | 2.63 | 1.3035 | 1.3035 | открыт
97 | ПС 35/10 Раменье | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | открыт | 97 | ПС 35/10 Раменье | 2,5+2,5 | 0.026 | 0.936 | 0.035 | 120 | 0.901 | 0 | 2.63 | 1.729 | 1.729 | открыт
98 | ПС 35/10 Рязанцево | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | открыт | 98 | ПС 35/10 Рязанцево | 2,5+2,5 | 0.077 | 1.357 |  |  | 1.357 | 0 | 2.63 | 1.273 | 1.273 | открыт
99 | ПС 35/10 Сараево | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | закрыт | 23 | SS 35/10 Saraevo | 1+1,6 | 0.81 | 2.13 |  |  | 2.13 | 0 | 1.05 | -1.08 | -1.08 | closed
100 | ПС 35/10 Селифонтово | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | открыт | 100 | ПС 35/10 Селифонтово | 2,5+2,5 | 0.987 | 2.437 | 0.953 | 120 | 1.484 | 0 | 2.63 | 1.146 | 1.146 | открыт
101 | ПС 35/10 Семибратово | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | открыт | 101 | ПС 35/10 Семибратово | 4,0+4,0 | 0.19 | 0.81 | 0.052 | 120 | 0.758 | 0 | 4.2 | 3.442 | 3.442 | открыт
102 | ПС 35/10 Скоморохово | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | открыт | 24 | ПС 35/10 Скоморохово | 1,6+1,6 | 0.9591 | 2.0591 |  |  | 2.0591 | 0 | 1.68 | -0.3791 | -0.3791 | closed
103 | ПС 35/10 Соломидино | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 сутки | 1.2 | 0 | 0.866 | -0.334 | -0.334 | закрыт | 25 | SS 35/10 Solomidino | 2.5 | 0.976 | 2.176 | 0.866 | 1 сутки | 2.176 | 0 | 0.866 | -1.31 | -1.31 | closed
104 | ПС 35/10 Ставотино | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | открыт | 104 | ПС 35/10 Ставотино | 4,0+4,0 | 0.387 | 1.857 | 0.346 | 120 | 1.511 | 0 | 4.2 | 2.689 | 2.689 | открыт
105 | ПС 35/10 Урусово | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | открыт | 105 | ПС 35/10 Урусово | 2,5+2,5 | 0.034 | 0.434 | 0.052 | 120 | 0.382 | 0 | 2.63 | 2.248 | 2.248 | открыт
106 | ПС 35/10 Филимоново | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | открыт | 106 | ПС 35/10 Филимоново | 2,5+2,5 | 0.845 | 1.695 |  |  | 1.695 | 0 | 2.63 | 0.935 | 0.935 | открыт
107 | ПС 35/10 Чопорово | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | открыт | 107 | ПС 35/10 Чопорово | 2,5+2,5 | 0.224 | 0.604 |  |  | 0.604 | 0 | 2.63 | 2.026 | 2.026 | открыт
108 | ПС 35/10 Щурово | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | открыт | 108 | ПС 35/10 Щурово | 2,5+2,5 | 0.047 | 1.157 | 0.242 | 120 | 0.915 | 0 | 2.63 | 1.715 | 1.715 | открыт
109 | ПС 35/10 Нексанс | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | открыт | 109 | ПС 35/10 Нексанс | 10+10 | 0 | 1.93 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | открыт
110 | ПС 35/6 Прибрежная | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | закрыт | 26 | SS 35/6 Pribrezhnaya | 10+10 | 0.0964 | 10.7964 |  |  | 10.7964 | 0 | 10.5 | -0.2964 | -0.2964 | closed
111 | ПС 110/10 Тишино | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | открыт | 111 | ПС 110/10 Тишино | 25+25 | 0.173 | 18.423 |  |  | 18.423 | 0 | 26.25 | 7.827 | 7.827 | открыт
112 | ПС 110/10 Продуктопровод | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | открыт | 112 | ПС 110/10 Продуктопровод | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | открыт
113 | ПС 110/10 Некоуз | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | открыт | 113 | ПС 110/10 Некоуз | 6,3+6,3 | 0.027 | 2.387 | 0.069 | 120 | 2.318 | 0 | 6.62 | 4.302 | 4.302 | открыт
114 | ПС 110/6 Южная | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | открыт | 114 | ПС 110/6 Южная | 25+25 | 0.16466 | 20.1947 |  |  | 20.1947 | 0 | 26.25 | 6.0553 | 6.0553 | открыт
115 | ПС 110/10 Оптика | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | открыт | 115 | ПС 110/10 Оптика | 10+10 | 0.301 | 5.691 | 0.26 | 120 | 5.431 | 0 | 10.5 | 5.069 | 5.069 | открыт
116 | ПС 110/6 Полиграфмаш | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | открыт | 116 | ПС 110/6 Полиграфмаш | 16+16 | 0.06 | 7.82 |  |  | 7.82 | 0 | 16.8 | 8.98 | 8.98 | открыт
117 | ПС 110/6/6 Западная | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | открыт | 117 | ПС 110/6/6 Западная | 63+63 | 1.2415 | 29.1415 |  |  | 29.1415 | 0 | 66.15 | 37.0085 | 37.0085 | открыт
118 | ПС 110/35/6 Волжская | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | открыт | 118 | ПС 110/35/6 Волжская | 40+40 |  | 10.881 |  |  | 10.881 | 0 | 42 | 31.119 | 31.119 | открыт
| Ном. Мощность СН, МВА | 40+40 |  |  | 4: 0; Т-1: 0; Т-2: 0 |  | Ном. Мощность СН, МВА | 40+40
| Ном. мощность НН, МВА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Ном. мощность НН, МВА | 40+40 | 0.131 | 10.881 |  |  | 10.881 | 0 | 42 | 31.119
119 | ПС 110/35/6 Левобережная | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | открыт | 119 | ПС 110/35/6 Левобережная | 16+16 |  | 15.2125 |  |  | 15.2125 | 0 | 16.8 | 1.5875 | 1.5875 | открыт
| Ном. Мощность СН, МВА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Ном. Мощность СН, МВА | 16+16 |  | 10.2215 |  |  | 10.2215 | 0 | 16.8 | 6.5785
| Ном. мощность НН, МВА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Ном. мощность НН, МВА | 16+16 | 0.031 | 4.991 |  |  | 4.991 | 0 | 16.8 | 11.809
120 | ПС 110/35/10 Пищалкино | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | открыт | 120 | ПС 110/35/10 Пищалкино | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | открыт
| Ном. Мощность СН, МВА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Ном. Мощность СН, МВА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Ном. мощность НН, МВА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Ном. мощность НН, МВА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | ПС 110/6 Судоверфь | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | открыт | 121 | ПС 110/6 Судоверфь | 10+10 | 0.144 | 5.464 |  |  | 5.464 | 0 | 10.5 | 5.036 | 5.036 | открыт
122 | ПС 110/6 Селехово | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | открыт | 122 | ПС 110/6 Селехово | 6,3+6,3 | 0.575 | 3.995 |  |  | 3.995 | 0 | 6.62 | 2.625 | 2.625 | открыт
123 | ПС 35/6 Каменники | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | открыт | 123 | ПС 35/6 Каменники | 4,0+4,0 | 0.149 | 2.449 |  |  | 2.449 | 0 | 4.2 | 1.751 | 1.751 | открыт
124 | ПС 35/10 Шашково | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | открыт | 124 | ПС 35/10 Шашково | 1,6+1,6 | 0.292 | 0.972 |  |  | 0.972 | 0 | 1.68 | 0.708 | 0.708 | открыт
125 | ПС 110/6 Веретье | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | открыт | 125 | ПС 110/6 Веретье | 25+25 | 1.142 | 22.502 |  |  | 22.502 | 0 | 26.25 | 3.748 | 3.748 | открыт
126 | ПС 35/10 Николо-Корма | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | открыт | 126 | ПС 35/10 Николо-Корма | 4,0+4,0 | 1.2418 | 4.0418 | 0.554 | 120 | 3.4878 | 0 | 4.2 | 0.7122 | 0.7122 | открыт
127 | ПС 35/10 Арефино | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | открыт | 127 | ПС 35/10 Арефино | 2,5+2,5 | 0.016 | 1.216 | 0.017 | 120 | 1.199 | 0 | 2.63 | 1.431 | 1.431 | открыт
128 | ПС 35/10 Князево | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | открыт | 128 | ПС 35/10 Князево | 1,6+2,5 | 0.083 | 0.903 |  |  | 0.903 | 0 | 1.68 | 0.777 | 0.777 | открыт
129 | ПС 35/10 Покров | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | открыт | 129 | ПС 35/10 Покров | 1,6+1,6 | 0.003 | 0.593 | 0.294 | 120 | 0.299 | 0 | 1.68 | 1.381 | 1.381 | открыт
130 | ПС 35/10 Аниково | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | открыт | 130 | ПС 35/10 Аниково | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | открыт
131 | ПС 35/10 Новое село | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | открыт | 131 | ПС 35/10 Новое село | 2,5+2,5 | 0.533 | 1.843 |  |  | 1.843 | 0 | 2.63 | 0.787 | 0.787 | открыт
132 | ПС 35/10 Большое село | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | открыт | 132 | ПС 35/10 Большое село | 6,3+6,3 | 0.7263 | 5.0363 |  |  | 5.0363 | 0 | 6.62 | 1.5837 | 1.5837 | открыт
133 | ПС 35/10 Брейтово | 6,3+4,0 | 6.3 | 4 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 4.2 | -0.4 | -0.4 | закрыт | 27 | SS 35/10 Breytovo | 6,3+4,0 | 1.22 | 5.82 |  |  | 5.82 | 0 | 4.2 | -1.62 | -1.62 | closed
134 | ПС 35/10 Станилово | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | открыт | 134 | ПС 35/10 Станилово | 1,6+1,6 | 0.015 | 1.075 | 0.208 | 120 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | открыт
135 | ПС 35/10 Знамово | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | открыт | 135 | ПС 35/10 Знамово | 2,5+2,5 | 0.01 | 0.92 | 0.173 | 120 | 0.747 | 0 | 2.63 | 1.883 | 1.883 | открыт
136 | ПС 35/10 Рождественно | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | открыт | 136 | ПС 35/10 Рождественно | 2,5+2,5 | 0.025 | 0.985 |  |  | 0.985 | 0 | 2.63 | 1.645 | 1.645 | открыт
137 | ПС 35/10 Заполье | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | открыт | 137 | ПС 35/10 Заполье | 2,5+2,5 | 0.094 | 0.634 |  |  | 0.634 | 0 | 2.63 | 1.996 | 1.996 | открыт
138 | ПС 35/10 Тихменево | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | открыт | 138 | ПС 35/10 Тихменево | 1,6+1,6 | 0.119 | 1.519 | 0.364 | 120 | 1.155 | 0 | 1.68 | 0.525 | 0.525 | открыт
139 | ПС 35/10 Лацкое | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | открыт | 139 | ПС 35/10 Лацкое | 1,6+2,5 | 0.01 | 0.23 | 0.017 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | открыт
140 | ПС 35/10 Борок | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | открыт | 140 | ПС 35/10 Борок | 2,5+4,0 | 0.231 | 1.791 | 0.277 | 120 | 1.514 | 0 | 2.63 | 1.116 | 1.116 | открыт
141 | ПС 35/10 Мышкин | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | открыт | 141 | ПС 35/10 Мышкин | 6,3+6,3 | 0.582 | 4.342 |  |  | 4.342 | 0 | 6.62 | 2.278 | 2.278 | открыт
142 | ПС 110/10 Волга | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | открыт | 142 | ПС 110/10 Волга | 5,6+6,3 | 0 | 2.13 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | открыт
143 | ПС 35/10 Красная горка | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | открыт | 143 | ПС 35/10 Красная горка | 4,0+2,5 | 0.379 | 2.469 | 0.104 | 120 | 2.365 | 0 | 2.63 | 0.265 | 0.265 | открыт
144 | ПС 110/35/6 Восточная | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | открыт | 144 | ПС 110/35/6 Восточная | 25+25 |  | 21.2339 |  |  | 21.2339 | 0 | 26.25 | 5.0161 | 5.0161 | открыт
| Ном. Мощность СН, МВА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Ном. Мощность СН, МВА | 25+25 |  | 4.7639 |  |  | 4.7639 | 0 | 26.25 | 21.4861
| Ном. мощность НН, МВА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Ном. мощность НН, МВА | 25+25 | 0.06 | 16.47 |  |  | 16.47 | 0 | 26.25 | 9.78
145 | ПС 110/35/10 Залесье | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | открыт | 145 | ПС 110/35/10 Залесье | 10+10 |  | 8.11 | 1.212 | 120 | 6.898 | 0 | 10.5 | 3.602 | 3.602 | открыт
| Ном. Мощность СН, МВА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 0.79 |  |  | 0.79 | 0 | 10.5 | 9.71
| Ном. мощность НН, МВА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.07 | 7.32 | 1.212 | 120 | 6.108 | 0 | 10.5 | 4.392
146 | ПС 110/10 Луговая | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | открыт | 146 | ПС 110/10 Луговая | 6,3+6,3 | 0.328 | 3.178 |  |  | 3.178 | 0 | 6.62 | 3.442 | 3.442 | открыт
147 | ПС 110/35/10 Лом | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | открыт | 147 | ПС 110/35/10 Лом | 10+10 |  | 9.2879 | 1.368 | 120 | 7.9199 | 0 | 10.5 | 2.5801 | 2.5801 | открыт
| Ном. Мощность СН, МВА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 7.4243 |  |  | 7.4243 | 0 | 10.5 | 3.0757
| Ном. мощность НН, МВА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.3836 | 1.8636 | 1.368 | 120 | 0.4956 | 0 | 10.5 | 10.0044
148 | ПС 35/10 Варегово | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | открыт | 148 | ПС 35/10 Варегово | 1,6+2,5 | 0.095 | 0.895 |  |  | 0.895 | 0 | 1.68 | 0.785 | 0.785 | открыт
149 | ПС 110/35/10 Шестихино | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | открыт | 149 | ПС 110/35/10 Шестихино | 10+10 |  | 9.518 | 0.242 | 120 | 9.276 | 0 | 10.5 | 1.224 | 1.224 | открыт
| Ном. Мощность СН, МВА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Ном. Мощность СН, МВА | 10+10 |  | 8.763 |  |  | 8.763 | 0 | 10.5 | 1.737
| Ном. мощность НН, МВА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Ном. мощность НН, МВА | 10+10 | 0.135 | 0.755 | 0.242 | 120 | 0.513 | 0 | 10.5 | 9.987
150 | ПС 110/35/10 Крюково | 6.3 | 6.3 |  | 4: 3.21; Мин. 11: 1.432; Мин. 12: открыт | 150 | ПС 110/35/10 Крюково | 6.3 |  | 3.501 |  |  |  | 0 |  |  | 1.432 | открыт
| Ном. Мощность СН, МВА | 6.3 |  |  | 4: 2.91; Т-1: 2.91 |  | Ном. Мощность СН, МВА | 6.3 |  | 3.201 |  |  |  | 0
| Ном. мощность НН, МВА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 сутки | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Ном. мощность НН, МВА | 6.3 | 0 | 0.3 | 1.732 | 1 сутки | 0.3 | 0 | 1.732 | 1.432
151 | ПС 35/10 Белое | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 сутки | 0.71 | 0 | 1.472 | 0.762 | 0.762 | открыт | 151 | ПС 35/10 Белое | 2.5 | 0.059 | 0.769 | 1.472 | 1 сутки | 0.769 | 0 | 1.472 | 0.703 | 0.703 | открыт
152 | ПС 110/35/10 Глебово | 10 | 10 |  | 4: 6.05; Мин. 11: -2.505; Мин. 12: закрыт | 28 | SS 110/35/10 Glebovo | 10 |  | 8.2199 |  |  |  | 0 |  |  | -3.935 | closed
| Ном. Мощность СН, МВА | 10 |  |  | 4: 2.87; Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 3.6099 |  |  |  | 0
| Ном. мощность НН, МВА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 сутки | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.43 | 4.61 | 0.675 | 1 сутки | 4.61 | 0 | 0.675 | -3.935
153 | ПС 35/6 Песочное | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | открыт | 153 | ПС 35/6 Песочное | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | открыт
154 | ПС 35/10 Демино | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | открыт | 154 | ПС 35/10 Демино | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | открыт
155 | ПС 110/6 КС-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | открыт | 155 | ПС 110/6 КС-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | открыт
156 | ПС 35/6 Макеиха | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 сутки | 0.31 | 0 | 1.68 | 1.37 | 1.37 | открыт | 156 | ПС 35/6 Макеиха | 1.6 | 0 | 0.31 | 1.68 | 1 сутки | 0.31 |  | 1.68 | 1.37 | 1.37 | открыт
157 | ПС 35/10 Ермаково | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 сутки | 1.02 | 0 | 1.212 | 0.192 | 0.192 | открыт | 157 | ПС 35/10 Ермаково | 1.6 | 0.08 | 1.1 | 1.212 | 1 сутки | 1.1 | 0 | 1.212 | 0.112 | 0.112 | открыт
158 | ПС 35/10 Милюшино | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 сутки | 0.84 | 0 | 0.918 | 0.078 | 0.078 | открыт | 29 | SS 35/10 Milyushino | 1.6 | 0.657 | 1.497 | 0.918 | 1 сутки | 1.497 | 0 | 0.918 | -0.579 | -0.579 | closed
159 | ПС 35/10 Сутка | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 сутки | 0.74 | 0 | 0.554 | -0.186 | -0.186 | закрыт | 30 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 сутки | 0.779 | 0 | 0.554 | -0.225 | -0.225 | closed
160 | ПС 35/10 Сить | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 сутки | 0.67 | 0 | 0.68 | 0.01 | 0.01 | открыт | 31 | ПС 35/10 Сить | 1.6 | 0.241 | 0.911 | 0.68 | 1 сутки | 0.911 | 0 | 0.68 | -0.231 | -0.231 | closed
161 | ПС 35/10 Горелово | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 сутки | 1.2 | 0 | 0.901 | -0.299 | -0.299 | закрыт | 32 | SS 35/10 Gorelovo | 1.6 | 0.451 | 1.651 | 0.901 | 1 сутки | 1.651 | 0 | 0.901 | -0.75 | -0.75 | closed
162 | ПС 35/6 Пищалкино | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 сутки | 0.74 | 0 | 1.68 | 0.94 | 0.94 | открыт | 162 | ПС 35/6 Пищалкино | 1.6 | 0 | 0.74 | 1.68 | 1 сутки | 0.74 | 0 | 1.68 | 0.94 | 0.94 | открыт
163 | ПС 35/6 Варегово | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 сутки | 0.02 | 0 | 1.68 | 1.66 | 1.66 | открыт | 163 | ПС 35/6 Варегово | 1.6 | 0 | 0.02 | 1.68 | 1 сутки | 0.02 | 0 | 1.68 | 1.66 | 1.66 | открыт
164 | ПС 35/10 Левобережная | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 сутки | 1.31 | 0 | 1.334 | 0.024 | 0.024 | открыт | 33 | SS 35/10 Levoberezhnaya | 4 | 0.367 | 1.677 | 1.334 | 1 сутки | 1.677 |  | 1.334 | -0.343 | -0.343 | closed
| Итого: | 2858.7 | 1456.3 | 1402.4 | 4: 885.648 |  | Итого: | 2857.9 |  | 1000.8415
| дефицит |  |  |  | Мин. 11: -15.784 |  | дефицит | [9 empty] | -75.594
| профицит |  |  |  | Мин. 11: 650.045 |  | профицит | [9 empty] | 545.634
[17 empty] | Total: | [6 empty] | 0 |  |  | -82.462
Е.В. Турапин
Note on G195: Т2
Note on G215: Т3
Note on G217: Т3
Note on H195: Т3