## Костромаэнерго
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Sandogora 35/6 kV | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | open | 1 | Sandogora 35/6 kV | 1 | 0.066 | 0.536 | 0.55 | 120 | -0.014 | 0 | 0.55 | 0.014 | 0.014 | open
2 | Gridino 35/10 kV | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | open | 2 | Gridino 35/10 kV | 1.8 | 0.445 | 1.175 | 1.2 | 120 | -0.025 | 0 | 1.2 | 0.025 | 0.025 | open
3 | Novinki 35/10 kV | 1.8 | 0.15 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.29 | 1.29 | open | 3 | Novinki 35/10 kV | 1.8 | 0.329 | 0.479 | 1.44 | 120 | -0.961 | 0 | 1.44 | 0.961 | 0.961 | open
4 | Priskokovo 35/10kV | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | open | 4 | Priskokovo 35/10kV | 2.5 | 0.155 | 1.655 | 1.5 | 120 | 0.155 | 0 | 1.5 | -0.155 | -0.155 | closed
5 | Grigortsevo 110/10 kV | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | open | 5 | Grigortsevo 110/10 kV | 2.5 | 0 | 0.25 | 1.5 | 120 | -1.25 | 0 | 1.5 | 1.25 | 1.25 | open
6 | Klementyevo 110/10 kV | 6.3 | 0.47 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.23 | 3.23 | open | 6 | Klementyevo 110/10 kV | 6.3 | 0.061 | 0.531 | 3.7 | 120 | -3.169 | 0 | 3.7 | 3.169 | 3.169 | open
7 | Rudino 35/10 kV | 2.5 | 0.27 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.23 | 1.23 | open | 7 | Rudino 35/10 kV | 2.5 | 0.027 | 0.297 | 1.5 | 120 | -1.203 | 0 | 1.5 | 1.203 | 1.203 | open
8 | Stoyankovo 35/10 kV | 1.6 | 0.14 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.58 | 0.58 | open | 8 | Stoyankovo 35/10 kV | 1.6 | 0.075 | 0.215 | 0.72 | 120 | -0.505 | 0 | 0.72 | 0.505 | 0.505 | open
9 | Adishchevo 35/10 kV | 4 | 1.39 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.21 | 1.21 | open | 9 | Adishchevo 35/10 kV | 4 | 0.023 | 1.413 | 2.6 | 120 | -1.187 | 0 | 2.6 | 1.187 | 1.187 | open
10 | Stolbovo 110/10 kV | 10 | 0.27 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.33 | 4.33 | open | 10 | Stolbovo 110/10 kV | 10 | 0.011 | 0.281 | 4.6 | 120 | -4.319 | 0 | 4.6 | 4.319 | 4.319 | open
11 | Raslovo 35/10 kV | 2.5 | 0.62 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.76 | 0.76 | open | 11 | Raslovo 35/10 kV | 2.5 | 0.316 | 0.936 | 1.38 | 120 | -0.444 | 0 | 1.38 | 0.444 | 0.444 | open
12 | Andreevskoe 35/10 kV | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | open | 12 | Andreevskoe 35/10 kV | 1.6 | 0.03 | 0.21 | 0.93 | 120 | -0.72 | 0 | 0.93 | 0.72 | 0.72 | open
13 | Popadyino 35/10 kV | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | open | 13 | Popadyino 35/10 kV | 1.6 | 0.124 | 0.344 | 0.88 | 120 | -0.536 | 0 | 0.88 | 0.536 | 0.536 | open
14 | Elegino 110/10 kV | 2.5 | 0.21 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.77 | 0.77 | open | 14 | Elegino 110/10 kV | 2.5 | 0.234 | 0.444 | 0.98 | 120 | -0.536 | 0 | 0.98 | 0.536 | 0.536 | open
15 | Krenyovo 35/10 kV | 2.5 | 0.47 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.03 | 2.03 | open | 15 | Krenyovo 35/10 kV | 2.5 | 0.059 | 0.529 | 2.5 | 1 day and night | -1.971 | 0 | 2.5 | 1.971 | 1.971 | open
16 | Semyonovskoe 35/10 kV | 1.6 | 0.2 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.4 | 1.4 | open | 16 | Semyonovskoe 35/10 kV | 1.6 | 0.03 | 0.23 | 1.6 | 1 day and night | -1.37 | 0 | 1.6 | 1.37 | 1.37 | open
17 | Khimik 35/10 kV | 3.2 | 0.19 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.25 | 1.25 | open | 17 | Khimik 35/10 kV | 3.2 | 0 | 0.19 | 1.44 | 120 | -1.25 | 0 | 1.44 | 1.25 | 1.25 | open
18 | N. Beryozovets 35/10 kV | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | open | 18 | N. Beryozovets 35/10 kV | 2.5 | 0.039 | 0.369 | 0.43 | 120 | -0.061 | 0 | 0.43 | 0.061 | 0.061 | open
19 | Stepanovo 35/10 kV | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | open | 19 | Stepanovo 35/10 kV | 4 | 0.121 | 0.441 | 2.32 | 120 | -1.879 | 0 | 2.32 | 1.879 | 1.879 | open
20 | Gorbachevo 35/10 kV | 1 | 0.15 | 1.7 | 120 | 1.7 | 0 | 1.7 | 1.55 | 1.55 | open | 20 | Gorbachevo 35/10 kV | 1 | 0 | 0.15 | 1.7 | 120 | -1.55 | 0 | 1.7 | 1.55 | 1.55 | open
21 | Kalinino 35/10 kV | 1 | 0.13 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.43 | 0.43 | open | 21 | Kalinino 35/10 kV | 1 | 0.017 | 0.147 | 0.56 | 120 | -0.413 | 0 | 0.56 | 0.413 | 0.413 | open
22 | Kuzemino 35/10 kV | 1.6 | 0.28 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.32 | 1.32 | open | 22 | Kuzemino 35/10 kV | 1.6 | 0 | 0.28 | 1.6 | 1 day and night | -1.32 | 0 | 1.6 | 1.32 | 1.32 | open
23 | Sovega 35/10 kV | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | open | 23 | Sovega 35/10 kV | 1 | 0 | 0.09 | 0.65 | 120 | -0.56 | 0 | 0.65 | 0.56 | 0.56 | open
24 | Lukovtsino 110/10 kV | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | open | 24 | Lukovtsino 110/10 kV | 2.5 | 0.006 | 0.196 | 1.38 | 120 | -1.184 | 0 | 1.38 | 1.184 | 1.184 | open
25 | Fyodorovskoe 110/10 kV | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | open | 25 | Fyodorovskoe 110/10 kV | 2.5 | 0.02 | 0.17 | 1.5 | 120 | -1.33 | 0 | 1.5 | 1.33 | 1.33 | open
26 | Pankratovo 35/10 kV | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | open | 26 | Pankratovo 35/10 kV | 1 | 0.034 | 0.094 | 0.39 | 120 | -0.296 | 0 | 0.39 | 0.296 | 0.296 | open
27 | Petrovskoe 35/10 kV | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | open | 27 | Petrovskoe 35/10 kV | 1.6 | 0.006 | 0.326 | 0.77 | 120 | -0.444 | 0 | 0.77 | 0.444 | 0.444 | open
28 | Kotelnikovo 35/10 kV | 1 | 0.13 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.13 | 0.13 | open | 28 | Kotelnikovo 35/10 kV | 1 | 0 | 0.13 | 0.26 | 120 | -0.13 | 0 | 0.26 | 0.13 | 0.13 | open
29 | Legitovo 35/10 kV | 2.5 | 0.37 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.73 | 0.73 | open | 29 | Legitovo 35/10 kV | 2.5 | 0.023 | 0.393 | 1.1 | 120 | -0.707 | 0 | 1.1 | 0.707 | 0.707 | open
30 | Sloboda 35/10 kV | 2.5 | 0.2 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.65 | 0.65 | open | 30 | Sloboda 35/10 kV | 2.5 | 0.003 | 0.203 | 0.85 | 120 | -0.647 | 0 | 0.85 | 0.647 | 0.647 | open
31 | Zavrazhye 35/10 kV | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | open | 31 | Zavrazhye 35/10 kV | 1.6 | 0.177 | 0.467 | 0.74 | 120 | -0.273 | 0 | 0.74 | 0.273 | 0.273 | open
32 | Okulovo 35/10 kV | 1.6 | 0.18 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.72 | 0.72 | open | 32 | Okulovo 35/10 kV | 1.6 | 0.206 | 0.386 | 0.9 | 120 | -0.514 | 0 | 0.9 | 0.514 | 0.514 | open
33 | Chernyshevo 35/10 kV | 4 | 0.57 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.23 | 1.23 | open | 33 | Chernyshevo 35/10 kV | 4 | 0.075 | 0.645 | 1.8 | 120 | -1.155 | 0 | 1.8 | 1.155 | 1.155 | open
34 | Yakovlevo 110/35/10 kV | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 | 5.24 | open | 34 | Yakovlevo 110/35/10 kV | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234 | 5.234 | open
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 |  |  |  | Nom. Capacity LV, MVA | 10 | 0.006 | 0.066 | 5.3 | 120 | -5.234 | 0 | 5.3 | 5.234
35 | Chermenino 35/10 kV | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | open | 35 | Chermenino 35/10 kV | 1.6 | 0 | 0.07 | 0.86 | 120 | -0.79 | 0 | 0.86 | 0.79 | 0.79 | open
36 | Nezhitino 35/10 kV | 1 | 0.24 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.3 | 0.3 | open | 36 | Nezhitino 35/10 kV | 1 | 0.076 | 0.316 | 0.54 | 120 | -0.224 | 0 | 0.54 | 0.224 | 0.224 | open
37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.47 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.52 | 0.52 | open | 37 | Nikolo-Makarovo 35/10 kV | 1.6 | 0.161 | 0.631 | 0.99 | 120 | -0.359 | 0 | 0.99 | 0.359 | 0.359 | open
38 | Gusevo 110/10 kV | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | open | 38 | Gusevo 110/10 kV | 2.5 | 0.036 | 0.326 | 1.63 | 120 | -1.304 | 0 | 1.63 | 1.304 | 1.304 | open
39 | Medveditsa 35/10 kV | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | open | 39 | Medveditsa 35/10 kV | 2.5 | 0 | 0.53 | 1.3 | 120 | -0.77 | 0 | 1.3 | 0.77 | 0.77 | open
40 | Novinskoe 110/10 kV | 2.5 | 0.04 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.19 | 1.19 | open | 40 | Novinskoe 110/10 kV | 2.5 | 0 | 0.04 | 1.23 | 120 | -1.19 | 0 | 1.23 | 1.19 | 1.19 | open
41 | Filino 35/10 kV | 1.6 | 0.4 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.56 | 0.56 | open | 41 | Filino 35/10 kV | 1.6 | 0.122 | 0.522 | 0.96 | 120 | -0.438 | 0 | 0.96 | 0.438 | 0.438 | open
42 | Dyakonovo 110/10 kV | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | open | 42 | Dyakonovo 110/10 kV | 2.5 | 0.012 | 0.292 | 1.13 | 120 | -0.838 | 0 | 1.13 | 0.838 | 0.838 | open
43 | Oktyabrskaya 110/10 kV | 2.5 | 0.91 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.59 | 1.59 | open | 43 | Oktyabrskaya 110/10 kV | 2.5 | 0.04 | 0.95 | 2.5 | 1 day and night | -1.55 | 0 | 2.5 | 1.55 | 1.55 | open
44 | Kuzhbal 35/10 kV | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | open | 44 | Kuzhbal 35/10 kV | 2.5 | 0.022 | 0.422 | 1.48 | 120 | -1.058 | 0 | 1.48 | 1.058 | 1.058 | open
45 | Nikolo-Poloma 110/10 kV | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | open | 45 | Nikolo-Poloma 110/10 kV | 2.5 | 0.064 | 1.104 | 1.13 | 120 | -0.026 | 0 | 1.13 | 0.026 | 0.026 | open
46 | Nikola 110/35/10 kV | 6.3 | 0.34 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.81 | 2.81 | open | 46 | Nikola 110/35/10 kV | 6.3 | 0 | 0.34 | 3.15 | 120 | -2.81 | 0 | 3.15 | 2.81 | 2.81 | open
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  |  |  | Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.34 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.81 |  |  |  | Nom. Capacity LV, MVA | 6.3 | 0 | 0.34 | 3.15 | 120 | -2.81 | 0 | 3.15 | 2.81
47 | Zavetluzhye 35/10 kV | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | open | 47 | Zavetluzhye 35/10 kV | 1.6 | 0 | 0.11 | 0.67 | 120 | -0.56 | 0 | 0.67 | 0.56 | 0.56 | open
48 | Talitsa 35/10 kV | 1.6 | 0.26 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.34 | 1.34 | open | 48 | Talitsa 35/10 kV | 1.6 | 0 | 0.26 | 1.6 | 1 day and night | -1.34 | 0 | 1.6 | 1.34 | 1.34 | open
49 | Khoroshaya 35/10 kV | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | open | 49 | Khoroshaya 35/10 kV | 2.5 | 0 | 0.06 | 1.95 | 120 | -1.89 | 0 | 1.95 | 1.89 | 1.89 | open
50 | Zabegaevo 35/10 kV | 1.6 | 0.11 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.77 | 0.77 | open | 50 | Zabegaevo 35/10 kV | 1.6 | 0 | 0.11 | 0.88 | 120 | -0.77 | 0 | 0.88 | 0.77 | 0.77 | open
51 | Ilyinskoe 35/10 kV | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | open | 51 | Ilyinskoe 35/10 kV | 1.6 | 0 | 0.04 | 0.9 | 120 | -0.86 | 0 | 0.9 | 0.86 | 0.86 | open
52 | Luptyug 35/10 kV | 2.5 | 0.18 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.17 | 1.17 | open | 52 | Luptyug 35/10 kV | 2.5 | 0 | 0.18 | 1.35 | 120 | -1.17 | 0 | 1.35 | 1.17 | 1.17 | open
53 | Solovetskoe 35/10 kV | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | open | 53 | Solovetskoe 35/10 kV | 1.6 | 0.007 | 0.097 | 0.72 | 120 | -0.623 | 0 | 0.72 | 0.623 | 0.623 | open
54 | Gudkovo 110/10 kV | 2.5 | 0.06 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.32 | 1.32 | open | 54 | Gudkovo 110/10 kV | 2.5 | 0.037 | 0.097 | 1.38 | 120 | -1.283 | 0 | 1.38 | 1.283 | 1.283 | open
55 | Shortyug 110/10 kV | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | open | 55 | Shortyug 110/10 kV | 6.3 | 0.03 | 0.55 | 3.47 | 120 | -2.92 | 0 | 3.47 | 2.92 | 2.92 | open
56 | Yakshanga 110/10 kV | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | open | 56 | Yakshanga 110/10 kV | 6.3 | 0.081 | 1.491 | 3.47 | 120 | -1.979 | 0 | 3.47 | 1.979 | 1.979 | open
57 | Katunino 35/10 kV | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | open | 57 | Katunino 35/10 kV | 2.5 | 0 | 0.17 | 1.33 | 120 | -1.16 | 0 | 1.33 | 1.16 | 1.16 | open
58 | Konyovo 35/10 kV | 1.6 | 0.33 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.55 | 0.55 | open | 58 | Konyovo 35/10 kV | 1.6 | 0.012 | 0.342 | 0.88 | 120 | -0.538 | 0 | 0.88 | 0.538 | 0.538 | open
59 | Shekshema 110/10 kV | 6.3 | 0.58 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.92 | 1.92 | open | 59 | Shekshema 110/10 kV | 6.3 | 0.052 | 0.632 | 2.5 | 1 day and night | -1.868 | 0 | 2.5 | 1.868 | 1.868 | open
60 | Golovino 35/10 kV | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | open | 60 | Golovino 35/10 kV | 1 | 0 | 0.06 | 0.12 | 120 | -0.06 | 0 | 0.12 | 0.06 | 0.06 | open
61 | Pishchyovka 35/10 kV | 1 | 0.19 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.26 | 0.26 | open | 61 | Pishchyovka 35/10 kV | 1 | 0.075 | 0.265 | 0.45 | 120 | -0.185 | 0 | 0.45 | 0.185 | 0.185 | open
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
62 | Vasilyovo 110/35/10 kV | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | open | 62 | Vasilyovo 110/35/10 kV | 10+10 | 3.792 | 5.922 | 0.86 | 120 | 5.062 | 0 | 10.5 | 5.438 | 5.438 | open
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 3.792 | 5.332 | 0.86 | 120 | 4.472 | 0 | 10.5 | 6.028
63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 7.21 | open | 63 | Kalinki 110/35/10/6 kV | 10+10+1,6 | 0.404 | 6.524 | 1.15 | 120 | 5.374 | 0 | 12.18 | 6.806 | 6.806 | open
| Nom. Capacity MV, MVA | 10+10+1,6 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59 |  |  |  | Nom. Capacity MV, MVA | 10+10+1,6 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.53 | 1.15 | 120 | 0.38 | 0 | 12.18 | 11.8 |  |  |  | Nom. Capacity LV, MVA | 10+10+1,6 | 0.404 | 1.934 | 1.15 | 120 | 0.784 | 0 | 12.18 | 11.396
64 | Apraksino 35/10 kV | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | open | 64 | Apraksino 35/10 kV | 2,5+2,5 | 0.844 | 2.574 | 0.425 | 120 | 2.149 | 0 | 2.625 | 0.476 | 0.476 | open
65 | Borshchino 35/10 kV | 4+4 | 0.63 | 0.62 | 120 | 0.01 | 0 | 4.2 | 4.19 | 4.19 | open | 65 | Borshchino 35/10 kV | 4+4 | 0.567 | 1.197 | 0.62 | 120 | 0.577 | 0 | 4.2 | 3.623 | 3.623 | open
66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 0.2 | 0.11 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | open | 66 | Gorkovskaya 35/10 kV | 1,6+1,6 | 0.022 | 0.222 | 0.11 | 120 | 0.112 | 0 | 1.68 | 1.568 | 1.568 | open
67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | open | 67 | Ilyinskoe 35/10 kV | 2,5+2,5 | 0.605 | 2.935 | 0.55 | 120 | 2.385 | 0 | 2.625 | 0.24 | 0.24 | open
68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 1.18 | 0.4 | 120 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | open | 68 | Kuznetsovo 35/10 kV | 2,5+2,5 | 0.347 | 1.527 | 0.4 | 120 | 1.127 | 0 | 2.625 | 1.498 | 1.498 | open
69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.74 | 0.29 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | open | 69 | Kuzmishchi 35/10 kV | 1,6+1,6 | 0.28 | 1.02 | 0.29 | 120 | 0.73 | 0 | 1.68 | 0.95 | 0.95 | open
70 | Minskoe 35/10 kV | 2,5+2,5 | 1.3 | 0.43 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | open | 70 | Minskoe 35/10 kV | 2,5+2,5 | 0.681 | 1.981 | 0.43 | 120 | 1.551 | 0 | 2.625 | 1.074 | 1.074 | open
71 | Miskovo 35/6 kV | 1,8+1,8 | 0.36 | 0.2 | 120 | 0.16 | 0 | 1.89 | 1.73 | 1.73 | open | 71 | Miskovo 35/6 kV | 1,8+1,8 | 0.124 | 0.484 | 0.2 | 120 | 0.284 | 0 | 1.89 | 1.606 | 1.606 | open
72 | Nikolskoe 35/6 kV | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | open | 72 | Nikolskoe 35/6 kV | 4+4 | 0.568 | 3.068 | 0.92 | 120 | 2.148 | 0 | 4.2 | 2.052 | 2.052 | open
73 | Samet 35/6 kV | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | open | 73 | Samet 35/6 kV | 1,6+4 | 0.226 | 1.656 | 0 | 0 | 1.656 | 0 | 1.68 | 0.024 | 0.024 | open
74 | Sukhonogovo 35/10 kV | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | open | 74 | Sukhonogovo 35/10 kV | 3,2+4 | 1.096 | 3.806 | 0 | 0 | 3.806 | 0 | 3.36 | -0.446 | -0.446 | closed
75 | Sushchevo 35/10 kV | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | open | 75 | Sushchevo 35/10 kV | 4+4 | 0.508 | 4.188 | 0.76 | 120 | 3.428 | 0 | 4.2 | 0.772 | 0.772 | open
76 | EMZ 35/6 kV | 1+1 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | open | 76 | EMZ 35/6 kV | 1+1 | 0 | 0.82 | 0 | 0 | 0.82 | 0 | 1.05 | 0.23 | 0.23 | open
77 | Krasnoe 110/35/10 kV | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | open | 77 | Krasnoe 110/35/10 kV | 16+16 | 2.326 | 14.736 | 0 | 0 | 14.736 | 0 | 16.8 | 2.064 | 2.064 | open
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 2.326 | 13.966 | 0 | 0 | 13.966 | 0 | 16.8 | 2.834
78 | Isaevo 35/10 kV | 4+4 | 1.65 | 1.03 | 120 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | open | 78 | Isaevo 35/10 kV | 4+4 | 3.189 | 4.839 | 1.03 | 120 | 3.809 | 0 | 4.2 | 0.391 | 0.391 | open
79 | Chapaevo 35/10 kV | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | open | 79 | Chapaevo 35/10 kV | 2,5+2,5 | 0.201 | 1.471 | 0.43 | 120 | 1.041 | 0 | 2.625 | 1.584 | 1.584 | open
80 | Chernevo 35/10 kV | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | open | 80 | Chernevo 35/10 kV | 1,8+1,8 | 0.01 | 0.38 | 0.43 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | open
81 | Nerekhta-1 110/35/10 kV | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | open | 81 | Nerekhta-1 110/35/10 kV | 25+25 | 0.826 | 19.336 | 2.75 | 120 | 16.586 | 0 | 26.25 | 9.664 | 9.664 | open
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 0.826 | 12.816 | 2.75 | 120 | 10.066 | 0 | 26.25 | 16.184
| Nerekhta-1 110/10 kV | 16+16 | 5.79 | 2.2 | 120 | 3.59 | 0 | 16.8 | 13.21 |  |  |  | Nerekhta-1 110/10 kV | 16+16 | 0 | 5.79 | 2.2 | 120 | 3.59 | 0 | 16.8 | 13.21
82 | Nerekhta-2 110/10/6 kV | 5,6+10 | 0.93 | 1.55 | 120 | -0.62 | 0 | 5.88 | 6.5 | 6.5 | open | 82 | Nerekhta-2 110/10/6 kV | 10+10 | 5.854 | 6.784 | 1.55 | 120 | 5.234 | 0 | 10.5 | 5.266 | 5.266 | open
83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.7 | 0.41 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | open | 83 | Vladychnoe 35/10 kV | 1,6+1,6 | 0.122 | 0.822 | 0.41 | 120 | 0.412 | 0 | 1.68 | 1.268 | 1.268 | open
84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.38 | 0.23 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | open | 84 | Tatarskoe 35/10 kV | 1,6+1,6 | 0.002 | 0.382 | 0.23 | 120 | 0.152 | 0 | 1.68 | 1.528 | 1.528 | open
85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 4 | 0.76 | 120 | 3.24 | 0 | 6.615 | 3.375 | 3.375 | open | 85 | Aleksandrovo 110/35/10 kV | 6,3+6,3 | 0.084 | 4.084 | 0.76 | 120 | 3.324 | 0 | 6.615 | 3.291 | 3.291 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.3 | 0 | 120 | 0.3 | 0 | 6.615 | 6.315
| Nom. Capacity LV, MVA | 6,3+6,3 | 3.7 | 0.76 | 120 | 2.94 | 0 | 6.615 | 3.675 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.084 | 3.784 | 0.76 | 120 | 3.024 | 0 | 6.615 | 3.591
86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 3.91 | 1.28 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | open | 86 | Krasnaya Polyana 110/35/10 kV | 10+10 | 1.242 | 5.152 | 1.28 | 120 | 3.872 | 0 | 10.5 | 6.628 | 6.628 | open
| Nom. Capacity MV, MVA | 10+10 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78
| Nom. Capacity LV, MVA | 10+10 | 3.19 | 1.28 | 120 | 1.91 | 0 | 10.5 | 8.59 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.242 | 4.432 | 1.28 | 120 | 3.152 | 0 | 10.5 | 7.348
87 | Igodovo 35/10 kV | 1,6+1,6 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | open | 87 | Igodovo 35/10 kV | 1,6+1,6 | 0.103 | 0.473 | 0.25 | 120 | 0.223 | 0 | 1.68 | 1.457 | 1.457 | open
88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | open | 88 | Klevantsovo 35/10 kV | 1,6+1,6 | 0.031 | 0.831 | 0.56 | 120 | 0.271 | 0 | 1.68 | 1.409 | 1.409 | open
89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | open | 89 | Ostrovskoe 35/10 kV | 2,5+2,5 | 0.083 | 1.403 | 0.52 | 120 | 0.883 | 0 | 2.625 | 1.742 | 1.742 | open
90 | Sudislavl 110/10 kV | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | open | 90 | Sudislavl 110/10 kV | 10+10 | 1.365 | 9.505 | 1.8 | 120 | 7.705 | 0 | 10.5 | 2.795 | 2.795 | open
91 | Voronye 35/10 kV | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | open | 91 | Voronye 35/10 kV | 1,8+1,8 | 0.074 | 0.564 | 0.4 | 120 | 0.164 | 0 | 1.89 | 1.726 | 1.726 | open
92 | Susanino 110/35/10 kV | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | open | 92 | Susanino 110/35/10 kV | 10+10 | 0.633 | 4.563 | 1.89 | 120 | 2.673 | 0 | 10.5 | 7.827 | 7.827 | open
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.633 | 4.183 | 1.89 | 120 | 2.293 | 0 | 10.5 | 8.207
93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.25 | 0.07 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open | 93 | Kaliniskaya 35/10 kV | 2,5+2,5 | 0.044 | 0.294 | 0.07 | 120 | 0.224 | 0 | 2.625 | 2.401 | 2.401 | open
94 | Airport 110/35/6 kV | 16+16 | 5.39 | 2.88 | 120 | 2.51 | 0 | 16.8 | 14.29 | 14.29 | open | 94 | Airport 110/35/6 kV | 16+16 | 9.844 | 15.234 | 2.88 | 120 | 12.354 | 0 | 16.8 | 4.446 | 4.446 | open
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 5.39 | 2.88 | 120 | 2.51 | 0 | 16.8 | 14.29 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 9.844 | 15.234 | 2.88 | 120 | 12.354 | 0 | 16.8 | 4.446
95 | Vostochnaya-2 110/35/10 kV | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | open | 95 | Vostochnaya-2 110/35/10 kV | 25+25 | 3.053 | 26.093 | 0.02 | 120 | 26.073 | 0 | 26.25 | 0.177 | 0.177 | open
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 3.053 | 6.853 | 0.02 | 120 | 6.833 | 0 | 26.25 | 19.417
96 | Kostroma-3 110/35/10 kV | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | closed | 96 | Kostroma-3 110/35/10 kV | 10+16 | 0.909 | 12.399 | 0 | 120 | 12.399 | 0 | 10.5 | -1.899 | -1.899 | closed
| Nom. Capacity MV, MVA | 10+16 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82
| Nom. Capacity LV, MVA | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 0.909 | 9.719 | 0 | 120 | 9.719 | 0 | 10.5 | 0.781
97 | Yuzhnaya 110/35/10 kV | 25+25 | 13.975 | 0 | 120 | 13.975 | 0 | 26.25 | 12.275 | 12.275 | open | 97 | Yuzhnaya 110/35/10 kV | 25+25 | 7.969 | 21.944 | 0 | 120 | 21.944 | 0 | 26.25 | 4.306 | 4.306 | open
| Nom. Capacity MV, MVA | 25+25 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9 |  |  |  | Nom. Capacity MV, MVA | 25+25 | 0 | 4.35 | 0 | 120 | 4.35 | 0 | 26.25 | 21.9
| Nom. Capacity LV, MVA | 25+25 | 9.625 | 0 | 120 | 9.625 | 0 | 26.25 | 16.625 |  |  |  | Nom. Capacity LV, MVA | 25+25 | 7.969 | 17.594 | 0 | 120 | 17.594 | 0 | 26.25 | 8.656
98 | Davydovskaya 110/10 kV | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | open | 98 | Davydovskaya 110/10 kV | 25+25 | 3.131 | 12.041 | 0.02 | 120 | 12.021 | 0 | 26.25 | 14.229 | 14.229 | open | commissioned on 09.2009
99 | Kostroma-1 110/6 kV | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | open | 99 | Kostroma-1 110/6 kV | 10+10 | 0.753 | 11.133 | 0 | 0 | 11.133 | 0 | 10.5 | -0.633 | -0.633 | closed
100 | Severnaya 110/6 kV | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | open | 100 | Severnaya 110/6 kV | 20+25 | 2.007 | 21.247 | 0 | 0 | 21.247 | 0 | 21 | -0.247 | -0.247 | closed
101 | Strommashina 110/6 kV | 40+40 | 13.83 | 0 | 0 | 13.83 | 0 | 42 | 28.17 | 28.17 | open | 101 | Strommashina 110/6 kV | 40+40 | 3.657 | 17.487 | 0 | 0 | 17.487 | 0 | 42 | 24.513 | 24.513 | open
102 | Tsentralnaya 110/10/6 kV | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | open | 102 | Tsentralnaya 110/10/6 kV | 25+25 | 6.899 | 23.339 | 0 | 0 | 23.339 | 0 | 26.25 | 2.911 | 2.911 | open
103 | Baydarka 35/6 kV | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | open | 103 | Baydarka 35/6 kV | 6,3+6,3 | 0.867 | 2.857 | 1.2 | 120 | 1.657 | 0 | 6.615 | 4.958 | 4.958 | open
104 | Volzhskaya 35/6 kV | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | open | 104 | Volzhskaya 35/6 kV | 4+4 | 0.562 | 1.852 | 0.76 | 120 | 1.092 | 0 | 4.2 | 3.108 | 3.108 | open
105 | Vostochnaya-1 35/6 kV | 10+10+6,3 | 22.36 | 0 | 0 | 22.36 | 0 | 17.115 | -5.245 | -5.245 | closed | 105 | Vostochnaya-1 35/6 kV | 10+10+6,3 | 2.378 | 24.738 | 0 | 0 | 24.738 | 0 | 17.115 | -7.623 | -7.623 | closed
106 | Karavaevo 35/10 kV | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | open | 106 | Karavaevo 35/10 kV | 6,3+6,3 | 1.641 | 5.101 | 0 | 0 | 5.101 | 0 | 6.615 | 1.514 | 1.514 | open
107 | Korkino 35/10 kV | 2,5+2,5 | 1.73 | 0.85 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | open | 107 | Korkino 35/10 kV | 2,5+2,5 | 0.472 | 2.202 | 0.85 | 120 | 1.352 | 0 | 2.625 | 1.273 | 1.273 | open
108 | KPD 110/35/10 kV | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | open | 108 | KPD 110/35/10 kV | 16+16 | 11.047 | 18.587 | 1.44 | 120 | 17.147 | 0 | 16.8 | -0.347 | -0.347 | closed
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18 |  |  |  | Nom. Capacity MV, MVA | 16+16 | 0 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32 |  |  |  | Nom. Capacity LV, MVA | 16+16 | 11.047 | 17.967 | 1.44 | 120 | 16.527 | 0 | 16.8 | 0.273
109 | SM State district power station 110/35/6 kV | 10+16 | 6.48 | 0 | 0 | 6.48 | 0 | 10.5 | 4.02 | 4.02 | open | 109 | SM State district power station 110/35/6 kV | 10+16 | 2.083 | 8.563 | 0 | 0 | 8.563 | 0 | 10.5 | 1.937 | 1.937 | open
| Nom. Capacity MV, MVA | 10+16 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88 |  |  |  | Nom. Capacity MV, MVA | 10+16 | 0 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88
| Nom. Capacity LV, MVA | 10+16 | 5.86 | 0 | 0 | 5.86 | 0 | 10.5 | 4.64 |  |  |  | Nom. Capacity LV, MVA | 10+16 | 2.083 | 7.943 | 0 | 0 | 7.943 | 0 | 10.5 | 2.557
110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.76 | 0.88 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open | 110 | Sidorovskoe 35/6 kV | 2,5+4 | 0.664 | 1.424 | 0.88 | 120 | 0.544 | 0 | 2.625 | 2.081 | 2.081 | open
111 | Buy (r) 110/35/10 kV | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | open | 111 | Buy (r) 110/35/10 kV | 4+10 | 0.477 | 2.347 | 0 | 120 | 2.347 | 0 | 4.2 | 1.853 | 1.853 | open
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33 |  |  |  | Nom. Capacity MV, MVA | 4+10 | 0 | 1.87 | 0 | 120 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 |  |  |  | Nom. Capacity LV, MVA | 4+10 | 0.477 | 0.477 | 0 | 120 | 0.477 | 0 | 4.2 | 3.723
112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | open | 112 | Buy (agriculture) 110/10 kV | 6,3+6,3 | 0.865 | 7.115 | 1.2 | 120 | 5.915 | 0 | 6.615 | 0.7 | 0.7 | open
113 | Zapadnaya 110/10 kV | 10+10 | 5.84 | 2.63 | 120 | 3.21 | 0 | 10.5 | 7.29 | 7.29 | open | 113 | Zapadnaya 110/10 kV | 10+10 | 0.074 | 5.914 | 2.63 | 120 | 3.284 | 0 | 10.5 | 7.216 | 7.216 | open
114 | Dor 35/10 kV | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | open | 114 | Dor 35/10 kV | 1,6+1,6 | 0.017 | 0.477 | 0.06 | 120 | 0.417 | 0 | 1.68 | 1.263 | 1.263 | open
115 | Dyakonovo 35/10 kV | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | open | 115 | Dyakonovo 35/10 kV | 1+1 | 0.012 | 0.242 | 0.26 | 120 | -0.018 | 0 | 1.05 | 1.068 | 1.068 | open
116 | Likurga 35/10 kV | 1,8+1,6 | 0.2 | 0.12 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | open | 116 | Likurga 35/10 kV | 1,8+1,6 | 0.001 | 0.201 | 0.12 | 120 | 0.081 | 0 | 1.68 | 1.599 | 1.599 | open
117 | Shushkodom 35/10 kV | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | open | 117 | Shushkodom 35/10 kV | 1+1 | 0.012 | 0.302 | 0.06 | 120 | 0.242 | 0 | 1.05 | 0.808 | 0.808 | open
118 | Novaya 110/35/10 kV | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | open | 118 | Novaya 110/35/10 kV | 6,3+6,3 | 0.753 | 3.683 | 0.64 | 120 | 3.043 | 0 | 6.615 | 3.572 | 3.572 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.753 | 1.853 | 0.64 | 120 | 1.213 | 0 | 6.615 | 5.402
119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | open | 119 | Orekhovo 110/35/10 kV | 6,3+6,3 | 0.179 | 1.539 | 0 | 120 | 1.539 | 0 | 6.615 | 5.076 | 5.076 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.179 | 1.009 | 0 | 120 | 1.009 | 0 | 6.615 | 5.606
120 | Loparevo 110/10 kV | 2,5+2,5 | 0.61 | 0.55 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | open | 120 | Loparevo 110/10 kV | 2,5+2,5 | 0.227 | 0.837 | 0.55 | 120 | 0.287 | 0 | 2.625 | 2.338 | 2.338 | open
121 | Poultry farm 35/10 kV | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | open | 121 | Poultry farm 35/10 kV | 4+4 | 0.03 | 1.76 | 1.28 | 120 | 0.48 | 0 | 4.2 | 3.72 | 3.72 | open
122 | Kabanovo 35/10 kV | 2,5+2,5 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open | 122 | Kabanovo 35/10 kV | 2,5+2,5 | 0 | 0.33 | 0.22 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | open
123 | Levkovo 35/10 kV | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | open | 123 | Levkovo 35/10 kV | 1,6+1,6 | 0.006 | 0.226 | 0.74 | 120 | -0.514 | 0 | 1.68 | 2.194 | 2.194 | open
124 | Pronino 35/10 kV | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open | 124 | Pronino 35/10 kV | 4+2,5 | 0.005 | 0.385 | 0.2 | 120 | 0.185 | 0 | 2.625 | 2.44 | 2.44 | open
125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.25 | 0.13 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | open | 125 | Toltunovo 35/10 kV | 2,5+2,5 | 0.346 | 0.596 | 0.13 | 120 | 0.466 | 0 | 2.625 | 2.159 | 2.159 | open
126 | Soligalich 110/35/10 kV | 10+10 | 5.73 | 1.7 | 120 | 4.03 | 0 | 10.5 | 6.47 | 6.47 | open | 126 | Soligalich 110/35/10 kV | 10+10 | 0.811 | 6.541 | 1.7 | 120 | 4.841 | 0 | 10.5 | 5.659 | 5.659 | open
| Nom. Capacity MV, MVA | 10+10 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35
| Nom. Capacity LV, MVA | 10+10 | 4.58 | 1.7 | 120 | 2.88 | 0 | 10.5 | 7.62 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0.811 | 5.391 | 1.7 | 120 | 3.691 | 0 | 10.5 | 6.809
127 | Pochinok 35/10 kV | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | open | 127 | Pochinok 35/10 kV | 1,6+2,5 | 0.023 | 0.553 | 0.34 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | open
128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | open | 128 | Chukhloma 110/35/10 kV | 6,3+6,3 | 0.518 | 4.488 | 2.06 | 120 | 2.428 | 0 | 6.615 | 4.187 | 4.187 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 0.518 | 3.368 | 2.06 | 120 | 1.308 | 0 | 6.615 | 5.307
129 | Suday 35/10 kV | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open | 129 | Suday 35/10 kV | 1,6+1,6 | 0.072 | 1.082 | 0.49 | 120 | 0.592 | 0 | 1.68 | 1.088 | 1.088 | open
130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 6.48 | 0.38 | 120 | 6.1 | 0 | 6.615 | 0.515 | 0.515 | open | 130 | Antropovo (r) 110/35/10 kV | 6,3+16 | 0.218 | 6.698 | 0.38 | 120 | 6.318 | 0 | 6.615 | 0.297 | 0.297 | open
| Nom. Capacity MV, MVA | 6,3+16 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 4.59 | 0 | 120 | 4.59 | 0 | 6.615 | 2.025
| Nom. Capacity LV, MVA | 6,3+16 | 1.89 | 0.38 | 120 | 1.51 | 0 | 6.615 | 5.105 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.218 | 2.108 | 0.38 | 120 | 1.728 | 0 | 6.615 | 4.887
131 | Palkino 35/10 kV | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | open | 131 | Palkino 35/10 kV | 2,5+4 | 0.011 | 0.711 | 0.45 | 120 | 0.261 | 0 | 2.625 | 2.364 | 2.364 | open
132 | Slovinka 35/10 kV | 1,6+1,6 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | open | 132 | Slovinka 35/10 kV | 1,6+1,6 | 0 | 0.15 | 0.1 | 120 | 0.05 | 0 | 1.68 | 1.63 | 1.63 | open
133 | Kady 110/35/10 kV | 10+10 | 3.87 | 0.69 | 120 | 3.18 | 0 | 10.5 | 7.32 | 7.32 | open | 133 | Kady 110/35/10 kV | 10+10 | 1.132 | 5.002 | 0.69 | 120 | 4.312 | 0 | 10.5 | 6.188 | 6.188 | open
| Nom. Capacity MV, MVA | 10+10 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 1.06 | 0 | 120 | 1.06 | 0 | 10.5 | 9.44
| Nom. Capacity LV, MVA | 10+10 | 2.81 | 0.69 | 120 | 2.12 | 0 | 10.5 | 8.38 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 1.132 | 3.942 | 0.69 | 120 | 3.252 | 0 | 10.5 | 7.248
134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | open | 134 | Ekaterinkino 35/10 kV | 1,6+1,6 | 0.037 | 0.127 | 0.1 | 120 | 0.027 | 0 | 1.68 | 1.653 | 1.653 | open
135 | Ilyinskoe 110/35/10 kV | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open | 135 | Ilyinskoe 110/35/10 kV | 10+10 | 0 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. Capacity LV, MVA | 10+10 | 0 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43
136 | Kologriv 35/10 kV | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | open | 136 | Kologriv 35/10 kV | 4+4 | 0.248 | 2.368 | 1.42 | 120 | 0.948 | 0 | 4.2 | 3.252 | 3.252 | open
137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0.4 | 0.08 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open | 137 | Ovsyannikovo 35/10 kV | 1,6+1,6 | 0 | 0.4 | 0.08 | 120 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | open
138 | Makaryev-1 110/35/10 kV | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | open | 138 | Makaryev-1 110/35/10 kV | 10+10 | 0.197 | 7.737 | 0.8 | 120 | 6.937 | 0 | 10.5 | 3.563 | 3.563 | open
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12 |  |  |  | Nom. Capacity MV, MVA | 10+10 | 0.197 | 2.377 | 0.8 | 120 | 1.577 | 0 | 10.5 | 8.923
139 | Gorchukha 35/10 kV | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | open | 139 | Gorchukha 35/10 kV | 2,5+2,5 | 0.039 | 1.229 | 0 | 0 | 1.229 | 0 | 2.625 | 1.396 | 1.396 | open
140 | Makaryev-2 35/10 kV | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | open | 140 | Makaryev-2 35/10 kV | 4+4 | 0.13 | 3.13 | 1.58 | 120 | 1.55 | 0 | 4.2 | 2.65 | 2.65 | open
141 | Timoshino 35/10 kV | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | open | 141 | Timoshino 35/10 kV | 1+1 | 0.004 | 0.184 | 0 | 0 | 0.184 | 0 | 1.05 | 0.866 | 0.866 | open
142 | Unzha 35/10 kV | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | open | 142 | Unzha 35/10 kV | 1+1,6 | 0 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | open
143 | Yakimovo 35/10 kV | 1,6+2,5 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open | 143 | Yakimovo 35/10 kV | 1,6+2,5 | 0 | 0.39 | 0.32 | 120 | 0.07 | 0 | 1.68 | 1.61 | 1.61 | open
144 | BKhZ 110/6 kV | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | open | 144 | BKhZ 110/6 kV | 25+25 | 0.306 | 2.886 | 0 | 0 | 2.886 | 0 | 26.25 | 23.364 | 23.364 | open
145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | open | 145 | Sosnovka 35/10 kV | 2,5+1,6 | 0.018 | 0.458 | 0.15 | 120 | 0.308 | 0 | 1.68 | 1.372 | 1.372 | open
146 | Georgievskoe 35/10 kV | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | open | 146 | Georgievskoe 35/10 kV | 2,5+2,5 | 0.07 | 2.22 | 1.23 | 120 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | open
147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | open | 147 | Neya 110/35/27,5/10 kV | 40+40+6,3 | 0.609 | 16.659 | 3.6 | 120 | 13.059 | 0 | 48.615 | 35.556 | 35.556 | open
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085 |  |  |  | Nom. Capacity MV, MVA | 40+40+6,3 | 0 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695 |  |  |  | Nom. Capacity LV, MVA | 40+40+6,3 | 0.609 | 8.129 | 3.6 | 120 | 4.529 | 0 | 48.615 | 44.086
148 | Vozherovo 35/10 kV | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | open | 148 | Vozherovo 35/10 kV | 1,6+1,6 | 0 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | open
149 | Matveevo 35/10 kV | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | open | 149 | Matveevo 35/10 kV | 1,8+4 | 0 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | open
150 | Parfenyevo 35/10 kV | 4+4 | 3.05 | 1.89 | 120 | 1.16 | 0 | 4.2 | 3.04 | 3.04 | open | 150 | Parfenyevo 35/10 kV | 4+4 | 0.056 | 3.106 | 1.89 | 120 | 1.216 | 0 | 4.2 | 2.984 | 2.984 | open
151 | Vokhma 110/35/10 kV | 6,3+16 | 5.42 | 0 | 0 | 5.42 | 0 | 6.615 | 1.195 | 1.195 | open | 151 | Vokhma 110/35/10 kV | 6,3+16 | 0.23 | 5.65 | 0 | 0 | 5.65 | 0 | 6.615 | 0.965 | 0.965 | open
| Nom. Capacity MV, MVA | 6,3+16 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085 |  |  |  | Nom. Capacity MV, MVA | 6,3+16 | 0 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085
| Nom. Capacity LV, MVA | 6,3+16 | 3.89 | 0 | 0 | 3.89 | 0 | 6.615 | 2.725 |  |  |  | Nom. Capacity LV, MVA | 6,3+16 | 0.23 | 4.12 | 0 | 0 | 4.12 | 0 | 6.615 | 2.495
152 | Lapshino 35/10 kV | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open | 152 | Lapshino 35/10 kV | 2,5+2,5 | 0 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open
153 | Spass 35/10 kV | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | open | 153 | Spass 35/10 kV | 1,6+2,5 | 0 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | open
154 | Bogovarovo 35/10 kV | 2,5+4 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | open | 154 | Bogovarovo 35/10 kV | 2,5+4 | 0.094 | 1.684 | 1 | 120 | 0.684 | 0 | 2.625 | 1.941 | 1.941 | open
155 | Pavino 110/35/10 kV | 10+6,3 | 2.56 | 0 | 0 | 2.56 | 0 | 6.615 | 4.055 | 4.055 | open | 155 | Pavino 110/35/10 kV | 10+6,3 | 0.078 | 2.638 | 0 | 0 | 2.638 | 0 | 6.615 | 3.977 | 3.977 | open
| Nom. Capacity MV, MVA | 10+6,3 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175 |  |  |  | Nom. Capacity MV, MVA | 10+6,3 | 0 | 0.44 | 0 | 0 | 0.44 | 0 | 6.615 | 6.175
| Nom. Capacity LV, MVA | 10+6,3 | 2.12 | 0 | 0 | 2.12 | 0 | 6.615 | 4.495 |  |  |  | Nom. Capacity LV, MVA | 10+6,3 | 0.078 | 2.198 | 0 | 0 | 2.198 | 0 | 6.615 | 4.417
156 | Ledengskaya 35/10 kV | 1,6+4 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open | 156 | Ledengskaya 35/10 kV | 1,6+4 | 0 | 0.08 | 0.07 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | open
157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | open | 157 | Pyshchug 110/35/10 kV | 6,3+6,3 | 1.607 | 4.027 | 0 | 0 | 4.027 | 0 | 6.615 | 2.588 | 2.588 | open
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495 |  |  |  | Nom. Capacity MV, MVA | 6,3+6,3 | 0 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315 |  |  |  | Nom. Capacity LV, MVA | 6,3+6,3 | 1.607 | 3.907 | 0 | 0 | 3.907 | 0 | 6.615 | 2.708
158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | open | 158 | Rozhdestvenskoe 110/35/10 kV | 10+4 | 0.139 | 1.909 | 0.75 | 120 | 1.159 | 0 | 4.2 | 3.041 | 3.041 | open
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51 |  |  |  | Nom. Capacity MV, MVA | 10+4 | 0 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87 |  |  |  | Nom. Capacity LV, MVA | 10+4 | 0.139 | 1.219 | 0.75 | 120 | 0.469 | 0 | 4.2 | 3.731
159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.37 | 0.27 | 120 | 0.1 | 0 | 1.68 | 1.58 | 1.58 | open | 159 | Odoevskoe 35/10 kV | 1,6+1,6 | 0.03 | 0.4 | 0.27 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | open
160 | Sharya (r) 110/35/6 kV | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | open | 160 | Sharya (r) 110/35/6 kV | 20+25 | 0.412 | 19.432 | 2 | 120 | 17.432 | 0 | 21 | 3.568 | 3.568 | open
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8 |  |  |  | Nom. Capacity MV, MVA | 20+25 | 0 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18 |  |  |  | Nom. Capacity LV, MVA | 20+25 | 0.412 | 7.232 | 2 | 120 | 5.232 | 0 | 21 | 15.768
161 | Industrial hub 110/6/6 kV | 25+25 | 5.71 | 2.5 | 120 | 3.21 | 0 | 26.25 | 23.04 | 23.04 | open | 161 | Industrial hub 110/6/6 kV | 25+25 | 0.32 | 6.03 | 2.5 | 120 | 3.53 | 0 | 26.25 | 22.72 | 22.72 | open
162 | Krivyachka 35/10 kV | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | open | 162 | Krivyachka 35/10 kV | 1,6+1 | 0.01 | 0.83 | 0.57 | 120 | 0.26 | 0 | 1.05 | 0.79 | 0.79 | open
163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.89 | 0 | 0 | 0.89 | 0 | 1.68 | 0.79 | 0.79 | open | 163 | Nikolo-Shanga 35/10 kV | 1,6+1,6 | 0.203 | 1.093 | 0 | 0 | 1.093 | 0 | 1.68 | 0.587 | 0.587 | open
164 | Tsentralnaya 35/6 kV | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | open | 164 | Tsentralnaya 35/6 kV | 10+10 | 2.051 | 11.011 | 3 | 120 | 8.011 | 0 | 10.5 | 2.489 | 2.489 | open
| Total over Kostromaenergo | 1705 | 423.835 | [8 empty] | 2: Total over Kostromaenergo; 3: 1705; 5: 524.246
| deficit | [8 empty] | -6.235 |  | 2: deficit; Min 12: -11.35
| proficit | [8 empty] | 502.7 |  | 2: proficit; Min 12: 412.024