## Смоленскэнерго
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Current deficit/ proficit, MVA
|  |  |  | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.24 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.46 | 0.46 | opened
2 | Verkhovye 35/10 | 4 | 0.59 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.77 | 0.77 | opened
3 | Neykovo 35/10 | 2.5 | 0.14 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.59 | 1.59 | opened
4 | Merlino 110/35/10 | 6.3 | 0.34 | 0.34 | 24 hours | 0.34 | 0 | 0.34 | 0 | 0 | opened
| Nom. capacity MV, МVА | 6.3 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0
| Nom. capacity LV, МVА | 6.3 | 0.24 | 0.24 | 24 hours | 0.24 | 0 | 0.24 | 0
5 | Belyaevo 35/10 | 1.6 | 0.3 | 2.11 | 24 hours | 2.11 | 0 | 2.11 | 1.81 | 1.81 | opened
6 | Zaozerye 35/10 | 1.6 | 0.17 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.68 | 0.68 | opened
7 | Selezni 35/10 | 2.5 | 0.37 | 2.21 | 24 hours | 2.21 | 0 | 2.21 | 1.84 | 1.84 | opened
8 | Logovo 110/10 | 6.3 | 0.4 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 0.96 | 0.96 | opened
9 | Dubrovka 35/10 | 2.5 | 0.24 | 1.36 | 24 hours | 1.36 | 0 | 1.36 | 1.12 | 1.12 | opened
10 | Svistovichi 35/10 | 2.5 | 0.28 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.57 | 0.57 | opened
11 | Elsha 35/10 | 1.6 | 0.09 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.76 | 0.76 | opened
12 | Sapsho 35/10 | 4 | 0.88 | 2.12 | 24 hours | 2.12 | 0 | 2.12 | 1.24 | 1.24 | opened
13 | Divo 110/10 | 2.5 | 0.6 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.25 | 0.25 | opened
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 24 hours | 1.02 | 0 | 1.02 | 0.57 | 0.57 | opened
15 | Zamoshye 35/10 | 2.5 | 0.07 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.61 | 0.61 | opened
16 | Loino 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened
17 | Rokot 35/10 | 2.5 | 0.29 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.01 | 1.01 | opened
18 | Nikontsy 35/10 | 2.5 | 0.15 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.7 | 0.7 | opened
19 | Batishchevo 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened
20 | Vasino 35/10 | 2.5 | 0.31 | 0 | 24 hours | 0 | 0 | 0 | -0.31 | -0.31 | closed
21 | Bulgakovo 35/10 | 2.5 | 0.26 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.47 | 1.47 | opened
22 | Spas-Ugly 35/10 | 1.6 | 0.16 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.52 | 0.52 | opened
23 | Tretyakovo 35/10 | 4 | 0.25 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.3 | 2.3 | opened
24 | Velisto 35/10 | 2.5 | 0.09 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 1.21 | 1.21 | opened
25 | Baturino 35/10 | 1.6 | 0.1 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.75 | 0.75 | opened
26 | Pechatniki 35/10 | 2.5 | 0.34 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.12 | 3.12 | opened
27 | Garistovo 35/10 | 1.6 | 0.18 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.67 | 0.67 | opened
28 | Bezzaboty 35/10 | 2.5 | 0.09 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.64 | 1.64 | opened
29 | Vysokoe 35/10 | 2.5 | 0.2 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.35 | 2.35 | opened
30 | Zaytsevo 35/10 | 1.6 | 0.35 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.5 | 0.5 | opened
31 | Saveevo 35/10 | 2.5 | 0.46 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.39 | 0.39 | opened
32 | Gorenovo 35/10 | 1.6 | 0.26 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.29 | 2.29 | opened
33 | Shpunty 35/10 | 2.5 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened
34 | Kadino 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened
35 | Stegrimovo 35/10 | 2.5 | 0.08 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.81 | 2.81 | opened
36 | Zhukovo 35/10 | 2.5 | 0.2 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.53 | 1.53 | opened
37 | Mikshino 35/10 | 2.5 | 0.13 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.6 | 1.6 | opened
38 | Petrovichi 35/10 | 2.5 | 0.18 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.37 | 2.37 | opened
39 | Mikulichi 35/10 | 2.5 | 0.51 | 4.59 | 24 hours | 4.59 | 0 | 4.59 | 4.08 | 4.08 | opened
40 | Nedeykovichi 35/10 | 2.5 | 0.22 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.63 | 0.63 | opened
41 | Posyolki 110/35/10 | 6.3 | 0.71 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.23 | 0.23 | opened
42 | Kuzmichi 35/10 | 2.5 | 0.34 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.39 | 1.39 | opened
43 | Maksheevo 110/10 | 6.3 | 0.41 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.14 | 2.14 | opened
44 | Putkovo 35/10 | 1.8 | 0.23 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.62 | 0.62 | opened
45 | Uspenskoe 35/10 | 2.5 | 0.49 | 2.55 | 24 hours | 2.55 | 0 | 2.55 | 2.06 | 2.06 | opened
46 | Kalpita 35/10 | 1.6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
47 | Kasnya 110/10 | 2.5 | 0.32 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 3.14 | 3.14 | opened
48 | Akatovo 35/10 | 1.6 | 1.01 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 1.88 | 1.88 | opened
49 | Gorki 35/10 | 1.6 | 0.18 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.5 | 0.5 | opened
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.06 | 0.06 | opened
51 | NS-21 110/10 | 16 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0 | 0 | opened
52 | NS-22 110/35/10 | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0 | 0 | opened
| Nom. capacity MV, МVА | 25 | 2.09 | 2.09 | 24 hours | 2.09 | 0 | 2.09 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 24 hours | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.47 | 3.46 | 24 hours | 3.46 | 0 | 3.46 | 2.99 | 2.99 | opened
54 | Torbeevo 110/10 | 6.3 | 0.35 | 2.89 | 24 hours | 2.89 | 0 | 2.89 | 2.54 | 2.54 | opened
55 | Leuzdovo 35/10 | 1 | 0.12 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.56 | 0.56 | opened
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.56 | 1.56 | opened
57 | Avrora 35/10 | 2.5 | 0.09 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.59 | 0.59 | opened
58 | Bekhteevo 35/10 | 2.5 | 0.08 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.6 | 0.6 | opened
59 | Sereda 35/10 | 2.5 | 0.38 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.3 | 0.3 | opened
60 | Mikhali 35/10 | 2.5 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 24 hours | 0 | 0 | 0 | -0.06 | -0.06 | closed
62 | Zakharyevskoe 35/10 | 1.6 | 0.19 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.66 | 0.66 | opened
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened
64 | Baskakovka 35/10 | 4 | 0.21 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.52 | 1.52 | opened
65 | Ekimtsevo 110/10 | 2.5 | 0.36 | 1.73 | 24 hours | 1.73 | 0 | 1.73 | 1.37 | 1.37 | opened
Two-transformer substations
66 | Smolensk 1 (FGC) 110/35/6 | 40+40 | 41.67 | 5.68 | 120 | 35.99 | 0 | 42 | 6.01 | 6.01 | opened
| Nom. capavity MV, МVА | 40+40 | 4.9 | 3.76 |  | 1.14 | 0 | 42 | 40.86
| Nom. capacity LV, МVА | 40+40 | 36.77 | 1.92 | 120 | 34.85 | 0 | 42 | 7.15
67 | Water intake 35/6 | 4+4 | 2.93 | 1.2 | 120 | 1.73 | 0 | 4.2 | 2.47 | 2.47 | opened
68 | Tychinino 35/10 | 4+4 | 1.1 | 0.91 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened
69 | Ryabtsevo 35/10 | 4+4 | 2.4 | 0 | 120 | 2.4 | 0 | 4.2 | 1.8 | 1.8 | opened
70 | Smolensk 2 110/6 | 40+40 | 16.21 | 6.41 | 120 | 9.8 | 0 | 42 | 32.2 | 32.2 | opened
71 | Vostochnaya 110/6 | 25+16 | 5.71 | 0 | 120 | 5.71 | 0 | 16.8 | 11.09 | 11.09 | opened
72 | Diffuzion 110/6 | 25+25 | 14.69 | 1.06 | 120 | 13.63 | 0 | 26.25 | 12.62 | 12.62 | opened
73 | Zavodskaya 110/35/10 | 16+16 | 17.31 | 17.07 | 120 | 0.24 | 0 | 16.8 | 16.56 | 13.12 | opened
| Nom. capacity MV, МVА | 16+16 | 15.1 | 11.42 |  | 3.68 | 0 | 16.8 | 13.12
| Nom. capacity LV, МVА | 16+16 | 2.21 | 5.65 | 120 | -3.44 | 0 | 16.8 | 20.24
74 | Yasennaya 35/6 | 10+10 | 8.98 | 0 | 120 | 8.98 | 0 | 10.5 | 1.52 | 1.52 | opened
75 | Gnezodovo 35/6 | 7,5+7,5 | 4.32 | 0.42 | 120 | 3.9 | 0 | 7.875 | 3.975 | 3.975 | opened
76 | Zapadnaya 110/6 | 25+16 | 13.58 | 0.63 | 120 | 12.95 | 0 | 16.8 | 3.85 | 3.85 | opened
77 | Katyn 2 110/35/10 | 10+16 | 4.58 | 2.59 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened
| Nom. capacity MV, МVА | 10+16 | 2.59 | 2.59 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.99 | 0 | 120 | 1.99 | 0 | 10.5 | 8.51
78 | Katyn 1 35/10 | 4+4 | 1.57 | 0.05 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | opened
79 | Lubnya 35/10 | 4+4 | 1.33 | 0.13 | 120 | 1.2 | 0 | 4.2 | 3 | 3 | opened
80 | Kozino 110/35/10 | 10+10 | 8.41 | 6.51 | 120 | 1.9 | 0 | 10.5 | 8.6 | 8.6 | opened
| Nom. capacity MV, МVА | 10+10 | 6.5 | 6.5 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.91 | 0.01 | 120 | 1.9 | 0 | 10.5 | 8.6
81 | Odintsovo 35/10 | 6,3+6,3 | 4.55 | 2.15 | 120 | 2.4 | 0 | 6.615 | 4.215 | 4.215 | opened
82 | Trudilovo 35/10 | 2,5+2,5 | 1.29 | 0.08 | 120 | 1.21 | 0 | 2.625 | 1.415 | 1.415 | opened
83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0 |  | 0 | 0 | 42 | 42 | 42 | opened
84 | Pronino 110/35/6 | 10+10 | 6.24 | 4.67 | 120 | 1.57 | 0 | 10.5 | 8.93 | 8.93 | opened
| Nom. capacity MV, МVА | 10+10 | 3.48 | 3.48 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.76 | 1.19 | 120 | 1.57 | 0 | 10.5 | 8.93
85 | Olsha 35/10 | 2,5+2,5 | 0.92 | 0 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
86 | Krasny bor 35/6 | 4+4 | 2.58 | 0 | 120 | 2.58 | 0 | 4.2 | 1.62 | 1.62 | opened
87 | Severnaya 110/35/6 | 25+25 | 17.69 | 6.13 | 120 | 11.56 | 0 | 26.25 | 14.69 | 14.69 | opened
| Nom. capacity MV, МVА | 25+25 | 3.54 | 3.54 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 14.15 | 2.59 | 120 | 11.56 | 0 | 26.25 | 14.69
88 | Peсhersk 35/6 | 4+4 | 2.59 | 0.34 | 120 | 2.25 | 0 | 4.2 | 1.95 | 1.95 | opened
89 | Kolodnya 35/6 | 6,3+4 | 2.56 | 0 | 120 | 2.56 | 0 | 4.2 | 1.64 | 1.64 | opened
90 | Tsentralnaya 110/10/6 | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18 | 11.18 | opened
| Nom. capacity MV, МVА | 25+25 | 0 | 0 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 20.83 | 5.76 | 120 | 15.07 | 0 | 26.25 | 11.18
91 | Chernushki 110/10/6 | 25+25 | 18.02 | 2.12 | 120 | 15.9 | 0 | 26.25 | 10.35 | 10.35 | opened
| Nom. capacity MV, МVА | 25+25 | 6.43 | 0 |  | 6.43 | 0 | 26.25 | 19.82
| Nom. Capacity LV, МVА | 25+25 | 11.59 | 2.12 | 120 | 9.47 | 0 | 26.25 | 16.78
92 | Yuzhnaya 110/35/6 | 40+40 | 32.46 | 7.03 | 120 | 25.43 | 0 | 42 | 16.57 | 16.57 | opened
| Nom. capacity MV, МVА | 40+40 | 1.31 | 1.31 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 31.15 | 5.72 | 120 | 25.43 | 0 | 42 | 16.57
93 | Karyernaya 110/35/6 | 16+16 | 3.21 | 2.39 | 120 | 0.82 | 0 | 16.8 | 15.98 | 15.98 | opened
| Nom. capacity MV, МВА | 16+16 | 2.39 | 2.39 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0.82 | 0 | 120 | 0.82 | 0 | 16.8 | 15.98
94 | Koshchino 35/10 | 4+4 | 0.87 | 0.11 | 120 | 0.76 | 0 | 4.2 | 3.44 | 3.44 | opened
95 | Kommunar 35/10 | 2,5+2,5 | 0.67 | 0.03 | 120 | 0.64 | 0 | 2.625 | 1.985 | 1.985 | opened
96 | Kasplya 110/35/10 | 10+10 | 3.4 | 3.07 | 120 | 0.33 | 0 | 10.5 | 10.17 | 10.17 | opened
| Nom. capacity MV, МVА | 10+10 | 2.21 | 2.21 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.19 | 0.86 | 120 | 0.33 | 0 | 10.5 | 10.17
97 | Apolye 35/10 | 2,5+2,5 | 0.79 | 0.17 | 120 | 0.62 | 0 | 2.625 | 2.005 | 2.005 | opened
98 | Zhukovskaya 35/10 | 4+4 | 1.4 | 0.19 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened
99 | Mazaltsevo 110/35/10 | 10+10 | 2.59 | 2.16 | 120 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.69 | 0.26 | 120 | 0.43 | 0 | 10.5 | 10.07
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
101 | Krasny 110/35/10 | 10+10 | 4.22 | 2.26 | 120 | 1.96 | 0 | 10.5 | 8.54 | 8.54 | opened
| Nom. capacity MV, МVА | 10+10 | 1.8 | 1.8 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.42 | 0.46 | 120 | 1.96 | 0 | 10.5 | 8.54
102 | Voloelovo 35/10 | 2,5+2,5 | 0.04 | 0.01 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | opened
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | opened
104 | Miganovo 35/10 | 2,5+2,5 | 1.18 | 0.49 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened
105 | Velizh 110/35/10 | 10+10 | 5.77 | 2.05 | 120 | 3.72 | 0 | 10.5 | 6.78 | 6.78 | opened
| Nom. capacity MV, МVА | 10+10 | 1.38 | 1.38 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.39 | 0.67 | 120 | 3.72 | 0 | 10.5 | 6.78
106 | Chepli 35/10 | 2,5+2,5 | 0.4 | 0.09 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
107 | Demidov 110/35/10 | 10+16 | 5.52 | 1.14 | 120 | 4.38 | 0 | 10.5 | 6.12 | 6.12 | opened
| Nom. capacity MV, МVА | 10+16 | 0.96 | 0.96 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.56 | 0.18 | 120 | 4.38 | 0 | 10.5 | 6.12
108 | Staroe selo 35/10 | 2,5+2,5 | 0.34 | 0.17 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
109 | Zakrutye 35/10 | 2,5+2,5 | 0.13 | 0 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
110 | Zaborye 35/10 | 1,6+2,5 | 0.34 | 0.21 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
111 | Mikhailovskoe 110/35/10 | 10+10 | 1.07 | 0.73 | 120 | 0.34 | 0 | 10.5 | 10.16 | 10.16 | opened
| Nom. capacity MV, МVА | 10+10 | 0.31 | 0.31 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.76 | 0.42 | 120 | 0.34 | 0 | 10.5 | 10.16
112 | Kardymovo 110/35/10 | 10+16 | 5.69 | 3.2 | 120 | 2.49 | 0 | 10.5 | 8.01 | 8.01 | opened
| Nom. capacity MV, МVА | 10+16 | 2.58 | 2.58 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.11 | 0.62 | 120 | 1.49 | 0 | 10.5 | 9.01
113 | Sinkovo 35/6 | 4+2,5 | 0.44 | 0.16 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
114 | Kamenka 35/10 | 2,5+2,5 | 1.4 | 0.42 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened
115 | Solovyevo 35/10 | 4+4 | 0.28 | 0.04 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened
116 | Rudnya (FGC) 110/35/10 | 10+16 | 8.33 | 1.87 | 120 | 6.46 | 0 | 10.5 | 4.04 | 4.04 | opened
| Nom. capacity MV, МVА | 10+16 | 0.94 | 0.94 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.39 | 0.93 | 120 | 6.46 | 0 | 10.5 | 4.04
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.2 | 0.75 | 120 | -0.55 | 0 | 2.625 | 3.175 | 3.175 | opened
118 | Mikulino 35/10 | 6,3+6,3 | 0.88 | 1.1 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.835 | opened
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.52 | 0.74 | 120 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | opened
120 | Kazimirovo 35/10 | 4+4 | 0.12 | 0.02 | 120 | 0.1 | 0 | 4.2 | 4.1 | 4.1 | opened
121 | Golynki 110/35/6 | 25+25 | 4.58 | 2.91 | 120 | 1.67 | 0 | 26.25 | 24.58 | 24.58 | opened
| Nom. Capacity MV, МVА | 25+25 | 2.75 | 2.75 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.83 | 0.16 | 120 | 1.67 | 0 | 26.25 | 24.58
122 | Belei 35/10 | 2,5+2,5 | 1.61 | 0.75 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | opened
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.15 | 1.45 | 120 | 1.7 | 0 | 6.615 | 4.915 | 4.915 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.39 | 1.39 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.76 | 0.06 | 120 | 1.7 | 0 | 6.615 | 4.915
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.19 | 0.19 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
125 | Safonovo 110/6 | 15+20 | 9.25 | 0.06 | 120 | 9.19 | 0 | 15.75 | 6.56 | 6.56 | opened
126 | Gornaya 110/35/6 | 25+25 | 11.7 | 11.58 | 120 | 0.12 | 0 | 26.25 | 26.13 | 26.13 | opened
| Nom. capacity MV, МVА | 25+25 | 6.91 | 6.91 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 4.79 | 4.67 | 120 | 0.12 | 0 | 26.25 | 26.13
127 | Water intake 35/6 | 6,3+4 | 1.68 | 0.69 | 120 | 0.99 | 0 | 4.2 | 3.21 | 3.21 | opened
128 | Vadino 35/10 | 4+4 | 1.23 | 0 | 120 | 1.23 | 0 | 4.2 | 2.97 | 2.97 | opened
129 | ZSSK 35/6 | 4+4 | 1.61 | 0.75 | 120 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
130 | Yanovo 35/10 | 4+6,3 | 0.27 | 0.05 | 120 | 0.22 | 0 | 4.2 | 3.98 | 3.98 | opened
131 | Kapyrevshchina 35/10 | 4+4 | 1.26 | 0.22 | 120 | 1.04 | 0 | 4.2 | 3.16 | 3.16 | opened
132 | Miropolye 35/10 | 2,5+2,5 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | opened
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 3.34 | 1.34 | 120 | 2 | 0 | 5.88 | 3.88 | 1.88 | opened
| Nom. capacity MV, МVА | 5,6+6,3 | 0.91 | 0.91 |  | 0 | 1 | 5.88 | 4.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.43 | 0.43 | 120 | 2 | 2 | 5.88 | 1.88
134 | Alferovo 35/10 | 2,5+2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened
135 | Kasulino 35/10 | 2,5+2,5 | 0.15 | 0 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.28 | 0.15 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
137 | Glinka 110/35/10 | 10+6,3 | 2 | 0.44 | 120 | 1.56 | 0 | 6.615 | 5.055 | 3.055 | opened
| Nom. capacity MV, МVА | 10+6,3 | 0.33 | 0.33 |  | 0 | 1 | 6.615 | 5.615
| Nom. capacity LV, МVА | 10+6,3 | 1.67 | 0.11 | 120 | 1.56 | 2 | 6.615 | 3.055
138 | Dobromino 35/10 | 2,5+2,5 | 0.24 | 0 | 120 | 0.24 | 0 | 2.625 | 2.385 | 2.385 | opened
139 | Bely kholm 35/10 | 1,6+1,6 | 0.09 | 0 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
140 | Dukhovshchina 110/35/10 | 10+10 | 3.26 | 1.89 | 120 | 1.37 | 0 | 10.5 | 9.13 | 9.13 | opened
| Nom. capacity MV, МVА | 10+10 | 1.63 | 1.63 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.63 | 0.26 | 120 | 1.37 | 0 | 10.5 | 9.13
141 | Zimets 35/10 | 4+4 | 0.3 | 0.06 | 120 | 0.24 | 0 | 4.2 | 3.96 | 3.96 | opened
142 | Beresnevo 35/10 | 1,6+1,6 | 0.3 | 0.01 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
143 | Prechistoe 110/35/10 | 6,3+6,3 | 1.92 | 0.14 | 120 | 1.78 | 0 | 6.615 | 4.835 | 4.835 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.34 | 0 |  | 1.34 | 0 | 6.615 | 5.275
| Nom. capacity LV, МVА | 6,3+6,3 | 0.58 | 0.14 | 120 | 0.44 | 0 | 6.615 | 6.175
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.38 | 0.07 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
145 | Ozyorny 35/10 | 6,3+6,3 | 1.32 | 0.01 | 120 | 1.31 | 0 | 6.615 | 5.305 | 5.305 | opened
146 | Igorevskaya 110/10 | 10+10 | 4.94 | 0 | 120 | 4.94 | 0 | 10.5 | 5.56 | 5.56 | opened
147 | Kanyutino 110/35/10 | 5,6+6,3 | 2.78 | 1.68 | 120 | 1.1 | 0 | 5.88 | 4.78 | 4.78 | opened
| Nom. capacity LV, МVА | 5,6+6,3 | 2.4 | 2.4 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.38 | 0.21 | 120 | 0.17 | 0 | 5.88 | 5.71
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.21 | 0.25 | 120 | 0.96 | 0 | 2.625 | 1.665 | 1.665 | opened
149 | Kholm-Zhirki 35/10 | 2,5+4 | 1.8 | 0.4 | 120 | 1.4 | 0 | 2.625 | 1.225 | 1.225 | opened
150 | Dorogobuzh 1 110/35/10 | 16+16 | 6.74 | 2.85 | 120 | 3.89 | 0 | 16.8 | 12.91 | 12.91 | opened
| Nom. capacity MV, МVА | 16+16 | 2.33 | 2.33 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.41 | 0.52 | 120 | 3.89 | 0 | 16.8 | 12.91
151 | Kaskovo 35/10 | 1,6+4 | 0.78 | 0.09 | 120 | 0.69 | 0 | 1.68 | 0.99 | 0.99 | opened
152 | Usvyatye 35/10 | 2,5+4 | 0.89 | 0 | 120 | 0.89 | 0 | 2.625 | 1.735 | 1.735 | opened
153 | Ushakovo 35/10 | 1,6+2,5 | 0.78 | 0 | 120 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | opened
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.16 | 0.04 | 120 | 0.12 | 0 | 6.615 | 6.495 | 6.495 | opened
156 | Elnya 110/35/10 | 16+16 | 7.26 | 3.03 | 120 | 4.23 | 0 | 16.8 | 12.57 | 12.57 | opened
| Nom. capacity MV, МVА | 16+16 | 2.49 | 2.49 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 4.77 | 0.54 | 10 | 4.23 | 0 | 16.8 | 12.57
157 | Pavlovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened
158 | Sharapovo 35/10 | 4+4 | 0.9 | 1 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
159 | Korobets 35/10 | 2,5+2,5 | 1.05 | 0.17 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
160 | Baltuty 35/10 | 2,5+2,5 | 0.53 | 0 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened
161 | Lapino 110/35/10 | 5,6+5,6 | 1.15 | 0.79 | 120 | 0.36 | 0 | 5.88 | 5.52 | 5.52 | opened
| Nom. capacity MV, МVА | 5,6+5,6 | 0.79 | 0.79 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.36 | 0 | 120 | 0.36 | 0 | 5.88 | 5.52
162 | Mutishche 35/10 | 1,6+2,5 | 0.28 | 0.08 | 120 | 0.2 | 0 | 1.68 | 1.48 | 1.48 | opened
163 | Suetovo 110/35/10 | 6,3+6,3 | 1.91 | 1.56 | 120 | 0.35 | 0 | 6.615 | 6.265 | 6.265 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.98 | 0.98 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.93 | 0.58 | 120 | 0.35 | 0 | 6.615 | 6.265
164 | Pushkino 35/10 | 2,5+2,5 | 0.56 | 0.04 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
165 | Yartsevo 1 110/10 | 40+40 | 13.57 | 5.34 | 120 | 8.23 | 0 | 42 | 33.77 | 33.77 | opened
166 | Yartsevo 2 110/10 | 16+16 | 10.61 | 0.75 | 120 | 9.86 | 0 | 16.8 | 6.94 | 6.94 | opened
167 | Saprykino 110/35/10 | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105 | 6.105 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.91 | 0.4 | 120 | 0.51 | 0 | 6.615 | 6.105
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.19 | 0 | 120 | 2.19 | 0 | 6.615 | 4.425 | 4.425 | opened
169 | Egoryevo 35/10 | 6,3+6,3 | 4.65 | 0 | 120 | 4.65 | 0 | 6.615 | 1.965 | 1.965 | opened
170 | Shalomino 35/10 | 1,6+2,5 | 0.59 | 0.13 | 120 | 0.46 | 0 | 1.68 | 1.22 | 1.22 | opened
171 | Roslavl 110/35/6 | 25+40 | 26.59 | 1.4 | 120 | 25.19 | 0 | 26.25 | 1.06 | 1.06 | opened
| Nom. capacity MV, МVА | 25+40 | 11.79 | 1.4 |  | 10.39 | 0 | 26.25 | 15.86
| Nom. сapacity LV, МVА | 25+40 | 14.8 | 0 | 120 | 14.8 | 0 | 26.25 | 11.45
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.88 | 0 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | opened
173 | Perenka 35/10 | 4+4 | 0.36 | 0 | 120 | 0.36 | 0 | 4.2 | 3.84 | 3.84 | opened
174 | Khoroshevo 35/10 | 2,5+4 | 1.19 | 0 | 120 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened
175 | Lipovka 35/10 | 2,5+2,5 | 0.52 | 0 | 120 | 0.52 | 0 | 2.625 | 2.105 | 2.105 | opened
176 | Kirilly 35/10 | 2,5+2,5 | 0.81 | 0 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened
177 | Desnogorsk 110/35/10 | 25+25 | 17.92 | 3.15 | 120 | 14.77 | 0 | 26.25 | 11.48 | 11.48 | opened
| Nom. capacity MV, МVА | 25+25 | 3.15 | 3.15 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacidty LV, МVА | 25+25 | 14.77 | 0 | 120 | 14.77 | 0 | 26.25 | 11.48
178 | Ekimovichi 35/10 | 4+4 | 2.31 | 0.24 | 120 | 2.07 | 0 | 4.2 | 2.13 | 2.13 | opened
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.18 | 0.07 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened
180 | Kokhany 35/10 | 1,6+1,6 | 0.33 | 0.09 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
181 | Koski 35/10 | 4+4 | 0.49 | 0 | 120 | 0.49 | 0 | 4.2 | 3.71 | 3.71 | opened
182 | Industrialnaya 110/35/6 | 16+16 | 4.43 | 0.7 | 120 | 3.73 | 0 | 16.8 | 13.07 | 4.565 | opened
| Nom. capacity MV, МVА | 16,3+5,3 | 0.7 | 0.7 |  | 0 | 1 | 5.565 | 4.565
| Nom. capacity LV, МVА | 16+10,7 | 3.73 | 0 | 120 | 3.73 | 2 | 11.235 | 5.505
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.88 | 0 | 120 | 0.88 | 0 | 2.625 | 1.745 | 1.745 | opened
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.11 | 0.72 | 120 | 0.39 | 0 | 6.615 | 6.225 | 6.225 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.72 | 0.72 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.39 | 0 | 120 | 0.39 | 0 | 6.615 | 6.225
185 | Bogdanovo 35/10 | 4+4 | 0.54 | 0 | 120 | 0.54 | 0 | 4.2 | 3.66 | 3.66 | opened
186 | Prigorye 110/35/10 | 10+2,5 | 0.89 | 0.48 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | opened
| Nom. capacity MV, МVА | 10+2,5 | 0.48 | 0.48 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.41 | 0 | 120 | 0.41 | 0 | 2.625 | 2.215
187 | Bekhovo 35/10 | 2,5+2,5 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | opened
188 | Pochinok 110/35/10 | 10+16 | 8.99 | 3.63 | 120 | 5.36 | 0 | 10.5 | 5.14 | 5.14 | opened
| Nom. capacidty MV, МVА | 10+16 | 3.55 | 3.55 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.44 | 0.08 | 120 | 5.36 | 0 | 10.5 | 5.14
189 | Divinskaya 35/10 | 4+4 | 1.23 | 0.17 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | opened
190 | Shatalovo 35/10 | 2,5+2,5 | 1.75 | 0 | 120 | 1.75 | 0 | 2.625 | 0.875 | 0.875 | opened
191 | Panskaya 35/10 | 6,3+6,3 | 1.48 | 0 | 120 | 1.48 | 0 | 6.615 | 5.135 | 5.135 | opened
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.28 | 1.44 | 120 | 1.84 | 0 | 6.615 | 4.775 | 4.775 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.99 | 0.99 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.29 | 0.45 | 120 | 1.84 | 0 | 6.615 | 4.775
193 | Belik 35/10 | 2,5+2,5 | 0.22 | 0.33 | 120 | -0.11 | 0 | 2.625 | 2.735 | 2.735 | opened
194 | Pervomayskaya 35/10 | 4+4 | 1.4 | 0 | 120 | 1.4 | 0 | 4.2 | 2.8 | 2.8 | opened
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.84 | 2.07 | 120 | -0.23 | 0 | 6.615 | 6.845 | 6.255 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 1.27 | 1.27 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.57 | 0.21 | 120 | 0.36 | 0 | 6.615 | 6.255
196 | Strigino 35/10 | 2,5+2,5 | 0.4 | 0 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | opened
197 | Komintern 35/10 | 2,5+2,5 | 0.58 | 0 | 120 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
198 | Monastyrshchina 110/35/10 | 10+10 | 4.37 | 1.9 | 120 | 2.47 | 0 | 10.5 | 8.03 | 8.03 | opened
| Nom. capacity MV, МVА | 10+10 | 1.9 | 1.9 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.47 | 0 | 120 | 2.47 | 0 | 10.5 | 8.03
199 | N.Mikhailov 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
200 | Tatarsk 35/10 | 3,2+4 | 0.81 | 0 | 120 | 0.81 | 0 | 3.36 | 2.55 | 2.55 | opened
201 | Turki 35/10 | 1,6+1,6 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | opened
202 | Sozh 35/10 | 4+4 | 0.52 | 0 | 120 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | opened
203 | Khislavichi 110/35/10 | 16+16 | 4.11 | 1.61 | 120 | 2.5 | 0 | 16.8 | 14.3 | 14.3 | opened
| Nom. capacity MV, МVА | 16+16 | 1.43 | 1.43 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.68 | 0.18 | 120 | 2.5 | 0 | 16.8 | 14.3
204 | Gorodishche 35/10 | 1,8+2,5 | 0.82 | 0 | 120 | 0.82 | 0 | 1.89 | 1.07 | 1.07 | opened
205 | Komarovka 35/10 | 4+4 | 0.32 | 0.02 | 120 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
206 | Cherepovo 35/10 | 2,5+2,5 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | opened
207 | Studenets 35/10 | 1,6+2,5 | 0.34 | 0.01 | 120 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
208 | Shumyachi 110/35/10 | 10+10 | 4.8 | 3.36 | 120 | 1.44 | 0 | 10.5 | 9.06 | 9.06 | opened
| Nom. capacity MV, МVА | 10+10 | 2.72 | 2.72 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.08 | 0.64 | 120 | 1.44 | 0 | 10.5 | 9.06
209 | Ershichi 110/35/10 | 10+10 | 2.25 | 0.62 | 120 | 1.63 | 0 | 10.5 | 8.87 | 8.87 | opened
| Nom. capacity MV, МVА | 10+10 | 0.4 | 0.4 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.85 | 0.22 | 120 | 1.63 | 0 | 10.5 | 8.87
210 | Rukhan 35/10 | 2,5+2,5 | 0.45 | 0 | 120 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | opened
211 | Vyazma 1 110/35/10 | 40+40 | 42.21 | 11.83 | 120 | 30.38 | 0 | 42 | 11.62 | 11.62 | opened
| Nom. capacity MV, МVА | 40+40 | 25.68 | 11.27 | 121 | 14.41 | 0 | 42 | 27.59
| Nom. capacity LV, МVА | 40+40 | 16.53 | 0.56 | 122 | 15.97 | 0 | 42 | 26.03
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.99 | 0 | 120 | 2.99 | 0 | 6.615 | 3.625 | 3.625 | opened
213 | Khmelita 35/10 | 1,6+2,5 | 0.49 | 0.11 | 120 | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened
214 | Isakovo 35/10 | 2,5+4 | 0.76 | 0.3 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
215 | Rizskoe 35/10 | 2,5+2,5 | 0.54 | 0.01 | 120 | 0.53 | 0 | 2.625 | 2.095 | 2.095 | opened
216 | Beryozka 35/10 | 4+4 | 0.98 | 0 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | opened
217 | Shimanovo 35/10 | 1,8+4 | 0.49 | 0.32 | 120 | 0.17 | 0 | 1.89 | 1.72 | 1.72 | opened
218 | Kaydakovo 35/10 | 4+4 | 1.1 | 0.2 | 120 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened
219 | Flour mill 35/10 | 10+10 | 6.82 | 0.13 | 120 | 6.69 | 0 | 10.5 | 3.81 | 3.81 | opened
220 | Kikino 35/10 | 2,5+2,5 | 0.58 | 0.41 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
221 | Vyazma 2 110/10 | 16+16 | 15.42 | 0 | 120 | 15.42 | 0 | 16.8 | 1.38 | 1.38 | opened
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.59 | 1.18 | 120 | 1.41 | 0 | 6.615 | 5.205 | 5.205 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.84 | 0.84 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.75 | 0.34 | 120 | 1.41 | 0 | 6.615 | 5.205
223 | Rossiya 110/35/10 | 10+16 | 2.8 | 1.79 | 120 | 1.01 | 0 | 10.5 | 9.49 | 9.49 | opened
| Nom. capacity MV, МVА | 10+16 | 1.47 | 1.47 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 1.33 | 0.32 | 120 | 1.01 | 0 | 10.5 | 9.49
224 | Semlevo 35/10 | 2,5+4 | 0.84 | 0 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
225 | Artyomovo 35/10 | 2,5+2,5 | 0.22 | 0 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened
226 | Gagarin 110/35/10 | 25+25 | 19.92 | 4.78 | 120 | 15.14 | 0 | 26.25 | 11.11 | 11.11 | opened
| Nom. capacity MV, МVА | 25+25 | 6.02 | 3.06 |  | 2.96 | 0 | 26.25 | 23.29
| Nom. capacity LV, МVА | 25+25 | 13.9 | 1.72 | 120 | 12.18 | 0 | 26.25 | 14.07
227 | Rodomanovo 35/10 | 4+4 | 0.76 | 1.18 | 120 | -0.42 | 0 | 4.2 | 4.62 | 4.62 | opened
228 | Klushino 35/10 | 4+4 | 0.82 | 0.57 | 120 | 0.25 | 0 | 4.2 | 3.95 | 3.95 | opened
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
230 | Karmanovo 35/10 | 4+4 | 3.84 | 0.21 | 120 | 3.63 | 0 | 4.2 | 0.57 | 0.57 | opened
231 | Sverchkovo 35/10 | 2,5+2,5 | 1.46 | 0.75 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened
232 | Lesnaya 35/10 | 4+4 | 0.74 | 0 | 120 | 0.74 | 0 | 4.2 | 3.46 | 3.46 | opened
233 | Tesovo 35/10 | 1,6+2,5 | 0.67 | 0.48 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened
234 | Svetotekhnika 110/10 | 16+16 | 3.92 | 0.97 | 120 | 2.95 | 0 | 16.8 | 13.85 | 13.85 | opened
235 | Mishino 110/35/10 | 10+10 | 3.98 | 2.2 | 120 | 1.78 | 0 | 10.5 | 8.72 | 8.72 | opened
| Nom. capacity MV, МVА | 10+10 | 2.44 | 2.44 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.54 | 0.64 | 120 | 0.9 | 0 | 10.5 | 9.6
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.35 | 0.59 | 120 | 0.76 | 0 | 6.615 | 5.855 | 5.855 | opened
237 | Bekrino 35/10 | 2,5+2,5 | 0.55 | 0.09 | 120 | 0.46 | 0 | 2.625 | 2.165 | 2.165 | opened
238 | Trubnaya 110/10 | 25+25 | 6.38 | 1.57 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | opened
239 | Temkino 110/35/10 | 10+10 | 3.88 | 1.3 | 120 | 2.58 | 0 | 10.5 | 7.92 | 7.92 | opened
| Nom. capacity MV, МVА | 10+10 | 1.05 | 1.05 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.83 | 0.25 | 120 | 2.58 | 0 | 10.5 | 7.92
240 | Narytka 35/10 | 2,5+2,5 | 0.15 | 0.05 | 120 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
241 | Novodugino 110/35/10 | 10+10 | 4.6 | 2.48 | 120 | 2.12 | 0 | 10.5 | 8.38 | 8.38 | opened
| Nom. capacity MV, МVА | 10+10 | 2 | 2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.6 | 0.48 | 120 | 2.12 | 0 | 10.5 | 8.38
242 | Vysokoe 35/10 | 1,6+4 | 0.55 | 0.42 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
243 | Khotkovo 35/10 | 4+4 | 0.67 | 0.26 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | opened
244 | Dneprovsk 110/35/10 | 10+10 | 4.66 | 3.47 | 120 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened
| Nom. capacity MV, МVА | 10+10 | 3.31 | 3.31 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.35 | 0.16 | 120 | 1.19 | 0 | 10.5 | 9.31
245 | Lipetsy 35/10 | 2,5+2,5 | 0.33 | 0.75 | 120 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | opened
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.52 | 0.7 | 120 | -0.18 | 0 | 1.68 | 1.86 | 1.86 | opened
247 | Sychevka 110/35/10 | 16+25 | 8.78 | 1.47 | 120 | 7.31 | 0 | 16.8 | 9.49 | 9.49 | opened
| Nom. capacity MV, МVА | 16+25 | 3.5 | 0.7 |  | 2.8 | 0 | 16.8 | 14
| Nom. capacfity LV, МVА | 16+25 | 5.28 | 0.77 | 120 | 4.51 | 0 | 16.8 | 12.29
248 | Sutormino 35/10 | 1,8+4 | 0.56 | 0.06 | 120 | 0.5 | 0 | 1.89 | 1.39 | 1.39 | opened
249 | Karavaevo 35/10 | 4+4 | 1.14 | 0.29 | 120 | 0.85 | 0 | 4.2 | 3.35 | 3.35 | opened
250 | Lukino 35/10 | 4+1,6 | 0.73 | 0.51 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
251 | Subbotniki 110/10 | 6,3+6,3 | 0.66 | 0 | 120 | 0.66 | 0 | 6.615 | 5.955 | 5.955 | opened
252 | Ugra 110/10 | 6,3+6,3 | 2.82 | 0 | 120 | 2.82 | 0 | 6.615 | 3.795 | 3.795 | opened
253 | Znamenka 110/35/10 | 10+10 | 2.52 | 1.35 | 120 | 1.17 | 0 | 10.5 | 9.33 | 9.33 | opened
| Nom. capacity MV, МVА | 10+10 | 1.32 | 1.32 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.2 | 0.03 | 120 | 1.17 | 0 | 10.5 | 9.33
254 | Losmino 35/10 | 2,5+2,5 | 1.14 | 0.4 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | opened
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.1 | 0.43 | 120 | 0.67 | 0 | 6.615 | 5.945 | 5.945 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.42 | 0.42 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.68 | 0.01 | 120 | 0.67 | 0 | 6.615 | 5.945
| Total: | 3150.6 | 566.25
| deficit | [8 empty] | -0.37
| proficit | [8 empty] | 1074.43

## Свод. тек. дефицит май 2010
List of indoor main substations of IDGC of Centre - Smolenskenergo division for Winter loads 2009 (current capacity deficit).
No. | Object of main substation, voltage class, transformer capacity (fixed MVA) |  | Current deficit, MVA | Note
Smolenskenergo
1 | Vasino 35/10 | 2.5 | -0.31 | closed
2 | Mytishino 35/10 | 1.6 | -0.06 | closed
Total current deficit (May 2010) |  |  | -0.37

## Свод. ожид. дефицит май 2010
List of indoor main substations of IDGC of Centre - Smolenskenergo division for expected loads taking into account new capacities on technological connection and other development of the power grid complex
No. | Object of main substation, voltage class, transformer capacity (fixed MVA) |  | Expected deficit, MVA | Note
Smolenskenergo
1 | Vasino 35/10 | 2.5 | #REF! | closed
2 | Avrora 35/10 | 2.5 | #REF! | closed
3 | Mytishino 35/10 | 1.6 | #REF! | closed
4 | Smolensk 1 (FGC) 110/35/6 | 40+40 | #REF! | closed
5 | Ryabtsevo 35/10 | 4+4 | #REF! | closed
6 | Diffuzion 110/6 | 25+25 | #REF! | closed
7 | Zapadnaya 110/6 | 25+16 | #REF! | closed
8 | Kozino 110/35/10 | 10+10 | #REF! | closed
9 | Odintsovo 35/10 | 6,3+6,3 | #REF! | closed
10 | Pechersk 35/6 | 4+4 | #REF! | closed
11 | Chernushki 110/10/6 | 25+25 | #REF! | closed
12 | Yuzhnaya 110/35/6 | 40+40 | #REF! | closed
13 | Zhukovskaya 35/10 | 4+4 | #REF! | closed
14 | Belei 35/10 | 2,5+2,5 | #REF! | closed
15 | Roslavl 110/35/6 | 25+40 | #REF! | closed
16 | Vyazma 1 110/35/10 | 40+40 | #REF! | closed
17 | Flour mill 35/10 | 10+10 | #REF! | closed
18 | Vyazma 2 110/10 | 16+16 | #REF! | closed
19 | Karmanovo 35/10 | 4+4 | #REF! | closed
Total expected deficit (May 2010) |  |  | #REF!