## Смоленскэнерго
Appendix 2
[9 empty] | Table 1 | [11 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | Gerchiki 35/10 | 2.5 | 0.3 | 0.7 | 1 сутки | 0.7 | 0 | 0.7 | 0.4 | 0.4 | open | 1 | Gerchiki 35/10 | 2.5 | 0.4 | 0.7 | 0.7 | 1 сутки | 0 | 0 | 0.7 | 0 | 0 | open
2 | Verkhovye 35/10 | 4 | 0.55 | 1.36 | 1 сутки | 1.36 | 0 | 1.36 | 0.81 | 0.81 | open | 2 | Verkhovye 35/10 | 4 | 0 | 0.55 | 1.36 | 1 сутки | -0.81 | 0 | 1.36 | 0.81 | 0.81 | open
3 | Neykovo 35/10 | 2.5 | 0.22 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.51 | 1.51 | open | 3 | Neykovo 35/10 | 2.5 | 0 | 0.22 | 1.73 | 1 сутки | -1.51 | 0 | 1.73 | 1.51 | 1.51 | open
4 | Merlino 110/35/10 | 6.3 | 0.35 | 0.35 | 1 сутки | 0.35 | 0 | 0.35 | 0 | 0 | open | 4 | Merlino 110/35/10 | 6.3 | 0.43 | 0.78 | 0.78 | 1 сутки | 0 | 0 | 0.78 | 0 | 0 | open
| Nom. capacity MV, МVА | 6.3 | 0.05 | 0.05 | 1 сутки | 0.05 | 0 | 0.05 | 0 |  |  |  | Nom. capacity MV, МVА | 6.3 | 0.03 | 0.08 | 0.08 |  | 0 | 0 | 0.08 | 0
| Nom. capacity LV, МVА | 6.3 | 0.3 | 0.3 | 1 сутки | 0.3 | 0 | 0.3 | 0 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.4 | 0.7 | 0.7 | 1 сутки | 0 | 0 | 0.7 | 0
5 | Belyaevo 35/10 | 1.6 | 0.22 | 2.11 | 1 сутки | 2.11 | 0 | 2.11 | 1.89 | 1.89 | open | 5 | Belyaevo 35/10 | 1.6 | 0 | 0.22 | 2.11 | 1 сутки | -1.89 | 0 | 2.11 | 1.89 | 1.89 | open
6 | Zaozerye 35/10 | 1.6 | 0.15 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.7 | 0.7 | open | 6 | Zaozerye 35/10 | 1.6 | 0 | 0.15 | 0.85 | 1 сутки | -0.7 | 0 | 0.85 | 0.7 | 0.7 | open
7 | Selezni 35/10 | 2.5 | 0.41 | 2.21 | 1 сутки | 2.21 | 0 | 2.21 | 1.8 | 1.8 | open | 7 | Selezni 35/10 | 2.5 | 0 | 0.41 | 2.21 | 1 сутки | -1.8 | 0 | 2.21 | 1.8 | 1.8 | open
8 | Logovo 110/10 | 6.3 | 0.43 | 1.36 | 1 сутки | 1.36 | 0 | 1.36 | 0.93 | 0.93 | open | 8 | Logovo 110/10 | 6.3 | 0 | 0.43 | 1.36 | 1 сутки | -0.93 | 0 | 1.36 | 0.93 | 0.93 | open
9 | Dubrovka 35/10 | 2.5 | 0.43 | 1.36 | 1 сутки | 1.36 | 0 | 1.36 | 0.93 | 0.93 | open | 9 | Dubrovka 35/10 | 2.5 | 0.1 | 0.53 | 1.36 | 1 сутки | -0.83 | 0 | 1.36 | 0.83 | 0.83 | open
10 | Svistovichi 35/10 | 2.5 | 0.17 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.68 | 0.68 | open | 10 | Svistovichi 35/10 | 2.5 | 0 | 0.17 | 0.85 | 1 сутки | -0.68 | 0 | 0.85 | 0.68 | 0.68 | open
11 | Elsha 35/10 | 1.6 | 0.09 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.76 | 0.76 | open | 11 | Elsha 35/10 | 1.6 | 0 | 0.09 | 0.85 | 1 сутки | -0.76 | 0 | 0.85 | 0.76 | 0.76 | open
12 | Sapsho 35/10 | 4 | 0.76 | 2.12 | 1 сутки | 2.12 | 0 | 2.12 | 1.36 | 1.36 | open | 12 | Sapsho 35/10 | 4 | 0.18 | 0.94 | 2.12 | 1 сутки | -1.18 | 0 | 2.12 | 1.18 | 1.18 | open
13 | Divo 110/10 | 2.5 | 0.43 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.42 | 0.42 | open | 13 | Divo 110/10 | 2.5 | 0.23 | 0.66 | 0.85 | 1 сутки | -0.19 | 0 | 0.85 | 0.19 | 0.19 | open
14 | Vachkovo 35/10 | 2.5 | 0.45 | 1.02 | 1 сутки | 1.02 | 0 | 1.02 | 0.57 | 0.57 | open | 14 | Vachkovo 35/10 | 2.5 | 0 | 0.45 | 1.02 | 1 сутки | -0.57 | 0 | 1.02 | 0.57 | 0.57 | open
15 | Zamoshye 35/10 | 2.5 | 0.14 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.54 | 0.54 | open | 15 | Zamoshye 35/10 | 2.5 | 0 | 0.14 | 0.68 | 1 сутки | -0.54 | 0 | 0.68 | 0.54 | 0.54 | open
16 | Loino 35/10 | 2.5 | 0.19 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.66 | 0.66 | open | 16 | Loino 35/10 | 2.5 | 0 | 0.19 | 0.85 | 1 сутки | -0.66 | 0 | 0.85 | 0.66 | 0.66 | open
17 | Rokot 35/10 | 2.5 | 0.22 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | 1.08 | 1.08 | open | 17 | Rokot 35/10 | 2.5 | 0 | 0.22 | 1.3 | 1 сутки | -1.08 | 0 | 1.3 | 1.08 | 1.08 | open
18 | Nikontsy 35/10 | 2.5 | 0.14 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.71 | 0.71 | open | 18 | Nikontsy 35/10 | 2.5 | 0 | 0.14 | 0.85 | 1 сутки | -0.71 | 0 | 0.85 | 0.71 | 0.71 | open
19 | Batishchevo 35/10 | 2.5 | 0.36 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.37 | 1.37 | open | 19 | Batishchevo 35/10 | 2.5 | 0 | 0.36 | 1.73 | 1 сутки | -1.37 | 0 | 1.73 | 1.37 | 1.37 | open
20 | Vasino 35/10 | 2.5 | 1.08 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 1.47 | 1.47 | open | 20 | Vasino 35/10 | 2.5 | 0 | 1.08 | 2.55 | 1 сутки | -1.47 | 0 | 2.55 | 1.47 | 1.47 | open
21 | Bulgakovo 35/10 | 2.5 | 0.36 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.37 | 1.37 | open | 21 | Bulgakovo 35/10 | 2.5 | 0 | 0.36 | 1.73 | 1 сутки | -1.37 | 0 | 1.73 | 1.37 | 1.37 | open
22 | Spas-Ugly 35/10 | 1.6 | 0.18 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.5 | 0.5 | open | 22 | Spas-Ugly 35/10 | 1.6 | 0 | 0.18 | 0.68 | 1 сутки | -0.5 | 0 | 0.68 | 0.5 | 0.5 | open
23 | Tretyakovo 35/10 | 4 | 0.36 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 2.19 | 2.19 | open | 23 | Tretyakovo 35/10 | 4 | 0 | 0.36 | 2.55 | 1 сутки | -2.19 | 0 | 2.55 | 2.19 | 2.19 | open
24 | Velisto 35/10 | 2.5 | 0.14 | 1.3 | 1 сутки | 1.3 | 0 | 1.3 | 1.16 | 1.16 | open | 24 | Velisto 35/10 | 2.5 | 0 | 0.14 | 1.3 | 1 сутки | -1.16 | 0 | 1.3 | 1.16 | 1.16 | open
25 | Baturino 35/10 | 1.6 | 0.14 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.71 | 0.71 | open | 25 | Baturino 35/10 | 1.6 | 0.18 | 0.32 | 0.85 | 1 сутки | -0.53 | 0 | 0.85 | 0.53 | 0.53 | open
26 | Pechatniki 35/10 | 2.5 | 0.72 | 3.46 | 1 сутки | 3.46 | 0 | 3.46 | 2.74 | 2.74 | open | 26 | Pechatniki 35/10 | 2.5 | 0 | 0.72 | 3.46 | 1 сутки | -2.74 | 0 | 3.46 | 2.74 | 2.74 | open
27 | Garistovo 35/10 | 1.6 | 0.1 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.75 | 0.75 | open | 27 | Garistovo 35/10 | 1.6 | 0 | 0.1 | 0.85 | 1 сутки | -0.75 | 0 | 0.85 | 0.75 | 0.75 | open
28 | Bezzaboty 35/10 | 2.5 | 0.14 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.59 | 1.59 | open | 28 | Bezzaboty 35/10 | 2.5 | 0 | 0.14 | 1.73 | 1 сутки | -1.59 | 0 | 1.73 | 1.59 | 1.59 | open
29 | Vysokoe 35/10 | 2.5 | 0.14 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 2.41 | 2.41 | open | 29 | Vysokoe 35/10 | 2.5 | 0 | 0.14 | 2.55 | 1 сутки | -2.41 | 0 | 2.55 | 2.41 | 2.41 | open
30 | Zaytsevo 35/10 | 1.6 | 0.38 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.47 | 0.47 | open | 30 | Zaytsevo 35/10 | 1.6 | 0 | 0.38 | 0.85 | 1 сутки | -0.47 | 0 | 0.85 | 0.47 | 0.47 | open
31 | Saveevo 35/10 | 2.5 | 0.33 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.52 | 0.52 | open | 31 | Saveevo 35/10 | 2.5 | 0 | 0.33 | 0.85 | 1 сутки | -0.52 | 0 | 0.85 | 0.52 | 0.52 | open
32 | Gorenovo 35/10 | 1.6 | 0.21 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 1.47 | 1.47 | open | 32 | Gorenovo 35/10 | 1.6 | 0 | 0.21 | 1.68 | 1 сутки | -1.47 | 0 | 1.68 | 1.47 | 1.47 | open
33 | Shpunty 35/10 | 2.5 | 0.36 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.49 | 0.49 | open | 33 | Shpunty 35/10 | 2.5 | 0.42 | 0.78 | 0.85 | 1 сутки | -0.07 | 0 | 0.85 | 0.07 | 0.07 | open
34 | Kadino 35/10 | 2.5 | 0.14 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.59 | 1.59 | open | 34 | Kadino 35/10 | 2.5 | 0 | 0.14 | 1.73 | 1 сутки | -1.59 | 0 | 1.73 | 1.59 | 1.59 | open
35 | Стегримово 35/10 | 2.5 | 0.12 | 2.89 | 1 сутки | 2.89 | 0 | 2.89 | 2.77 | 2.77 | open | 35 | Стегримово 35/10 | 2.5 | 0 | 0.12 | 2.89 | 1 сутки | -2.77 | 0 | 2.89 | 2.77 | 2.77 | open
36 | Zhukovo 35/10 | 2.5 | 0.26 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.47 | 1.47 | open | 36 | Zhukovo 35/10 | 2.5 | 0 | 0.26 | 1.73 | 1 сутки | -1.47 | 0 | 1.73 | 1.47 | 1.47 | open
37 | Mikshino 35/10 | 2.5 | 0.11 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.62 | 1.62 | open | 37 | Mikshino 35/10 | 2.5 | 0 | 0.11 | 1.73 | 1 сутки | -1.62 | 0 | 1.73 | 1.62 | 1.62 | open
38 | Petrovichi 35/10 | 2.5 | 0.16 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 2.39 | 2.39 | open | 38 | Petrovichi 35/10 | 2.5 | 0 | 0.16 | 2.55 | 1 сутки | -2.39 | 0 | 2.55 | 2.39 | 2.39 | open
39 | Mikulichi 35/10 | 2.5 | 0.35 | 2.625 | 1 сутки | 2.625 | 0 | 2.625 | 2.275 | 2.275 | open | 39 | Mikulichi 35/10 | 2.5 | 0.07 | 0.42 | 2.625 | 1 сутки | -2.205 | 0 | 2.625 | 2.205 | 2.205 | open
40 | Nedeykovichi 35/10 | 2.5 | 0.24 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.61 | 0.61 | open | 40 | Nedeykovichi 35/10 | 2.5 | 0 | 0.24 | 0.85 | 1 сутки | -0.61 | 0 | 0.85 | 0.61 | 0.61 | open
41 | Posyolki 110/35/10 | 6.3 | 0.48 | 0.94 | 1 сутки | 0.94 | 0 | 0.94 | 0.46 | 0.46 | open | 41 | Posyolki 110/35/10 | 6.3 | 0 | 0.48 | 0.94 | 1 сутки | -0.46 | 0 | 0.94 | 0.46 | 0.46 | open
42 | Kuzmichi 35/10 | 2.5 | 0.21 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.52 | 1.52 | open | 42 | Kuzmichi 35/10 | 2.5 | 0 | 0.21 | 1.73 | 1 сутки | -1.52 | 0 | 1.73 | 1.52 | 1.52 | open
43 | Maksheevo 110/10 | 6.3 | 0.53 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 2.02 | 2.02 | open | 43 | Maksheevo 110/10 | 6.3 | 0 | 0.53 | 2.55 | 1 сутки | -2.02 | 0 | 2.55 | 2.02 | 2.02 | open
44 | Putkovo 35/10 | 1.8 | 0.22 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.63 | 0.63 | open | 44 | Putkovo 35/10 | 1.8 | 0.06 | 0.28 | 0.85 | 1 сутки | -0.57 | 0 | 0.85 | 0.57 | 0.57 | open
45 | Uspenskoe 35/10 | 2.5 | 0.45 | 2.55 | 1 сутки | 2.55 | 0 | 2.55 | 2.1 | 2.1 | open | 45 | Uspenskoe 35/10 | 2.5 | 0.15 | 0.6 | 2.55 | 1 сутки | -1.95 | 0 | 2.55 | 1.95 | 1.95 | open
46 | Kalpita 35/10 | 1.6 | 0.05 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.8 | 0.8 | open | 46 | Kalpita 35/10 | 1.6 | 0 | 0.05 | 0.85 | 1 сутки | -0.8 | 0 | 0.85 | 0.8 | 0.8 | open
47 | Kasnya 110/10 | 2.5 | 0.29 | 2.62 | 1 сутки | 2.62 | 0 | 2.62 | 2.33 | 2.33 | open | 47 | Kasnya 110/10 | 2.5 | 0 | 0.29 | 2.62 | 1 сутки | -2.33 | 0 | 2.62 | 2.33 | 2.33 | open
48 | Akatovo 35/10 | 1.6 | 1.06 | 1.68 | 1 сутки | 1.68 | 0 | 1.68 | 0.62 | 0.62 | open | 48 | Akatovo 35/10 | 1.6 | 1.62 | 2.68 | 1.68 | 1 сутки | 1 | 0 | 1.68 | -1 | -1 | closed
49 | Gorki 35/10 | 1.6 | 0.19 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.49 | 0.49 | open | 49 | Gorki 35/10 | 1.6 | 0 | 0.19 | 0.68 | 1 сутки | -0.49 | 0 | 0.68 | 0.49 | 0.49 | open
50 | Druzhba 35/10 | 2.5 | 0.79 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.06 | 0.06 | open | 50 | Druzhba 35/10 | 2.5 | 0 | 0.35 | 0.85 | 1 сутки | -0.5 | 0 | 0.85 | 0.5 | 0.5 | open
51 | NS-21 110/10 | 16 | 0 | 0 | 1 сутки | 0 | 0 | 0 | 0 | 0 | open | 51 | NS-21 110/10 | 16 | 0 | 0 | 0 | 1 сутки | 0 | 0 | 0 | 0 | 0 | open
52 | NS-22 110/35/10 | 25 | 2.97 | 2.97 | 1 сутки | 2.97 | 0 | 2.97 | 0 | 0 | open | 52 | NS-22 110/35/10 | 25 | 1.81 | 4.78 | 4.78 | 1 сутки | 0 | 0 | 4.78 | 0 | 0 | open
| Nom. capacity MV, МVА | 25 | 2.97 | 2.97 | 1 сутки | 2.97 | 0 | 2.97 | 0 |  |  |  | Nom. capacity MV, МVА | 25 | 1.81 | 4.78 | 4.78 | 1 сутки | 0 | 0 | 4.78 | 0
| Nom. capacity LV, МVА | 25 | 0 | 0 | 1 сутки | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity LV, МVА | 25 | 0 | 0 | 0 | 1 сутки | 0 | 0 | 0 | 0
53 | Shuyskoe 35/10 | 2.5 | 0.44 | 2.62 | 1 сутки | 2.62 | 0 | 2.62 | 2.18 | 2.18 | open | 53 | Shuyskoe 35/10 | 2.5 | 0.05 | 0.49 | 2.62 | 1 сутки | -2.13 | 0 | 2.62 | 2.13 | 2.13 | open
54 | Torbeevo 110/10 | 6.3 | 0.3 | 2.89 | 1 сутки | 2.89 | 0 | 2.89 | 2.59 | 2.59 | open | 54 | Torbeevo 110/10 | 6.3 | 0.15 | 0.45 | 2.89 | 1 сутки | -2.44 | 0 | 2.89 | 2.44 | 2.44 | open
55 | Leuzdovo 35/10 | 1 | 0.14 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.54 | 0.54 | open | 55 | Leuzdovo 35/10 | 1 | 0.3 | 0.44 | 0.68 | 1 сутки | -0.24 | 0 | 0.68 | 0.24 | 0.24 | open
56 | Maltsevo 35/10 | 2.5 | 0.17 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.56 | 1.56 | open | 56 | Maltsevo 35/10 | 2.5 | 0.01 | 0.18 | 1.73 | 1 сутки | -1.55 | 0 | 1.73 | 1.55 | 1.55 | open
57 | Avrora 35/10 | 2.5 | 0.26 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.42 | 0.42 | open | 57 | Avrora 35/10 | 2.5 | 3.91 | 4.17 | 0.68 | 1 сутки | 3.49 | 0 | 0.68 | -3.49 | -3.49 | closed
58 | Bekhteevo 35/10 | 2.5 | 0.13 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.55 | 0.55 | open | 58 | Bekhteevo 35/10 | 2.5 | 0.07 | 0.2 | 0.68 | 1 сутки | -0.48 | 0 | 0.68 | 0.48 | 0.48 | open
59 | Sereda 35/10 | 2.5 | 0.31 | 0.68 | 1 сутки | 0.68 | 0 | 0.68 | 0.37 | 0.37 | open | 59 | Sereda 35/10 | 2.5 | 0 | 0.31 | 0.68 | 1 сутки | -0.37 | 0 | 0.68 | 0.37 | 0.37 | open
60 | Mikhali 35/10 | 2.5 | 0.08 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.77 | 0.77 | open | 60 | Mikhali 35/10 | 2.5 | 0 | 0.08 | 0.85 | 1 сутки | -0.77 | 0 | 0.85 | 0.77 | 0.77 | open
61 | Mytishino 35/10 | 1.6 | 0.06 | 0 | 1 сутки | 0 | 0 | 0 | -0.06 | -0.06 | closed | 61 | Mytishino 35/10 | 1.6 | 0 | 0.06 | 0 | 1 сутки | 0.06 | 0 | 0 | -0.06 | -0.06 | closed
62 | Zakharyevskoe 35/10 | 1.6 | 0.04 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.81 | 0.81 | open | 62 | Zakharyevskoe 35/10 | 1.6 | 0 | 0.04 | 0.85 | 1 сутки | -0.81 | 0 | 0.85 | 0.81 | 0.81 | open
63 | Kholm 35/10 | 1.6 | 0.05 | 0.85 | 1 сутки | 0.85 | 0 | 0.85 | 0.8 | 0.8 | open | 63 | Kholm 35/10 | 1.6 | 0 | 0.05 | 0.85 | 1 сутки | -0.8 | 0 | 0.85 | 0.8 | 0.8 | open
64 | Baskakovka 35/10 | 4 | 0.24 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.49 | 1.49 | open | 64 | Baskakovka 35/10 | 4 | 0 | 0.24 | 1.73 | 1 сутки | -1.49 | 0 | 1.73 | 1.49 | 1.49 | open
65 | Ekimtsevo 110/10 | 2.5 | 0.25 | 1.73 | 1 сутки | 1.73 | 0 | 1.73 | 1.48 | 1.48 | open | 65 | Ekimtsevo 110/10 | 2.5 | 0 | 0.25 | 1.73 | 1 сутки | -1.48 | 0 | 1.73 | 1.48 | 1.48 | open
Two-transformer substations | [11 empty] | 1: Two-transformer substations
66 | Smolensk 1 (FGC) 110/35/6 | 40+40 | 35.1 | 4.35 | 120 | 30.75 | 0 | 42 | 11.25 | 11.25 | open | 66 | Smolensk 1 (FGC) 110/35/6 | 40+40 | 21.49 | 56.59 | 13.04 | 120 | 43.55 | 0 | 42 | -1.55 | -1.55 | closed
| Nom. capacity MV, МVА | 40+40 | 2.43 | 2.43 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, МVА | 40+40 | 8.69 | 11.12 | 11.12 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 32.67 | 1.92 | 120 | 30.75 | 0 | 42 | 11.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 12.8 | 45.47 | 1.92 | 120 | 43.55 | 0 | 42 | -1.55
67 | Water intake 35/6 | 4+4 | 2.18 | 1.2 | 120 | 0.98 | 0 | 4.2 | 3.22 | 3.22 | open | 67 | Water intake 35/6 | 4+4 | 5.73 | 7.91 | 1.2 | 120 | 6.71 | 0 | 4.2 | -2.51 | -2.51 | closed
68 | Tychinino 35/10 | 4+4 | 1.06 | 0.91 | 120 | 0.15 | 0 | 4.2 | 4.05 | 4.05 | open | 68 | Tychinino 35/10 | 4+4 | 0.25 | 1.31 | 0.91 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open
69 | Ryabtsevo 35/10 | 4+4 | 3.29 | 0 | 120 | 3.29 | 0 | 4.2 | 0.91 | 0.91 | open | 69 | Ryabtsevo 35/10 | 4+4 | 2.72 | 6.01 | 0 | 120 | 6.01 | 0 | 4.2 | -1.81 | -1.81 | closed
70 | Smolensk 2 110/6 | 40+40 | 18.45 | 6.41 | 120 | 12.04 | 0 | 42 | 29.96 | 29.96 | open | 70 | Smolensk 2 110/6 | 40+40 | 3.01 | 21.46 | 6.41 | 120 | 15.05 | 0 | 42 | 26.95 | 26.95 | open
71 | Vostochnaya 110/6 | 25+16 | 8.22 | 0 | 120 | 8.22 | 0 | 16.8 | 8.58 | 8.58 | open | 71 | Vostochnaya 110/6 | 25+16 | 5.35 | 13.57 | 0 | 120 | 13.57 | 0 | 16.8 | 3.23 | 3.23 | open
72 | Diffuzion 110/6 | 25+25 | 14.7 | 1.06 | 120 | 13.64 | 0 | 26.25 | 12.61 | 12.61 | open | 72 | Diffuzion 110/6 | 25+25 | 18.73 | 33.43 | 1.06 | 120 | 32.37 | 0 | 26.25 | -6.12 | -6.12 | closed
73 | Zavodskaya 110/35/10 | 16+16 | 10.63 | 13.03 | 120 | -2.4 | 0 | 16.8 | 19.2 | 16.8 | open | 73 | Zavodskaya 110/35/10 | 16+16 | 13.3 | 23.93 | 16.72 | 120 | 7.21 | 0 | 16.8 | 9.59 | 9.59 | open
| Nom. capacity MV, МVА | 16+16 | 7.38 | 7.38 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 3.69 | 11.07 | 11.07 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 3.25 | 5.65 | 120 | -2.4 | 0 | 16.8 | 19.2 |  |  |  | Nom. capacity LV, МVА | 16+16 | 9.61 | 12.86 | 5.65 | 120 | 7.21 | 0 | 16.8 | 9.59
74 | Yasennaya 35/6 | 10+10 | 8.82 | 0 | 120 | 8.82 | 0 | 10.5 | 1.68 | 1.68 | open | 74 | Yasennaya 35/6 | 10+10 | 0.99 | 9.81 | 0 | 120 | 9.81 | 0 | 10.5 | 0.69 | 0.69 | open
75 | Gnezodovo 35/6 | 7,5+7,5 | 5.89 | 0.42 | 120 | 5.47 | 0 | 7.875 | 2.405 | 2.405 | open | 75 | Gnezodovo 35/6 | 7,5+7,5 | 2.69 | 8.58 | 0.42 | 120 | 8.16 | 0 | 7.875 | -0.285 | -0.285 | closed
76 | Zapadnaya 110/6 | 25+16 | 13.4 | 0.63 | 120 | 12.77 | 0 | 16.8 | 4.03 | 4.03 | open | 76 | Zapadnaya 110/6 | 25+16 | 7.48 | 20.88 | 0.63 | 120 | 20.25 | 0 | 16.8 | -3.45 | -3.45 | closed
77 | Katyn 2 110/35/10 | 10+16 | 3.69 | 1.44 | 120 | 2.25 | 0 | 10.5 | 8.25 | 8.25 | open | 77 | Katyn 2 110/35/10 | 10+16 | 9.88 | 13.57 | 6.19 | 120 | 7.38 | 0 | 10.5 | 3.12 | 3.12 | open
| Nom. capacity MV, МVА | 10+16 | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 4.75 | 6.19 | 6.19 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 2.25 | 0 | 120 | 2.25 | 0 | 10.5 | 8.25 |  |  |  | Nom. capacity LV, МVА | 10+16 | 5.13 | 7.38 | 0 | 120 | 7.38 | 0 | 10.5 | 3.12
78 | Katyn 1 35/10 | 4+4 | 1.69 | 0.05 | 120 | 1.64 | 0 | 4.2 | 2.56 | 2.56 | open | 78 | Katyn 1 35/10 | 4+4 | 1.12 | 2.81 | 0.05 | 120 | 2.76 | 0 | 4.2 | 1.44 | 1.44 | open
79 | Lubnya 35/10 | 4+4 | 1.2 | 0.13 | 120 | 1.07 | 0 | 4.2 | 3.13 | 3.13 | open | 79 | Lubnya 35/10 | 4+4 | 3.12 | 4.32 | 0.13 | 120 | 4.19 | 0 | 4.2 | 0.01 | 0.01 | open
80 | Kozino 110/35/10 | 10+10 | 10.41 | 6.5 | 120 | 3.91 | 0 | 10.5 | 6.59 | 6.59 | open | 80 | Kozino 110/35/10 | 10+10 | 14.47 | 24.88 | 1.83 | 120 | 23.05 | 0 | 10.5 | -12.55 | -12.55 | closed
| Nom. capacity MV, МVА | 10+10 | 6.49 | 6.49 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 6.71 | 13.2 | 1.82 |  | 11.38 | 0 | 10.5 | -0.88
| Nom. capacity LV, МVА | 10+10 | 3.92 | 0.01 | 120 | 3.91 | 0 | 10.5 | 6.59 |  |  |  | Nom. capacity LV, МVА | 10+10 | 7.76 | 11.68 | 0.01 | 120 | 11.67 | 0 | 10.5 | -1.17
81 | Odintsovo 35/10 | 6,3+6,3 | 5.97 | 2.15 | 120 | 3.82 | 0 | 6.615 | 2.795 | 2.795 | open | 81 | Odintsovo 35/10 | 6,3+6,3 | 5.41 | 11.38 | 2.15 | 120 | 9.23 | 0 | 6.615 | -2.615 | -2.615 | closed
82 | Trudilovo 35/10 | 2,5+2,5 | 1.1 | 0.08 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | open | 82 | Trudilovo 35/10 | 2,5+2,5 | 0.94 | 2.04 | 0.08 | 120 | 1.96 | 0 | 2.625 | 0.665 | 0.665 | open
83 | KS-3 SSNo.2 110/10 | 40+40 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | open | 83 | KS-3 SSNo.2 110/10 | 40+40 | 0 | 0.98 | 0 |  | 0.98 | 0 | 42 | 41.02 | 41.02 | open
84 | Pronino 110/35/6 | 10+10 | 6.31 | 4.62 | 120 | 1.69 | 0 | 10.5 | 8.81 | 8.81 | open | 84 | Pronino 110/35/6 | 10+10 | 5.34 | 11.65 | 9 | 120 | 2.65 | 0 | 10.5 | 7.85 | 7.85 | open
| Nom. capacity MV, МVА | 10+10 | 3.43 | 3.43 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 4.38 | 7.81 | 7.81 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.88 | 1.19 | 120 | 1.69 | 0 | 10.5 | 8.81 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.96 | 3.84 | 1.19 | 120 | 2.65 | 0 | 10.5 | 7.85
85 | Olsha 35/10 | 2,5+2,5 | 1.06 | 0 | 120 | 1.06 | 0 | 2.625 | 1.565 | 1.565 | open | 85 | Olsha 35/10 | 2,5+2,5 | 0.76 | 1.82 | 0 | 120 | 1.82 | 0 | 2.625 | 0.805 | 0.805 | open
86 | Krasny bor 35/6 | 4+4 | 3.08 | 0 | 120 | 3.08 | 0 | 4.2 | 1.12 | 1.12 | open | 86 | Krasny bor 35/6 | 4+4 | 3.62 | 6.7 | 0 | 120 | 6.7 | 0 | 4.2 | -2.5 | -2.5 | closed
87 | Severnaya 110/35/6 | 25+25 | 19.98 | 10.5 | 120 | 9.48 | 0 | 26.25 | 16.77 | 16.77 | open | 87 | Severnaya 110/35/6 | 25+25 | 8.94 | 28.92 | 7.7 | 120 | 21.22 | 0 | 26.25 | 5.03 | 5.03 | open
| Nom. capacity MV, МVА | 25+25 | 7.91 | 7.91 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.11 | 5.11 | 5.11 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 12.07 | 2.59 | 120 | 9.48 | 0 | 26.25 | 16.77 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.83 | 15.9 | 2.59 | 120 | 13.31 | 0 | 26.25 | 12.94
88 | Peсhersk 35/6 | 4+4 | 3.32 | 0.34 | 120 | 2.98 | 0 | 4.2 | 1.22 | 1.22 | open | 88 | Peсhersk 35/6 | 4+4 | 3.74 | 7.06 | 0.34 | 120 | 6.72 | 0 | 4.2 | -2.52 | -2.52 | closed
89 | Kolodnya 35/6 | 6,3+4 | 3.01 | 0 | 120 | 3.01 | 0 | 4.2 | 1.19 | 1.19 | open | 89 | Kolodnya 35/6 | 6,3+4 | 1.35 | 4.36 | 0 | 120 | 4.36 | 0 | 4.2 | -0.16 | -0.16 | closed
90 | Tsentralnaya 110/10/6 | 25+25 | 19.2 | 7.75 | 120 | 11.45 | 0 | 26.25 | 14.8 | 14.8 | open | 90 | Tsentralnaya 110/10/6 | 25+25 | 12.36 | 31.56 | 8.43 | 120 | 23.13 | 0 | 26.25 | 3.12 | 3.12 | open
| Nom. capacity MV, МVА | 25+25 | 1.99 | 1.99 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 9.54 | 11.53 | 3 |  | 8.53 | 0 | 26.25 | 17.72
| Nom. capacity LV, МVА | 25+25 | 17.21 | 5.76 | 120 | 11.45 | 0 | 26.25 | 14.8 |  |  |  | Nom. capacity LV, МVА | 25+25 | 2.82 | 20.03 | 5.43 | 120 | 14.6 | 0 | 26.25 | 11.65
91 | Chernushki 110/10/6 | 25+25 | 20.97 | 2.12 | 120 | 18.85 | 0 | 26.25 | 7.4 | 7.4 | open | 91 | Chernushki 110/10/6 | 25+25 | 12.6 | 33.57 | 2.12 | 120 | 31.45 | 0 | 26.25 | -5.2 | -5.2 | closed
| Nom. capacity MV, МVА | 25+25 | 8.1 | 0 |  | 8.1 | 0 | 26.25 | 18.15 |  |  |  | Nom. capacity MV, МVА | 25+25 | 5.92 | 14.02 | 0 |  | 14.02 | 0 | 26.25 | 12.23
| Nom. Capacity LV, МVА | 25+25 | 12.87 | 2.12 | 120 | 10.75 | 0 | 26.25 | 15.5 |  |  |  | Nom. Capacity LV, МVА | 25+25 | 6.68 | 19.55 | 2.12 | 120 | 17.43 | 0 | 26.25 | 8.82
92 | Yuzhnaya 110/35/6 | 40+40 | 36.1 | 15.48 | 120 | 20.62 | 0 | 42 | 21.38 | 21.38 | open | 92 | Yuzhnaya 110/35/6 | 40+40 | 24.86 | 60.96 | 19.55 | 120 | 41.41 | 0 | 42 | 0.59 | 0.59 | open
| Nom. capacity MV, МVА | 40+40 | 9.76 | 9.76 |  | 0 | 0 | 42 | 42 |  |  |  | Nom. capacity MV, МVА | 40+40 | 4.07 | 13.83 | 13.83 |  | 0 | 0 | 42 | 42
| Nom. capacity LV, МVА | 40+40 | 26.34 | 5.72 | 120 | 20.62 | 0 | 42 | 21.38 |  |  |  | Nom. capacity LV, МVА | 40+40 | 20.79 | 47.13 | 5.72 | 120 | 41.41 | 0 | 42 | 0.59
93 | Karyernaya 110/35/6 | 16+16 | 5.7 | 5.13 | 120 | 0.57 | 0 | 16.8 | 16.23 | 16.23 | open | 93 | Karyernaya 110/35/6 | 16+16 | 5.85 | 11.55 | 8.65 | 120 | 2.9 | 0 | 16.8 | 13.9 | 13.9 | open
| Nom. capacity MV, МВА | 16+16 | 5.13 | 5.13 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МВА | 16+16 | 3.52 | 8.65 | 8.65 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 0.57 | 0 | 120 | 0.57 | 0 | 16.8 | 16.23 |  |  |  | Nom. capacity LV, МVА | 16+16 | 2.33 | 2.9 | 0 | 120 | 2.9 | 0 | 16.8 | 13.9
94 | Koshchino 35/10 | 4+4 | 0.55 | 0.11 | 120 | 0.44 | 0 | 4.2 | 3.76 | 3.76 | open | 94 | Koshchino 35/10 | 4+4 | 0.58 | 1.13 | 0.11 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | open
95 | Kommunar 35/10 | 2,5+2,5 | 0.44 | 0.03 | 120 | 0.41 | 0 | 2.625 | 2.215 | 2.215 | open | 95 | Kommunar 35/10 | 2,5+2,5 | 0.13 | 0.57 | 0.03 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open
96 | Kasplya 110/35/10 | 10+10 | 3.6 | 3.33 | 120 | 0.27 | 0 | 10.5 | 10.23 | 10.23 | open | 96 | Kasplya 110/35/10 | 10+10 | 6.77 | 10.37 | 9.77 | 120 | 0.6 | 0 | 10.5 | 9.9 | 9.9 | open
| Nom. capacity MV, МVА | 10+10 | 2.47 | 2.47 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 6.44 | 8.91 | 8.91 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.13 | 0.86 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.33 | 1.46 | 0.86 | 120 | 0.6 | 0 | 10.5 | 9.9
97 | Apolye 35/10 | 2,5+2,5 | 0.71 | 0.17 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open | 97 | Apolye 35/10 | 2,5+2,5 | 0.02 | 0.73 | 0.17 | 120 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | open
98 | Zhukovskaya 35/10 | 4+4 | 2.01 | 0.19 | 120 | 1.82 | 0 | 4.2 | 2.38 | 2.38 | open | 98 | Zhukovskaya 35/10 | 4+4 | 5.6 | 7.61 | 0.19 | 120 | 7.42 | 0 | 4.2 | -3.22 | -3.22 | closed
99 | Mazaltsevo 110/35/10 | 10+10 | 6.01 | 5.6 | 120 | 0.41 | 0 | 10.5 | 10.09 | 10.09 | open | 99 | Mazaltsevo 110/35/10 | 10+10 | 9.41 | 15.42 | 14.97 | 120 | 0.45 | 0 | 10.5 | 10.05 | 10.05 | open
| Nom. capacity MV, МVА | 10+10 | 5.34 | 5.34 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 9.37 | 14.71 | 14.71 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.67 | 0.26 | 120 | 0.41 | 0 | 10.5 | 10.09 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.04 | 0.71 | 0.26 | 120 | 0.45 | 0 | 10.5 | 10.05
100 | Petrishchevo 35/10 | 1,6+2,5 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | open | 100 | Petrishchevo 35/10 | 1,6+2,5 | 0 | 0.24 | 0.01 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | open
101 | Krasny 110/35/10 | 10+10 | 3.52 | 1.06 | 120 | 2.46 | 0 | 10.5 | 8.04 | 8.04 | open | 101 | Krasny 110/35/10 | 10+10 | 1.55 | 5.07 | 1.95 | 120 | 3.12 | 0 | 10.5 | 7.38 | 7.38 | open
| Nom. capacity MV, МVА | 10+10 | 0.6 | 0.6 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.89 | 1.49 | 1.49 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.92 | 0.46 | 120 | 2.46 | 0 | 10.5 | 8.04 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.66 | 3.58 | 0.46 | 120 | 3.12 | 0 | 10.5 | 7.38
102 | Voloelovo 35/10 | 2,5+2,5 | 0.33 | 0.01 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | open | 102 | Voloelovo 35/10 | 2,5+2,5 | 0.02 | 0.35 | 0.01 | 120 | 0.34 | 0 | 2.625 | 2.285 | 2.285 | open
103 | Kryukovo 35/10 | 2,5+2,5 | 0.12 | 0.26 | 120 | -0.14 | 0 | 2.625 | 2.765 | 2.765 | open | 103 | Kryukovo 35/10 | 2,5+2,5 | 0.4 | 0.52 | 0.26 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open
104 | Miganovo 35/10 | 2,5+2,5 | 1.51 | 0.49 | 120 | 1.02 | 0 | 2.625 | 1.605 | 1.605 | open | 104 | Miganovo 35/10 | 2,5+2,5 | 0.47 | 1.98 | 0.49 | 120 | 1.49 | 0 | 2.625 | 1.135 | 1.135 | open
105 | Velizh 110/35/10 | 10+10 | 5.7 | 1.59 | 120 | 4.11 | 0 | 10.5 | 6.39 | 6.39 | open | 105 | Velizh 110/35/10 | 10+10 | 2.2 | 7.9 | 1.89 | 120 | 6.01 | 0 | 10.5 | 4.49 | 4.49 | open
| Nom. capacity MV, МVА | 10+10 | 0.92 | 0.92 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.3 | 1.22 | 1.22 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.78 | 0.67 | 120 | 4.11 | 0 | 10.5 | 6.39 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.9 | 6.68 | 0.67 | 120 | 6.01 | 0 | 10.5 | 4.49
106 | Chepli 35/10 | 2,5+2,5 | 0.37 | 0.09 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open | 106 | Chepli 35/10 | 2,5+2,5 | 0 | 0.37 | 0.09 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open
107 | Demidov 110/35/10 | 10+16 | 5.78 | 1.47 | 120 | 4.31 | 0 | 10.5 | 6.19 | 6.19 | open | 107 | Demidov 110/35/10 | 10+16 | 2.1 | 7.88 | 1.74 | 120 | 6.14 | 0 | 10.5 | 4.36 | 4.36 | open
| Nom. capacity MV, МVА | 10+16 | 1.29 | 1.29 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.27 | 1.56 | 1.56 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 4.49 | 0.18 | 120 | 4.31 | 0 | 10.5 | 6.19 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.83 | 6.32 | 0.18 | 120 | 6.14 | 0 | 10.5 | 4.36
108 | Staroe selo 35/10 | 2,5+2,5 | 0.4 | 0.17 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | open | 108 | Staroe selo 35/10 | 2,5+2,5 | 0 | 0.4 | 0.17 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | open
109 | Zakrutye 35/10 | 2,5+2,5 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open | 109 | Zakrutye 35/10 | 2,5+2,5 | 0 | 0.36 | 0 | 120 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | open
110 | Zaborye 35/10 | 1,6+2,5 | 0.39 | 0.21 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open | 110 | Zaborye 35/10 | 1,6+2,5 | 0 | 0.39 | 0.21 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | open
111 | Mikhailovskoe 110/35/10 | 10+10 | 2.35 | 1.24 | 120 | 1.11 | 0 | 10.5 | 9.39 | 9.39 | open | 111 | Mikhailovskoe 110/35/10 | 10+10 | 0.6 | 2.95 | 1.42 | 120 | 1.53 | 0 | 10.5 | 8.97 | 8.97 | open
| Nom. capacity MV, МVА | 10+10 | 0.82 | 0.82 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.18 | 1 | 1 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.53 | 0.42 | 120 | 1.11 | 0 | 10.5 | 9.39 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.32 | 1.85 | 0.42 | 120 | 1.43 | 0 | 10.5 | 9.07
112 | Kardymovo 110/35/10 | 10+16 | 5.84 | 3.24 | 120 | 2.6 | 0 | 10.5 | 7.9 | 7.9 | open | 112 | Kardymovo 110/35/10 | 10+16 | 9.56 | 15.4 | 5.44 | 120 | 9.96 | 0 | 10.5 | 0.54 | 0.54 | open
| Nom. capacity MV, МVА | 10+16 | 2.62 | 2.62 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 2.2 | 4.82 | 4.82 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 3.22 | 0.62 | 120 | 2.6 | 0 | 10.5 | 7.9 |  |  |  | Nom. capacity LV, МVА | 10+16 | 7.36 | 10.58 | 0.62 | 120 | 9.96 | 0 | 10.5 | 0.54
113 | Sinkovo 35/6 | 4+2,5 | 1.54 | 0.16 | 120 | 1.38 | 0 | 2.625 | 1.245 | 1.245 | open | 113 | Sinkovo 35/6 | 4+2,5 | 0.06 | 1.6 | 0.16 | 120 | 1.44 | 0 | 2.625 | 1.185 | 1.185 | open
114 | Kamenka 35/10 | 2,5+2,5 | 1.56 | 0.42 | 120 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | open | 114 | Kamenka 35/10 | 2,5+2,5 | 0.62 | 2.18 | 0.42 | 120 | 1.76 | 0 | 2.625 | 0.865 | 0.865 | open
115 | Solovyevo 35/10 | 4+4 | 0.45 | 0.04 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | open | 115 | Solovyevo 35/10 | 4+4 | 0.15 | 0.6 | 0.04 | 120 | 0.56 | 0 | 4.2 | 3.64 | 3.64 | open
116 | Rudnya (FGC) 110/35/10 | 10+16 | 8.56 | 2.37 | 120 | 6.19 | 0 | 10.5 | 4.31 | 4.31 | open | 116 | Rudnya (FGC) 110/35/10 | 10+16 | 1.88 | 10.44 | 2.86 | 120 | 7.58 | 0 | 10.5 | 2.92 | 2.92 | open
| Nom. capacity MV, МVА | 10+16 | 1.44 | 1.44 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 0.49 | 1.93 | 1.93 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 7.12 | 0.93 | 120 | 6.19 | 0 | 10.5 | 4.31 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.39 | 8.51 | 0.93 | 120 | 7.58 | 0 | 10.5 | 2.92
117 | Zhichitsy 35/10 | 2,5+2,5 | 0.19 | 0.75 | 120 | -0.56 | 0 | 2.625 | 3.185 | 3.185 | open | 117 | Zhichitsy 35/10 | 2,5+2,5 | 0.05 | 0.24 | 0.75 | 120 | -0.51 | 0 | 2.625 | 3.135 | 3.135 | open
118 | Mikulino 35/10 | 6,3+6,3 | 0.98 | 1.1 | 120 | -0.12 | 0 | 6.615 | 6.735 | 6.735 | open | 118 | Mikulino 35/10 | 6,3+6,3 | 0.18 | 1.16 | 1.1 | 120 | 0.06 | 0 | 6.615 | 6.555 | 6.555 | open
119 | Lyubavichi 35/10 | 2,5+2,5 | 0.62 | 0.74 | 120 | -0.12 | 0 | 2.625 | 2.745 | 2.745 | open | 119 | Lyubavichi 35/10 | 2,5+2,5 | 0.29 | 0.91 | 0.74 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
120 | Kazimirovo 35/10 | 4+4 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | open | 120 | Kazimirovo 35/10 | 4+4 | 0 | 0.35 | 0.02 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | open
121 | Golynki 110/35/6 | 25+25 | 3.35 | 1.81 | 120 | 1.54 | 0 | 26.25 | 24.71 | 24.71 | open | 121 | Golynki 110/35/6 | 25+25 | 4.21 | 7.56 | 5.86 | 120 | 1.7 | 0 | 26.25 | 24.55 | 24.55 | open
| Nom. Capacity MV, МVА | 25+25 | 1.65 | 1.65 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. Capacity MV, МVА | 25+25 | 4.05 | 5.7 | 5.7 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 1.7 | 0.16 | 120 | 1.54 | 0 | 26.25 | 24.71 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.16 | 1.86 | 0.16 | 120 | 1.7 | 0 | 26.25 | 24.55
122 | Belei 35/10 | 2,5+2,5 | 1.78 | 0.75 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | open | 122 | Belei 35/10 | 2,5+2,5 | 3.58 | 5.36 | 0.75 | 120 | 4.61 | 0 | 2.625 | -1.985 | -1.985 | closed
123 | Ponizovye 110/35/10 | 6,3+6,3 | 3.27 | 2.35 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | open | 123 | Ponizovye 110/35/10 | 6,3+6,3 | 0.22 | 3.49 | 2.57 | 120 | 0.92 | 0 | 6.615 | 5.695 | 5.695 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 2.29 | 2.29 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.22 | 2.51 | 2.51 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.98 | 0.06 | 120 | 0.92 | 0 | 6.615 | 5.695
124 | Klyarinovo 35/10 | 2,5+2,5 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open | 124 | Klyarinovo 35/10 | 2,5+2,5 | 0 | 0.35 | 0.19 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | open
125 | Safonovo 110/6 | 15+20 | 11.46 | 0.06 | 120 | 11.4 | 0 | 15.75 | 4.35 | 4.35 | open | 125 | Safonovo 110/6 | 15+20 | 3.51 | 14.97 | 0.06 | 120 | 14.91 | 0 | 15.75 | 0.84 | 0.84 | open
126 | Gornaya 110/35/6 | 25+25 | 16.12 | 15.14 | 120 | 0.98 | 0 | 26.25 | 25.27 | 25.27 | open | 126 | Gornaya 110/35/6 | 25+25 | 3.58 | 19.7 | 18.49 | 120 | 1.21 | 0 | 26.25 | 25.04 | 25.04 | open
| Nom. capacity MV, МVА | 25+25 | 10.47 | 10.47 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 3.35 | 13.82 | 13.82 |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, МVА | 25+25 | 5.65 | 4.67 | 120 | 0.98 | 0 | 26.25 | 25.27 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.23 | 5.88 | 4.67 | 120 | 1.21 | 0 | 26.25 | 25.04
127 | Water intake 35/6 | 6,3+4 | 3.1 | 0.69 | 120 | 2.41 | 0 | 4.2 | 1.79 | 1.79 | open | 127 | Water intake 35/6 | 6,3+4 | 0.54 | 3.64 | 0.69 | 120 | 2.95 | 0 | 4.2 | 1.25 | 1.25 | open
128 | Vadino 35/10 | 4+4 | 1.78 | 0 | 120 | 1.78 | 0 | 4.2 | 2.42 | 2.42 | open | 128 | Vadino 35/10 | 4+4 | 2.18 | 3.96 | 0 | 120 | 3.96 | 0 | 4.2 | 0.24 | 0.24 | open
129 | ZSSK 35/6 | 4+4 | 1.81 | 0.75 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | open | 129 | ZSSK 35/6 | 4+4 | 1.03 | 2.84 | 0.75 | 120 | 2.09 | 0 | 4.2 | 2.11 | 2.11 | open
130 | Yanovo 35/10 | 4+6,3 | 0.37 | 0.05 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | open | 130 | Yanovo 35/10 | 4+6,3 | 0 | 0.37 | 0.05 | 120 | 0.32 | 0 | 4.2 | 3.88 | 3.88 | open
131 | Kapyrevshchina 35/10 | 4+4 | 1.35 | 0.22 | 120 | 1.13 | 0 | 4.2 | 3.07 | 3.07 | open | 131 | Kapyrevshchina 35/10 | 4+4 | 0 | 1.35 | 0.22 | 120 | 1.13 | 0 | 4.2 | 3.07 | 3.07 | open
132 | Miropolye 35/10 | 2,5+2,5 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | open | 132 | Miropolye 35/10 | 2,5+2,5 | 0 | 0.67 | 0 | 120 | 0.67 | 0 | 2.625 | 1.955 | 1.955 | open
133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 4.8 | 2.63 | 120 | 2.17 | 0 | 5.88 | 3.71 | 1.71 | open | 133 | Izdeshkovo 110/35/10 | 5,6+6,3 | 1.31 | 6.11 | 3.45 | 120 | 2.66 | 0 | 5.88 | 3.22 | 3.22 | open
| Nom. capacity MV, МVА | 5,6+6,3 | 2.2 | 2.2 |  | 0 | 1 | 5.88 | 4.88 |  |  |  | Nom. capacity MV, МVА | 5,6+6,3 | 0.82 | 3.02 | 3.02 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 2.6 | 0.43 | 120 | 2.17 | 2 | 5.88 | 1.71 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0.49 | 3.09 | 0.43 | 120 | 2.66 | 0 | 5.88 | 3.22
134 | Alferovo 35/10 | 2,5+2,5 | 0.75 | 0.2 | 120 | 0.55 | 0 | 2.625 | 2.075 | 2.075 | open | 134 | Alferovo 35/10 | 2,5+2,5 | 0.13 | 0.88 | 0.2 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | open
135 | Kasulino 35/10 | 2,5+2,5 | 0.32 | 0 | 120 | 0.32 | 0 | 2.625 | 2.305 | 2.305 | open | 135 | Kasulino 35/10 | 2,5+2,5 | 0.06 | 0.38 | 0 | 120 | 0.38 | 0 | 2.625 | 2.245 | 2.245 | open
136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.6 | 0.15 | 120 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | open | 136 | Bogdanovshchina 35/10 | 1,6+1,6 | 0.65 | 1.25 | 0.15 | 120 | 1.1 | 0 | 1.68 | 0.58 | 0.58 | open
137 | Glinka 110/35/10 | 10+6,3 | 2.13 | 0.56 | 120 | 1.57 | 0 | 6.615 | 5.045 | 3.045 | open | 137 | Glinka 110/35/10 | 10+6,3 | 0.45 | 2.58 | 0.99 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | open
| Nom. capacity MV, МVА | 10+6,3 | 0.45 | 0.45 |  | 0 | 1 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, МVА | 10+6,3 | 0.43 | 0.88 | 0.88 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 10+6,3 | 1.68 | 0.11 | 120 | 1.57 | 2 | 6.615 | 3.045 |  |  |  | Nom. capacity LV, МVА | 10+6,3 | 0.02 | 1.7 | 0.11 | 120 | 1.59 | 0 | 6.615 | 5.025
138 | Dobromino 35/10 | 2,5+2,5 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | open | 138 | Dobromino 35/10 | 2,5+2,5 | 0.14 | 0.39 | 0 | 120 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | open
139 | Bely kholm 35/10 | 1,6+1,6 | 0.18 | 0 | 120 | 0.18 | 0 | 1.68 | 1.5 | 1.5 | open | 139 | Bely kholm 35/10 | 1,6+1,6 | 0.04 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open
140 | Dukhovshchina 110/35/10 | 10+10 | 3.65 | 1.99 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | open | 140 | Dukhovshchina 110/35/10 | 10+10 | 1.67 | 5.32 | 3.04 | 120 | 2.28 | 0 | 10.5 | 8.22 | 8.22 | open
| Nom. capacity MV, МVА | 10+10 | 1.73 | 1.73 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.05 | 2.78 | 2.78 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.92 | 0.26 | 120 | 1.66 | 0 | 10.5 | 8.84 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.62 | 2.54 | 0.26 | 120 | 2.28 | 0 | 10.5 | 8.22
141 | Zimets 35/10 | 4+4 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | open | 141 | Zimets 35/10 | 4+4 | 0 | 0.2 | 0.06 | 120 | 0.14 | 0 | 4.2 | 4.06 | 4.06 | open
142 | Beresnevo 35/10 | 1,6+1,6 | 0.53 | 0.01 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open | 142 | Beresnevo 35/10 | 1,6+1,6 | 0 | 0.53 | 0.01 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open
143 | Prechistoe 110/35/10 | 6,3+6,3 | 2.02 | 0.14 | 120 | 1.88 | 0 | 6.615 | 4.735 | 4.735 | open | 143 | Prechistoe 110/35/10 | 6,3+6,3 | 0.21 | 2.23 | 0.14 | 120 | 2.09 | 0 | 6.615 | 4.525 | 4.525 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 1.5 | 0 |  | 1.5 | 0 | 6.615 | 5.115 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.21 | 1.71 | 0 |  | 1.71 | 0 | 6.615 | 4.905
| Nom. capacity LV, МVА | 6,3+6,3 | 0.52 | 0.14 | 120 | 0.38 | 0 | 6.615 | 6.235 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.52 | 0.14 | 120 | 0.38 | 0 | 6.615 | 6.235
144 | Vorontsovo 35/10 | 2,5+2,5 | 0.24 | 0.07 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 144 | Vorontsovo 35/10 | 2,5+2,5 | 0 | 0.24 | 0.07 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
145 | Ozyorny 35/10 | 6,3+6,3 | 1.58 | 0.01 | 120 | 1.57 | 0 | 6.615 | 5.045 | 5.045 | open | 145 | Ozyorny 35/10 | 6,3+6,3 | 0.34 | 1.92 | 0.01 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | open
146 | Igorevskaya 110/10 | 10+10 | 7.93 | 0 | 120 | 7.93 | 0 | 10.5 | 2.57 | 2.57 | open | 146 | Igorevskaya 110/10 | 10+10 | 0.22 | 1.15 | 0 | 120 | 1.15 | 0 | 10.5 | 9.35 | 9.35 | open
147 | Kanyutino 110/35/10 | 5,6+6,3 | 3.4 | 1.68 | 120 | 1.72 | 0 | 5.88 | 4.16 | 4.16 | open | 147 | Kanyutino 110/35/10 | 5,6+6,3 | 2.93 | 6.33 | 6.13 | 120 | 0.2 | 0 | 5.88 | 5.68 | 5.68 | open
| Nom. capacity LV, МVА | 5,6+6,3 | 2.99 | 2.99 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 2.93 | 5.92 | 5.92 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+6,3 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68 |  |  |  | Nom. capacity LV, МVА | 5,6+6,3 | 0 | 0.41 | 0.21 | 120 | 0.2 | 0 | 5.88 | 5.68
148 | Bogolyubovo 35/10 | 2,5+2,5 | 1.11 | 0.25 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | open | 148 | Bogolyubovo 35/10 | 2,5+2,5 | 0 | 1.11 | 0.25 | 120 | 0.86 | 0 | 2.625 | 1.765 | 1.765 | open
149 | Kholm-Zhirki 35/10 | 2,5+4 | 2.73 | 0.4 | 120 | 2.33 | 0 | 2.625 | 0.295 | 0.295 | open | 149 | Kholm-Zhirki 35/10 | 2,5+4 | 0.29 | 3.02 | 0.4 | 120 | 2.62 | 0 | 2.625 | 0.005 | 0.005 | open
150 | Dorogobuzh 1 110/35/10 | 16+16 | 10.38 | 4.87 | 120 | 5.51 | 0 | 16.8 | 11.29 | 11.29 | open | 150 | Dorogobuzh 1 110/35/10 | 16+16 | 2.5 | 12.88 | 5.96 | 120 | 6.92 | 0 | 16.8 | 9.88 | 9.88 | open
| Nom. capacity MV, МVА | 16+16 | 4.35 | 4.35 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 1.09 | 5.44 | 5.44 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 6.03 | 0.52 | 120 | 5.51 | 0 | 16.8 | 11.29 |  |  |  | Nom. capacity LV, МVА | 16+16 | 1.41 | 7.44 | 0.52 | 120 | 6.92 | 0 | 16.8 | 9.88
151 | Kaskovo 35/10 | 1,6+4 | 0.84 | 0.09 | 120 | 0.75 | 0 | 1.68 | 0.93 | 0.93 | open | 151 | Kaskovo 35/10 | 1,6+4 | 0.18 | 1.02 | 0.09 | 120 | 0.93 | 0 | 1.68 | 0.75 | 0.75 | open
152 | Usvyatye 35/10 | 2,5+4 | 0.79 | 0 | 120 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | open | 152 | Usvyatye 35/10 | 2,5+4 | 0.68 | 1.47 | 0 | 120 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | open
153 | Ushakovo 35/10 | 1,6+2,5 | 0.84 | 0 | 120 | 0.84 | 0 | 1.68 | 0.84 | 0.84 | open | 153 | Ushakovo 35/10 | 1,6+2,5 | 0 | 0.84 | 0 | 120 | 0.84 | 0 | 1.68 | 0.84 | 0.84 | open
154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | open | 154 | Artek (departamental) 35/10 | 4+4 | 0 | 0 | 0 | 120 | 0 | 0 | 4.2 | 4.2 | 4.2 | open
155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | open | 155 | Ivano-Gudino 110/10 | 6,3+6,3 | 0 | 0.2 | 0.04 | 120 | 0.16 | 0 | 6.615 | 6.455 | 6.455 | open
156 | Elnya 110/35/10 | 16+16 | 4.43 | 2.7 | 120 | 1.73 | 0 | 16.8 | 15.07 | 15.07 | open | 156 | Elnya 110/35/10 | 16+16 | 0.61 | 5.04 | 2.91 | 120 | 2.13 | 0 | 16.8 | 14.67 | 14.67 | open
| Nom. capacity MV, МVА | 16+16 | 2.16 | 2.16 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.21 | 2.37 | 2.37 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.27 | 0.54 | 10 | 1.73 | 0 | 16.8 | 15.07 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.4 | 2.67 | 0.54 | 120 | 2.13 | 0 | 16.8 | 14.67
157 | Pavlovo 35/10 | 2,5+2,5 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open | 157 | Pavlovo 35/10 | 2,5+2,5 | 0 | 0.14 | 0 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open
158 | Sharapovo 35/10 | 4+4 | 0.48 | 1 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | open | 158 | Sharapovo 35/10 | 4+4 | 0 | 0.48 | 1 | 120 | -0.52 | 0 | 4.2 | 4.72 | 4.72 | open
159 | Korobets 35/10 | 2,5+2,5 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | open | 159 | Korobets 35/10 | 2,5+2,5 | 0 | 1.08 | 0.17 | 120 | 0.91 | 0 | 2.625 | 1.715 | 1.715 | open
160 | Baltutino 35/10 | 2,5+2,5 | 0.54 | 0 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | open | 160 | Baltutino 35/10 | 2,5+2,5 | 0.15 | 0.69 | 0 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | open
161 | Lapino 110/35/10 | 5,6+5,6 | 1.13 | 0.72 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | open | 161 | Lapino 110/35/10 | 5,6+5,6 | 0.03 | 1.16 | 0.75 | 120 | 0.41 | 0 | 5.88 | 5.47 | 5.47 | open
| Nom. capacity MV, МVА | 5,6+5,6 | 0.72 | 0.72 |  | 0 | 0 | 5.88 | 5.88 |  |  |  | Nom. capacity MV, МVА | 5,6+5,6 | 0.03 | 0.75 | 0.75 |  | 0 | 0 | 5.88 | 5.88
| Nom. capacity LV, МVА | 5,6+5,6 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47 |  |  |  | Nom. capacity LV, МVА | 5,6+5,6 | 0 | 0.41 | 0 | 120 | 0.41 | 0 | 5.88 | 5.47
162 | Mutishche 35/10 | 1,6+2,5 | 0.14 | 0.08 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | open | 162 | Mutishche 35/10 | 1,6+2,5 | 0 | 0.14 | 0.08 | 120 | 0.06 | 0 | 1.68 | 1.62 | 1.62 | open
163 | Suetovo 110/35/10 | 6,3+6,3 | 3.12 | 2.33 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | open | 163 | Suetovo 110/35/10 | 6,3+6,3 | 1.32 | 4.44 | 3.41 | 120 | 1.03 | 0 | 6.615 | 5.585 | 5.585 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 1.75 | 1.75 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 1.08 | 2.83 | 2.83 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.37 | 0.58 | 120 | 0.79 | 0 | 6.615 | 5.825 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.24 | 1.61 | 0.58 | 120 | 1.03 | 0 | 6.615 | 5.585
164 | Pushkino 35/10 | 2,5+2,5 | 0.97 | 0.04 | 120 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | open | 164 | Pushkino 35/10 | 2,5+2,5 | 1.08 | 2.05 | 0.04 | 120 | 2.01 | 0 | 2.625 | 0.615 | 0.615 | open
165 | Yartsevo 1 110/10 | 40+40 | 17.99 | 5.34 | 120 | 12.65 | 0 | 42 | 29.35 | 29.35 | open | 165 | Yartsevo 1 110/10 | 40+40 | 2.68 | 20.67 | 5.34 | 120 | 15.33 | 0 | 42 | 26.67 | 26.67 | open
166 | Yartsevo 2 110/10 | 16+16 | 12.7 | 0.75 | 120 | 11.95 | 0 | 16.8 | 4.85 | 4.85 | open | 166 | Yartsevo 2 110/10 | 16+16 | 5.57 | 18.27 | 0.75 | 120 | 17.52 | 0 | 16.8 | -0.72 | -0.72 | closed
167 | Saprykino 110/35/10 | 6,3+6,3 | 1.72 | 0.4 | 120 | 1.32 | 0 | 6.615 | 5.295 | 5.295 | open | 167 | Saprykino 110/35/10 | 6,3+6,3 | 0.04 | 1.76 | 0.87 | 120 | 0.89 | 0 | 6.615 | 5.725 | 5.725 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.47 | 0.47 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.25 | 0.4 | 120 | 0.85 | 0 | 6.615 | 5.765 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.04 | 1.29 | 0.4 | 120 | 0.89 | 0 | 6.615 | 5.725
168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 2.87 | 0 | 120 | 2.87 | 0 | 6.615 | 3.745 | 3.745 | open | 168 | Dorogobuzh 2 35/10 | 6,3+6,3 | 0.79 | 3.66 | 0 | 120 | 3.66 | 0 | 6.615 | 2.955 | 2.955 | open
169 | Egoryevo 35/10 | 6,3+6,3 | 5.39 | 0 | 120 | 5.39 | 0 | 6.615 | 1.225 | 1.225 | open | 169 | Egoryevo 35/10 | 6,3+6,3 | 1.36 | 6.75 | 0 | 120 | 6.75 | 0 | 6.615 | -0.135 | -0.135 | closed
170 | Shalomino 35/10 | 1,6+2,5 | 0.65 | 0.13 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open | 170 | Shalomino 35/10 | 1,6+2,5 | 0 | 0.65 | 0.13 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | open
171 | Roslavl 110/35/6 | 25+40 | 24.09 | 1.4 | 120 | 22.69 | 0 | 26.25 | 3.56 | 3.56 | open | 171 | Roslavl 110/35/6 | 25+40 | 1.93 | 26.02 | 1.4 | 120 | 24.62 | 0 | 26.25 | 1.63 | 1.63 | open
| Nom. capacity MV, МVА | 25+40 | 11.48 | 1.4 |  | 10.08 | 0 | 26.25 | 16.17 |  |  |  | Nom. capacity MV, МVА | 25+40 | 0.75 | 12.23 | 1.4 |  | 10.83 | 0 | 26.25 | 15.42
| Nom. сapacity LV, МVА | 25+40 | 12.61 | 0 | 120 | 12.61 | 0 | 26.25 | 13.64 |  |  |  | Nom. сapacity LV, МVА | 25+40 | 1.18 | 13.79 | 0 | 120 | 13.79 | 0 | 26.25 | 12.46
172 | Meet processing plant 35/6 | 6,3+6,3 | 1.69 | 0 | 120 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | open | 172 | Meet processing plant 35/6 | 6,3+6,3 | 0.11 | 1.8 | 0 | 120 | 1.8 | 0 | 6.615 | 4.815 | 4.815 | open
173 | Perenka 35/10 | 4+4 | 0.4 | 0 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open | 173 | Perenka 35/10 | 4+4 | 0.01 | 0.41 | 0 | 120 | 0.41 | 0 | 4.2 | 3.79 | 3.79 | open
174 | Khoroshevo 35/10 | 2,5+4 | 1.03 | 0 | 120 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | open | 174 | Khoroshevo 35/10 | 2,5+4 | 0.08 | 1.11 | 0 | 120 | 1.11 | 0 | 2.625 | 1.515 | 1.515 | open
175 | Lipovka 35/10 | 2,5+2,5 | 0.43 | 0 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | open | 175 | Lipovka 35/10 | 2,5+2,5 | 0 | 0.43 | 0 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | open
176 | Kirilly 35/10 | 2,5+2,5 | 0.76 | 0 | 120 | 0.76 | 0 | 2.625 | 1.865 | 1.865 | open | 176 | Kirilly 35/10 | 2,5+2,5 | 0.52 | 1.28 | 0 | 120 | 1.28 | 0 | 2.625 | 1.345 | 1.345 | open
177 | Desnogorsk 110/35/10 | 25+25 | 18.65 | 5.42 | 120 | 13.23 | 0 | 26.25 | 13.02 | 13.02 | open | 177 | Desnogorsk 110/35/10 | 25+25 | 0.63 | 19.28 | 3.16 | 120 | 16.12 | 0 | 26.25 | 10.13 | 10.13 | open
| Nom. capacity MV, МVА | 25+25 | 5.42 | 5.42 |  | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity MV, МVА | 25+25 | 0.62 | 6.04 | 3.16 |  | 2.88 | 0 | 26.25 | 23.37
| Nom. capacidty LV, МVА | 25+25 | 13.23 | 0 | 120 | 13.23 | 0 | 26.25 | 13.02 |  |  |  | Nom. capacidty LV, МVА | 25+25 | 0.01 | 13.24 | 0 | 120 | 13.24 | 0 | 26.25 | 13.01
178 | Ekimovichi 35/10 | 4+4 | 2.3 | 0.24 | 120 | 2.06 | 0 | 4.2 | 2.14 | 2.14 | open | 178 | Ekimovichi 35/10 | 4+4 | 0.07 | 2.37 | 0.24 | 120 | 2.13 | 0 | 4.2 | 2.07 | 2.07 | open
179 | Ivanovskaya 35/10 | 2,5+2,5 | 0.21 | 0.07 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open | 179 | Ivanovskaya 35/10 | 2,5+2,5 | 0 | 0.21 | 0.07 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | open
180 | Kokhany 35/10 | 1,6+1,6 | 0.35 | 0.09 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | open | 180 | Kokhany 35/10 | 1,6+1,6 | 0.09 | 0.44 | 0.09 | 120 | 0.35 | 0 | 1.68 | 1.33 | 1.33 | open
181 | Koski 35/10 | 4+4 | 0.39 | 0 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | open | 181 | Koski 35/10 | 4+4 | 0.01 | 0.4 | 0 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open
182 | Industrialnaya 110/35/6 | 16+16 | 4.62 | 1.33 | 120 | 3.29 | 0 | 16.8 | 13.51 | 4.565 | open | 182 | Industrialnaya 110/35/6 | 16+16 | 2.11 | 6.73 | 1.43 | 120 | 5.3 | 0 | 16.8 | 11.5 | 5.565 | open
| Nom. capacity MV, МVА | 16,3+5,3 | 1.33 | 1.33 |  | 0 | 1 | 5.565 | 4.565 |  |  |  | Nom. capacity MV, МVА | 16,3+5,3 | 0.1 | 1.43 | 1.43 |  | 0 | 0 | 5.565 | 5.565
| Nom. capacity LV, МVА | 16+10,7 | 3.29 | 0 | 120 | 3.29 | 2 | 11.235 | 5.945 |  |  |  | Nom. capacity LV, МVА | 16+10,7 | 2.01 | 5.3 | 0 | 120 | 5.3 | 0 | 11.235 | 5.935
183 | Astapkovichi 35/10 | 2,5+2,5 | 0.83 | 0 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | open | 183 | Astapkovichi 35/10 | 2,5+2,5 | 0 | 0.83 | 0 | 120 | 0.83 | 0 | 2.625 | 1.795 | 1.795 | open
184 | Barsuki 110/35/10 | 6,3+6,3 | 1.14 | 0.86 | 120 | 0.28 | 0 | 6.615 | 6.335 | 6.335 | open | 184 | Barsuki 110/35/10 | 6,3+6,3 | 0.03 | 1.17 | 0.89 | 120 | 0.28 | 0 | 6.615 | 6.335 | 6.335 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 0.86 | 0.86 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.03 | 0.89 | 0.89 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 6.615 | 6.335
185 | Bogdanovo 35/10 | 4+4 | 0.26 | 0 | 120 | 0.26 | 0 | 4.2 | 3.94 | 3.94 | open | 185 | Bogdanovo 35/10 | 4+4 | 0.02 | 0.28 | 0 | 120 | 0.28 | 0 | 4.2 | 3.92 | 3.92 | open
186 | Prigorye 110/35/10 | 10+2,5 | 0.94 | 0.66 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open | 186 | Prigorye 110/35/10 | 10+2,5 | 0 | 0.94 | 0.66 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open
| Nom. capacity MV, МVА | 10+2,5 | 0.66 | 0.66 |  | 0 | 0 | 2.625 | 2.625 |  |  |  | Nom. capacity MV, МVА | 10+2,5 | 0 | 0.66 | 0.66 |  | 0 | 0 | 2.625 | 2.625
| Nom. Capacity LV, МVА | 10+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 |  |  |  | Nom. Capacity LV, МVА | 10+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345
187 | Bekhovo 35/10 | 2,5+2,5 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open | 187 | Bekhovo 35/10 | 2,5+2,5 | 0 | 0.28 | 0 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open
188 | Pochinok 110/35/10 | 10+16 | 9.02 | 3.12 | 120 | 5.9 | 0 | 10.5 | 4.6 | 4.6 | open | 188 | Pochinok 110/35/10 | 10+16 | 1.85 | 10.87 | 3.92 | 120 | 6.95 | 0 | 10.5 | 3.55 | 3.55 | open
| Nom. capacidty MV, МVА | 10+16 | 3.04 | 3.04 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacidty MV, МVА | 10+16 | 0.8 | 3.84 | 3.84 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 5.98 | 0.08 | 120 | 5.9 | 0 | 10.5 | 4.6 |  |  |  | Nom. capacity LV, МVА | 10+16 | 1.05 | 7.03 | 0.08 | 120 | 6.95 | 0 | 10.5 | 3.55
189 | Divinskaya 35/10 | 4+4 | 1.19 | 0.17 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | open | 189 | Divinskaya 35/10 | 4+4 | 0.04 | 1.23 | 0.17 | 120 | 1.06 | 0 | 4.2 | 3.14 | 3.14 | open
190 | Shatalovo 35/10 | 2,5+2,5 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | open | 190 | Shatalovo 35/10 | 2,5+2,5 | 0 | 1.42 | 0 | 120 | 1.42 | 0 | 2.625 | 1.205 | 1.205 | open
191 | Panskaya 35/10 | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | open | 191 | Panskaya 35/10 | 6,3+6,3 | 0.69 | 2.05 | 0 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | open
192 | Stodolishche 110/35/10 | 6,3+6,3 | 3.41 | 1.82 | 120 | 1.59 | 0 | 6.615 | 5.025 | 5.025 | open | 192 | Stodolishche 110/35/10 | 6,3+6,3 | 2.56 | 5.97 | 2.08 | 120 | 3.89 | 0 | 6.615 | 2.725 | 2.725 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 1.37 | 1.37 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.26 | 1.63 | 1.63 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 2.04 | 0.45 | 120 | 1.59 | 0 | 6.615 | 5.025 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.3 | 4.34 | 0.45 | 120 | 3.89 | 0 | 6.615 | 2.725
193 | Belik 35/10 | 2,5+2,5 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | open | 193 | Belik 35/10 | 2,5+2,5 | 0 | 0.16 | 0.33 | 120 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | open
194 | Pervomayskaya 35/10 | 4+4 | 1.52 | 0 | 120 | 1.52 | 0 | 4.2 | 2.68 | 2.68 | open | 194 | Pervomayskaya 35/10 | 4+4 | 0.07 | 1.59 | 0 | 120 | 1.59 | 0 | 4.2 | 2.61 | 2.61 | open
195 | Vaskovo 110/35/10 | 6,3+6,3 | 1.85 | 2.07 | 120 | -0.22 | 0 | 6.615 | 6.835 | 6.355 | open | 195 | Vaskovo 110/35/10 | 6,3+6,3 | 0.77 | 2.62 | 2.32 | 120 | 0.3 | 0 | 6.615 | 6.315 | 6.315 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 1.38 | 1.38 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.73 | 2.11 | 2.11 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 0.47 | 0.21 | 120 | 0.26 | 0 | 6.615 | 6.355 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.04 | 0.51 | 0.21 | 120 | 0.3 | 0 | 6.615 | 6.315
196 | Strigino 35/10 | 2,5+2,5 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 196 | Strigino 35/10 | 2,5+2,5 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
197 | Komintern 35/10 | 2,5+2,5 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open | 197 | Komintern 35/10 | 2,5+2,5 | 0 | 0.27 | 0 | 120 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | open
198 | Monastyrshchina 110/35/10 | 10+10 | 6.21 | 1.77 | 120 | 4.44 | 0 | 10.5 | 6.06 | 6.06 | open | 198 | Monastyrshchina 110/35/10 | 10+10 | 0.16 | 6.37 | 1.81 | 120 | 4.56 | 0 | 10.5 | 5.94 | 5.94 | open
| Nom. capacity MV, МVА | 10+10 | 1.77 | 1.77 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.04 | 1.81 | 1.81 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 4.44 | 0 | 120 | 4.44 | 0 | 10.5 | 6.06 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.12 | 4.56 | 0 | 120 | 4.56 | 0 | 10.5 | 5.94
199 | N.Mikhailov 35/10 | 4+4 | 0.57 | 0 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | open | 199 | N.Mikhailov 35/10 | 4+4 | 0 | 0.57 | 0 | 120 | 0.57 | 0 | 4.2 | 3.63 | 3.63 | open
200 | Tatarsk 35/10 | 3,2+4 | 0.94 | 0 | 120 | 0.94 | 0 | 3.36 | 2.42 | 2.42 | open | 200 | Tatarsk 35/10 | 3,2+4 | 0.02 | 0.96 | 0 | 120 | 0.96 | 0 | 3.36 | 2.4 | 2.4 | open
201 | Turki 35/10 | 1,6+1,6 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | open | 201 | Turki 35/10 | 1,6+1,6 | 0 | 0.17 | 0 | 120 | 0.17 | 0 | 1.68 | 1.51 | 1.51 | open
202 | Sozh 35/10 | 4+4 | 0.4 | 0 | 120 | 0.4 | 0 | 4.2 | 3.8 | 3.8 | open | 202 | Sozh 35/10 | 4+4 | 0.02 | 0.42 | 0 | 120 | 0.42 | 0 | 4.2 | 3.78 | 3.78 | open
203 | Khislavichi 110/35/10 | 16+16 | 3.95 | 1.62 | 120 | 2.33 | 0 | 16.8 | 14.47 | 14.47 | open | 203 | Khislavichi 110/35/10 | 16+16 | 0.49 | 4.44 | 1.82 | 120 | 2.62 | 0 | 16.8 | 14.18 | 14.18 | open
| Nom. capacity MV, МVА | 16+16 | 1.44 | 1.44 |  | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity MV, МVА | 16+16 | 0.2 | 1.64 | 1.64 |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, МVА | 16+16 | 2.51 | 0.18 | 120 | 2.33 | 0 | 16.8 | 14.47 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.29 | 2.8 | 0.18 | 120 | 2.62 | 0 | 16.8 | 14.18
204 | Gorodishche 35/10 | 1,8+2,5 | 0.73 | 0 | 120 | 0.73 | 0 | 1.89 | 1.16 | 1.16 | open | 204 | Gorodishche 35/10 | 1,8+2,5 | 0 | 0.73 | 0 | 120 | 0.73 | 0 | 1.89 | 1.16 | 1.16 | open
205 | Komarovka 35/10 | 4+4 | 0.15 | 0.02 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | open | 205 | Komarovka 35/10 | 4+4 | 0 | 0.15 | 0.02 | 120 | 0.13 | 0 | 4.2 | 4.07 | 4.07 | open
206 | Cherepovo 35/10 | 2,5+2,5 | 0.26 | 0 | 120 | 0.26 | 0 | 2.625 | 2.365 | 2.365 | open | 206 | Cherepovo 35/10 | 2,5+2,5 | 0.05 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open
207 | Studenets 35/10 | 1,6+2,5 | 0.29 | 0.01 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | open | 207 | Studenets 35/10 | 1,6+2,5 | 0.15 | 0.44 | 0.01 | 120 | 0.43 | 0 | 1.68 | 1.25 | 1.25 | open
208 | Shumyachi 110/35/10 | 10+10 | 4.78 | 2.84 | 120 | 1.94 | 0 | 10.5 | 8.56 | 8.56 | open | 208 | Shumyachi 110/35/10 | 10+10 | 0.55 | 5.33 | 3.03 | 120 | 2.3 | 0 | 10.5 | 8.2 | 8.2 | open
| Nom. capacity MV, МVА | 10+10 | 2.2 | 2.2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.19 | 2.39 | 2.39 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.58 | 0.64 | 120 | 1.94 | 0 | 10.5 | 8.56 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.36 | 2.94 | 0.64 | 120 | 2.3 | 0 | 10.5 | 8.2
209 | Ershichi 110/35/10 | 10+10 | 2.26 | 0.42 | 120 | 1.84 | 0 | 10.5 | 8.66 | 8.66 | open | 209 | Ershichi 110/35/10 | 10+10 | 0.39 | 2.65 | 0.42 | 120 | 2.23 | 0 | 10.5 | 8.27 | 8.27 | open
| Nom. capacity MV, МVА | 10+10 | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0 | 0.2 | 0.2 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.06 | 0.22 | 120 | 1.84 | 0 | 10.5 | 8.66 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.39 | 2.45 | 0.22 | 120 | 2.23 | 0 | 10.5 | 8.27
210 | Rukhan 35/10 | 2,5+2,5 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open | 210 | Rukhan 35/10 | 2,5+2,5 | 0 | 0.31 | 0 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | open
211 | Vyazma 1 110/35/10 | 40+40 | 41.71 | 11.83 | 120 | 29.88 | 0 | 42 | 12.12 | 12.12 | open | 211 | Vyazma 1 110/35/10 | 40+40 | 17.88 | 59.59 | 15.76 | 120 | 43.83 | 0 | 42 | -1.83 | -1.83 | closed
| Nom. capacity MV, МVА | 40+40 | 26.3 | 11.27 | 121 | 15.03 | 0 | 42 | 26.97 |  |  |  | Nom. capacity MV, МVА | 40+40 | 8.77 | 35.07 | 15.2 |  | 19.87 | 0 | 42 | 22.13
| Nom. capacity LV, МVА | 40+40 | 15.41 | 0.56 | 122 | 14.85 | 0 | 42 | 27.15 |  |  |  | Nom. capacity LV, МVА | 40+40 | 9.11 | 24.52 | 0.56 | 120 | 23.96 | 0 | 42 | 18.04
212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 2.38 | 0 | 120 | 2.38 | 0 | 6.615 | 4.235 | 4.235 | open | 212 | Vyazma-Bryanskaya 35/10 | 6,3+6,3 | 1.62 | 4 | 0 | 120 | 4 | 0 | 6.615 | 2.615 | 2.615 | open
213 | Khmelita 35/10 | 1,6+2,5 | 0.38 | 0.11 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | open | 213 | Khmelita 35/10 | 1,6+2,5 | 0.35 | 0.73 | 0.11 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | open
214 | Isakovo 35/10 | 2,5+4 | 0.58 | 0.3 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | open | 214 | Isakovo 35/10 | 2,5+4 | 0.05 | 0.63 | 0.3 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | open
215 | Rizskoe 35/10 | 2,5+2,5 | 0.73 | 0.01 | 120 | 0.72 | 0 | 2.625 | 1.905 | 1.905 | open | 215 | Rizskoe 35/10 | 2,5+2,5 | 0.27 | 1 | 0.01 | 120 | 0.99 | 0 | 2.625 | 1.635 | 1.635 | open
216 | Beryozka 35/10 | 4+4 | 0.97 | 0 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | open | 216 | Beryozka 35/10 | 4+4 | 0.42 | 1.39 | 0 | 120 | 1.39 | 0 | 4.2 | 2.81 | 2.81 | open
217 | Shimanovo 35/10 | 1,8+4 | 0.47 | 0.32 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | open | 217 | Shimanovo 35/10 | 1,8+4 | 0.31 | 0.78 | 0.32 | 120 | 0.46 | 0 | 1.89 | 1.43 | 1.43 | open
218 | Kaydakovo 35/10 | 4+4 | 1.04 | 0.2 | 120 | 0.84 | 0 | 4.2 | 3.36 | 3.36 | open | 218 | Kaydakovo 35/10 | 4+4 | 0.13 | 1.17 | 0.2 | 120 | 0.97 | 0 | 4.2 | 3.23 | 3.23 | open
219 | Flour mill 35/10 | 10+10 | 7.89 | 0.13 | 120 | 7.76 | 0 | 10.5 | 2.74 | 2.74 | open | 219 | Flour mill 35/10 | 10+10 | 4.63 | 12.52 | 0.13 | 120 | 12.39 | 0 | 10.5 | -1.89 | -1.89 | closed
220 | Kikino 35/10 | 2,5+2,5 | 0.56 | 0.41 | 120 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | open | 220 | Kikino 35/10 | 2,5+2,5 | 0.83 | 1.39 | 0.41 | 120 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | open
221 | Vyazma 2 110/10 | 16+16 | 15.6 | 0 | 120 | 15.6 | 0 | 16.8 | 1.2 | 1.2 | open | 221 | Vyazma 2 110/10 | 16+16 | 4.95 | 20.55 | 0 | 120 | 20.55 | 0 | 16.8 | -3.75 | -3.75 | closed
222 | Tumanovo 110/35/10 | 6,3+6,3 | 2.19 | 1.22 | 120 | 0.97 | 0 | 6.615 | 5.645 | 5.645 | open | 222 | Tumanovo 110/35/10 | 6,3+6,3 | 0.3 | 2.49 | 1.38 | 120 | 1.11 | 0 | 6.615 | 5.505 | 5.505 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 0.88 | 0.88 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0.16 | 1.04 | 1.04 |  | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.31 | 0.34 | 120 | 0.97 | 0 | 6.615 | 5.645 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.14 | 1.45 | 0.34 | 120 | 1.11 | 0 | 6.615 | 5.505
223 | Rossiya 110/35/10 | 10+16 | 2.38 | 1.82 | 120 | 0.56 | 0 | 10.5 | 9.94 | 9.94 | open | 223 | Rossiya 110/35/10 | 10+16 | 1.44 | 3.82 | 3.25 | 120 | 0.57 | 0 | 10.5 | 9.93 | 9.93 | open
| Nom. capacity MV, МVА | 10+16 | 1.5 | 1.5 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+16 | 1.43 | 2.93 | 2.93 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+16 | 0.88 | 0.32 | 120 | 0.56 | 0 | 10.5 | 9.94 |  |  |  | Nom. capacity LV, МVА | 10+16 | 0.01 | 0.89 | 0.32 | 120 | 0.57 | 0 | 10.5 | 9.93
224 | Semlevo 35/10 | 2,5+4 | 0.87 | 0 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | open | 224 | Semlevo 35/10 | 2,5+4 | 0.71 | 1.58 | 0 | 120 | 1.58 | 0 | 2.625 | 1.045 | 1.045 | open
225 | Artyomovo 35/10 | 2,5+2,5 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | open | 225 | Artyomovo 35/10 | 2,5+2,5 | 0 | 0.25 | 0 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | open
226 | Gagarin 110/35/10 | 25+25 | 23.41 | 4.78 | 120 | 18.63 | 0 | 26.25 | 7.62 | 7.62 | open | 226 | Gagarin 110/35/10 | 25+25 | 16.39 | 39.8 | 6.82 | 120 | 32.98 | 0 | 26.25 | -6.73 | -6.73 | closed
| Nom. capacity MV, МVА | 25+25 | 8.21 | 3.06 |  | 5.15 | 0 | 26.25 | 21.1 |  |  |  | Nom. capacity MV, МVА | 25+25 | 6.72 | 14.93 | 5.1 |  | 9.83 | 0 | 26.25 | 16.42
| Nom. capacity LV, МVА | 25+25 | 15.2 | 1.72 | 120 | 13.48 | 0 | 26.25 | 12.77 |  |  |  | Nom. capacity LV, МVА | 25+25 | 9.67 | 24.87 | 1.72 | 120 | 23.15 | 0 | 26.25 | 3.1
227 | Rodomanovo 35/10 | 4+4 | 0.91 | 1.18 | 120 | -0.27 | 0 | 4.2 | 4.47 | 4.47 | open | 227 | Rodomanovo 35/10 | 4+4 | 2.41 | 3.32 | 1.18 | 120 | 2.14 | 0 | 4.2 | 2.06 | 2.06 | open
228 | Klushino 35/10 | 4+4 | 0.78 | 0.57 | 120 | 0.21 | 0 | 4.2 | 3.99 | 3.99 | open | 228 | Klushino 35/10 | 4+4 | 0.89 | 1.67 | 0.57 | 120 | 1.1 | 0 | 4.2 | 3.1 | 3.1 | open
229 | Ivino 35/10 | 1,6+1,6 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open | 229 | Ivino 35/10 | 1,6+1,6 | 0 | 0.22 | 0 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | open
230 | Karmanovo 35/10 | 4+4 | 3.56 | 0.21 | 120 | 3.35 | 0 | 4.2 | 0.85 | 0.85 | open | 230 | Karmanovo 35/10 | 4+4 | 1.5 | 5.06 | 0.21 | 120 | 4.85 | 0 | 4.2 | -0.65 | -0.65 | closed
231 | Sverchkovo 35/10 | 2,5+2,5 | 2.04 | 0.75 | 120 | 1.29 | 0 | 2.625 | 1.335 | 1.335 | open | 231 | Sverchkovo 35/10 | 2,5+2,5 | 0.19 | 2.23 | 0.75 | 120 | 1.48 | 0 | 2.625 | 1.145 | 1.145 | open
232 | Lesnaya 35/10 | 4+4 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | open | 232 | Lesnaya 35/10 | 4+4 | 0 | 1.43 | 0 | 120 | 1.43 | 0 | 4.2 | 2.77 | 2.77 | open
233 | Tesovo 35/10 | 1,6+2,5 | 0.52 | 0.48 | 120 | 0.04 | 0 | 1.68 | 1.64 | 1.64 | open | 233 | Tesovo 35/10 | 1,6+2,5 | 0.09 | 0.61 | 0.48 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | open
234 | Svetotekhnika 110/10 | 16+16 | 4.5 | 0.97 | 120 | 3.53 | 0 | 16.8 | 13.27 | 13.27 | open | 234 | Svetotekhnika 110/10 | 16+16 | 4.31 | 8.81 | 0.97 | 120 | 7.84 | 0 | 16.8 | 8.96 | 8.96 | open
235 | Mishino 110/35/10 | 10+10 | 3.81 | 2.2 | 120 | 1.61 | 0 | 10.5 | 8.89 | 8.89 | open | 235 | Mishino 110/35/10 | 10+10 | 1.61 | 5.42 | 3.99 | 120 | 1.43 | 0 | 10.5 | 9.07 | 9.07 | open
| Nom. capacity MV, МVА | 10+10 | 2.53 | 2.53 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.82 | 3.35 | 3.35 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.28 | 0.64 | 120 | 0.64 | 0 | 10.5 | 9.86 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.79 | 2.07 | 0.64 | 120 | 1.43 | 0 | 10.5 | 9.07
236 | Nikolskoe 35/10 | 6,3+6,3 | 1.71 | 0.59 | 120 | 1.12 | 0 | 6.615 | 5.495 | 5.495 | open | 236 | Nikolskoe 35/10 | 6,3+6,3 | 0.6 | 2.31 | 0.59 | 120 | 1.72 | 0 | 6.615 | 4.895 | 4.895 | open
237 | Bekrino 35/10 | 2,5+2,5 | 0.51 | 0.09 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | open | 237 | Bekrino 35/10 | 2,5+2,5 | 0 | 0.51 | 0.09 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | open
238 | Trubnaya 110/10 | 25+25 | 6.49 | 1.57 | 120 | 4.92 | 0 | 26.25 | 21.33 | 21.33 | open | 238 | Trubnaya 110/10 | 25+25 | 5.01 | 11.5 | 1.57 | 120 | 9.93 | 0 | 26.25 | 16.32 | 16.32 | open
239 | Temkino 110/35/10 | 10+10 | 3.66 | 1.65 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | open | 239 | Temkino 110/35/10 | 10+10 | 3.08 | 6.74 | 2.57 | 120 | 4.17 | 0 | 10.5 | 6.33 | 6.33 | open
| Nom. capacity MV, МVА | 10+10 | 1.4 | 1.4 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.92 | 2.32 | 2.32 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.26 | 0.25 | 120 | 2.01 | 0 | 10.5 | 8.49 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.16 | 4.42 | 0.25 | 120 | 4.17 | 0 | 10.5 | 6.33
240 | Narytka 35/10 | 2,5+2,5 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open | 240 | Narytka 35/10 | 2,5+2,5 | 0 | 0.22 | 0.05 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | open
241 | Novodugino 110/35/10 | 10+10 | 3.9 | 1.89 | 120 | 2.01 | 0 | 10.5 | 8.49 | 8.49 | open | 241 | Novodugino 110/35/10 | 10+10 | 1.47 | 5.37 | 3.14 | 120 | 2.23 | 0 | 10.5 | 8.27 | 8.27 | open
| Nom. capacity MV, МVА | 10+10 | 1.41 | 1.41 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 1.25 | 2.66 | 2.66 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 2.49 | 0.48 | 120 | 2.01 | 0 | 10.5 | 8.49 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.22 | 2.71 | 0.48 | 120 | 2.23 | 0 | 10.5 | 8.27
242 | Vysokoe 35/10 | 1,6+4 | 0.57 | 0.42 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | open | 242 | Vysokoe 35/10 | 1,6+4 | 0.85 | 1.42 | 0.42 | 120 | 1 | 0 | 1.68 | 0.68 | 0.68 | open
243 | Khotkovo 35/10 | 4+4 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | open | 243 | Khotkovo 35/10 | 4+4 | 0 | 0.84 | 0.26 | 120 | 0.58 | 0 | 4.2 | 3.62 | 3.62 | open
244 | Dneprovsk 110/35/10 | 10+10 | 2.57 | 1.88 | 120 | 0.69 | 0 | 10.5 | 9.81 | 9.81 | open | 244 | Dneprovsk 110/35/10 | 10+10 | 1 | 3.57 | 2.85 | 120 | 0.72 | 0 | 10.5 | 9.78 | 9.78 | open
| Nom. capacity MV, МVА | 10+10 | 1.72 | 1.72 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.97 | 2.69 | 2.69 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 0.85 | 0.16 | 120 | 0.69 | 0 | 10.5 | 9.81 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.03 | 0.88 | 0.16 | 120 | 0.72 | 0 | 10.5 | 9.78
245 | Lipetsy 35/10 | 2,5+2,5 | 0.24 | 0.75 | 120 | -0.51 | 0 | 2.625 | 3.135 | 3.135 | open | 245 | Lipetsy 35/10 | 2,5+2,5 | 0.29 | 0.53 | 0.75 | 120 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | open
246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.66 | 0.7 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | open | 246 | Nakhimovskaya 35/10 | 1,6+1,6 | 0.04 | 0.7 | 0.7 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | open
247 | Sychevka 110/35/10 | 16+25 | 8.8 | 1.47 | 120 | 7.33 | 0 | 16.8 | 9.47 | 9.47 | open | 247 | Sychevka 110/35/10 | 16+25 | 7.14 | 15.94 | 1.78 | 120 | 14.16 | 0 | 16.8 | 2.64 | 2.64 | open
| Nom. capacity MV, МVА | 16+25 | 3.43 | 0.7 |  | 2.73 | 0 | 16.8 | 14.07 |  |  |  | Nom. capacity MV, МVА | 16+25 | 3.62 | 7.05 | 1.01 |  | 6.04 | 0 | 16.8 | 10.76
| Nom. capacfity LV, МVА | 16+25 | 5.37 | 0.77 | 120 | 4.6 | 0 | 16.8 | 12.2 |  |  |  | Nom. capacfity LV, МVА | 16+25 | 3.52 | 8.89 | 0.77 | 120 | 8.12 | 0 | 16.8 | 8.68
248 | Sutormino 35/10 | 1,8+4 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | open | 248 | Sutormino 35/10 | 1,8+4 | 0 | 0.55 | 0.06 | 120 | 0.49 | 0 | 1.89 | 1.4 | 1.4 | open
249 | Karavaevo 35/10 | 4+4 | 1.29 | 0.29 | 120 | 1 | 0 | 4.2 | 3.2 | 3.2 | open | 249 | Karavaevo 35/10 | 4+4 | 0.38 | 1.67 | 0.29 | 120 | 1.38 | 0 | 4.2 | 2.82 | 2.82 | open
250 | Lukino 35/10 | 4+1,6 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | open | 250 | Lukino 35/10 | 4+1,6 | 0 | 1.37 | 0.51 | 120 | 0.86 | 0 | 1.68 | 0.82 | 0.82 | open
251 | Subbotniki 110/10 | 6,3+6,3 | 0.75 | 0 | 120 | 0.75 | 0 | 6.615 | 5.865 | 5.865 | open | 251 | Subbotniki 110/10 | 6,3+6,3 | 0.37 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495 | 5.495 | open
252 | Ugra 110/10 | 6,3+6,3 | 3.64 | 0 | 120 | 3.64 | 0 | 6.615 | 2.975 | 2.975 | open | 252 | Ugra 110/10 | 6,3+6,3 | 0.72 | 4.36 | 0 | 120 | 4.36 | 0 | 6.615 | 2.255 | 2.255 | open
253 | Znamenka 110/35/10 | 10+10 | 3.58 | 2.35 | 120 | 1.23 | 0 | 10.5 | 9.27 | 9.27 | open | 253 | Znamenka 110/35/10 | 10+10 | 2.72 | 6.3 | 2.48 | 120 | 3.82 | 0 | 10.5 | 6.68 | 6.68 | open
| Nom. capacity MV, МVА | 10+10 | 2.32 | 2.32 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, МVА | 10+10 | 0.13 | 2.45 | 2.45 | 120 | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, МVА | 10+10 | 1.26 | 0.03 | 120 | 1.23 | 0 | 10.5 | 9.27 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.59 | 3.85 | 0.03 | 120 | 3.82 | 0 | 10.5 | 6.68
254 | Losmino 35/10 | 2,5+2,5 | 1.5 | 0.4 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | open | 254 | Losmino 35/10 | 2,5+2,5 | 0 | 1.5 | 0.4 | 120 | 1.1 | 0 | 2.625 | 1.525 | 1.525 | open
255 | Vskhody 110/35/10 | 6,3+6,3 | 1.41 | 0.37 | 120 | 1.04 | 0 | 6.615 | 5.575 | 5.575 | open | 255 | Vskhody 110/35/10 | 6,3+6,3 | 0.19 | 1.6 | 0.37 | 120 | 1.23 | 0 | 6.615 | 5.385 | 5.385 | open
| Nom. capacity MV, МVА | 6,3+6,3 | 0.36 | 0.36 |  | 0 | 0 | 6.615 | 6.615 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 | 0 | 0.36 | 0.36 | 120 | 0 | 0 | 6.615 | 6.615
| Nom. capacity LV, МVА | 6,3+6,3 | 1.05 | 0.01 | 120 | 1.04 | 0 | 6.615 | 5.575 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.16 | 1.21 | 0.01 | 120 | 1.2 | 0 | 6.615 | 5.415
| Total: | 3150.6 | 578.51 | [8 empty] | 2: Total:; 3: 3150.6; 4: 389.48; 5: 967.99
| deficit | [8 empty] | -0.06 |  | 2: deficit; Min 12: -66.73
| proficit | [8 empty] | 1048.955 |  | 2: proficit; Min 12: 815.715

## Свод. тек. дефицит январь 2011
The list of closed supply centers of IDGC of Centre - Smolenskenergo division (current deficit of capacity).
No. | Name of supply center, voltage class, power of transformers (inst. MVA) |  | Current deficit, MVA | Note
Smolenskenergo
1 | Mytishino 35/10 | 1.6 | -0.06 | closed
Total current deficit (January 2011) |  |  | -0.06

## Свод. ожид. деф. январь 2011
The list of closed supply centers of IDGC of Centre - Smolenskenergo division with expected load taking into account new connections and other development of the electical networks
No. | Name of supply center, voltage class, power of transformers (inst. MVA) |  | Expected deficit, MVA | Note
Smolenskenergo
1 | Akatovo 35/10 | 1.6 | -1 | closed
2 | Avrora 35/10 | 2.5 | -3.49 | closed
3 | Mytishino 35/10 | 1.6 | -0.06 | closed
4 | Smolensk 1 (FSK) 110/35/6 | 40+40 | -1.55 | closed
5 | Ryabtsevo 35/10 | 4+4 | -2.51 | closed
6 | Diffuzion 110/6 | 4+4 | -1.81 | closed
7 | Zavodskaya 110/35/10 | 25+25 | -6.12 | closed
8 | Gnezodovo 35/6 | 7,5+7,5 | -0.285 | closed
9 | Zapadnaya 110/6 | 25+16 | -3.45 | closed
10 | Kozino 110/35/10 | 10+10 | -12.55 | closed
11 | Odintsovo 35/10 | 6,3+6,3 | -2.615 | closed
12 | Krasny bor 35/6 | 4+4 | -2.5 | closed
13 | Peсhersk 35/6 | 4+4 | -2.52 | closed
14 | Kolodnya 35/6 | 6,3+4 | -0.16 | closed
15 | Chernushki 110/10/6 | 25+25 | -5.2 | closed
16 | Yuzhnaya 110/35/6 | 4+4 | -3.22 | closed
17 | Zhukovskaya 35/10 | 2,5+2,5 | -1.985 | closed
18 | Belei 35/10 | 16+16 | -0.72 | closed
19 | Yartsevo 2 110/10 | 6,3+6,3 | -0.135 | closed
20 | Vyazma 1 110/35/10 | 40+40 | -1.83 | closed
21 | Flour mill 35/10 | 10+10 | -1.89 | closed
22 | Vyazma 2 110/10 | 16+16 | -3.75 | closed
23 | Gagarin 110/35/10 | 25+25 | -6.73 | closed
24 | Karmanovo 35/10 | 4+4 | -0.65 | closed
Total expected deficit (January 2011) |  |  | -66.73