## ярославль
[13 empty] | table 1 | [13 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | open | 1 | SS 35/10 Matveevo | 1.6 | 0.02 | 0.28 | 0.779 | 1 day and night | 0.28 | 0 | 0.779 | 0.499 | 0.499 | open
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | open | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | open
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | closed | 3 | SS 35/10 Shirinye | 2.5 | 0.165 | 2.315 | 1.68 | 1 day and night | 2.315 | 0 | 1.68 | -0.635 | -0.635 | closed
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | open | 4 | SS 110/10 Pokrov | 2.5 | 0.006 | 0.276 | 1.282 | 1 day and night | 0.276 | 0 | 1.282 | 1.006 | 1.006 | open
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | open | 5 | SS 35/10 Obnora | 1.6 | 0.058 | 0.258 | 1.212 | 1 day and night | 0.258 | 0 | 1.212 | 0.954 | 0.954 | open
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | open | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 17.5999 |  |  | 17.5999 | 0 | 10.5 | -7.0999 | -7.0999 | closed
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 15.1944 |  |  | 15.1944 | 0 | 10.5 | -4.6944
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.4355 | 2.4055 |  |  | 2.4055 | 0 | 10.5 | 8.0945
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | open | 7 | SS 35/10 Ananyino | 1,6+1,6 | 0.673 | 1.983 |  |  | 1.983 | 0 | 1.68 | -0.303 | -0.303 | closed
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | open | 8 | SS 110/10/10 Bragino | 40+40 | 3.5264 | 38.4364 | 2.338 | 120 | 36.0984 | 0 | 42 | 5.9016 | 5.9016 | open
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | open | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.719 | 2.749 | 0.554 | 120 | 2.195 | 0 | 4.2 | 2.005 | 2.005 | open
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | open | 10 | SS 35/10 Vatolino | 4,0+4,0 | 1.596 | 5.016 |  |  | 5.016 | 0 | 4.2 | -0.816 | -0.816 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | open | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.1206 | 4.2406 |  |  | 4.2406 | 0 | 6.62 | 2.3794 | 2.3794 | open
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | open | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.052 | 2.022 |  |  | 2.022 | 0 | 4.2 | 2.178 | 2.178 | open
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | open | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.052 | 0.762 |  |  | 0.762 | 0 | 1.68 | 0.918 | 0.918 | open
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | open | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 2.2714 | 3.4414 |  |  | 3.4414 | 0 | 4.2 | 0.7586 | 0.7586 | open
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | open | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | open
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | open | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.157 | 2.367 | 0.139 | 120 | 2.228 | 0 | 2.63 | 0.402 | 0.402 | open
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | open | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.071 | 0.731 | 0.329 | 120 | 0.402 | 0 | 2.63 | 2.228 | 2.228 | open
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | open | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.617 | 3.227 | 0.312 | 120 | 2.915 | 0 | 4.2 | 1.285 | 1.285 | open
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | open | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 4.4999 | 7.3699 | 0.866 | 120 | 6.5039 | 0 | 4.2 | -2.3039 | -2.3039 | closed
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | open | 21 | SS 110/6 Depo | 16+16 | 3.5606 | 10.6306 |  |  | 10.6306 | 0 | 16.8 | 6.1694 | 6.1694 | open
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | open | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.509 | 2.099 | 1.039 | 120 | 1.06 | 0 | 1.68 | 0.62 | 0.62 | open
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | open | 23 | SS 110/10 Druzhba | 16+16 | 0.3763 | 5.8863 | 1.932 | 120 | 3.9543 | 0 | 16.8 | 12.8457 | 12.8457 | open
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | open | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.5445 | 5.4145 | 1.386 | 120 | 4.0285 | 0 | 6.62 | 2.5915 | 2.5915 | open
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | open | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.453 | 1.683 |  |  | 1.683 | 0 | 2.63 | 0.947 | 0.947 | open
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | open | 26 | SS 35/6 Zavolzhskaya | 10+10 | 2.1792 | 11.8992 |  |  | 11.8992 | 0 | 10.5 | -1.3992 | -1.3992 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | open | 27 | SS 110/6/6 Institutskaya | 40+40 | 3.8904 | 35.7204 |  |  | 35.7204 | 0 | 42 | 6.2796 | 6.2796 | open
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | open | 28 | SS 35/10 Koza | 1,6+1,6 | 0.022 | 0.322 | 0.052 | 120 | 0.27 | 0 | 1.68 | 1.41 | 1.41 | open
29 | SS 110/35/6 Konstantinovo | 20+16 | 20 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | open | 29 | SS 110/35/6 Konstantinovo | 20+16 |  | 12.7635 | 0.021 | 120 | 12.7425 | 0 | 16.8 | 4.0575 | 4.0575 | open
| Nom. capacity MV, МVА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 16.8 | 9.33 |  |  |  | Nom. capacity MV, МVА | 20+16 |  | 9.2985 |  |  | 9.2985 | 0 | 16.8 | 7.5015
| Nom. capacity LV, МVА | 20+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Nom. capacity LV, МVА | 20+16 | 0.375 | 3.465 | 0.021 | 120 | 3.444 | 0 | 16.8 | 13.356
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | open | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.106 | 2.586 | 0.242 | 120 | 2.344 | 0 | 2.63 | 0.286 | 0.286 | open
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | open | 31 | SS 35/10 Lesnye Polyany | 10+10 | 0.849 | 7.929 | 1.212 | 120 | 6.717 | 0 | 10.5 | 3.783 | 3.783 | open
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | open | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 4.746 | 10.596 | 2.338 | 120 | 8.258 | 0 | 6.62 | -1.638 | -1.638 | closed
33 | SS 35/10 Nekrasovo | 10+10 | 10 | 10 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 10.5 | -0.67 | -0.67 | closed | 33 | SS 35/10 Nekrasovo | 10+10 | 1.5384 | 12.7084 |  |  | 12.7084 | 0 | 10.5 | -2.2084 | -2.2084 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | open | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.02 | 0.75 | 0.398 | 120 | 0.352 | 0 | 2.63 | 2.278 | 2.278 | open
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | open | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.7506 |  |  | 22.7506 | 0 | 26.25 | 3.4994 | 3.4994 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 8.4306 |  |  | 8.4306 | 0 | 26.25 | 17.8194
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.05 | 14.32 |  |  | 14.32 | 0 | 26.25 | 11.93
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | open | 36 | SS 110/6/6 Orion | 40+40 | 0.85634 | 15.5663 |  |  | 15.5663 | 0 | 42 | 26.4337 | 26.4337 | open
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 23.9815 |  |  | 23.9815 | 0 | 21 | -2.9815 | -2.9815 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.0185 |  |  | 6.0185 | 0 | 21 | 14.9815
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.11302 | 17.963 |  |  | 17.963 | 0 | 21 | 3.037
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | open | 38 | SS 110/10 Pereval | 16+16 | 9.6489 | 18.1589 |  |  | 18.1589 | 0 | 16.8 | -1.3589 | -1.3589 | closed
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | open | 39 | SS 110/6/6 Perekop | 25+25 | 0.66846 | 10.9985 |  |  | 10.9985 | 0 | 26.25 | 15.2515 | 15.2515 | open
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | open | 40 | SS 110/6/6 Poligraf | 40+40 | 3.6221 | 37.5921 |  |  | 37.5921 | 0 | 42 | 4.4079 | 4.4079 | open
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | open | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.155 | 0.52 | 120 | 3.635 | 0 | 10.5 | 6.865 | 6.865 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 1.048 |  |  | 1.048 | 0 | 10.5 | 9.452
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.287 | 3.107 | 0.52 | 120 | 2.587 | 0 | 10.5 | 7.913
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | open | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.7093 | 3.7593 | 0.26 | 120 | 3.4993 | 0 | 2.63 | -0.8693 | -0.8693 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | open | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.01 | 0.24 | 0.052 | 120 | 0.188 | 0 | 2.63 | 2.442 | 2.442 | open
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | open | 44 | SS 110/6/6 Severnaya | 63+63 | 6.7866 | 44.7767 |  |  | 44.7767 | 0 | 66.15 | 21.3734 | 21.3734 | open
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | open | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.544 | 1.884 | 0.987 | 120 | 0.897 | 0 | 2.63 | 1.733 | 1.733 | open
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | open | 46 | SS 110/6 Tormoznaya | 16+16 | 0.33224 | 14.8402 |  |  | 14.8402 | 0 | 16.8 | 1.9598 | 1.9598 | open
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | open | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0 | 0.34 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | open
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | open | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.304 | 0.994 | 0.191 | 120 | 0.803 | 0 | 2.63 | 1.827 | 1.827 | open
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.313 | 7.573 |  |  | 7.573 | 0 | 6.62 | -0.953 | -0.953 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | open | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.125 | 0.845 |  |  | 0.845 | 0 | 2.63 | 1.785 | 1.785 | open
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | open | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.858 | 2.438 | 0.346 | 120 | 2.092 | 0 | 4.2 | 2.108 | 2.108 | open
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | MVA 4: 2.92; Min 11: 2.83; Min 12: open | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8025 |  |  |  | 0 |  |  | 2.8175 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 2.13; MVA Т-2: 2.13 |  | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0125 | 0.8025 | 0.26 | 120 | 0.5425 | 0 | 3.36 | 2.8175
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | open | 54 | SS 110/10 Chayka | 25+25 | 2.1193 | 21.4993 |  |  | 21.4993 | 0 | 26.25 | 4.7507 | 4.7507 | open
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | open | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.454 | 3.024 | 0.156 | 120 | 2.868 | 0 | 2.63 | -0.238 | -0.238 | closed
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | open | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.67 | 2.1 |  |  | 2.1 | 0 | 4.2 | 2.1 | 2.1 | open
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | open | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 6.0268 | 38.0068 |  |  | 38.0068 | 0 | 42 | 3.9932 | 3.9932 | open
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | open | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.453 | 7.333 |  |  | 7.333 | 0 | 26.25 | 18.917 | 18.917 | open
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | open | 59 | ПС 110/6/6 Kotorosl | 25+25 | 1.2351 | 7.2751 |  |  | 7.2751 |  | 26.25 | 18.9749 | 18.9749 | open
60 | SS 35/6 Kelnot | 3,2 | 3.2 |  | 0.29 | 0.29 |  | 3.36 | 1 day and night | 0.29 | 0 | 3.36 | 3.07 | 3.07 | open | 60 | SS 35/6 Kelnot | 3,2 | 0 | 0.29 | 3.36 | 1 day and night | 0.29 |  | 3.36 | 3.07 | 3.07 | open
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | open | 61 | SS 110/10 Altynovo | 6,3+6,3 | 0.7315 | 4.0315 |  |  | 4.0315 | 0 | 6.62 | 2.5885 | 2.5885 | open
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | open | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 10.2282 |  |  | 10.2282 | 0 | 10.5 | 0.27175 | 0.27175 | open
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 4.157 |  |  | 4.157 | 0 | 10.5 | 6.343
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Nom. capacity LV, МVА | 16+10 | 1.6212 | 6.0712 |  |  | 6.0712 | 0 | 10.5 | 4.4288
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | open | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.7665 | 0.537 | 120 | 3.2295 | 0 | 10.5 | 7.2705 | 7.2705 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.4255 |  |  | 2.4255 | 0 | 10.5 | 8.0745
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.041 | 1.341 | 0.537 | 120 | 0.804 | 0 | 10.5 | 9.696
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | open | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | open
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | closed | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | closed
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | open | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.731 |  |  | 1.731 | 0 | 6.62 | 4.889 | 4.889 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 0.36; MVA Т-2: 0.36; Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.36 |  |  | 0.36 | 0 | 6.62 | 6.26
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.031 | 1.371 |  |  | 1.371 | 0 | 6.62 | 5.249
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | closed | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 23.1172 | 0.97 | 120 | 22.1472 | 0 | 6.62 | -15.5272 | -15.5272 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 10.9357 |  |  | 10.9357 | 0 | 6.62 | -4.3157
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 9.4915 | 12.1815 | 0.97 | 120 | 11.2115 | 0 | 6.62 | -4.5915
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | open | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 32.9065 |  |  | 32.9065 | 0 | 26.25 | -6.6565 | -6.6565 | closed
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 18.3055 |  |  | 18.3055 | 0 | 26.25 | 7.9445
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | open | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.4745 | 2.2345 |  |  | 2.2345 | 0 | 2.63 | 0.3955 | 0.3955 | open
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | closed | 71 | SS 110/35/10 Rostov | 20+25 |  | 23.191 |  |  | 23.191 | 0 | 21 | -2.191 | -2.191 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 1.938 |  |  | 1.938 | 0 | 21 | 19.062
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 1.703 | 21.253 |  |  | 21.253 | 0 | 21 | -0.253
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | closed | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 11.8963 |  |  | 11.8963 | 0 | 6.62 | -5.2763 | -5.2763 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 5.7023 |  |  | 5.7023 | 0 | 6.62 | 0.91775
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.704 | 6.194 |  |  | 6.194 | 0 | 6.62 | 0.426
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | open | 73 | SS 110/35/10 Uglich | 25+25 |  | 27.1479 |  |  | 27.1479 | 0 | 26.25 | -0.8979 | -0.8979 | closed
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 18.7184 |  |  | 18.7184 | 0 | 26.25 | 7.5316
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 3.8395 | 8.4295 |  |  | 8.4295 | 0 | 26.25 | 17.8205
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | open | 74 | SS 110/10 Ustye | 10+10 | 0.208 | 4.558 | 0.797 | 120 | 3.761 | 0 | 10.5 | 6.739 | 6.739 | open
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | open | 75 | SS 110/10 Shurskol | 10+10 | 0.055 | 1.395 | 0.97 | 120 | 0.425 | 0 | 10.5 | 10.075 | 10.075 | open
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | open | 76 | SS 110/10 Yur.Sloboda | 10+10 | 0.896 | 8.066 | 0.866 | 120 | 7.2 | 0 | 10.5 | 3.3 | 3.3 | open
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.075 | 1.005 |  |  | 1.005 | 0 | 2.63 | 1.625 | 1.625 | open
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | open | 78 | SS 35/6 Batki | 1,6+1,6 | 0.271 | 1.411 |  |  | 1.411 | 0 | 1.68 | 0.269 | 0.269 | open
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | open | 79 | SS 35/10 Beregovaya | 1,6 | 0.01 | 0.19 | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | open
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | open | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.053 | 1.813 | 0.225 |  | 1.588 | 0 | 2.63 | 1.042 | 1.042 | open
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | open | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.262 | 0.762 | 0.087 | 120 | 0.675 | 0 | 1.68 | 1.005 | 1.005 | open
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | open | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.163 | 0.913 | 0.52 | 120 | 0.393 | 0 | 1.68 | 1.287 | 1.287 | open
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | open | 83 | SS 35/10 Glebovo | 2,5+2,5 | 2.13 | 4.21 |  |  | 4.21 | 0 | 2.63 | -1.58 | -1.58 | closed
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.227 | 1.157 |  |  | 1.157 | 0 | 2.63 | 1.473 | 1.473 | open
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | open | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.07 | 1.18 |  |  | 1.18 | 0 | 1.68 | 0.5 | 0.5 | open
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | open | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.078 | 1.618 |  |  | 1.618 | 0 | 1.68 | 0.062 | 0.062 | open
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | open | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0795 | 1.5695 |  |  | 1.5695 | 0 | 2.63 | 1.0605 | 1.0605 | open
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | open | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 2.502 | 4.742 |  |  | 4.742 | 0 | 6.62 | 1.878 | 1.878 | open
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | open | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | open
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | open | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.204 | 2.934 | 0.953 | 120 | 1.981 | 0 | 4.2 | 2.219 | 2.219 | open
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | open | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.328 | 1.678 |  |  | 1.678 | 0 | 2.63 | 0.952 | 0.952 | open
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | open | 92 | SS 35/6 Kupan | 2,5+2,5 | 0.90874 | 3.4887 |  |  | 3.4887 | 0 | 2.63 | -0.85874 | -0.85874 | closed
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | open | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.21 | 1.2 | 0.502 | 120 | 0.698 | 0 | 2.63 | 1.932 | 1.932 | open
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | open | 94 | SS 35/10 Nagorye | 4,0+4,0 | 1.381 | 4.871 |  |  | 4.871 | 0 | 4.2 | -0.671 | -0.671 | closed
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | open | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.107 | 2.237 | 0.087 | 120 | 2.15 | 0 | 4.2 | 2.05 | 2.05 | open
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | open | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.2165 | 1.3265 |  |  | 1.3265 | 0 | 2.63 | 1.3035 | 1.3035 | open
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | open | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.026 | 0.936 | 0.035 | 120 | 0.901 | 0 | 2.63 | 1.729 | 1.729 | open
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | open | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.077 | 1.357 |  |  | 1.357 | 0 | 2.63 | 1.273 | 1.273 | open
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | closed | 99 | SS 35/10 Saraevo | 1+1,6 | 0.798 | 2.118 |  |  | 2.118 | 0 | 1.05 | -1.068 | -1.068 | closed
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | open | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 0.977 | 2.427 | 0.953 | 120 | 1.474 | 0 | 2.63 | 1.156 | 1.156 | open
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | open | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.068 | 0.688 | 0.052 | 120 | 0.636 | 0 | 4.2 | 3.564 | 3.564 | open
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | open | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 0.9441 | 2.0441 |  |  | 2.0441 | 0 | 1.68 | -0.3641 | -0.3641 | closed
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | closed | 103 | SS 35/10 Solomidino | 2.5 | 0.948 | 2.148 | 0.866 | 1 day and night | 2.148 | 0 | 0.866 | -1.282 | -1.282 | closed
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | open | 104 | SS 35/10 Stavotino | 4,0+4,0 | 0.362 | 1.832 | 0.346 | 120 | 1.486 | 0 | 4.2 | 2.714 | 2.714 | open
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | open | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.034 | 0.434 | 0.052 | 120 | 0.382 | 0 | 2.63 | 2.248 | 2.248 | open
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | open | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 0.84 | 1.69 |  |  | 1.69 | 0 | 2.63 | 0.94 | 0.94 | open
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | open | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.182 | 0.562 |  |  | 0.562 | 0 | 2.63 | 2.068 | 2.068 | open
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | open | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.062 | 1.172 | 0.242 | 120 | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | open | 109 | SS 35/10 Neksans | 10+10 | 0 | 1.93 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | open
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | closed | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.0549 | 10.7549 |  |  | 10.7549 | 0 | 10.5 | -0.2549 | -0.2549 | closed
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | open | 111 | SS 110/10 Tishino | 25+25 | 0.173 | 18.423 |  |  | 18.423 | 0 | 26.25 | 7.827 | 7.827 | open
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | open | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.012 | 2.372 | 0.069 | 120 | 2.303 | 0 | 6.62 | 4.317 | 4.317 | open
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | open | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.13496 | 20.165 |  |  | 20.165 | 0 | 26.25 | 6.085 | 6.085 | open
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | open | 115 | SS 110/10 Optika | 10+10 | 0.25 | 5.64 | 0.26 | 120 | 5.38 | 0 | 10.5 | 5.12 | 5.12 | open
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | open | 116 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 7.82 |  |  | 7.82 | 0 | 16.8 | 8.98 | 8.98 | open
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | open | 117 | SS 110/6/6 Zapadnaya | 63+63 | 1.2415 | 29.1415 |  |  | 29.1415 | 0 | 66.15 | 37.0085 | 37.0085 | open
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | open | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.881 |  |  | 10.881 | 0 | 42 | 31.119 | 31.119 | open
| Nom. capacity MV, МVА | 40+40 |  |  | MVA 4: 0; MVA Т-1: 0; MVA Т-2: 0 |  | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.131 | 10.881 |  |  | 10.881 | 0 | 42 | 31.119
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | open | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.1635 |  |  | 15.1635 | 0 | 16.8 | 1.6365 | 1.6365 | open
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 10.1725 |  |  | 10.1725 | 0 | 16.8 | 6.6275
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.031 | 4.991 |  |  | 4.991 | 0 | 16.8 | 11.809
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open | 121 | SS 110/6 Dock yard | 10+10 | 0.144 | 5.464 |  |  | 5.464 | 0 | 10.5 | 5.036 | 5.036 | open
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | open | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.42 | 3.84 |  |  | 3.84 | 0 | 6.62 | 2.78 | 2.78 | open
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | open | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 2.449 |  |  | 2.449 | 0 | 4.2 | 1.751 | 1.751 | open
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | open | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.266 | 0.946 |  |  | 0.946 | 0 | 1.68 | 0.734 | 0.734 | open
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | open | 125 | SS 110/6 Veretye | 25+25 | 1.088 | 22.448 |  |  | 22.448 | 0 | 26.25 | 3.802 | 3.802 | open
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | open | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 1.136 | 3.936 | 0.554 | 120 | 3.382 | 0 | 4.2 | 0.818 | 0.818 | open
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | open | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.018 | 1.218 | 0.017 | 120 | 1.201 | 0 | 2.63 | 1.429 | 1.429 | open
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | open | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.079 | 0.899 |  |  | 0.899 | 0 | 1.68 | 0.781 | 0.781 | open
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | open | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.003 | 0.593 | 0.294 | 120 | 0.299 | 0 | 1.68 | 1.381 | 1.381 | open
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | open | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | open
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | open | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.283 | 1.593 |  |  | 1.593 | 0 | 2.63 | 1.037 | 1.037 | open
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | open | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.688 | 4.998 |  |  | 4.998 | 0 | 6.62 | 1.622 | 1.622 | open
133 | SS 35/10 Breytovo | 6,3+4,0 | 6.3 | 4 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 4.2 | -0.4 | -0.4 | closed | 133 | SS 35/10 Breytovo | 6,3+4,0 | 1.1 | 5.7 |  |  | 5.7 | 0 | 4.2 | -1.5 | -1.5 | closed
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | open | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.015 | 1.075 | 0.208 | 120 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | open
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | open | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.01 | 0.92 | 0.173 | 120 | 0.747 | 0 | 2.63 | 1.883 | 1.883 | open
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | open | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0 | 0.96 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | open
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | open | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.09 | 0.63 |  |  | 0.63 | 0 | 2.63 | 2 | 2 | open
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | open | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.119 | 1.519 | 0.364 | 120 | 1.155 | 0 | 1.68 | 0.525 | 0.525 | open
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | open | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.002 | 0.222 | 0.017 | 120 | 0.205 | 0 | 1.68 | 1.475 | 1.475 | open
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | open | 140 | SS 35/10 Borok | 2,5+4,0 | 0.209 | 1.769 | 0.277 | 120 | 1.492 | 0 | 2.63 | 1.138 | 1.138 | open
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | open | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.472 | 4.232 |  |  | 4.232 | 0 | 6.62 | 2.388 | 2.388 | open
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open | 142 | SS 110/10 Volga | 5,6+6,3 | 0 | 2.13 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | open | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.251 | 2.341 | 0.104 | 120 | 2.237 | 0 | 2.63 | 0.393 | 0.393 | open
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | open | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 21.049 |  |  | 21.049 | 0 | 26.25 | 5.201 | 5.201 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 4.579 |  |  | 4.579 | 0 | 26.25 | 21.671
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.06 | 16.47 |  |  | 16.47 | 0 | 26.25 | 9.78
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | open | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.11 | 1.212 | 120 | 6.898 | 0 | 10.5 | 3.602 | 3.602 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 0.79 |  |  | 0.79 | 0 | 10.5 | 9.71
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.07 | 7.32 | 1.212 | 120 | 6.108 | 0 | 10.5 | 4.392
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | open | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.286 | 3.136 |  |  | 3.136 | 0 | 6.62 | 3.484 | 3.484 | open
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | open | 147 | SS 110/35/10 Lom | 10+10 |  | 9.0014 | 1.368 | 120 | 7.6334 | 0 | 10.5 | 2.8666 | 2.8666 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 7.136 |  |  | 7.136 | 0 | 10.5 | 3.364
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.3854 | 1.8654 | 1.368 | 120 | 0.4974 | 0 | 10.5 | 10.0026
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | open | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.095 | 0.895 |  |  | 0.895 | 0 | 1.68 | 0.785 | 0.785 | open
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | open | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 9.2385 | 0.242 | 120 | 8.9965 | 0 | 10.5 | 1.5035 | 1.5035 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 8.4835 |  |  | 8.4835 | 0 | 10.5 | 2.0165
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.135 | 0.755 | 0.242 | 120 | 0.513 | 0 | 10.5 | 9.987
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | MVA 4: 3.21; Min 11: 1.432; Min 12: open | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.446 |  |  |  | 0 |  |  | 1.432 | open
| Nom. capacidty MV, МVА | 6.3 |  |  | MVA 4: 2.91; MVA Т-1: 2.91 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.146 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.3 | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | open | 151 | SS 35/10 Beloe | 2.5 | 0.059 | 0.769 | 1.472 | 1 day and night | 0.769 | 0 | 1.472 | 0.703 | 0.703 | open
152 | SS 110/35/10 Glebovo | 10 | 10 |  | MVA 4: 6.05; Min 11: -2.505; Min 12: closed | 152 | SS 110/35/10 Glebovo | 10 |  | 7.829 |  |  |  | 0 |  |  | -3.597 | closed
| Nom. capacity MV, МVА | 10 |  |  | MVA 4: 2.87; MVA Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 3.557 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.092 | 4.272 | 0.675 | 1 day and night | 4.272 | 0 | 0.675 | -3.597
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | open | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | open
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | open | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | open
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | open | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | open
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | open | 157 | SS 35/10 Ermakovo | 1.6 | 0.063 | 1.083 | 1.212 | 1 day and night | 1.083 | 0 | 1.212 | 0.129 | 0.129 | open
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | open | 158 | SS 35/10 Milyushino | 1.6 | 0.632 | 1.472 | 0.918 | 1 day and night | 1.472 | 0 | 0.918 | -0.554 | -0.554 | closed
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | closed | 159 | SS 35/10 Sutka | 2.5 | 0.032 | 0.772 | 0.554 | 1 day and night | 0.772 | 0 | 0.554 | -0.218 | -0.218 | closed
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | open | 160 | SS 35/10 Sit | 1.6 | 0.241 | 0.911 | 0.68 | 1 day and night | 0.911 | 0 | 0.68 | -0.231 | -0.231 | closed
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | closed | 161 | SS 35/10 Gorelovo | 1.6 | 0.321 | 1.521 | 0.901 | 1 day and night | 1.521 | 0 | 0.901 | -0.62 | -0.62 | closed
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | open | 164 | SS 35/10 Levoberezhnaya | 4 | 0.3326 | 1.6426 | 1.334 | 1 day and night | 1.6426 |  | 1.334 | -0.3086 | -0.3086 | closed
| Total: | 2857.9 | 1455.5 | 1402.4 | MVA 4: 885.648 |  | Total: | 2857.9 |  | 991.966
| deficit |  |  |  | Min 11: -15.784 |  | deficit | [9 empty] | -75.594
| proficit |  |  |  | Min 11: 650.045 |  | proficit | [9 empty] | 545.369
Note on G215: Т3
Note on G213: Т3
Note on G193: Т2
Note on H193: Т3

## Свод тек.деф.зима
The list of closed supply centers of IDGC of Centre with winter load (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA |  |  |  | Current deficit, MVA
Yarenergo
1 | SS 35/10 Shirinye | 2.5 |  |  |  |  | -0.47
2 | SS 35/10 Nekrasovo | 10+10 |  |  |  |  | -0.67
3 | SS 110/35/6 Pavlovskaya | 20+25 |  |  |  |  | -2.56
4 | SS 35/10 Tutaev-35 | 6,3+6,3 |  |  |  |  | -0.64
5 | SS 110/6 Kinoplyonka | 6,3+10 |  |  |  |  | -3.28
6 | SS 110/35/10 Nila | 6,3+6,3 |  |  |  |  | -2.76
7 | SS 110/35/10 Rostov | 20+25 |  |  |  |  | -0.21
8 | SS 110/35/10 Technical school | 6,3+6,3 | 3.48 | 3.48 | 0 | 2.63 | -1
9 | SS 35/10 Saraevo | 1+1,6 | 11.67 | 11.67 | 0 | 10.5 | -0.27
10 | SS 35/10 Solomidino | 2.5 | 25.25 | 25.25 | 0 | 21 | -0.334
11 | SS 35/6 Pribrezhnaya | 10+10 | 45.91 | 45.91 | 0 | 42 | -0.2
12 | SS 35/10 Breytovo | 6,3+4,0 | 6.83 | 6.83 | 0 | 6.62 | -0.4
13 | SS 110/35/10 Glebovo | 10 |  |  |  |  | -2.505
14 | SS 35/10 Sutka | 2.5 |  |  |  |  | -0.186
15 | SS 35/10 Gorelovo | 1.6 |  |  |  |  | -0.299
Total current deficit (winter) | [6 empty] | -15.784

## Свод ожид.деф.зима
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Ярэнерго
1 | SS 35/10 Shirinye | 2.5 | [8 empty] | -0.635 | closed
2 | SS 110/35/10 Abbakumtsevo | 10+10 | [8 empty] | -7.0999 | closed
3 | SS 35/10 Ananyino | 1,6+1,6 | [8 empty] | -0.303 | closed
4 | SS 35/10 Vatolino | 4,0+4,0 | [8 empty] | -0.816 | closed
5 | SS 35/10 Guzitsino | 4,0+4,0 | [8 empty] | -2.3039 | closed
6 | SS 35/6 Zavolzhskaya | 10+10 | [8 empty] | -1.3992 | closed
7 | SS 35/10 Modelovo-2 | 6,3+6,3 | [8 empty] | -1.638 | closed
8 | SS 35/10 Nekrasovo | 10+10 | [8 empty] | -2.2084 | closed
9 | SS 110/35/6 Pavlovskaya | 20+25 | [8 empty] | -2.9815 | closed
10 | SS 110/10 Pereval | 16+16 | [8 empty] | -1.3589 | closed
11 | SS 35/10 Preventorium | 2,5+2,5 | [8 empty] | -0.8693 | closed
12 | SS 35/10 Tutaev-35 | 6,3+6,3 | [8 empty] | -0.953 | closed
13 | SS 35/6 Chebakovo | 2,5+2,5 | [8 empty] | -0.238 | closed
14 | SS 110/6 Kinoplyonka | 6,3+10 | [8 empty] | -6.134 | closed
15 | SS 110/35/10 Nila | 6,3+6,3 | [8 empty] | -15.5272 | closed
16 | SS 110/35/6 Pereslavl | 25+25 | [8 empty] | -6.6565 | closed
17 | SS 110/35/10 Rostov | 20+25 | [8 empty] | -2.191 | closed
18 | SS 110/35/10 Technical school | 6,3+6,3 | [8 empty] | -5.2763 | closed
19 | SS 110/35/10 Uglich | 25+25 | [8 empty] | -0.8979 | closed
20 | SS 35/10 Glebovo | 2,5+2,5 | [8 empty] | -1.58 | closed
21 | SS 35/6 Kupan | 2,5+2,5 | [8 empty] | -0.85874 | closed
22 | SS 35/10 Nagorye | 4,0+4,0 | [8 empty] | -0.671 | closed
23 | SS 35/10 Saraevo | 1+1,6 | [8 empty] | -1.068 | closed
24 | ПС 35/10 Скоморохово | 1,6+1,6 | [8 empty] | -0.3641 | closed
25 | SS 35/10 Solomidino | 2.5 | [8 empty] | -1.282 | closed
26 | SS 35/6 Pribrezhnaya | 10+10 | [8 empty] | -0.2549 | closed
27 | SS 35/10 Breytovo | 6,3+4,0 | [8 empty] | -1.5 | closed
28 | SS 110/35/10 Glebovo | 10 | [8 empty] | -3.597 | closed
29 | SS 35/10 Milyushino | 1.6 | [8 empty] | -0.554 | closed
30 | SS 35/10 Sutka | 2.5 | [8 empty] | -0.218 | closed
31 | ПС 35/10 Сить | 1.6 | [8 empty] | -0.231 | closed
32 | SS 35/10 Gorelovo | 1.6 | [8 empty] | -0.62 | closed
33 | SS 35/10 Levoberezhnaya | 4 | [8 empty] | -0.3086 | closed
| Total: | [9 empty] | -72.5943