## апрель 2009
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including redistribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | SS 35/10 Matveevo | 1.6 | 0.35 | 0.837 | 24 hours | 0.837 | 0 | 0.837 | 0.487 | 0.487 | opened
2 | SS 35/10 Mikhailovskoe | 6.3 | 1.34 | 6.62 | 24 hours | 6.62 | 0 | 6.62 | 5.28 | 5.28 | opened
3 | SS 35/10 Shirinye | 2.5 | 2.56 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | -1.798 | -1.798 | closed
4 | SS 110/10 Pokrov | 2.5 | 0.29 | 0.945 | 24 hours | 0.945 | 0 | 0.945 | 0.655 | 0.655 | opened
5 | SS 35/10 Obnora | 1.6 | 0.4 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.7 | 0.7 | opened
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 11.1 |  |  | 11.1 | 0 | 10.5 | -0.6 | -0.6 | closed
| Nom. capacity MV, МVА | 10+10 | 8.84 |  |  | 8.84 | 0 | 10.5 | 1.66
| Nom. capacity LV, МVА | 10+10 | 2.26 |  |  | 2.26 | 0 | 10.5 | 8.24
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.49 |  |  | 1.49 | 0 | 1.68 | 0.19 | 0.19 | opened
8 | SS 110/10/10 Bragino | 40+40 | 35.09 | 1.937 | 120 | 33.153 | 0 | 42 | 8.847 | 8.847 | opened
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 2.85 | 0.843 | 120 | 2.007 | 0 | 4.2 | 2.193 | 2.193 | opened
10 | SS 35/10 Vatolino | 2,5+4,0 | 3.52 |  |  | 3.52 | 0 | 2.63 | -0.89 | -0.89 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 4.85 |  |  | 4.85 | 0 | 6.62 | 1.77 | 1.77 | opened
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 2.28 |  |  | 2.28 | 0 | 4.2 | 1.92 | 1.92 | opened
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.76 |  |  | 0.76 | 0 | 1.68 | 0.92 | 0.92 | opened
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 1.66 |  |  | 1.66 | 0 | 4.2 | 2.54 | 2.54 | opened
15 | SS 35/10 Volna | 2,5+2,5 | 3.06 |  |  | 3.06 | 0 | 2.63 | -0.43 | -0.43 | closed
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 1.89 | 0.2 | 120 | 1.69 | 0 | 2.63 | 0.94 | 0.94 | opened
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.52 | 0.22 | 120 | 0.3 | 0 | 2.63 | 2.33 | 2.33 | opened
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 3.05 | 0.674 | 120 | 2.376 | 0 | 4.2 | 1.824 | 1.824 | opened
19 | SS 35/10 Guzitsino | 4,0+4,0 | 2.91 | 1.02 | 120 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 1.75 |  |  | 1.75 | 0 | 6.62 | 4.87 | 4.87 | opened
21 | SS 110/6 Depo | 16+16 | 8.33 |  |  | 8.33 | 0 | 16.8 | 8.47 | 8.47 | opened
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.23 | 0.956 | 120 | 0.274 | 0 | 1.68 | 1.406 | 1.406 | opened
23 | SS 110/10 Druzhba | 16+16 | 6.33 | 0.16 | 120 | 6.17 | 0 | 16.8 | 10.63 | 10.63 | opened
24 | SS 35/10 Dubki | 6,3+6,3 | 4.62 | 0.787 | 120 | 3.833 | 0 | 6.62 | 2.787 | 2.787 | opened
25 | SS 35/10 Dybino | 2,5+2,5 | 1.22 |  |  | 1.22 | 0 | 2.63 | 1.41 | 1.41 | opened
26 | SS 35/6 Zavolzhskaya | 10+10 | 12.43 |  |  | 12.43 | 0 | 10.5 | -1.93 | -1.93 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 38.2 |  |  | 38.2 | 0 | 42 | 3.8 | 3.8 | opened
28 | SS 35/10 Koza | 1,6+1,6 | 0.41 | 0.179 | 120 | 0.231 | 0 | 1.68 | 1.449 | 1.449 | opened
29 | SS 110/35/6 Konstantinovo | 20+20 | 13.99 | 0.1 | 120 | 13.89 | 0 | 21 | 7.11 | 7.11 | opened
| Nom. capacity MV, МVА | 20+20 | 9.73 |  |  | 9.73 | 0 | 21 | 11.27
| Nom. capacity LV, МVА | 20+20 | 4.26 | 0.1 | 120 | 4.16 | 0 | 21 | 16.84
30 | SS 35/10 Kurba | 2,5+2,5 | 2.58 | 1.71 | 120 | 0.87 | 0 | 2.63 | 1.76 | 1.76 | opened
31 | SS 35/10 Lesnye Polyany | 10+10 | 6.92 | 0.48 | 120 | 6.44 | 0 | 10.5 | 4.06 | 4.06 | opened
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 7.16 | 3.69 | 120 | 3.47 | 0 | 6.62 | 3.15 | 3.15 | opened
33 | SS 35/10 Nekrasovo | 10+10 | 9.86 |  |  | 9.86 | 0 | 10.5 | 0.64 | 0.64 | opened
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 1.049 | 0.38 | 120 | 0.669 | 0 | 2.63 | 1.961 | 1.961 | opened
35 | SS 110/35/6 Oil refinary plant | 25+25 | 16.28 |  |  | 16.28 | 0 | 26.25 | 9.97 | 9.97 | opened
| Nom. capacity MV, МVА | 25+25 | 8.4 |  |  | 8.4 | 0 | 26.25 | 17.85
| Nom. capacity LV, МVА | 25+25 | 7.88 |  |  | 7.88 | 0 | 26.25 | 18.37
36 | SS 110/6/6 Orion | 40+40 | 14.32 |  |  | 14.32 | 0 | 42 | 27.68 | 27.68 | opened
37 | SS 110/35/6 Pavlovskaya | 20+25 | 21.5 |  |  | 21.5 | 0 | 21 | -0.5 | -0.5 | closed
| Nom. capacity MV, МVА | 20+25 | 7.1 |  |  | 7.1 | 0 | 21 | 13.9
| Nom. capaity LV, МVА | 20+25 | 14.4 |  |  | 14.4 | 0 | 21 | 6.6
38 | SS 110/10 Pereval | 16+16 | 8.6 |  |  | 8.6 | 0 | 16.8 | 8.2 | 8.2 | opened
39 | SS 110/6/6 Perekop | 25+25 | 13.51 |  |  | 13.51 | 0 | 26.25 | 12.74 | 12.74 | opened
40 | SS 110/6/6 Poligraf | 40+40 | 40.327 |  |  | 40.327 | 0 | 42 | 1.673 | 1.673 | opened
41 | SS 110/35/10 Prechistoe | 10+10 | 5.37 | 0.213 | 120 | 5.157 | 0 | 10.5 | 5.343 | 5.343 | opened
| Nom. capacity MV, МVА | 10+10 | 1.79 |  |  | 1.79 | 0 | 10.5 | 8.71
| Nom. capacity LV, МVА | 10+10 | 3.58 | 0.213 | 120 | 3.367 | 0 | 10.5 | 7.133
42 | SS 35/10 Preventorium | 2,5+2,5 | 0.61 | 0.316 | 120 | 0.294 | 0 | 2.63 | 2.336 | 2.336 | opened
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.12 | 0.044 | 120 | 0.076 | 0 | 2.63 | 2.554 | 2.554 | opened
44 | SS 110/6/6 Severnaya | 63+63 | 39.51 |  |  | 39.51 | 0 | 66.15 | 26.64 | 26.64 | opened
45 | SS 35/10 Sereda | 2,5+2,5 | 1.36 | 0.108 | 120 | 1.252 | 0 | 2.63 | 1.378 | 1.378 | opened
46 | SS 110/6 Tormoznaya | 16+16 | 16.63 |  |  | 16.63 | 0 | 16.8 | 0.17 | 0.17 | opened
47 | SS 110/6 Petrol station pump | 16+16 | 4.52 |  |  | 4.52 | 0 | 16.8 | 12.28 | 12.28 | opened
48 | SS 35/10 Troitsa | 2,5+2,5 | 0.5 | 0.108 | 120 | 0.392 | 0 | 2.63 | 2.238 | 2.238 | opened
49 | SS 35/10 Tunoshna | 4,0+2,5 | 0.61 | 0.01 | 120 | 0.6 | 0 | 2.63 | 2.03 | 2.03 | opened
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 7.54 |  |  | 7.54 | 0 | 6.62 | -0.92 | -0.92 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.78 |  |  | 0.78 | 0 | 2.63 | 1.85 | 1.85 | opened
52 | SS 35/10 Urozhay | 4,0+4,0 | 3.2 | 0.825 | 120 | 2.375 | 0 | 4.2 | 1.825 | 1.825 | opened
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.75 | 0.134 | 120 | 0.31 | 0 | 3.36 | 3.05 | 2.054 | opened
| Nom. capacity MV, МVА | 6.3 | 2.31
| Nom. capacity LV, МVА | 6.3 | 1.44 | 0.134 | 120 | 1.306 | 0 | 3.36 | 2.054
54 | SS 110/10 Chayka | 25+25 | 22.04 |  |  | 22.04 | 0 | 26.25 | 4.21 | 4.21 | opened
55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.78 | 0.19 | 120 | 1.59 | 0 | 2.63 | 1.04 | 1.04 | opened
56 | SS 35/10 Shchedrino | 4,0+4,0 | 2.19 |  |  | 2.19 | 0 | 4.2 | 2.01 | 2.01 | opened
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 32.63 |  |  | 32.63 | 0 | 42 | 9.37 | 9.37 | opened
58 | SS 110/10/6 Yartsevo | 25+25 | 10.32 |  |  | 10.32 | 0 | 26.25 | 15.93 | 15.93 | opened
59 | SS 110/10 Altynovo | 6,3+6,3 | 3.512 |  |  | 3.512 | 0 | 6.62 | 3.108 | 3.108 | opened
60 | SS 110/35/10 Borisogleb | 10+16 | 7.938 |  |  | 7.938 | 0 | 10.5 | 2.562 | 2.562 | opened
| Nom. capacity MV, МVА | 10+16 | 2.72 |  |  | 2.72 | 0 | 10.5 | 7.78
| Nom. capacity LV, МVА | 10+16 | 5.218 |  |  | 5.218 | 0 | 10.5 | 5.282
61 | SS 110/35/10 Vasilkovo | 10+10 | 2.78 | 0.472 | 120 | 2.308 | 0 | 10.5 | 8.192 | 8.192 | opened
| Nom. capacity MV, МVА | 10+10 | 1.732 |  |  | 1.732 | 0 | 10.5 | 8.768
| Nom. capacity LV, МVА | 10+10 | 1.048 | 0.472 | 120 | 0.576 | 0 | 10.5 | 9.924
62 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.28 | 0.07 | 120 | 0.21 | 0 | 6.62 | 6.41 | 6.41 | opened
63 | SS 110/6 Gavrilov Yam | 16+16 | 13.286 |  |  | 13.286 | 0 | 16.8 | 3.514 | 3.514 | opened
64 | SS 110/6 Kinoplyonka | 6,3+10 | 6.814 |  |  | 6.814 | 0 | 6.62 | -0.194 | -0.194 | closed
65 | SS 110/35/10 Klimatino | 6,3+6,3 | 1.257 |  |  | 1.257 | 0 | 6.62 | 5.363 | 5.363 | opened
| Nom. capacity MV, МVА | 6,3+6,3 | 0.313 |  |  | 0.313 | 0 | 6.62 | 6.307
| Nom. capacity LV, МVА | 6,3+6,3 | 0.944 |  |  | 0.944 | 0 | 6.62 | 5.676
66 | SS 110/35/10 Nila | 6,3+6,3 | 11.107 | 0.45 | 120 | 10.657 | 0 | 6.62 | -4.037 | -4.037 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 8.33 |  |  | 8.33 | 0 | 6.62 | -1.71
| Nom. capacity LV, МVА | 6,3+6,3 | 2.777 | 0.45 | 120 | 2.327 | 0 | 6.62 | 4.293
67 | SS 110/35/6 Pereslavl | 25+25 | 26.546 |  |  | 26.546 | 0 | 26.25 | -0.296 | -0.296 | closed
| Nom. capacity MV, МVА | 25+25 | 11.941 |  |  | 11.941 | 0 | 26.25 | 14.309
| Nom. capacity LV, МVА | 25+25 | 14.605 |  |  | 14.605 | 0 | 26.25 | 11.645
68 | SS 110/10 Ploski | 2,5+2,5 | 1.778 |  |  | 1.778 | 0 | 2.63 | 0.852 | 0.852 | opened
69 | SS 110/35/10 Rostov | 25+20 | 21.343 |  |  | 21.343 | 0 | 21 | -0.343 | -0.343 | closed
| Nom. capacity MV, МVА | 25+20 | 1.894 |  |  | 1.894 | 0 | 21 | 19.106
| Nom. Capacity LV, МVА | 25+20 | 19.449 |  |  | 19.449 | 0 | 21 | 1.551
70 | SS 110/35/10 Technical school | 6,3+6,3 | 8.359 |  |  | 8.359 | 0 | 6.62 | -1.739 | -1.739 | closed
| Nom. capacity MV, МVА | 6,3+6,3 | 4.041 |  |  | 4.041 | 0 | 6.62 | 2.579
| Nom. capacity LV, МVА | 6,3+6,3 | 4.318 |  |  | 4.318 | 0 | 6.62 | 2.302
71 | SS 110/35/10 Uglich | 25+25 | 24.206 |  |  | 24.206 | 0 | 26.25 | 2.044 | 2.044 | opened
| Nom. capacidty MV, МVА | 25+25 | 18.6 |  |  | 18.6 | 0 | 26.25 | 7.65
| Nom. capacity LV, МVА | 25+25 | 5.606 |  |  | 5.606 | 0 | 26.25 | 20.644
72 | SS 110/10 Ustye | 10+10 | 4.915 | 0.32 | 120 | 4.595 | 0 | 10.5 | 5.905 | 5.905 | opened
73 | SS 110/10 Shurskol | 10+10 | 1.976 | 1.18 | 120 | 0.796 | 0 | 10.5 | 9.704 | 9.704 | opened
74 | SS 110/10 Yur.Sloboda | 10+10 | 9.319 | 0.173 | 120 | 9.146 | 0 | 10.5 | 1.354 | 1.354 | opened
75 | SS 35/10 Aleshkino | 2,5+2,5 | 0.47 |  |  | 0.47 | 0 | 2.63 | 2.16 | 2.16 | opened
76 | SS 35/6 Batki | 1,6+1,6 | 1.548 |  |  | 1.548 | 0 | 1.68 | 0.132 | 0.132 | opened
77 | SS 35/10 Beregovaya | 1.6 | 0.25 | 1.71 | 24 hours | 1.71 | 0 | 1.71 | 1.46 | 1.46 | opened
78 | SS 35/10 Berendeevo | 2,5+2,5 | 1.428 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | -0.628 | -0.628 | closed
79 | SS 35/10 Vorzha | 1,8+1,8 | 0.524 | 0.454 | 120 | 0.07 | 0 | 1.89 | 1.82 | 1.82 | opened
80 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.09 | 0.182 | 120 | 0.908 | 0 | 1.68 | 0.772 | 0.772 | opened
81 | SS 35/10 Glebovo | 2,5+2,5 | 2.049 |  |  | 2.049 | 0 | 2.63 | 0.581 | 0.581 | opened
82 | SS 35/10 Gorki | 2,5+2,5 | 1.021 |  |  | 1.021 | 0 | 2.63 | 1.609 | 1.609 | opened
83 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.165 |  |  | 1.165 | 0 | 1.68 | 0.515 | 0.515 | opened
84 | SS 35/10 Zaozerye | 2,5+1,6 | 1.199 |  |  | 1.199 | 0 | 1.68 | 0.481 | 0.481 | opened
85 | SS 35/10 Ilyinskoe | 2,5+2,5 | 1.511 |  |  | 1.511 | 0 | 2.63 | 1.119 | 1.119 | opened
86 | SS 35/10 Kibernetik | 6,3+6,3 | 1.835 |  |  | 1.835 | 0 | 6.62 | 4.785 | 4.785 | opened
87 | SS 35/10 Klementyevo | 2.5 | 0.342 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.418 | 0.418 | opened
88 | SS 35/10 Krasnoe | 4,0+4,0 | 1.74 | 0.81 | 120 | 0.93 | 0 | 4.2 | 3.27 | 3.27 | opened
89 | SS 35/10 Kulakovo | 2,5+2,5 | 1.675 |  |  | 1.675 | 0 | 2.63 | 0.955 | 0.955 | opened
90 | SS 35/6 Kupan | 2,5+2,5 | 2.398 |  |  | 2.398 | 0 | 2.63 | 0.232 | 0.232 | opened
91 | SS 35/10 Markovo | 2,5+2,5 | 1.224 | 0.36 | 120 | 0.864 | 0 | 2.63 | 1.766 | 1.766 | opened
92 | SS 35/10 Nagorye | 4,0+4,0 | 3.343 |  |  | 3.343 | 0 | 4.2 | 0.857 | 0.857 | opened
93 | SS 35/10 Porechye | 6,3+6,3 | 1.911 | 0.036 | 120 | 1.875 | 0 | 6.62 | 4.745 | 4.745 | opened
94 | SS 35/10 Pruzhinino | 2,5+2,5 | 1.254 |  |  | 1.254 | 0 | 2.63 | 1.376 | 1.376 | opened
95 | SS 35/10 Ramenye | 2,5+2,5 | 0.839 | 0.087 | 120 | 0.752 | 0 | 2.63 | 1.878 | 1.878 | opened
96 | SS 35/10 Ryazantsevo | 1,6+1,6 | 1.853 |  |  | 1.853 | 0 | 1.68 | -0.173 | -0.173 | closed
97 | SS 35/10 Saraevo | 1+1,6 | 1.291 |  |  | 1.291 | 0 | 1.05 | -0.241 | -0.241 | closed
98 | SS 35/10 Selifontovo | 2,5+2,5 | 1.399 | 0.182 | 120 | 1.217 | 0 | 2.63 | 1.413 | 1.413 | opened
99 | SS 35/10 Semibratovo | 4,0+4,0 | 1.206 | 0.25 | 120 | 0.956 | 0 | 4.2 | 3.244 | 3.244 | opened
100 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.252 |  |  | 1.252 | 0 | 1.68 | 0.428 | 0.428 | opened
101 | SS 35/10 Solomidino | 2.5 | 0.612 | 1.18 | 24 hours | 1.18 | 0 | 1.18 | 0.568 | 0.568 | opened
102 | SS 35/10 Stavotino | 4,0+4,0 | 1.336 | 0.445 | 120 | 0.891 | 0 | 4.2 | 3.309 | 3.309 | opened
103 | SS 35/10 Urusovo | 2,5+2,5 | 0.529 | 0.053 | 120 | 0.476 | 0 | 2.63 | 2.154 | 2.154 | opened
104 | SS 35/10 Filimonovo | 2,5+2,5 | 0.522 |  |  | 0.522 | 0 | 2.63 | 2.108 | 2.108 | opened
105 | SS 35/10 Choporovo | 2,5+2,5 | 0.532 |  |  | 0.532 | 0 | 2.63 | 2.098 | 2.098 | opened
106 | SS 35/10 Shchurovo | 2,5+2,5 | 1.07 | 0.27 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened
107 | SS 35/10 Neksans | 10+10 | 1.619 |  |  | 1.619 | 0 | 10.5 | 8.881 | 8.881 | opened
108 | SS 35/6 Pribrezhnaya | 10+10 | 13.006 |  |  | 13.006 | 0 | 10.5 | -2.506 | -2.506 | closed
109 | SS 110/10 Product pipeline | 6,3+6,3 | 1.45 |  |  | 1.45 | 0 | 6.62 | 5.17 | 5.17 | opened
110 | SS 110/10 Nekouz | 6,3+6,3 | 2.82 | 0.084 | 120 | 2.736 | 0 | 6.62 | 3.884 | 3.884 | opened
111 | SS 110/6 Yuzhnaya | 25+25 | 19.89 |  |  | 19.89 | 0 | 26.25 | 6.36 | 6.36 | opened
112 | SS 110/10 Optika | 10+10 | 4.97 | 1.18 | 120 | 3.79 | 0 | 10.5 | 6.71 | 6.71 | opened
113 | SS 110/6 Poligrafmash | 16+16 | 8.54 |  |  | 8.54 | 0 | 16.8 | 8.26 | 8.26 | opened
114 | SS 110/6/6 Zapadnaya | 63+63 | 56.01 |  |  | 56.01 | 0 | 66.15 | 10.14 | 10.14 | opened
115 | SS 110/35/6 Volzhskaya | 40+40 | 8.3 |  |  | 8.3 | 0 | 42 | 33.7 | 33.7 | opened
| Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 | 8.3 |  |  | 7.9 | 0 | 42 | 34.1
116 | SS 110/35/6 Levoberezhnaya | 16+16 | 14.456 |  |  | 14.456 | 0 | 16.8 | 2.344 | 2.344 | opened
| Nom. capacity MV, МVА | 16+16 | 9.321 |  |  | 9.321 | 0 | 16.8 | 7.479
| Nom. capacity LV, МVА | 16+16 | 5.135 |  |  | 5.135 | 0 | 16.8 | 11.665
117 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 2.2 |  |  | 2.2 | 0 | 7.88 | 5.68 | 5.68 | opened
| Nom. capacity MV, МVА | 7,5+7,5 | 1.45 |  |  | 1.45 | 0 | 7.88 | 6.43
| Nom. capacity LV, МVА | 7,5+7,5 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13
118 | SS 110/6 Dock yard | 10+10 | 4.43 |  |  | 4.43 | 0 | 10.5 | 6.07 | 6.07 | opened
119 | SS 110/6 Selekhovo | 6,3+6,3 | 4.27 |  |  | 4.27 | 0 | 6.62 | 2.35 | 2.35 | opened
120 | SS 35/6 Kamenniki | 4,0+4,0 | 1.74 |  |  | 1.74 | 0 | 4.2 | 2.46 | 2.46 | opened
121 | SS 35/10 Shashkovo | 1,6+1,6 | 1.03 | 0.532 | 120 | 0.498 | 0 | 1.68 | 1.182 | 1.182 | opened
122 | SS 110/6 Мукуену | 25+25 | 19.05 |  |  | 19.05 | 0 | 26.25 | 7.2 | 7.2 | opened
123 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.53 | 0.83 | 120 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened
124 | SS 35/10 Arefino | 2,5+2,5 | 0.95 | 0.361 | 120 | 0.589 | 0 | 2.63 | 2.041 | 2.041 | opened
125 | SS 35/10 Knyazevo | 2,5+1,6 | 0.81 |  |  | 0.81 | 0 | 1.68 | 0.87 | 0.87 | opened
126 | SS 35/10 Pokrov | 1,6+1,6 | 0.71 | 0.34 | 120 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | opened
127 | SS 35/10 Anikovo | 2,5+2,5 | 1.13 | 0.29 | 120 | 0.84 | 0 | 2.63 | 1.79 | 1.79 | opened
128 | SS 35/10 Novoe selo | 2,5+2,5 | 0.05 |  |  | 0.05 | 0 | 2.63 | 2.58 | 2.58 | opened
129 | SS 35/10 Bolshoe selo | 6,3+6,3 | 5.2 |  |  | 5.2 | 0 | 6.62 | 1.42 | 1.42 | opened
130 | SS 35/10 Breytovo | 4,0+4,0 | 4.21 |  |  | 4.21 | 0 | 4.2 | -0.01 | -0.01 | closed
131 | SS 35/10 Stanilovo | 1,6+1,6 | 0.83 | 0.27 | 120 | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened
132 | SS 35/10 Znamovo | 2,5+2,5 | 0.82 | 0.82 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened
133 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.85 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | opened
134 | SS 35/10 Zapolye | 2,5+2,5 | 0.45 |  |  | 0.45 | 0 | 2.63 | 2.18 | 2.18 | opened
135 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.43 | 0.843 | 120 | 0.587 | 0 | 1.68 | 1.093 | 1.093 | opened
136 | SS 35/10 Latskoe | 1,6+2,5 | 0.24 | 0.053 | 120 | 0.187 | 0 | 1.68 | 1.493 | 1.493 | opened
137 | SS 35/10 Borok | 2,5+4,0 | 1.73 | 0.572 | 120 | 1.158 | 0 | 2.63 | 1.472 | 1.472 | opened
138 | SS 35/10 Myshkin | 6,3+6,3 | 4.31 | 0.386 | 120 | 3.924 | 0 | 6.62 | 2.696 | 2.696 | opened
139 | SS 110/10 Volga | 6,3+5,6 | 1.85 |  |  | 1.85 | 0 | 5.88 | 4.03 | 4.03 | opened
140 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 2 | 0.309 | 120 | 1.691 | 0 | 2.63 | 0.939 | 0.939 | opened
141 | SS 110/35/6 Vostochnaya | 25+25 | 19.27 |  |  | 19.27 | 0 | 26.25 | 6.98 | 6.98 | opened
| Nom. capacity MV, МVА | 25+25 | 3.688 |  |  | 3.688 | 0 | 26.25 | 22.562
| Nom. capacity LV, МVА | 25+25 | 15.582 |  |  | 15.582 | 0 | 26.25 | 10.668
142 | SS 110/35/10 Zalesye | 10+10 | 9.362 | 1.13 | 120 | 8.232 | 0 | 10.5 | 2.268 | 2.268 | opened
| Nom. capacity MV, МVА | 10+10 | 2.187 |  |  | 2.187 | 0 | 10.5 | 8.313
| Nom. capacity LV, МVА | 10+10 | 7.175 | 1.13 | 120 | 6.045 | 0 | 10.5 | 4.455
143 | SS 110/10 Lugovaya | 6,3+6,3 | 2.93 |  |  | 2.93 | 0 | 6.62 | 3.69 | 3.69 | opened
144 | SS 110/35/10 Lom | 10+10 | 8.743 | 1.54 | 120 | 7.203 | 0 | 10.5 | 3.297 | 3.297 | opened
| Nom. capacity MV, МVА | 10+10 | 6.877 |  |  | 6.877 | 0 | 10.5 | 3.623
| Nom. capacity LV, МVА | 10+10 | 1.866 | 1.54 | 120 | 0.326 | 0 | 10.5 | 10.174
145 | SS 35/10 Varegovo | 2,5+1,6 | 0.88 |  |  | 0.88 | 0 | 1.68 | 0.8 | 0.8 | opened
146 | SS 110/35/10 Shestikhino | 10+10 | 8.57 | 0.306 | 120 | 8.264 | 0 | 10.5 | 2.236 | 2.236 | opened
| Nom. capacity MV, МVА | 10+10 | 7.809 |  |  | 7.809 | 0 | 10.5 | 2.691
| Nom. capacity LV, МVА | 10+10 | 0.761 | 0.306 | 120 | 0.455 | 0 | 10.5 | 10.045
147 | SS 110/35/10 Kryukovo | 6.3 | 2.327 | 0.87 | 24 hours | 1.457 | 0 | 6.62 | 5.163 | 4.543 | opened
| Nom. capacidty MV, МVА | 6.3 | 2.077 |  |  | 2.077 | 0 | 6.62 | 4.543
| Nom. capacity LV, МVА | 6.3 | 0.25 | 0.87 | 24 hours | -0.62 | 0 | 6.62 | 7.24
148 | SS 35/10 Beloe | 2.5 | 0.74 | 1.58 | 24 hours | 1.58 | 0 | 1.58 | 0.84 | 0.84 | opened
149 | SS 110/35/10 Glebovo | 10 | 6.473 | 0.654 | 24 hours | 5.819 | 0 | 10.5 | 4.681 | 4.681 | opened
| Nom. capacity MV, МVА | 10 | 3.485 |  |  | 3.485 | 0 | 10.5 | 7.015
| Nom. capacity LV, МVА | 10 | 2.988 | 0.654 | 24 hours | 2.334 | 0 | 10.5 | 8.166
150 | SS 35/10 Ermakovo | 1.6 | 1.02 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | -0.15 | -0.15 | closed
151 | SS 35/10 Milyushino | 1.6 | 0.78 | 1.053 | 24 hours | 1.053 | 0 | 1.053 | 0.273 | 0.273 | opened
152 | SS 35/10 Sutka | 2.5 | 0.68 | 0.87 | 24 hours | 0.87 | 0 | 0.87 | 0.19 | 0.19 | opened
153 | SS 35/10 Sit | 1.6 | 0.55 | 0.55 | 24 hours | 0.55 | 0 | 0.55 | 0 | 0 | opened
154 | SS 35/10 Gorelovo | 1.6 | 0.67 | 0.78 | 24 hours | 0.78 | 0 | 0.78 | 0.11 | 0.11 | opened
155 | SS 35/6 Pishchalkino | 1.6 | 0.89 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 0.79 | 0.79 | opened
156 | SS 35/6 Varegovo | 1.6 | 0.258 | 1.68 | 24 hours | 1.68 | 0 | 1.68 | 1.422 | 1.422 | opened
| Total: | 2618.6 | 907.904
| deficit | [8 empty] | -17.385
| proficit | [8 empty] | 511.476